## PDB Bill AMR
BPDB BILL FOR DPDC
[8 empty] | 132 KV LEVEL |  |  |  | Month June-2023 | [45 empty] | Considering P.F | [17 empty] | 132KV LEVEL | [7 empty] | Month :January--2018
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import / Export at 132 kV level |  | Remarks for KWH | KVAR CALCULATION | [5 empty] | PFC Calculation |  |  |  |  | Remarks for KVAR | Remarks for KVAR |  |  |  | DPDC |  |  |  | PDB |  |  |  |  | DPDC-PDB | [17 empty] | 0.9 | 0.9 | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import / Export at 132 kV level |  | KVAR CALCULATION |  |  | Reactive Energy Import / Export at 132 kV level |  | P.F | Remark
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Diff. | KVAR Import | KVAR Export | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit |  |  |  |  | NAME OF THE CIRCUIT | PF | CF | Pfc unit | PFC Surcharge | PF | CF | Pfc unit | PFC Surcharge | Difference |  |  |  | PF | 132 kv PFC CALCULATION===> | [13 empty] | 0.9 | 0.9 | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff | Diff | [5 empty] | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 19 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 29 | 30 |  |  | 2 | [7 empty] | Rate | Unit | Taka | [7 empty] | (A) 132 KV Level | [6 empty] | Month June-2023 |  |  | 0.9 | 0.9 | [11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [27 empty] | 0.89 | 0.005 | [18 empty] | SS | Meter No | Feeder Name | Net Mwh | Net Mvarh | PF | Percent | PF Unit | PFCharge(Tk.) | Remark | 0.9 | 0.9
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | AMR | Digital | 960000 | 2226.297 | 2227.617 | 1.32 |  | 1267200 |  |  | 1943.884 | 1950.36 | 6.476 |  | 6216960 | 938880 | 5227200 | 0.94 | 0 | 0 | Loop PFC is Considered |  | 0.88 | 0.01 | Hasnabad to Lalbagh | 0.94 | 0 | #REF! | #REF! | 0.8 | 9% | 3715286 | 21838451.108 | #REF! | #REF! | 0.89 | 0.005 | #REF! |  | 17610187.05 | #REF! |  | HARIG | EXP-08993646E | Haripur-Matuail 132 KV CKT | 18988800 | 7176000 | 0.94 |  |  |  |  | 0.9 | 0.9 | 0 | 1267200 | 0 | 31939200 | 0 | -30672000 | [5 empty] | 1 | Hasnabad to Lalbagh | Hasnabad Grid | 132 | Export | 8993531 | AMR | Digital | 960000 | 2226.297 | 2227.617 | 1.32 |  | 1267200 | 2020.336 | 2046.546 | 26.21 |  | 25161600 | 0.050299
|  |  | 132 | Import |  |  |  | 960000 | 666.114 | 666.456 | 0.342 | 328320 |  |  |  | 372.088 | 373.119 | 1.031 | 989760 | [5 empty] | 0 |  |  | 0.87 | 0.02 | [11 empty] | 0.88 | 0.01 | [5 empty] | HARIG | EXP-08993647E | Haripur-Shyampur 132 KV CKT IMP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0.9 | 0.9 | 328320 | 0 |  |  | 328320 | 0 | [8 empty] | 132 | Import |  |  |  | 960000 | 666.114 | 666.456 | 0.342 | 328320 |  | 1108.958 | 1108.958 | 0 | 0 |  | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | AMR | Digital | 960000 | 231.085 | 260.441 | 29.356 |  | 28181760 |  |  | 103.312 | 116.75 | 13.438 |  | 12900480 | 28181760 | 12900480 | 0.91 | 0 | 0
|  |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | AMR | Digital | 960000 | 117.004 | 125.28 | 8.276 |  | 7944960 |  |  | 41.721 | 44.06 | 2.339 |  | 2245440 | 7944960 | 2245440 | 0.96 | 0 | 0 |  |  | 0.86 | 0.03 | Hasnabad to Shyampur | 0.96 | 0 | #REF! | #REF! | 0.86 | 3% | 936662 | 5505699.236 | #REF! | #REF! | 0.87 | 0.02 | #REF! |  | 3624083.25 | #REF! |  | HARIG |  |  | 18789120 | 6920640 | 0.94 | 0% | #REF! | #REF! |  | 0.9 | 0.9 | 0 | 7944960 |  | 25914240 | 0 | -17969280 | [5 empty] | 2 | Hasnabad to Shyampur |  | 132 | Export | 8993532 | AMR | Digital | 960000 | 117.004 | 125.28 | 8.276 |  | 7944960 | 1401.753 | 1424.799 | 23.046 |  | 22124160 | 0.33798
|  |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  | 0.85 | 0.04 | [11 empty] | 0.86 | 0.03 | [5 empty] | HASNG | EXP-50146912E | Hasnabad-kamrangirchar 132 kv CKT-1 IMP | 37065600 | 20373120 | 0.88 | 0% | #REF! | #REF! | disputed | 0.9 | 0.9 | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  | 131.694 | 131.694 | 0 | 0 |  | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | AMR | Digital | 960000 | 363.871 | 363.871 | 0 |  | 0 |  |  | 211.998 | 211.998 | 0 |  | 0 | 0 | 0 |  |  | 0 | [22 empty] | HASNG | EXP-08993531E | Hasnabad-Lalbag 132 KV CKT IMP | 938880 | 5227200 | 0.94 | 0% | #REF! | #REF! | [23 empty] | 363.871
|  |  | 132 | Import |  |  |  | 960000 | 5.419 | 5.419 | 0 | 0 |  |  |  | 4.069 | 4.069 | 0 | 0 | [5 empty] | 0 | [22 empty] | HASNG | EXP-08993532E | Hasnabad-Shyampur 132 KV CKT IMP | 7944960 | 2245440 | 0.96 | 0% | #REF! | #REF! | [23 empty] | 5.419
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [10 empty] | Total=> | 328320 | 37393920 | 37065600 | Total=> |  |  |  | 989760 | 21362880 | 37065600 | 20373120 | 0.88 |  | 0 |  |  | 0.84 | 0.05 | Hasnabad to Kamrangirchar | 0.88 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! | 0.85 | 0.04 | #REF! |  |  | 17576092.7654 |  | KALLG | EXP-5014660E | Kallyanpur-Lalbag 132 kv Ckt-2 Exp | 18802560 | 9370560 | 0.9 | 0 | #REF! | #REF! |  | 0.9 | 0.9 | 328320 | 37393920 |  | 26328000 | 328320 | 11065920 | [5 empty] | 3 | Hasnabad to Kamrangirchar |  | 132 | Export | 50146912 | AMR | Digital | 960000 | 0 | 0 | 0 |  | 0 | 362.107 | 372.478 | 10.371 |  | 9956160 | #DIV/0!
6 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Export | 8993624 | AMR | Digital | 960000 | 4743.032 | 4768.057 | 25.025 |  | 24024000 |  |  | 2372.854 | 2380.261 | 7.407 |  | 7110720 | 24024000 | 7110720 | 0.96 | 0 | 0 |  |  | 0.81 | 0.08 | [11 empty] | 0.82 | 0.07 | [5 empty] | MANIG | 50147582E | 230/132 kv Transformer-2 | 103233600 | 32656320 | 0.95 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 24024000 | 197760 |  | -197760 | 24024000 | [8 empty] | 132 | Import |  |  |  | 960000 | 4743.032 | 4768.057 | 25.025 | 24024000 |  | 2.109 | 2.187 | 0.078 | 74880 |  | 1
|  |  | 132 | Import |  | AMR |  | 960000 | 11.003 | 11.003 | 0 | 0 |  |  |  | 7.78 | 7.78 | 0 | 0 | [5 empty] | 0 |  |  | 0.8 | 0.09 | [11 empty] | 0.81 | 0.08 |  |  | 0 |  |  | PPACK | EXP-12393383E | Powerpack-Hasnabad-Kamrangirchar 132 kv | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | P.Plant | #REF! | #REF! | 0 | 0 | 197760 | 84181440 | -197760 | -84181440 | [16 empty] | Total=> | #REF! | #REF! |  |  |  | 74880 | 57241920
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [10 empty] | Total=> | 0 | 24024000 | 24024000 | Total=> |  |  |  | 0 | 7110720 | 24024000 | 7110720 | 0.96 |  | 0 |  |  | 0.78 | 0.12 | [11 empty] | 0.79 | 0.105 | [5 empty] | RAMPG | EXP-08993661E | Rampura-Mogbazar 132 kv CKT-2 | 11003520 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 24024000 |  |  | 0 | 24024000 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 2.168 | 2.179 | 0.011 | 10560 |  | #DIV/0!
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | AMR | Digital | 960000 | 1078.582 | 1098.154 | 19.572 |  | 18789120 |  |  | 748.04 | 755.249 | 7.209 |  | 6920640 | 18789120 | 6920640 | 0.94 | 0 | 0 |  |  | 0.77 | 0.135 | Maniknager-2 (new line) | 0.94 | 0 | #REF! |  | 0.91028 | [5 empty] | 0.78 | 0.12 | #REF! |  | 423441.72 | #REF! |  | RAMPG | EXP-08993661E | Rampura-Ullon U/G 132 kv CKT-2 | 88166400 | 34776960 | 0.93 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 18789120 |  | 17099520 | 0 | 1689600 | [5 empty] | 6 | Maniknager-2 (new line) |  | 132 | Export | 8993624 | AMR | Digital | 960000 | 1078.582 | 1098.154 | 19.572 |  | 18789120 | 1800.618 | 1803.395 | 2.777 |  | 2665920 | 0.99008
|  |  | 132 | Import |  | AMR |  | 960000 | 70.056 | 70.056 | 0 | 0 |  |  |  | 141.149 | 141.149 | 0 | 0 | [5 empty] | 0 |  |  | 0.76 | 0.15 | [11 empty] | 0.77 | 0.135 | [5 empty] | RAMPG | EXP-08993661E | Rampura-Madartheck 132 kv CKT-1 | 62636160 | 19319040 | 0.94 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 | 22080 |  | -22080 | 0 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 70.056 | 70.056 | 0 | 0 |  | 0.11 | 0.289 | 0.179 | 171840 |  | #DIV/0!
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | AMR | Digital | 960000 | 255.206 | 274.986 | 19.78 |  | 18988800 |  |  | 101.496 | 108.971 | 7.475 |  | 7176000 | 18988800 | 7176000 | 0.94 | 0 | 0 |  |  | 0.75 | 0.165 | Matuail | 0.94 | 0 | #REF! | 0 | 0 | [5 empty] | 0.76 | 0.15 | #REF! |  |  |  |  | SIDDG | 08993683E | Siddhirgonj 132/33 kv Transformer-1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 18988800 |  | 29952960 | 0 | -10964160 | [5 empty] | 7 | Matuail |  | 132 | Export | 8993646 | AMR | Digital | 960000 | 255.206 | 274.986 | 19.78 |  | 18988800 | 1660.595 | 1660.595 | 0 |  | 0 | 0
|  |  | 132 | Import |  | AMR |  | 960000 | 4.361 | 4.361 | 0 | 0 |  |  |  | 30.491 | 30.491 | 0 | 0 | [5 empty] | 0 | [15 empty] | 0.75 | 0.165 | [5 empty] | SIDDG | 08993682E | Siddhirgonj 132/33 kv Transformer-2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 4.361 | 4.361 | 0 | 0 |  | 0.002 | 0.002 | 0 | 0 |  | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [10 empty] | Total=> | 0 | 37777920 | 37777920 | Total=> |  |  |  | 0 | 14096640 | 37777920 | 14096640 | 0.94 |  | 0 | [19 empty] | #REF! |  |  | SIDDG | EXP-08993681E | Siddhirgong-Ullon 132 kv CKT-1 IMP | 12288000 | 1241280 | 0.99 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 37777920 | 22080 | 47052480 | -22080 | -9274560 | [16 empty] | Total=> | 0 | 37777920 |  |  |  | 182400 | 2665920
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 |  | Digital | 480000 | 2736.898 | 2778.291 | 41.393 |  | 19868640 |  |  | 1120.433 | 1135.696 | 15.263 |  | 7326240 | 19868640 | 7326240 | 0.94 | 0 | 0 |  |  |  |  | Kallyanpur to Lalbagh 1 | 0.94 | 0 | #REF! |  | 0.92609 | [7 empty] | #REF! |  | 304546.23 | #REF! |  | SIDDG | EXP-08993680E | Siddhirgong-Maniknagar 132 kv CKT-2 IMP | 11610240 | 1743360 | 0.99 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 19868640 |  | 349440 | 0 | 19519200 | [5 empty] | 8 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | AMR | Digital | 960000 | 2736.898 | 2778.291 | 41.393 |  | 39737280 | 634.446 | 634.49 | 0.044 |  | 42240 | 1
10 | Tranformer 1 |  | 132 | Export | 80505634 | AMR |  | 480000 | 8341.911 | 8380.88 | 38.969 |  | 18705120 |  |  | 4899.194 | 4918.609 | 19.415 |  | 9319200 | 18705120 | 9319200 | 0.9 | 0 | 0 | [22 empty] | SIDDG | EXP- 8993555E | Siddhirgong-Matuail 132 kv CKT IMP | 26601600 | 11219520 | 0.92 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 18705120 |  |  | 0 | 18705120 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 8341.911 | 8380.88 | 38.969 | 37410240 |  | 132.04 | 132.04 | 0 | 0 |  | 0
11 | Tranformer 2 |  | 132 | Export | 80505637 | AMR |  | 480000 | 8293.77 | 8332.942 | 39.172 |  | 18802560 |  |  | 4858.482 | 4878.004 | 19.522 |  | 9370560 | 18802560 | 9370560 | 0.9 | 0 | 0 |  |  |  |  | Kallyanpur to Lalbagh 2 | 0.9 | 0 | #REF! | 0 | 0.93379 | [7 empty] | #REF! |  |  |  |  | SITAG | 080505634NE | Sitalakhya 132/33 kv Transformer-1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 18802560 |  | 352320 | 0 | 18450240 | [5 empty] | 9 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | AMR | Digital | 960000 | 8293.77 | 8332.942 | 39.172 |  | 37605120 | 6.002 | 6.043 | 0.041 |  | 39360 | 1
12 | MI CEMENT |  | 132 | Export | 38992489 (New) |  |  | 480000 | 237.085 | 256.334 | 19.249 |  | 9239520 |  |  | 46.824 | 50.024 | 3.2 |  | 1536000 | 9239520 | 1536000 | 0.99 | 0 | 0 | Main+ Backup | [21 empty] | SITAG | 080505637NE | Sitalakhya 132/33 kv Transformer-2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 9239520 |  |  | 0 | 9239520 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 237.085 | 256.334 | 19.249 | 18479040 |  | 2.422 | 2.425 | 0.003 | 2880
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [10 empty] | Total=> |  | 66615840 | 66615840 | Total=> |  |  |  |  | 27552000 | 66615840 | 27552000 | 0.92 | 0 | 0 | [19 empty] | 0 |  |  |  |  | Sub Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 66615840 |  | 701760 | 0 | 65914080 | [16 empty] | Total=> | 55889280 | 77342400 |  |  | 0 | 2880 | 81600
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | AMR | Digital | 960000 | 8261.732 | 8298.965 | 37.233 |  | 35743680 |  |  | 4614.751 | 4632.01 | 17.259 |  | 16568640 | 35743680 | 16568640 | 0.91 | 0 | 0 |  |  |  |  | 132 kv DPAL | [27 empty] | #REF! | #REF! | 0 | 35743680 |  |  | 0 | 35743680 | [5 empty] | PP | 132 kv DPAL |  | 132 | Export | 16529653 |  |  | 144000 | 8261.732 | 8298.965 | 37.233
14 | XFR- T2 |  | 132 | Export | 8993682 | AMR | Digital | 960000 | 8252.57 | 8289.656 | 37.086 |  | 35602560 |  |  | 4609.479 | 4626.732 | 17.253 |  | 16562880 | 35602560 | 16562880 | 0.91 | 0 | 0 | [24 empty] | PDB Bill= |  |  |  |  | 12015662.3971 | 70628063.57 |  | #REF! | #REF! | 0 | 35602560 |  |  | 0 | 35602560 | [8 empty] | 132 | Import |  |  |  | 144000 | 8252.57 | 8289.656 | 37.086
15 | Ullon-1 |  | 132 | Export | 8993681 | AMR | Digital | 1440000 | 2593.526 | 2618.149 | 24.623 |  | 35457120 |  |  | 1364.675 | 1368.787 | 4.112 |  | 5921280 | 35457120 | 5921280 | 0.99 | 0 | 0 | [24 empty] | Difference= |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 35457120 |  |  | 0 | 35457120
|  |  | 132 | Import |  | AMR |  | 1440000 | 9.184 | 9.184 | 0 | 0 |  |  |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0 |  |  |  |  | Tranformer 3 | 0 | 0 | #REF! |  | 0.91797 | [7 empty] | #REF! | [27 empty] | 10 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 |  | Digital | 480000 | 9.184 | 9.184 | 0 |  | 0 | 155.967 | 169.111 | 13.144 |  | 6309120 | #DIV/0!
16 | Ullon-2 |  | 132 | Export | 8993680 | AMR | Digital | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 |  |  | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Tranformer 1 | 0 | 0 | #REF! | #REF! | 0.85075 | 4% | 550541 | 3236079.998 | #REF! | #REF! |  |  | #REF! |  | 4415892.17 | #REF! |  | (B) 33 KV Level | [9 empty] | #REF! | #REF! | 0 | 0 |  | 18315840 | 0 | -18315840 | [5 empty] | 11 | Tranformer 1 |  | 132 | Export | 80505634 | AMR |  | 480000 | 1373.548 | #REF! | #REF! |  | #REF! | 3659.429 | 3677.143 | 17.714 |  | 8502720 | #REF!
|  |  | 132 | Import |  | AMR |  | 1440000 | 22.279 | 22.279 | 0 | 0 |  |  |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0 |  |  |  |  | Tranformer 2 | 0 | 0 | #REF! | #REF! | 0.85475 | 4% | 562291 | 3305146.498 | #REF! | #REF! |  |  | #REF! |  | 4436657.97 | #REF! |  | SS | Meter No | Feeder Name | Net Mwh | Net Mvarh | PF | Percent | PF Unit | PFCharge(Tk.) | Remark | #REF! | #REF! | 0 | 0 |  | 18543840 | 0 | -18543840 | [5 empty] | 12 | Tranformer 2 |  | 132 | Export | 80505637 | AMR |  | 480000 | 22.279 | 22.279 | 0 |  | 0 | 3613.988 | 3631.772 | 17.784 |  | 8536320 | #DIV/0!
17 | Matuail |  | 132 | Export | 8993555 |  |  | 1440000 | 2725.888 | 2753.041 | 27.153 |  | 39100320 |  |  | 1272.534 | 1284.566 | 12.032 |  | 17326080 | 39100320 | 17326080 | 0.91 | 0 | 0 |  |  |  |  | MI CEMENT | 0.91 | 0 | #REF! |  | 0.97856 | [7 empty] | #REF! | [14 empty] | #REF! | #REF! | 0 | 39100320 |  | 6388800 | 0 | 32711520 | [5 empty] | 13 | MI CEMENT |  | 132 | Export | 8993599 |  |  | 480000 | 2725.888 | 2753.041 | 27.153 |  | 13033440 | 86.18 | 90.41 | 4.23 |  | 2030400 | 0.98808
|  |  | 132 | Import |  |  |  | 1440000 | 771.699 | 771.699 | 0 | 0 |  |  |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0 | [19 empty] | 0 |  |  | HASNG | 8993839 | Hasnabad-Lalbag 33kv CKT-1 | 7832160 | 3090420 | 0.9302 | 0% | #REF! | #REF! |  | #REF! | #REF! | 1373.548 | 0 |  | 43248480 | 1373.548 | -43248480 | [18 empty] | #REF! |  |  |  |  | 25378560
[11 empty] | Total=> | 0 | 145903680 | 145903680 | Total=> |  |  |  | 0 | 56378880 | 145903680 | 56378880 | 0.93 |  | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [7 empty] | 132 KV LEVEL |  |  |  | Month June-2023
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | AMR | Digital | 960000 | 5714.359 | 5756.396 | 42.037 |  | 40355520 |  |  | 2921.368 | 2941.337 | 19.969 |  | 19170240 | 40355520 | 19170240 | 0.9 | 0 | 0 | [23 empty] | 8993831 | Hasnabad-Postogola 33kv CKT | 6627420 | 2605680 | 0.93065 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 40355520 |  |  | 0 | 40355520
|  |  |  | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0 |  |  |  |  | XFR- T1 | 0 | 0 | #REF! | #REF! | 0.88207 | 1% | 257688 | 1514690.064 | #REF! | #REF! |  |  | #REF! |  | 2442859.18 | #REF! |  | KALLG | 0 | Kallyanpur-Lalmatia 33Kv U/G CKT | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  | 25236000 | 0 | -25236000 | [5 empty] | 14 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | AMR | Digital | 480000 | 0 | 0 | 0 |  | 0 | 3455.283 | 3483.956 | 28.673 |  | 13763040 | #DIV/0!
19 | Mogbazar-2 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 4882.347 | 4914.803 | 32.456 |  | 31157760 |  |  | 2485.2 | 2500.392 | 15.192 |  | 14584320 | 31157760 | 14584320 | 0.91 | 0 | 0 | [20 empty] | #REF! |  |  | 0 | Kallyanpur-Sherebanglanagar 33Kv U/G CKT | 0 | 0 | 0 | 0% | #REF! | #REF!
|  |  |  | Import |  | AMR |  | 960000 | 0.084 | 0.084 | 0 | 0 |  |  |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0 |  |  |  |  | XFR- T2 | 0 | 0 | #REF! | #REF! | 0.88144 | 1% | 261797 | 1538842.766 | #REF! | #REF! |  |  | #REF! |  |  |  |  | SATMG | 0 | Satmosjid 132/33 Transformer 2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  | 25056000 | 0 | -25056000 | [5 empty] | 15 | XFR- T2 |  | 132 | Export | 8993682 | AMR | Digital | 480000 | 0.084 | 0.084 | 0 |  | 0 | 3443.894 | 3473.119 | 29.225 |  | 14028000 | #DIV/0!
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 4374.65 | 4387.45 | 12.8 |  | 12288000 | 83379360 |  | 1767.606 | 1768.899 | 1.293 |  | 1241280 | 12288000 | 1241280 | 0.99 | 0 | 0 |  |  |  |  | Ullon-1 | 0.99 | 0 | #REF! |  | 0 | [7 empty] | #REF! |  | 1720626.97 | #REF! |  |  | 0 | Satmosjid 132/33 Transformer 1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 12288000 |  | 19805760 | 0 | -7517760 | [5 empty] | 16 | Ullon-1 |  | 132 | Export | 8993681 | AMR | Digital | 1440000 | 4374.65 | 4387.45 | 12.8 |  | 18432000 | 1028.421 | 1028.891 | 0.47 |  | 676800
|  |  |  | Import |  | AMR |  | 960000 | 1.56 | 1.56 | 0 | 0 |  |  |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0 | [24 empty] | Sub Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 1440000 | 1.56 | 1.56 | 0 | 0 |  | 17.383 | 17.383 | 0 | 0 |  | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | AMR | Digital | 960000 | 4060.204 | 4072.298 | 12.094 |  | 11610240 |  |  | 1628.497 | 1630.313 | 1.816 |  | 1743360 | 11610240 | 1743360 | 0.99 | 0 | 0 |  |  |  |  | Maniknagar -1 | 0.99 | 0 | #REF! | 0 | 0.54893 |  |  |  |  | D |  |  | #REF! |  | 286432.59 | #REF! | [11 empty] | #REF! | #REF! | 0 | 11610240 |  |  | 0 | 11610240 | [5 empty] | 17 | Maniknagar -1 |  | 132 | Export | 8993680 | AMR | Digital | 1440000 | 4060.204 | 4072.298 | 12.094 |  | 17415360 | 1172.921 | 1173.122 | 0.201 |  | 289440 | 0.99986
|  |  |  | Import |  | AMR |  | 960000 | 1.329 | 1.329 | 0 | 0 |  |  |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  | 0.80443 |  |  |  |  | D | [5 empty] | #REF! |  |  |  | PDB Bill= |  |  |  |  | 966275.4892 | 5728081.1 |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 1440000 | 1.329 | 1.329 | 0 | 0 |  | 7.625 | 10.539 | 2.914 | 4196160 |  | #DIV/0!
22 | Madartheck 1 |  | 132 | Export | 50146667 | AMR | Digital | 960000 | 1730.856 | 1758.566 | 27.71 |  | 26601600 |  |  | 630.701 | 642.388 | 11.687 |  | 11219520 | 26601600 | 11219520 | 0.92 | 0 | 0 | [19 empty] | 9263097.88 | #REF! |  |  |  | Difference= |  |  |  |  | #REF! | #REF! | [23 empty] | 1730.856 | 1758.566 | 27.71
23 | Madartheck 2 |  | 132 | Export | 50146668 | AMR | Digital | 960000 | 1525.358 | 1552.894 | 27.536 |  | 26434560 |  |  | 655.937 | 667.626 | 11.689 |  | 11221440 | 26434560 | 11221440 | 0.92 | 0 | 0 | [19 empty] | 0 |  |  |  |  | G.Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 26434560 |  | 70097760 | 0 | -43663200 | [16 empty] | Total=> | 0 | 35847360 |  |  |  | 4196160 | 28757280
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | AMR | Digital | 960000 | 134.079 | 145.541 | 11.462 |  | 11003520 |  |  | 2.481 | 2.481 | 0 |  | 0 | 11003520 | 0 | 0 | 0 | 0 |  |  |  |  | Mogbazar-1 | 0 | 0 | #REF! | #REF! | 0.87223 | 2% | 449203 | 2640415.234 | #REF! | #REF! |  |  | #REF! |  | 4005767.65 | #REF! | [11 empty] | #REF! | #REF! | 0 | 11003520 |  | 28729920 | 0 | -17726400 | [5 empty] | 18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | AMR | Digital | 960000 | 134.079 | 145.541 | 11.462 |  | 11003520 | 1862.487 | 1875.606 | 13.119 |  | 12594240 | 0.65795
| Dhaka University-1 (Imp) |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 51.664 | 55.44 | 3.776 | 3624960 |  | 0 | [36 empty] | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 |  | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | AMR | Digital | 960000 | 135.244 | 146.811 | 11.567 |  | 11104320 |  |  | 1.801 | 1.801 | 0 |  | 0 | 11104320 | 0 | 0 | 0 | 0 |  |  |  |  | Mogbazar-2 | 0 | 0 | #REF! | #REF! | 0.85962 | 4% | 712666 | 4189050.748 | #REF! | #REF! |  |  | #REF! |  | 1576789.96 | #REF! | [11 empty] | #REF! | #REF! | 0 | 11104320 |  | 22309440 | 0 | -11205120 | [5 empty] | 19 | Mogbazar-2 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 135.244 | 146.811 | 11.567 |  | 11104320 | 1668.059 | 1679.09 | 11.031 |  | 10589760 | 0.72368
| Dhaka University-2 (Imp) |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 51.662 | 58.541 | 6.879 | 6603840 | [38 empty] | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 |  | 0
Maniknagar 230/132 Kv s/s | [10 empty] | Total=> | 0 | 170555520 | 170555520 | Total=> |  |  |  | 10228800 | 59180160 | 170555520 | 48951360 | 0.96 |  | 0 |  |  |  |  | Ullon U/G -1 | 0.96 | 0 |  |  | 0.92127 | [7 empty] | #REF! |  | 0 | [12 empty] | #REF! | #REF! | 0 | 170555520 |  | 20752320 | 0 | 149803200 | [5 empty] | 20 | Ullon U/G -1 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 0 | 0 | 0 |  | 288 | 1191.821 | 1208.951 | 17.13 |  | 16444800 | #DIV/0!
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 |  |  | 1920000 | 3087.962 | 3134.038 | 46.076 |  | 88465920 |  | July | 1574.245 | 1592.402 | 18.157 |  | 34861440 | 88465920 | 34861440 | 0.93 | 0 | 0 | [32 empty] | #REF! | #REF! | 0 | 88465920 |  |  | 0 | 88465920 | [9 empty] | Import |  | AMR |  | 960000 | 3087.962 | 3134.038 | 46.076 | 44232960 |  | 4.871 | 4.871 | 0 | 0 |  | 0
27 | Maniknagar-2 |  | 132 | Export | 50147585 |  |  | 1920000 | 3081.57 | 3127.49 | 45.92 |  | 88166400 |  |  | 1571.752 | 1589.865 | 18.113 |  | 34776960 | 88166400 | 34776960 | 0.93 | 0 | 0 |  |  |  |  | Ullon U/G -2 | 0.93 | 0 |  |  | 0.9144 | [7 empty] | #REF! |  | 1640187.72 | #REF! | [11 empty] | #REF! | #REF! | 0 | 88166400 |  | 19657920 | 0 | 68508480 | [5 empty] | 21 | Ullon U/G -2 |  | 132 | Export | 8993660 | AMR | Digital | 960000 | 3081.57 | 3127.49 | 45.92 |  | 44083200 | 1094.655 | 1111.663 | 17.008 |  | 16327680 | 0.93774
Shyampur 230/132 Kv s/s | [10 empty] | Total=> |  | 176632320 | 176632320 | T-1 Missing Unit |  |  |  |  | 69638400 | 176632320 | 69638400 | 0.93 | [34 empty] | #REF! | #REF! | 0 | 176632320 | 1920 |  | -1920 | 176632320 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 3.421 | 3.421 | 0 | 0 |  | 0
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 |  |  | 1920000 | 1376.368 | 1408.991 | 32.623 |  | 62636160 |  | 0 | 686.869 | 696.931 | 10.062 |  | 19319040 | 62636160 | 19319040 | 0.94 | 0 | 0 | Loop PFC is Considered |  |  |  | Madartheck 1 | 0.94 | 0 |  |  | 0.93148 | [7 empty] | #REF! |  | 403606.99 | #REF! | [11 empty] | #REF! | #REF! | 0 | 62636160 |  | 6391680 | 0 | 56244480 | [5 empty] | 22 | Madartheck 1 |  | 132 | Export | 50146667 | AMR | Digital | 960000 | 1376.368 | 1408.991 | 32.623 |  | 31318080 | 182.547 | 185.946 | 3.399 |  | 3263040 | 0.99462
|  |  | 132 | Import | wp002497 |  |  | 1920000 | 0.245 | 0.245 | 0 | 0 |  |  |  | 9.391 | 9.392 | 0.001 | 1920 |  |  |  |  | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 |  |  | 1920000 | 0.216 | 0.216 | 0 | 0 |  |  |  | 9.657 | 9.657 | 0 | 0 | [6 empty] | 0 | Missing Unit |  |  | Madartheck 2 | 0 |  |  |  | 0.92039 | [7 empty] | #REF! | [14 empty] | #REF! | #REF! | 0 | 0 |  | 6862080 | 0 | -6862080 | [5 empty] | 23 | Madartheck 2 |  | 132 | Export | 50146668 | AMR | Digital | 960000 | 0.216 | 0.216 | 0 |  | 0 | 152.673 | 156.273 | 3.6 |  | 3456000 | #DIV/0!
|  |  | 132 | Export | 38992559 |  |  | 1920000 | 1467.736 | 1500.185 | 32.449 |  | 62302080 |  |  | 726.775 | 736.877 | 10.102 |  | 19395840 | 62302080 | 19395840 | 0.94 | 0 | 0 | Loop PFC is Considered | [53 empty] | 1467.736
keranigonj 230/132 Kv s/s | [6 empty] | PDB | 81086400 |  |  | Total=> | 0 | 124938240 | 124938240 |  |  |  | 38712960 | 1920 | 38714880 | 124938240 | 38712960 | 0.94 | [56 empty] | 0
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 |  |  | 1440000 | 816.161 | 851.661 | 35.5 |  | 51120000 |  |  | 185.308 | 190.217 | 4.909 |  | 7068960 | 51120000 | 7063200 | 0.99 | 0 | 0 | [54 empty] | 816.161
|  |  | 132 | Import |  |  |  | 1440000 | 0.021 | 0.021 | 0 | 0 |  |  |  | 0.831 | 0.835 | 0.004 | 5760 | [60 empty] | 0.021
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 |  |  | 1440000 | 539.605 | 575.795 | 36.19 |  | 52113600 |  |  | 217.857 | 235.63 | 17.773 |  | 25593120 | 52113600 | 25593120 | 0.9 | 0 | 0 | [19 empty] | 0 | [12 empty] | #REF! | #REF! | 0 | 52113600 | 1920 | 104703360 | -1920 | -52589760 | [16 empty] | Total=> | 44232960 | 97509408 |  |  |  | 0 | 62675520
|  |  | 132 | Import |  |  |  | 1440000 | 0 | 0 | 0 | 0 |  |  |  | 0.831 | 0.831 | 0 | 0 |  | 0 | 0 | [7 empty] | Maniknagar-1 | 0 | 0 | #REF! | #REF! | 0.88854 | 1% | 586810 | 3449269.18 | #REF! | #REF! | 3 |  | #REF! |  | 3285623.31 | #REF! | [11 empty] | #REF! | #REF! | 0 | 0 |  | 37914240 | 0 | -37914240 | [5 empty] | 24 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 |  |  | 1920000 | 0 | 0 | 0 |  | 0 | 645.022 | 660.803 | 15.781 |  | 30299520 | #DIV/0!
Madangonj 132/33 Kv s/s | [10 empty] | Total=> | 0 | 103233600 | 103233600 | Missing Unit |  |  |  | 5760 | 32662080 | 103233600 | 32656320 | 0.95 |  |  | Missing Unit |  |  |  | Maniknagar-2 | 0.95 | 0 | #REF! | #REF! | 0.88875 | 1% | 578093 | 3398030.654 | #REF! | #REF! | 2 |  | #REF! |  | 3282801.87 | #REF! | [11 empty] | #REF! | #REF! | 0 | 103233600 |  | 38054400 | 0 | 65179200 | [5 empty] | 25 | Maniknagar-2 |  | 132 | Export | 50147585 |  |  | 1920000 | 0 | 0 | 0 |  | 0 | 646.845 | 662.374 | 15.529 |  | 29815680 | #DIV/0!
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 |  |  | 960000 | 235.539 | 247.775 | 12.236 |  | 11746560 |  | 0 | 61.712 | 64.691 | 2.979 |  | 2859840 | 11746560 | 2859840 | 0.97 | 0 | 0 | 0 | [16 empty] | #REF! |  | #REF! |  | 67003528.91 | 11399035.2007 | [9 empty] | #REF! | #REF! | 0 | 11746560 |  | 75968640 | 0 | -64222080 | [12 empty] | PDB | 81086400 | Diff | Diff | Total=> |  | 0 |  |  |  | 0 | 60115200
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [9 empty] | 16853.26 | [6 empty] | 4103
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 |  |  | 960000 | 144.939 | 159.043 | 14.104 |  | 13539840 |  |  | 31.207 | 35.118 | 3.911 |  | 3754560 | 13539840 | 3754560 | 0.96 | 0 | 0 | [21 empty] | #REF! | #REF! | [9 empty] | #REF! | #REF! | 0 | 13539840 | 221760 | 425953920 | -221760 | -412414080 | [7 empty] | TOTAL Import | [6 empty] | Active Energy ==> |  |  | #REF! | #REF! | Reactive Energy ==> |  |  | 4456320 | 236916000
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [9 empty] | 354818.25 | [6 empty] | 98390
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 |  |  | 960000 | 32.177 | 32.177 | 0 |  | 0 |  |  | 16.205 | 16.205 | 0 |  | 0 | 0 | 0 | [8 empty] | Unit | #REF! | #REF! | #REF! |  |  | 8611037 | 50615675.486 | #REF! | #REF! | #REF! |  |  |  | #REF! | [12 empty] | #REF! | #REF! |  | 0 |  | 425732160 | 0 | -425732160 | [7 empty] | NET TOTAL IMPORT (Energy export - Energy import) | [6 empty] | Active Energy ==> |  |  |  | #REF! | Reactive Energy ==> |  |  |  | 232459680 | #REF!
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 |  |  | 960000 | 18.041 | 18.041 | 0 | 0 |  |  |  | 14.511 | 14.511 | 0 | 0 | [53 empty] | Average Power Factor at 132 KV level | [16 empty] | #REF!
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[11 empty] | Total=> | 0 | 25658071.51 | 25658071.51 |  |  |  |  | 0 | 6716893 | 25658071.51 | 6716893 | 0.97 | [7 empty] | PDB 132 |  |  | 70628063.57 | [11 empty] | 2019622.176 | #REF!
[47 empty] | #REF! | #REF! | [9 empty] | 0 | 0 | 0 | 0 | 0 | 515260800 | 0 | -515260800 | [7 empty] | TOTAL Import | [6 empty] | Active Energy ==> |  |  | #VALUE! | #REF! | Reactive Energy ==> |  |  | 2880 | 258165600
TOTAL => | [11 empty] | 328320 | 912733111.51 | [5 empty] | 11226240 | 333413533 | [10 empty] | Unit | #REF! | #REF! | #REF! |  |  | 12570126 | 73887200.628 | #REF! | #REF! | #REF! |  |  |  | #REF! | [12 empty] | 0 | 0 |  | 912733111.51 |  | 515260800 | 0 | 397472311.51 | [7 empty] | NET TOTAL IMPORT (Energy export - Energy import) | [6 empty] | Active Energy ==> |  |  |  | #REF! | Reactive Energy ==> |  |  |  | 258162720 | #REF!
NET TOTAL IMPORT (Energy export - Energy import) => | [10 empty] | BPDB |  | 912404791.51 | 912404791.51 | 0 |  |  |  |  | 322187293 | 912404791.51 | 322187293 | 0.94 |  | 0 |  | 0.94294 | [45 empty] | Average Power Factor at 132 KV level | [16 empty] | #REF!
[12 empty] | 132 KV level | KWH | KVARH
[13 empty] | 912404791.51 | 322187293
[13 empty] | 650527200 | 211203360 | [16 empty] | Diff |  |  | #REF!
[8 empty] | 33 KV LEVEL |  |  |  | Month June-2023
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 33kV voltage levels |  | Remarks for KWH | KVAR CALCULATION | [5 empty] | PFC Calculation |  |  |  |  | Remarks for KVAR | Remarks for KVAR (Bus Loss)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Diff. | KVAR Import | KVAR Export | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 11 | 12 | 13 | 14 | 15 | 16 | 18 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 30 | 28
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | AMR-1 | Digital | 48000 | 11910.314 | 11910.314 | 0 |  | 0 |  |  | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | PF 0.90 Considered | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | AMR-2 | Digital | 48000 | 14467.636 | 14467.636 | 0 |  | 0 |  |  | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | AMR-3 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 |  |  | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [52 empty] | 33 KV LEVEL
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  | 5241 | 179431602 |  |  | Total=> |  | 0 | [6 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | DPDC |  |  |  | PDB |  |  |  | DPDC-PDB | [20 empty] | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 33kV voltage levels |  | KVAR CALCULATION |  |  | Reactive Energy Import / Export at 33 kV level |  | P.F | Remark
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 29344.892 | 29344.892 | 0 |  | 0 |  |  | 7711.314 | 7711.314 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | NAME OF THE CIRCUIT | PF | CF | Pfc unit | PFC Surcharge | PF | CF | Pfc unit | PFC Surcharge | Difference | [19 empty] | PDB | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff | [6 empty] | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
4 | Shah Cement |  | 33 | Export | 8993841 | AMR-4 | Digital | 36000 | 39195.806 | 39285.417 | 89.611 |  | 3225996 |  |  | 10339.1 | 10366.967 | 27.867 |  | 1003212 | 3225996 | 1003212 | 0.95489 | 0 | 0 |  | 733 |  |  | 2 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | [30 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
5 | Mandal para |  | 33 | Export | 8993842 | AMR-5 | Digital | 180000 | 2588.486 | 2588.486 | 0 |  | 0 |  |  | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [43 empty] | 1: Pagla Power Generation
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [10 empty] | Total=> |  | 3225996 | Missing Unit | [5 empty] | 1003212 | 3225996 | 1003212 |  |  | 0 |  | 733 |  |  | Shyampur 33//11kv S/S | [29 empty] | 0 | 3225996 | 0 | NO NEED | [7 empty] | 1 | Shyampur 33//11kv S/S | Pagla Rental | 33 | Export | 96833444 | - | Digital | 1000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | AMR-6 | Digital | 180000 | 1072.053 | 1072.053 | 0 |  | 0 | KWH | KVARH | 547.36 | 547.36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | Meter Replaced | [33 empty] | 180000 | 0 | 0 | NO NEED | [7 empty] | 5: Import; 8: Digital; 9: 1000; 10: 1072.053; 11: 1072.053; 12: 0; 13: 0; 15: 547.36; 16: 547.36; 17: 0; 18: 0; 20: 0
|  |  | 33 | Export | 38992490 (new) |  |  | 180000 | 1.103 | 1.16 | 0.057 |  | 10260 |  |  | 0.103 | 0.103 | 0 |  | 0 | 10260 | 0 | 0 | 0 | 0 | on 27/7/2022 |  |  |  | Shyampur 33//11kv S/S | [41 empty] | Shyampur 33//11kv S/S | Pagla Rental | 33 | Export | 216742477 | new |  | 82500 | 1.103 | 1.16 | 0.057 |  | 4705.5 | 0.103 | 0.103 | 0 |  | 0 | 0
7 | Shere Bangla |  | 33 | Export | 8993833 | AMR-7 | Digital | 180000 | 317.19 | 317.19 | 0 |  | 0 |  |  | 244.203 | 244.203 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [45 empty] | 5: Import; 9: 82500; 10: 317.19; 11: 317.19; 12: 0; 13: 0; 15: 244.203; 16: 244.203; 17: 0; 18: 0; 20: 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | AMR-8 | Digital | 180000 | 4175.969 | 4184.327 | 8.358 |  | 1504440 |  |  | 2253.803 | 2254.664 | 0.861 |  | 154980 | 1504440 | 154980 | 0.99474 | 0 | 0 | [45 empty] | 12: 0; 13: 0; 14: 4705.5
9 | Satmosjid -2 |  | 33 | Export | 8993669E | AMR-9 | Digital | 180000 | 5705.38 | 5753.894 | 48.514 |  | 8732520 |  | 16790 | 2607.416 | 2625.381 | 17.965 |  | 3233700 | 8732520 | 3233700 | 0.93777 | 0 | 0 | [45 empty] | 1: HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS); 7: Units without wheeling Charge=>; 12: 4705.5; 18: 0; 19: 0
10 | Kallayanpur T3 |  | 33 | Export | 8993831 |  |  | 180000 | 6458.759 | 6495.578 | 36.819 |  | 6627420 |  |  | 3161.659 | 3176.135 | 14.476 |  | 2605680 | 6627420 | 2605680 | 0.93065 | 0 | 0 |  |  |  |  | Postagola (IG GATE) | 0.93065 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [19 empty] | 0 | 6627420 | 0 | 0 | 0 | [6 empty] | 2 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | AMR-1 | Digital | 48000 | 6458.759 | 6495.578 | 36.819 |  | 1767312 | 3161.659 | 3176.135 | 14.476 |  | 694848 | 0.93065
11 | Kallayanpur T4 |  | 33 | Export | 8993839 |  |  | 180000 | 8574.056 | 8617.568 | 43.512 |  | 7832160 |  |  | 4003.47 | 4020.639 | 17.169 |  | 3090420 | 7832160 | 3090420 | 0.9302 | 0 | 0 |  |  |  |  | Lalbag-1 | 0.9302 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [18 empty] | 13363 | 0 | 7832160 | 0 | 2863680 | 0 | [6 empty] | 3 | Lalbag-1 |  | 33 | Export | 8993861E | AMR-2 | Digital | 48000 | 8574.056 | 8617.568 | 43.512 |  | 2088576 | 4003.47 | 4020.639 | 17.169 |  | 824112 | 0.9302
12 | Kallayanpur T5 |  | 33 | Export | 38992611 |  |  | 180000 | 65.069 | 86.616 | 21.547 |  | 3878460 |  | 57240 | 15.871 | 21.209 | 5.338 |  | 960840 | 3878460 | 960840 | 0.97066 | 0 | 0 |  |  |  |  | Lalbag-2 | 0.97066 | 0 | #REF! | #REF! |  |  |  |  | #REF! | [5 empty] | 0 | [13 empty] | 8899 | 0 | 3878460 | 0 | 129744 | 0 | [6 empty] | 4 | Lalbag-2 |  | 33 | Export | 8993820 | AMR-3 | Digital | 48000 | 65.069 | 86.616 | 21.547 |  | 1034256 | 15.871 | 21.209 | 5.338 |  | 256224 | 0.97066
| Export to Desco at 11 KV | [10 empty] | 7037675 | [6 empty] | 1276740 |  | -7037675 | -1276740 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | AMR-10 | 1 | 180000 | 5413.706 | 5450.602 | 36.896 |  | 6641280 |  |  | 2671.485 | 2685.406 | 13.921 |  | 2505780 | 6641280 | 2505780 | 0.93562 | 0 | 0
[11 empty] | Total=> | 7037675 | 35226540 | 28188865 |  |  |  |  | 1276740 | 12551400 | 28188865 | 11274660 |  |  |  |  | 0 |  |  | Aganagor-1 | [40 empty] | 1: 1; 2: Aganagor-1; 4: 33; 5: import; 6: 122218112; 7: REB; 8: 1.005; 9: 1000; 10: 0; 11: 0; 12: 0; 13: 0
SATMOSJID 132/33KV SS (
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E |  | 1 | 750000 | 3062.422 | 3099.791 | 37.369 |  | 28026750 |  |  | 1546.826 | 1562.816 | 15.99 |  | 11992500 | 28026750 | 11992500 | 0.91937 | 0 | 0 |  |  |  |  | Aganagor-2 | [40 empty] | 1: 2; 2: Aganagor-2; 4: 33; 5: import; 6: 12920031; 7: REB; 8: 1.005; 9: 5500; 10: 3062.422; 11: 3099.791; 12: 37.369; 13: 206557.1475
15 | Transformer-2 |  | 33 | Export | 50148569E |  | 1 | 750000 | 2701.161 | 2739.184 | 38.023 |  | 28517250 |  |  | 1342.604 | 1358.853 | 16.249 |  | 12186750 | 28517250 | 12186750 | 0.91955 | 0 | 0 |  |  |  |  | Aganagor-3 | [40 empty] | 1: 3; 2: Aganagor-3; 4: 33; 5: import; 6: 15716186; 7: REB; 8: 1.005; 9: 5500; 10: 2701.161; 11: 2739.184; 12: 38.023; 13: 210172.1325
AGARGAON 132/33KV SS | [5 empty] | CF | = | 1.001 |  |  | Total=> |  | 56544000 | [6 empty] | 24179250 | 56544000 | 24179250 |  | 0 | 0 | [45 empty] | 1: MADANGONJ 132/33 KV S/S (Tel: 01711-202009); 6: 33 KV Buss Loss; 8: 12922; 12: Total=>; 13: 416729.28; 14: 4890144; 19: 1775184; 20: 0
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 1.001 | 1 | 180000 | 1853.024 | 1885.528 | 32.504 |  | 5856575.5761 |  |  | 629.834 | 638.443 | 8.609 |  | 1551170.9062 | 5856575.5761 | 1551170.9062 | 0.96667 | 0 | 0 |  |  |  |  | 132 kv102 MW | [40 empty] | 1: PP; 2: 132 kv102 MW; 4: QRPP; 5: import; 6: 13176571; 9: 960000; 10: 1853.024; 11: 1885.528; 12: 32.504
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 1.001 | 1 | 180000 | 630.272 | 646.365 | 16.093 |  | 2899639.1443 |  |  | 43.198 | 44.81 | 1.612 |  | 290450.4008 | 2899639.1443 | 290450.4008 | 0.99502 | 0 | 0 | [45 empty] | 5: Export; 9: 960000; 10: 630.272; 11: 646.365; 12: 16.093
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 1.001 | 1 | 180000 | 106.915 | 106.915 | 0 |  | 0 |  |  | 4.16 | 4.16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 1.001 | 1 | 180000 | 990.553 | 1026.085 | 35.532 |  | 6402161.0685 |  |  | 422.754 | 435.896 | 13.142 |  | 2367927.5234 | 6402161.0685 | 2367927.5234 | 0.9379 | 0 | 0
20 | Monipuripara-2 |  |  |  |  | 1.001 | 1 | 180000 | 716.372 | 741.116 | 24.744 |  | 4458377.6168 |  |  | 268.299 | 275.308 | 7.009 |  | 1262882.6671 | 4458377.6168 | 1262882.6671 | 0.96215 | 0 | 0 | [45 empty] | 2: Units without wheeling Charge( UNITS FROM QRPP)=>
| Maniknagar 230/132 kv |  |  |  |  | CF | = | 1.025 |  |  |  |  | 19616753.4056 | [6 empty] | 5472431.4976 | 19616753.4056 | 5472431.4976 |  |  | 0 |  |  |  |  | Shah Cement | 0 | 0 | #REF! | [26 empty] | 0 | 19616753.4056 | 0 | 5352552 | 0 | [6 empty] | 5 | Shah Cement | Madangonj Grid | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 1.025 |  | 1 | 391339 | 397817.5 | 6478.5 |  | 6640.4625 |  |  | 250703.8 | 254717.8 | 4014 |  | 4114.35 | 6640.4625 | 4114.35 | 0.85006 | 0.04 | 0 |  |  |  |  | Shah Cement | 0.85006 | 0.04 | #REF! | [26 empty] | 0 | 6640.4625 | 0 | 5352552 | 0 | [6 empty] | 5 | Shah Cement |  | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 391339 | 397817.5 | 6478.5 |  | 116613000 | 250703.8 | 254717.8 | 4014 |  | 72252000 | 0.85006
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 1.025 |  | 1 | 364399.6 | 369244.1 | 4844.5 |  | 4965.6125 |  |  | 126702.6 | 129044.5 | 2341.9 |  | 2400.4475 | 4965.6125 | 2400.4475 | 0.90032 | 0 | 0 |  |  |  |  | Mandal para | 0.90032 | 0 | #REF! | [26 empty] | 0 | 4965.6125 | 0 | 4402000 | 0 | [6 empty] | 6 | Mandal para |  | 33 | Export | 8993842 | AMR-5 | Digital | 180000 | 364399.6 | 369244.1 | 4844.5 |  | 872010000 | 126702.6 | 129044.5 | 2341.9 |  | 421542000 | 0.90032
Shyampur 230/132 kv | [5 empty] | CF | = | 1.025 |  |  |  |  | 11606.075 | [6 empty] | 6514.7975 | 11606.075 | 6514.7975 |  |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 1.025 | 1 | 2400 | 337.075 | 341.169 | 4.094 |  | 10071.24 |  |  | 213.274 | 216.631 | 3.357 |  | 8258.22 | 10071.24 | 8258.22 | [7 empty] | Aux T1 | [29 empty] | 0 | 10071.24 | 0 | 0 | 0 | [6 empty] | 7 | Aux T1 |  | 0.4 | Export | 9187973 | G.E.C | Analog | 10 | 337.075 | 341.169 | 4.094 |  | 0 | 213.274 | 216.631 | 3.357 |  | 33.57 | 0.77328
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 1.025 |  | 2400 | 82.99 | 87.479 | 4.489 |  | 11042.94 |  |  | 46.059 | 48.561 | 2.502 |  | 6154.92 | 11042.94 | 6154.92 | [7 empty] | Aux T2 | [29 empty] | 0 | 11042.94 | 0 | 15440 | 0 | [6 empty] | 8 | Aux T2 |  | 0.4 | Export | 9187972 | G.E.C | Analog | 10 | 82.99 | 87.479 | 4.489 | 1.025 | 46.0123 | 46.059 | 48.561 | 2.502 |  | 25.02 | 0.87349
[13 empty] | 21114.18 | [6 empty] | 14413.14 | 21114.18 | 14413.14 | [48 empty] | 1: HARIPUR 130/132 KV S/S (Tel: 01730-335255); 14: 988623046.0122
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  |  | PGCB | #REF! |  |  |  | 7037675 | 114646009.6606 |  | Total KVAR/P.F.C UNIT => |  |  |  | 1276740 | 43227221.4351 |  |  |  |  | 0 | Bus Loss Unit | 733 | [43 empty] | 1: KALLYANPUR 132/33 KV S/S (Tel: 9007406); 12: Total=>; 19: 493794058.59
NET TOTAL IMPORT 33 KV (Energy export - Energy import) => | [6 empty] | PGCB | #REF! |  |  | BPDB |  | 107608334.6606 | NET KVAR/ PFC UNIT AT 33 KV LEVEL => | [5 empty] | 41950481.4351 | 107608334.6606 | 41950481.4351 | 0.9317 |  |  |  | 0.9317 |  |  | Jigatala (JP garden) | [29 empty] | 0 | #REF! | 0 | 0 | 0 | [6 empty] | 9 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 | AMR-6 | Digital | 180000 | 1071.741 | 0 | -1071.741 |  | -192913380 | 0 | 0 | 0 |  | 0 | 0
NET TOTAL IMPORT 11 KV (Energy export - Energy import) => | [6 empty] | PGCB | [5 empty] | 728262.5 | Tariff point Total ( 33 KV and 11 Kv )=> |  |  |  | 108336597.1606
[30 empty] | Shere Bangla | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [19 empty] | 0 | 0 | 0 | 640000 | 0 | [6 empty] | 10 | Shere Bangla |  | 33 | Export | 8993833 | AMR-7 | Digital | 180000 | 298.605 | 0 | -298.605 |  | -53748900 | 0 | 0 | 0 |  | 0 | 0
[12 empty] | 33 KV level | KWH | KVARH | [15 empty] | Satmosjid-1 | [27 empty] | PDB Wrong | 114789 | 33 KV level | KWH | 0 | 12255000 | #VALUE! | [6 empty] | 11 | Satmosjid-1 |  | 33 | Export | 8993638E | AMR-8 | Digital | 180000 | 3925.828 | 0 | -3925.828 |  | -706649040 | 0 | 0 | 0 |  | 0 | 0
[13 empty] | 107608334.6606 | 41950481.4351 | [15 empty] | Satmosjid -2 | 0 | 0 | #REF! | [26 empty] | 0 | 107608334.6606 | 0 | 1370000 | 0 | [6 empty] | 12 | Satmosjid -2 |  | 33 | Export | 8993669E | AMR-9 | Digital | 180000 | 3400.926 | 0 | -3400.926 |  | -612166680 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Lalmatia | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [18 empty] | 137051 | 0 | 0 | 0 | 10341000 | 0 | [6 empty] | 13 | Lalmatia |  | 33 | Export | 8993836E | AMR-10 | 1 | 180000 | 4091.905 | 0 | -4091.905 |  | -736542900 | 0 | 0 | 0 |  | 0 | 0
[60 empty] | 180000 | #REF! | 0 | 42721968 | [7 empty] | 1: SATMOSJID 132/33KV SS (; 12: Total=>; 14: -2302020900; 19: 0
| 11&0.4 KV LEVEL | [11 empty] | 0 | [16 empty] | Transformer-1 | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E |  | 1 | 750000 | 872.986 | 0 | -872.986 | 0 | -654739500 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Transformer-2 | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 15 | Transformer-2 |  | 33 | Export | 50148569E |  | 1 | 750000 | 467.14 | 0 | -467.14 |  | -350355000 | 0 | 0 | 0 |  | 0 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 11 kV voltage levels |  | Remarks for KWH | KVAR CALCULATION | [11 empty] | Remarks for KVAR | [5 empty] | #REF! | [37 empty] | 12: Total=>; 14: -1005094500; 19: 0; 20: 0
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | CF | OMF | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | Diff. | KVAR Import | KVAR Export |  |  | P.F | P.F.C Corr. Factor | [5 empty] | DPDC-CKT-1 | [40 empty] | 16 | DPDC-CKT-1 | Sher-e Bangla S/S | 33 | Export |  | 1.0016 |  | 180000 | 579.468 | Reading at 00.00hr 01.07.2023 | #VALUE! |  | #VALUE! | Reading at 00.00hr 01.06.2023 | Reading at 00.00hr 01.07.2023 | #VALUE! |  | #VALUE! | #VALUE!
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 11 | 12 | 13 | 14 | 15 | 16 | 18 | 18 | 19 | 20 | 21 |  |  | 22 | 23 |  |  | 26 |  |  | DPDC-CKT-2 | [40 empty] | 17 | DPDC-CKT-2 |  | 33 | Export |  | 1.0016 |  | 180000 | 110.481 | 11 | -99.481 |  | -17934396.0456 | 18 | 18 | 0 |  | 0 | 0
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [29 empty] | DPDC-CKT-2 | [40 empty] | 17 | DPDC-CKT-2 |  | 33 | Export |  | 1.0016 |  | 180000 | 110.481 | 0 | -110.481 |  | -19917471.7736 | 0 | #REF! | #REF! |  | #REF! | #REF!
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | Secure | Digital | 40000 | 1915.47 | 1915.47 | 0 |  | 0 |  | Same Meter | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | L & G | Digital | 8000 | 40126.43 | 40126.43 | 0 |  | 0 |  |  | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | Secure | Digital | 40000 | 9317.28 | 9317.28 | 0 |  | 0 |  |  | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1 | [46 empty] | 2: Maniknagar 230/132 kv; 14: #VALUE!
| Swerage 11KV O/H |  | 11 | Export | 14959 | Secure | Digital | 40000 | 782.24 | 782.24 | 0 |  | 0 |  |  | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1 | [5 empty] | Axuxilary -1 | [40 empty] | 18 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 1 |  | 1 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | L & G | Digital | 8000 | 34050.59 | 34050.59 | 0 |  | 0 |  |  | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1 | [5 empty] | Axuxilary -2 | [40 empty] | 19 | Axuxilary -2 |  | 33 | Export | AH14044072 | 1 |  | 1 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | Secure | Digital | 40000 | 994.03 | 994.03 | 0 |  | 0 |  |  | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1 | [6 empty] | Unit | #REF! | [38 empty] | 14: 0; 19: 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | Secure | Digital | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 |  |  | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [10 empty] | Total=> |  | 0 | 0 | [5 empty] | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | Secure | Digital | 40000 | 9151.97 | 9164.92 | 12.95 |  | 518000 | 530950 | Same Meter | 3452.81 | 3457.08 | 4.27 |  | 170800 | 175070 |  | 0.94971 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | Secure | Digital | 40000 | 3855.49 | 3859.52 | 4.03 |  | 161200 | 165230 |  | 1262.76 | 1262.98 | 0.22 |  | 8800 | 9020 |  | 0.99851 | 1 |  | 8063.0273 | RMU Feeder KVARH Back Calculation as per KWH Percentage |  |  |  |  | 5.928 | [26 empty] | SHYAMPUR 33KV | NET=> | #REF! | NET=> | 42721968 | [7 empty] | 3: TOTAL Import; 10: Active Energy ==>; 13: 416729.28; 14: #VALUE!; 15: Reactive Energy ==>; 18: 0; 19: 495569242.59 | Bus Loss Unit
3a | PD Betar |  | 11 | Import | 2612100427 |  | Digital | 600 | 8820 | 8834 | 14 | 8400 |  | 8610 |  | 2870 | 2874 | 4 | 2400 |  | 2460 |  | 0.96152 | 1 | [6 empty] | 0 | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 3: NET TOTAL IMPORT (Energy export - Energy import); 10: Active Energy ==>; 14: #VALUE!; 15: Reactive Energy ==>; 19: 495569242.59; 20: #VALUE!
3b | SE,NB,Betar |  | 11 | Import | 2612100517 |  | Digital | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 0 |  | 572 | 572 | 0 | 0 |  | 0 |  | 0 | 1 | [46 empty] | 3: Average Power Factor at 33 KV level; 20: #VALUE!
3b | SE,NB,Betar |  | 11 | Import | 645015020085 |  | Digital | 300 | 1398 | 1398 | 0 | 0 |  | 0 |  | 494 | 494 | 0 | 0 |  | 0 |  | 0 | 1 | [6 empty] | PDB 33 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 |  |  | 300 | 739 | 756 | 17 | 5100 |  | 5227.5 |  | 236 | 243 | 7 | 2100 |  | 2152.5 |  | 0.92468 | 1 |  | Estimated |  |  |  |  | Diff | #REF!
3c | NINS & H |  | 11 | Import | Dhk-59122 |  | Digital | 1000 | 26885 | 26885 | 0 | 0 |  | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 |  | 0 | 1 | [5 empty] | 11 kv
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | Secure | Digital | 40000 | 3975.03 | 3976.15 | 1.12 |  | 44800 | 45920 |  | 1886.11 | 1886.88 | 0.77 |  | 30800 | 31570 |  | 0.82404 | 1.0922
5 | BICC - U/G |  | 11 | Export | 15024 | Secure | Digital | 40000 | 1038.1 | 1038.1 | 0 |  | 0 | 0 |  | 297.32 | 297.32 | 0 |  | 0 | 0 |  | 0 | 1
6 | NEC |  | 11 | Export | 15023 | Secure | Digital | 40000 | 431.56 | 431.56 | 0 |  | 0 | 0 |  | 56.29 | 56.29 | 0 |  | 0 | 0 |  | 0 | 1
7 | Manikmia Avenue |  | 11 | Export | 76026327 | L & G | Digital | 40000 | 3357 | 3357 | 0 |  | 0 | 0 |  | 1465 | 1465 | 0 |  | 0 | 0 |  | 0 | 1
| Manikmia Avenue | new | 11 | Export | DHK27341 |  | Digital | 40000 | 175.92 | 175.92 | 0 |  | 0 | 0 |  | 57.975 | 57.975 | 0 |  | 0 | 0
[11 empty] | Total=> |  | 724000 | 742100 |  |  |  |  | 4500 | 210400
TOTAL => | [11 empty] | 13500 | 724000 | [5 empty] | 4500 | 210400
NET TOTAL IMPORT (Energy export - Energy import) => | [12 empty] | 710500 | [6 empty] | 205900 | [6 empty] | 0.96048
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB) | [12 empty] | 728262.5 | [6 empty] | 211047.5 |  |  | 0.96048 |  |  |  | 0.96048 | [22 empty] | Accoding to PDB | [20 empty] | 6: 11&0.4 KV LEVEL
| 11 KV P.C Culture Housing | [11 empty] | 33 KV level | KWH | KVARH | [34 empty] | Input | KWH | KVAR | [7 empty] | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | 1: SUBSTATION-FEEDER-METERS INFORMATION; 9: KWH CALCULATION; 13: Energy Import/Export at 11 kV voltage levels; 15: KVAR CALCULATION; 18: Reactive Energy Import / Export at 11 kV level; 20: P.F; 21: Remark
| 11 KV Nearest RMU | [12 empty] | 728262.5 | 211047.5 | [14 empty] | NAME OF THE CIRCUIT | [18 empty] | BICC |  | 962.34 | 265.23 | [7 empty] | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff |  | 11 KV and .4 KV import converted into 132 KV for maching the calculation with PDB |  |  |  | Energy Import/Export at 132 kV voltage levels |  | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
| 11 KV NEC Feeder. | [28 empty] | 2 | [18 empty] | NEC |  | 431.17 | 56.22 | [7 empty] | 0 | 0 |  |  |  |  | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Energy Import (KWh) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| 11 KV Shyamoli O/H | [47 empty] | Shamoly 11KV O/H |  | 8700.85 | 3294.12 | [7 empty] | 0 | 0 | 0 | 0 |  |  | 1 | 2 | 3 | 4 | 14 | 1: KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| 11 KV BCFCC Feeder. | [28 empty] | Adabor 11KV O/H | [18 empty] | Sher-E-Bangla Nagar |  | 3602.65 | 1739.62 | [6 empty] | #REF! | 0 | 0 | 0 | 1770400 | 0 |  | KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) |  |  |  |  | 1 | Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
| 11 KV Sher-e-bangla Nagar | [28 empty] | Monsurabab 11KV O/H | [18 empty] | Manik Mia 11KV O/H |  | 2963 | 1326 | [7 empty] | 0 | 0 | 0 | 2723600 | 0 |  | 1 | Adabor 11KV O/H | Kallyanpur 33/11KV | 11 |  | 2 | Monsurabab 11KV O/H |  | 11 | Export | 77816681 | L & G | Digital | 8000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
| 11 KV Manik Mia Feeder. | [28 empty] | Beri Bandh 11KV O/H | [29 empty] | 0 | 0 | 0 | 2425600 | 0 |  | 2 | Monsurabab 11KV O/H |  | 11 |  | 3 | Beri Bandh 11KV O/H |  | 11 | Export | 14960 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Swerage 11KV O/H | [18 empty] | 11KV RMU U/G |  | 3335.92 | 1118.77 | [7 empty] | 0 | 0 | 0 | 2718800 | 0 |  | 3 | Beri Bandh 11KV O/H |  | 11 |  | 4 | Swerage 11KV O/H |  | 11 | Export | 14959 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Ring Road 11KV O/H | [28 empty] | #REF! | 0 | 0 | 0 | 2162240 | 0 |  | 4 | Swerage 11KV O/H |  | 11 |  | 5 | Ring Road 11KV O/H |  | 11 | Export | 77816675 | L & G | Digital | 8000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | RMU Feeder | [18 empty] | PD Betar |  | 2961 | 799 | [7 empty] | 0 | 0 | 0 | 203200 | 0 |  | 5 | Ring Road 11KV O/H |  | 11 |  | 6 | RMU Feeder |  | 11 | Export | 14997 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | P.C Culture Housing 11 KV | [18 empty] | SE, NB, Betar |  | 2075 | 509 | [6 empty] | #REF! | 0 | 0 | 0 | 1652000 | 0 |  | 6 | RMU Feeder |  | 11 |  |  | P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[49 empty] | NINS&H |  | 13570 | 6541 | [6 empty] | #REF! |  | 0 |  | 13655840 |  |  | 7 | P.C Culture Housing 11 KV |  | 11 |  | 1: AGARGAON 33/11 KV S/S (Tel: 8122865); 12: Total=>; 14: 0; 16: 0; 19: 0
[30 empty] | Shyamoli 11KV O/H | [28 empty] | #REF! | 0 | 0 | 0 | 2340400 | 0 |  | AGARGAON 33/11 KV S/S (Tel: 8122865) |  |  |  |  | 7 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | 11 KV R.M.U Feeder | [18 empty] | Adabor 11KV O/H |  | 1568.4 | 6107.4 | [6 empty] | #REF! | 0 | 0 | 0 | 906000 | 0 |  | 7 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 |  | 8 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[49 empty] | (Beri Bandh) 11KV O/H |  | 9192.76 | 3796.33 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[49 empty] | Ring Road 11 KV O/H |  | 32749.69 | 16758.17 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[80 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0
[80 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0
[49 empty] | Swerage 11KV O/H |  | 480.82 | 4422.64 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[30 empty] | 11 KV Sher-e-banglanagar | [18 empty] | RMU 11 KV |  | 993.85 | 211.73 | [6 empty] | #REF! | 0 | 0 | 0 | 443600 | 0 |  | 8 | 11 KV R.M.U Feeder |  | 11 |  | 9 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | BICC - U/G | [18 empty] | Monsurabad |  | 38635.52 | 19957.6 | [6 empty] | #REF! | 0 | 0 | 0 | 322800 | 0 |  | 9 | Sher-e-banglanagar |  | 11 |  | 10 | BICC - U/G |  | 11 | Export | 15024 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | NEC | [29 empty] | 0 | 0 | 0 | 115200 | 0 |  | 10 | BCFCC - U/G |  | 11 |  | 11 | NEC |  | 11 | Export | 15023 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Manikmia Avenue | [29 empty] | 0 | 0 | 0 | 900000 | 0 |  | 11 | NEC |  | 11 |  | 12 | Manikmia Avenue |  | 11 | Export | 76026327 | L & G | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[66 empty] | 12 | Manikmia Avenue |  | 11 |  | 1: Import from Baridhara 33/11 KV S/S (Tel: 02-9888965, Mob: 01730-335248); 12: Total==>; 14: 0; 19: 0
[59 empty] | SHYAMPUR 11KV | #REF! | 0 | 118200 | 18683840 |  |  | 4 | Nanruti S/S (Yousuf-01818284943) | Tejgaon | 0.4 | #REF! | 3: TOTAL ==>; 14: 0; 19: 0
[66 empty] | Sum > |  |  |  | #REF! | 3: NET TOTAL IMPORT (Energy export - Energy import) ==>; 14: 0; 19: 0
[66 empty] | Net 132KV Import > |  |  |  |  | 3: 11 kV import converted into 33 kV import (Adding 2.5%) ==>; 14: 0; 19: 0
[73 empty] | Average Power Factor at 33 KV level==> | [16 empty] | 0

## PDB SUM AMR (hidden)
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month June-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 912404791.51 | 8.1335 | 7421044372 |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 912404791.51 | 912404791.51 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 7421044372 | 7421044372 | 0
2a | 33kv | 107608334.6606 | 8.22 | 884540511 |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 107608334.6606 | 107608334.6606 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 884540511 | 884540511 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 728262.5 | 8.22 | 5986318 |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 728262.5 | 728262.5 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 5986318 | 5986318 | 0
2c | Bus Loss Units (33kv) | 733 | 8.22 | 6024 |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 733 | 733 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 6024 | 6024 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 108337330.1606 |  | 890532853 |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 108337330.1606 | 108337330.1606 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 890532853 | 890532853 | 0
4 | TOTAL 132kv & 33kv (1+3) | 1020742121.6706 |  | 8311577225 |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 1020742121.6706 | 1020742121.6706 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 8311577225 | 8311577225 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 0 | 8.22 | 0 |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 0 |  | 0 |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 0 | 0 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 0 | 0 | 0
8 | TOTAL Billed Amount => (4+7) | 1020742121.6706 |  | 8311577225 |  | 8449333177.94 | 10 | সর্বমোট (৬+৯) | 1020742121.6706 | 1020742121.6706 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 8311577225 | 8311577225 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 498694634 | Source Tax
10 | NET BILL TOTAL => (8-9) |  |  | 7812882591
11*** | 21th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  | 137755952.94 | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 7950638543.94
"In word: Taka Seven Hundred Eighty Three Crore Eighty Seven Lac Thirty Six Thousand Eight Hundred Sixty Three and Poisa Ninety Four"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | #VALUE!
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Certified For Payment
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0
| Total | 3306142870.56
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month June-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [8 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[11 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month June-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 912404791.51 | 0.2886 | 263320022.8298 |  |  | 1 | 132 †Kwf (GbvwR©) | 912404791.51 | 912404791.51 | 912404791.51 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 7421044372 | 263320022.8298 | 263320022.8298 | 0
2a | 33kv Level | 107608334.6606 | 0.2944 | 31679893.7241 |  |  | 2 | 33 †Kwf (GbvwR©) | 107608334.6606 | 107608334.6606 | 107608334.6606 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 884540511 | 31679893.7241 | 31679893.7241 | 0 |  | 33KV Amount (2+3+4) => | 31894509.9993
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 728262.5 | 0.2944 | 214400.48 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 728262.5 | 728262.5 | 728262.5 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 5986318 | 214400.48 | 214400.48 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 733 | 0.2944 | 216.1952 |  |  | 4 | 33 ‡Kwf evm jm | 733 | 733 | 733 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 6024 | 215.7952 | 216.1952 | -0.4 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 108337330.1606 | 0.2944 | 31894510.3993 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 108337330.1606 | 108337330.1606 | 108337330.1606 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 890532853 | 31894509.9993 | 31894510.3993 | -0.4
4 | TOTAL=> (1+3) | 1020742121.6706 |  | 295214533.2291 |  |  | 6 | me©‡gvU (1+5) | 1020742121.6706 | 1020742121.6706 | 1020742121.6706 | 0 |  |  | 6 | me©‡gvU (1+5) | 8311577225 | 295214532.8291 | 295214533.2291 | -0.4
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000
6*** | Add: Ref. No. 27.87.0000.517.31.031.20.43; Date:09/11/2022 (8th Installment) |  |  | 25993419.79 |  |  | ‡gvU (GbvwR©) |  | 1020741388.6706 | 1020741388.6706 | 1020741388.6706 | 0 |  |  | ‡gvU (GbvwR©) |  | 8311571201 | 295214317.0339 | 31894510.3993 | 263319806.6346
7 | Grand TOTAL=> (4-5+6) |  |  | 319707953.0191
| CERTIFED UNITS |  |  | 1020742121.6706
| CERTIFED TAKA |  |  | 295214533.2291
| CERTIFED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 8th Installment of Wheeling Charge Due) |  |  | 319707953.0191
evsjv
In word: Taka Thirty One Crore Fifty Four Lac Eighty Two Thousand One Hundred and Seventy Seven
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Certified For Payment
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
| CERTIFED UNITS | 0
| CERTIFED TAKA | 0
In word:Nine Core Ninety Lac Seventy Six Thousand Eight Hundred Eighty Three Taka only.
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check
[6 empty] | Month June-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import / Export at 132 kV level | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 14 | 15
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 125898234.18 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 125594352 | Fatullah Grid | 36921600 | 303882.18 | 0.2414%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 1267200 |  |  |  | Shyampur Grid | 88672752
|  |  | 132 | Import |  | 328320 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 28181760 | 36126720 | Postogola 132/33 KV Grid | 36043200 | Postogola Grid | 36043200 | 83520 | 0.2312%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 7944960
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 328320 | 37393920
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 24024000 | 105487200 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 104160960 | Ullon Grid | 23916960 | 1326240 | 1.257%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 67312800
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 24024000 |  |  |  | DU Grid | 12931200
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 18789120 | 141011520 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 138622400 | Lalbagh Grid | 51932000 | 2389120 | 1.694%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 35851200
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 18988800 |  |  |  | Jigatola Grid | 50839200
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 37777920
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 19868640 | 57376320 | Sitalakhya 132/33 KV Grid | 57361055 | Sitalakhya Grid | 57361055 | 15265 | 0.02661%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 18705120
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 18802560
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 9239520 | 9239520 | Sitalakhya NOCS | 9239520 | Sitalakhya NOCS | 9239520 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 66615840
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 35743680 | 71346240 | Siddirganj 132/33 KV Grid | 71561760 | Siddirganj Grid | 71561760 | -215520 | -0.3021%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 35602560
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 35457120 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 39100320 | 39100320 | Matuail 132/33 KV Grid | 39106681 | Matuail Grid | 39106681 | -6361 | -0.01627%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 145903680
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | Month June-2023 | 0
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 40355520 | 71513280 | Moghbazar 132/33 KV Grid | 71275200 | Moghbazar Gird | 71275200 | 238080 | 0.3329%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 31157760
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 12288000 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 11610240
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 26601600 | 53036160 | Madartek 132/33 KV Grid | 53036160 | Madartek Grid | 53036160 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 26434560
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 11003520 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 11104320
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 170555520
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 88465920 | 176632320 | Maniknagar 132/33 KV Grid | 175981472 | Kazla Grid | 55224000 | 650848 | 0.3685%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 88166400 |  |  |  | Motijheel Grid | 24379200
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 176632320 |  |  |  | Narinda Grid | 40233600
[11 empty] | Bangabhaban Grid | 6132000
[11 empty] | Maniknagar Grid | 50012672
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 62636160 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 62302080
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 124938240
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 51120000 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 52113600
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 103233600
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 11746560 | 25286400 | Charsyedpur 132/33 KV Grid | 25596000 | Charsyedpur Grid | 25596000 | -309600 | -1.224%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 13539840
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 0 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 0 | 25658071.51 | 912054234.18 |  | 907578760 |  | 907578760 | 4475474.18 | 0.4907%
[9 empty] | 33 KV Transmission Loss |  | 107587220.4806 | 107566755.3528 | 20465.1278 | 0.01902%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 728262.5 | 729492.5 | -1230 | -0.1689%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 1020369717.1606 | 1015875007.8528 | 4494709.3078 | 0.4405%
[9 empty] | From Summary Sheet |  |  |  | 4789065.5973 | 0.4692%
[9 empty] | Mismatch in KWH |  |  |  | -294356.2895
| 33 KV LEVEL |  |  |  |  | Month June-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import/Export at 33kV voltage levels | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 13 | 14
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 3225996 | 3225996 | Sitalakhya NOCS | 3226729 | Sitalakhya NOCS | 3226729 | -733 | -0.02272%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 3225996
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 10260 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 10260 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 10260
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 1504440 | 73422240 | Shatmasjid 132/33 KV Grid | 73167750 | Asadgate SS | 16775910 | 254490 | 0.3466%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 8732520 |  |  |  | Lalmatia SS | 15393240
[11 empty] | Japan Garden SS | 17395200
[11 empty] | Jigatola Old SS | 2164800
[11 empty] | Shatmasjid SS | 19938600
[11 empty] | BGB SS | 1500000
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 6627420 | 11300365 | Adabor NOCS | 11544206 | Adabor NOCS | 11544206 | -243841 | -2.158%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 7832160
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 3878460
| Export to Desco at 11 KV |  |  |  |  | 7037675 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 6641280 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 7037675 | 35226540
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 28026750 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 28517250
AGARGAON 132/33KV SS | [5 empty] | 0 | 56544000
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 5856575.5761 | 8756214.7204 | Sherebanglanagar 33/11 KV SS | 8756214.7204 | Sherebanglanagar SS | 8756214.7204 | 0 | 0%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 2899639.1443
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 0 | 6402161.0685 | 10860538.6852 | Monipuripara 33/11 KV SS | 10860538.6852 | Monipuripara SS | 10860538.6852 | 0 | 0%
20 | Monipuripara-2 |  |  |  |  | 0 | 4458377.6168
| Maniknagar 230/132 kv |  |  |  |  | 0 | 19616753.4056
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 6640.4625 | 11606.075 | Maniknagar 33/11 KV SS | 11316.9472 | Maniknagar 33/11 KV SS | 11316.9472 | 289.1278 | 2.491%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 4965.6125
Shyampur 230/132 kv | [5 empty] | 0 | 11606.075
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 10071.24 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 11042.94
[6 empty] | 0 | 21114.18
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 7037675 | 114646009.6606 | 107587220.4806 |  | 107566755.3528 |  | 107566755.3528 | 20465.1278 | 0.01902%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import/Export at 11 kV voltage levels | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 13 | 14
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 518000 | 728262.5 | Sherebanglanagar NOCS | 729492.5 | Sherebanglanagar NOCS | 729492.5 | -1230 | -0.1689%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 161200
3a | PD Betar |  | 11 | Import | 2612100427 | 8400 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 5100 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 44800
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 0
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 724000
TOTAL => | [5 empty] | 13500 | 724000 | 728262.5 |  | 729492.5 |  | 729492.5 | -1230 | -0.1689%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 86.616 | 65.069 |  | 21.547 | 180000 | 3878460 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Previous | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8617.568 | 8574.056 |  | 43.512 | 180000 | 7832160 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.68 | 995.71 | 0.03
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6495.578 | 6458.759 |  | 36.819 | 180000 | 6627420 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9633.08 | 9640.43 | 7.35
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4319.26 | 4371.7 | 52.44
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 3408.3 | 3311 |  | 99.7325 | 8000 | 797860 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 51326.05 | 51616.27 | 290.22
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 41632.55 | 41775.56 | 143.01
03 |  | 11 KV Bashir Uddin |  | 74819925 | 394.664 | 207.725 |  | 191.6125 | 16000 | 3065799.6 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 1991.3 | 2054.75 | 63.45
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8076.21 | 8133.47 | 57.26
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1125.19 | 1111.6 |  | 13.9298 | 40000 | 557190 | 0 | 1 |  | #DIV/0! | 0 |  | 0 |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9341.2 | 9355.62 | 14.42
05 |  | 11 KV Lalkuthy |  | DHK15018 | 995.15 | 995.15 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9510.27 | 9446.45 |  | 65.4155 | 40000 | 2616620 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [6 empty] | 0
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 51616.27 | 51326.05 |  | 297.4755 | 8000 | 2379804 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  |  | 0
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8133.47 | 8076.21 |  | 58.6915 | 40000 | 2347660 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  |  | 0
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2054.75 | 1991.3 |  | 65.0363 | 40000 | 2601450 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  |  | 0
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  |  | 0
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.696 | 3273.691 |  | 0.005125 | 40000 | 205 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  |  | 0
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9640.43 | 9633.08 |  | 7.5338 | 40000 | 301350 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  |  | 0
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9355.62 | 9341.2 |  | 14.7805 | 40000 | 591220 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  |  | 0
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4371.7 | 4319.26 |  | 53.751 | 40000 | 2150040 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  |  | 0
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.71 | 995.68 |  | 0.03075 | 40000 | 1230 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 41775.56 | 41632.55 |  | 146.5852 | 8000 | 1172682 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 7037674.6 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 11300365.4 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## Forwarding (hidden)
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 33009538.7975 | 32859668.0006 | 149870.7969 | 0.45609
Kakrail | 26094458.147 | 27021147.7998 | -926689.6528 | -3.4295 | DPH-1 Fdr Add To Kakrail NOCS
Moghbazar | 19191663.6958 | 20914248.216 | -1722584.5202 | -8.2364 | Ullon 132/33 Kv 33 kv Fdr Adjustment and Loss Fix
Khilgaon | 15814616.5953 | 16885238.3373 | -1070621.742 | -6.3406
Satmosjid | 21874027.2652 | 23263785.2371 | -1389757.9719 | -5.9739
Sherebanglanagar | 23841857.0802 | 25253205.2481 | -1411348.1679 | -5.5888
Dhanmondi | 23157735.0016 | 24559325.7701 | -1401590.7685 | -5.707
Jhigatala | 27497787.9591 | 28755390.4901 | -1257602.531 | -4.3734
Azimpur | 19273690.4419 | 19894403.1357 | -620712.6939 | -3.12
Paribagh | 33925839.4802 | 36106922.2961 | -2181082.8159 | -6.0406
Shyamoli | 18283221.4148 | 18566131.7394 | -282910.3246 | -1.5238
Adabor | 31334492.2359 | 33991693.0318 | -2657200.7959 | -7.8172
Lalbagh | 36512406.1293 | 35248383.1173 | 1264023.012 | 3.586
Kamrangirchar | 41297895.4236 | 40914828.615 | 383066.8086 | 0.93625
Ramna | 27950585.9269 | 28263881.9666 | -313296.0397 | -1.1085
Rajarbagh | 18065624.986 | 19358621.1692 | -1292996.1832 | -6.6792
Bashabo | 14134545.9205 | 14863749.6586 | -729203.7381 | -4.9059
Bonoseeri | 23898161.7109 | 26204619.7329 | -2306458.022 | -8.8017 | Bonosree 33/11 Loss Fix Reading Adjusted
Motijheel | 22370326.0361 | 22841984.5538 | -471658.5177 | -2.0649
Mughdapara | 18048010.2028 | 19312756.5241 | -1264746.3213 | -6.5488 | Madartek 33/11 Loss Fix and Green Model Town Reading Change
Banglabazar | 16832238.2088 | 17151582.8188 | -319344.61 | -1.8619
Bongshal | 19304876.681 | 20320381.2069 | -1015504.5258 | -4.9975
Narinda | 14569881.1136 | 15337870.9921 | -767989.8785 | -5.0071
Swamibagh | 14638867.6103 | 15002409.2817 | -363541.6714 | -2.4232
Kazla | 41076724.8443 | 37908086.6755 | 3168638.1688 | 8.3587
Maniknagar | 20369532.5037 | 20947278.5152 | -577746.0115 | -2.7581
Shyampur | 71611732.1812 | 70064491.3479 | 1547240.8333 | 2.2083
Matuail | 23414723.2501 | 24090523.3179 | -675800.0678 | -2.8053
Postogola | 15678261.2905 | 16221258.1373 | -542996.8468 | -3.3474
Jurain | 29540384.3679 | 29718071.1615 | -177686.7936 | -0.59791
Narayangonj-West | 31820650.1222 | 30810293.9579 | 1010356.1643 | 3.2793
Narayangonj-East | 32234510.966 | 31744596.4334 | 489914.5326 | 1.5433
Damra | 23689068.4661 | 24103097.7168 | -414029.2508 | -1.7177
Siddhirgonj | 49889071.0956 | 51252886.2733 | -1363815.1777 | -2.661
Fatulla | 33687593.9843 | 33019604.8442 | 667989.1401 | 2.023
Shitalakha | 66193265.9901 | 63180638.7532 | 3012627.2369 | 4.7683
TOTAL=> | 1000127867.1263 | 1015953056.0733 | -15825188.947 | -1.5577

## %Loss
Source 132 kv Tariff Point
Source 33 kv Tariff Point
Source 132 kv NON Tariff Point
Source 33 kv NON Tariff Point
[136 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
IMPORT
|  | NORTH | [172 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[135 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
| 1 | Moghbazar 132/33/11KV S/S | 1 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
| 2 | Moghbazar 33/11KV S/S | 2 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
| 3 | Green Road 33/11KV S/S | 3 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
| 4 | Lalmatia 33/11KV S/S | 4 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
| 5 | Tejgoan 33/11KV S/S | 5 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
| 6 | Moghbazar T&T 33/11 KV, | 6 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
| 7 | Dhanmondi 132/33/11KV S/S | 7 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
| 8 | Dhanmondi 33/11KV S/S | 8 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
| 9 | Kawranbazar 33/11KV S/S | 9 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
| 10 | New Ramna 33/11KV S/S | 10 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
| 11 | Ullon 132/33/11KV S/S | 11 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
| 12 | Ullon local 33/11KV S/S | 12 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
| 13 | Kakrail 33/11KV S/S | 13 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
| 14 | Khillgaon 33/11KV S/S | 14 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
| 15 | Goran 33/11KV S/S | 15 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
| 16 | Taltola 33/11KV S/S | 16 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
| 17 | Satmasjid 33/11KV S/S | 17 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
| 18 | Jigatola OLD 33/11KV S/S | 18 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
| 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| 20 | Kamrangirchar 132/33/11KV S/S | 20 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
| 21 | Kamrangirchar 33/11KV S/S | 21 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
| 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
Narinda | 23 | Banshal 33/11KV S/S | 23 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
| 24 | Japan Garden 33/11 KV, | 24 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
| 25 | Azimpur 33/11 KV, | 25 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
| 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
| 27 | LALBAGH 132/33 KV S/S | 27 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
| 28 | LALBAGH 33/11 KV S/S | 28 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
| 29 | Asad Gate 33/11 KV S/S | 29 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
| 30 | Shatmasjid 132/33 KV S/S | 30 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
Madartek | 31 | Banasree 33/11 SS | 31 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
Maniknagar | 32 | Mugdhapara Hospital | 32 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
| 33 | DMC | 33 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
| 34 | Green Road Dormatory 33/11 SS | 34 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
| 35 | BSMMU 33/11KV S/S | 35 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
| 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
| 37 | Dhaka University 132/33 KV S/S | 37 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
| 38 | Dhaka University 33/11 KV S/S | 38 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
| 39 | Monipuripara 33/11 KV S/S | 39 | 3.2344 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
Not Clear | 40 | BGB 33/11 KV S/S | 40 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
| 41 | BB Aveneu 33/11 KV S/S | 41 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
| 42 | Jigatola 132/33 KV S/S | 42 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
| 43 | Jigatola New 33/11 KV S/S | 43 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
| 44 | Ispahani 33/11 KV S/S |  | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
| 45 | Kamrangirchar-2 33/11 KV S/S |  | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
| 1 | Bangabhaban 132/11KV S/S | 1 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
| 2 | Narinda 132/33KV S/S | 2 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
| 3 | Narinda 33/11KV S/S | 3 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
| 4 | Kumertuly 33/11KV S/S | 4 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
| 5 | Maniknagar 132/33/11KV S/S | 5 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
| 6 | Maniknagar 33/11KV S/S | 26 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
| 7 | Madarteck 132/33KV S/S | 6 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
| 8 | Madarteck 33/11KV S/S | 7 | 3.8449 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
| 9 | Kazla 132/133 KV SS | 39 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
| 10 | Kazla 33/11KV S/S | 8 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
| 11 | Shyampur 132/33KV S/S | 9 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
| 12 | Shyampur 33/11KV S/S | 10 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
| 13 | Shyampur BISIC 33/11KV S/S | 11 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
| 14 | Postogola 132/33 KV S/S | 43 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
| 15 | Postogola 33/11KV S/S | 12 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
| 16 | Fatullah Old 33/11KV S/S | 13 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
| 17 | Sitalakhya 132/33KV S/S | 14 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
| 18 | Sitalakhya 33/11KV S/S | 15 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
| 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
|  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
| 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
| 21 | Siddhirganj 33/11KV S/S | 19 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
| 22 | Demra 33/11KV S/S | 20 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
| 23 | Mondalpara 33/11KV S/S | 21 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
| 24 | Khanpur 33/11KV S/S | 22 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
| 25 | Matuail 132/33 KV S/S | 24 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
| 26 | Matuail 33/11KV S/S | 23 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
| 27 | Sarulia 33/11KV S/S | 25 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
| 28 | IG Gate GIS 33/11 kV | 27 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
| 29 | Motijheel Old 33/11 kV | 28 | 6.6229 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
| 30 | Mitford 33/11 kV | 29 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
| 31 | Biddyut Bhaban 33/11 KV | 30 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
| 32 | Nandalalpur 33/11 kV | 31 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
| 33 | Dapa 33/11 kV | 32 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
| 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
| 35 | Amulia 33/11 kv | 34 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
| 36 | New Fatullah 132/33 KV SS | 35 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
| 37 | New Fatullah 33/11 KV SS | 36 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
| 38 | P & T 33/11 KV SS | 37 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
| 39 | Motijheel 132/33 KV SS | 38 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
| 40 | Motijheel 33/11 KV SS (new) | 39 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 41 | Kamalapur Railway 33/11 KV SS | 40 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
| 42 | Char Syedpur 132/33KV S/S | 41 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
| 43 | Char Syedpur 33/11 KV S/S New | 42 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
| 44 | MI CEMENT 132/33 kV |  | 0.022722

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) | 132 | IMPORT |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000
| 132 KV DHANMONDI-3 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000
[8 empty] | Total Import/Export |  | 0 | 0
[9 empty] | Net Total | 59172000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 | 132 |  | SIEM0480 | 1 | 1632756 | 1632756 | 0 | 1000 | 0
| 132 kV Dhaka University | 132 |  | SIEM0480 | 1 | 59905 | 68964 | 9059 | 1000 | 9059000
3 | 132 kV Dhaka University | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 | 132 |  | SIEM0481 | 1 | 2071385 | 2101057 | 29672 | 1000 | 29672000
8 | 132 kV Ullon Circuit-3 | 132 |  | SIEM0484 | 1 | 2827813 | 2857313 | 29500 | 1000 | 29500000
[7 empty] | 0 | Total Import/Export |  | 68231000 | 0
[7 empty] | 0 | Net Total |  | 68231000
| DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| 132 KV Dhaka University (Export) | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) | 132 |  |  | 1 | 59905 | 68964 | 9059 | 1000 |  | 9059000
[7 empty] | 0 |  | Total |  | 9059000
| DHANMONDI 132 KV SIDE | [5 empty] | 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) | 132 | NET IMPORT | SIEM0487 | 1 | 849792 | 858848 | 9056 | 1000 |  | 9056000
5 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | SIEM0496 | 1 | 1445679 | 1455043 | 9364 | 2000 |  | 18728000
9 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | SIEM0493 | 1 | 1317896 | 1325611 | 7715 | 2000 |  | 15430000
10 | 132/33kV, 80/120 MVA GT-3 (HV) | 132 |  | SIEM0497 | 1 | 1273558 | 1286041 | 12483 | 2000 |  | 24966000
[9 empty] | Total |  | 68180000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 68180000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 68180000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 68180000 |  | 132/33 kv GT LV Side |  | 67312800
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 867200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.272%
| 132 KV TOTAL IMPORT |  | 68180000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2184.48 | 2210.16 | 25.68 | 720000 | 18489600
12 | 132/33 kV GT-2 Incoming | 33 |  | BD001818 | 1 | 2158.72 | 2179.89 | 21.17 | 720000 | 15242400
17 | 132/33 kV GT-3 Incoming | 33 |  | BD001863 | 1 | 1864.35 | 1898.61 | 34.26 | 720000 | 24667200
24 | 132/33 kV GT-4 Incoming | 33 |  | BD001916 | 1 | 1762.32 | 1780.89 | 18.57 | 480000 | 8913600
[7 empty] | 0 |  | Total | 67312800 |  | 0
| DHANMONDI 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [6 empty] | 14971048.3716 | Dhanmondi 33/11 kv ss | 0.36165 | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 | 33 |  | BD001861 | 1 | 2024.03 | 2052.39 | 28.36 | 240000 |  | 6806400 | 6808513.9804 |  |  |  |  | 33/11 kV 20/28 MVA T-1 | 6808513.9804 | 6424413.8049 | 384100.1755 | 5.9788 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 |  | BD001892 | 1 | 2315.96 | 2349.96 | 34 | 240000 |  | 8160000 | 8162534.3912 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 8162534.3912 | 8148798.5197 | 13735.8716 | 0.16856 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 14966400 | 14971048.3716 |  |  |  |  | 33 KV Feeders | 14971048.3716 | 14573212.3246 | 397836.0471 | 2.7299 | OK
5 | New Ramna Circuit-1 | 33 |  | BD001919 | 1 | 1435.41 | 1451.13 | 15.72 | 240000 |  | 3772800 | 3773971.7832 |  | 6614053.6023 | New Ramna 33/11 kv ss | 2.8644 | New Ramna Circuit-1 | 3773971.7832 | 3633696.4811 | 140275.3022 | 3.8604 | OK
8 | Kakrail Circuit-1 | 33 |  | BD001825 | 1 | 782.32 | 804.13 | 21.81 | 240000 |  | 5234400 | 5236025.7374 |  |  |  |  | Kakrail Circuit-1 | 5236025.7374 | 5069883.1933 | 166142.5441 | 3.277 | OK
9 | Kawran Bazar Circuit-1 | 33 |  | BD001820 | 1 | 1811.32 | 1826.25 | 14.93 | 240000 |  | 3583200 | 3584312.8959 |  | 10911387.8847 | Kakrail 33/11 kv ss | 1.8285 | Kawran Bazar Circuit-1 | 3584312.8959 | 4010755.5343 | -426442.6384 | -10.6325 | OK
10 | New Ramna Circuit-2 | 33 |  | BD001816 | 1 | 1164.56 | 1176.39 | 11.83 | 240000 |  | 2839200 | 2840081.8191 |  |  |  |  | New Ramna Circuit-2 | 2840081.8191 | 2449683.0209 | 390398.7981 | 15.9367 | OK
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 |  | 0 | 0 |  | 3584312.8959 | Kawran Bazar 33/11 kv ss | 0.69515 | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder | 33 |  | BD001840 | 1 | 377.52 | 391.38 | 13.86 | 240000 |  | 3326400 | 3327433.1371 |  |  |  |  | DMC Hospital Feeder | 3327433.1371 | 2790717.3239 | 536715.8133 | 19.2322 | OK
15 | Green Road Circuit-2 (U/G) | 33 |  | BD001918 | 1 | 2031.88 | 2059.78 | 27.9 | 240000 |  | 6696000 | 6698079.6916 |  | 3327433.1371 | DMC Hospital 33/11 kv ss | 0.90537 | Green Road Circuit-2 (U/G) | 6698079.6916 | 7334639.1627 | -636559.4711 | -8.6788 | OK
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1565.51 | 1589.15 | 23.64 | 240000 |  | 5673600 | 5675362.1473 |  |  |  |  | Kakrail Circuit-2 | 5675362.1473 | 5636672.5982 | 38689.5491 | 0.68639 | OK
18 | BSMMU Hospital Circuit-1 | 33 |  | BD001920 | 1 | 679.62 | 694.88 | 15.26 | 240000 |  | 3662400 | 3663537.4944 |  | 14308442.6387 | Green Road 33/11 kv ss | 0.33416 | BSMMU Hospital Circuit-1 | 3663537.4944 | 3609679.9809 | 53857.5136 | 1.492 | OK
19 | Azimpur Circuit-1 | 33 |  | BD001822 | 1 | 1906.63 | 1942.41 | 35.78 | 240000 |  | 8587200 | 8589867.074 |  |  |  |  | Azimpur Circuit-1 | 8589867.074 | 8235257.9204 | 354609.1536 | 4.306 | OK
20 | Azimpur Circuit-2 | 33 |  | BD001857 | 1 | 1804.37 | 1804.37 | 0 | 240000 |  | 0 | 0 |  | 4981546.724 | BSMMU 33/11 kv ss | 0.89671 | Azimpur Circuit-2 | 0 | 4354191.4872 | -4354191.4872 | -100 | CHECK
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 139.74 | 145.23 | 5.49 | 240000 |  | 1317600 | 1318009.2296 |  |  |  |  | BSMMU Hospital Circuit-2 | 1318009.2296 | 1282481.111 | 35528.1187 | 2.7703 | OK
23 | Green Road Circuit-1 | 33 |  | BD001865 | 1 | 1347.73 | 1379.43 | 31.7 | 240000 |  | 7608000 | 7610362.9471 |  | 8589867.074 | Azimpur 33/11 kv ss | 1.4942 | Green Road Circuit-1 | 7610362.9471 | 6962383.4095 | 647979.5376 | 9.3069 | OK
26 | 33/0.4 kV, 500 kVA AT-1 | 0.4 |  | 84.2659 | 1 | 311229 | 313699 | 2470 | 10 |  | 24700 | 24707.6715 | Paribag |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 24707.6715 | 10867.4663 | 13840.2052 | 127.3545 | FAULT
25 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 |  | 84.2673 | 1 | 478688 | 478688 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 13078.9857 | -13078.9857 | -100 | CHECK
[9 empty] | Total |  | 52325500 | 52341751.6284 | [5 empty] | 52341751.6284 | 55393987.6754 | -3052236.0471 | -5.51 | OK
[8 empty] | Grand Total |  | 67312800 | 67291900 | 67312800 | 0.031059
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming | 11 | IMPORT | DHK60884 | 1 | 800612.84 | 845791.6 | 45178.76 | 180 | 8132176.8 |  | 8188549.8812
16 | 33/11 kV Transformer-1 Incoming | 11 |  | DHK60976 | 1 | 418508.56 | 455929.7 | 37421.14 | 180 | 6735805.2 |  | 6782498.4905
[7 empty] | 0 |  | Total | 14867982 |  | 14971048.3716
| DHANMONDI 11 kV SIDE | [5 empty] | 0
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 3920074 | 5173196 | 1253122 | 1 |  | 1253122 | 1257653.9222 | Paribag |  |  |  | 11 kV Balaka Feeder | 1257653.9222 | 1137299.4891 | 120354.4331 | 10.5825 | OK
5 | 11 kV Mogbazar O/H | 11 |  | HA021100463-02 | 1 | 44616340 | 46129640 | 1513300 | 1 |  | 1513300 | 1518772.8573 | Paribag |  |  |  | 11 kV Mogbazar O/H | 1518772.8573 | 1477894.3769 | 40878.4804 | 2.766 | OK
6 | 11 kV Panthopath Feeder | 11 |  | HA021101078-02 | 1 | 56931817 | 59070322 | 2138505 | 1 |  | 2138505 | 2146238.9144 | Paribag |  |  |  | 11 kV Panthopath Feeder | 2146238.9144 | 2162610.3185 | -16371.4041 | -0.75702 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 |  | DHK60882 | 1 | 201916.09 | 208836.3 | 6920.21 | 60 |  | 415212.6 | 416714.2185 | Paribag |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 416714.2185 | 395540.6076 | 21173.6109 | 5.3531 | OK
8 | 11 kV P G Hospital Feeder | 11 |  | DHK60889 | 1 | 275542.83 | 279161.7 | 3618.87 | 60 |  | 217132.2 | 217917.4597 | Paribag |  |  |  | 11 kV P G Hospital Feeder | 217917.4597 | 226732.9713 | -8815.5116 | -3.8881 | OK
9 | 11 kV Abdul Monem Ltd | 11 |  | DHK60890 | 1 | 684.97 | 691.92 | 6.95 | 60000 |  | 417000 | 418508.0827 | Paribag |  |  |  | 11 kV Abdul Monem Ltd | 418508.0827 | 415788.2923 | 2719.7904 | 0.65413 | OK
10 | 11 kV Surjasen Hall Feeder | 11 |  | DHK60880 | 1 | 526282.72 | 538943.6 | 12660.88 | 60 |  | 759652.8 | 762400.0883 | Ramna |  |  |  | 11 kV Surjasen Hall Feeder | 762400.0883 | 500947.7604 | 261452.3278 | 52.1915 | FAULT
11 | 11 kV Azimpur-1 Feeder | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | 11 |  | DHK60873 | 1 | 910191.77 | 918512 | 8320.23 | 60 |  | 499213.8 | 501019.2093 | Ramna |  |  |  | 11 kV TSC Feeder | 501019.2093 | 594864.6942 | -93845.4849 | -15.7759 | OK
13 | 11 kV SCADA Bhaban | 11 |  | DHK60883 | 1 | 27965.2 | 28074.3 | 109.1 | 60 |  | 6546 | 6569.6736 | Paribag |  |  |  | 11 kV SCADA Bhaban | 6569.6736 | 7038.2714 | -468.5977 | -6.6579 | OK
14 | 11 kV DPH Sw/S-2 | 11 |  | DHK60871 | 1 | 455579.68 | 474478.5 | 18898.82 | 60 |  | 1133929.2 | 1138030.0608 | Paribag |  |  |  | 11 kV DPH Sw/S-2 | 1138030.0608 | 1225995.769 | -87965.7081 | -7.175 | OK
17 | 11 kV New Elephant Road Feeder | 11 |  | DHK60981 | 1 | 38853.86 | 61120.9 | 22267.04 | 60 |  | 1336022.4 | 1340854.1319 | Paribag |  |  |  | 11 kV New Elephant Road Feeder | 1340854.1319 | 1236853.2667 | 104000.8652 | 8.4085 | OK
18 | 11 kV Dhanmondi O/H Feeder | 11 |  | DHK61110 | 1 | 356765.96 | 380880.9 | 24114.94 | 60 |  | 1446896.4 | 1452129.1083 | Paribag |  |  |  | 11 kV Dhanmondi O/H Feeder | 1452129.1083 | 1368507.5074 | 83621.6009 | 6.1104 | OK
19 | 11 kV Sonargaon Feeder | 11 |  | DHK61115 | 1 | 283945.16 | 312180.8 | 28235.64 | 60 |  | 1694138.4 | 1700265.2603 | Paribag |  |  |  | 11 kV Sonargaon Feeder | 1700265.2603 | 1714907.3622 | -14642.1019 | -0.85381 | OK
20 | 11 kV Museum Feeder | 11 |  | DHK61107 | 1 | 542994.77 | 545315.1 | 2320.33 | 60 |  | 139219.8 | 139723.2891 | Ramna |  |  |  | 11 kV Museum Feeder | 139723.2891 | 145373.4466 | -5650.1575 | -3.8867 | OK
21 | 11 kV Shanta property | 11 |  | DHK61112 | 1 | 334966.62 | 338664.1 | 3697.48 | 60 |  | 221848.8 | 222651.1173 | Paribag |  |  |  | 11 kV Shanta property | 222651.1173 | 196910.1041 | 25741.0132 | 13.0725 | OK
22 | 11 kV BIRDEM RMU Feeder | 11 |  | DHK61108 | 1 | 672823.56 | 685561.8 | 12738.24 | 60 |  | 764294.4 | 767058.4747 | Kakrail |  |  |  | 11 kV BIRDEM RMU Feeder | 767058.4747 | 1048103.4598 | -281044.9851 | -26.8146 | OK
23 | 11 kV Azimpur-2 Feeder | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 | 11 |  | DHK60978 | 1 | 751590.62 | 767608.4 | 16017.78 | 60 |  | 961066.8 | 964542.5031 | Kakrail |  |  |  | 11 kV DPH Sw/S-1 | 964542.5031 | 717844.627 | 246697.8761 | 34.3665 | OK
[9 empty] | Total | 14971048.3716 | 14917100.6 | 14971048.3716 | 0.36165
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag at 33 KV level |  |  | 11861012.4787
[6 empty] | Azimpur at 33 KV level |  |  | 0
[6 empty] | Ramna at 33 KV level |  |  | 1403142.5867
[6 empty] | Kakrail at 33 KV level |  |  | 1731600.9777
[6 empty] | Total = |  |  | 14995756.0431 | 2.8303e-09
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1811.32 | 1826.25 | 14.93 | 240000 | 0 | 3583200 | 3584312.8959
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 3583200 | 3584312.8959
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar | 33 | 0 | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
KAWRANBAZAR 33 KV SIDE (RECEIVING)
1 | 33 kV Dhanmondi Circuit-1 | 33 |  | DHK61036 | 1 | 3391.88 | 3405.32 | 13.44 | 270000 | 3628800
5 | 33 kV Dhanmondi Circuit-2 | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar | 33 |  | DHK 61038 | 1 | 1059.48 | 1059.48 | 0 | 270000 | 0
[7 empty] | 0 |  | Total | 3628800 | 0 | 3584312.8959
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| KAWRANBAZAR 33 KV SIDE | [5 empty] | 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | DHK61039 | 1 | 5091.79 | 5111.93 | 20.14 | 180000 |  | 3625200
3 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
[9 empty] | Total |  | 3625200 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 3584312.8959 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 3584312.8959
| MOGBAZAR 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 3584312.8959 |  | 33 KV TX HV SIDE |  | 3625200
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -40887.1041
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -1.141%
| TOTAL IMPORT |  | 3584312.8959
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK00182 | 1 | 13286.8 | 13643.5 | 356.7 | 10000 | 3567000 |  | 3584312.8959
15 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
[7 empty] | 0 |  | Total | 3567000 |  | 3584312.8959
| KAWRANBAZAR 11 KV SIDE | [5 empty] | 0
6 | WASA Bhaban | 11 |  | 8536188 | 1.14 | 2089.7 | 2288.8 | 199.1 | 1000 | 986040 | 986040 | 992894.4687 | Shere b.nagar | From Customer End |  |  | WASA Bhaban | 992894.4687 | 967717.4567 | 25177.0121 | 2.6017 | OK
7 | Sangsad Bhaban | 11 |  | 8536178 | 1.14 | 567782 | 568300 | 518 | 44 |  | 25982.88 | 26163.5003 | Shere b.nagar |  |  |  | Sangsad Bhaban | 26163.5003 | 291323.9838 | -265160.4835 | -91.0191 | CHECK
8 | Air Port Road (West) | 11 |  | 8536182 | 1.14 | 99649.5 | 100568.1 | 918.6 | 1000 |  | 1047204 | 1054483.651 | Shere b.nagar |  |  |  | Air Port Road (West) | 1054483.651 | 1142492.7318 | -88009.0808 | -7.7033 | OK
9 | ICC (PM Office) | 11 |  | 8536193 | 1.14 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | 11 |  | DHK00183 | 1.14 | 14511.4 | 15079.3 | 567.9 | 444.44 |  | 287733.1226 | 289733.3028 | Shere b.nagar |  |  |  | (UTC) Tower | 289733.3028 | 306081.9435 | -16348.6407 | -5.3413 | OK
11 | Sonargaon Hotel | 11 |  | 8536190 | 1.14 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Estimated |  |  | Sonargaon Hotel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Panthopath | 11 |  | 8536184 | 1.14 | 33415.5 | 34310.5 | 895 | 1000 |  | 1020300 | 1027392.6275 | Shere b.nagar |  |  |  | Panthopath | 1027392.6275 | 1044641.4249 | -17248.7974 | -1.6512 | OK
13 | Titas Bhaban | 11 |  | DHK00190 | 1.14 | 55090.4 | 55463.3 | 372.9 | 444.44 |  | 188934.1106 | 190247.4883 | Kakrail |  |  |  | Titas Bhaban | 190247.4883 | 258497.9936 | -68250.5053 | -26.4027 | OK
16 | Green Road Dormatory s/s | 11 |  | DHK00021 | 1.14 | 0 | 0 | 0 | 444.44 |  | 0 | 0 |  |  |  |  | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 | 11 |  | 85-12906 | 1.14 | 67959 | 68255 | 296 | 10 |  | 3374.4 | 3397.8572 | Shere b.nagar |  |  |  | Aux. Transformer, AT-1 | 3397.8572 | 0 | 3397.8572 | #DIV/0! | #DIV/0!
27 | Aux. Transformer, AT-2 | 11 |  | 85-12909 | 1.14 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 3584312.8959 | 3559568.5133 | 3584312.8959 | 0.69515
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail at 33 KV level |  |  | 190247.4883
[5 empty] | Shere b.nagar at 33 KV level |  |  | 3394065.4076
[5 empty] | Total = |  |  | 3584312.8959 | 0
[8 empty] | Customer Name | Customer Number | Feeder name | Consumption | OMF
[8 empty] | Square Hospital | 27529489 | Wasa Bhaban | 986040 | 6000
[8 empty] | NOCS Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[8 empty] | ShereBangla Nagar | 2249.27 | 2365.07 | 874.47 | 923.01
[10 empty] | 2023-06-01 |  | 2023-06-01
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1435.41 | 1451.13 | 15.72 | 240000 | 0 | 3772800 | 3773971.7832
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1164.56 | 1176.39 | 11.83 | 240000 | 0 | 2839200 | 2840081.8191
[9 empty] | Total | 0 | 6612000 | 6614053.6023
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1513800 | 1520843.5632
[9 empty] | Total | 0 | 1513800 | 1520843.5632
NEW RAMNA 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 8134897.1655
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  |  | 0 |  |  | 0
| Feeder No.2 | 33 | [5 empty] | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.3. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 8134897.1655 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 6614053.6023 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 8134897.1655
| NARINDA 33 KV SIDE |  | 1520843.5632 |  | 33 KV NET IMPORT |  |  | 8134897.1655 |  | 33 KV TX HV SIDE |  | 8134897.1655
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 8134897.1655
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK 00002 | 1 | 24554.2 | 24930.5 | 376.3 | 10000 | 3763000 |  | 3775576.3628
15 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK 00007 | 1 | 12884.6 | 13167.7 | 283.1 | 10000 | 2831000 |  | 2840461.5155
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming | 11 |  | DHKA2182 | 1 | 574.76 | 583.17 | 8.41 | 180000 | 1513800 |  | 1518859.2873 |  | 5214200 | Converted 9 Days Reading into 31 days | Due to BUS PT Missing
[9 empty] | Total | 8107800 |  | 8134897.1655
NEW RAMNA 11 KV SIDE
4 | Police Bhaban | 11 |  | DHK 00005 | 1 | 72836.6 | 73101.3 | 264.7 | 444.44 |  | 117643.268 | 121013.0538 | Ramna |  |  |  | Police Bhaban | 121013.0538 | 111715.2077 | 9297.846 | 8.3228 | OK
5 | Water Works | 11 |  | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Lalbag |  |  |  | Water Works | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | GPO | 11 |  | DHK 00060 | 1 | 97306.6 | 97916.8 | 610.2 | 444.44 |  | 271197.288 | 278965.4908 | Ramna |  |  |  | GPO | 278965.4908 | 233730.721 | 45234.7698 | 19.3534 | OK
7 | Culvert Road | 11 |  | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 65 | 765109.8 | 787025.6832 | Ramna |  |  |  | Culvert Road | 787025.6832 | 769934.2629 | 17091.4203 | 2.2199 | OK
8 | Secretariat (East) | 11 |  | DHK00059 | 1 | 81714.5 | 81719.4 | 4.9 | 444.44 |  | 2177.756 | 2240.1359 | Ramna |  |  |  | Secretariat (East) | 2240.1359 | 29358.1395 | -27118.0036 | -92.3696 | CHECK
9 | Siddik Bazar | 11 |  | DHK00076 | 1 | 27275.4 | 29231.2 | 1955.8 | 444.44 |  | 869235.752 | 894134.2296 | Bangshal |  |  |  | Siddik Bazar | 894134.2296 | 765262.7858 | 128871.4438 | 16.8402 | OK
10 | Bokshi Bazar | 11 |  | DHK 00206 | 1 | 84325 | 85464 | 1139 | 444.44 |  | 506217.16 | 520717.296 | Ramna |  |  |  | Bokshi Bazar | 520717.296 | 447450.7163 | 73266.5797 | 16.3742 | OK
11 | Ramna 11 kV Sw/S Circuit-1 | 11 |  | DHK00198 | 1 | 44281.1 | 46597.3 | 2316.2 | 444.44 |  | 1029411.928 | 1058898.5083 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 1058898.5083 | 1085933.5304 | -27035.0221 | -2.4896 | OK
12 | TNT RMU | 11 |  | DHK 00207 | 1 | 59418.3 | 60351.5 | 933.2 | 444.44 |  | 414751.408 | 426631.5896 | Ramna |  |  |  | TNT RMU | 426631.5896 | 435698.3854 | -9066.7957 | -2.081 | OK
13 | DIT 11 kV Sw/S Circuit-1 | 11 |  | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 35665.375 | -35665.375 | -100 | CHECK
16 | Secretariat (West) | 11 |  | DHK 00006 | 1 | 67064.7 | 67894.2 | 829.5 | 444.44 |  | 368662.98 | 379223 | Ramna |  |  |  | Secretariat (West) | 379223 | 77048.1002 | 302174.8998 | 392.1899 | FAULT
17 | Ramna 11 kV Sw/S Circuit-2 | 11 |  | DHK00197 | 1 | 84761.5 | 84763.4 | 1.9 | 444.44 |  | 844.436 | 868.6241 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 868.6241 | 952.8917 | -84.2676 | -8.8434 | OK
18 | Sayed Nazrul Islam Road | 11 |  | DHK00186 | 1 | 21662.7 | 24569.9 | 2907.2 | 444.44 |  | 1292075.968 | 1329086.3239 | Ramna |  |  |  | Sayed Nazrul Islam Road | 1329086.3239 | 1287356.6852 | 41729.6387 | 3.2415 | OK
19 | Gulistan Complex | 11 |  | DHK00030 | 1 | 53974.5 | 54446.3 | 471.8 | 444.44 |  | 209686.792 | 215693.0819 | Ramna |  |  |  | Gulistan Complex | 215693.0819 | 200288.7599 | 15404.3219 | 7.6911 | OK
20 | Mohanagor Nattomanso | 11 |  | DHK 00008 | 1 | 99681.5 | 99840.8 | 159.3 | 444.44 |  | 70799.292 | 72827.2741 | Ramna |  |  |  | Mohanagor Nattomanso | 72827.2741 | 40429.8335 | 32397.4406 | 80.1325 | FAULT
21 | DIT 11 kV Sw/S Circuit-2 | 11 |  | DHK00196 | 1 | 23893.8 | 24947 | 1053.2 | 444.44 |  | 468084.208 | 481492.0598 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-2 | 481492.0598 | 701782.0483 | -220289.9885 | -31.3901 | OK
22 | Jail | 11 |  | DHK00009 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | 11 |  | HA021100713-02 | 1 | 75857044 | 75962552 | 105508 | 1 |  | 105508 | 108530.1819 | Ramna |  |  |  | Kosturi Bazar | 108530.1819 | 101993.6695 | 6536.5124 | 6.4087 | OK
24 | Kaptan Bazar | 11 |  | HA021101251-02 | 1 | 5820909 | 6236867 | 415958 | 1 |  | 415958 | 427872.7434 | Narinda |  |  |  | Kaptan Bazar | 427872.7434 | 409490.3581 | 18382.3853 | 4.4891 | OK
25 | G.T.V | 11 |  | HA-021101054-02 | 1 | 70498299 | 71120147 | 621848 | 1 |  | 621848 | 639660.2776 | Ramna |  |  |  | G.T.V | 639660.2776 | 603518.518 | 36141.7596 | 5.9885 | OK
26 | Kazi Alauddin Road | 11 |  | HA021100951-02 | 1 | 5667944 | 6043531 | 375587 | 1 |  | 375587 | 386345.3523 | Bangshal |  |  |  | Kazi Alauddin Road | 386345.3523 | 300171.4873 | 86173.865 | 28.7082 | OK
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 |  | 2436 | 1 | 67423 | 67423 | 0 | 10 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 10.2097 | -10.2097 | -100 | CHECK
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 |  | 2437 | 1 | 88090 | 88447 | 357 | 10 |  | 3570 | 3672.2594 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 3672.2594 | 3624.4279 | 47.8316 | 1.3197 | OK
[9 empty] | Grand Total | 8134897.1655 | 7908369.036 | 8134897.1655 | 2.8644
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 5945052.7804
[5 empty] | Lalbag | at 33 KV level |  | 0
[5 empty] | Bangshal | at 33 KV level |  | 1280479.5819
[5 empty] | Motijheel | at 33 KV level |  | 481492.0598
[5 empty] | Narinda | at 33 KV level |  | 427872.7434
[5 empty] | Total = |  |  | 8134897.1655 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 782.32 | 804.13 | 21.81 | 240000 | 0 | 5234400 | 5236025.7374
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1565.51 | 1589.15 | 23.64 | 240000 | 0 | 5673600 | 5675362.1473
[9 empty] | Total | 0 | 10908000 | 10911387.8847
ULLON 33 KV SIDE
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9044 | 1163.9083 | 0.0039 | 240000 | 0 | 936 | 941.5329
[9 empty] | Total | 0 | 936 | 941.5329
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder | 33 | IMPORT |  | 1 | 226957 | 226957 | 0 | 1000 |  | 0
[9 empty] | Total | 0 | 0 | 0
KAKRAIL 33 KV SIDE (RECEIVING)
5 | 33 kV Dhanmondi-2 | 33 |  | 06604376 | 1 | 5222.44 | 5254.06 | 31.62 | 180000 | 5691600
2 | 33 kV Dhanmondi-1 | 33 |  | 06604375 | 1 | 1979.76 | 2009.03 | 29.27 | 180000 | 5268600 | Previus Reading e amader kono dosomik cilo na
| 33 KV Kakrail From ULLON | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
[9 empty] | Total | 10960200 | 0 | 0
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 10911387.8847 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KAKRAIL 33 KV NET IMPORT |  | 10912329.4176
| ULLON 33 KV SIDE |  | 941.5329 |  | KAKRAIL 33 KV NET IMPORT |  |  | 10912329.4176 |  | KAKRAIL KV NET IMPORT |  | 10891556.917
| Taltola 33 KV SIDE |  | 0 | [6 empty] | LOSS UNITS=> |  | 20772.5006
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1904%
| TOTAL IMPORT |  | 10912329.4176
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK00017 | 1 | 17807.9 | 18397 | 589.1 | 8888.89 | 5236445.099 |  | 5246432.1064
15 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK00018 | 1 | 4442.8 | 5079 | 636.2 | 8888.89 | 5655111.818 |  | 5665897.3113
[7 empty] | 0 |  | Total | 10891556.917 |  | 10912329.4176
| KAKRAIL 11 KV SIDE | [5 empty] | 0
7 | Pioneer | 11 |  | 06604395 | 1 | 23641.25 | 23746.79 | 105.54 | 8000 |  | 844320 | 859758.1646 | Ramna |  |  |  | Pioneer | 859758.1646 | 826396.2524 | 33361.9122 | 4.037 | OK
8 | Pir Saheber Goli | 11 |  | DHK-00102 | 1 | 76172.5 | 79643 | 3470.5 | 444.444 |  | 1542442.902 | 1570646.0565 | Rajarbag |  |  |  | Pir Saheber Goli | 1570646.0565 | 1456807.534 | 113838.5224 | 7.8142 | OK
9 | Montri Para | 11 |  | DHK-00110 | 1 | 12504.9 | 12608.2 | 103.3 | 2222.22 |  | 229555.326 | 233752.6835 | Kakrail |  |  |  | Montri Para | 233752.6835 | 183436.8651 | 50315.8185 | 27.4295 | OK
10 | Baily Road 11 kV Sw/S-2 | 11 |  | 9119865 | 1 | 60588.9 | 62936.7 | 2347.8 | 1000 |  | 2347800 | 2390728.8929 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-2 | 2390728.8929 | 2272508.865 | 118220.0278 | 5.2022 | OK
11 | Jamuna U/G 11 KV Jonaki O/H | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | 11 |  | 1025651 | 1 | 28699 | 28975.9 | 276.9 | 1000 |  | 276900 | 281963.0422 | Ramna |  |  |  | High Court | 281963.0422 | 304725.5352 | -22762.493 | -7.4698 | OK
13 | Secretaiat | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | 11 |  | 06604402 | 1 | 5592.5 | 5631.51 | 39.01 | 40000 |  | 1560400 | 1588931.4952 | Rajarbag |  |  |  | Shanti Nagar Bazar | 1588931.4952 | 1455327.1248 | 133604.3704 | 9.1804 | OK
17 | Tottho Bhovon | 11 |  | 9119867 | 1 | 31865.1 | 32076 | 210.9 | 1000 |  | 210900 | 214756.2499 | Kakrail |  |  |  | Tottho Bhovon | 214756.2499 | 266523.7033 | -51767.4534 | -19.4232 | OK
18 | Central Police Hospital/ PNT (Circuit House) | 11 |  | DHK00199 | 1 | 78080.07 | 78368.5 | 288.43 | 2222.22 |  | 640954.9146 | 652674.6032 | Kakrail |  |  |  | Central Police Hospital/ PNT (Circuit House) | 652674.6032 | 659362.3521 | -6687.7489 | -1.0143 | OK
19 | Baily Road 11 kV Sw/S-1 | 11 |  | DHK00027 | 1 | 54773.6 | 55235.8 | 462.2 | 2222.22 |  | 1027110.084 | 1045890.5162 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-1 | 1045890.5162 | 1203453.6068 | -157563.0906 | -13.0926 | OK
20 | Bijoy Nagar | 11 |  | D1025656 | 1 | 64877.9 | 65886.7 | 1008.8 | 1000 |  | 1008800 | 1027245.6372 | Ramna |  |  |  | Bijoy Nagar | 1027245.6372 | 1033096.3518 | -5850.7146 | -0.56633 | OK
21 | Shilpakala Academy | 11 |  | D0086137 | 1 | 24493.9 | 25394.3 | 900.4 | 1000 |  | 900400 | 916863.5723 | Ramna |  |  |  | Shilpakala Academy | 916863.5723 | 907912.3538 | 8951.2186 | 0.98591 | OK
22 | Judges Complex | 11 |  | 06604344 | 1 | 667.77 | 670.94 | 3.17 | 40000 |  | 126800 | 129118.504 | Kakrail |  |  |  | Judges Complex | 129118.504 | 137005.2472 | -7886.7433 | -5.7565 | OK
23 | Auxiliary Transformer, AT-1 | 11 |  | 39333 | 1 | 492441 | 492441 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Auxiliary Transformer, AT-2 | 11 |  | 39254 | 1 | 1195010 | 1195010 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10912329.4176 | 10716383.2266 | 10912329.4176 | 1.8285
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 3085830.4163
[5 empty] | Rajarbag | at 33 KV level |  | 3159577.5517
[5 empty] | Kakrail | at 33 KV level |  | 4666921.4496
[5 empty] | Total = |  |  | 10912329.4176 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 679.62 | 694.88 | 15.26 | 240000 | 0 | 3662400 | 3663537.4944
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 139.74 | 145.23 | 5.49 | 240000 | 0 | 1317600 | 1318009.2296
[9 empty] | Total |  | 4980000 | 4981546.724 | 0.031059
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 | 33 |  | BD017073 | 1 | 60215.13 | 64006.23 | 3791.1 | 1000 | 3791100
4 | 33 kV Dhanmondi Incoming Circuit-2 | 33 |  | BD017074 | 1 | 33466.76 | 34819.01 | 1352.25 | 1000 | 1352250
| 33 KV Ullon-1 Feeder | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
[7 empty] | 0 |  | Total | 5143350 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
0
0
[7 empty] | 0 |  | Total
0
| BSMMU HOSPITAL 33 KV SIDE | [5 empty] | 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017072 | 1 | 88059.92 | 92337.81 | 4277.89 | 888.89 |  | 3802573.6421
6 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017076 | 1 | 30490.64 | 32017.33 | 1526.69 | 888.89 |  | 1357059.4741
[9 empty] | Total |  | 5159633.1162 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4981546.724 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 4981546.724
[5 empty] | 33 KV NET IMPORT |  |  | 4981546.724 |  | 33/11 KV XF HV SIDE |  | 5159633.1162
[10 empty] | LOSS UNITS=> |  | -178086.3922
[10 empty] | LOSS % IN => |  | -3.575%
| TOTAL IMPORT |  | 4981546.724
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD017081 | 1 | 66067.88 | 69838.24 | 3770.36 | 1000 | 3770360 |  | 3673561.9956
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD017082 | 1 | 26276.62 | 27619.07 | 1342.45 | 1000 | 1342450 |  | 1307984.7285
[6 empty] | 0 | 0 |  | Total | 5112810 |  | 4981546.724
| BSMMU HOSPITAL 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV Jamuna (F1) | 11 |  | BD017073 | 1 | 0.3512 | 0.3625 | 0.0113 | 2000 |  | 22.6 | 22.8027 | Kakrail |  |  |  | 11 kV Jamuna (F1) | 22.8027 | 22.5473 | 0.25531 | 1.1323 | OK
9 | 11 kV Pukur Par (F2) | 11 |  | BD017074 | 1 | 2883.64 | 2906.26 | 22.62 | 2000 |  | 45240 | 45645.6695 | Kakrail |  |  |  | 11 kV Pukur Par (F2) | 45645.6695 | 45879.8149 | -234.1454 | -0.51035 | OK
10 | 11 kV BSMMU Convention center (F3) | 11 |  | BD017075 | 1 | 1695.63 | 1714.95 | 19.32 | 2000 |  | 38640 | 38986.4869 | Kakrail |  |  |  | 11 kV BSMMU Convention center (F3) | 38986.4869 | 53187.5695 | -14201.0826 | -26.7 | OK
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 |  | BD017076 | 1 | 2841.69 | 2929.26 | 87.57 | 2000 |  | 175140 | 176710.4897 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 176710.4897 | 172426.7726 | 4283.7172 | 2.4844 | OK
12 | 11 kV Holi Family Feeder (F5) | 11 |  | BD017077 | 1 | 13664.28 | 14032.26 | 367.98 | 2000 |  | 735960 | 742559.3925 | Kakrail |  |  |  | 11 kV Holi Family Feeder (F5) | 742559.3925 | 663133.437 | 79425.9555 | 11.9774 | OK
13 | 11 kV Navy House Feeder (F6) | 11 |  | BD017078 | 1 | 25982.79 | 26311.05 | 328.26 | 2000 |  | 656520 | 662407.0498 | Kakrail |  |  |  | 11 kV Navy House Feeder (F6) | 662407.0498 | 617092.5697 | 45314.4802 | 7.3432 | OK
14 | 11 kV Paribagh Feeder (F7) | 11 |  | BD017079 | 1 | 30291.6 | 31129.75 | 838.15 | 2000 |  | 1676300 | 1691331.4714 | Paribag |  |  |  | 11 kV Paribagh Feeder (F7) | 1691331.4714 | 1532172.4233 | 159159.0481 | 10.3878 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 |  | BD017080 | 1 | 5957.89 | 6172.02 | 214.13 | 2000 |  | 428260 | 432100.2302 | Paribag |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 432100.2302 | 400577.6906 | 31522.5396 | 7.8693 | OK
18 | 11 kV Oncology Bhaban (F9) | 11 |  | BD017083 | 1 | 2161.63 | 2225.09 | 63.46 | 2000 |  | 126920 | 128058.0984 | Paribag |  |  |  | 11 kV Oncology Bhaban (F9) | 128058.0984 | 129888.7959 | -1830.6975 | -1.4094 | OK
19 | Rupayan Trade Center | 11 |  | BD017084 | 1 | 928.49 | 1068.48 | 139.99 | 2000 |  | 279980 | 282490.5956 | Kakrail |  |  |  | Rupayan Trade Center | 282490.5956 | 277634.2814 | 4856.3142 | 1.7492 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 |  | BD017085 | 1 | 1996.69 | 2058.21 | 61.52 | 2000 |  | 123040 | 124143.3062 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 124143.3062 | 110824.2128 | 13319.0934 | 12.0182 | OK
21 | 11 kV BSMMU RMU (F12) | 11 |  | BD017086 | 1 | 1881.92 | 1965.52 | 83.6 | 2000 |  | 167200 | 168699.2913 | Paribag |  |  |  | 11 kV BSMMU RMU (F12) | 168699.2913 | 166467.8321 | 2231.4592 | 1.3405 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 |  | BD017087 | 1 | 3915.28 | 4032.7 | 117.42 | 2000 |  | 234840 | 236945.8228 | Paribag |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 236945.8228 | 229298.4167 | 7647.406 | 3.3351 | OK
23 | 11 kV BCS Academy RMU (F14) | 11 |  | BD017088 | 1 | 965.83 | 995.07 | 29.24 | 2000 |  | 58480 | 59004.3933 | Paribag |  |  |  | 11 kV BCS Academy RMU (F14) | 59004.3933 | 75292.0174 | -16287.6242 | -21.6326 | OK
24 | Spare | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | 11 |  | BD017090 | 1 | 971.62 | 1147.96 | 176.34 | 2000 |  | 352680 | 355842.5004 | Paribag |  |  |  | BSMMU Super Specialist Hospital RMU | 355842.5004 | 253677.7304 | 102164.7699 | 40.2734 | FAULT
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKD4418 | 1 | 2460.23 | 2605.78 | 145.55 | 100 |  | 14555 | 14685.5155 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 14685.5155 | 15087.5942 | -402.0788 | -2.665 | OK
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 |  | 0 | 0 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 5159633.1162 | 5113777.6 | 5159633.1162 | 0.89671
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 2072965.793
[5 empty] | Paribag | at 33 KV level |  | 3086667.3232
[5 empty] | Total = |  |  | 5159633.1162 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 | 132 |  | 8993518 | 1 | 1078.582 | 1098.154 | 19.572 | 960000 | 0 | 18789120
|  | 132 |  |  | 1 | 70.056 | 70.056 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 | 132 |  | 5014660 | 1 | 255.206 | 274.986 | 19.78 | 960000 | 0 | 18988800
|  | 132 |  |  | 1 | 4.361 | 4.361 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 | 132 |  | 38992597 | 1 | 539.605 | 575.795 | 36.19 | 1440000 | 0 | 52113600
|  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 89891520
[9 empty] | Net Total | 89891520
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 | 132 | RECEIVE | 6604452 | 1 | 238756 | 256887 | 18131 | 1000 | 18131000
|  | 132 |  |  | 1 | 6755 | 6755 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) | 132 |  |  | 1 | 4278687 | 4330666 | 51979 | 1000 | 51979000
|  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar | 132 |  |  | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  |  | 1 | 442987 | 479088 | 36101 | 1000 |  | 36101000
| Kallyanpur-2 | 132 |  | 6604428 | 1 | 337429 | 355386 | 17957 | 1000 | 17957000
|  | 132 |  |  | 1 | 7111 | 7111 | 0 | 1000 |  | 0
[7 empty] | 0 | Total Import/Export |  | 88067000 | 36101000
[7 empty] | 0 | Net Total |  | 51966000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
6 | Kamrangirchar | 132 |  | SIEM491 | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  | SIEM491 | 1 | 442987 | 479088 | 36101 | 1000 |  | 36101000
[7 empty] | 0 |  | Total |  | 36101000
| LALBAGH 132 KV SIDE | [5 empty] | 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | SIEM494 | 1 | 2146660 | 2172619 | 25959 | 1000 |  | 25959000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | SIEM499 | 1 | 2258635 | 2284660 | 26025 | 1000 |  | 26025000
[9 empty] | Total |  | 51984000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 89891520 |  | EXPORT TO OTHER S/S |  |  | 36101000 |  | 132 KV NET IMPORT |  | 53790520
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 53790520 |  | 132/33 KV GT LV SIDE |  | 51932000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1858520
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 3.455%
| 132 KV TOTAL IMPORT |  | 89891520
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) | 33 |  | SIEM0517 | 1 | 2146183 | 2172088 | 25905 | 1000 | 25905000
16 | 132/33 kV GT-2 Incoming (LV) | 33 |  | SIEM0518 | 1 | 2232627 | 2258654 | 26027 | 1000 | 26027000
[7 empty] | 0 |  | Total | 51932000 |  | 0
| LALBAGH 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SIEM0502 | 1 | 825730 | 831689 | 5959 | 2000 |  | 11918000 | 12007552.0327 |  | 24514831.0168 | Lalbagh New 33/11 kv ss | 0.048472 | 33/11 kV, 20/28 MVA T-1 (HV) | 12007552.0327 | 12114093.0414 | -106541.0088 | -0.87948 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SIEM0501 | 1 | 818657 | 824864 | 6207 | 2000 |  | 12414000 | 12507278.9842 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 12507278.9842 | 13441114.0219 | -933835.0377 | -6.9476 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 24332000 | 24514831.0168 |  |  |  |  | 33 KV Feeders | 24514831.0168 | 25555207.0633 | -1040376.0465 | -4.0711 | OK
9 | Spare | 33 |  | SIEM0500 | 1 |  | 0 |  | 2000 |  | 0 | 0 |  | 9474661.7985 | Mitford 33/11 kv ss | 0.32559 | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 | 33 |  | SIEM0513 | 1 | 314345 | 316938 | 2593 | 2000 |  | 5186000 | 5224967.6826 |  |  |  |  | Mitford Circuit-1 | 5224967.6826 | 4393243.7005 | 831723.9821 | 18.9319 | OK
12 | Azimpur Circuit-1 | 33 |  | SIEM0503 | 1 | 70528 | 70528 | 0 | 2000 |  | 0 | 0 |  | 7248055.825 | Azimpur 33/11 kv ss | 1.4942 | Azimpur Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Azimpur Circuit-2 | 33 |  | SIEM0507 | 1 | 78121 | 81718 | 3597 | 2000 |  | 7194000 | 7248055.825 |  |  |  |  | Azimpur Circuit-2 | 7248055.825 | 3212999.283 | 4035056.542 | 125.5854 | FAULT
17 | Lalbagh old | 33 |  | SIEM0509 | 1 | 212298 | 217599 | 5301 | 2000 |  | 10602000 | 10681663.5887 |  | 10681663.5887 | Lalbagh old 33/11 kv ss | 0.65746 | Lalbagh old | 10681663.5887 | 10588018.9139 | 93644.6748 | 0.88444 | OK
18 | Mitford Circuit-2 | 33 |  | SIEM0511 | 1 | 355038 | 357147 | 2109 | 2000 |  | 4218000 | 4249694.1159 |  |  |  |  | Mitford Circuit-2 | 4249694.1159 | 4712935.1185 | -463241.0026 | -9.8291 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKC7982 | 1 | 7071.66 | 7177.43 | 105.77 | 120 |  | 12692.4 | 12787.7709 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-1 | 12787.7709 | 12005.9207 | 781.8502 | 6.5122 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHU02670 | 1 | 27089.5 | 27089.5 | 0 | 120 |  | 0 | 0 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 27212692.4 | 27417168.9832 |  |  |  |  | 0 | 27417168.9832 | 22919202.9367 | 4497966.0465 | 19.6253 | OK
[8 empty] | Grand Total |  | 51932000 | 51544692.4 | 51932000 | 0.7514
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK98833 | 1 | 577429.7 | 583394.6 | 5964.9 | 2000 | 11929800 |  | 12015983.8557
11 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK98832 | 1 | 573415.4 | 579620 | 6204.6 | 2000 | 12409200 |  | 12498847.1611
[7 empty] | 0 |  | Total | 24339000 |  | 24514831.0168
| LALBAGH 11 kV SIDE | [5 empty] | 0 | [7 empty] | 266
3 | Chata Mosjid | 11 |  |  | 1 | 167272.9 | 169591.28 | 2318.38 | 1000 |  | 2318380 | 2319503.7751 | Kamrangirchar |  | 177 |  | Chata Mosjid | 2319503.7751 | 2426211.3577 | -106707.5826 | -4.3981 | OK
4 | AC mosjid | 11 |  |  | 1 | 4071.8 | 5346.4008 | 1274.6008 | 1000 |  | 1274600.8 | 1275218.63 | Lalbag |  | 89 |  | AC mosjid | 1275218.63 | 1340177.0113 | -64958.3813 | -4.847 | OK
5 | Kazi Reaz Uddin Road | 11 |  |  | 1 | 16630.49 | 18853.63 | 2223.14 | 1000 |  | 2223140 | 2224217.61 | Lalbag |  | 29.6667 |  | Kazi Reaz Uddin Road | 2224217.61 | 2267338.6868 | -43121.0769 | -1.9018 | OK
6 | Nazimuddin | 11 |  |  | 1 | 4214.292 | 4214.292 | 0 | 1000 | Estimated | 0 | 0 | Lalbag | NO LOAD | 206.6667 |  | Nazimuddin | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Kamal Bagh | 11 |  |  | 1 | 117683.69 | 13296.26 | -104387.43 | 1000 | Estimated | 1589074.2 | 1589844.4629 | Lalbag | 135 |  |  | Kamal Bagh | 1589844.4629 | 1583845.5588 | 5998.9041 | 0.37876 | OK
8 | Rahamatganj | 11 |  |  | 1 | 37932 | 8699.95 | -29232.05 | 1000 | Estimated | 2471893.2 | 2473091.3867 | Lalbag | 210 |  |  | Rahamatganj | 2473091.3867 | 2558519.7488 | -85428.3621 | -3.339 | OK
9 | Water Works 11kV Sw/S-1 | 11 |  |  | 1 | 18780.18 | 20641.601 | 1861.421 | 1000 |  | 1861421 | 1862323.276 | Lalbag |  |  |  | Water Works 11kV Sw/S-1 | 1862323.276 | 1854345.8684 | 7977.4076 | 0.4302 | OK
12 | City Colony | 11 |  |  | 1 | 20434.814 | 22484.11 | 2049.296 | 1000 |  | 2049296 | 2050289.3435 | Lalbag |  |  |  | City Colony | 2050289.3435 | 2080353.5364 | -30064.1928 | -1.4451 | OK
13 | Water Works 11kV Sw/S-2 | 11 |  |  | 1 | 29754.25 | 32750 | 2995.75 | 1000 |  | 2995750 | 2997202.1128 | Lalbag |  |  |  | Water Works 11kV Sw/S-2 | 2997202.1128 | 3092062.2371 | -94860.1243 | -3.0679 | OK
14 | Chun Goli | 11 |  |  | 1 | 5535.3348 | 6376.308 | 840.9732 | 1000 |  | 840973.2 | 841380.8401 | Lalbag |  |  |  | Chun Goli | 841380.8401 | 894878.3402 | -53497.5 | -5.9782 | OK
15 | Alir Ghat | 11 |  |  | 1 | 117703.2 | 119606.4 | 1903.2 | 1000 |  | 1903200 | 1904122.5273 | Lalbag |  |  |  | Alir Ghat | 1904122.5273 | 2096766.6729 | -192644.1456 | -9.1877 | OK
16 | Club Ghat | 11 |  |  | 1 | 11435.815 | 13974.46 | 2538.645 | 1000 |  | 2538645 | 2539875.5429 | Lalbag | 230 |  |  | Club Ghat | 2539875.5429 | 2741271.1594 | -201395.6165 | -7.3468 | OK
17 | Debidas Ghat | 11 |  |  | 1 | 21794.4 | 26831.902 | 5037.502 | 1000 | Estimated | 2436580.44 | 2437761.5097 | Lalbag | 207 |  |  | Debidas Ghat | 2437761.5097 | 2619436.8857 | -181675.3759 | -6.9357 | OK
18 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 24514831.0168 | 24502953.84 | 24514831.0168 | 0.048472
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 2319503.7751
[5 empty] | Lalbag | at 33 KV level |  | 22195327.2417
[5 empty] | Total = |  |  | 24514831.0168 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAG Grid 33 KV SIDE
17 | Lalbagh old | 33 | 0 | SIEM0509 | 1 | 212298 | 217599 | 5301 | 2000 | 0 | 10602000 | 10681663.5887
[9 empty] | Total |  | 10602000 | 10681663.5887 | 0.7514
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 | 33 | 0 | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
[9 empty] | Total |  | 0 | 10681663.5887
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 10681663.5887 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALBAGH OLD 33 KV NET IMPORT |  | 10681663.5887
| KAMRANGIRCHAR 33 KV SIDE |  | 0 |  | LALBAGH OLD 33 KV NET IMPORT |  |  | 10681663.5887 |  | 33 KV TX HV SIDE |  | 10681663.5887
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 10681663.5887
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) | 11 |  | 8838010 | 1 | 74809 | 77733.6 | 2924.6 | 1000 | 2924600 |  | 4197673.96
27 | 33/11 kV T1 Incoming (LV) | 11 |  | 06604426 | 1 | 35456.08 | 35625.3 | 169.22 | 16000 | 2707520 |  | 3886099.3641
28 | 33/11 kV T2 Incoming (LV) | 11 |  |  | 1 | 600632 | 602442 | 1810 | 1000 | 1810000 |  | 2597890.2645
0
[7 empty] | 0 |  | Total | 7442120 |  | 10681663.5887
| LALBAGH OLD 11 KV SIDE | [5 empty] | 0
15 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | 11 |  | 8838019 | 1 | 72291.8 | 74886.8 | 2595 | 1000 |  | 2595000 | 2612060.995 | Lalbag |  |  |  | Sowari Ghat | 2612060.995 | 2829205.9908 | -217144.9958 | -7.6751 | OK
17 | Novo Kumar (Kara Odidoptor) | 11 |  | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 117709.2 | 118483.0867 | Lalbag | 10 |  |  | Novo Kumar (Kara Odidoptor) | 118483.0867 | 132959.886 | -14476.7993 | -10.8881 | OK
19 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1294801.2 | 1303313.9541 | Lalbag | 110 |  |  | Eidgah | 1303313.9541 | 1329598.8604 | -26284.9064 | -1.9769 | OK
23 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | 11 |  |  | 1 | 82497.9 | 87070.4 | 4572.5 | 444.44 | Estimated | 1942201.8 | 1954970.9311 | Lalbag | 165 |  |  | Modumoti | 1954970.9311 | 2054834.6025 | -99863.6714 | -4.8599 | OK
25 | Lalbagh O/H | 11 |  | 61389152 | 1 | 439667 | 440314 | 647 | 1000 | Estimated | 1059382.8 | 1066347.7806 | Lalbag | 90 |  |  | Lalbagh O/H | 1066347.7806 | 1087853.6131 | -21505.8325 | -1.9769 | OK
26 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | 11 |  | 61389109 | 1 | 399921 | 400866 | 945 | 1000 |  | 945000 | 951212.9635 | Lalbag |  |  |  | Water Works 11 kV Sw/S-2 | 951212.9635 | 980831.1601 | -29618.1966 | -3.0197 | OK
31 | Islambagh | 11 |  | 61389186 | 1 | 498372 | 499228 | 856 | 1000 |  | 856000 | 861627.8273 | Lalbag |  |  |  | Islambagh | 861627.8273 | 876487.4197 | -14859.5924 | -1.6954 | OK
32 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | 11 |  | 61389202 | 1 | 15416 | 15477 | 61 | 1000 |  | 61000 | 61401.0484 | Lalbag |  |  |  | WASA Low Lift Pump | 61401.0484 | 45712.4958 | 15688.5526 | 34.3201 | OK
34 | Shahi Mosjid | 11 |  | 06604459 | 1 | 35388.6 | 35606.2 | 217.6 | 8000 |  | 1740800 | 1752245.002 | Azimpur |  |  |  | Shahi Mosjid | 1752245.002 | 1250534.8854 | 501710.1165 | 40.1196 | FAULT
35 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer | 0.415 |  | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 |  | 0 | 0 | Lalbag |  |  |  | 33/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10681663.5887 | 10611895 | 10681663.5887 | 0.65746
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Lalbag | at 33 KV level |  | 8929418.5867
[5 empty] | Azimpur | at 33 KV level |  | 1752245.002
[5 empty] | Total = |  |  | 10681663.5887 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 | 33 | 0 | SIEM0513 | 1 | 314345 | 316938 | 2593 | 2000 | 0 | 5186000 | 5224967.6826
18 | Mitford Circuit-2 | 33 | 0 | SIEM0511 | 1 | 355038 | 357147 | 2109 | 2000 | 0 | 4218000 | 4249694.1159
[9 empty] | Total | 0 | 9404000 | 9474661.7985
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 1210.49 | 1220.69 | 10.2 | 540000 |  | 5508000
| Lalbagh Circuit-2 | 33 |  | DHK68131 | 1 | 1278.66 | 1286.43 | 7.77 | 540000 |  | 4195800
[7 empty] | 0 |  | Total |  | 9703800
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
1 | Kumartuly Circuit-1 | 33 |  | DHK-66493 | 1 | 1284426 | 1285151 | 725 | 180 |  | 130500
6 | Kumartuly Circuit-2 | 33 |  | DHK-60914 | 1 | 759468.5 | 759469.7 | 1.2 | 180 |  | 216
[7 empty] | 0 |  | Total |  | 130716
0
| MIDFORT 33 KV SIDE | [5 empty] | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-66494 | 1 | 2756388 | 2793057 | 36669 | 180 |  | 6600420
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHKA-2193 | 1 | 535.4201 | 558.559 | 23.1389 | 180000 |  | 4165002
[9 empty] | Total |  | 10765422 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 9474661.7985 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9605377.7985
| IMPORT-2 |  | 130716 |  | 33 KV NET IMPORT |  |  | 9605377.7985 |  | 33 KV TX HV SIDE |  | 10765422
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -1160044.2015
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -12.08%
| TOTAL IMPORT |  | 9605377.7985
11 KV SIDE of___MIDFORT 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK-66484 | 1 | 2688460 | 2717650 | 29190 | 180 | 5254200 |  | 5353744.9722
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK-66476 | 1 | 2018638 | 2041819 | 23181 | 180 | 4172580 |  | 4251632.8263
[7 empty] | 0 |  | Total | 9426780 |  | 9605377.7985
| MIDFORT 11 KV SIDE | [5 empty] | 0
7 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | 11 |  | DHK-60904 | 1 | 954595.7 | 963274.2 | 8678.5 | 60 |  | 520710 | 522405.3875 | Lalbag |  |  |  | Chawk Bazar | 522405.3875 | 508276.2976 | 14129.09 | 2.7798 | OK
10 | Spare | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | 11 |  | DHK-66485 | 1 | 782736 | 795411 | 12675 | 60 |  | 760500 | 762976.1234 | Bangshal |  |  |  | Chatrabas | 762976.1234 | 353557.5482 | 409418.5752 | 115.7997 | FAULT
12 | Begum Bazar | 11 |  | DHK-66481 | 1 | 3586533 | 3626756 | 40223 | 60 |  | 2413380 | 2421237.7604 | Bangshal |  |  |  | Begum Bazar | 2421237.7604 | 2357293.0663 | 63944.6941 | 2.7126 | OK
13 | SCC ROAD | 11 |  | DHK-60901 | 1 | 21576.1 | 48991.1 | 27415 | 60 |  | 1644900 | 1650255.6547 | Bangshal |  |  |  | SCC ROAD | 1650255.6547 | 1574186.7645 | 76068.8902 | 4.8323 | OK
16 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | 11 |  | DHK-61104 | 1 | 652439.3 | 668332.7 | 15893.4 | 60 |  | 953604 | 956708.8537 | Bangshal |  |  |  | Armanitola | 956708.8537 | 952602.7371 | 4106.1166 | 0.43104 | OK
18 | Mitford Hospital (RMU) | 11 |  | DHK-61101 | 1 | 374512.4 | 383048.6 | 8536.2 | 60 |  | 512172 | 513839.5885 | Bangshal |  |  |  | Mitford Hospital (RMU) | 513839.5885 | 528540.0121 | -14700.4236 | -2.7813 | OK
19 | Emamganj | 11 |  | DHK-68130 | 1 | 1435.73 | 1447.92 | 12.19 | 60000 |  | 731400 | 733781.3763 | Bangshal |  |  |  | Emamganj | 733781.3763 | 1159712.4523 | -425931.076 | -36.7273 | OK
20 | Kamal Dho Road | 11 |  | DHK-68129 | 1 | 1205.82 | 1216.26 | 10.44 | 60000 |  | 626400 | 628439.5052 | Lalbag |  |  |  | Kamal Dho Road | 628439.5052 | 594724.3345 | 33715.1707 | 5.669 | OK
21 | Spare | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | 11 |  | DHK-68127 | 1 | 1481.94 | 1505.39 | 23.45 | 60000 |  | 1407000 | 1411581.0725 | Bangshal |  |  |  | Panghat | 1411581.0725 | 1500768.6523 | -89187.5797 | -5.9428 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | U0004460 | 1 | 5513.28 | 5554.67 | 41.39 | 100 |  | 4139 | 4152.4762 | Bangshal |  |  |  | 11/0.4 kV Auxiliary Transformer | 4152.4762 | 4434.1352 | -281.6589 | -6.3521 | OK
[9 empty] | Grand Total | 9605377.7985 | 9574205 | 9605377.7985 | 0.32559
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 8454532.9058
[5 empty] | Lalbag | at 33 KV level |  | 1150844.8928
[5 empty] | Total = |  |  | 9605377.7985 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 | 33 | 0 | SIEM0503 | 1 | 70528 | 70528 | 0 | 2000 | 0 | 0 | 0
15 | Azimpur Circuit-2 | 33 | 0 | SIEM0507 | 1 | 78121 | 81718 | 3597 | 2000 | 0 | 7194000 | 7248055.825
[9 empty] | Total | 0 | 7194000 | 7248055.825
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1906.63 | 1942.41 | 35.78 | 240000 | 0 | 8587200 | 8589867.074
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1804.37 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 8587200 | 8589867.074
[9 empty] | GRAND TOTAL |  | 15781200 | 15837922.8991
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 782901 | 782901 | 0 | 180 |  | 0
| Dhanmondi Circuit-1 | 33 |  | DHK68131 | 1 | 1153680 | 1169765 | 16085 | 540 |  | 8685900
| Dhanmondi Circuit-2 | 33 |  |  | 1 | 133153 | 133153 | 0 | 540 |  | 0
| Lalbagh Circuit-2 | 33 |  | DHK68132 | 1 | 866755 | 906735 | 39980 | 180 |  | 7196400
[7 empty] | 0 |  | Total |  | 15882300 | #REF!
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  | 1 | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| AZIMPUR 33 KV SIDE | [5 empty] | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK61094 | 1 | 190365 | 238697 | 48332 | 180 |  | 8699760
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK60919 | 1 | 325834 | 365851 | 40017 | 180 |  | 7203060
[9 empty] | Total |  | 15902820 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 7248055.825 |  | EXPORT TO OTHER S/S |  |  | 0 |  | AZIMPUR 33 KV NET IMPORT |  | 15837922.8991
| DHANMONDI 33 kV SIDE |  | 8589867.074 |  | AZIMPUR 33 KV NET IMPORT |  |  | 15837922.8991 |  | 33 KV TX HV SIDE |  | 15902820
[10 empty] | LOSS UNITS=> |  | -64897.1009
[10 empty] | LOSS % IN => |  | -0.4098%
| TOTAL IMPORT |  | 15837922.8991
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) | 11 |  | DHK60909 | 1 | 193178 | 241529 | 48351 | 180 | 8703180 |  | 8651799.3254
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK60902 | 1 | 340948 | 381108 | 40160 | 180 | 7228800 |  | 7186123.5737
[7 empty] | 0 |  | Total | 15931980 |  | 15837922.8991
| AZIMPUR 11 KV SIDE | [5 empty] | 0
7 | Chadni chwok | 11 |  | DHK60916 | 1 | 386413 | 399421 | 13008 | 60 |  | 780480 | 792142.0147 | Paribag |  |  |  | Chadni chwok | 792142.0147 | 648152.1238 | 143989.8908 | 22.2154 | OK
8 | BGB | 11 |  | DHK61090 | 1 | 661190 | 665574 | 4384 | 60 |  | 263040 | 266970.3715 | Jigatola |  |  |  | BGB | 266970.3715 | 253340.1998 | 13630.1717 | 5.3802 | OK
9 | Pari Bibi Mazar | 11 |  | DHK61091 | 1 | 708482 | 745025 | 36543 | 60 |  | 2192580 | 2225341.7622 | Azimpur |  |  |  | Pari Bibi Mazar | 2225341.7622 | 2144033.6462 | 81308.116 | 3.7923 | OK
10 | Azimpur | 11 |  | DHK61086 | 1 | 264194 | 282859 | 18665 | 60 |  | 1119900 | 1136633.6642 | Azimpur |  |  |  | Azimpur | 1136633.6642 | 1104066.6214 | 32567.0428 | 2.9497 | OK
11 | Aazd | 11 |  | DHK61089 | 1 | 938971 | 960626 | 21655 | 60 |  | 1299300 | 1318714.278 | Azimpur |  |  |  | Aazd | 1318714.278 | 1257709.9294 | 61004.3485 | 4.8504 | OK
12 | Dayra Sharif | 11 |  | DHK61088 | 1 | 482306 | 498851 | 16545 | 60 |  | 992700 | 1007533.0284 | Azimpur |  |  |  | Dayra Sharif | 1007533.0284 | 980271.2172 | 27261.8112 | 2.781 | OK
13 | Naya palton | 11 |  | DHK86065 | 1 | 1842.39 | 1871.03 | 28.64 | 60000 |  | 1718400 | 1744076.5145 | Azimpur |  |  |  | Naya palton | 1744076.5145 | 1689342.4234 | 54734.0911 | 3.24 | OK
16 | Viqarunnisa Noon School | 11 |  | DHK66477 | 1 | 1560667 | 1584644 | 23977 | 60 |  | 1438620 | 1460116.0121 | Azimpur |  |  |  | Viqarunnisa Noon School | 1460116.0121 | 1388906.1459 | 71209.8663 | 5.127 | OK
17 | Subal Das Lane | 11 |  | DHK66480 | 1 | 3964091 | 3981086 | 16995 | 60 |  | 1019700 | 1034936.4652 | Azimpur |  |  |  | Subal Das Lane | 1034936.4652 | 1287496.6695 | -252560.2043 | -19.6164 | OK
18 | Lalbagh | 11 |  | DHK61093 | 1 | 646194 | 685659 | 39465 | 60 |  | 2367900 | 2403281.4122 | Azimpur |  |  |  | Lalbagh | 2403281.4122 | 2365446.3751 | 37835.037 | 1.5995 | OK
19 | Zahrul Haque Hall | 11 |  | DHK66497 | 1 | 1217962 | 1228090 | 10128 | 60 |  | 607680 | 616760.0188 | Ramna |  |  |  | Zahrul Haque Hall | 616760.0188 | 675859.2968 | -59099.278 | -8.7443 | OK
20 | Eden College | 11 |  | DHK60917 | 1 | 918378 | 925859 | 7481 | 60 |  | 448860 | 455566.9136 | Azimpur |  |  |  | Eden College | 455566.9136 | 455119.369 | 447.5446 | 0.098336 | OK
21 | Nilkhet/ PWD-01 | 11 |  | DHK60918 | 1 | 456044 | 466773 | 10729 | 60 |  | 643740 | 653358.8311 | Azimpur |  |  |  | Nilkhet/ PWD-01 | 653358.8311 | 648152.1238 | 5206.7073 | 0.80332 | OK
22 | BUET | 11 |  | DHK66496 | 1 | 937828 | 949620 | 11792 | 60 |  | 707520 | 718091.8386 | Ramna |  |  |  | BUET | 718091.8386 | 902348.6159 | -184256.7773 | -20.4197 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIG2780 | 1 | 381002 | 385337 | 4335 | 1 |  | 4335 | 4399.774 | Azimpur |  |  |  | 11/0.4 kV Auxiliary Transformer | 4399.774 | 2203.9333 | 2195.8407 | 99.6328 | FAULT
[9 empty] | Grand Total | 15837922.8991 | 15604755 | 15837922.8991 | 1.4942
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 792142.0147
[5 empty] | Jigatola | at 33 KV level |  | 266970.3715
[5 empty] | Azimpur | at 33 KV level |  | 13443958.6555
[5 empty] | Ramna | at 33 KV level |  | 1334851.8575
[5 empty] | Total = |  |  | 15837922.8991 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar | 132 |  | 38992596 | 1 | 816.161 | 851.661 | 35.5 | 1440000 | 0 | 51120000
|  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 51120000
[9 empty] | Net Total | 51120000
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj | 132 | RECEIVE |  | 1 | 5585.08 | 5638.47 | 53.39 | 960000 | 51254400
|  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh | 132 |  |  | 1 | 2970.27 | 3007.85 | 37.58 | 960000 | 36076800
|  | 132 |  |  | 1 | 7.78 | 7.78 | 0 | 960000 |  | 0
[7 empty] | 0 | Total Import/Export |  | 87331200 | 0
[7 empty] | 0 | Net Total |  | 87331200
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
5 | 132 kV Jigatola-1 | 132 |  | 42003953362 | 1 | 172.77 | 190.71 | 17.94 | 1440000 |  | 25833600
6 | 132 kV Jigatola-2 | 132 |  | 42003953364 | 1 | 169.18 | 186.66 | 17.48 | 1440000 |  | 25171200
[7 empty] | 0 |  | Total |  | 51004800
| KAMRANGIRCHAR 132 KV SIDE | [5 empty] | 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | 30799138 | 1 | 3359.89 | 3372.07 | 12.18 | 960000 |  | 11692800
2 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | 30799148 | 1 | 3337.49 | 3349.64 | 12.15 | 960000 |  | 11664000
7 | 132/33 kV, 50/75 MVA GT-3 (HV) | 132 |  | BD001910 | 1 | 1136.12 | 1149.12 | 13 | 960000 |  | 12480000
[9 empty] | Total |  | 35836800 | 86841600
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 51120000 |  | EXPORT TO OTHER S/S |  |  | 51004800 |  | 132 KV NET IMPORT |  | 36192000
| FROM LALBAGH 132/33 KV GRID |  | 36076800 |  | 132 KV NET IMPORT |  |  | 36192000 |  | 33 KV NET IMPORT |  | 35851200
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 340800
[10 empty] | LOSS % IN => |  | 0.9416%
| 132 KV TOTAL IMPORT |  | 87196800
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming | 33 |  | BD001914 | 1 | 2286.99 | 2312.97 | 25.98 | 480000 | 12470400 |  | 12588943.0981
14 | 132/33 kV GT-1 Incoming (LV) | 33 |  | 30799094 | 1 | 6819.07 | 6843.58 | 24.51 | 480000 | 11764800 |  | 11876635.6942
19 | 132/33 kV GT-2 Incoming | 33 |  | 30799150 | 1 | 6720.51 | 6744.71 | 24.2 | 480000 | 11616000 |  | 11726421.2077
[7 empty] | 0 |  | Total | 35851200 |  | 36192000
| KAMRANGIRCHAR 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) | 33 |  | 30799129 | 1 | 6770.39 | 6805.63 | 35.24 | 240000 |  | 8457600 | 8516522.3851 |  | 25931408.9648 | Kamrangir Char 33/11 kv ss | 1.54 | 33/11 kV, 20/28 MVA T31 (HV) | 8516522.3851 | 8414359.77 | 102162.6151 | 1.2141 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) | 33 |  | 30799110 | 1 | 6668.04 | 6702.87 | 34.83 | 240000 |  | 8359200 | 8417436.8522 |  |  |  |  | 33/11 kV, 20/28 MVA T32 (HV) | 8417436.8522 | 8327414.6059 | 90022.2464 | 1.081 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) | 33 |  | 30799137 | 1 | 3806.33 | 3843.56 | 37.23 | 240000 |  | 8935200 | 8997449.7275 |  |  |  |  | 33/11 kV, 20/28 MVA T-33 (HV) | 8997449.7275 | 9179960.2427 | -182510.5152 | -1.9881 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 25752000 | 25931408.9648 |  |  |  |  | 33 KV Feeders | 25931408.9648 | 25921734.6186 | 9674.3462 | 0.037321 | OK
8 | Dhaka Uddyan 2 | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | 0.41675 | Dhaka Uddyan 2 | 0 | 741449.0383 | -741449.0383 | -100 | CHECK
9 | Dhaka Uddyan 1 | 33 |  | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Dhaka Uddyan 1 | 0 | 782506.4769 | -782506.4769 | -100 | CHECK
10 | Spare Feeder -2 | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 | 33 |  | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 |  | 0 | 0 |  | 6464726.8389 | Kamrangir Char-2 33/11 kv ss | 0.77279 | Lalbagh Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Zigatola Circuit-1 (BGB-1) | 33 |  | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 | 33 |  | 30799147 | 1 | 1464.97 | 1491.72 | 26.75 | 240000 |  | 6420000 | 6464726.8389 |  | 3455064.1963 | BGB 33/11 kv ss | 0.9905 | Kamrangir Char-2 | 6464726.8389 | 6685117.0618 | -220390.2229 | -3.2967 | OK
22 | Zigatola Circuit-2 (BGB-2) | 33 |  | 30799131 | 1.35 | 1854.46 | 1865.05 | 10.59 | 240000 |  | 3431160 | 3455064.1963 |  |  |  |  | Zigatola Circuit-2 (BGB-2) | 3455064.1963 | 3573446.2444 | -118382.0481 | -3.3128 | OK
[9 empty] | Total |  | 9851160 | 9919791.0352 |  |  |  |  | 0 | 9919791.0352 | 11782518.8214 | -1862727.7862 | -15.8092 | OK
[8 empty] | Grand Total |  | 35851200 | 35603160 | 35851200 | 0.69668
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 8388000 |  | 8508027.5275
11 | 33/11 kV T-32 Incoming | 11 |  | 6604433 | 1 | 7481.25 | 7527.85 | 46.6 | 180000 | 8388000 |  | 8508027.5275
22 | 33/11 kV T-33 Incoming | 11 |  | DHK 95817 | 1 | 4456105 | 4504936 | 48831 | 180 | 8789580 |  | 8915353.9098
[7 empty] | 0 |  | Total | 25565580 |  | 25931408.9648
| KAMRANGIRCHAR 11 kV SIDE | [5 empty] | 0 | [7 empty] | 220
4 | Rasulpur | 11 |  | HA-021101042-02 | 1 | 89078209 | 90531613 | 1453404 | 1 |  | 1453404 | 1475786.882 | Kamrangirchar |  |  |  | Rasulpur | 1475786.882 | 1248201.2259 | 227585.6561 | 18.2331 | OK
5 | Bheribadh | 11 |  | HA-021101105-02 | 1 | 59737086 | 62150594 | 2413508 | 1 |  | 2413508 | 2450676.7878 | Kamrangirchar |  |  |  | Bheribadh | 2450676.7878 | 2398606.8547 | 52069.9331 | 2.1708 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | 11 |  | 30799521 | 1 | 2623.32 | 2629.31 | 5.99 | 60000 |  | 359400 | 364934.8739 | Kamrangirchar |  |  |  | Panna Tower 11 KV Faridpur Tower Express | 364934.8739 | 488122.7019 | -123187.828 | -25.2371 | OK
8 | Panna Battery Express | 11 |  | DHK15431 | 1 | 5243.73 | 5261.14 | 17.41 | 60000 |  | 1044600 | 1060687.1709 | Kamrangirchar |  |  |  | Panna Battery Express | 1060687.1709 | 1118589.0702 | -57901.8993 | -5.1763 | OK
9 | Eidgah | 11 |  | 30799460 | 1 | 5297.07 | 5334.36 | 37.29 | 60000 |  | 2237400 | 2271856.6688 | Kamrangirchar |  |  |  | Eidgah | 2271856.6688 | 2848456.9491 | -576600.2803 | -20.2425 | OK
10 | Bot Tola Mazar | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | 11 |  | HA-021101055-02 | 1 | 97687286 | 99557723 | 1870437 | 1 |  | 1870437 | 1899242.3224 | Kamrangirchar |  |  |  | Huzur Para | 1899242.3224 | 1901795.8946 | -2553.5723 | -0.13427 | OK
13 | Kamrangirchar | 11 |  | HA-021101015-02 | 1 | 17588896 | 19388783 | 1799887 | 1 |  | 1799887 | 1827605.83 | Kamrangirchar |  |  |  | Kamrangirchar | 1827605.83 | 1737567.1439 | 90038.6861 | 5.1819 | OK
14 | Munshihati | 11 |  | HA-021100854-02 | 1 | 48912982 | 50206769 | 1293787 | 1 |  | 1293787 | 1313711.7297 | Kamrangirchar |  |  |  | Munshihati | 1313711.7297 | 1205376.9608 | 108334.7689 | 8.9876 | OK
15 | Jhawchar | 11 |  | HA-021101028-02 | 1 | 97420106 | 98824125 | 1404019 | 1 |  | 1404019 | 1425641.3374 | Kamrangirchar |  |  |  | Jhawchar | 1425641.3374 | 1328999.0751 | 96642.2623 | 7.2718 | OK
16 | RMU Express | 11 |  | HA-021101248-02 | 1 | 4693909 | 5318135 | 624226 | 1 |  | 624226 | 633839.2782 | Kamrangirchar |  |  |  | RMU Express | 633839.2782 | 704501.3661 | -70662.0879 | -10.0301 | OK
17 | Koyla Ghat | 11 |  | HA-021101259-02 | 1 | 14045899 | 15254118 | 1208219 | 1 | ESTIMATED | 2189391.12 | 2223108.4368 | Kamrangirchar | 180 |  |  | Koyla Ghat | 2223108.4368 | 1816011.9444 | 407096.4925 | 22.4171 | OK
18 | Muslimbagh | 11 |  | HA-021100908-02 | 1 | 22904364 | 24575572 | 1671208 | 1 |  | 1671208 | 1696945.1326 | Kamrangirchar |  |  |  | Muslimbagh | 1696945.1326 | 1737474.4882 | -40529.3556 | -2.3327 | OK
19 | Noyagaon | 11 |  | HA-021101087-02 | 1 | 516458 | 3217494 | 2701036 | 1 |  | 2701036 | 2742632.8101 | Kamrangirchar |  |  |  | Noyagaon | 2742632.8101 | 2660587.4202 | 82045.3899 | 3.0837 | OK
20 | Nurbagh | 11 |  | HA-021100982-02 | 1 | 19118491 | 21245035 | 2126544 | 1 |  | 2126544 | 2159293.4513 | Kamrangirchar |  |  |  | Nurbagh | 2159293.4513 | 2300317.433 | -141023.9817 | -6.1306 | OK
21 | Ali Nagar | 11 |  | HA-021101022-02 | 1 | 17434438 | 19758728 | 2324290 | 1 |  | 2324290 | 2360084.8023 | Kamrangirchar |  |  |  | Ali Nagar | 2360084.8023 | 2402380.2856 | -42295.4832 | -1.7606 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKE6223 | 1 | 42637.18 | 42845.32 | 208.14 | 120 |  | 24976.8 | 25361.4506 | Kamrangirchar |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 25361.4506 | 24745.805 | 615.6457 | 2.4879 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 | Kamrangirchar |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 25931408.9648 | 25538113.92 | 25931408.9648 | 1.54
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 25931408.9648
[5 empty] | Jigatola | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 25931408.9648 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1854.46 | 1865.05 | 10.59 | 240000 | 0 | 3431160 | 3455064.1963
[9 empty] | TOTAL |  | 3431160 | 3455064.1963
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old | 33 | 0 | 43998033 | 1 | 119.18 | 151.9 | 32.72 | 270000 |  | 1500000 | 1494155.0851
[9 empty] | TOTAL |  | 1500000 | 1500000
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 | 33 | 0 | 0 | 1 | 36.64 | 55.2 | 18.56 | 360000 | 0 | 6681600 | 6676399.5755
11 | BGB-2 | 33 | 0 | 0 | 1 | 220.47 | 231.07 | 10.6 | 360000 | 0 | 3816000 | 3813029.93
[9 empty] | Total | 0 | 10497600 | 10489429.5054
[9 empty] | GRAND TOTAL |  | 15428760 | 15444493.7017
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 | 33 |  | 43998032 | 1 | 1043.59 | 1043.59 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old | 33 |  | 43998033 | 1 | 119.18 | 151.9 | 32.72 | 270000 | 8834400
| 33 kV Zigatola-1 | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 | 33 |  | 43998027 | 1 | 741.9 | 755.48 | 13.58 | 270000 | 3666600
| 33 kV Zigatola-2 | 33 |  | 43998031 | 1 | 293.2 | 307.36 | 14.16 | 270000 | 3823200
[9 empty] | Total | 16324200 | 0 | 0
BGB 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[9 empty] | Total |  | 0
BGB 33 KV SIDE
6 | 33/11 kV T1 | 33 |  | 43998028 | 1 | 694.308 | 727.04 | 32.732 | 270000 |  | 8837640
9 | 33/11 kV T2 | 33 |  | 43998029 | 1 | 701.99 | 729.69 | 27.7 | 270000 |  | 7479000
11 | 33/11 kV T3 | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
[9 empty] | Total |  | 16316640
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 15444493.7017 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BGB 33 KV NET IMPORT |  | 15444493.7017
[5 empty] | BGB 33 KV NET IMPORT |  |  | 15444493.7017 |  | 33 KV TX HV SIDE |  | 16316640
[10 empty] | LOSS UNITS=> |  | -872146.2983
[10 empty] | LOSS % IN => |  | -5.647%
| TOTAL IMPORT |  | 15444493.7017
11 KV SIDE of___BGB 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming | 11 |  |  | 1 | 86023405 | 94784488 | 8761083 | 1 | 8761083 |  | 8841136.6885
29 | 33/11 kV T-2 Incoming | 11 |  |  | 1 | 87853081 | 95260896 | 7407815 | 1 | 7407815 |  | 7475503.3115
30 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
[7 empty] | 0 |  | Total | 16168898 |  | 16316640
| BGB 11 KV SIDE | [5 empty] | 0
12 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | 11 |  |  | 1 | 6757988 | 8188769 | 1430781 | 1 |  | 1430781 | 1444952.9565 | Azimpur |  |  |  | Nababgonj Park | 1444952.9565 | 1573011.5868 | -128058.6303 | -8.141 | OK
16 | Kholamura Ghat | 11 |  |  | 1 | 72049102 | 74784480 | 2735378 | 1 |  | 2735378 | 2762472.0542 | Kamrangirchar |  |  |  | Kholamura Ghat | 2762472.0542 | 2841690.4191 | -79218.365 | -2.7877 | OK
17 | Khalpar | 11 |  |  | 1 | 81615032 | 82977184 | 1362152 | 1 |  | 1362152 | 1375644.1828 | Kamrangirchar |  |  |  | Khalpar | 1375644.1828 | 1437529.7992 | -61885.6163 | -4.305 | OK
18 | Shahidnagar | 11 |  |  | 1 | 12336427 | 14195510 | 1859083 | 1 |  | 1859083 | 1877497.3089 | Azimpur |  |  |  | Shahidnagar | 1877497.3089 | 1808709.9159 | 68787.393 | 3.8031 | OK
19 | BGB 1 No Gate | 11 |  |  | 1 | 29847534 | 31209790 | 1362256 | 1 |  | 1362256 | 1375749.2129 | Azimpur |  |  |  | BGB 1 No Gate | 1375749.2129 | 1318685.5995 | 57063.6135 | 4.3273 | OK
21 | Ganaktuli | 11 |  |  | 1 | 21869943 | 22588480 | 718537 | 1 |  | 718537 | 725654.1445 | Jigatola |  |  |  | Ganaktuli | 725654.1445 | 693078.4919 | 32575.6526 | 4.7001 | OK
22 | Thana | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | 11 |  |  | 1 | 28102896 | 30156751 | 2053855 | 1 |  | 2053855 | 2074198.5352 | Jigatola |  |  |  | Bot Tola Mazar | 2074198.5352 | 1909183.4664 | 165015.0688 | 8.6432 | OK
24 | Sikder Medical | 11 |  |  | 1 | 33392224 | 34515480 | 1123256 | 1 |  | 1123256 | 1134381.9061 | Jigatola |  |  |  | Sikder Medical | 1134381.9061 | 1138392.2283 | -4010.3222 | -0.35228 | OK
25 | Gas Field | 11 |  |  | 1 | 49867262 | 51908120 | 2040858 | 1 |  | 2040858 | 2061072.7993 | Kamrangirchar |  |  |  | Gas Field | 2061072.7993 | 1985612.1672 | 75460.6321 | 3.8004 | OK
26 | Hazaribagh | 11 |  |  | 1 | 36947488 | 38417940 | 1470452 | 1 |  | 1470452 | 1485016.8997 | Jigatola |  |  |  | Hazaribagh | 1485016.8997 | 1465699.7946 | 19317.105 | 1.3179 | OK
27 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 |  |  | 1 | 1998.58 | 2056.85 | 58.27 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 |  |  | 1 | 1590.01 | 1644.21 | 54.2 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 16316640 | 16156608 | 16316640 | 0.9905
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Azimpur | at 33 KV level |  | 4698199.4783
[5 empty] | Kamrangirchar | at 33 KV level |  | 6199189.0362
[5 empty] | Jigatola | at 33 KV level |  | 5419251.4855
[5 empty] | Total = |  |  | 16316640 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 | 132 | 0 | 42003953362 | 1 | 172.77 | 190.71 | 17.94 | 1440000 | 0 | 25833600 | 0
6 | 132 kV Jigatola-2 | 132 | 0 |  | 1 | 169.18 | 186.66 | 17.48 | 1440000 | 0 | 25171200 | 0
[8 empty] | Total Import/Export |  | 0 | 51004800
[9 empty] | Net Total | 51004800
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 | 132 | RECEIVE | 6604452 | 1 | 207.24 | 228.78 | 21.54 | 1200000 | 25848000
| 132 kV Kamrangirchar 2 | 132 |  |  | 1 | 202.78 | 223.76 | 20.98 | 1200000 | 25176000
[7 empty] | 0 | Total Import/Export |  | 51024000 | 0
[7 empty] | 0 | Net Total |  | 51024000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| JIGATOLA 132 KV SIDE | [5 empty] | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  |  | 1 | 163.21 | 179.19 | 15.98 | 1200000 |  | 19176000
3 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  |  | 1 | 246.97 | 273.54 | 26.57 | 1200000 |  | 31884000
[9 empty] | Total |  | 51060000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 51004800 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 51004800
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 51004800 |  | 33 KV NET IMPORT |  | 50839200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 165600
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3247%
| 132 KV TOTAL IMPORT |  | 51004800
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  |  | 1 | 270.5 | 296.99 | 26.49 | 720000 | 19072800
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  |  | 1 | 409.76 | 453.88 | 44.12 | 720000 | 31766400
[7 empty] | 0 |  | Total | 50839200 |  | 0
| JIGATOLA 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  |  | 1 | 493.08 | 518.72 | 25.64 | 240000 |  | 6153600 | 6148810.5286 |  | 19352925.4935 | JIGATOLA NEW 3/11 KV SS | 0.14554 | 33/11 kV 28/35 MVA T-1 | 6148810.5286 | 6563664.1126 | -414853.584 | -6.3205 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  |  | 1 | 345.81 | 379.18 | 33.37 | 240000 |  | 8008800 | 8002566.5888 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 8002566.5888 | 7897020.7975 | 105545.7913 | 1.3365 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  |  | 1 | 301.57 | 323.26 | 21.69 | 240000 |  | 5205600 | 5201548.3761 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 5201548.3761 | 5407768.5692 | -206220.1931 | -3.8134 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 19368000 | 19352925.4935 |  |  |  |  | 33 KV Feeders | 19352925.4935 | 19868453.4793 | -515527.9858 | -2.5947 | OK
2 | BGB-1 | 33 |  |  | 1 | 36.64 | 55.2 | 18.56 | 360000 |  | 6681600 | 6676399.5755 |  | 10489429.5054 | BGB 33/11 kv ss | 0.9905 | BGB-1 | 6676399.5755 | 0 | 6676399.5755 | #DIV/0! | #DIV/0!
2 | Spair | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 | 33 |  |  | 1 | 153.69 | 171.09 | 17.4 | 360000 |  | 6264000 | 6259124.602 |  |  |  |  | Dhaka Uddyan-1 | 6259124.602 | 6313060.2033 | -53935.6013 | -0.85435 | OK
4 | Green Road -1 | 33 |  |  | 1 | 23.2 | 23.2 | 0 | 360000 |  | 0 | 0 |  | 14014683.5916 | Dhaka Uddan 33/11 kv ss | 0.41675 | Green Road -1 | 0 | 2000035.0274 | -2000035.0274 | -100 | CHECK
9 | Green Road -2 | 33 |  |  | 1 | 9.84 | 23.22 | 13.38 | 360000 |  | 4816800 | 4813050.9871 |  |  |  |  | Green Road -2 | 4813050.9871 | 3532435.9656 | 1280615.0215 | 36.253 | OK
10 | Dhaka Uddyan-2 | 33 |  |  | 1 | 153.28 | 174.84 | 21.56 | 360000 |  | 7761600 | 7755558.9896 |  |  |  |  | Dhaka Uddyan-2 | 7755558.9896 | 6510905.3948 | 1244653.5948 | 19.1164 | OK
11 | BGB-2 | 33 |  |  | 1 | 220.47 | 231.07 | 10.6 | 360000 |  | 3816000 | 3813029.93 |  | 2169110.4224 | Jigatla Old 33/11 kv ss | 1.3735 | BGB-2 | 3813029.93 | 3518047.2244 | 294982.7056 | 8.3848 | OK
12 | Jigatola Old | 33 |  |  | 1 | 4.23 | 10.26 | 6.03 | 360000 |  | 2170800 | 2169110.4224 |  |  |  |  | Jigatola Old | 2169110.4224 | 1197862.7052 | 971247.7172 | 81.0817 | FAULT
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 31510800 | 31486274.5065 |  |  |  |  | 0 | 31486274.5065 | 23072346.5207 | 8413927.9858 | 36.4676 | OK
[8 empty] | Grand Total |  | 50839200 | 50878800 | 50839200 | -0.077832
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 67.61 | 92.16 | 24.55 | 250000 | 6137500 |  | 6143984.4933
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 73.52 | 105.52 | 32 | 250000 | 8000000 |  | 8008452.2927
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 56.84 | 77.62 | 20.78 | 250000 | 5195000 |  | 5200488.7076
[7 empty] | 0 |  | Total | 19332500 |  | 19352925.4935
| JIGATOLA 11 kV SIDE | [5 empty] | 0
| Salek Garden | 11 |  | 2761 | 1 | 506.46 | 549.1 | 42.64 | 60000 |  | 2558400 | 2562123.5191 | Jigatola |  |  |  | Salek Garden | 2562123.5191 | 2460950.9042 | 101172.6149 | 4.1111 | OK
4 | Jigatola Local | 11 |  | 2850 | 1 | 408.27 | 438.35 | 30.08 | 60000 |  | 1804800 | 1807426.7227 | Jigatola |  |  |  | Jigatola Local | 1807426.7227 | 1737565.9216 | 69860.8011 | 4.0206 | OK
5 | Modina Rayer Bazar | 11 |  | 2851 | 1 | 603.31 | 603.31 | 0 | 60000 |  | 0 | 0 | Switching |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | City College | 11 |  | 2784 | 1 | 450.2 | 479.78 | 29.58 | 60000 |  | 1774800 | 1777383.0604 | Jigatola |  |  |  | City College | 1777383.0604 | 2346194.6487 | -568811.5882 | -24.244 | OK
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office | 11 |  | 2836 | 1 | 330.76 | 358.58 | 27.82 | 60000 |  | 1669200 | 1671629.3692 | Jigatola |  |  |  | Post Office | 1671629.3692 | 1589764.671 | 81864.6982 | 5.1495 | OK
11 | Leather Institute | 11 |  | 2835 | 1 | 54.22 | 57.38 | 3.16 | 60000 |  | 189600 | 189875.9456 | Jigatola |  |  |  | Leather Institute | 189875.9456 | 195265.8799 | -5389.9342 | -2.7603 | OK
12 | Mina Bazar | 11 |  | 2853 | 1 | 169.47 | 181.89 | 12.42 | 60000 |  | 745200 | 746284.571 | Jigatola |  |  |  | Mina Bazar | 746284.571 | 706562.076 | 39722.495 | 5.6219 | OK
13 | Mitali | 11 |  | 2852 | 1 | 278.85 | 330.42 | 51.57 | 60000 |  | 3094200 | 3098703.3274 | Jigatola |  |  |  | Mitali | 3098703.3274 | 2956625.83 | 142077.4975 | 4.8054 | OK
14 | Road-2 | 11 |  | 2839 | 1 | 546.35 | 584.66 | 38.31 | 60000 |  | 2298600 | 2301945.4038 | Jigatola |  |  |  | Road-2 | 2301945.4038 | 2450136.1786 | -148190.7747 | -6.0483 | OK
15 | SS-2 | 11 |  | 2838 | 1 | 253.56 | 272.32 | 18.76 | 60000 |  | 1125600 | 1127238.2087 | Jigatola |  |  |  | SS-2 | 1127238.2087 | 1112715.1061 | 14523.1026 | 1.3052 | OK
16 | Spare | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar | 11 |  | 2843 | 1 | 440.65 | 471.44 | 30.79 | 60000 |  | 1847400 | 1850088.7231 | Jigatola |  |  |  | Bou Bazar | 1850088.7231 | 1774816.6433 | 75272.0798 | 4.2411 | OK
18 | BGB | 11 |  | 2764 | 1 | 152.88 | 169.64 | 16.76 | 60000 |  | 1005600 | 1007063.5596 | Jigatola |  |  |  | BGB | 1007063.5596 | 934872.9509 | 72190.6087 | 7.722 | OK
19 | Dhamondi-12 | 11 |  | 2763 | 1 | 354.88 | 375.07 | 20.19 | 60000 |  | 1211400 | 1213163.0828 | Dhanmondi |  |  |  | Dhamondi-12 | 1213163.0828 | 1602982.669 | -389819.5862 | -24.3184 | OK
[9 empty] | Total | 19352925.4935 | 19324800 | 19352925.4935 | 0.14554
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Jigatola | at 33 KV level |  | 18139762.4107 | Including Switching
[5 empty] | Dhanmondi | at 33 KV level |  | 1213163.0828
[5 empty] | Total = |  |  | 19352925.4935 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [13 empty] | Month June-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
No. | Name of Feeders. |  | CF | Number |  | 2023-04-01 | 2023-04-01 |  |  | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar | 11 | 0 | 2851 | 1 | 603.31 | 603.31 | 0 | 60000 | 0 | 0 | 0
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated From source End | 0 | 0 | Dhanmondi
3 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 2184 | 200 | Estimated From source End | 0 | 0 | Jigatola
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1854.46 | 1865.05 | 10.59 | 240000 | 0 | 3431160 | 3455064.1963
[9 empty] | Total |  | 3431160 | 3455064.1963
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit | 33 | 0 | 214393/37-2711 | 1 | 7975.877 | 10131.445 | 2155.568 | 1000 | Estimated | 1487700 | 1481903.0134
[9 empty] | Total |  | 1487700 | 1481903.0134
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 | NET IMPORT | DHK61073 | 1 | 3996.93 | 4005.95 | 9.02 | 240000 |  | 2164800
2 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
[9 empty] | Total |  | 2164800 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 1481903.0134
| Satmasjid 33 KV SIDE |  | 1481903.0134 |  | 33 KV NET IMPORT |  |  | 1481903.0134 |  | ZIGATOLA OLD 11 KV NET IMPORT |  | 2164800
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -682896.9866
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -46.08%
| TOTAL IMPORT |  | 1481903.0134
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0 |  | 0
16 | 33/11 kV T-2 Incoming | 11 |  | DHK61029 | 1.25 | 4793.85 | 4794.86 | 1.01 | 180000 | 227250 |  | 149093.7207
17 | 33/11 kV T-1 Incoming | 11 |  | DHK61028 | 1.32 | 1830.29 | 1838.84 | 8.55 | 180000 | 2031480 |  | 1332809.2927
[7 empty] | 0 |  | Total | 2258730 |  | 1481903.0134
| ZIGATOLA OLD 11 KV SIDE | [5 empty] | 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Lalmatia SW |  |  |  | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | 11 |  | DHK60946 | 1 | 1111.52 | 1125.53 | 14.01 | 60000 |  | 840600 | 852145.3731 | Jigatola |  |  |  | Simanto Square | 852145.3731 | 901151.3428 | -49005.9696 | -5.4382 | OK
12 | Post Office | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | 11 |  | DHK61070 | 1 | 3394.83 | 3415.05 | 20.22 | 60000 |  | 1213200 | 1229862.9154 | Jigatola |  |  |  | Green Road Via Park | 1229862.9154 | 476757.7712 | 753105.1442 | 157.9639 | FAULT
15 | PWD Quarters 11 kV Saleq Grand | 11 |  | DHK61028 | 1 | 3628.17 | 3629.4 | 1.23 | 60000 |  | 73800 | 74813.6195 | Jigatola |  |  |  | PWD Quarters 11 kV Saleq Grand | 74813.6195 | 63933.0345 | 10880.585 | 17.0187 | OK
18 | Road No.-2 | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 |  | 243284 | 1 | 83536 | 83791 | 255 | 10 |  | 2550 | 2585.0234 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 2585.0234 | 3440.2061 | -855.1827 | -24.8585 | OK
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 |  | 412277 | 1 | 38966 | 39498 | 532 | 10 |  | 5320 | 5393.0685 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 5393.0685 | 0 | 5393.0685 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 2164800 | 2135470 | 2164800 | 1.3735
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Jigatola | at 33 KV level |  | 2164800
[5 empty] | Total = |  |  | 2164800 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) | 33 | 0 | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 | 33 | 0 | 0 | 1 | 153.69 | 171.09 | 17.4 | 360000 | 0 | 6264000 | 6259124.602
10 | Dhaka Uddyan-2 | 33 | 0 | 0 | 1 | 153.28 | 174.84 | 21.56 | 360000 | 0 | 7761600 | 7755558.9896
[9 empty] | Total | 0 | 14025600 | 14014683.5916
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | RECEIVE | BD017107 | 1 | 90469.03 | 90469.03 | 0 | 1125 |  | 0
| 33 kV Jigatala Incoming Circuit-1 | 33 |  | BD017098 | 1 | 48947.36 | 54665.75 | 5718.39 | 1125 |  | 6433188.75
| 33 kV Jigatala Incoming Circuit-2 | 33 |  | BD017097 | 1 | 48882.9 | 56008.57 | 7125.67 | 1125 |  | 8016378.75
| 33 kV Kamrangirchar Circuit-2 (O/H) | 33 |  | BD017108 | 1 | 73739.05 | 73739.05 | 0 | 1125 |  | 0
[7 empty] | 0 |  | Total |  | 14449567.5 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| DHAKA UDDYAN 33 KV SIDE | [5 empty] | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017100 | 1 | 57497.06 | 63967.95 | 6470.89 | 1000 |  | 6470890
3 | 33/11 kV, 28/35 MVA T-3 (Future) | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017109 | 1 | 38362.57 | 46404.61 | 8042.04 | 1000 |  | 8042040
[9 empty] | Total |  | 14512930 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 14014683.5916
| JIGATOLA 33 KV SIDE |  | 14014683.5916 |  | 33 KV NET IMPORT |  |  | 14014683.5916 |  | 33 KV TX HV |  | 14512930
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -498246.4084
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -3.555%
| TOTAL IMPORT |  | 14014683.5916
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD014060 | 1 | 56544.83 | 62776.85 | 6232.02 | 1000 | 6232020 |  | 6256127.0967
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD014061 | 1 | 37780.41 | 45509.07 | 7728.66 | 1000 | 7728660 |  | 7758556.4949
[7 empty] | 0 |  | Total | 13960680 |  | 14014683.5916
| DHAKA UDDYAN 11 KV SIDE | [5 empty] | 0
7 | Spare | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | 11 |  | BD014031 | 1 | 48238.67 | 48613.5 | 374.83 | 1000 |  | 374830 | 376392.0985 | Adabor |  |  |  | D Block dhaka uddyan | 376392.0985 | 356370.9019 | 20021.1966 | 5.6181 | OK
8 | Dill Mohammad O/H | 11 |  | BD014027 | 1 | 13971.54 | 15908.7 | 1937.16 | 1000 |  | 1937160 | 1945233.0858 | Adabor |  |  |  | Dill Mohammad O/H | 1945233.0858 | 1925614.3584 | 19618.7274 | 1.0188 | OK
9 | Turag O/H | 11 |  | BD014028 | 1 | 24750.51 | 25472.56 | 722.05 | 1000 |  | 722050 | 725059.1327 | Adabor |  |  |  | Turag O/H | 725059.1327 | 419185.0275 | 305874.1053 | 72.9688 | FAULT
10 | Nabadoy O/H | 11 |  | BD014025 | 1 | 34037.39 | 34907.65 | 870.26 | 1000 |  | 870260 | 873886.7957 | Adabor |  |  |  | Nabadoy O/H | 873886.7957 | 1264712.0241 | -390825.2284 | -30.9023 | OK
11 | Chandrima O/H | 11 |  | BD014024 | 1 | 2884.39 | 3855 | 970.61 | 1000 |  | 970610 | 974655.0029 | Adabor |  |  |  | Chandrima O/H | 974655.0029 | 879754.0777 | 94900.9252 | 10.7872 | OK
12 | Shyamoli Housing Project-2 | 11 |  | BD014029 | 1 | 23461.67 | 24761.38 | 1299.71 | 1000 |  | 1299710 | 1305126.5223 | Adabor |  |  |  | Shyamoli Housing Project-2 | 1305126.5223 | 2226602.9518 | -921476.4296 | -41.3849 | CHECK
13 | Spare | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | 11 |  | BD013959 | 1 | 33037.97 | 35792.66 | 2754.69 | 1000 |  | 2754690 | 2766170.13 | Satmasjid |  |  |  | U Lab | 2766170.13 | 2585824.4138 | 180345.7163 | 6.9744 | OK
19 | Akota | 11 |  | BD014020 | 1 | 5038.54 | 5565.65 | 527.11 | 1000 |  | 527110 | 529306.7232 | Adabor |  |  |  | Akota | 529306.7232 | 494561.9781 | 34744.745 | 7.0254 | OK
20 | Burigonga O/H | 11 |  | BD014019 | 1 | 3859.78 | 4279.01 | 419.23 | 1000 |  | 419230 | 420977.1349 | Adabor |  |  |  | Burigonga O/H | 420977.1349 | 372374.7602 | 48602.3747 | 13.052 | OK
21 | Garden City | 11 |  | BD014021 | 1 | 78655.82 | 81041.07 | 2385.25 | 1000 |  | 2385250 | 2395190.4943 | Satmasjid |  |  |  | Garden City | 2395190.4943 | 2278829.2831 | 116361.2111 | 5.1062 | OK
22 | Avenue O/H | 11 |  | BD014017 | 1 | 11015.72 | 11977.96 | 962.24 | 1000 |  | 962240 | 966250.121 | Adabor |  |  |  | Avenue O/H | 966250.121 | 894892.5874 | 71357.5337 | 7.9739 | OK
23 | Chand Uddyan | 11 |  | BD014018 | 1 | 6743.1 | 7472.53 | 729.43 | 1000 |  | 729430 | 732469.8888 | Satmasjid |  |  |  | Chand Uddyan | 732469.8888 | 645275.1572 | 87194.7316 | 13.5128 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4416 | 1 | 1720.85 | 1760.35 | 39.5 | 100 |  | 3950 | 3966.4616 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3966.4616 | 1513.851 | 2452.6106 | 162.0114 | FAULT
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 2409.7413 | -2409.7413 | -100 | CHECK
[9 empty] | Grand Total | 14014683.5916 | 13956520 | 14014683.5916 | 0.41675
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 8120853.0785
[5 empty] | Satmasjid | at 33 KV level |  | 5893830.5131
[5 empty] | Total = |  |  | 14014683.5916 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 | 33 | IMPORT | 8993638E | 1 | 4175.969 | 4184.327 | 8.358 | 180000 | 0 | 1504440
9 | Satmosjid -2 | 33 |  | 8993669E | 1 | 5705.38 | 5753.894 | 48.514 | 180000 | 0 | 8732520
13 | Lalmatia | 33 |  |  | 1 | 5413.706 | 5450.602 | 36.896 | 180000 | 0 | 6641280
14 | Transformer-1 | 33 |  | 50147586E | 1 | 3062.422 | 3099.791 | 37.369 | 750000 | 0 | 28026750
15 | Transformer-2 | 33 |  | 50148569E | 1 | 2701.161 | 2739.184 | 38.023 | 750000 | 0 | 28517250
[8 empty] | Total Import/Export |  | 0 | 73422240
[9 empty] | Net Total | 73422240
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | RECEIVE |  | 1 |  |  | 0
| 33 KV GT-2 Incomming |  |  |  | 1 |  |  | 0
| 33 KV Satmosjid-1 Incomming |  |  |  | 1 |  |  | 0
Total Import/Export
[8 empty] | Net Total |  | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | EXPORT | [7 empty] | 0
| Feeder No.2 | [9 empty] | 0
[9 empty] | Total |  | 0
SATMOSJID 132 KV SIDE
[9 empty] | Total |  | 0
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 73422240 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 73422240
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 73422240 |  | 33 KV NET IMPORT |  | 73422240
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 73422240
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming | 33 |  | 50147586 | 1 | 3062.422 | 3099.791 | 37.369 | 750000 | 28026750
10 | 132/33 kV, 80/120 MVA GT-2 Incoming | 33 |  | 50148569 | 1 | 2701.161 | 2739.184 | 38.023 | 750000 | 28517250
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
[7 empty] | 0 |  | Total | 56544000 |  | 73422240
| SATMOSJID 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SICAM | 1 | 29.58 | 39.43 | 9.85 | 1000 | Estimated | 9903973.5 | 9865381.5788 |  | -0.10672 | Satmasjid 3/11 kv ss | 19730763.1576 | 33/11 kV, 20/28 MVA T-1 (HV) | 9865381.5788 | 9621589.1239 | 243792.4549 | 2.5338 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SICAM | 1 | 30.11 | 40.13 | 10.02 | 1000 | Estimated | 9903973.5 | 9865381.5788 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 9865381.5788 | 9621589.1239 | 243792.4549 | 2.5338 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 19807947 | 19730763.1576 |  |  |  |  | 33 KV Feeders | 19730763.1576 | 19243178.2478 | 487584.9098 | 2.5338 | OK
6 | BGB | 33 |  | 214393/40-2711 | 1 | 31.1554 | 31.16 | 0.0046 | 1000 | Estimated | 1500000 | 1494155.0851 |  | 0.9905 | BGB 33/11 KV SS | 1494155.0851 | BGB | 1494155.0851 | 8821206.0951 | -7327051.0099 | -83.0618 | CHECK
| Asad Gate Circuit-1 | 33 |  | 214393/44-2711 | 1 | 46.0777 | 54.83 | 8.7523 | 1000 | Estimated | 9837093.6 | 9798762.2837 |  | 1.0884 | ASADGATE 33/11 KV SS | 16609775.004 | Asad Gate Circuit-1 | 9798762.2837 | 8702671.9579 | 1096090.3258 | 12.5949 | OK
8 | Lalmatia Circuit-2 | 33 |  | SICAM | 1 | 58.14 | 82.53 | 24.39 | 1000 | Estimated | 15393240 | 15333258.5486 |  | 0.43418 | LALMATIA 33/11 KV SS | 15333258.5486 | Lalmatia Circuit-2 | 15333258.5486 | 13435879.8635 | 1897378.6851 | 14.1217 | OK
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 83.3379 | 235.65 | 152.3121 | 1000 | Estimated | 6837656.4 | 6811012.7204 |  | 1.3735 | JIGATOLA OLD 33/11 KV SS | 1481903.0134 | Asad Gate Circuit-2 | 6811012.7204 | 8460368.1416 | -1649355.4212 | -19.4951 | OK
13 | Jigatola U/G Circuit | 33 |  | 214393/37-2711 | 1 | 7975.877 | 10131.445 | 2155.568 | 1000 | Estimated | 1487700 | 1481903.0134 |  | -0.065475 | JAPAN GARDEN 33/11 KV SS | 18772385.1912 | Jigatola U/G Circuit | 1481903.0134 | 1445282.3546 | 36620.6589 | 2.5338 | OK
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 23770 | 32260 | 8490 | 1000 | Estimated | 18845820 | 18772385.1912 |  |  |  |  | Japan Garden City-2 | 18772385.1912 | 16099903.3397 | 2672481.8515 | 16.5994 | OK
[9 empty] | Total |  | 53901510 | 53691476.8424 |  |  |  |  | 0 | 53691476.8424 | 56965311.7522 | -3273834.9098 | -5.7471 | OK
[8 empty] | Grand Total |  | 73422240 | 73709457 | 73422240 | -0.38966
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming | 11 |  | DHK60998 | 1 | 4684.51 | 4739.43 | 54.92 | 180000 | 9885600 |  | 9782554.0545
24 | 33/11 kV T-2 Incoming | 11 |  | DHK61044 | 1 | 4771.4 | 4827.25 | 55.85 | 180000 | 10053000 |  | 9948209.1031
[7 empty] | 0 |  | Total | 19938600 |  | 19730763.1576
| SATMOSJID 11 kV SIDE | [5 empty] | 0
16 | Lalmatia O/H | 11 |  | DHK61042 | 1 | 3104.91 | 3125.6 | 20.69 | 60000 |  | 1241400 | 1240075.1783 | Satmasjid |  |  |  | Lalmatia O/H | 1240075.1783 | 1343819.1874 | -103744.0091 | -7.7201 | OK
16 | Asad Avenue (South) | 11 |  | DHK 60999 | 1 | 2892.58 | 2895.94 | 3.36 | 60000 |  | 201600 | 201384.8525 | Satmasjid |  |  |  | Asad Avenue (South) | 201384.8525 | 143036.2105 | 58348.6421 | 40.7929 | FAULT
17 | Madrasha Road | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | 11 |  | DHK61002 | 1 | 2314.11 | 2340.79 | 26.68 | 60000 |  | 1600800 | 1599091.6268 | Satmasjid |  |  |  | Bashbari | 1599091.6268 | 1533732.8114 | 65358.8154 | 4.2614 | OK
19 | Road-27 | 11 |  | DHK61001 | 1 | 1430.55 | 1432.05 | 1.5 | 60000 |  | 90000 | 89903.952 | Satmasjid |  |  |  | Road-27 | 89903.952 | 435118.5562 | -345214.6042 | -79.3381 | CHECK
20 | Boishakhi O/H | 11 |  | DHK61024 | 1 | 3992.78 | 4043.27 | 50.49 | 60000 |  | 3029400 | 3026167.0253 | Dhanmondi |  |  |  | Boishakhi O/H | 3026167.0253 | 2814447.7883 | 211719.237 | 7.5226 | OK
21 | Katasur O/H | 11 |  | DHK61003 | 1 | 3557.69 | 3581.57 | 23.88 | 60000 |  | 1432800 | 1431270.9163 | Satmasjid |  |  |  | Katasur O/H | 1431270.9163 | 1334804.3002 | 96466.6161 | 7.227 | OK
22 | Nurjahan Road | 11 |  | DHK61000 | 1 | 1769.35 | 1793.34 | 23.99 | 60000 |  | 1439400 | 1437863.8728 | Shyamoli |  |  |  | Nurjahan Road | 1437863.8728 | 1376873.7739 | 60990.0989 | 4.4296 | OK
25 | polpar over head | 11 |  | DHK61003 | 1 | 1725.79 | 1761.42 | 35.63 | 60000 |  | 2137800 | 2135518.5405 | Dhanmondi |  |  |  | polpar over head | 2135518.5405 | 2016930.7661 | 118587.7745 | 5.8796 | OK
26 | Satmosjid Housing | 11 |  | DHK61043 | 1 | 2792.38 | 2792.38 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  | Satmosjid Housing | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | Physical College | 11 |  | DHK61041 | 1 | 3172.69 | 3216.68 | 43.99 | 60000 |  | 2639400 | 2636583.2332 | Satmasjid |  |  |  | Physical College | 2636583.2332 | 2184607.6683 | 451975.5649 | 20.6891 | OK
28 | Asad Avenue (North) | 11 |  | DHK61022 | 1 | 2725.31 | 2725.31 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  | Asad Avenue (North) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare Feeder | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | 11 |  | DHK61023 | 1 | 1015.9 | 1042.11 | 26.21 | 60000 |  | 1572600 | 1570921.7218 | Dhanmondi |  |  |  | Ghraphic artch college | 1570921.7218 | 1701409.7136 | -130487.9918 | -7.6694 | OK
31 | Mohammadpur O/H | 11 |  | DHK61025 | 1 | 2104.86 | 2132.57 | 27.71 | 60000 |  | 1662600 | 1660825.6738 | Shyamoli |  |  |  | Mohammadpur O/H | 1660825.6738 | 1343218.1949 | 317607.4789 | 23.6453 | OK
32 | Bosila Feeder | 11 |  | DHK60997 | 1 | 3970.07 | 4018.46 | 48.39 | 60000 |  | 2903400 | 2900301.4925 | Satmasjid |  |  |  | Bosila Feeder | 2900301.4925 | 3015179.277 | -114877.7845 | -3.81 | OK
33 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIB 7375 | 1 | 5415.28 | 5560.3 | 145.02 | 60 |  | 8701.2 | 8691.9141 | Satmasjid |  |  |  | 11/0.4 kV Auxiliary Transformer | 8691.9141 | 0 | 8691.9141 | #DIV/0! | #DIV/0!
[9 empty] | Total | 19938600 | 19959901.2 | 19938600 | -0.10672
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Satmasjid | at 33 KV level |  | 10107303.1657
[5 empty] | Shyamoli | at 33 KV level |  | 3098689.5466
[5 empty] | Dhanmondi | at 33 KV level |  | 6732607.2877
[5 empty] | Total = |  |  | 19938600 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 | 33 |  | 38992490 (new) | 1 | 1.103 | 1.16 | 0.057 | 180000 | 0 | 10260 | 10260
| Kallyanpur to Japangarden-2 | 33 |  | 8993669E | 1 | 5705.38 | 5753.894 | 48.514 | 180000 | 0 | 8732520 | 8732520
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 23770 | 32260 | 8490 | 1000 | Estimated | 18845820 | 18772385.1912
[9 empty] | Total | 0 | 27588600 | 27515165.1912
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G | 33 | RECEIVE | DHK86051 | 1 | 2888.25 | 2920.04 | 31.79 | 270000 |  | 8583300
| kallyanpur U/G-2 | 33 |  | DHK61100 | 1 | 2774.74 | 2807.02 | 32.28 | 270000 |  | 8715600
[7 empty] | 0 |  | Total |  | 17298900
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| 33 KV Japan Genden City | 33 |  | DHK15681 | 1 | 273.18 | 358.27 | 85.09 | 18000 |  | 1531620 | 1531620 | Adabor
[6 empty] | 0 | 0
[7 empty] | 0 |  | Total |  | 1531620
0
| JAPAN GERDEN CITY 33 KV SIDE | [5 empty] | 0
| 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61080 | 1 | 4133.56 | 4181.99 | 48.43 | 180000 |  | 8717400
3 | 33/11 kV 20/28 MVA T-1 (HV) | 33 |  | 86052 | 1 | 4894.24 | 4942 | 47.76 | 180000 |  | 8596800
[9 empty] | Total |  | 17314200 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 18845820 |  | EXPORT TO OTHER S/S |  |  | 1531620 |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 17314200
| IMPORT-2 |  |  |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  |  | 17314200 |  | 33 KV TX HV SIDE |  | 17314200
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 18845820
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK61079 | 1 | 5521.1 | 5575.08 | 53.98 | 160000 | 8636800 |  | 8596583.1126
10 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK61082 | 1 | 4597.17 | 4651.91 | 54.74 | 160000 | 8758400 |  | 8717616.8874
[7 empty] | 0 |  | Total | 17395200 |  | 17314200
| JAPAN GERDEN CITY 11 KV SIDE | [5 empty] | 0
5 | Dhaka Uddyan | 11 |  | DHK86067 | 1 | 3249.24 | 3249.81 | 0.57 | 60000 |  | 34200 | 34177.6075 | Adabor |  |  |  | Dhaka Uddyan | 34177.6075 | 0 | 34177.6075 | #DIV/0! | #DIV/0!
| Shia Mosjid | 11 |  | DHK60950 | 1 | 3353.91 | 3392.62 | 38.71 | 60000 |  | 2322600 | 2321079.2736 | Shyamoli |  |  |  | Shia Mosjid | 2321079.2736 | 1677029.4105 | 644049.8631 | 38.4042 | OK
6 | Shekhar Tek | 11 |  | DHK60977 | 1 | 2275.45 | 2311.48 | 36.03 | 60000 |  | 2161800 | 2160384.5576 | Adabor |  |  |  | Shekhar Tek | 2160384.5576 | 1966584.1503 | 193800.4074 | 9.8547 | OK
7 | Madrasha Road | 11 |  | DHK61083 | 1 | 1925.96 | 1945.1 | 19.14 | 60000 |  | 1148400 | 1147648.0831 | Shyamoli |  |  |  | Madrasha Road | 1147648.0831 | 1148666.6379 | -1018.5548 | -0.088673 | OK
8 | Baitul Aman Housing | 11 |  | DHK668115 | 1 | 3971.87 | 4021.57 | 49.7 | 60000 |  | 2982000 | 2980047.5303 | Adabor |  |  |  | Baitul Aman Housing | 2980047.5303 | 2714650.3131 | 265397.2171 | 9.7765 | OK
11 | Shyamoli Square | 11 |  | DHK86063 | 1 | 446.82 | 452.52 | 5.7 | 30000 |  | 171000 | 170888.0374 | Shyamoli |  |  |  | Shyamoli Square | 170888.0374 | 163284.9924 | 7603.045 | 4.6563 | OK
12 | Mohammadi Housing | 11 |  | DHK60948 | 1 | 3719.11 | 3751.71 | 32.6 | 60000 |  | 1956000 | 1954719.3056 | Adabor |  |  |  | Mohammadi Housing | 1954719.3056 | 1343295.1846 | 611424.1209 | 45.5167 | FAULT
13 | Chand Housing | 11 |  | DHK60867 | 1 | 2131.68 | 2147.7 | 16.02 | 60000 |  | 961200 | 960570.6526 | Satmasjid |  |  |  | Chand Housing | 960570.6526 | 891350.9825 | 69219.6701 | 7.7657 | OK
14 | PC Culture Housing | 11 |  | DHK60979 | 1 | 3977.85 | 4021.99 | 44.14 | 60000 |  | 2648400 | 2646665.9554 | Adabor |  |  |  | PC Culture Housing | 2646665.9554 | 2456140.6176 | 190525.3379 | 7.7571 | OK
15 | Mehedibagh | 11 |  | DHK68121 | 1 | 2158.29 | 2208.55 | 50.26 | 60000 |  | 3015600 | 3013625.5306 | Adabor |  |  |  | Mehedibagh | 3013625.5306 | 2845397.7111 | 168227.8195 | 5.9123 | OK
16 | 33/11 kV Incoming (Spare) | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer | 11 |  |  | 1 | 636966 | 642363 | 5397 | 1 |  | 5397 | 5393.4663 | Adabor |  |  |  | 11/0.4 kV Auxiliary Transformer | 5393.4663 | 0 | 5393.4663 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 17395200 | 17406597 | 17395200 | -0.065475
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Adabor | at 33 KV level |  | 12795013.9533
[5 empty] | Shyamoli | at 33 KV level |  | 3639615.3941
[5 empty] | Satmasjid | at 33 KV level |  | 960570.6526
[5 empty] | Total = |  |  | 17395200 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) | 132 |  | 42627810 | 1 | 134.079 | 145.541 | 11.462 | 960000 | 0 | 11003520
2 | Dhaka University-1 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) | 132 |  | 42627812 | 1 | 135.244 | 146.811 | 11.567 | 960000 | 0 | 11104320
3 | Dhaka University-2 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 22107840
[9 empty] | Net Total | 22107840
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 | 132 |  | 2877 | 1 | 107.3 | 116.48 | 9.18 | 1200000 |  | 11016000
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 | 132 |  | 2811 | 1 | 108.18 | 117.43 | 9.25 | 1200000 |  | 11100000
[7 empty] | 0 | Total Import/Export |  | 0 | 22116000
[7 empty] | 0 | Net Total |  | 22116000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| 132 kV Dhaka University | 132 | 0 | SIEM0480 | 1 | 59905 | 68964 | 9059 | 1000 |  | 9059000
0
[7 empty] | 0 |  | Total |  | 9059000
| DHAKA UNIVERSITY 132 KV SIDE | [5 empty] | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | 2752 | 1 | 190.62 | 196.09 | 5.47 | 1200000 |  | 6564000
4 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | 2867 | 1 | 208.59 | 214.02 | 5.43 | 1200000 |  | 6516000
[9 empty] | Total |  | 13080000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 22107840 |  | EXPORT TO OTHER S/S |  |  | 9059000 |  | 132 KV NET IMPORT |  | 13080000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 13080000 |  | 33 KV NET IMPORT |  | 12931200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 148800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.138%
| 132 KV TOTAL IMPORT |  | 22107840
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  | 2769 | 1 | 315.51 | 324.48 | 8.97 | 720000 | 6458400
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  | 2830 | 1 | 344.44 | 353.43 | 8.99 | 720000 | 6472800
[7 empty] | 0 |  | Total | 12931200 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  | 2751 | 1.15 | 29.58 | 31.01 | 1.43 | 240000 |  | 394680 | 399578.32 |  | 0.021568 | DHAKA UNIVERSITY 33/11 KV SS | 1789415.9547 | 33/11 kV 28/35 MVA T-1 | 399578.32 | 446503.3607 | -46925.0407 | -10.5094 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  | 4253 | 1 | 43.14 | 46.78 | 3.64 | 240000 |  | 873600 | 884442.1312 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 884442.1312 | 959807.3862 | -75365.2551 | -7.8521 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  | 2808 | 1 | 14.4 | 16.48 | 2.08 | 240000 |  | 499200 | 505395.5035 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 505395.5035 | 511254.1856 | -5858.6821 | -1.1459 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 1767480 | 1789415.9547 |  |  |  |  | 33 KV Feeders | 1789415.9547 | 1917564.9326 | -128148.9779 | -6.6829 | OK
2 | Spare | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 | 33 |  | 2804 | 1.48 | 130.96 | 139.96 | 9 | 360000 |  | 4795200 | 4854712.5772 |  | 1.3691 | BB AVENUE 33/11 KV SS | 6356320.3713 | BB Avenue-1 | 4854712.5772 | 3999213.5198 | 855499.0573 | 21.3917 | OK
3 | DMC Circuit-1 | 33 |  | 2861 | 1.45 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 |  |  |  |  | DMC Circuit-1 | 0 | 1673211.9592 | -1673211.9592 | -100 | CHECK
4 | Biddyut Bhaban Circuit-1 | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | 0.90537 | DMC 33/11 KV SS | 4785463.674 | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 | 33 |  | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Biddyut Bhaban Circuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | DMC Circuit-2 | 33 |  | 2803 | 1 | 275.43 | 288.56 | 13.13 | 360000 |  | 4726800 | 4785463.674 |  | 0.38532 | BIDDYUT BHABAN 33/11 KV SS | 0 | DMC Circuit-2 | 4785463.674 | 3393087.9207 | 1392375.7533 | 41.0357 | FAULT
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 175.97 | 180.09 | 4.12 | 360000 |  | 1483200 | 1501607.7941 |  |  |  |  | BB Avenue-2 | 1501607.7941 | 2358521.6677 | -856913.8736 | -36.3327 | OK
12 | Spare | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 11005200 | 11141784.0453 |  |  |  |  | 0 | 11141784.0453 | 11424035.0674 | -282251.0221 | -2.4707 | OK
[8 empty] | Grand Total |  | 12931200 | 12772680 | 12931200 | 1.2411
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 36.01 | 38.03 | 2.02 | 250000 | 505000 |  | 487145.5833
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 40.08 | 43.53 | 3.45 | 250000 | 862500 |  | 832006.0706
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 13.12 | 15.07 | 1.95 | 250000 | 487500 |  | 470264.3008
[6 empty] | 0 | 0 |  | Total | 1855000 |  | 1789415.9547
| DHAKA UNIVERSITY 11 kV SIDE |  |  |  |  | 0 | 0
| Mokarom Bhabon | 11 |  | 2761 | 1 | 44.12 | 46.92 | 2.8 | 60000 |  | 168000 | 168036.2342 | Ramna |  |  |  | Mokarom Bhabon | 168036.2342 | 191876.7922 | -23840.558 | -12.4249 | OK
4 | 11 kV Shaid Minar RMU | 11 |  | 2850 | 1 | 105.12 | 110.73 | 5.61 | 60000 |  | 336600 | 336672.5979 | Ramna |  |  |  | 11 kV Shaid Minar RMU | 336672.5979 | 339844.4752 | -3171.8773 | -0.93333 | OK
5 | 11 kV Shaidulla Hall | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | 11 |  | 2836 | 1 | 81.98 | 86.15 | 4.17 | 60000 |  | 250200 | 250253.9631 | Ramna |  |  |  | MBA Bhabon | 250253.9631 | 301348.8178 | -51094.8547 | -16.9554 | OK
11 | Suprime Court | 11 |  | 2835 | 1 | 39.19 | 44.16 | 4.97 | 60000 |  | 298200 | 298264.3158 | Ramna |  |  |  | Suprime Court | 298264.3158 | 306762.2696 | -8497.9539 | -2.7702 | OK
12 | Karjon Hall | 11 |  | 2853 | 1 | 45.01 | 50.23 | 5.22 | 60000 |  | 313200 | 313267.551 | Ramna |  |  |  | Karjon Hall | 313267.551 | 333228.0341 | -19960.4831 | -5.99 | OK
13 | Spare | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | 11 |  | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | Swimming Pool | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU | 11 |  | 2772 | 1 | 54.79 | 62.93 | 8.14 | 60000 |  | 488400 | 488505.3381 | Ramna |  |  |  | Police Head Quarter RMU | 488505.3381 | 444504.5437 | 44000.7944 | 9.8988 | OK
17 | Spare | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare | 11 |  | 2764 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Spare | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 1855000 | 1854600 | 1855000 | 0.021568
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 1855000
[5 empty] | Total = |  |  | 1855000 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 | 33 | 0 | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 88662.91 | 109268.7 | 20605.79 | 270 |  | 5563563.3
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 21216.15 | 21216.15 | 0 | 270 |  | 0
| Dhaka University Incoming-1 | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58472.99 | 58473.17 | 0.18 | 270 | 48.6
| Dhaka University Incoming-2 | 33 |  | DHK-C9343 | 1 | 45329.41 | 45329.41 | 0 | 270 |  | 0
[7 empty] | 0 |  | Total |  | 5563563.3 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58472.99 | 58473.17 | 0.18 | 270 |  | 48.6
[6 empty] | 0 | 0
[7 empty] | 0 |  | Total |  | 48.6
0
| BIDDYUT BHABAN 33 KV SIDE | [5 empty] | 0
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-C9342 | 1 | 60685.49 | 69335.3 | 8649.81 | 270 |  | 2335448.7
3 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK-C9308 | 1 | 91727.57 | 103692.2 | 11964.63 | 270 |  | 3230450.1
[9 empty] | Total |  | 5565898.8 | 5565947.4
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 5563563.3 |  | EXPORT TO OTHER S/S |  |  | 48.6 |  | 33 KV NET IMPORT |  | 5563514.7
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 5563514.7 |  | 33 KV TX HV SIDE |  | 5565898.8
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -2384.1
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.04285%
| TOTAL IMPORT |  | 5563563.3
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK-C9316 | 1 | 39063.58 | 48730 | 9666.42 | 240 | 2319940.8 |  | 2327513.4507
10 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK-C9377 | 1 | 39057.53 | 52497 | 13439.47 | 240 | 3225472.8 |  | 3236001.2493
[7 empty] | 0 |  | Total | 5545413.6 |  | 5563514.7
| BIDDYUT BHABAN 11 KV SIDE | [5 empty] | 0
6 | Segunbagicha | 11 |  | DHK-C9360 | 1 | 61185.99 | 71954 | 10768.01 | 60 |  | 646080.6 | 648570.0837 | Ramna |  |  |  | Segunbagicha | 648570.0837 | 628132.1417 | 20437.9419 | 3.2538 | OK
| Secretariat RMU | 11 |  | DHK-C9379 | 1 | 66319.31 | 68931.7 | 2612.39 | 60 |  | 156743.4 | 157347.3651 | Ramna |  |  |  | Secretariat RMU | 157347.3651 | 189151.3106 | -31803.9455 | -16.814 | OK
7 | NBR RMU | 11 |  | DHK-C9319 | 1 | 35791.29 | 43622.4 | 7831.11 | 60 |  | 469866.6 | 471677.0943 | Ramna |  |  |  | NBR RMU | 471677.0943 | 454185.7713 | 17491.323 | 3.8511 | OK
8 | Ramna 11 kV Sw/S-2 | 11 |  | DHK-C9364 | 1 | 81944.91 | 99344.1 | 17399.19 | 60 |  | 1043951.4 | 1047973.9631 | Ramna |  |  |  | Ramna 11 kV Sw/S-2 | 1047973.9631 | 1309281.295 | -261307.3319 | -19.9581 | OK
11 | Ramna 11 kV Sw/S-1 | 11 |  | DHK-C9375 | 1 | 30061.75 | 30685.5 | 623.75 | 60 |  | 37425 | 37569.2064 | Ramna |  |  |  | Ramna 11 kV Sw/S-1 | 37569.2064 | 3932.094 | 33637.1123 | 855.4504 | FAULT
12 | Family Planning | 11 |  | DHK-C9378 | 1 | 33829.12 | 41466 | 7636.88 | 60 |  | 458212.8 | 459978.3897 | Ramna |  |  |  | Family Planning | 459978.3897 | 450311.5022 | 9666.8876 | 2.1467 | OK
13 | Muktijuddho Montranalaya | 11 |  | DHK-C9376 | 1 | 9833.69 | 26269.1 | 16435.41 | 60 |  | 986124.6 | 989924.3443 | Ramna |  |  |  | Muktijuddho Montranalaya | 989924.3443 | 925250.3935 | 64673.9509 | 6.9899 | OK
14 | Purana Palton | 11 |  | DHK-C9318 | 1 | 38036.29 | 43328.3 | 5292.01 | 60 |  | 317520.6 | 318744.0733 | Ramna |  |  |  | Purana Palton | 318744.0733 | 328976.7665 | -10232.6933 | -3.1105 | OK
15 | Tip Top Feeder | 11 |  | DHK-C9318 | 1 | 42816.99 | 66509.6 | 23692.61 | 60 |  | 1421556.6 | 1427034.1549 | Kakrail |  |  |  | Tip Top Feeder | 1427034.1549 | 1299449.2529 | 127584.902 | 9.8184 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 |  | DHKD3784 | 1 | 331579 | 336257 | 4678 | 1 |  | 4678 | 4696.0253 | Ramna |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 4696.0253 | 4800.6724 | -104.6471 | -2.1798 | OK
[9 empty] | Grand Total | 5563514.7 | 5542159.6 | 5563514.7 | 0.38532
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 4136480.5451
[5 empty] | Kakrail | at 33 KV level |  | 1427034.1549
[5 empty] | Total = |  |  | 5563514.7 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 | 33 | 0 | 2861 | 1.45 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 | 33 | 0 | 2803 | 1 | 275.43 | 288.56 | 13.13 | 360000 | 0 | 4726800 | 4785463.674
[9 empty] | Total | 0 | 4726800 | 4785463.674
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 377.52 | 391.38 | 13.86 | 240000 | 0 | 3326400 | 3327433.1371
[9 empty] | Total |  | 3326400 | 3327433.1371
| DMCH 33 KV SIDE (RECEIVING) | [10 empty] | 8112896.8112
| 33 kV DU Incoming Circuit-1 | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
[9 empty] | Total |  | 0 | 0
DMCH 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[9 empty] | Total |  | 0
DMCH 33 KV SIDE
| 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | 00000069 | 1 | 118781280 | 122143200 | 3361920 | 1 |  | 3361920
2 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
[9 empty] | Total |  | 3361920 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 4785463.674 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 8112896.8112
| DHANMONDI 33 kV SIDE |  | 3327433.1371 |  | 33 KV NET IMPORT |  |  | 8112896.8112 |  | 33 KV TX HV SIDE |  | 8112896.8112
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 8112896.8112
11 KV SIDE of___DMCH 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000056 | 1 | 117615056 | 120948056 | 3333000 | 1 | 3333000 |  | 3369754.5129
14 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000034 | 1 | 143263472 | 147954880 | 4691408 | 1 | 4691408 |  | 4743142.2982
[7 empty] | 0 |  | Total | 8024408 |  | 8112896.8112
| DMCH 11 KV SIDE | [5 empty] | 0
6 | Nearest O/H | 11 |  | 00000126 | 1 | 6865423 | 7074262 | 208839 | 1 |  | 208839 | 210729.7741 | Ramna |  |  |  | Nearest O/H | 210729.7741 | 229906.9253 | -19177.1512 | -8.3413 | OK
| Jagannath Hall | 11 |  | 00000002 | 1 | 2433494 | 2545753.8 | 112259.8 | 1 |  | 112259.8 | 113276.1711 | Ramna |  |  |  | Jagannath Hall | 113276.1711 | 96242.8599 | 17033.3111 | 17.6983 | OK
7 | Samsun Nahar Hall | 11 |  | 00000024 | 1 | 8763059 | 9054018 | 290959 | 1 |  | 290959 | 293593.2672 | Ramna |  |  |  | Samsun Nahar Hall | 293593.2672 | 312413.2678 | -18820.0006 | -6.0241 | OK
8 | Spare, 4L | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | 11 |  | 00000023 | 1 | 20238430 | 20726990 | 488560 | 1 |  | 488560 | 492983.2953 | Lalbag |  |  |  | Board Office O/H, (5L) | 492983.2953 | 466712.6927 | 26270.6026 | 5.6289 | OK
10 | OT- Complex | 11 |  | 00000167 | 1 | 5287027 | 5711026 | 423999 | 1 |  | 423999 | 427837.7768 | Ramna |  |  |  | OT- Complex | 427837.7768 | 405707.0733 | 22130.7035 | 5.4548 | OK
11 | Alia Mdrasha O/H, (7L) | 11 |  | 00000148 | 1 | 9243737 | 9318217 | 74480 | 1 |  | 74480 | 75154.3226 | Lalbag |  |  |  | Alia Mdrasha O/H, (7L) | 75154.3226 | 71193.4446 | 3960.878 | 5.5635 | OK
12 | Majed Sordar Road | 11 |  | 00000164 | 1 | 51746392 | 53489908 | 1743516 | 1 |  | 1743516 | 1759301.3409 | Bangshal |  |  |  | Majed Sordar Road | 1759301.3409 | 1689289.8138 | 70011.5271 | 4.1444 | OK
15 | Chankharpool, 9L | 11 |  | 00000001 | 1 | 44457492 | 45648168 | 1190676 | 1 |  | 1190676 | 1201456.0712 | Bangshal |  |  |  | Chankharpool, 9L | 1201456.0712 | 1157798.1959 | 43657.8753 | 3.7708 | OK
16 | Shahidullah College O/H, (10L) | 11 |  | 00000003 | 1 | 12322570 | 12584169 | 261599 | 1 |  | 261599 | 263967.4494 | Lalbag |  |  |  | Shahidullah College O/H, (10L) | 263967.4494 | 265403.8751 | -1436.4257 | -0.54122 | OK
17 | Ananda Bazar | 11 |  | 00000111 | 1 | 14499445 | 14714284 | 214839 | 1 |  | 214839 | 216784.0965 | Ramna |  |  |  | Ananda Bazar | 216784.0965 | 169141.9631 | 47642.1334 | 28.167 | OK
18 | Hosseni Dalan O/H, (12L) | 11 |  |  | 1 | 4.6 | 23.41 | 18.81 | 60000 |  | 1614720 | 1629339.2554 | Lalbag | Previous Meter Consumption Added |  |  | Hosseni Dalan O/H, (12L) | 1629339.2554 | 1651805.4359 | -22466.1805 | -1.3601 | OK
19 | Badrun Nessa College | 11 |  | 00000006 | 1 | 18502514 | 19009274 | 506760 | 1 |  | 506760 | 511348.0734 | Lalbag |  |  |  | Badrun Nessa College | 511348.0734 | 487810.3149 | 23537.7585 | 4.8252 | OK
20 | Dhaka Medical College, Unit-II | 11 |  | 00000125 | 1 | 11041413 | 11353372 | 311959 | 1 |  | 311959 | 314783.3957 | Ramna |  |  |  | Dhaka Medical College, Unit-II | 314783.3957 | 318669.3545 | -3885.9588 | -1.2194 | OK
21 | Spare, 15L | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | 11 |  | 00000127 | 1 | 19088354 | 19677112 | 588758 | 1 |  | 588758 | 594088.462 | Ramna |  |  |  | Sheikh Hasina National Burn Institute | 594088.462 | 527600.9918 | 66487.4702 | 12.6018 | OK
23 | Aux. Transformer, AT-1 | 0.415 |  | DHKF-7804 | 1 | 2469.39 | 2551.19 | 81.8 | 100 |  | 8180 | 8254.0596 | Ramna |  |  |  | Aux. Transformer, AT-1 | 8254.0596 | 7320.9952 | 933.0644 | 12.745 | OK
24 | Aux. Transformer, AT-2 | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 8112896.8112 | 8040103.8 | 8112896.8112 | 0.90537
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2179347.0029
[5 empty] | Lalbag | at 33 KV level |  | 2972792.3961
[5 empty] | Bangshal | at 33 KV level |  | 2960757.4121
[5 empty] | Total = |  |  | 8112896.8112 | 0
Previous Meter Consumption
[6 empty] | Previous | Present | Difference | Consumption
|  |  |  | Hosseni Dalan O/H |  | 26760014 | 27246134 | 486120 | 486120
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 | 33 | 0 | 2804 | 1.48 | 130.96 | 139.96 | 9 | 360000 | 0 | 4795200 | 4854712.5772
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 175.97 | 180.09 | 4.12 | 360000 | 0 | 1483200 | 1501607.7941
[9 empty] | Total | 0 | 6278400 | 6356320.3713
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 | 33 |  | BD 017078 | 1 |  | 0 | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 | 33 |  | BD 017090 | 1 | 63228.14 | 64705.72 | 1477.58 | 1125 |  | 1662277.5
[7 empty] | 0 |  | Total | 0 | 1662277.5 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
[7 empty] | 0 |  | Total |  | 0
0
| BB AVENEU 33 KV SIDE | [5 empty] | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD 017093 | 1 | 83011.26 | 87852.83 | 4841.57 | 1000 |  | 4841570
3 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD 017094 | 1 | 48613.46 | 50094.48 | 1481.02 | 1000 |  | 1481020
[9 empty] | Total |  | 6322590 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 6356320.3713 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BB AVENEU 33 KV NET IMPORT |  | 6356320.3713
[5 empty] | BB AVENEU 33 KV NET IMPORT |  |  | 6356320.3713 |  | 33 KV TX HV SIDE |  | 6322590
[10 empty] | LOSS UNITS=> |  | 33730.3713
[10 empty] | LOSS % IN => |  | 0.5307%
| TOTAL IMPORT |  | 6356320.3713
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD 014052 | 1 | 83276.64 | 88103.06 | 4826.42 | 1000 | 4826420 |  | 4880668.5312
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD 014055 | 1 | 48131.71 | 49590.96 | 1459.25 | 1000 | 1459250 |  | 1475651.8401
[7 empty] | 0 |  | Total | 6285670 |  | 6356320.3713
| BB AVENEU 11 KV SIDE | [5 empty] | 0
6 | Secratariet East | 11 |  | BD 013966 | 1 | 3164.56 | 3406.54 | 241.98 | 1000 |  | 241980 | 245293.0009 | Ramna |  |  |  | Secratariet East | 245293.0009 | 245463.3743 | -170.3734 | -0.069409 | OK
| Taher Bag O/H | 11 |  | BD 014045 | 1 | 16925.42 | 17659.83 | 734.41 | 1000 |  | 734410 | 744464.9674 | Narinda |  |  |  | Taher Bag O/H | 744464.9674 | 740283.3012 | 4181.6661 | 0.56487 | OK
7 | Al Raji Complex | 11 |  | BD 013983 | 1 | 12207.81 | 12982.02 | 774.21 | 1000 |  | 774210 | 784809.8778 | Ramna |  |  |  | Al Raji Complex | 784809.8778 | 793405.3649 | -8595.4871 | -1.0834 | OK
8 | Raduni | 11 |  | BD 013999 | 1 | 25230.43 | 26506.32 | 1275.89 | 1000 |  | 1275890 | 1293358.488 | Ramna |  |  |  | Raduni | 1293358.488 | 1280815.0384 | 12543.4496 | 0.97933 | OK
9 | Sundor Bon Square O/H | 11 |  | BD 013954 | 1 | 11796.22 | 12263.75 | 467.53 | 1000 |  | 467530 | 473931.0551 | Narinda |  |  |  | Sundor Bon Square O/H | 473931.0551 | 515871.5523 | -41940.4971 | -8.13 | OK
10 | Shromo Bhobon O/H | 11 |  | BD 013985 | 1 | 11614.06 | 12112.38 | 498.32 | 1000 |  | 498320 | 505142.6077 | Ramna |  |  |  | Shromo Bhobon O/H | 505142.6077 | 521299.6391 | -16157.0314 | -3.0994 | OK
11 | Nawabpur Road | 11 |  | BD 013953 | 1 | 17725.04 | 18556.72 | 831.68 | 1000 |  | 831680 | 843066.7121 | Narinda |  |  |  | Nawabpur Road | 843066.7121 | 849749.7199 | -6683.0077 | -0.78647 | OK
12 | Spair | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | 11 |  | BD 013984 | 1 | 9842.75 | 10306.68 | 463.93 | 1000 |  | 463930 | 470281.7667 | Ramna |  |  |  | Ahad Police Box | 470281.7667 | 423970.1788 | 46311.5879 | 10.9233 | OK
17 | Nearest O/H | 11 |  | BD 013997 | 1 | 2274.44 | 2390.76 | 116.32 | 1000 |  | 116320 | 117912.5625 | Ramna |  |  |  | Nearest O/H | 117912.5625 | 115595.8875 | 2316.6749 | 2.0041 | OK
18 | Natab Bhaban | 11 |  | BD 014000 | 1 | 4442.04 | 4625.24 | 183.2 | 1000 |  | 183200 | 185708.2311 | Ramna |  |  |  | Natab Bhaban | 185708.2311 | 177165.0302 | 8543.2009 | 4.8222 | OK
19 | Spare | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | 11 |  | BD 013956 | 1 | 1395.25 | 1404.54 | 9.29 | 1000 |  | 9290 | 9417.1914 | Ramna |  |  |  | Awami League Party Office | 9417.1914 | 9250.1106 | 167.0808 | 1.8063 | OK
21 | Khaddar Bazar | 11 |  | BD 014012 | 1 | 8928.66 | 9317.61 | 388.95 | 1000 |  | 388950 | 394275.1992 | Ramna |  |  |  | Khaddar Bazar | 394275.1992 | 392631.6173 | 1643.5819 | 0.41861 | OK
22 | Bangobondu National Stidium | 11 |  | BD 014008 | 1 | 5862.17 | 6146.93 | 284.76 | 1000 |  | 284760 | 288658.7112 | Ramna |  |  |  | Bangobondu National Stidium | 288658.7112 | 290128.194 | -1469.4828 | -0.50649 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4418 | 1 | 1124.63 | 1124.63 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 1718.8942 | -1718.8942 | -100 | CHECK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 41.9 | 41.9 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 387.2849 | -387.2849 | -100 | CHECK
[9 empty] | Grand Total | 6356320.3713 | 6270470 | 6356320.3713 | 1.3691
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 4294857.6367
[5 empty] | Narinda | at 33 KV level |  | 2061462.7346
[5 empty] | Total = |  |  | 6356320.3713 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
[9 empty] | Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 0
[5 empty] | KALLYANPUR 33 KV NET IMPORT |  |  | 0 |  | KALLYANPUR 11 KV NET IMPORT |  | 0
[5 empty] | TOTAL EXPORT |  |  | 0 |  | LOSS UNITS=> |  | 0
[5 empty] | 132KV NET LOSS => |  |  | #DIV/0! |  | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming | 11 |  | 74819926 | 1 | 0 | 0 | 0
[6 empty] | 0 | 0 |  | Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  |  |  |  | 0 | 0
A | From Kallyanpur S/S. |  |  |  |  | 0 | 0
| 11 KV Gano Bhavan RMU | 11 |  | DHK14997 | 1 | 995.68 | 995.71 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar |  |  |  | 11 KV Gano Bhavan RMU | 1230 | 1230 | 4.6612e-09 | 3.7896e-10 | OK
| 11 KV Beribandh Feeder. | 11 |  | DHK14960 | 1 | 9633.08 | 9640.43 | 7.35 | 40000 |  | 294000 | 301350 | Adabor |  |  |  | 11 KV Beribandh Feeder. | 301350 | 184500 | 116850 | 63.3333 | FAULT
| 11 KV Adabor O/H | 11 |  | DHK14957 | 1 | 4319.26 | 4371.7 | 52.44 | 40000 |  | 2097600 | 2150040 | Adabor |  |  |  | 11 KV Adabor O/H | 2150040 | 2995460 | -845420 | -28.2234 | OK
| 11 KV Mansurabad | 11 |  | 77816681 | 1 | 51326.05 | 51616.27 | 290.22 | 8000 |  | 2321760 | 2379804 | Adabor |  |  |  | 11 KV Mansurabad | 2379804 | 2220888 | 158916 | 7.1555 | OK
| 11 KV Ring Road Feeder | 11 |  | 77816675 | 1 | 41632.55 | 41775.56 | 143.01 | 8000 |  | 1144080 | 1172682 | Adabor |  |  |  | 11 KV Ring Road Feeder | 1172682 | 1124384 | 48298 | 4.2955 | OK
| 11 KV Sewarage Pump | 11 |  | DHK14959 | 1 | 1991.3 | 2054.75 | 63.45 | 40000 |  | 2538000 | 2601450 | Adabor |  |  |  | 11 KV Sewarage Pump | 2601450 | 535870 | 2065580 | 385.4629 | FAULT
| 11 KV Technical School (DPDC) | 11 |  | DHK15019 | 1 | 8076.21 | 8133.47 | 57.26 | 40000 |  | 2290400 | 2347660 | Adabor |  |  |  | 11 KV Technical School (DPDC) | 2347660 | 2184890 | 162770 | 7.4498 | OK
| 11 KV Goidertek (DPDC) | 11 |  | DHK14996 | 1 | 9341.2 | 9355.62 | 14.42 | 40000 |  | 576800 | 591220 | Adabor |  |  |  | 11 KV Goidertek (DPDC) | 591220 | 558420 | 32800 | 5.8737 | OK
B | From Agargaon S/S. | 11 | [9 empty] | 0
| 11 KV P.C Culture Housing | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H | 11 |  | DHK-15026 | 1 | 9151.97 | 9164.92 | 12.95 | 40000 |  | 518000 | 530950 | Shere b.nagar
| 11 KV Nearest RMU | 11 |  | DHK-15027 | 1 | 3855.49 | 3859.52 | 4.03 | 40000 |  | 161200 | 165230 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar | 11 |  | DHK-15025 | 1 | 3975.03 | 3976.15 | 1.12 | 40000 |  | 44800 | 45920 | Shere b.nagar
| 11 KV BCFCC Feeder. | 11 |  | DHK-15024 | 1 | 1038.1 | 1038.1 | 0 | 40000 |  | 0 | 0
| 11 KV NEC Feeder. | 11 |  | DHK-15023 | 1 | 431.56 | 431.56 | 0 | 40000 |  | 0 | 0
| 11 KV Manik Mia Feeder. | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0
[6 empty] | Export To Desco |  | 13837.5 | Grand Total | 0 | 11987840 | 12287536 | 2.5
DESCO | 11 kV Tolarbugh | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 0 | 0 | 0 | #DIV/0!
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 11544206
[5 empty] | Shere b.nagar | at 33 KV level |  | 729492.5
[5 empty] | Satmasjid | at 33 KV level
[5 empty] | DESCO | at 33 KV level |  | 13837.5
[5 empty] | Total = |  |  | 12287536 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 | 33 | 0 | 30799147 | 1 | 1464.97 | 1491.72 | 26.75 | 240000 | 0 | 6420000 | 6464726.8389
[9 empty] | Total | 0 |  | 6464726.8389
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
[9 empty] | Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming | 33 | EXPORT |  |  |  |  | 0 | 240000 |  | 0
| Lalbagh Incoming | 33 | [5 empty] | 0 | 240000 |  | 0
[9 empty] | Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 6464726.8389 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 6464726.8389
| IMPORT-2 |  |  |  | KALLYANPUR 33 KV NET IMPORT |  |  | 6464726.8389 |  | KALLYANPUR 11 KV NET IMPORT |  | 6464726.8389
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6464726.8389
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar-2 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0
[9 empty] | Total | 0 |  | 6464726.8389
| Kamrangirchar-2 11 KV SIDE | [13 empty] | 110
1 | Nizambag | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1000528.2 | 1008260.1492 | Kamrangirchar | 85 | 50 |  | Nizambag | 1008260.1492 | 972380.6635 | 35879.4856 | 3.6899 | OK
2 | Merry Stopes | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 353127.6 | 355856.5232 | Kamrangirchar | 30 | 60 |  | Merry Stopes | 355856.5232 | 364642.7488 | -8786.2256 | -2.4095 | OK
3 | Mujibur Ghat | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1294801.2 | 1304807.2519 | Kamrangirchar | 110 | 20 |  | Mujibur Ghat | 1304807.2519 | 1337023.4124 | -32216.1605 | -2.4095 | OK
4 | Madrasa | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1530219.6 | 1542044.934 | Kamrangirchar | 130 | 70 |  | Madrasa | 1542044.934 | 1701666.1612 | -159621.2271 | -9.3803 | OK
5 | Thana | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1412510.4 | 1423426.093 | Kamrangirchar | 120 |  |  | Thana | 1423426.093 | 1337023.4124 | 86402.6806 | 6.4623 | OK
6 | Al-Hera | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 823964.4 | 830331.8876 | Kamrangirchar | 70 |  |  | Waz Uddin School | 830331.8876 | 972380.6635 | -142048.776 | -14.6084 | OK
8 | 11/0.4 kV Auxiliary Transformer | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off | [7 empty] | Grand Total | 6464726.8389 | 6415151.4 | 6464726.8389 | 0.77279
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 6464726.8389
[5 empty] | Total = |  |  | 6464726.8389 | 0
Formulas:
Corrected = [Active Energy in kWh]
Note on F941: User: Grid CF=1.5

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) | 132 | IMPORT | 8993631 | 1 | 5714.359 | 5756.396 | 42.037 | 960000 | 0 | 40355520
| 132 KV Mogbazar-2 CKT(EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) | 132 |  | 8993659 | 1 | 4882.347 | 4914.803 | 32.456 | 960000 | 0 | 31157760
| 132 KV Mogbazar-1 CKT(EXP) | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 71513280
[9 empty] | Net Total | 71513280
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE | 6604452 | 1 | 9191.87 | 9248.01 | 56.14 | 720000 | 40420800
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  | 6604428 | 1 | 5489.95 | 5533.5 | 43.55 | 720000 | 31356000
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
[8 empty] | Total Import/Export |  | 71776800 | 0
[8 empty] | Net Total |  | 71776800 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0 |  |  | future Scope
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0 |  |  | No meter
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 71776800
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 71513280 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 71513280
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 71513280 |  | MOGBAZAR 33 KV NET IMPORT |  | 71275200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 238080
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3329%
| 132 KV TOTAL IMPORT |  | 71513280
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming | 33 | IMPORT | 76026303 | 1 | 9814.76 | 9864.79 | 50.03 | 480000 | 24014400 |  | 24094615.1148
| 132/33 KV GT-2 Incomming | 33 |  | 76026307 | 1 | 9809.83 | 9859.88 | 50.05 | 480000 | 24024000 |  | 24104247.1816
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 8021.51 | 8069.92 | 48.41 | 480000 | 23236800 |  | 23314417.7035
[7 empty] | 0 |  | Total | 71275200 |  | 71513280
| MOGBAZAR 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. | 33 |  | 6604465 | 1 | 6938.25 | 6959.93 | 21.68 | 180000 |  | 3902400 | 3899553.3751 |  | 20208348.1599 | MOGBAZAR 33/11 KV SS | 5.4552 | 33/11 KV Transformer No.1. | 3899553.3751 | 5075185.8236 | -1175632.4485 | -23.1643 | OK
| 33/11 KV Transformer No.2. | 33 |  | 202006985 | 1 | 35648331276 | 35656606639 | 8275363 | 3 | T2 Incomer side | 3707100 | 3704395.8376 |  |  |  |  | 33/11 KV Transformer No.2. | 3704395.8376 | 4826900.3057 | -1122504.4681 | -23.2552 | OK
| 33/11 KV Transformer No.3. | 33 |  | 6604338 | 1 | 6980.86 | 7011.3 | 30.44 | 180000 |  | 5479200 | 5475203.1705 |  |  |  |  | 33/11 KV Transformer No.3. | 5475203.1705 | 4305833.3784 | 1169369.7921 | 27.1578 | OK
| 33/11 KV Transformer No.4 | 33 |  |  | 1 | 992649 | 1034346 | 41697 | 180000 | T4 Incomer side | 7134400 | 7129195.7767 |  |  |  |  | 33/11 KV Transformer No.4 | 7129195.7767 | 6317722.2805 | 811473.4962 | 12.8444 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 20223100 | 20208348.1599 |  |  |  |  | 33 KV Feeders | 20208348.1599 | 20525641.7881 | -317293.6282 | -1.5458 | OK
8 | 33 kV Tejgaon U/G Feeder-1 | 33 |  | 76026300 | 1 | 6673.48 | 6695.56 | 22.08 | 360000 |  | 7948800 | 7943001.7086 |  | 21807280.959 | Tejgoan 33/11 kv ss | 0.90377 | 33 kV Tejgaon U/G Feeder-1 | 7943001.7086 | 7976588.0874 | -33586.3788 | -0.42106 | OK
9 | 33 kV Tejgaon U/G Feeder-2 | 33 |  | 06604453 | 1 | 6435.77 | 6474.31 | 38.54 | 360000 |  | 13874400 | 13864279.2504 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 13864279.2504 | 13260442.6166 | 603836.6339 | 4.5537 | OK
10 | Bashundhara City | 33 |  | 660434 | 1 | 739.39 | 753.18 | 13.79 | 180000 |  | 2482200 | 2480389.347 | Shere b.nagar | 5987828.9601 | Ispahani 33/11 kv ss | 0.62377 | Bashundhara City | 2480389.347 | 2161081.9864 | 319307.3606 | 14.7753 | OK
11 | Ispahani-1 | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 2665263.8855 | -2665263.8855 | -100 | CHECK
12 | Ispahani-2 | 33 |  |  | 1 | 3791.06 | 3824.35 | 33.29 | 180000 |  | 5992200 | 5987828.9601 |  | 9535149.4608 | Green Road Dormatory 33/11 kv ss | -0.81473 | Ispahani-2 | 5987828.9601 | 2935877.963 | 3051950.9971 | 103.9536 | FAULT
13 | 33 kV Green Road Dormitory | 33 |  | 76026305 | 1 | 7993.99 | 8019.59 | 25.6 | 180000 | Reading From G. Dormitory Side | 9542110 | 9535149.4608 |  |  |  |  | 33 kV Green Road Dormitory | 9535149.4608 | 6704636.3993 | 2830513.0614 | 42.2172 | FAULT
14 | 33 KV T&T-1 | 33 |  | 6604337 | 1 | 4500.97 | 4533.36 | 32.39 | 180000 |  | 5830200 | 5825947.1318 |  | 11239994.945 | T&T 33/11 kv ss | 0.02402 | 33 KV T&T-1 | 5825947.1318 | 5563289.1437 | 262657.9881 | 4.7213 | OK
13 | 33 KV T&T-2 | 33 |  | 6604336 | 1 | 5594.46 | 5624.56 | 30.1 | 180000 |  | 5418000 | 5414047.8132 |  |  |  |  | 33 KV T&T-2 | 5414047.8132 | 5474378.13 | -60330.3169 | -1.102 | OK
14 | 33KV Karwan Bazar | 33 |  | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.69515 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | AT-1 | 33 |  | 6603338 | 1 | 1546.46 | 1749.21 | 202.75 | 80 |  | 16220 | 16208.1682 |  |  |  |  | AT-1 | 16208.1682 | 0 | 16208.1682 | #DIV/0! | #DIV/0!
20 | AT-2 | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 51104130 | 51066851.8401 |  |  |  |  | 0 | 51066851.8401 | 46741558.2119 | 4325293.6282 | 9.2536 | OK
[8 empty] | Grand Total |  | 71275200 | 71327230 | 71275200 | -0.072945
-0.3377
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2480389.347
[8 empty] | Total = | 2480389.347 | 0 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 | 11 | Import | 6604457 | 1 | 528622.1 | 532514.4 | 3892.3 | 1000 | 3892300 |  | 3902583.1448
2 | 33/11 kV Transformer-2 | 11 | Import | 30/11009-1101 | 1 | 571655.2 | 575362.3 | 3707.1 | 1000 | 3707100 |  | 3716893.8613
3 | 33/11 kV Transformer-3 | 11 | Import | 6604454 | 1 | 564172.6 | 569593.9 | 5421.3 | 1000 | 5421300 |  | 5435622.6404
4 | 33/11 kV Transformer-4 | 11 | Import |  | 1 | 919.91 | 964.5 | 44.59 | 160000 | 7134400 |  | 7153248.5134
[7 empty] | 0 |  | Total | 20155100 |  | 20208348.1599
| MOGBAZAR 11 kV SIDE | [5 empty] | 0
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40402.7 | 40404.3 | 1.6 | 1000 |  | 1600 | 1691.4448 | Moghbazar |  |  |  | 11 kV Doctor's Lane | 1691.4448 | 1119.369 | 572.0758 | 51.107 | FAULT
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 79796.2 | 80555.5 | 759.3 | 1000 |  | 759300 | 802696.2793 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 802696.2793 | 1023306.7911 | -220610.5119 | -21.5586 | OK
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 1589911.0287 | -1589911.0287 | -100 | CHECK
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 118798.7 | 119107.7 | 309 | 1000 |  | 309000 | 326660.2796 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 326660.2796 | 342221.6327 | -15561.3531 | -4.5472 | OK
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 120528.2 | 122850.8 | 2322.6 | 1000 |  | 2322600 | 2455343.5773 | Moghbazar |  |  |  | 11KV Ambagan | 2455343.5773 | 1989016.959 | 466326.6183 | 23.4451 | OK
0
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 141604.5 | 142744.5 | 1140 | 1000 |  | 1140000 | 1205154.4296 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1205154.4296 | 1055666.7314 | 149487.6981 | 14.1605 | OK
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9327.8 | 9488.7 | 160.9 | 1000 |  | 160900 | 170095.919 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 170095.919 | 154167.6401 | 15928.279 | 10.3318 | OK
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 118443.2 | 120465.9 | 2022.7 | 1000 |  | 2022700 | 2138303.3901 | Kakrail |  |  |  | 11 kV Bangla Motor | 2138303.3901 | 1962152.1029 | 176151.2872 | 8.9775 | OK
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 171354 | 172255.3 | 901.3 | 1000 |  | 901300 | 952812.0065 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 952812.0065 | 1869447.9972 | -916635.9907 | -49.0324 | CHECK
0
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 115816.3 | 117632.1 | 1815.8 | 1000 |  | 1815800 | 1919578.4326 | Kakrail |  |  |  | 11 kV Iskaton | 1919578.4326 | 1819483.4353 | 100094.9973 | 5.5013 | OK
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 81467.2 | 82976.9 | 1509.7 | 1000 |  | 1509700 | 1595983.8968 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1595983.8968 | 78254.0694 | 1517729.8273 | 1939.49 | FAULT
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 122407.2 | 122785.5 | 378.3 | 1000 |  | 378300 | 399920.9831 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 399920.9831 | 690345.3929 | -290424.4098 | -42.0694 | CHECK
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 111507.7 | 112406.9 | 899.2 | 1000 |  | 899200 | 950591.9851 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 950591.9851 | 944645.6784 | 5946.3067 | 0.62947 | OK
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43325.7 | 0 | 1000 |  | 0 | 0 | Kakrail |  |  |  | 11 kV BSRS Feeder | 0 | 323294.1205 | -323294.1205 | -100 | CHECK
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8294.9 | 8423.8 | 128.9 | 1000 |  | 128900 | 136267.0228 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 136267.0228 | 122011.2214 | 14255.8014 | 11.684 | OK
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  |  | 13055099.6465 | 12349300 | 13055099.6465 | 5.7153 |  |  |  |  | 13055099.6465 | 13965044.1701
1 | 11 kV TCB Feeder | 11 | T-4 |  | 1 | 33653.6 | 34661.4 | 1007.8 | 1000 |  | 1007800 | 1058026.2525 | Kakrail |  |  |  | 11 kV TCB Feeder | 1058026.2525 | 587067.814 | 470958.4385 | 80.2222 | FAULT
2 | 11 kV Tejgaon SS-2 | 11 | T-4 |  | 1 | 27179.6 | 28639.4 | 1459.8 | 1000 |  | 1459800 | 1532552.8114 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1532552.8114 | 1481122.0985 | 51430.7129 | 3.4724 | OK
3 | Holy Day Inn | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 497820 | 522630.1141 | Tejgaon |  |  |  | Holy Day Inn | 522630.1141 | 493817.3233 | 28812.7908 | 5.8347 | OK
4 | Polly Bhabon-2 | 11 | T-4 |  | 1 | 18301.8 | 18322 | 20.2 | 1000 | Consumer meter damaged, 12 months average | 28632 | 30058.9479 | Kakrail |  |  |  | Polly Bhabon-2 | 30058.9479 | 29444.1053 | 614.8426 | 2.0882 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 |  | 1 | 11538.8 | 13294.2 | 1755.4 | 1000 |  | 1755400 | 1842884.7823 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1842884.7823 | 1860061.7445 | -17176.9622 | -0.92346 | OK
6 | 11 kV Tejturibazar | 11 | T-4 |  | 1 | 129174.3 | 129914.1 | 739.8 | 1000 |  | 739800 | 776669.7972 | Kakrail |  |  |  | 11 kV Tejturibazar | 776669.7972 | 731592.6735 | 45077.1236 | 6.1615 | OK
7 | Songsad | 11 | T-4 |  | 1 | 1949 | 2467.7 | 518.7 | 1000 |  | 518700 | 544550.7215 | Shere b.nagar |  |  |  | Songsad | 544550.7215 | 126381.9385 | 418168.783 | 330.877 | FAULT
| Chennel 24 | 11 | T-4 |  | 1 | 7307.13 | 7308.75 | 1.62 | 1000 |  | 1620 | 1700.7368 | Moghbazar |  |  |  | Chennel 24 | 1700.7368 | 1164.858 | 535.8788 | 46.0038 | FAULT
8 | Sonargaon | 11 | T-4 |  | 1 | 38114.9 | 38919 | 804.1 | 1000 |  | 804100 | 844174.3497 | Kakrail |  |  |  | Sonargaon | 844174.3497 | 839625.5215 | 4548.8282 | 0.54177 | OK
| AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 7215.9345 | -7215.9345 | -100 | CHECK
| AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 7153248.5134 | 6813672 | 7153248.5134 | 4.9838
[9 empty] | Total | 20208348.1599 | 19162972 | 20208348.1599 | 5.4552
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | [14 empty] | AMR Meter Information
[5 empty] | Moghbazar | at 33 KV level |  | 2858656.742 | [14 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
[5 empty] | Tejgaon | at 33 KV level |  | 7244852.759 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 75270 | 3000
[5 empty] | Kakrail | at 33 KV level |  | 9560287.9373 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 422550 | 3000
[5 empty] | Shere b.nagar | at 33 KV level |  | 544550.7215 | [14 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 28632 | 300
[5 empty] | Total = |  |  | 20208348.1599 | 0
AMR Meter Information
[23 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[23 empty] | Shah Garments | 732.02 | 751.49 | 200.55 | 206.17
[23 empty] | Habib Hotel | 2314.07 | 2416.56 | 751.1 | 789.46
[23 empty] | The Joint Director BRDB | 1002.66 | 1083.78 | 206.49 | 220.81
[25 empty] | 751.49 | 206.17
[25 empty] | 2416.56 | 789.46
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [23 empty] | 1083.78 | 220.81
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 | 33 | 0 | 6604337 | 1 | 4500.97 | 4533.36 | 32.39 | 180000 | 0 | 5830200 | 5825947.1318
13 | 33 KV T&T-2 | 33 | 0 | 6604336 | 1 | 5594.46 | 5624.56 | 30.1 | 180000 | 0 | 5418000 | 5414047.8132
0 | Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 11248200 | 11239994.945
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder | 33 | Import | DHK60891 | 1 | 955990 | 966779 | 10789 | 360 | 3884040
2 | 33 kV Moghbazar-2 Feeder | 33 | Import | DHK68131 | 1 | 867760 | 877078 | 9318 | 360 | 3354480
| 33 kV Ullon Feeder | 33 | Import | DHK68132 | 1 | 349.75 | 349.75 | 0 | 180000 | 0
[7 empty] | 0 |  | Total | 7238520 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
0
| Mogbazar T&T 33 KV SIDE | [5 empty] | 0
3 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 966463 | 998825 | 32362 | 180 |  | 5825160
4 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 799053 | 819230 | 20177 | 180 |  | 5418000 |  |  | Meter Problem
[9 empty] | Total |  | 11243160 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 11239994.945 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 11239994.945
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 11239994.945 |  | 33/11 KV XF LV SIDE |  | 11315880
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -75885.055
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.6751%
| TOTAL IMPORT |  | 11239994.945
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 982217 | 1014802 | 32585 | 180 | 5865300 |  | 5825966.9023 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 929641 | 959922 | 30281 | 180 | 5450580 |  | 5414028.0426 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 11315880 |  | 11239994.945 | -0.67061 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 109708 | 133254 | 23546 | 60 |  | 1412760 | 1413099.3422 | Kakrail |  |  |  | 11 kV post office | 1413099.3422 | 1314936.3633 | 98162.979 | 7.4652 | OK
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 374779 | 399215 | 24436 | 60 |  | 1466160 | 1466512.1688 | Kakrail |  |  |  | 11 kV anarkoli | 1466512.1688 | 1363050.3594 | 103461.8095 | 7.5905 | OK
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 931981 | 938252 | 6271 | 60 |  | 376260 | 376350.3769 | Moghbazar |  |  |  | 11 kV sonalibagh | 376350.3769 | 416269.8468 | -39919.4698 | -9.5898 | OK
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1912434 | 1927455 | 15021 | 60 |  | 901260 | 901476.4809 | Moghbazar |  |  |  | 11 Kv desh tv | 901476.4809 | 862940.0791 | 38536.4018 | 4.4657 | OK
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 532.55 | 561.01 | 28.46 | 60000 |  | 1707600 | 1708010.1623 | Moghbazar |  |  |  | 11 Kv Btcl | 1708010.1623 | 1630130.9123 | 77879.25 | 4.7775 | OK
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 864753 | 874964 | 10211 | 60 |  | 612660 | 612807.1598 | Kakrail |  |  |  | 11 kV century | 612807.1598 | 591251.5937 | 21555.566 | 3.6458 | OK
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 434155 | 452115 | 17960 | 60 |  | 1077600 | 1077858.8375 | Moghbazar |  |  |  | 11 kV cinema hall | 1077858.8375 | 1046359.7284 | 31499.1091 | 3.0104 | OK
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 642051 | 669487 | 27436 | 60 |  | 1646160 | 1646555.4045 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1646555.4045 | 1662984.8723 | -16429.4678 | -0.98795 | OK
4 | 11 kv Sherebangla | 11 |  | DHK60915 | 1 | 645233 | 668842 | 23609 | 60 |  | 1416540 | 1416880.2502 | Moghbazar |  |  |  | 11 kv Sherebangla | 1416880.2502 | 1438632.4204 | -21752.1702 | -1.512 | OK
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 297424 | 308967 | 11543 | 60 |  | 692580 | 692746.3564 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 692746.3564 | 708065.6738 | -15319.3174 | -2.1635 | OK
6 | Auxiliary |  | Export | U0004461 | 1 | 7968.46 | 8028.17 | 59.71 | 60 |  | 3582.6 | 3583.4605 | Moghbazar |  |  |  | Auxiliary | 3583.4605 | 3045.4245 | 538.0361 | 17.667 | OK
[9 empty] | Grand Total | 11315880 | 11313162.6 | 11315880 | 0.02402
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 3492418.6708
[5 empty] | Moghbazar | at 33 KV level |  | 6176905.9247
[5 empty] | Khilgaon | at 33 KV level |  | 1646555.4045
[5 empty] | Total = |  |  | 11315880 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 | 132 | IMPORT | 8993681 | 1 | 2593.526 | 2618.149 | 24.623 | 1440000 | 0 | 35457120
| Ullon-1 | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 35457120
[8 empty] | Net Total |  | 35457120
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) | 132 |  | 8993624 | 1 | 4743.032 | 4768.057 | 25.025 | 960000 | 0 | 24024000
| Maniknager-2 (new line to ullon) | 132 |  |  | 1 | 11.003 | 11.003 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 24024000
[8 empty] | Net Total |  | 24024000
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 | 132 |  | 8993659 | 1 | 4374.65 | 4387.45 | 12.8 | 960000 | 0 | 12288000
| Ullon U/G-1 | 132 |  |  | 1 | 1.56 | 1.56 | 0 | 960000 | 0 | 0
| Ullon U/G-2 | 132 |  | 8993660 | 1 | 4060.204 | 4072.298 | 12.094 | 960000 | 0 | 11610240
| Ullon U/G-2 | 132 |  |  | 1 | 1.329 | 1.329 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 23898240
[8 empty] | Net Total |  | 23898240
ULLON 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
| EXPORT TO OTHERS 132/33 KV SS | [12 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 | 132 |  |  | 1 | 1632756 | 1632756 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 | 132 |  |  | 1 | 2071385 | 2101057 | 29672 | 1000 |  | 29672000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 | 132 |  |  | 1 | 2827813 | 2857313 | 29500 | 1000 |  | 29500000 |  |  | 132 kV Ullon CKT-3 | 31978000
[9 empty] | Total |  | 59172000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 24207360
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 35457120 |  | EXPORT TO OTHER S/S |  |  | 59172000 |  | 132 KV NET IMPORT |  | 24207360
| HORIPUR 132 SIDE (TARIFF POINT) |  | 24024000 |  | 132 KV Net EXPORT |  |  | 24207360 |  | 132/33 KV GT LV Side |  | 23916960
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 23898240 | [6 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 290400
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.2%
| 132 KV TOTAL IMPORT |  | 83379360
33 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming | 33 | Import | BD001812 | 1 | 2106.811 | 2131.9868 | 25.1758 | 480000 | 12084384 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming | 33 | Import | BD001858 | 1 | 2029.6535 | 2054.3047 | 24.6512 | 480000 | 11832576 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 23916960 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1503.439 | 1533.8259 | 30.3869 | 240000 | Estimated | 7292856 | 7335965.7983 |  | 15162035.693 | Taltola 33/11 kv ss | 1.017 | Taltala-1 | 7335965.7983 | 6736010.2412 | 599955.5571 | 8.9067 | OK
| Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Mgbazar T&T | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9044 | 1163.9083 | 0.0039 | 240000 |  | 936 | 941.5329 |  | 0 | Mgbazar T&T 33/11 kv ss | 0.02402 | Kakrail | 941.5329 | 0 | 941.5329 | #DIV/0! | #DIV/0!
2 | Taltala-2 | 33 | Export | BD001837 | 1 | 2463.334 | 2495.751 | 32.417 | 240000 |  | 7780080 | 7826069.8947 |  |  |  |  | Taltala-2 | 7826069.8947 | 7516984.2137 | 309085.681 | 4.1118 | OK
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 941.5329 | Kakrail 33/11 kv ss | 1.8285 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 0.90044 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.6699 | 61.9199 | 0.25 | 240000 |  | 60000 | 60354.6742 |  | 0 | Tejgoan 33/11 kv ss | 0.90377 | Khailgaon | 60354.6742 | 149060.0067 | -88705.3325 | -59.5098 | CHECK
4 | AT at GIS Building | 415 | Export | DHKE4577 | 1 | 134040 | 141164 | 7124 | 1 |  | 7124 | 7166.1117 |  | 60354.6742 | Khilgoan 33/11 kv ss | 1.7001 | AT at GIS Building | 7166.1117 | 0 | 7166.1117 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | TOTAL= |  | 15140996 | 15230498.0117 |  |  |  |  | 0 | 15230498.0117 | 14402054.4615 | 828443.5502 | 5.7523 | OK
| 33 KV Local Feeder -1 | 33 | NET IMPORT |  | 1 | 1097.744 | 1116.0406 | 18.2966 | 240000 |  | 4391184 | 4417141.3282 |  | 8686461.9883 | Ullon 33/11 kv ss | 1.7875 | 33 KV Local Feeder -1 | 4417141.3282 | 3401630.7953 | 1015510.5329 | 29.8536 | OK
| 33KV Local Feeder- 2 | 33 |  |  | 1 | 827.3438 | 845.0281 | 17.6843 | 240000 |  | 4244232 | 4269320.6601 |  |  |  |  | 33KV Local Feeder- 2 | 4269320.6601 | 3996724.7692 | 272595.8909 | 6.8205 | OK
[9 empty] | TOTAL= |  | 8635416 | 8686461.9883 |  |  |  |  | 0 | 8686461.9883 | 7398355.5645 | 1288106.4238 | 17.4107 | OK
[9 empty] | Grand Total | 23916960 | 23776412 | 23916960 | 0.59112
11 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 8635416 |  | 8686461.9883 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 1118237.4 | 1138226.0536 | Moghbazar | 95 |  |  | West Malibagh | 1138226.0536 | 978294.9507 | 159931.103 | 16.3479 | OK
2 | Ullon | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1589074.2 | 1617479.1288 | Moghbazar | 135 |  |  | Ullon | 1617479.1288 | 1406298.9916 | 211180.1373 | 15.0167 | OK
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1647928.8 | 1677385.7633 | Moghbazar | 140 |  |  | Mohanagar | 1677385.7633 | 1345155.5572 | 332230.2061 | 24.6983 | OK
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1294801.2 | 1317945.9568 | Moghbazar | 110 |  |  | Bagichartek | 1317945.9568 | 1100581.8195 | 217364.1373 | 19.7499 | OK
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1530219.6 | 1557572.4944 | Moghbazar | 130 |  |  | Mirbagh | 1557572.4944 | 1345155.5572 | 212416.9373 | 15.7913 | OK
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 1353655.8 | 1377852.5912 | Moghbazar | 115 |  |  | West Rampura | 1377852.5912 | 1222868.6883 | 154983.9029 | 12.6738 | OK
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 8686461.9883 | 8533917 | 8686461.9883 | 1.7875
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 8686461.9883
[5 empty] | Total = |  |  | 8686461.9883 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 | 132 | Export | 50146667 | 1 | 1730.856 | 1758.566 | 27.71 | 960000 | 0 | 26601600
2 | Rampura to Madartek-2 | 132 | Export | 50146668 | 1 | 1525.358 | 1552.894 | 27.536 | 960000 | 0 | 26434560
[8 empty] | Total Import/Export |  | 0 | 53036160
[8 empty] | Net Total |  | 53036160
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 | 132 | Import | SIEM0492 | 1 | 1519412 | 1545900 | 26488 | 1000 | 26488000
|  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 | 132 | Import | SIEM0489 | 1 | 1468831 | 1495344 | 26513 | 1000 | 26513000
|  | 132 | Export |  | 1 |  | 0 | 0
[7 empty] | 0 | Total Import/Export |  | 53001000 | 0
[7 empty] | 0 | Net Total |  | 53001000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 |  |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| MADERTEK 132 KV SIDE | [5 empty] | 0
3 | 133 kV GT-1 | 132 | Export |  | 1 | 1355242 | 1381875 | 26633 | 1000 |  | 26633000
4 | 133 kV GT-2 | 132 | Export |  | 1 | 1344009 | 1370463 | 26454 | 1000 |  | 26454000
[9 empty] | Total |  | 53087000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 53036160 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 53036160
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 53036160 |  | 33 KV NET IMPORT |  | 53235000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -198840
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.3749%
| 132 KV TOTAL IMPORT |  | 53036160
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0516 | 1 | 1503865 | 1530511 | 26646 | 1000 | 26646000 |  | 26546473.5486
2 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0515 | 3 | 499309 | 508172 | 8863 | 1000 | 26589000 |  | 26489686.4514
[7 empty] | 0 |  | Total | 53235000 |  | 53036160
| MADERTEK 33 KV SIDE | [5 empty] | 0
| 33/11 kv Transforfers | [5 empty] | 0
1 | 33 kV T-1 | 33 | Import | SIEM0512 | 1 | 399032 | 403503 | 4471 | 2000 |  | 8942000 | 8927214.4929 |  | 21368608.7012 | Madartek 33/11 kv ss
2 | 33 kV T-3 | 33 | Export |  | 1 | 72634 | 74323 | 1689 | 2000 |  | 3378000 | 3372414.511
2 | 33 kV T-2 | 33 | Export | SIEM0505 | 1 | 401771 | 406313 | 4542 | 2000 |  | 9084000 | 9068979.6973
| 33 kv Feeders | [5 empty] | 0 |  | Total |  | 21404000 | 21368608.7012 |  | 15238761.1294 | Banasree 33/11 kv ss
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 93583 | 98470 | 4887 | 2000 |  | 9774000 | 9757838.7892
1 | Goran | 33 | Export | SIEM0510 | 1 | 339866 | 344806 | 4940 | 2000 |  | 9880000 | 9863663.5193 |  | 9863663.5193 | Goran 33/11 kv ss
3 | Amulia | 33 | Export | SIEM0505 | 1 | 34124 | 35220 | 1096 | 6000 |  | 6576000 | 6565126.6501
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 85518 | 88263 | 2745 | 2000 |  | 5490000 | 5480922.3402 |  | 6565126.6501 | Amulia 33/11 kv ss
[9 empty] | Total |  | 31720000 | 31667551.2988
[8 empty] | Grand Total |  | 53036160 | 53124000 | 53036160 | -0.16535
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | GJU 71154 | 1 | 371943.7 | 376390.4 | 4446.7 | 2000 | 8893400 |  | 8923135.4354 |  | Consumption of Other NOCS | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | GJU 71155 | 1 | 374822.1 | 379344.7 | 4522.6 | 2000 | 9045200 |  | 9075442.9848 |  | 7222310.3269 | [5 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming | 11 | Import | 6604399 | 1 | 4651.48 | 4670.14 | 18.66 | 180000 | 3358800 |  | 3370030.2809 |  | Consumption of Mugpadara Check | [5 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 21297400 |  | 21368608.7012 |  | 14075089.6731 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 6677.95 | 8495.5256 | 1817.5756 | 1000 |  | 1817575.6 | 1887459.924 | Mugdapara |  |  |  | Sobujbagh | 1887459.924 | 1753548.1446 | 133911.7794 | 7.6366 | OK
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 95560.9 | 97494.4 | 1933.5 | 1000 |  | 1933500 | 2007841.5243 | Mugdapara |  |  |  | Madertek | 2007841.5243 | 1858521.5132 | 149320.0111 | 8.0343 | OK
3 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 5644.71 | 7021.7968 | 1377.0868 | 1000 |  | 1377086.8 | 1430034.683 | Mugdapara |  |  |  | Rajarbagh | 1430034.683 | 1264456.5681 | 165578.1148 | 13.0948 | OK
| Goran | 11 |  | X1390296 | 1 | 24684 | 26638.6 | 1954.6 | 1000 |  | 1954600 | 2029752.8023 | Bashabo |  |  |  | Goran | 2029752.8023 | 1851494.7743 | 178258.028 | 9.6278 | OK
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 6722.86 | 8205.6192 | 1482.7592 | 1000 |  | 1482759.2 | 1539770.102 | Mugdapara |  |  |  | Dhakhingaon | 1539770.102 | 2039169.8043 | -499399.7023 | -24.4903 | OK
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 79376.5 | 79747.1 | 370.6 | 1000 |  | 370600 | 384849.2728 | Maniknagar |  |  |  | Manda | 384849.2728 | 881499.2996 | -496650.0269 | -56.3415 | CHECK
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 282.33 | 510.4637 | 228.1337 | 1000 |  | 228133.68 | 236905.237 | Mugdapara |  |  |  | Green Model Town | 236905.237 | 209712.5124 | 27192.7246 | 12.9667 | OK
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 1799.56 | 2474.7662 | 675.2062 | 1000 |  | 675206.2 | 701167.3368 | Mugdapara |  |  |  | Biswa Road | 701167.3368 | 331641.7074 | 369525.6295 | 111.4231 | FAULT
2 | Mugdapara | 11 |  | X0854272 | 1 | 3507.9 | 3786.4 | 278.5 | 1000 |  | 278500 | 289208.1016 | Maniknagar |  |  |  | Mugdapara | 289208.1016 | 256934.2344 | 32273.8672 | 12.5611 | OK
| Singapur | 11 |  | X1390302 (N) | 1 | 28808.4 | 31151.7 | 2343.3 | 1000 |  | 2343300 | 2433398.0056 | Banosree |  |  |  | Singapur | 2433398.0056 | 2200082.1244 | 233315.8811 | 10.6049 | OK
| Trimohony | 11 |  | X1390308 | 1 | 22519.4 | 24527.3 | 2007.9 | 1000 |  | 2007900 | 2085102.1446 | Banosree |  |  |  | Trimohony | 2085102.1446 | 1604947.893 | 480154.2516 | 29.9171 | OK
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 8633.04 | 10561.687 | 1928.647 | 1000 |  | 1928647 | 2002801.9303 | Mugdapara | Closing Conveted to MWH from GWH |  |  | Mayakanon | 2002801.9303 | 1839386.3794 | 163415.5509 | 8.8842 | OK
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 3107.93 | 3952.1608 | 844.2308 | 1000 |  | 844230.8 | 876690.7972 | Mugdapara |  |  |  | Ahmedbagh | 876690.7972 | 596386.824 | 280303.9732 | 47.0004 | FAULT
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 702966 | 712365 | 9399 | 200 |  | 1879800 | 1952076.8023 | Mugdapara |  |  |  | Wasa Road | 1952076.8023 | 480873.3471 | 1471203.4552 | 305.9441 | FAULT
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 739373 | 746576 | 7203 | 200 |  | 1440600 | 1495989.9146 | Mugdapara |  |  |  | Nandipara | 1495989.9146 | 298789.1572 | 1197200.7573 | 400.6841 | FAULT
| AT-1 | 0.415 |  |  | 1 | 238.06 | 357.37 | 119.31 | 80 |  | 9544.8 | 9911.7899 | Mugdapara |  |  |  | AT-1 | 9911.7899 | 10372.6886 | -460.8987 | -4.4434 | OK
3 | AT-2 | 0.415 |  | 63394003 | 1 | 89.44 | 157.43 | 67.99 | 80 |  | 5439.2 | 5648.3329 | Mugdapara |  |  |  | AT-2 | 5648.3329 | 500.2223 | 5148.1105 | 1029.1645 | FAULT
[9 empty] | Total | 21368608.7012 | 20577423.28 | 21368608.7012 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 21368608.7012 | 20577423.28 | 21368608.7012 | 3.8449
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 4518500.1502
[5 empty] | Bashabo | at 33 KV level |  | 2029752.8023
[5 empty] | Maniknagar | at 33 KV level |  | 674057.3744
[5 empty] | Mugdapara | at 33 KV level |  | 14146298.3743
[5 empty] | Total = |  |  | 21368608.7012 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 | 33 | 0 | 76026300 | 1 | 6673.48 | 6695.56 | 22.08 | 360000 | 0 | 7948800 | 7943001.7086
9 | 33 kV Tejgaon U/G Feeder-2 | 33 | 0 | 06604453 | 1 | 6435.77 | 6474.31 | 38.54 | 360000 | 0 | 13874400 | 13864279.2504
0 | Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 21823200 | 21807280.959
TEJGOAN 33 KV SIDE (RECEIVING)
[7 empty] | 0 |  | Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| TEJGOAN 33 KV SIDE | [5 empty] | 0
1 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 610667.6 | 640150.1 | 29482.5 | 270 |  | 7960275
2 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 381042.3 | 432407.9 | 51365.6 | 180 |  | 9245808
3 | 33/11 kV Transfomer-3 (T3) | 33 | Export | BD001872 | 1 | 1123.5396 | 209525.9 | 208402.3604 | 180000 |  | 6481000
[9 empty] | Total |  | 23687083 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 21807280.959 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TEJGOAN 33 KV NET IMPORT |  | 21807280.959
| IMPORT-2 |  |  |  | TEJGOAN 33 KV NET IMPORT |  |  | 21807280.959 |  | 33 KV TX HV Side |  | 23687083
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -1879802.041
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -8.62%
| TOTAL IMPORT |  | 21807280.959
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 750350.9 | 791843.8 | 41492.9 | 180 | 7468722 |  | 7649957.3737 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 665903.9 | 706686.8 | 40782.9 | 180 | 7340922 |  | 7519056.1898 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming | 11 | Import | BD001875 | 1 | 203044.9 | 209525.9 | 6481 | 1000 | 6481000 |  | 6638267.3956 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 21290644 |  | 21807280.959 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | 11 |  | DHK60950 | 1 | 176336.6 | 201859.3 | 25522.7 | 60 |  | 1531362 | 1545202.0376 | Tejgaon |  |  |  | Nakhal Para Feeder | 1545202.0376 | 1536369.5556 | 8832.482 | 0.57489 | OK
2 | Badda-Meghna Feeder | 11 |  | DHK60979 | 1 | 876525.4 | 888283.6 | 11758.2 | 60 |  | 705492 | 711868.0468 | Tejgaon |  |  |  | Badda-Meghna Feeder | 711868.0468 | 842649.7133 | -130781.6665 | -15.5203 | OK
3 | Rasulbagh Feeder | 11 |  | DHK60948 | 1 | 931276.3 | 961752.1 | 30475.8 | 60 |  | 1828548 | 1845073.9247 | Tejgaon |  |  |  | Rasulbagh Feeder | 1845073.9247 | 1902151.6741 | -57077.7494 | -3.0007 | OK
4 | Lukas | 11 |  | 8A021100948-02 | 1 | 62085526 | 64421346 | 2335820 | 1 |  | 2335820 | 2356930.5125 | Tejgaon |  |  |  | Lukas | 2356930.5125 | 2345545.782 | 11384.7305 | 0.48538 | OK
5 | PWD RMU | 11 |  |  | 1 | 650851.8 | 652660.7 | 1808.9 | 1 |  | 1808.9 | 1825.2484 | Tejgaon |  |  |  | PWD RMU | 1825.2484 | 1757.0539 | 68.1945 | 3.8812 | OK
1 | Civil Aviation Feeder | 11 |  | DHK60977 | 1 | 744587.4 | 791561.7 | 46974.3 | 60 |  | 2818458 | 2843930.4649 | Tejgaon |  |  |  | Civil Aviation Feeder | 2843930.4649 | 2795399.6317 | 48530.8331 | 1.7361 | OK
2 | Ahasanullah Eng. | 11 |  | DHK60867 | 1 | 848834.7 | 859374.2 | 10539.5 | 60 |  | 632370 | 638085.1899 | Tejgaon |  |  |  | Ahasanullah Eng. | 638085.1899 | 673101.4258 | -35016.2359 | -5.2022 | OK
3 | New GMG Feeder | 11 |  | DHK61106 | 1 | 970375 | 1007264.2 | 36889.2 | 60 |  | 2213352 | 2233355.6797 | Tejgaon |  |  |  | New GMG Feeder | 2233355.6797 | 2281871.6214 | -48515.9417 | -2.1261 | OK
4 | Shikajo | 11 |  | HA021101036-02 | 1 | 61878821 | 62704679 | 825858 | 1 |  | 825858 | 833321.8823 | Tejgaon |  |  |  | Shikajo | 833321.8823 | 756034.1648 | 77287.7175 | 10.2228 | OK
5 | Kahinur | 11 |  |  | 1 | 475997.5 | 496661.5 | 20664 | 60 |  | 1239840 | 1251045.3402 | Tejgaon |  |  |  | Kahinur | 1251045.3402 | 1294083.2246 | -43037.8843 | -3.3257 | OK
6 | Link road | 11 |  | 8A021100380-02 | 1 | 63506551 | 63919556 | 413005 | 1 |  | 413005 | 416737.628 | Tejgaon |  |  |  | Link road | 416737.628 | 435428.3198 | -18690.6917 | -4.2925 | OK
7 | Shanta | 11 |  |  | 1 | 289500.3 | 299552.9 | 10052.6 | 60 |  | 603156 | 608607.1616 | Tejgaon |  |  |  | Shanta | 608607.1616 | 630895.3248 | -22288.1632 | -3.5328 | OK
1 | Karnafuly Feeder | 11 |  | DHK61084 | 1 | 33015.5 | 33696.3 | 680.8 | 1000 |  | 680800 | 686952.8872 | Tejgaon |  |  |  | Karnafuly Feeder | 686952.8872 | 738300.0364 | -51347.1492 | -6.9548 | OK
2 | Butex | 11 |  |  | 1 | 803.1 | 892.3 | 89.2 | 1000 |  | 89200 | 90006.1656 | Tejgaon |  |  |  | Butex | 90006.1656 | 91610.1416 | -1603.976 | -1.7509 | OK
3 | OriON LAB | 11 |  |  | 1 | 7919755 | 8007550 | 87795 | 1 |  | 87795 | 88588.4676 | Tejgaon |  |  |  | OriON LAB | 88588.4676 | 248723.2522 | -160134.7846 | -64.3827 | CHECK
4 | Nina kabbo | 11 |  | 201101025-2 | 1 | 16283296 | 16563888 | 280592 | 1 |  | 280592 | 283127.915 | Tejgaon |  |  |  | Nina kabbo | 283127.915 | 99489.3009 | 183638.6141 | 184.5813 | FAULT
5 | Satrong | 11 |  | HA021100515-2 | 1 | 88090387 | 89639487 | 1549100 | 1 |  | 1549100 | 1563100.3489 | Tejgaon |  |  |  | Satrong | 1563100.3489 | 1367977.887 | 195122.4619 | 14.2636 | OK
6 | South East RMU | 11 |  |  | 1 | 464.1 | 601.9 | 137.8 | 1000 |  | 137800 | 139045.3993 | Tejgaon |  |  |  | South East RMU | 139045.3993 | 149070.967 | -10025.5677 | -6.7254 | OK
7 | Rangs Bhaban | 11 |  | HA021100939-2 | 1 | 121073 | 270974 | 149901 | 1 |  | 149901 | 151255.7649 | Tejgaon |  |  |  | Rangs Bhaban | 151255.7649 | 161670.1139 | -10414.349 | -6.4417 | OK
8 | Babli | 11 |  |  | 1 | 51912.4 | 54005.3 | 2092.9 | 1000 |  | 2092900 | 2111815.0669 | Tejgaon |  |  |  | Babli | 2111815.0669 | 1541422.4274 | 570392.6395 | 37.0043 | OK
| SPL | 11 |  |  | 1 | 3055.8 | 3461.1 | 405.3 | 1000 |  | 405300 | 408962.9923 | Tejgaon |  |  |  | SPL | 408962.9923 | 372268.4438 | 36694.5485 | 9.857 | OK
9 | DNCC Hospital | 11 |  |  | 1 | 12507.9 | 13491.4 | 983.5 | 1000 |  | 983500 | 992388.6083 | Tejgaon |  |  |  | DNCC Hospital | 992388.6083 | 965076.0343 | 27312.574 | 2.8301 | OK
| 11/.415 kv Local transformer | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  | 6000 | 6054.2264 | Tejgaon
[9 empty] | Grand Total | 21807280.959 | 21611957.9 | 21807280.959 | 0.90377
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Tejgaon | at 33 KV level |  | 21807280.959
[5 empty] | Total = |  |  | 21807280.959 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 | 33 | 0 | 214393/44-2711 | 1 | 46.0777 | 54.83 | 8.7523 | 1000 | Estimated | 9837093.6 | 9798762.2837
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 83.3379 | 235.65 | 152.3121 | 1000 | Estimated | 6837656.4 | 6811012.7204
[9 empty] | Total |  | 16674750 | 9041302.7186
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import | DHKC9350 | 1 | 45637.3 | 77676.95 | 32039.65 | 270 | 8650705.5
2 | Shatmasjid-2 | 33 | Import | DHKC9354 | 1 | 92961.2 | 123054.55 | 30093.35 | 270 | 8125204.5
[7 empty] | 0 |  | Total | 16775910
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| ASADGATE 33 KV SIDE | [5 empty] | 0
1 | Transfomer-1 (T1) | 33 | Export | DHKC9353 | 1 | 29507.07 | 84521.34 | 55014.27 | 180 |  | 9902568.6
2 | Transfomer-2 (T2) | 33 | Export | DHKC9305 | 1 | 61134.42 | 99475.18 | 38340.76 | 180 |  | 6901336.8
[9 empty] | Total |  | 16803905.4 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 16775910 |  | EXPORT TO OTHER S/S |  |  | 0 |  | ASADGATE 33 KV NET IMPORT |  | 16775910
| IMPORT-2 |  |  |  | ASADGATE 33 KV NET IMPORT |  |  | 16775910 |  | ASADGATE 11 KV NET IMPORT |  | 16775910
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 16775910
11 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHKC9371 | 1 | 3122.15 | 57772.67 | 54650.52 | 180 | 9837093.6 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHKC9337 | 1 | 63256.85 | 101243.83 | 37986.98 | 180 | 6837656.4 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 16674750 |  | 16775910 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | 11 |  | DHKC9332 | 1 | 65439.13 | 69014.8 | 3575.67 | 60 |  | 214540.2 | 216875.2359 | Shere b.nagar |  |  |  | Gonobhaban | 216875.2359 | 216836.1836 | 39.0523 | 0.01801 | OK
2 | Rapa Plaza Feeder | 11 |  | DHKC9339 | 1 | 36328.06 | 56103.84 | 19775.78 | 60 |  | 1186546.8 | 1199461.0668 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1199461.0668 | 1170856.0696 | 28604.9972 | 2.4431 | OK
3 | Shukrabad/ South Plaza | 11 |  | DHKC9324 | 1 | 77512.2 | 95989.52 | 18477.32 | 60 |  | 1108639.2 | 1120705.5276 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 1120705.5276 | 1130327.1946 | -9621.667 | -0.85123 | OK
4 | Wasa O/H | 11 |  | DHKC9333 | 1 | 43612.07 | 78543.28 | 34931.21 | 60 |  | 2095872.6 | 2118683.8855 | Satmasjid |  |  |  | Wasa O/H | 2118683.8855 | 1049087.4751 | 1069596.4105 | 101.9549 | FAULT
5 | Bangabandhu Memorial Museum | 11 |  | DHKC9334 | 1 | 14682.59 | 15026.42 | 343.83 | 60 |  | 20629.8 | 20854.3329 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 20854.3329 | 20897.995 | -43.6621 | -0.20893 | OK
6 | Iqbal Road O/H | 11 |  | DHKC9330 | 1 | 16028.77 | 43449.53 | 27420.76 | 60 |  | 1645245.6 | 1663152.3025 | Shyamoli |  |  |  | Iqbal Road O/H | 1663152.3025 | 1601413.1174 | 61739.1851 | 3.8553 | OK
7 | Town Hall | 11 |  | DHKC9351 | 1 | 29046.8 | 64380.78 | 35333.98 | 60 |  | 2120038.8 | 2143113.1083 | Shyamoli |  |  |  | Town Hall | 2143113.1083 | 2338946.2013 | -195833.093 | -8.3727 | OK
8 | Post Office | 11 |  | DHKC9331 | 1 | 14408.51 | 39135.17 | 24726.66 | 60 |  | 1483599.6 | 1499746.9623 | Shyamoli |  |  |  | Post Office | 1499746.9623 | 1492441.2314 | 7305.7308 | 0.48952 | OK
9 | Shangshad Bhaban | 11 |  | DHKC9370 | 1 | 98850.73 | 106671.66 | 7820.93 | 60 |  | 469255.8 | 474363.1372 | Shere b.nagar |  |  |  | Shangshad Bhaban | 474363.1372 | 422562.5169 | 51800.6203 | 12.2587 | OK
10 | Jakir Hossain Road | 11 |  | DHKC9373 | 1 | 52169.33 | 81724.89 | 29555.56 | 60 |  | 1773333.6 | 1792634.4006 | Satmasjid |  |  |  | Jakir Hossain Road | 1792634.4006 | 1277863.2905 | 514771.1101 | 40.2837 | FAULT
11 | New Colony O/H Feeder | 11 |  | DHKC9369 | 1 | 69251.43 | 69251.43 | 0 | 60 |  | 0 | 0 | Satmasjid |  |  |  | New Colony O/H Feeder | 0 | 1328527.8719 | -1328527.8719 | -100 | CHECK
12 | Aurangzeb Feeder | 11 |  | DHKC9321 | 1 | 12056.46 | 42513.02 | 30456.56 | 60 |  | 1827393.6 | 1847282.7847 | Shyamoli |  |  |  | Aurangzeb Feeder | 1847282.7847 | 2012075.4293 | -164792.6446 | -8.1902 | OK
13 | Asadgate Local Feeder | 11 |  | DHKC9338 | 1 | 93460.16 | 132726.29 | 39266.13 | 60 |  | 2355967.8 | 2381609.9379 | Satmasjid |  |  |  | Asadgate Local Feeder | 2381609.9379 | 1832840.2298 | 548769.7081 | 29.9409 | OK
14 | Sonarbangla Road | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli | Check |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | 11 |  | DHKC9366 | 1 | 42688.17 | 47034.27 | 4346.1 | 60 |  | 260766 | 263604.1533 | Shyamoli |  |  |  | Humayun Road | 263604.1533 | 1670349.266 | -1406745.1127 | -84.2186 | CHECK
16 | NHA | 11 |  | DHKC9374 | 1 | 52311.92 | 52748.02 | 436.1 | 60 |  | 26166 | 26450.7883 | Shyamoli |  |  |  | NHA | 26450.7883 | 221861.5773 | -195410.789 | -88.0778 | CHECK
17 | Auxiliary transformer | 0.415 |  |  | 1 | 626701 | 633994 | 7293 | 1 |  | 7293 | 7372.3763 | Satmasjid |  |  |  | Auxiliary transformer | 7372.3763 | 6148.5505 | 1223.8259 | 19.9043 | OK
[9 empty] | Grand Total | 16775910 | 16595288.4 | 16775910 | 1.0884
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 1811943.9007
[5 empty] | Dhanmondi | at 33 KV level |  | 1220315.3996
[5 empty] | Satmasjid | at 33 KV level |  | 6300300.6004
[5 empty] | Shyamoli | at 33 KV level |  | 7443350.0993
at 33 KV level
[5 empty] | Total = |  |  | 16775910 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADARTEK 33 KV SIDE
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 93583 | 98470 | 4887 | 2000 | 0 | 9774000 | 9757838.7892
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 85518 | 88263 | 2745 | 2000 | 0 | 5490000 | 5480922.3402
[9 empty] | Total |  | 15264000 | 15238761.1294 | -0.16535
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import |  | 1 | 17062220 | 17062220 | 0 | 1 | 0
2 | Madertek Circuit-02 | 33 | Import |  | 1 | 14889540 | 14889540 | 0 | 1 | 0
3 | Ullon O/H | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
[9 empty] | Total | 0 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 | 33 | Export | 14 | 1 | 2307620 | 11566520 | 9258900 | 1 |  | 9258900
2 | Transformer-02 | 33 | Export | 74 | 1 | 7251760 | 12581140 | 5329380 | 1 |  | 5329380 |  |  | Meter Problem
[9 empty] | Total |  | 14588280 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV Import |  |  | KWH |  | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 15238761.1294 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 15238761.1294
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 15238761.1294 |  | 33 KV TX HV SIDE |  | 14588280
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 650481.1294
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 4.269%
| TOTAL IMPORT |  | 15238761.1294
11 KV SIDE of___BANASREE 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 9258900 |  | 9671747.8292 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | 198 | 1 |  |  | 0 | 1 | 5329380 |  | 5567013.3003 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 14588280 |  | 15238761.1294 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | 11 |  | 141 | 1 | 1717760 | 3861980 | 2144220 | 1 |  | 2144220 | 2168323.5267 | Banosree | Grid Provided the Reading of 00:00 hour of 30.06.23 instead of 01.07.23 |  |  | Angur Jora | 2168323.5267 | 1879685.8324 | 288637.6942 | 15.3556 | OK
2 | Block F-G Avenue | 11 |  | 68 | 1 | 2777480 | 5519540 | 2742060 | 1 |  | 2742060 | 2772883.9436 | Banosree |  |  |  | Block F-G Avenue | 2772883.9436 | 2653782.5782 | 119101.3654 | 4.488 | OK
3 | Banasree Main Road(Monpura) | 11 |  | 168 | 1 | 2694560 | 4446260 | 1751700 | 1 |  | 1751700 | 1771391.1453 | Banosree |  |  |  | Banasree Main Road(Monpura) | 1771391.1453 | 1640446.1666 | 130944.9788 | 7.9823 | OK
4 | Baitul Kuddus | 11 |  | 62 | 1 | 5086120 | 7309220 | 2223100 | 1 |  | 2223100 | 2248090.2296 | Banosree |  |  |  | Baitul Kuddus | 2248090.2296 | 2090165.4312 | 157924.7984 | 7.5556 | OK
5 | Ideal | 11 |  |  | 1 | 6710680 | 7487660 | 776980 | 1 |  | 776980 | 785714.1589 | Banosree |  |  |  | Ideal | 785714.1589 | 730886.4987 | 54827.6602 | 7.5015 | OK
6 | Central Mosque | 11 |  | 46 | 1 | 5624400 | 7813780 | 2189380 | 1 |  | 2189380 | 2213991.1776 | Banosree |  |  |  | Central Mosque | 2213991.1776 | 2027033.5767 | 186957.6009 | 9.2232 | OK
7 | Larive | 11 |  | 47 | 1 | 7265440 | 8407420 | 1141980 | 1 |  | 1141980 | 1154817.1834 | Banosree |  |  |  | Larive | 1154817.1834 | 1075325.8802 | 79491.3032 | 7.3923 | OK
8 | Bank Colony | 11 |  |  | 1 | 3178720 | 3914160 | 735440 | 1 |  | 735440 | 743707.201 | Khilgaon |  |  |  | Bank Colony | 743707.201 | 684269.1356 | 59438.0653 | 8.6864 | OK
9 | Salambagh | 11 |  |  | 1 | 1440440 | 2367500 | 927060 | 1 |  | 927060 | 937481.2326 | Khilgaon |  |  |  | Salambagh | 937481.2326 | 1234217.735 | -296736.5024 | -24.0425 | OK
10 | Titas Road | 11 |  |  | 1 | 1526120 | 1963420 | 437300 | 1 |  | 437300 | 442215.7606 | Khilgaon |  |  |  | Titas Road | 442215.7606 | 461564.0031 | -19348.2425 | -4.1919 | OK
11 | AT-1 | 0.415 |  | 7734 | 1 | 3113.136 | 3257.088 | 143.952 | 1 |  | 143.952 | 145.5702 | Banosree |  |  |  | AT-1 | 145.5702 | 0 | 145.5702 | #DIV/0! | #DIV/0!
12 | AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15238761.1294 | 15069363.952 | 15238761.1294 | 1.1241
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 13115356.9352
[5 empty] | Khilgaon | at 33 KV level |  | 2123404.1942
[5 empty] | Total = |  |  | 15238761.1294 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADERTEK 33 KV SIDE
1 | Goran | 33 | Export | SIEM0510 | 1 | 339866 | 344806 | 4940 | 2000 | 0 | 9880000 | 9863663.5193
ULLON 33 KV SIDE
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 9880000 | 9863663.5193
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import | HA-030701133-03 | 1 | 88618525 | 98517711 | 9899186 | 1 | 9899186
2 | Ullon O/H | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
[7 empty] | 0 |  | Total | 9899186 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| GORAN 33 KV SIDE | [5 empty] | 0
1 | Transformer-01 | 33 | Export | HA-030800176-03 | 1 | 9395119 | 12308534 | 2913415 | 1 |  | 2913415
2 | Transformer-02 | 33 | Export | HA-030701133-03 | 1 | 75193098 | 78054579 | 2861481 | 1 |  | 2861481
3 | Transformer-03 | 33 | Export | DHK-57075 | 1 | 11429.52 | 11600.76 | 171.24 | 120000 |  | 4105104 |  |  | Problem
[9 empty] | Total |  | 9880000
| 33 KV IMPORT |  | KWH |  | 33 KV IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 9863663.5193 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9863663.5193
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 9863663.5193 |  | 33 KV TX HV SIDE |  | 9880000
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -16336.4807
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.1656%
| TOTAL IMPORT |  | 9863663.5193
11 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming | 11 | IMPORT |  | 1 | 50001787 | 52909528 | 2907741 | 1 | 2907741 |  | 2910138.0275
| 33/11 kV Transfomer-2 Incoming | 11 |  |  | 1 | 82735440 | 85589016 | 2853576 | 1 | 2853576 |  | 2855928.376
| 33/11 kV Transfomer-3 Incoming | 11 |  |  | 1 | 63563369 | 67657591 | 4094222 | 1 | 4094222 |  | 4097597.1158
[7 empty] | 0 |  | Total | 9855539 |  | 9863663.5193
| GORAN 11 KV SIDE | [5 empty] | 0
1 | Meradia | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estimated | 0 | 0 | Banosree |  |  |  | Meradia | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Shipahibagh | 11 |  | HA-021001030-02 | 1 | 35007828 | 36289191 | 1281363 | 1 |  | 1281363 | 1292900.8718 | Bashabo |  |  |  | Shipahibagh | 1292900.8718 | 1411235.5236 | -118334.6518 | -8.3852 | OK
3 | Farazi Hospital | 11 |  | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | Farazi Hospital | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | West Bansree | 11 |  | New Meter | 1 | 89182268 | 91131594 | 1949326 | 1 |  | 1949326 | 1966878.4605 | Banosree |  |  |  | West Bansree | 1966878.4605 | 1837316.4777 | 129561.9827 | 7.0517 | OK
5 | Model School(Nearest) | 11 |  | HA-030701099-03 | 1 | 12612480 | 15066081 | 2453601 | 1 |  | 2453601 | 2475694.1412 | Banosree |  |  |  | Model School(Nearest) | 2475694.1412 | 2316464.2537 | 159229.8875 | 6.8738 | OK
6 | Bhuiyan Para | 11 |  | HA-021100508-02 | 1 | 50569666 | 53101375 | 2531709 | 1 |  | 2531709 | 2554505.4549 | Banosree |  |  |  | Bhuiyan Para | 2554505.4549 | 2408712.741 | 145792.7139 | 6.0527 | OK
7 | Bonobithi (Ideal) School | 11 |  | HA-021100879-02 | 1 | 12579186 | 14133451 | 1554265 | 1 |  | 1554265 | 1568260.1835 | Banosree |  |  |  | Bonobithi (Ideal) School | 1568260.1835 | 1428642.8767 | 139617.3068 | 9.7727 | OK
8 | AT-01 | 0.415 |  | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 | 0.415 |  | 3043146 | 1 | 4637.2 | 4704.4 | 67.2 | 80 |  | 5376 | 5424.4075 | Banosree |  |  |  | AT-02 | 5424.4075 | 4669.3803 | 755.0272 | 16.1698 | OK
[9 empty] | Grand Total | 9863663.5193 | 9775640 | 9863663.5193 | 0.90044
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 8570762.6475
[5 empty] | Bashabo | at 33 KV level |  | 1292900.8718
[5 empty] | Total = |  |  | 9863663.5193 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV Sending SIDE
8 | Lalmatia Circuit-2 | 33 | 0 | SICAM | 1 | 58.14 | 82.53 | 24.39 | 1000 | Estimated | 15393240 | 15333258.5486
[9 empty] | Total |  | 15393240 | 15333258.5486
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import |  | 1 |  |  | 0 |  | 0
2 | Shatmasjid-2 | 33 | Import |  | 1 |  |  | 0 |  | 0
3 | Kallayanpur | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
[9 empty] | Total | 0 | 0 | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 15333258.5486 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALMATIA 33 KV NET IMPORT |  | 15333258.5486
| IMPORT-2 |  |  |  | LALMATIA 33 KV NET IMPORT |  |  | 15333258.5486 |  | LALMATIA 11 KV NET IMPORT |  | 15393240
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -59981.4514
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.3912%
| TOTAL IMPORT |  | 15333258.5486
11 KV SIDE of___LALMATIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | DHK000180 | 1 | 2647739 | 2720296 | 72557 | 90 | 6530130 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | DHK000177 | 1 | 2599626 | 2698105 | 98479 | 90 | 8863110 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 15393240 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1412510.4 | 1418643.1678 | Dhanmondi | Estimated |  |  | Shankor O/H | 1418643.1678 | 1399733.2864 | 18909.8814 | 1.351 | OK
2 | Bangabobondhu museum | 11 | Export |  | 1 | 627449 | 627449 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 76132438 | 78185685 | 2053247 | 1 |  | 2053247 | 2062161.6863 | Dhanmondi |  |  |  | Road No-13/A | 2062161.6863 | 2160918.3029 | -98756.6166 | -4.5701 | OK
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 96836903 | 99151250 | 2314347 | 1 |  | 2314347 | 2324395.3174 | Dhanmondi |  |  |  | Jaforabad | 2324395.3174 | 2181617.4346 | 142777.8827 | 6.5446 | OK
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25242.7 | 25444.9 | 202.2 | 3333.33 |  | 673999.326 | 676925.663 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 676925.663 | 643438.6457 | 33487.0173 | 5.2044 | OK
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 68865.4 | 69354.4 | 489 | 3333.33 |  | 1629998.37 | 1637075.4163 | Dhanmondi |  |  |  | Road No -15 | 1637075.4163 | 1478674.7103 | 158400.706 | 10.7123 | OK
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 76765.7 | 77227.8 | 462.1 | 3333.33 |  | 1540331.793 | 1547019.5294 | Dhanmondi |  |  |  | Road No-27 South | 1547019.5294 | 1459995.3095 | 87024.2199 | 5.9606 | OK
| Road 25 | 11 | Export |  | 1 | 69416.1 | 69810.6 | 394.5 | 3333.3 |  | 1314986.85 | 1320696.1949 | Dhanmondi |  |  |  | Road 25 | 1320696.1949 | 1108412.3257 | 212283.8692 | 19.1521 | OK
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37575.5 | 37703.6 | 128.1 | 3333.33 |  | 426999.573 | 428853.4986 | Dhanmondi |  |  |  | Ibne Sina | 428853.4986 | 403274.921 | 25578.5776 | 6.3427 | OK
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 57291365 | 59045605 | 1754240 | 1 |  | 1754240 | 1761856.4725 | Dhanmondi |  |  |  | Road No-31 (PARI) | 1761856.4725 | 924073.8841 | 837782.5884 | 90.6619 | FAULT
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 64955658 | 67161693 | 2206035 | 1 |  | 2206035 | 2215613.0537 | Dhanmondi |  |  |  | Satmoszid Road West | 2215613.0537 | 2070071.1797 | 145541.874 | 7.0308 | OK
[9 empty] | Grand Total | 15393240 | 15326695.312 | 15393240 | 0.43418
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Dhanmondi | at 33 KV level |  | 15393240
[5 empty] | Total = |  |  | 15393240 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2031.88 | 2059.78 | 27.9 | 240000 | 0 | 6696000 | 6698079.6916
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1347.73 | 1379.43 | 31.7 | 240000 | 0 | 7608000 | 7610362.9471
[9 empty] | Total | 0 | 14304000 | 14308442.6387
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 | 33 |  |  | 1 | 0 | 0 | 0 | 3000
[9 empty] | Total | 0 | 0 | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory | 33 | EXPORT | [7 empty] | 0
| Green Road Dormatory | 33 | [8 empty] | 0
Total
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0 | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 14308442.6387 |  | EXPORT TO OTHER S/S |  |  | 0 |  | Green Road 33 KV NET IMPORT |  | 14308442.6387
| IMPORT-2 |  |  |  | Green Road 33 KV NET IMPORT |  |  | 14308442.6387 |  | Green Road 11 KV NET IMPORT |  | 14308442.6387
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 14308442.6387 |  | LOSS UNITS=> |  | 0
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 14308442.6387
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 00138 | 1 | 2854577 | 2939427 | 84850 | 100 | 8485000
2 | Transfomer-2 Incoming | 11 | Import | HA-021101496 | 1 | 7981.2672 | 2649.9952 | -5331.272 | 10000 | 6696000
[7 empty] | 0 |  | Total | 15181000 |  | 14308442.6387
| Green Road 11 KV SIDE | [5 empty] | 0
1 | Lab aid/local RMU | 11 |  | 3C65883 | 1 | 48899 | 54004 | 5105 | 300 |  | 1531500 | 1536617.643 | Paribag |  |  |  | Lab aid/local RMU | 1536617.643 | 1422394.5672 | 114223.0759 | 8.0303 | OK
2 | Green View | 11 |  | DHK000151 | 1 | 66511.6 | 66871.1 | 359.5 | 3333.33 |  | 1198332.135 | 1202336.4681 | Paribag |  |  |  | Green View | 1202336.4681 | 1154869.3417 | 47467.1264 | 4.1102 | OK
3 | Central Road | 11 |  | 65943 | 1 | 9730 | 15582 | 5852 | 300 |  | 1755600 | 1761466.4931 | Paribag |  |  |  | Central Road | 1761466.4931 | 1692090.5953 | 69375.8978 | 4.1 | OK
4 | New Market | 11 |  | DHK000194 | 1 | 45899.3 | 46255.4 | 356.1 | 3333.33 |  | 1186998.813 | 1190965.2748 | Jigatola |  |  |  | New Market | 1190965.2748 | 1011316.673 | 179648.6018 | 17.7638 | OK
5 | DPH Feeder | 11 |  | HA-021100459 | 1 | 41350 | 41476.6 | 126.6 | 1 | 20 | 235418.4 | 236205.0715 | Paribag | Estimated |  |  | DPH Feeder | 236205.0715 | 247670.0176 | -11464.9462 | -4.6291 | OK
6 | Dhanmondi Rd 4(md Banglo | 11 |  | 6604464 | 1 | 4450.58 | 4476.72 | 26.14 | 60000 |  | 1568400 | 1573640.9477 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1573640.9477 | 1319464.1465 | 254176.8012 | 19.2636 | OK
1 | Green Road East | 11 |  | HA-021101050 | 1 | 92229088 | 93757224 | 1528136 | 1 |  | 1528136 | 1533242.4019 | Paribag |  |  |  | Green Road East | 1533242.4019 | 1471624.0188 | 61618.3831 | 4.1871 | OK
2 | North Road | 11 |  | HA-021100884 | 1 | 76809718 | 78525314 | 1715596 | 1 |  | 1715596 | 1721328.8161 | Paribag |  |  |  | North Road | 1721328.8161 | 1634915.8518 | 86412.9644 | 5.2855 | OK
3 | Green road SS | 11 |  | DHK00135 | 1 | 16023524 | 17244056 | 1220532 | 1 |  | 1220532 | 1224610.5159 | Paribag |  |  |  | Green road SS | 1224610.5159 | 1315498.6273 | -90888.1114 | -6.909 | OK
4 | Plane Moszid | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 80 | 941673.6 | 944820.2858 | Paribag | Estimated |  |  | Plane Moszid | 944820.2858 | 990680.0705 | -45859.7846 | -4.6291 | OK
5 | Malancha | 11 |  | HA-021100953 | 1 | 30602490 | 31976092 | 1373602 | 1 |  | 1373602 | 1378192.0129 | Paribag |  |  |  | Malancha | 1378192.0129 | 1148505.9825 | 229686.0304 | 19.9987 | OK
| AT -1 |  |  |  |  | 22891 | 22891 |  | 1 |  | 5000 | 5016.7079 | Paribag |  |  |  | AT -1 | 5016.7079 | 5090.5253 | -73.8173 | -1.4501 | OK
[9 empty] | Grand Total | 14308442.6387 | 14260788.948 | 14308442.6387 | 0.33416
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 11543836.4163
[5 empty] | Jigatola | at 33 KV level |  | 2764606.2224
[5 empty] | Total = |  |  | 14308442.6387 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory | 33 | 0 | 76026305 | 1 | 7993.99 | 8019.59 | 25.6 | 180000 | Reading From G. Dormitory Side | 9542110 | 9535149.4608
[9 empty] | Total | 0 | 9542110 | 9535149.4608
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 | 33 | 0 | 0 | 1 | 23.2 | 23.2 | 0 | 360000 | 0 | 0 | 0
9 | Green Road -2 | 33 | 0 | 0 | 1 | 9.84 | 23.22 | 13.38 | 360000 | 0 | 4816800 | 4813050.9871
[9 empty] | Total | 0 | 4816800 | 4813050.9871
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [9 empty] | 14358910 | 14348200.4478
1 | Mogbazar Grid | 33 | Import | BD 017064 | 1 | 14646.27 | 24188.38 | 9542.11 | 1000 | 9542110
2 | Green Road SS | 33 | Import | BD 017070 | 1 | 32911.2 | 32911.2 | 0 | 1000 | 0
3 | Jigatola Ckt-1 | 33 | Import |  | 1 | 8290.49 | 8292.49 | 2 | 1000 | 2000
NEW | Jigatola Ckt-2 | 33 |  |  | 1 | 3351.43 | 8339.09 | 4987.66 | 1000 | 4987660 |  |  |  | NEW FOUND
[7 empty] | 0 |  | Total | 14531770 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| GREEN ROAD DORMITORY 33 KV SIDE | [5 empty] | 0
1 | Transformer-01 | 33 | Export | BD 017065 | 1 | 97528.28 | 108288.53 | 10760.25 | 888.89 |  | 9564678.6225
2 | Transformer-02 | 33 | Export | BD 017069 | 1 | 88794.35 | 94422.74 | 5628.39 | 888.89 |  | 5003019.5871
[9 empty] | Total |  | 14567698.2096 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 14348200.4478 |  | EXPORT TO OTHER S/S |  |  | 0 |  | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 14348200.4478
[5 empty] | GREEN ROAD DORMITORY 33 KV NET IMPORT |  |  | 14348200.4478 |  | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 14567698.2096
[5 empty] | TOTAL EXPORT |  |  | 14348200.4478 |  | LOSS UNITS=> |  | -219497.7618
[5 empty] | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | -1.53%
| TOTAL IMPORT |  | 14348200.4478
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD 014050 | 1 | 63005.48 | 72549.81 | 9544.33 | 1000 | 9544330
2 | Transformer-02 Incoming | 11 | Import | BD 014059 | 1 | 66648.64 | 71630.36 | 4981.72 | 1000 | 4981720
[7 empty] | 0 |  | Total | 14526050 |  | 14567698.2096
| GREEN ROAD DORMITORY 11 KV SIDE | [5 empty] | 0
1 | North Dhanmondi | 11 |  | BD 014039 | 1 | 21702.59 | 21956.7 | 254.11 | 2000 |  | 508220 | 504079.3978 | Paribag |  |  |  | North Dhanmondi | 504079.3978 | 452285.2955 | 51794.1023 | 11.4516 | OK
2 | Lake circus | 11 |  | BD 014047 | 1 | 33605.68 | 34637.48 | 1031.8 | 2000 |  | 2063600 | 2046787.3073 | Paribag |  |  |  | Lake circus | 2046787.3073 | 1887308.9386 | 159478.3687 | 8.45 | OK
3 | Bashir Uddin | 11 |  | BD 014037 | 1 | 13668.5 | 14070.93 | 402.43 | 2000 |  | 804860 | 798302.5936 | Paribag |  |  |  | Bashir Uddin | 798302.5936 | 740604.9957 | 57697.5979 | 7.7906 | OK
4 | Raza Bazar | 11 |  | BD 013939 | 1 | 19945.29 | 20615.43 | 670.14 | 2000 |  | 1340280 | 1329360.3858 | Shere b.nagar |  |  |  | Raza Bazar | 1329360.3858 | 1277085.001 | 52275.3849 | 4.0933 | OK
5 | Rasel Squar | 11 |  | BD 013970 | 1 | 30409.89 | 31411.16 | 1001.27 | 2000 |  | 2002540 | 1986224.7792 | Shere b.nagar |  |  |  | Rasel Squar | 1986224.7792 | 1860400.7233 | 125824.0559 | 6.7633 | OK
6 | Bow Bazar | 11 |  | BD 013967 | 1 | 22875.2 | 23561.5 | 686.3 | 2000 |  | 1372600 | 1361417.0663 | Shere b.nagar |  |  |  | Bow Bazar | 1361417.0663 | 1195690.6937 | 165726.3726 | 13.8603 | OK
7 | BRB Hospital | 11 |  | BD 014003 | 1 | 12053.73 | 12424.41 | 370.68 | 2000 |  | 741360 | 735319.9448 | Shere b.nagar |  |  |  | BRB Hospital | 735319.9448 | 733624.2823 | 1695.6626 | 0.23114 | OK
8 | Green Road North | 11 |  | BD 013969 | 1 | 14142.63 | 14760.23 | 617.6 | 2000 |  | 1235200 | 1225136.5003 | Paribag |  |  |  | Green Road North | 1225136.5003 | 1163648.4072 | 61488.0931 | 5.2841 | OK
1 | Water Bhaban | 11 |  | BD 014004 | 1 | 4730.78 | 4898.2 | 167.42 | 2000 |  | 334840 | 332111.9703 | Shere b.nagar |  |  |  | Water Bhaban | 332111.9703 | 301428.8307 | 30683.1396 | 10.1792 | OK
2 | Alamin Road | 11 |  | BD 014006 | 1 | 17886.83 | 18211.68 | 324.85 | 2000 |  | 649700 | 644406.723 | Paribag |  |  |  | Alamin Road | 644406.723 | 578607.7993 | 65798.9237 | 11.3719 | OK
3 | Katal Bagan | 11 |  |  | 1 | 5394.19 | 6635.26 | 1241.07 | 2000 |  | 2482140 | 2461917.3517 | Paribag |  |  |  | Katal Bagan | 2461917.3517 | 1880307.9323 | 581609.4193 | 30.9316 | OK
4 | Eastern Pantho chaya | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan | 11 |  | BD 014005 | 1 | 5394.19 | 5575.77 | 181.58 | 2000 |  | 363160 | 360201.2398 | Paribag |  |  |  | Kalabagan | 360201.2398 | 320179.3518 | 40021.8881 | 12.4998 | OK
6 | Univer Hospital | 11 |  | BD 013963 | 1 | 606.64 | 745.38 | 138.74 | 2000 |  | 277480 | 275219.2974 | Paribag |  |  |  | Univer Hospital | 275219.2974 | 258266.1053 | 16953.192 | 6.5642 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 |  | BD 013971 | 1 | 9267.96 | 9523.65 | 255.69 | 2000 |  | 511380 | 507213.6524 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 507213.6524 | 520651.6433 | -13437.9909 | -2.581 | OK
[9 empty] | Grand Total | 14567698.2096 | 14687360 | 14567698.2096 | -0.81473
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 8823264.0632
[5 empty] | Shere b.nagar | at 33 KV level |  | 5744434.1464
[5 empty] | Total = |  |  | 14567698.2096 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
ULLON 33 KV SIDE
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1503.439 | 1533.8259 | 30.3869 | 240000 | Estimated | 7292856 | 7335965.7983
2 | Taltala-2 | 33 |  | BD001837 | 1 | 2463.334 | 2495.751 | 32.417 | 240000 | 0 | 7780080 | 7826069.8947
[9 empty] | Total | 0 | 15072936 | 15162035.693
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 | 0 | 0
| 33 KV Ullon-ckt-2 incoming | 33 |  |  | 1 |  |  | 0 | 1000 | 0 | 0
[9 empty] | Total | 0 | 0 | 15162035.693
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) | 33 | EXPORT | [7 empty] | 0
| 33 KV Khilgaon Feeder(Import) | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
[9 empty] | Total |  | 0 | 15162035.693 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 15162035.693 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TALTOLA 33 KV NET IMPORT |  | 15162035.693
| IMPORT-2 |  |  |  | TALTOLA 33 KV NET IMPORT |  |  | 15162035.693 |  | TALTOLA 11 KV NET IMPORT |  | 15162035.693
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 15162035.693 |  | LOSS UNITS=> |  | 0
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 15162035.693
11 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming | 11 | Import | 06604431 | 1 | 8463.21 | 8505.82 | 42.61 | 160000 | 6817600
2 | Transformer-02 Incoming | 11 | Import | 06604341 | 1 | 9170.65 | 9219.12 | 48.47 | 160000 | 7755200
3 | Transformer-03 Incoming | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
[7 empty] | 0 |  | Total | 14572800 |  | 15162035.693
| TALTOLA 11 KV SIDE | [5 empty] | 0
1 | Matir Masjid | 11 |  | DHK00170 | 1 | 17730 | 20154.5 | 2424.5 | 888.8889 |  | 2155111.1111 | 2177028.2382 | Khilgaon |  |  |  | Matir Masjid | 2177028.2382 | 2023352.6919 | 153675.5463 | 7.5951 | OK
2 | Hajipara | 11 |  | DHK-00108 | 1 | 1596.3 | 2631.3 | 1035 | 2222.2222 |  | 2300000 | 2323390.6234 | Khilgaon |  |  |  | Hajipara | 2323390.6234 | 1505682.5673 | 817708.0561 | 54.3081 | FAULT
3 | Nearest Feeder | 11 |  | DHK-00106 | 1 | 90788.1 | 90788.1 | 0 | 2222.222 |  | 0 | 0 | Bashabo |  |  |  | Nearest Feeder | 0 | 102528.7436 | -102528.7436 | -100 | CHECK
4 | Reazbagh | 11 |  | DHK-00109 | 1 | 94301.5 | 95125.7 | 824.2 | 2222.222 |  | 1831555.3724 | 1850181.9906 | Khilgaon |  |  |  | Reazbagh | 1850181.9906 | 1693614.7124 | 156567.2782 | 9.2446 | OK
5 | Chowdhury Para | 11 |  | DHK-00107 | 1 | 51884.4 | 52175.6 | 291.2 | 2222.222 |  | 647111.0464 | 653692.0598 | Khilgaon |  |  |  | Chowdhury Para | 653692.0598 | 575139.5465 | 78552.5133 | 13.658 | OK
6 | Model Colleg | 11 |  | 9122392 | 1 | 2456.34 | 2474.25 | 17.91 | 40000 |  | 716400 | 723685.6707 | Khilgaon |  |  |  | Model Colleg | 723685.6707 | 1038453.9207 | -314768.25 | -30.3112 | OK
1 | East Rampura | 11 |  | DHK-00181 | 1 | 97163 | 97687.4 | 524.4 | 2222.222 |  | 1165333.2168 | 1177184.4648 | Khilgaon |  |  |  | East Rampura | 1177184.4648 | 1381135.5698 | -203951.1051 | -14.7669 | OK
2 | Adarshabagh | 11 |  | DHK-00090 | 1 | 47488.7 | 48490.9 | 1002.2 | 2222.222 |  | 2227110.8884 | 2249760.2414 | Bashabo |  |  |  | Adarshabagh | 2249760.2414 | 2012766.0076 | 236994.2339 | 11.7746 | OK
3 | Khailgaon Govt Colony | 11 |  | DHK00167 | 1 | 73598.82 | 74331.4 | 732.58 | 2222.222 |  | 1627955.3928 | 1644511.4325 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1644511.4325 | 1548206.2687 | 96305.1638 | 6.2204 | OK
4 | TV Road | 11 |  | 6604434 | 1 | 4998.51 | 5034.04 | 35.53 | 40000 |  | 1421200 | 1435653.3713 | Khilgaon |  |  |  | TV Road | 1435653.3713 | 1278251.1059 | 157402.2653 | 12.3139 | OK
5 | Tilpa Para | 11 |  | 06604476 | 1 | 6526.36 | 6549.26 | 22.9 | 40000 |  | 916000 | 925315.57 | Bashabo |  |  |  | Tilpa Para | 925315.57 | 631719.4629 | 293596.1071 | 46.4757 | FAULT
1 | Navana | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 232625.2878 | -232625.2878 | -100 | CHECK
2 | AT-01 | 0.415 |  | 9187958 | 1 | 283.22 | 288.03 | 4.81 | 80 |  | 384.8 | 388.7134 | Bashabo |  |  |  | AT-01 | 388.7134 | 5004.1149 | -4615.4015 | -92.2321 | CHECK
3 | AT-02 | 0.415 |  | 9187959 | 1 | 0 | 123.08 | 123.08 | 10 |  | 1230.8 | 1243.317 | Bashabo |  |  |  | AT-02 | 1243.317 | 0 | 1243.317 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15162035.693 | 15009392.6279 | 15162035.693 | 1.017
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Khilgaon | at 33 KV level |  | 11985327.8512
[5 empty] | Bashabo | at 33 KV level |  | 3176707.8418
[5 empty] | Total = |  |  | 15162035.693 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 | 33 | Import | 35786569 | 1.001 | 1853.024 | 1885.528 | 32.504 | 180000 | 0 | 5856575.5761
2 | Sher-e-Banglanagar Ckt-02 | 33 | Import | 35786575 | 1.001 | 630.272 | 646.365 | 16.093 | 180000 | 0 | 2899639.1443
[9 empty] | Total | 0 | 8756214.7204 | 0
[9 empty] | Net Total | 8756214.7204
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
[9 empty] | Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 | 33 | Export | DHK 66500 | 1 | 696458 | 712641 | 16183 | 180 |  | 2912940
[9 empty] | Total |  | 2912940 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 8756214.7204 |  | EXPORT TO OTHER S/S |  |  | 0 |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 8756214.7204
| IMPORT-2 |  |  |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  |  | 8756214.7204 |  | 33 KV TX HV SIDE |  | 8756214.7204
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 8756214.7204
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 66503 | 1 | 2124390 | 2157894 | 33504 | 180 | 6030720 |  | 5896256.0143
2 | Transfomer-2 Incoming | 11 | Import | DHK 66495 | 1 | 678643 | 694894 | 16251 | 180 | 2925180 |  | 2859958.7061
[7 empty] | 0 |  | Total | 8955900 |  | 8756214.7204
| SHER-E-BANGLANAGAR 11 KV SIDE | [5 empty] | 0
1 | Sher-e-Banglanagar Local | 11 |  | DHK 66503 | 1 | 73849 | 76044 | 2195 | 60 |  | 131700 | 130259.0089 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 130259.0089 | 137740.1655 | -7481.1566 | -5.4314 | OK
2 | Mirpur Road East | 11 |  | DHK 60961 | 1 | 805750 | 815519 | 9769 | 60 |  | 586140 | 579726.769 | Shere b.nagar |  |  |  | Mirpur Road East | 579726.769 | 591320.8565 | -11594.0875 | -1.9607 | OK
3 | Gonobhaban school | 11 |  | DHK 66492 | 1 | 519667 | 523059 | 3392 | 60 |  | 203520 | 201293.1928 | Shere b.nagar |  |  |  | Gonobhaban school | 201293.1928 | 178100.36 | 23192.8328 | 13.0223 | OK
4 | Babor Road | 11 |  | DHK 66489 | 1 | 688132 | 727817 | 39685 | 60 |  | 2381100 | 2355047.2749 | Shyamoli |  |  |  | Babor Road | 2355047.2749 | 1531864.2685 | 823183.0064 | 53.7373 | FAULT
5 | College Gate | 11 |  | DHK 66487 | 1 | 2552998 | 2587196 | 34198 | 60 |  | 2051880 | 2029429.4244 | Shyamoli |  |  |  | College Gate | 2029429.4244 | 1693179.314 | 336250.1104 | 19.8591 | OK
6 | Parade ground | 11 |  | DHK 66490 | 1 | 938217 | 938247 | 30 | 60 |  | 1800 | 1780.3054 | Satmasjid |  |  |  | Parade ground | 1780.3054 | 0 | 1780.3054 | #DIV/0! | #DIV/0!
7 | Hospital RMU | 11 |  | DHK 66491 | 1 | 873509 | 882954 | 9445 | 60 |  | 566700 | 560499.4711 | Shere b.nagar |  |  |  | Hospital RMU | 560499.4711 | 544171.0965 | 16328.3746 | 3.0006 | OK
1 | Shamoly Square | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | 11 |  | DHK 60964 | 1 | 189395.3 | 191126.8 | 1731.5 | 60 |  | 103890 | 102753.2911 | Shere b.nagar |  |  |  | Gonobhaban RMU | 102753.2911 | 81921.1363 | 20832.1548 | 25.4295 | OK
3 | Krishi University | 11 |  | DHK 60963 | 1 | 330598.6 | 340100.1 | 9501.5 | 60 |  | 570090 | 563852.3796 | Shere b.nagar |  |  |  | Krishi University | 563852.3796 | 574020.0379 | -10167.6583 | -1.7713 | OK
4 | NEC | 11 |  | DHK 86073 | 1 | 25.3 | 29.93 | 4.63 | 60000 |  | 277800 | 274760.4607 | Shere b.nagar |  |  |  | NEC | 274760.4607 | 284784.5503 | -10024.0896 | -3.5199 | OK
5 | Novo Theater/Army Musium | 11 |  | DHK 86074 | 1 | 323.21 | 342.41 | 19.2 | 60000 |  | 1152000 | 1139395.431 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 1139395.431 | 1105819.0374 | 33576.3936 | 3.0363 | OK
6 | Netor | 11 |  | DHK 60962 | 1 | 92954.2 | 103402.9 | 10448.7 | 60 |  | 626922 | 620062.5542 | Shere b.nagar |  |  |  | Netor | 620062.5542 | 596532.4766 | 23530.0775 | 3.9445 | OK
7 | BICC | 11 |  |  | 1 | 26.67 | 29.93 | 3.26 | 60000 |  | 195600 | 193459.8492 | Shere b.nagar |  |  |  | BICC | 193459.8492 | 69152.9813 | 124306.8679 | 179.7563 | FAULT
8 | Auxiliary | 0.415 |  |  | 1 | 5090.45 | 5156.09 | 65.64 | 60 |  | 3938.4 | 3895.3081 | Shere b.nagar |  |  |  | Auxiliary | 3895.3081 | 5642.8833 | -1747.5751 | -30.9695 | OK
[9 empty] | Grand Total | 8756214.7204 | 8853080.4 | 8756214.7204 | -1.0941
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 3697714.4114 | Including 41% of Novo Theatre
[5 empty] | Shyamoli | at 33 KV level |  | 4384476.6993
[5 empty] | Satmasjid | at 33 KV level |  | 1780.3054
[5 empty] | Tejgaon | at 33 KV level |  | 672243.3043 | 59% of Novo Theatre
[5 empty] | Total = |  |  | 8756214.7204 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | Estimated | 9372512 | 9409882.1944
6 | 33kV Mugdapara Hospital-2 Feeder | 33 |  | ABB03918 | 1 | 288011 | 292711 | 4700 | 2000 | 0 | 9400000 | 9437479.7949
[9 empty] | Total | 0 | 18772512 | 18847361.9892
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 | 33 | Import | 38 | 1 | 271264128 | 280636640 | 9372512 | 1 | 9372512
2 | Maniknagor Incoming-02 | 33 | Import | 15 | 1 | 186357776 | 195727056 | 9369280 | 1 | 9369280
[7 empty] | 0 |  | Total | 18741792 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| MUGDAPARA HOSPITAL 33 KV SIDE | [5 empty] | 0
3 | Transformer-01 | 33 | Export | 16 | 1 | 259894444 | 269258400 | 9363956 | 1 |  | 9363956
4 | Transformer-02 | 33 | Export | 196 | 1 | 197611920 | 206984400 | 9372480 | 1 |  | 9372480
[9 empty] | Total |  | 18736436 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 18741792 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18741792
[5 empty] | 33 KV NET IMPORT |  |  | 18741792 |  | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 18736436
[10 empty] | LOSS UNITS=> |  | 5356
[10 empty] | LOSS % IN => |  | 0.02858%
| TOTAL IMPORT |  | 18741792
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | 192 | 1 | 257944528 | 267260736 | 9316208 | 1 | 9316208 |  | 9361554.7516
2 | Transformer-02 Incoming | 11 | Import | 118 | 1 | 196174496 | 205509296 | 9334800 | 1 | 9334800 |  | 9380237.2484
[7 empty] | 0 |  | Total | 18651008 |  | 18741792
| MUGDAPARA HOSPITAL 11 KV SIDE | [5 empty] | 0
1 | City Corporation | 11 |  | 93 | 1 | 38782904 | 39720584 | 937680 | 1 |  | 937680 | 951549.8845 | Bashabo |  |  |  | City Corporation | 951549.8845 | 660250.7383 | 291299.1463 | 44.1195 | FAULT
2 | Bot tola | 11 |  |  | 1 | 49052840 | 51317676 | 2264836 | 1 |  | 2264836 | 2298336.7826 | Maniknagar |  |  |  | Bot tola | 2298336.7826 | 2240795.0697 | 57541.7128 | 2.5679 | OK
3 | Jhilpar | 11 |  | 145 | 1 | 32593720 | 33590076 | 996356 | 1 |  | 996356 | 1011093.8025 | Mugdapara |  |  |  | Jhilpar | 1011093.8025 | 1160185.3486 | -149091.5461 | -12.8507 | OK
4 | Central Bashaboo | 11 |  | 128 | 1 | 34044596 | 35782472 | 1737876 | 1 |  | 1737876 | 1763582.1465 | Bashabo |  |  |  | Central Bashaboo | 1763582.1465 | 1733572.9987 | 30009.1477 | 1.7311 | OK
5 | Kadamtala | 11 |  | 8 | 1.5 | 17533438 | 17980396 | 446958 | 1 |  | 670437 | 680353.9053 | Mugdapara |  |  |  | Kadamtala | 680353.9053 | 1958904.8441 | -1278550.9388 | -65.2687 | CHECK
6 | Ansar VDP | 11 |  | 119 | 1 | 17300398 | 18412676 | 1112278 | 1 |  | 1112278 | 1128730.4864 | Khilgaon |  |  |  | Ansar VDP | 1128730.4864 | 727503.1317 | 401227.3546 | 55.1513 | FAULT
7 | Mugda Hospital Express-01 | 11 |  |  | 1 | 5309707 | 5599066 | 289359 | 1 |  | 289359 | 293639.1125 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 293639.1125 | 272764.3875 | 20874.7251 | 7.653 | OK
8 | Boro Masjid | 11 |  | 7 | 1.22 | 45410408 | 46545848 | 1135440 | 1 |  | 1385236.8 | 1405726.812 | Mugdapara |  |  |  | Boro Masjid | 1405726.812 | 1342757.2732 | 62969.5388 | 4.6896 | OK
1 | Anandodhara | 11 |  | 120 | 1 | 44960492 | 45910688 | 950196 | 1 |  | 950196 | 964251.0175 | Maniknagar |  |  |  | Anandodhara | 964251.0175 | 915566.0508 | 48684.9667 | 5.3175 | OK
2 | Culvert | 11 |  | 117 | 1 | 34952276 | 36749792 | 1797516 | 1 |  | 1797516 | 1824104.3237 | Bashabo |  |  |  | Culvert | 1824104.3237 | 1912589.1389 | -88484.8152 | -4.6264 | OK
3 | Mugda Hospital Express-02 | 11 |  | 97 | 1 | 4845548 | 4845548 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | 11 |  | 98 | 1 | 23101984 | 24721380 | 1619396 | 1 |  | 1619396 | 1643349.6255 | Bashabo |  |  |  | Jhor Pukur | 1643349.6255 | 1429146.8866 | 214202.7389 | 14.9882 | OK
5 | T&T | 11 |  | 99 | 1 | 22071346 | 22630184 | 558838 | 1 |  | 558838 | 567104.166 | Mugdapara |  |  |  | T&T | 567104.166 | 852556.8368 | -285452.6708 | -33.482 | OK
6 | Haider Ali | 11 |  | 9 | 1 | 62774928 | 64773440 | 1998512 | 1 |  | 1998512 | 2028073.3969 | Maniknagar |  |  |  | Haider Ali | 2028073.3969 | 1439434.5953 | 588638.8016 | 40.8938 | FAULT
| 11kv Tilpapara | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 2150000 | 2181802.1625 | Bashabo
7 | AT-01 | 11 |  |  | 1 | 2782 | 2875 | 93 | 1 |  | 93 | 94.3756 | Mugdapara |  |  |  | AT-01 | 94.3756 | 0 | 94.3756 | #DIV/0! | #DIV/0!
8 | AT-02 | 11 |  |  | 1 | 17 | 17 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-02 | 0 | 8.4563 | -8.4563 | -100 | CHECK
[9 empty] | Grand Total | 18741792 | 18468609.8 | 18741792 | 1.4792
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bashabo | at 33 KV level |  | 8364388.1427
[5 empty] | Maniknagar | at 33 KV level |  | 5290661.197
[5 empty] | Mugdapara | at 33 KV level |  | 3958012.174
[5 empty] | Khilgaon | at 33 KV level |  | 1128730.4864
[5 empty] | Total = |  |  | 18741792 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Taltola 33 KV SIDE
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.6699 | 61.9199 | 0.25 | 240000 | 0 | 60000 | 60354.6742
MANKNAGAR 33 KV SIDE
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 263791 | 267046 | 3255 | 2000 | 0 | 6510000 | 6535956.7515
[9 empty] | Total | 0 | 6570000 | 6596311.4257
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming | 33 |  |  | 1 | 55929 | 56486 | 557 | 270 |  | 150390
| 33 kV Maniknagor Incoming | 33 |  |  | 1.08 | 932297 | 968067 | 35770 | 180 |  | 6953688
[7 empty] | 0 |  | Total |  | 7104078
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| KHILGOAN 33 KV SIDE | [5 empty] | 0
3 | Transformer -01 | 33 | Export | DHK60982 | 1 | 805616 | 806471 | 855 | 180 |  | 153900
4 | Transformer -02 | 33 | Export | DHK60947 | 1 | 682617 | 718382 | 35765 | 180 |  | 6437700
[9 empty] | Total |  | 6591600 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 6596311.4257 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 6591600
[5 empty] | 33 KV NET IMPORT |  |  | 6591600 |  | 33 KV TX HV SIDE |  | 6591600
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6596311.4257
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | DHK60927 | 1 | 806409 | 807197 | 788 | 180 | 141840 |  | 148728.1182
2 | Transformer-02 Incoming | 11 | Import | DHK60928 | 1 | 845039 | 879175 | 34136 | 180 | 6144480 |  | 6442871.8818
[7 empty] | 0 |  | Total | 6286320 |  | 6591600
| KHILGOAN 11 KV SIDE | [5 empty] | 0
1 | Shantinagar s/s-1 | 11 |  | DHK60932 | 1 | 232427 | 277582 | 45155 | 60 |  | 2709300 | 2755360.6206 | Rajarbag |  |  |  | Shantinagar s/s-1 | 2755360.6206 | 2616486.0095 | 138874.6111 | 5.3077 | OK
2 | Gulbagh | 11 |  | DHK60934 | 1 | 111867 | 117195 | 5328 | 60 |  | 319680 | 325114.8574 | Rajarbag |  |  |  | Gulbagh | 325114.8574 | 314880.9114 | 10233.946 | 3.2501 | OK
3 | Rampura BTV | 11 |  | DHK60933 | 1 | 14053 | 14073 | 20 | 60 |  | 1200 | 1220.4011 | Khilgaon |  |  |  | Rampura BTV | 1220.4011 | 241.3343 | 979.0668 | 405.6891 | FAULT
4 | West Shantibag | 11 |  | DHK60926 | 1 | 490108 | 505382 | 15274 | 60 |  | 916440 | 932020.3326 | Rajarbag |  |  |  | West Shantibag | 932020.3326 | 912726.2746 | 19294.058 | 2.1139 | OK
1 | East Malibagh | 11 |  | DHK60929 | 1 | 537667 | 560235 | 22568 | 60 |  | 1354080 | 1377100.6198 | Rajarbag |  |  |  | East Malibagh | 1377100.6198 | 1289630.0978 | 87470.5219 | 6.7826 | OK
2 | Police Line | 11 |  | DHK60930 | 1 | 545249 | 555020 | 9771 | 60 |  | 586260 | 596226.9654 | Rajarbag |  |  |  | Police Line | 596226.9654 | 576125.2774 | 20101.688 | 3.4891 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 |  | DHK61017 | 1 | 187933 | 190385 | 2452 | 60 |  | 147120 | 149621.1769 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 149621.1769 | 146188.2445 | 3432.9323 | 2.3483 | OK
4 | Benjir Bagan | 11 |  | DHK60985 | 1 | 157675 | 160865 | 3190 | 60 |  | 191400 | 194653.9781 | Rajarbag |  |  |  | Benjir Bagan | 194653.9781 | 180699.0476 | 13954.9304 | 7.7227 | OK
5 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 830961 | 834990 | 4029 | 60 |  | 241740 | 245849.8049 | Switching |  |  |  | Shantinagar s/s-2 | 245849.8049 | 203082.8028 | 42767.0021 | 21.0589 | OK
6 | AT-1 & AT-2 | 0.415 |  | ELIB 7374 | 1 | 1628.18 | 1864.68 | 236.5 | 60 |  | 14190 | 14431.2432 | Rajarbag |  |  |  | AT-1 & AT-2 | 14431.2432 | 0 | 14431.2432 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 6591600 | 6481410 | 6591600 | 1.7001
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Rajarbag | at 33 KV level |  | 6380946.5633 | Including Switching
[5 empty] | Khilgaon | at 33 KV level |  | 1220.4011
[5 empty] | Moghbazar | at 33 KV level |  | 127666.1608
[5 empty] | Kakrail | at 33 KV level |  | 81766.8748
[5 empty] | Total = |  |  | 6591600 | 0
11 KV SIDE of___Santinagar Switching S/S | [13 empty] | Month June-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
From Source End
1 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 830961 | 834990 | 4029 | 60 |  | 241740 | 245849.8049 | 1.7001
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 35808 | 36416.7693 | Rajarbag
2 | 11 Fortune(MogBazar)-new | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 125532 | 127666.1608 | Moghbazar
3 | Centerpoint-Kakrail | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 80400 | 81766.8748 | Kakrail
[11 empty] | 241740 | 245849.8049 | 1.7001
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 | 33 | Import |  | 1 | 990.553 | 1026.085 | 35.532 | 180000 | 0 | 6402161.0685
2 | Sherebangla to Monipuripara-2 | 33 | Import |  | 1 | 716.372 | 741.116 | 24.744 | 180000 | 0 | 4458377.6168
[9 empty] | Total | 0 | 10860538.6852 | 0
[9 empty] | Net Total | 10860538.6852
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | BD017103 | 1 | 18652.7 | 24341.45 | 5688.75 | 1000 | 5688750
2 | Agargaon Ckt-02 | 33 | Import | BD017104 | 1 | 14516.91 | 18474.38 | 3957.47 | 1000 | 3957470
[7 empty] | 0 |  | Total | 9646220 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| MONIPURIPARA 33 KV SIDE | [5 empty] | 0
3 | Transformer-01 | 33 | Export | BD017102 | 1 | 78812.11 | 85228.28 | 6416.17 | 888.8889 |  | 5703262.2935
4 | Transformer-02 | 33 | Export | BD017105 | 1 | 29326.38 | 33794.26 | 4467.88 | 888.8889 |  | 3971448.9385
[9 empty] | Total |  | 9674711.232 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 10860538.6852 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10860538.6852
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 10860538.6852 |  | 33 KV TX HV SIDE |  | 9674711.232
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 1185827.4532
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 10.92%
| TOTAL IMPORT |  | 10860538.6852
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD014058 | 1 | 78157.18 | 84552.88 | 6395.7 | 1000 | 6395700 |  | 6409177.8947
2 | Transformer -02 Incoming | 11 | Import | BD014062 | 1 | 28475.48 | 32917.48 | 4442 | 1000 | 4442000 |  | 4451360.7906
[7 empty] | 0 |  | Total | 10837700 | 0 | 10860538.6852
| MONIPURIPARA 11 KV SIDE | [5 empty] | 0
1 | Spare | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | 11 |  | BD013947 | 1 | 28604.46 | 29462.81 | 858.35 | 1000 |  | 858350 | 886112.5599 | Shere b.nagar |  |  |  | Monipuripara west | 886112.5599 | 873090.4062 | 13022.1537 | 1.4915 | OK
3 | Biggan College | 11 |  | BD013949 | 1 | 16491.07 | 17308.18 | 817.11 | 1000 |  | 817110 | 843538.6891 | Kakrail |  |  |  | Biggan College | 843538.6891 | 853994.1863 | -10455.4972 | -1.2243 | OK
4 | Green Road South | 11 |  | BD013948 | 1 | 26639.32 | 27673.13 | 1033.81 | 1000 |  | 1033810 | 1067247.656 | Shere b.nagar |  |  |  | Green Road South | 1067247.656 | 986346.7996 | 80900.8564 | 8.2021 | OK
5 | BARC Building O/H | 11 |  | BD014010 | 1 | 11567.27 | 12194.37 | 627.1 | 1000 |  | 627100 | 647382.9863 | Shere b.nagar |  |  |  | BARC Building O/H | 647382.9863 | 632910.7169 | 14472.2694 | 2.2866 | OK
6 | Green Road North | 11 |  | BD014036 | 1 | 53150.66 | 55063.73 | 1913.07 | 1000 |  | 1913070 | 1974946.5311 | Shere b.nagar |  |  |  | Green Road North | 1974946.5311 | 1871294.3358 | 103652.1953 | 5.5391 | OK
7 | Chundrima Uddan | 11 |  | BD014035 | 1 | 26974.49 | 28003.9 | 1029.41 | 1000 |  | 1029410 | 1062705.342 | Shere b.nagar |  |  |  | Chundrima Uddan | 1062705.342 | 1015615.1889 | 47090.1531 | 4.6366 | OK
8 | RMU-1 Feeder | 11 |  | BD013940 | 1 | 0 | 146.76 | 146.76 | 1000 |  | 146760 | 151506.8204 | Shere b.nagar |  |  |  | RMU-1 Feeder | 151506.8204 | 0 | 151506.8204 | #DIV/0! | #DIV/0!
1 | Spare-03 | 11 |  | BD013946 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-03 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | 11 |  | BD013964 | 1 | 40112.39 | 40142.51 | 30.12 | 1000 |  | 30120 | 31094.2044 | Kakrail |  |  |  | kawran Bazar North | 31094.2044 | 0 | 31094.2044 | #DIV/0! | #DIV/0!
3 | NAM Bhanan RMU | 11 |  | BD013950 | 1 | 13253.69 | 14281.17 | 1027.48 | 1000 |  | 1027480 | 1060712.9179 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 1060712.9179 | 1013545.3917 | 47167.5262 | 4.6537 | OK
4 | Novo Theater | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | 11 |  | BD013962 | 1 | 35872.57 | 36592.1 | 719.53 | 1000 |  | 719530 | 742802.5517 | Tejgaon |  |  |  | Monipuripara Nearest | 742802.5517 | 733061.8614 | 9740.6903 | 1.3288 | OK
6 | Holy Cross | 11 |  | BD013965 | 1 | 33881.78 | 35046.94 | 1165.16 | 1000 |  | 1165160 | 1202846.0538 | Tejgaon |  |  |  | Holy Cross | 1202846.0538 | 1126874.592 | 75971.4618 | 6.7418 | OK
7 | Honda Goli | 11 |  | BD014011 | 1 | 11371.49 | 12339.97 | 968.48 | 1000 |  | 968480 | 999804.6158 | Tejgaon |  |  |  | Honda Goli | 999804.6158 | 953126.0337 | 46678.5822 | 4.8974 | OK
8 | Navy Quarter | 11 |  | BD013941 | 1 | 4780.31 | 4964.2 | 183.89 | 1000 |  | 183890 | 189837.7569 | Tejgaon |  |  |  | Navy Quarter | 189837.7569 | 175339.91 | 14497.8469 | 8.2684 | OK
9 | AT-01 | 0.415 |  |  | 1 | 1762.39 | 1834.42 | 72.03 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 585.48 | 585.48 | 0 | 1 |  | 0 | 0 | Shere b.nagar |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10860538.6852 | 10520270 | 10860538.6852 | 3.2344
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 6850614.8135
[5 empty] | Kakrail | at 33 KV level |  | 874632.8935
[5 empty] | Tejgaon | at 33 KV level |  | 3135290.9782
[5 empty] | Total = |  |  | 10860538.6852 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Mogbazar 33 KV SIDE
11 | Ispahani-1 | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 | 33 | 0 | 0 | 1 | 3791.06 | 3824.35 | 33.29 | 180000 | 0 | 5992200 | 5987828.9601
[9 empty] | Total | 0 | 5992200 | 5987828.9601
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 | 33 | Import |  | 1 | 14271.41 | 20256.66 | 5985.25 | 1000 | 5985250
[7 empty] | 0 |  | Total | 5985250 | 0 | 0
| Ispahani 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| Ispahani 33 KV SIDE | [5 empty] | 0
3 | Transformer-01 | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 | 33 | Export |  | 1 | 10392.07 | 17125.58 | 6733.51 | 888.8889 |  | 5985342.297
[9 empty] | Total |  | 5985342.297 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 5987828.9601 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 5987828.9601
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 5987828.9601 |  | 33 KV TX HV SIDE |  | 5985342.297
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 2486.6631
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.04153%
| TOTAL IMPORT |  | 5987828.9601
11 KV SIDE of___ Ispahani 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 44929 | 44929 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming | 11 | Import |  | 1 | 2991.27 | 4941.97 | 1950.7 | 1000 | 1950700 |  | 5987828.9601
[7 empty] | 0 |  | Total | 1950700 | 0 | 5987828.9601
| Ispahani 11 KV SIDE | [5 empty] | 0
1 | Doctor Goli | 11 |  | BD013944 | 1 | 5839.76 | 6792.09 | 952.33 | 1000 |  | 952330 | 958270.3835 | Moghbazar |  |  |  | Doctor Goli | 958270.3835 | 898591.0283 | 59679.3552 | 6.6414 | OK
2 | Ispahani | 11 |  | BD013947 | 1 | 6529.14 | 7580.78 | 1051.64 | 1000 |  | 1051640 | 1058199.8531 | Moghbazar |  |  |  | Ispahani | 1058199.8531 | 999582.0108 | 58617.8422 | 5.8642 | OK
3 | BTCL | 11 |  | BD013949 | 1 | 3442.04 | 3962.52 | 520.48 | 1000 |  | 520480 | 523726.617 | Kakrail |  |  |  | BTCL | 523726.617 | 532492.3633 | -8765.7463 | -1.6462 | OK
4 | Vikarunnesa | 11 |  | BD013948 | 1 | 2973.78 | 4102.97 | 1129.19 | 1000 |  | 1129190 | 1136233.5895 | Kakrail |  |  |  | Vikarunnesa | 1136233.5895 | 1092064.7445 | 44168.845 | 4.0445 | OK
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | 11 |  |  | 1 | 4695.65 | 5737.24 | 1041.59 | 1000 |  | 1041590 | 1048087.1638 | Moghbazar |  |  |  | Wireless | 1048087.1638 | 896344.5253 | 151742.6385 | 16.9291 | OK
2 | Kazir Goli | 11 |  |  | 1 | 3648.07 | 4903.55 | 1255.48 | 1000 |  | 1255480 | 1263311.3532 | Kakrail |  |  |  | Kazir Goli | 1263311.3532 | 1182067.1763 | 81244.177 | 6.8731 | OK
3 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 5987828.9601 | 5950710 | 5987828.9601 | 0.62377
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 3064557.4003
[5 empty] | Kakrail | at 33 KV level |  | 2923271.5598
[5 empty] | Total = |  |  | 5987828.9601 | 0
Note on I443: User: Direct Difference by Grd 1902.747

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 | 132 | IMPORT | 8993683 | 1 | 8261.732 | 8298.965 | 37.233 | 960000 | 0 | 35743680
| XFR- T2 | 132 |  | 8993682 | 1 | 8252.57 | 8289.656 | 37.086 | 960000 | 0 | 35602560
[9 empty] | Total | 0 | 71346240
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** | 132 | P. Cell | 08993685 | 1 | 8261.725 | 8298.952 | 37.227 | 960000 | 35737920
| 132/33 kV Transformer-2(HV) ** | 132 | P. Cell | 08993684 | 1 | 8252.56 | 8289.645 | 37.085 | 960000 | 35601600
[9 empty] | Total | 71339520
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 71346240 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 71346240
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 71346240 |  | 33 KV NET IMPORT |  | 71561760
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 71346240 |  | LOSS UNITS=>(132 HV-33 LV) |  | -215520
| IMPORT-4 |  |  |  | Loss Units=> (132 IMP-132 EXP) |  |  | 0 |  | LOSS % IN => |  | -0.3021%
| 132 KV TOTAL IMPORT |  | 71346240 |  | 132 KV NET LOSS => |  |  | 0%
| 33 KV GT INCOMING-NOCS |  | 71561760
| Loss Units=> (132 IMP-33 IMP) |  | -215520
| LOSS % IN => |  | -0.3021%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | IMPORT
3 | 132/33 kV Transformer, T-1 (LV) | 33 | PGCB | J2002016494 | 1 | 21360.979 | 21608.775 | 247.796 | 144000 | 35682624
4 | 132/33 kV Transformer, T-2 (LV) | 33 | PGCB | J2002016859 | 1 | 31340.717 | 31587.816 | 247.099 | 144000 | 35582256
| DPDC |  |  |  |  | 0 | 0 |  | Total | 71264880
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | DPDC | 07389553 | 1 | 1453.21 | 1527.81 | 74.6 | 480000 | 35808000
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | DPDC | 07389485 | 1.038 | 854.94 | 925.57 | 70.63 | 480000 | 35190691.2
| P.Cell |  |  |  |  | 0 | 0 |  | Total | 70998691.2
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | P.Cell | 08993674 | 1 | 10718.396 | 10793.03 | 74.634 | 480000 | 35824320
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | P.Cell | 8993667 | 1 | 10628.551 | 10703.004 | 74.453 | 480000 | 35737440
[9 empty] | Total | 71561760
MOGBAZAR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 33 | DPDC | 07389555 | 1 | 5578.69 | 5606.73 | 28.04 | 240000 |  | 6729600 | 6742821.4846 |  | 14221485.8274 | Siddhirganj 33/11 kv ss | 1.2405 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 6742821.4846 | 6486018.3466 | 256803.1381 | 3.9593 | OK
|  | 33 | P.Cell | 08993675 | 1 | 4935.315 | 4963.364 | 28.049 | 240000 |  | 6731760 | 6744985.7283 |  |  |  |  | 0 | 6744985.7283 | 6484343.6093 | 260642.1191 | 4.0196 | OK
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 33 | DPDC | 07389487 | 1 | 5744.3 | 5775.4 | 31.1 | 240000 |  | 7464000 | 7478664.3428 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 7478664.3428 | 7636802.1255 | -158137.7827 | -2.0707 | OK
|  | 33 | P.Cell | 08993666 | 1 | 5008.477 | 5039.611 | 31.134 | 240000 |  | 7472160 | 7486840.3746 |  |  |  |  | 0 | 7486840.3746 | 7638476.8628 | -151636.4882 | -1.9852 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 14193600 | 14221485.8274 |  |  |  |  | 33 KV Feeders | 14221485.8274 | 14122820.4721 | 98665.3554 | 0.69862 | OK
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4155.568 | 4197.894 | 42.326 | 240000 |  | 10158240 | 10178197.6519 |  | 18784673.4342 | Sarulia 33/11 kv ss |  | 33 kV Sarulia-1 Feeder | 10178197.6519 | 9992439.7736 | 185757.8783 | 1.859 | OK
|  | 33 | P.Cell | 08993679 | 1 | 4156.359 | 4198.71 | 42.351 | 240000 |  | 10164240 | 10184209.4399 |  |  |  |  | 0 | 10184209.4399 | 9988851.0508 | 195358.3891 | 1.9558 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss |  | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6047.67 | 6094.16 | 46.49 | 240000 |  | 11157600 | 11179521.0706 |  |  |  |  | 33 kV Demra-1 Feeder | 11179521.0706 | 12273431.9874 | -1093910.9168 | -8.9128 | OK
|  | 33 | P.Cell | 08993676 | 1 | 5693.208 | 5739.735 | 46.527 | 240000 |  | 11166480 | 11188418.517 |  |  |  |  | 0 | 11188418.517 | 12271039.5055 | -1082620.9886 | -8.8226 | OK
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5523.57 | 5573.43 | 49.86 | 240000 |  | 11966400 | 11989910.1007 |  | 23169431.1714 | Demra 33/11 kv ss |  | 33 kV Demra-2 Feeder | 11989910.1007 | 10373801.3835 | 1616108.7172 | 15.5788 | OK
|  | 33 | P.Cell | 08993665 | 1 | 5231.773 | 5281.677 | 49.904 | 240000 |  | 11976960 | 12000490.8477 |  |  |  |  | 0 | 12000490.8477 | 10367820.1788 | 1632670.6689 | 15.7475 | OK
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4469.84 | 4500.27 | 30.43 | 240000 |  | 7303200 | 7317548.4229 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 7317548.4229 | 5615154.9463 | 1702393.4766 | 30.3178 | OK
|  | 33 | P.Cell | 08993678 | 1 | 3715.504 | 3745.951 | 30.447 | 240000 |  | 7307280 | 7321636.4388 |  |  |  |  | 0 | 7321636.4388 | 5612283.968 | 1709352.4707 | 30.4573 | OK
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3886.4 | 3922.19 | 35.79 | 240000 |  | 8589600 | 8606475.7823 |  |  |  |  | 33 kV Sarulia-2 Feeder | 8606475.7823 | 8163148.1367 | 443327.6456 | 5.4308 | OK
|  | 33 | P.Cell | 08993663 | 1 | 3608.278 | 3644.087 | 35.809 | 240000 |  | 8594160 | 8611044.7412 |  |  |  |  | 0 | 8611044.7412 | 8171282.575 | 439762.1662 | 5.3818 | OK
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 353746.5 | 357772.9 | 4026.4 | 2000 |  | 8052800 | 8068621.1441 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 8068621.1441 | 8850787.3005 | -782166.1563 | -8.8372 | OK
[9 empty] | Total | 71561760 | 71421440 | 71561760 | 0.19647
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 15386169.567
[5 empty] | Total = |  |  | 15386169.567 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | IMPORT
8 | 33/11 kV Transformer-1 Incoming | 11 | New | XA587379 | 1 | 665827.4 | 672550.3 | 6722.9 | 1000 | 6722900 |  | 6767385.8345
9 | 33/11 kV Transformer-2 Incoming | 11 | New | DHKA9985 | 1 | 292971.1 | 300376.2 | 7405.1 | 1000 | 7405100 |  | 7454099.993
[7 empty] | 0 |  | Total | 14128000 |  | 14221485.8274
| SIDDHIRGANJ 11 kV SIDE |  | EXPORT |  |  |  | 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 207823.5 | 210341.9 | 2518.4 | 1000 |  | 2518400 | 2549641.8301 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 2549641.8301 | 2438789.3271 | 110852.5031 | 4.5454 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16587.7 | 16731.5 | 143.8 | 1000 |  | 143800 | 145583.9006 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 145583.9006 | 138711.8093 | 6872.0913 | 4.9542 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 105223.6 | 106740.6 | 1517 | 1000 |  | 1517000 | 1535819.0344 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1535819.0344 | 1523513.0022 | 12306.0323 | 0.80774 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 164769.1 | 167267.3 | 2498.2 | 1000 |  | 2498200 | 2529191.2405 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2529191.2405 | 2405949.7847 | 123241.4558 | 5.1224 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6907.4 | 6948.3 | 40.9 | 1000 |  | 40900 | 41407.382 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 41407.382 | 36566.7297 | 4840.6523 | 13.2379 | OK
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 71952.3 | 73247.9 | 1295.6 | 1000 |  | 1295600 | 1311672.4727 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1311672.4727 | 1337959.5143 | -26287.0417 | -1.9647 | OK
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 141739.7 | 144040.1 | 2300.4 | 1000 |  | 2300400 | 2328937.4468 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 2328937.4468 | 2238024.8856 | 90912.5613 | 4.0622 | OK
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 64.2821 | 71.4752 | 7.1931 | 40000 |  | 287724 | 291293.3394 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 291293.3394 | 424399.7103 | -133106.3709 | -31.3634 | OK
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 12873.4 | 13546.5 | 673.1 | 1000 |  | 673100 | 681450.0937 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 681450.0937 | 758130.0486 | -76679.9549 | -10.1144 | OK
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 140787.7 | 143559.8 | 2772.1 | 1000 |  | 2772100 | 2806489.0873 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2806489.0873 | 2820775.6603 | -14286.5731 | -0.50648 | OK
[9 empty] | Total | 14221485.8274 | 14047224 | 14221485.8274 | 1.2405
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 13930192.4881
[5 empty] | Matuail | at 33 KV level |  | 291293.3394
[5 empty] | Total = |  |  | 14221485.8274 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6047.67 | 6094.16 | 46.49 | 240000 | 0 | 11157600 | 11179521.0706
0 | 0 | 33 | P.Cell | 08993676 | 1 | 5693.208 | 5739.735 | 46.527 | 240000 | 0 | 11166480 | 11188418.517
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5523.57 | 5573.43 | 49.86 | 240000 | 0 | 11966400 | 11989910.1007
0 | 0 | 33 | P.Cell | 08993665 | 1 | 5231.773 | 5281.677 | 49.904 | 240000 | 0 | 11976960 | 12000490.8477
[9 empty] | Total | 0 | 23124000 | 23169431.1714
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 | 33 | Digital | DHK60885 | 3 | 270310.8 | 292407.2 | 22096.4 | 240 | 15909408
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
[7 empty] | 0 |  | Total | 15909408 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1006.87 | 1008.73 | 1.86 | 240000 |  | 446400 |  | Siddirgonj
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 446400
0
| DEMRA 33 KV SIDE | [5 empty] | 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60886 | 1 | 645996.4 | 690613.3 | 44616.9 | 240 |  | 10708056
8 | 33/11 kV, 10/14 MVA T-2 (HV) | 33 | Digital | 05002303 | 1 |  | 0 |  | 240 |  | 0
9 | 33/11 kV, 20/28 MVA T-3 (HV) | 33 |  |  | 1 |  | 0 |  | 180 |  | 0
[9 empty] | Total |  | 10708056 | 0
[5 empty] | 33 KV Export-Import |  |  | KWH
[5 empty] | Total Import |  |  | 23169431.1714
[5 empty] | Siddirgonj NOCS |  |  | 446400
[5 empty] | Net Import to Demra 33/11 KV SS |  |  | 22723031.1714
11 KV SIDE of___DEMRA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK60881 | 1 | 166670.6 | 225987.3 | 59316.7 | 180 | 10677006 |  | 11185260.617
19 | 33/11 kV, 20/28 MVA T-3 Incoming. | 11 |  | DHK60925 | 1 | 589350.8 | 650536.9 | 61186.1 | 180 | 11013498 |  | 11537770.5543
[7 empty] | 0 |  | Total | 21690504 |  | 22723031.1714
| DEMRA 11 KV SIDE | [5 empty] | 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 |  | HA021101013-02 | 1 | 41495960 | 43772221 | 2276261 | 1 |  | 2276261 | 2312393.5546 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2312393.5546 | 2206583.7096 | 105809.845 | 4.7952 | OK
12 | 11 kV DND (WASA) Feeder. | 11 |  | HA021100992-02 | 1 | 5288520 | 5367438 | 78918 | 1 |  | 78918 | 80170.7162 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 80170.7162 | 6927.7253 | 73242.9908 | 1057.2444 | FAULT
13 | 11 kV Local Feeder | 11 |  | HA021100794-02 | 1 | 6636120 | 8692106 | 2055986 | 1 |  | 2055986 | 2088621.9879 | Siddirgonj |  |  |  | 11 kV Local Feeder | 2088621.9879 | 1417684.9395 | 670937.0484 | 47.3262 | FAULT
14 | 11 kV Mouchak Feeder | 11 |  | DHK60888 | 1 | 817710.4 | 855586.5 | 37876.1 | 60 |  | 2272566 | 2308639.9015 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2308639.9015 | 2074135.4747 | 234504.4268 | 11.3061 | OK
15 | 11 kV Overhead-1 Feeder | 11 |  | HA021100829-02 | 1 | 75894360 | 76972401 | 1078041 | 1 |  | 1078041 | 1095153.438 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 1095153.438 | 1095304.9401 | -151.5021 | -0.013832 | OK
16 | 11 kV Provati Steel Feeder | 11 |  | DHK60874 | 1 | 544937.6 | 544937.6 | 0 | 60 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Islambagh Feeder. | 11 |  | DHKA2190 | 1 | 950.6676 | 999.9264 | 49.2588 | 60000 |  | 2955528 | 3002442.9965 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 3002442.9965 | 2983539.0327 | 18903.9638 | 0.63361 | OK
20 | 11 kV Taj Jute Feeder. | 11 |  | DHK61062 | 1 | 563396.8 | 590904.5 | 27507.7 | 60 |  | 1650462 | 1676660.8446 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1676660.8446 | 1675376.4941 | 1284.3505 | 0.07666 | OK
21 | 11 kV Al-Aksa Steel Feeder | 11 |  | DHK61061 | 1 | 708770.6 | 732963.2 | 24192.6 | 60 |  | 1451556 | 1474597.4818 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1474597.4818 | 1597579.1906 | -122981.7088 | -7.698 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 |  | DHKA2189 | 1 | 905.2486 | 945.7312 | 40.4826 | 60000 |  | 2428956 | 2467512.3805 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2467512.3805 | 2370283.5934 | 97228.7871 | 4.102 | OK
23 | 11 kV Over Head Feeder-2. | 11 |  | HA021100488-02 | 1 | 22702980 | 24800709 | 2097729 | 1 |  | 2097729 | 2131027.6013 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 2131027.6013 | 2071443.4949 | 59584.1064 | 2.8765 | OK
24 | 11 kV Shimrail Express Feeder. | 11 |  | HA021100511-02 | 1 | 8067222 | 8095991 | 28769 | 1 |  | 28769 | 29225.6688 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 29225.6688 | 0 | 29225.6688 | #DIV/0! | #DIV/0!
25 | 11 kV Sarder & Khadem Steel Feeder | 11 |  | HA021100413-02 | 1 | 79767340 | 80407905 | 640565 | 1 |  | 640565 | 650733.1002 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 650733.1002 | 409613.9007 | 241119.1995 | 58.865 | FAULT
26 | 11 kV Siddhirgonj Mazar Feeder | 11 |  | HA021100393-02 | 1 | 21884266 | 22161663 | 277397 | 1 |  | 277397 | 281800.301 | Siddirgonj | New Meter |  |  | 11 kV Siddhirgonj Mazar Feeder | 281800.301 | 832832.3648 | -551032.0638 | -66.1636 | CHECK
27 | 11 kV AST Beverage Feeder | 11 |  |  | 1 | 19198420 | 20233737 | 1035317 | 1 |  | 1035317 | 1051751.2525 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 1051751.2525 | 1163750.6238 | -111999.3713 | -9.624 | OK
28 | 11 kV Karim Market Feeder | 11 |  |  | 1 | 53529387 | 53935137 | 405750 | 1 | Previous Meter Details Below | 2039919 | 2072299.946 | Matuail | New Meter |  |  | 11 kV Karim Market Feeder | 2072299.946 | 2089377.8867 | -17077.9407 | -0.81737 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 22723031.1714 | 22367970 | 22723031.1714 | 1.5874
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 7387136.4971
[5 empty] | Demra | at 33 KV level |  | 2781760.7015
[5 empty] | Siddirgonj | at 33 KV level |  | 12554133.9728
[5 empty] | Total = |  |  | 22723031.1714 | 0
| Feeder Name | CF | Previous | Closing | OMF | Consumption
| 11 kV Karim Market Feeder | 1 | 52656280 | 54290449 | 1 | 1634169
33 KV SIDE of___ SARULIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4155.568 | 4197.894 | 42.326 | 240000 | 0 | 10158240 | 10178197.6519
0 | 0 | 33 | P.Cell | 08993679 | 1 | 4156.359 | 4198.71 | 42.351 | 240000 | 0 | 10164240 | 10184209.4399
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3886.4 | 3922.19 | 35.79 | 240000 | 0 | 8589600 | 8606475.7823
| 0 | 33 | P.Cell | 08993663 | 1 | 3608.278 | 3644.087 | 35.809 | 240000 | 0 | 8594160 | 8611044.7412
[9 empty] | Total | 0 | 18747840 | 18784673.4342
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) | 33 |  | 30799103 | 1 | 4262.36 | 4297.89 | 35.53 | 240000 | 8527200
7 | 33 kV Siddhirgonj-1 Incoming (=L41) | 33 |  | 30799100 | 1 | 4177.23 | 4218.87 | 41.64 | 240000 | 9993600
[7 empty] | 0 |  | Total | 18520800 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| SARULIA 33 KV SIDE | [5 empty] | 0
4 | 33/11 kV Transformer-1 (=T31) | 33 |  | 30799099 | 1 | 4551.82 | 4598.9 | 47.08 | 180000 |  | 8474400
5 | 33/11 kV Transformer-2 (=T32) | 33 |  | 30799139 | 1 | 3966.18 | 3992.89 | 26.71 | 180000 |  | 4807800
6 | 33/11 kV Transformer-3 (=T33) | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 13282200 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 18784673.4342 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18784673.4342
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 18784673.4342 |  | 33 KV NET Receiving |  | 18520800
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 18784673.4342 |  | LOSS UNITS=> |  | 263873.4342
| IMPORT-4 |  |  |  | 132KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 1.405%
| TOTAL IMPORT |  | 18784673.4342
11 KV SIDE of___SARULIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) | 11 |  | 2007754972 | 1 | 9196.41 | 9249.26 | 52.85 | 160000 | 8456000 |  | 9363441.3762
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) | 11 |  | 30799500 | 1 | 8722.01 | 8762.37 | 40.36 | 80000 | 3228800 |  | 3575293.2256
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) | 11 |  | HA021100368-02 | 1 | 33058580 | 38337970 | 5279390 | 1 | 5279390 |  | 5845938.8324
[7 empty] | 0 |  | Total | 16964190 |  | 18784673.4342
| SARULIA 11 KV SIDE | [5 empty] | 0
8 | 11 kV Dayagonj Feeder (=L11) | 11 |  | 2007755114 | 1 | 5681.21 | 5723.87 | 42.66 | 60000 |  | 2559600 | 2648546.8605 | Demra | In May-23, substation Loss was -2.32%. That's why in June-23, substation loss is higher. |  |  | 11 kV Dayagonj Feeder (=L11) | 2648546.8605 | 3036942.6611 | -388395.8007 | -12.789 | OK
9 | 11 kV Karim Jute Feeder (=L12) | 11 |  | 30799484 | 1 | 20.9002 | 21.1189 | 0.2187 | 60000 |  | 13122 | 13577.9934 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 13577.9934 | 12817.0467 | 760.9467 | 5.937 | OK
11 | 11 kV Konapara (=L13) **** | 11 |  | DHKA2191 | 1 | 1949.7345 | 2005.823 | 56.0885 | 60000 |  | 3365310 | 3482255.5223 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 3482255.5223 | 2467003.1131 | 1015252.4092 | 41.1533 | FAULT
12 | 11 kV Sanarpar Feeder (=L14) | 11 |  | 575926 | 1 | 45987.8 | 48458.1 | 2470.3 | 1000 |  | 2470300 | 2556143.6589 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2556143.6589 | 2386518.0767 | 169625.5823 | 7.1077 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | 11 |  | 30799450 | 1 | 1800.14 | 1804.9 | 4.76 | 60000 |  | 285600 | 295524.6849 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 295524.6849 | 302404.9427 | -6880.2579 | -2.2752 | OK
14 | 11 kV Tengra Feeder (=L16) | 11 |  | 30799145 | 1 | 5390.98 | 5426.47 | 35.49 | 60000 |  | 2129400 | 2203397.2826 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 2203397.2826 | 3315319.3041 | -1111922.0215 | -33.5389 | OK
16 | 11 kV Police Line Feeder (=L17) | 11 |  | 30799480 | 1 | 3276.53 | 3297.43 | 20.9 | 60000 |  | 1254000 | 1297576.8726 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1297576.8726 | 1183247.2468 | 114329.6258 | 9.6624 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | 11 |  | 30799119 | 1 | 1621.73 | 1630.73 | 9 | 60000 |  | 540000 | 558765.1604 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 558765.1604 | 495803.4526 | 62961.7078 | 12.6989 | OK
18 | 11 kV Spare Feeder (=F9) | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | 11 |  | HA021100493-02 | 1 | 74707530 | 77608653 | 2901123 | 1 |  | 2901123 | 3001937.8862 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 3001937.8862 | 2753359.8865 | 248577.9996 | 9.0282 | OK
21 | 11 kV Baser Pool Feeder (=L11) | 11 |  | HA021100518-02 | 1 | 50715102 | 50867999 | 152897 | 1 |  | 152897 | 158210.2162 | Demra |  |  |  | 11 kV Baser Pool Feeder (=L11) | 158210.2162 | 30254.1689 | 127956.0473 | 422.9369 | FAULT
22 | 11 kV Dip-Pur Feeder (=L12) | 11 |  | HA021100697-02 | 1 | 18260443 | 20487902 | 2227459 | 1 |  | 2227459 | 2304863.862 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 2304863.862 | 2171918.011 | 132945.8511 | 6.1211 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 18520800 | 17898811 | 18520800 | 3.475
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Demra | at 33 KV level |  | 15964656.3411
[5 empty] | Matuail | at 33 KV level |  | 2556143.6589
[5 empty] | Total = |  |  | 18520800 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 92642.466 | 101599.843 | 8957.377 | 1000 | 0 | 8957377 | 8965472.3475
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 335.3629 | 370.6713 | 35.3084 | 240000 | 0 | 8474016 | 8481674.5037
| Siddhirganj 33 KV SIDE | [7 empty] | Total |  | 17431393 | 17447146.8512
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) | 33 |  | 84663042 | 1 | 342.79 | 378.07 | 35.28 | 240000 | 8467200
6 | 33 kV Shitalakhya-2 Feeder (Old) | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 8474016 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
[7 empty] | 0 |  | Total | 16941216 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
11 | 33 kV ACI Pharmacuticles Feeder | 33 |  | DHKC4791 | 1 | 874.23 | 885.85 | 11.62 | 90000 |  | 1045800 |  | N.Gonj (East)
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 1045800
0
| KHANPUR 33 KV SIDE | [5 empty] | 0
9 | 33/11 kV, 20/28 MVA T1 Transformer | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer | 33 |  | DHKC 9361 | 1 | 40559.36 | 40559.36 | 0 | 240 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 15895416 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 17447146.8512 |  | EXPORT TO N.Gonj (East) |  |  | 1045800 |  | 33 KV NET IMPORT |  | 16401346.8512
| SIDDIRGANJ 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 16401346.8512 |  | 33 KV TX HV SIDE |  | 15895416
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 505930.8512
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 3.085%
| TOTAL IMPORT |  | 17447146.8512
11 KV SIDE of___KHANPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. | 11 |  | DHKC 9313 | 1 | 12703062.9 | 17083226 | 4380163.1 | 1 | 4380163.1 |  | 4815530.5138
18 | 33/11 kV Transformer-2 Incoming. | 11 |  | DHKC 9346 | 1 | 40577422.11 | 42701376.1 | 2123953.99 | 1 | 2123953.99 |  | 2335064.9314
24 | 33/11 kV 20/28 MVA T4 Incoming | 11 |  | 06604325 | 1 | 74.01 | 97.63 | 23.62 | 240000 | 5668800 |  | 6232251.8028
30 | 33/11 kV 20/28 MVA T1 Incoming | 11 |  | 06604374 | 1 | 42.22 | 53.66 | 11.44 | 240000 | 2745600 |  | 3018499.6031
[7 empty] | 0 |  | Total | 14918517.09 |  | 16401346.8512
| KHANPUR 11 KV SIDE | [5 empty] | 0
12 | 11 kV Khanpur Feeder | 11 |  | DHKC 9348 | 1 | 86157.18 | 116751.32 | 30594.14 | 60 |  | 1835648.4 | 1858439.2031 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1858439.2031 | 1689432.0922 | 169007.1108 | 10.0038 | OK
13 | 11 kV Mission Para Feeder. | 11 |  | DHKC 9347 | 1 | 76552.26 | 103983.86 | 27431.6 | 60 |  | 1645896 | 1666330.9001 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1666330.9001 | 1591097.4109 | 75233.4892 | 4.7284 | OK
14 | 11 kV Esha Kha Feeder | 11 |  | DHKC 9311 | 1 | 49376.9 | 64482.72 | 15105.82 | 60 |  | 906349.2 | 917602.1317 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 917602.1317 | 1040108.3114 | -122506.1796 | -11.7782 | OK
15 | 11 kV New Hazigonj Feeder | 11 |  | DHKC 9314 | 1 | 100.41 | 134.23 | 33.82 | 60000 |  | 2029200 | 2054393.8757 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 2054393.8757 | 2135156.6373 | -80762.7617 | -3.7825 | OK
16 | 11 kV Spare Feeder. | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | 11 |  | 6604412 | 1 | 2.82 | 3.83 | 1.01 | 60000 |  | 60600 | 61352.3895 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 61352.3895 | 59949.0945 | 1403.2951 | 2.3408 | OK
20 | 11 kV Old Hajiganj Feeder. | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | 11 |  | 06604389 | 1 | 62961.9 | 84767.18 | 21805.28 | 60 |  | 1308316.8 | 1324560.4284 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 1324560.4284 | 1260578.6756 | 63981.7528 | 5.0756 | OK
22 | 11 kV Spare Feeder. | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | 11 |  | 6604415 | 1 | 140.58 | 186.02 | 45.44 | 40000 |  | 1817600 | 1840166.7201 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1840166.7201 | 1800087.6245 | 40079.0956 | 2.2265 | OK
26 | 11 kV Mondalpara Feeder. | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | 11 |  | 06604392 | 1 | 109.7 | 145.84 | 36.14 | 40000 |  | 1445600 | 1463548.0912 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1463548.0912 | 1396793.7162 | 66754.375 | 4.7791 | OK
28 | 11 kV Bishaw Road Feeder. | 11 |  | 06604393 | 1 | 147.19 | 191.13 | 43.94 | 40000 |  | 1757600 | 1779421.78 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 1779421.78 | 1969640.6189 | -190218.839 | -9.6575 | OK
29 | 11 kV Chasara Feeder. | 11 |  | 06604391 | 1 | 152.29 | 204.54 | 52.25 | 40000 |  | 2090000 | 2115948.7484 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 2115948.7484 | 2048765.3497 | 67183.3987 | 3.2792 | OK
31 | 11 kV Pathan Tully Feeder. | 11 |  | 06604388 | 1 | 32.71 | 32.71 | 0 | 40000 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder. | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | 11 |  | 6604289 | 1 | 107.18 | 139.69 | 32.51 | 40000 |  | 1300400 | 1316545.3361 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1316545.3361 | 1343505.6323 | -26960.2962 | -2.0067 | OK
34 | 11 kV Spare Feeder. | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 |  | 412109 | 1 | 9109.5 | 9109.5 | 0 | 10 |  | 0 | 0 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 |  | 243285 | 1 | 6388.1 | 6388.1 | 0 | 10 |  | 3000 | 3037.247 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3037.247 | 3027.732 | 9.515 | 0.31426 | OK
[9 empty] | Grand Total | 16401346.8512 | 16200210.4 | 16401346.8512 | 1.2416
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3956115.4685
[5 empty] | N.Gonj (East) | at 33 KV level |  | 12445231.3827
[5 empty] | Total = |  |  | 16401346.8512 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail | 132 | Impt | 8993555 | 1 | 2725.888 | 2753.041 | 27.153 | 1440000 | 0 | 39100320
|  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar | 132 | Impt |  | 1 |  |  | 0 |  | 0 | 0
|  | 132 | Expt |  | 1 |  |  | 0 |  | 0
[8 empty] | Total Import/Export |  | 0 | 39100320
[9 empty] | Net Total | 39100320
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder | 132 | Impt |  | 1 |  |  | 0 | 1 | 0
|  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  | 132 | Expt |  | 1 | 8832554 | 8832555 | 1 | 1 | 1
|  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder | 132 | Impt | HA040700237-03 | 1 | 35292309 | 35292309 | 0 | 1
|  | 132 |  | 06604364 | 1 | 6008.61 | 6049.84 | 41.23 | 960000 | 39580800
|  | 132 | Expt | HA040700237-04 | 1 |  | 0 | 0 | 1 |  | 0
|  | 132 |  | 06604364 | 1 |  | 0 | 0 | 960000 |  | 0
[7 empty] | 0 | Total Import/Export |  | 39580801 | 0
[7 empty] | 0 | Net Total |  | 39580801
| MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| MOGBAZAR 132 KV SIDE | [5 empty] | 0
4 | 132/33 KV Transformer, GT-1 | 132 | DPDC | H/A040700240-03 | 1 | 99094.673 | 118600.357 | 19505.684 | 1000 |  | 19505684
|  | 132 | P. Cell | 08993572 | 1 | 4868.146 | 4908.847 | 40.701 | 480000 |  | 19536480
5 | 132/33 KV Transformer, GT-2 | 132 | DPDC | H/A030700918-03 | 1 | 59813.966 | 79349.314 | 19535.348 | 1000 |  | 19535348
|  | 132 | P. Cell | 08993577 | 1 | 4919.775 | 4970.503 | 50.728 | 480000 |  | 24349440
[9 empty] | Total |  | 39041032
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 39100320 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 39100320
| 132 KV Sending From Maniknagar |  | 0 |  | 132 KV NET IMPORT |  |  | 39100320 |  | 132/33 KV GT LV Side |  | 39106681
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -6361
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.01627%
| 132 KV TOTAL IMPORT |  | 39100320
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| MATUAIL 33 KV SIDE |  | IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 90418.204 | 110045.545 | 19627.341 | 1000 | 19627341
|  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 11480.344 | 30959.684 | 19479.34 | 1000 | 19479340
|  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
[7 empty] | 0 |  | Total | 39106681 |  | 0
| MATUAIL 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 | 33 | DPDC | H/A060300287-03 | 1.45 | 43922.238 | 50642.239 | 6720.001 | 1000 |  | 9744001.45 | 9811264.6101 |  | 17962285.6258 | Matuail 33/11 kv ss | 1.4349 | 33/11 KV Transformer, T-3 | 9811264.6101 | 9361396.9663 | 449867.6439 | 4.8056 | OK
|  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 | 33 | DPDC | H/A060300190-03 | 1 | 37839.029 | 45927.458 | 8088.429 | 1000 |  | 8088429 | 8144263.6895 |  |  |  |  | 33/11 KV Transformer, T-4 | 8144263.6895 | 7756788.9606 | 387474.7289 | 4.9953 | OK
|  | 33 | P. Cell | 08993581 | 1 | 6114.386 | 6159.359 | 44.973 | 180000 |  | 8095140 | 8151021.0157 |  |  |  |  | 0 | 8151021.0157 | 7753908.3193 | 397112.6964 | 5.1215 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 17839141.45 | 17962285.6258 |  |  |  |  | 33 KV Feeders | 17962285.6258 | 17115305.2855 | 846980.3403 | 4.9487 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 5989040 | 13380800 | 7391760 | 1 |  | 7391760 | 7442785.5606 |  | 16540194.7367 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 7442785.5606 | 7306501.5105 | 136284.0501 | 1.8652 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC |  | 1 | 9902.221 | 9902.222 | 0.001 | 1000 | From Customer End | 10962.5847 | 11038.2598 | Matuail |  |  |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 11038.2598 | 10991.7418 | 46.518 | 0.42321 | OK
|  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 0 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 55353.737 | 59915.41 | 4561.673 | 1000 |  | 4561673 | 4593162.3776 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 4593162.3776 | 5084619.6602 | -491457.2825 | -9.6656 | OK
|  | 33 | P. Cell | 08993580 | 1.5 | 1313.084 | 1330.064 | 16.98 | 180000 |  | 4584600 | 4616247.6435 |  |  |  |  | 0 | 4616247.6435 | 5104119.3859 | -487871.7424 | -9.5584 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 4593162.3776 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 | DPDC | 00000154 | 1 | 2822240 | 11857280 | 9035040 | 1 |  | 9035040 | 9097409.1761 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 9097409.1761 | 9282142.1719 | -184732.9958 | -1.9902 | OK
[9 empty] | Total |  | 20999435.5847 | 21144395.3742 |  |  |  |  | 0 | 21144395.3742 | 21684255.0845 | -539859.7103 | -2.4896 | OK
[8 empty] | Grand Total |  | 39106681 | 38838577.0347 | 39106681 | 0.6903
[5 empty] | 33 KV EXPORT |  |  | KWH
[5 empty] | EXPORT TO Matuail |  |  | 11038.2598
[5 empty] | Total Export |  |  | 11038.2598 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426631 | 1 | 7311696 | 7421109 | 109413 | 90 | 9847170 |  | 9896256.9159
11 | 33/11 kV Transformer, T-4 Incoming | 11 |  | 51426633 | 1 | 7026474 | 7115652 | 89178 | 90 | 8026020 |  | 8066028.71
[7 empty] | 0 |  | Total | 17873190 |  | 17962285.6258
| MATUAIL 11 kV SIDE | [5 empty] | 0
3 | 11 kV Link Road Feeder | 11 | Backup | DHK66629 | 1 | 23009.26 | 23250.37 | 241.11 | 8000 |  | 1928880 | 1956558.029 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 1956558.029 | 1882008.2759 | 74549.7532 | 3.9612 | OK
|  | 11 |  | HA021100475-02 | 1 | 83653.744 | 85577.974 | 1924.23 | 1000 |  | 1924230 | 1951841.3049 | N.Gonj (East) |  |  |  | 0 | 1951841.3049 | 1877540.2045 | 74301.1004 | 3.9574 | OK
4 | 11 kV Lamapara Express Feeder | 11 |  | HA021100928-03 | 1 | 75563.19 | 76566.376 | 1003.186 | 1000 |  | 1003186 | 1017580.9915 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1017580.9915 | 1063497.0225 | -45916.031 | -4.3175 | OK
5 | 11 kV Kutubpur Feeder*** | 11 |  | DHK66616 | 1 | 17315.9 | 17507.52 | 191.62 | 8000 |  | 1532960 | 1554956.8642 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1554956.8642 | 1703285.4205 | -148328.5563 | -8.7084 | OK
|  | 11 | Backup | XA575929 | 1 | 37443.2 | 38974.7 | 1531.5 | 1000 |  | 1531500 | 1553475.9142 | N.Gonj (East) |  |  |  | 0 | 1553475.9142 | 1701405.1914 | -147929.2772 | -8.6945 | OK
6 | 11 kV Ramarbagh Feeder (F1) | 11 |  | DHK66625 | 1 | 3463.92 | 3485.92 | 22 | 60000 |  | 1320000 | 1338941.0426 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1338941.0426 | 835792.1765 | 503148.8662 | 60.2002 | FAULT
|  | 11 | Backup |  | 1 | 8395.82 | 8395.82 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 837818.9826 | -837818.9826 | -100 | CHECK
7 | 11 kV Tushardhara Feeder (F2) | 11 |  | DHK66623 | 1 | 3701.54 | 3746.82 | 45.28 | 60000 |  | 2716800 | 2755784.1096 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2755784.1096 | 2760297.6743 | -4513.5647 | -0.16352 | OK
8 | 11 kV Matuail Medical Feeder (F3) | 11 |  | DHK66627 | 1 | 3258.78 | 3271.85 | 13.07 | 60000 |  | 784200 | 795452.7012 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 795452.7012 | 696897.8308 | 98554.8705 | 14.1419 | OK
|  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | 11 |  | HA021101044-02 | 1 | 64851.309 | 65208.095 | 356.786 | 1000 |  | 356786 | 361905.6203 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 361905.6203 | 323912.9361 | 37992.6843 | 11.7293 | OK
12 | 11 kV Shibu Market Feeder (F7) | 11 |  | DHK66624 | 1 | 2356.06 | 2362.42 | 6.36 | 60000 |  | 381600 | 387075.6832 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 387075.6832 | 615623.4101 | -228547.7269 | -37.1246 | OK
13 | 11 kV Soma-Sagar Steel (F6) | 11 |  | HA060300286-03 | 1 | 75021.472 | 76206.462 | 1184.99 | 1000 |  | 1184990 | 1201993.7471 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 1201993.7471 | 1110650.3388 | 91343.4083 | 8.2243 | OK
14 | 11 kV Jhalkuri Feeder (F8) | 11 |  | DHK66626 | 1 | 4291.01 | 4334.87 | 43.86 | 60000 |  | 2631600 | 2669361.5514 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2669361.5514 | 2690547.2387 | -21185.6873 | -0.78741 | OK
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK6622 | 1 | 4144.98 | 4168.25 | 23.27 | 60000 |  | 1396200 | 1416234.4574 | Matuail |  |  |  | 0 | 1416234.4574 | 1374993.3702 | 41241.0872 | 2.9994 | OK
16 | 11 kV Rajmahal Feeder (F10) | 11 |  | DHKA2187 | 1 | 104.4696 | 108.4909 | 4.0213 | 60000 |  | 241278 | 244740.1643 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 244740.1643 | 218634.2568 | 26105.9075 | 11.9404 | OK
17 | 11 kV Bhuighor Bazar | 11 |  | HA021100861-02 | 1 | 73094.967 | 74536.429 | 1441.462 | 1000 |  | 1441462 | 1462145.9342 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 1462145.9342 | 1034107.8281 | 428038.1061 | 41.392 | FAULT
18 | 11 kV Tokkar Math Feeder | 11 |  | HA021200298-02 | 1 | 78743.932 | 79511.406 | 767.474 | 1000 |  | 767474 | 778486.6953 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 778486.6953 | 733095.2742 | 45391.421 | 6.1917 | OK
19 | 11 kV Osmani Stadium Feeder***** | 11 |  | XA575922 | 1 | 170.9 | 184 | 13.1 | 1000 |  | 13100 | 13287.9755 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 13287.9755 | 64493.8811 | -51205.9056 | -79.3965 | CHECK
16 | 33/0.415 KV Transformer, AT-1 | 0.415 |  | 2001123043119 | 1 | 7194 | 7271 | 77 | 160 |  | 12320 | 12496.7831 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 12496.7831 | 11807.0303 | 689.7528 | 5.8419 | OK
17 | 33/0.415 KV Transformer, AT-2 | 0.415 |  | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 |  | 0 | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 0 | 129.3921 | -129.3921 | -100 | CHECK
[9 empty] | Total | 17962285.6258 | 17708186 | 17962285.6258 | 1.4349
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 4524379.1606
[5 empty] | Shyampur | at 33 KV level |  | 257236.9474
[5 empty] | Fatullah | at 33 KV level |  | 3719785.1437
[5 empty] | Matuail | at 33 KV level |  | 9460884.3742
[5 empty] | Total = |  |  | 17962285.6258 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 5989040 | 13380800 | 7391760 | 1 | 0 | 7391760 | 7442785.5606
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 |  | 00000154 | 1 | 2822240 | 11857280 | 9035040 | 1 | 0 | 9035040 | 9097409.1761
[9 empty] | Total | 0 | 16426800 | 16540194.7367
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder | 33 |  | 00000079 | 1 | 310417664 | 319364640 | 8946976 | 1 | 8946976
7 | 33 kV Matuail-1 Feeder | 33 |  | 00000114 | 1 | 254261424 | 261599760 | 7338336 | 1 | 7338336
[7 empty] | 0 |  | Total | 16285312 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE | [5 empty] | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000075 | 1 | 325047360 | 334076864 | 9029504 | 1 |  | 9029504
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000156 | 1 | 239696160 | 246952320 | 7256160 | 1 |  | 7256160
[9 empty] | Total |  | 16285664
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 16540194.7367 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 16540194.7367
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 16540194.7367 |  | 33 KV TX HV Side |  | 16285664
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 254530.7367
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.539%
| TOTAL IMPORT |  | 16540194.7367
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming | 11 |  | 00000144 | 1 | 323844352 | 332845958 | 9001606 | 1 | 9001606 |  | 9175110.4756
18 | 11 kV T-1 Incoming | 11 |  | 00000054 | 1 | 238185712 | 245411520 | 7225808 | 1 | 7225808 |  | 7365084.2611
[7 empty] | 0 |  | Total | 16227414 |  | 16540194.7367
| LAXMI NARAYAN COTTON MILL 11 KV SIDE | [5 empty] | 0
1 | 11 kV Godnail (F16) | 11 |  | 00000109 | 1 | 21004948 | 22845784 | 1840836 | 1 |  | 1840836 | 1848814.9706 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1848814.9706 | 1869406.9017 | -20591.9311 | -1.1015 | OK
2 | 11 kV M. Circus (F15) | 11 |  | 00000123 | 1 | 103491504 | 105458624 | 1967120 | 1 |  | 1967120 | 1975646.3394 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1975646.3394 | 2135882.0516 | -160235.7122 | -7.5021 | OK
3 | 11 kV Wapderpool (F14) | 11 |  | 00000190 | 1 | 55179144 | 55796344 | 617200 | 1 |  | 617200 | 619875.2088 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 619875.2088 | 595303.4365 | 24571.7723 | 4.1276 | OK
4 | 11 kV Chowdhury Bari (F13) | 11 |  | 00000191 | 1 | 94163728 | 96441288 | 2277560 | 1 |  | 2277560 | 2287431.9192 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2287431.9192 | 2194488.2982 | 92943.621 | 4.2353 | OK
5 | 11 kV Ailpara (F12) | 1 |  | 00000192 | 1 | 46804564 | 49107040 | 2302476 | 1 |  | 2302476 | 2312455.9158 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2312455.9158 | 2506620.5244 | -194164.6086 | -7.7461 | OK
6 | 11 kV Spare (F11) | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | 11 |  | 00000197 | 1 | 13020328 | 14248885 | 1228557 | 1 |  | 1228557 | 1233882.0915 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1233882.0915 | 1248729.4855 | -14847.394 | -1.189 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 |  | 00000198 | 1 | 3985110 | 3997630 | 12520 | 1 |  | 12520 | 12574.267 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 12574.267 | 42071.0581 | -29496.7911 | -70.1118 | CHECK
12 | 11 kV Lucky Bazar (F5) | 11 |  | 00000199 | 1 | 85797352 | 87124224 | 1326872 | 1 |  | 1326872 | 1332623.2308 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1332623.2308 | 1392661.9878 | -60038.757 | -4.3111 | OK
13 | 11 kV Enayetnagar (F4) | 11 |  | 00000200 | 1 | 27625972 | 29163608 | 1537636 | 1 |  | 1537636 | 1544300.7721 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1544300.7721 | 1576051.8888 | -31751.1167 | -2.0146 | OK
14 | 11 kV Bhuiyapara (F3) | 11 |  | 00000201 | 1 | 60310572 | 62323408 | 2012836 | 1 |  | 2012836 | 2021560.4921 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 2021560.4921 | 1949356.1666 | 72204.3255 | 3.704 | OK
15 | 11 kV Arambagh (F2) | 11 |  | 00000202 | 1 | 5922585 | 6951863 | 1029278 | 1 |  | 1029278 | 1033739.3311 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 1033739.3311 | 1073358.7436 | -39619.4126 | -3.6912 | OK
16 | 11 kV Spare (F1) | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 |  | 00000204 | 1 | 1532.1 | 1577 | 44.9 | 100 |  | 4490 | 4509.4616 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 4509.4616 | 4713.1396 | -203.678 | -4.3215 | OK
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 |  | 00000205 | 1 | 60.71 | 60.71 | 0 | 100 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 16227414 | 16157381 | 16227414 | 0.43344
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 7291423.7545
[5 empty] | Siddirgonj | at 33 KV level |  | 8935990.2455
[5 empty] | Total = |  |  | 16227414 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side | [7 empty] | Total | 0 | 0 | 0
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 633.63 | 659.92 | 26.29 | 360000 | 0 | 9464400 | 9456716.1108
0 | 0 | 33 | Backup | 041808904262 | 1 | 633.65 | 659.94 | 26.29 | 360000 | 0 | 9464400 | 9456716.1108
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 453.33 | 468.43 | 15.1 | 360000 | 0 | 5436000 | 5431586.6593
0 | 0 | 33 | Backup | 041808904258 | 1 | 453.51 | 468.61 | 15.1 | 360000 | 0 | 5436000 | 5431586.6593
[9 empty] | Total | 0 | 14900400 | 14888302.7701
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) | 33 | Digital | DHK60875 | 1 | 154661.5 | 193655.1 | 38993.6 | 240 | 9358464
9 | 33 kV New Fatulla-2 | 33 | Digital | DHK2186 | 1 | 297.7603 | 312.8299 | 15.0696 | 360000 | 5425056
[7 empty] | 0 |  | Total | 14783520 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| FATULLAH OLD 33 KV SIDE | [5 empty] | 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60980 | 1 | 871747.5 | 897422.1 | 25674.6 | 240 |  | 6161904
13 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 | Digital | DHK60952 | 1 | 480197.3 | 493721.2 | 13523.9 | 240 |  | 9358464 |  |  | Meter Problem
[9 empty] | Total |  | 15520368 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 14888302.7701
| New Fatullah 33 kv Side |  | 14888302.7701 |  | 33 KV Net Import |  |  | 14888302.7701 |  | 33 KV TX HV Side |  | 15520368
[10 empty] | LOSS UNITS=> |  | -632065.2299
[10 empty] | LOSS % IN => |  | -4.245%
| TOTAL IMPORT |  | 14888302.7701
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 | New | DHK61060 | 1 | 1009715.8 | 1009715.8 | 0 | 180 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 | New | DHK61054 | 1 | 359028.9 | 376872.2 | 17843.3 | 180 | 3211794 |  | 4744395.5845 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming | 11 | New | DHK60924 | 1.1 | 435449.4 | 458218.3 | 22768.9 | 180 | 4508242.2 |  | 6659482.0178 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming | 11 | New | DHK61051 | 1 | 833559.1 | 859768.4 | 26209.3 | 90 | 2358837 |  | 3484425.1678 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | Total | 10078873.2 |  | 14888302.7701 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [5 empty] | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | 11 | New |  | 1 | 74349258 | 74957542 | 608284 | 1 |  | 608284 | 608736.535 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 608736.535 | 686221.5647 | -77485.0297 | -11.2915 | OK
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 86574371 | 87261856 | 687485 | 1 |  | 687485 | 687996.4568 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 687996.4568 | 904286.638 | -216290.1812 | -23.9183 | OK
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 83099.6 | 105562.1 | 22462.5 | 60 |  | 1347750 | 1348752.6633 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1348752.6633 | 1520277.0648 | -171524.4016 | -11.2824 | OK
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 275685 | 291780 | 16095 | 60 |  | 965700 | 966418.4358 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 966418.4358 | 973413.7301 | -6995.2943 | -0.71864 | OK
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 906898.46 | 938604.3 | 31705.84 | 60 |  | 1902350.4 | 1903765.6601 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1903765.6601 | 1898489.4903 | 5276.1698 | 0.27791 | OK
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 37019.5 | 48136.4 | 11116.9 | 60 |  | 667014 | 667510.2274 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 667510.2274 | 661387.5474 | 6122.68 | 0.92573 | OK
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 588771.6 | 602547.3 | 13775.7 | 60 |  | 826542 | 827156.9088 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 827156.9088 | 863427.9271 | -36271.0183 | -4.2008 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 466043.56 | 486964.4 | 20920.84 | 60 |  | 1255250.4 | 1256184.2479 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1256184.2479 | 1130265.9765 | 125918.2714 | 11.1406 | OK
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 855908.3 | 860387.5 | 4479.2 | 60 |  | 268752 | 268951.939 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 268951.939 | 461817.7457 | -192865.8067 | -41.7623 | CHECK
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 487049.3 | 501840.9 | 14791.6 | 60 |  | 887496 | 888156.2557 | Fatullah |  |  |  | 11 kV Dhaka Steel | 888156.2557 | 505747.1466 | 382409.1091 | 75.6127 | FAULT
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 98802056 | 99488328 | 686272 | 1 |  | 686272 | 686782.5544 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 686782.5544 | 645276.6941 | 41505.8603 | 6.4323 | OK
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24231901 | 24567287 | 335386 | 1 |  | 335386 | 335635.5116 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 335635.5116 | 326421.8579 | 9213.6537 | 2.8226 | OK
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14466321 | 14795210 | 328889 | 1 |  | 328889 | 329133.6781 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 329133.6781 | 311868.8913 | 17264.7868 | 5.5359 | OK
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 26912795 | 27036113 | 123318 | 1 |  | 123318 | 123409.7429 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 123409.7429 | 535601.4665 | -412191.7236 | -76.9587 | CHECK
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 9716958 | 11860750 | 2143792 | 1 |  | 2143792 | 2145386.8814 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 2145386.8814 | 2599917.6327 | -454530.7513 | -17.4825 | OK
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 875390 | 2718344 | 1842954 | 1 |  | 1842954 | 1844325.072 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1844325.072 | 1788794.6263 | 55530.4456 | 3.1043 | OK
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 14888302.7701 | 14877234.8 | 14888302.7701 | 0.074395
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 12240018.0342
[5 empty] | N.Gonj (West) | at 33 KV level |  | 1296732.9918
[5 empty] | Sytalakhya | at 33 KV level |  | 1351551.7441
[5 empty] | Total = |  |  | 14888302.7701 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder | 132 | Export | 041808902770 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904227 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902770 | 1 | 157.03 | 172.02 | 14.99 | 1200000 | 17988000
|  | 132 |  | 041808904227 | 1 | 157.01 | 172 | 14.99 | 1200000 | 17988000
3 | 132 kV Haripur Feeder | 132 | Export | 041808902766 | 1 | 52.36 | 52.36 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904230 | 1 | 52.38 | 52.38 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902766 | 1 | 719.42 | 719.42 | 0 | 1200000 | 0
|  | 132 |  | 041808904230 | 1 | 719.67 | 719.67 | 0 | 1200000 | 0
4 | 132 kV Aggreko Feeder | 132 | Export | 041808902768 | 1 | 30.27 | 30.52 | 0.25 | 1200000 |  | 300000
|  | 132 |  | 041808904219 | 1 | 30.27 | 30.52 | 0.25 | 1200000 |  | 300000
|  | 132 | Import | 041808902768 | 1 | 256.63 | 257.68 | 1.05 | 1200000 | 1260000
|  | 132 |  | 041808904219 | 1 | 256.63 | 257.68 | 1.05 | 1200000 | 1260000
6 | 132 kV Shyampur-2 Feeder | 132 | Export | 041808902793 | 1 | 120.72 | 120.72 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904278 | 1 | 120.73 | 120.73 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902793 | 1 | 148.45 | 163.55 | 15.1 | 1200000 | 18120000
|  | 132 |  | 041808904278 | 1 | 148.48 | 163.58 | 15.1 | 1200000 | 18120000
[7 empty] | 0 | Total Import/Export |  | 37368000 | 300000
[7 empty] | 0 |  | Net Total | 37068000
| NEW FATULLAH 132 KV SIDE (RECEIVING) | [5 empty] | 0
0
0
0
0
[7 empty] | 0 | Total Import/Export |  | 0 | 0
[7 empty] | 0 | Net Total |  | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| FATULLAH 132 KV SIDE | [5 empty] | 0
2 | 132/33 kV, 80/120 MVA GT-1 | 132 | Export | 041808902767 | 1 | 539.67 | 557.72 | 18.05 | 1200000 |  | 21660000
|  | 132 | Export | 041808904228 | 1 | 539.54 | 557.58 | 18.04 | 1200000 |  | 21648000
5 | 132/33 kV, 80/120 MVA GT-2 | 132 | Export | 041808902792 | 1 | 414.71 | 427.55 | 12.84 | 1200000 |  | 15408000
|  | 132 | Export | 041808904251 | 1 | 414.56 | 427.39 | 12.83 | 1200000 |  | 15396000
[9 empty] | Total |  | 37068000
| 132 KV IMPORT |  | KWH | [6 empty] | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 37068000 | [6 empty] | 132 KV NET IMPORT |  | 37068000
| IMPORT-2 | [8 empty] | 132/33 KV GT LV Side |  | 36921600
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 146400
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3949%
| 132 KV TOTAL IMPORT |  | 37068000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902796 | 1 | 895.19 | 925.15 | 29.96 | 720000 | 21571200
|  | 33 | Backup | 041808904255 | 1 | 895.19 | 925.15 | 29.96 | 720000 | 21571200
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902802 | 1 | 688.17 | 709.49 | 21.32 | 720000 | 15350400
|  | 33 | Backup | 041808904281 | 1 | 688 | 709.32 | 21.32 | 720000 | 15350400
[7 empty] | 0 |  | Total | 36921600 |  | 0
| FATULLAH 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902868 | 1 | 707.01 | 731.27 | 24.26 | 240000 |  | 5822400 | 5817672.9516 |  | 11234871.3019 | New Fatullah 33/11 kv ss | 0.25585 | 33/11 kV, 28/35 MVA T-1 (=H5) | 5817672.9516 | 6020117.4846 | -202444.5329 | -3.3628 | OK
|  | 33 | Backup | 041808904277 | 1 | 706.58 | 730.82 | 24.24 | 240000 |  | 5817600 | 5812876.8486 |  |  |  |  | 0 | 5812876.8486 | 6017719.0314 | -204842.1828 | -3.404 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902824 | 1 | 612.92 | 635.51 | 22.59 | 240000 |  | 5421600 | 5417198.3503 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 5417198.3503 | 5945765.436 | -528567.0857 | -8.8898 | OK
|  | 33 | Backup | 041808904267 | 1 | 612.83 | 635.41 | 22.58 | 240000 |  | 5419200 | 5414800.2988 |  |  |  |  | 0 | 5414800.2988 | 5945765.436 | -530965.1372 | -8.9301 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 11244000 | 11234871.3019 |  |  |  |  | 33 KV Feeders | 11234871.3019 | 11965882.9205 | -731011.6186 | -6.1091 | OK
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 712.24 | 729.74 | 17.5 | 360000 |  | 6300000 | 6294885.2012 |  | 10798425.928 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 6294885.2012 | 7699034.7114 | -1404149.5102 | -18.238 | OK
|  | 33 | Backup | 041808904220 | 1 | 711.88 | 729.37 | 17.49 | 360000 |  | 6296400 | 6291288.1239 |  |  |  |  | 0 | 6291288.1239 | 7695437.0316 | -1404148.9077 | -18.2465 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 633.63 | 659.92 | 26.29 | 360000 |  | 9464400 | 9456716.1108 |  | 14888302.7701 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 9456716.1108 | 9508667.6365 | -51951.5257 | -0.54636 | OK
|  | 33 | Backup | 041808904262 | 1 | 633.65 | 659.94 | 26.29 | 360000 |  | 9464400 | 9456716.1108 |  |  |  |  | 0 | 9456716.1108 | 9512265.3163 | -55549.2055 | -0.58397 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 489.77 | 502.29 | 12.52 | 360000 |  | 4507200 | 4503540.7268 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 4503540.7268 | 3770368.4007 | 733172.3261 | 19.4456 | OK
|  | 33 | Backup | 041808904219 | 1 | 490.06 | 502.59 | 12.53 | 360000 |  | 4510800 | 4507137.804 |  |  |  |  | 0 | 4507137.804 | 3770368.4007 | 736769.4033 | 19.541 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 453.33 | 468.43 | 15.1 | 360000 |  | 5436000 | 5431586.6593 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 5431586.6593 | 6130446.3309 | -698859.6716 | -11.3998 | OK
|  | 33 | Backup | 041808904258 | 1 | 453.51 | 468.61 | 15.1 | 360000 |  | 5436000 | 5431586.6593 |  |  |  |  | 0 | 5431586.6593 | 6134044.0107 | -702457.3514 | -11.4518 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907981 | 1 | 1007.9 | 1135.45 | 127.55 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 25707600 | 25686728.6981 |  |  |  |  | 0 | 25686728.6981 | 27108517.0795 | -1421788.3814 | -5.2448 | OK
[8 empty] | Grand Total |  | 36921600 | 36951600 | 36921600 | -0.081187
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902832 | 1 | 676.78 | 700.01 | 23.23 | 250000 | 5807500 |  | 5817790.021
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902765 | 1 | 586.61 | 608.24 | 21.63 | 250000 | 5407500 |  | 5417081.2809
[7 empty] | 0 |  | Total | 11215000 |  | 11234871.3019
| FATULLAH 11 kV SIDE | [5 empty] | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 823.84 | 855.85 | 32.01 | 60000 |  | 1920600 | 1925513.8961 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 1925513.8961 | 2018573.5941 | -93059.698 | -4.6102 | OK
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 366.25 | 390.79 | 24.54 | 60000 |  | 1472400 | 1476167.1668 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1476167.1668 | 1492878.3256 | -16711.1587 | -1.1194 | OK
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 506.79 | 518.47 | 11.68 | 60000 |  | 700800 | 702593.0118 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 702593.0118 | 691704.3007 | 10888.711 | 1.5742 | OK
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1118.86 | 1147.26 | 28.4 | 60000 |  | 1704000 | 1708359.7204 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1708359.7204 | 1811062.3039 | -102702.5835 | -5.6708 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 116.01 | 135.99 | 19.98 | 60000 |  | 1198800 | 1201867.1554 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 1201867.1554 | 1168078.0452 | 33789.1102 | 2.8927 | OK
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 48.55 | 58.08 | 9.53 | 60000 |  | 571800 | 573262.9625 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 573262.9625 | 566596.0446 | 6666.9179 | 1.1767 | OK
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1045.24 | 1064.3 | 19.06 | 60000 |  | 1143600 | 1146525.925 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1146525.925 | 1680540.7098 | -534014.7847 | -31.7764 | OK
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1234.36 | 1275.93 | 41.57 | 60000 |  | 2494200 | 2500581.4639 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2500581.4639 | 2536449.5967 | -35868.1327 | -1.4141 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 11234871.3019 | 11206200 | 11234871.3019 | 0.25585
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 11234871.3019
[5 empty] | Total = |  |  | 11234871.3019 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 712.24 | 729.74 | 17.5 | 360000 | 0 | 6300000 | 6294885.2012
0 | 0 | 33 | Backup | 041808904220 | 1 | 711.88 | 729.37 | 17.49 | 360000 | 0 | 6296400 | 6291288.1239
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 489.77 | 502.29 | 12.52 | 360000 | 0 | 4507200 | 4503540.7268
0 | 0 | 33 | Backup | 041808904219 | 1 | 490.06 | 502.59 | 12.53 | 360000 | 0 | 4510800 | 4507137.804
| DAPA 33 KV SIDE (RECEIVING) | [7 empty] | Total | 0 | 10807200 | 10798425.928
5 | 33 kV New Fatullah Incoming Circuit-2 | 33 | Import |  | 1 | 175998960 | 180495536 | 4496576 | 1 | 4496576
6 | 33 kV Shyampur Incoming Circuit | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 | 33 | Import |  | 1 | 255965664 | 262254512 | 6288848 | 1 | 6288848
[7 empty] | 0 |  | Total | 10785424 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| DAPA 33 KV SIDE | [5 empty] | 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) | 33 | Export | 00000135 | 1 | 267562800 | 272058944 | 4496144 | 1 |  | 4496144
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) | 33 | Export | 00000193 | 1 | 257657760 | 263941440 | 6283680 | 1 |  | 6283680
[9 empty] | Total |  | 10779824 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 10798425.928 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10798425.928
[5 empty] | 33 KV NET IMPORT |  |  | 10798425.928 |  | 33 KV TX HV SIDE |  | 10779824
[10 empty] | LOSS UNITS=> |  | 18601.928
[10 empty] | LOSS % IN => |  | 0.1723%
| TOTAL IMPORT |  | 10798425.928
11 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000035 | 1 | 56156320 | 62408928 | 6252608 | 1 | 6252608 |  | 6293307.1129
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000143 | 1 | 266400336 | 270876320 | 4475984 | 1 | 4475984 |  | 4505118.8151
[7 empty] | 0 |  | Total | 10728592 |  | 10798425.928
| DAPA 11 KV SIDE | [5 empty] | 0
11 | 11 kV Katherpol Feeder | 11 |  | 00000031 | 1 | 59742536 | 61558008 | 1815472 | 1 |  | 1815472 | 1825325.1091 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 1825325.1091 | 2095256.7912 | -269931.6821 | -12.883 | OK
12 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | 11 |  | 00000032 | 1 | 61871328 | 63039328 | 1168000 | 1 |  | 1168000 | 1174339.0851 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1174339.0851 | 1364658.7564 | -190319.6713 | -13.9463 | OK
14 | 11 kV Shiachar Feeder | 11 |  | 00000030 | 1 | 61991488 | 63888724 | 1897236 | 1 |  | 1897236 | 1907532.8668 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 1907532.8668 | 1901950.2285 | 5582.6383 | 0.29352 | OK
15 | 11 kV Sastapur Feeder | 11 |  | 00000106 | 1 | 67891392 | 69229072 | 1337680 | 1 |  | 1337680 | 1344939.9892 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 1344939.9892 | 1492863.3157 | -147923.3266 | -9.9087 | OK
17 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | 11 |  | 00000172 | 1 | 4889120 | 4960188 | 71068 | 1 |  | 71068 | 71453.7073 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 71453.7073 | 791901.0884 | -720447.3811 | -90.9769 | CHECK
19 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | 11 |  | 00000044 | 1 | 74945536 | 76099056 | 1153520 | 1 |  | 1153520 | 1159780.4978 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 1159780.4978 | 373576.7292 | 786203.7686 | 210.4531 | FAULT
23 | 11 kV Kotaler Bag Feeder | 11 |  | 00000050 | 1 | 79654888 | 81048560 | 1393672 | 1 |  | 1393672 | 1401235.8745 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 1401235.8745 | 1515181.1462 | -113945.2718 | -7.5202 | OK
24 | 11 kV Idrakpur Feeder | 11 |  | 00000021 | 1 | 73516904 | 74625056 | 1108152 | 1 |  | 1108152 | 1114166.2721 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 1114166.2721 | 1068664.5804 | 45501.6917 | 4.2578 | OK
25 | 11 kV Isdair Feeder | 11 |  | 00000029 | 1 | 38441108 | 39230944 | 789836 | 1 |  | 789836 | 794122.676 | Fatullah |  |  |  | 11 kV Isdair Feeder | 794122.676 | 792940.801 | 1181.8751 | 0.14905 | OK
26 | 11 kV Shah Fateullah Express | 11 |  | 0000051 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKF 7522 | 1 | 2900 | 2955 | 55 | 100 |  | 5500 | 5529.8501 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 5529.8501 | 5198.5629 | 331.2872 | 6.3727 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10798425.928 | 10740136 | 10798425.928 | 0.54273
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 10798425.928
[5 empty] | Total = |  |  | 10798425.928 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 | 132 | IMPORT | 50501730 | 1 | 2736.898 | 2778.291 | 41.393 | 480000 | 0 | 19868640
2 | Tranformer 1 | 132 |  | 80505634 | 1 | 8341.911 | 8380.88 | 38.969 | 480000 | 0 | 18705120
3 | Tranformer 2 | 132 |  | 80505637 | 1 | 8293.77 | 8332.942 | 39.172 | 480000 | 0 | 18802560
4 | MI CEMENT | 132 |  | 38992489 (New) | 1 | 237.085 | 256.334 | 19.249 | 480000 | 0 | 9239520
[8 empty] | Total Import/Export |  | 0 | 66615840
[9 empty] | Net Total | 66615840
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 237.068 | 256.333 | 19.265 | 480000 |  | 9247200
|  | 132 | DPDC | 16402670 | 1 | 1762.138 | 1781.37 | 19.232 | 480000 |  | 9231360
[9 empty] | Total |  | 9231360
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 57384480
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 66615840 |  | EXPORT TO OTHER S/S |  |  | 9231360 |  | 132 KV NET IMPORT |  | 57384480
| IMPORT-2 |  |  |  | 132 KV NET IMPORT for Sitalakhya 33/11 KV |  |  | 57384480 |  | GT (33 KV Side) |  | 57361055
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 23425
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.04082%
| 132 KV TOTAL IMPORT |  | 66615840
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A030701130-03 | 1 | 33767.132 | 52592.299 | 18825.167 | 1000 | 18825167
|  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  | 33 | DPDC | BD001913 | 1 | 1649.3934 | 1688.3762 | 38.9828 | 480000 | 18711744
18 | 132/33 KV Transformer, GT-3 Incoming | 33 | DPDC | BD001915 | 1 | 2729.5 | 2770.8003 | 41.3003 | 480000 | 19824144
[7 empty] | 0 |  | Total | 57361055 |  | 0
| SITALAKHYA 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 | 33 | DPDC | H/A030701089-03 | 1 | 52483.717 | 61282.784 | 8799.067 | 1000 |  | 8799067 | 8807019.2728 |  | 13596048.513 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 8807019.2728 | 9161254.0741 | -354234.8013 | -3.8667 | OK
|  | 33 | P. Cell | 08993597 | 1 | 5792.471 | 5829.305 | 36.834 | 240000 |  | 8840160 | 8848149.4111 |  |  |  |  | 0 | 8848149.4111 | 9126162.145 | -278012.7339 | -3.0463 | OK
13 | 33/11 KV Transformer T-4 | 33 | DPDC | H/A030701087-03 | 1 | 61585.847 | 66370.552 | 4784.705 | 1000 |  | 4784705 | 4789029.2402 |  |  |  |  | 33/11 KV Transformer T-4 | 4789029.2402 | 4643948.6492 | 145080.591 | 3.1241 | OK
|  | 33 | P. Cell | 08993925 | 1 | 5603.238 | 5629.89 | 26.652 | 180000 |  | 4797360 | 4801695.6773 |  |  |  |  | 0 | 4801695.6773 | 4631678.5271 | 170017.1503 | 3.6707 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 13583772 | 13596048.513 |  |  |  |  | 33 KV Feeders | 13596048.513 | 13805202.7233 | -209154.2103 | -1.515 | OK
10 | 33 KV Char Syedpur Feeder (F1) | 33 | DPDC | H/A030701083-03 | 1 | 42622.663 | 42622.665 | 0.002 | 1000 |  | 2 | 2.0018 |  | 2.0018 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 2.0018 | 0 | 2.0018 | #DIV/0! | #DIV/0!
| 34 KV Char Syedpur Feeder (F1) | 33 | P. Cell | 08993596 | 1 | 2186.817 | 2186.817 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 98984.656 | 108788.348 | 9803.692 | 1000 |  | 9803692 | 9812552.2159 |  | 9812552.2159 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 9812552.2159 | 10966972.5378 | -1154420.3219 | -10.5263 | OK
| 34 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9619.053 | 9673.683 | 54.63 | 180000 |  | 9833400 | 9842287.0649 |  |  |  |  | 34 KV Panchabati BSCIC Feeder (F3) | 9842287.0649 | 10921759.0333 | -1079471.9684 | -9.8837 | OK
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 36660.866 | 37583.454 | 922.588 | 1000 |  | 922588 | 923421.8011 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 923421.8011 | 1229303.7954 | -305881.9943 | -24.8825 | OK
|  | 33 | P. Cell | 08993926 | 1 | 2279.147 | 2284.281 | 5.134 | 180000 |  | 924120 | 924955.1856 |  | 17447146.8512 | Khanpur 33/11 kv ss |  | 0 | 924955.1856 | 1226652.1207 | -301696.9351 | -24.5952 | OK
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 92642.466 | 101599.843 | 8957.377 | 1000 |  | 8957377 | 8965472.3475 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 8965472.3475 | 8963101.6544 | 2370.6931 | 0.026449 | OK
|  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1480.0066 | 1522.167 | 42.1604 | 180000 |  | 7588872 | 7595730.5431 |  | 15577849.9749 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 7595730.5431 | 7255990.2812 | 339740.2619 | 4.6822 | OK
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 335.3629 | 370.6713 | 35.3084 | 240000 |  | 8474016 | 8481674.5037 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 8481674.5037 | 8525241.2411 | -43566.7375 | -0.51103 | OK
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1225.4364 | 1258.6652 | 33.2288 | 240000 |  | 7974912 | 7982119.4318 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 7982119.4318 | 7687356.0419 | 294763.3899 | 3.8344 | OK
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4621.1 | 4646.3 | 25.2 | 160 |  | 4032 | 4035.644 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 4035.644 | 2848.7249 | 1186.9191 | 41.6649 | FAULT
[9 empty] | Total |  | 43725489 | 43765006.487 |  |  |  |  | 0 | 43765006.487 | 44630814.2767 | -865807.7897 | -1.9399 | OK
[8 empty] | Grand Total |  | 57361055 | 57309261 | 57361055 | 0.090376
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 927457.445
[5 empty] | Total = |  |  | 927457.445
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming | 11 |  | DHK 9372 | 1 | 70573.2195 | 119718.09 | 49144.8705 | 180 | 8846076.69 |  | 8832944.5359
10 | 33/11 kV Transformer, T-4 Incoming | 11 |  | DHK 9368 | 1 | 34487.0985 | 60988.1285 | 26501.03 | 180 | 4770185.4 |  | 4763103.9771
[7 empty] | 0 |  | Total | 13616262.09 |  | 13596048.513
| SITALAKHYA 11 kV SIDE | [5 empty] | 0
3 | 11 kV Bholail Feeder (F-3) | 11 |  | DHK 9335 | 1 | 17557.5729 | 68294.86 | 50737.2871 | 60 |  | 3044237.226 | 3046734.2178 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 3046734.2178 | 2464743.5384 | 581990.6795 | 23.6126 | OK
4 | 11 kV Crony Apparels (F-2) | 11 |  | DHK 9336 | 1 | 10186.2566 | 28231.2805 | 18045.0239 | 60 |  | 1082701.434 | 1083589.5043 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1083589.5043 | 1409860.9795 | -326271.4752 | -23.1421 | OK
5 | 11 kV Baburail Feeder (F-5) | 11 |  | DHK 9322 | 1 | 14240.3356 | 48193.1576 | 33952.822 | 60 |  | 2037169.32 | 2038840.2789 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 2038840.2789 | 1960329.6227 | 78510.6562 | 4.005 | OK
6 | 11 kV Goghchar Feeder (F-1) | 11 |  | DHK 9323 | 1 | 68546.5464 | 90249.8775 | 21703.3311 | 60 |  | 1302199.866 | 1303267.9767 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1303267.9767 | 1261095.5642 | 42172.4126 | 3.3441 | OK
7 | 11 kV Norshinghopur (F-2) | 11 |  | DHK 9365 | 1 | 47651.0611 | 70175.942 | 22524.8809 | 60 |  | 1351492.854 | 1352601.3966 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1352601.3966 | 1471201.0567 | -118599.6601 | -8.0614 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 |  | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 |  | 0 | 0 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 0 | 554462.5713 | -554462.5713 | -100 | CHECK
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 |  | H/A030701125-03 | 1 | 72602.239 | 72836.303 | 234.064 | 1000 |  | 234064 | 234255.9876 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 234255.9876 | 224598.6372 | 9657.3504 | 4.2998 | OK
12 | 11 kV Kashipur Feeder (F-7) | 11 |  | H/A030800169-03 | 1 | 31592.82 | 33256.036 | 1663.216 | 1000 |  | 1663216 | 1664580.229 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1664580.229 | 1652181.4751 | 12398.7539 | 0.75045 | OK
13 | 11 kV Spare Feeder (F-6) | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | 11 |  | H/A030701098-03 | 1 | 76031.283 | 77120.905 | 1089.622 | 1000 |  | 1089622 | 1090515.7468 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 1090515.7468 | 1082731.082 | 7784.6648 | 0.71898 | OK
15 | 11 kV B. K. Road Feeder (F-9) | 11 |  | H/A030800205-03 | 1 | 93037 | 93822.411 | 785.411 | 1000 |  | 785411 | 786055.2221 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 786055.2221 | 765048.1281 | 21007.0939 | 2.7459 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 |  | H/A030701091-03 | 1 | 51115.194 | 52130.183 | 1014.989 | 1000 |  | 1014989 | 1015821.5301 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 1015821.5301 | 958950.0681 | 56871.462 | 5.9306 | OK
[9 empty] | Total | 13616262.09 | 13605102.7 | 13616262.09 | 0.082024
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 1020311.2097
[5 empty] | Sytalakhya | at 33 KV level |  | 9466594.8546
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3129356.0257
[5 empty] | Total = |  |  | 13616262.09 | 0
MI CEMENT 132/33 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
1 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 237.068 | 256.333 | 19.265 | 480000 | 9247200 |  | 9239520
|  | 132 | DPDC | 16402670 | 1 | 1762.138 | 1781.37 | 19.232 | 480000 | 9231360
2 | 132/33 kV Transformer (132 kV Side) | 132 |  | 06502030 | 1 | 3503.713 | 3542.414 | 38.701 | 240000 |  | 9288240
[7 empty] | 0 | Total Import/Export |  | 9231360 | 9288240
[7 empty] | 0 |  | Net Total
0
3 | 132/33 kV Transformer (33 kV Side) | 33 |  | 14718815 | 1 | 6914.144 | 6990.664 | 76.52 | 120000 | 9182400
4 | 33 kV Outgoing Feeder-1 | 33 |  | 11745824 | 1 | 3609.947 | 3630.823 | 20.876 | 120000 |  | 2505120
5 | 33 kV Outgoing Feeder-2 | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 6677280
[8 empty] | Total Import/Export |  | 9182400 | 9182400
[8 empty] | Net Total |  | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 9239520
[5 empty] | Total = |  |  | 9239520
192
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1480.0066 | 1522.167 | 42.1604 | 180000 | 0 | 7588872 | 7595730.5431
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1225.4364 | 1258.6652 | 33.2288 | 240000 | 0 | 7974912 | 7982119.4318
[9 empty] | Total | 0 | 15563784 | 15577849.9749
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder | 33 |  | 00000188 | 1 | 297807296 | 305372960 | 7565664 | 1 | 7565664
7 | 33 kV Shitalakhya-1 Feeder | 33 |  | 00000153 | 1 | 294503584 | 302469120 | 7965536 | 1 | 7965536
[7 empty] | 0 |  | Total | 15531200 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| MONDOLPARA 33 KV SIDE | [5 empty] | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000116 | 1 | 302422336 | 309984960 | 7562624 | 1 |  | 7562624
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000194 | 1 | 289720064 | 297679680 | 7959616 | 1 |  | 7959616
[9 empty] | Total |  | 15522240 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 15577849.9749 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 15577849.9749
[5 empty] | 33 KV NET IMPORT |  |  | 15577849.9749 |  | 33 KV TX HV SIDE |  | 15522240
[10 empty] | LOSS UNITS=> |  | 55609.9749
[10 empty] | LOSS % IN => |  | 0.357%
| TOTAL IMPORT |  | 15577849.9749
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming | 11 |  | 00000055 | 1 | 288316736 | 296240160 | 7923424 | 1 | 7923424 |  | 8020228.8447
19 | 11 kV T-2 Incoming | 11 |  | 00000017 | 1 | 300184960 | 307651360 | 7466400 | 1 | 7466400 |  | 7557621.1302
[7 empty] | 0 |  | Total | 15389824 |  | 15577849.9749
| MONDOLPARA 11 KV SIDE | [5 empty] | 0
9 | 11 kV River View | 11 |  | 00000061 | 1 | 4718732 | 5548248 | 829516 | 1 |  | 829516 | 838140.6773 | N.Gonj (East) |  |  |  | 11 kV River View | 838140.6773 | 803073.4017 | 35067.2756 | 4.3666 | OK
10 | 11 kV Railgate B.B. Road | 11 |  | 00000191 | 1 | 21484788 | 22140866 | 656078 | 1 |  | 656078 | 662899.4007 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 662899.4007 | 611819.3181 | 51080.0826 | 8.3489 | OK
11 | 11 kV DIT | 11 |  | 00000174 | 1 | 130377160 | 133509912 | 3132752 | 1 |  | 3132752 | 3165323.9759 | N.Gonj (West) |  |  |  | 11 kV DIT | 3165323.9759 | 2992837.0935 | 172486.8824 | 5.7633 | OK
12 | 11 kV Dalpatti | 11 |  | 00000182 | 1 | 2382434 | 3037272 | 654838 | 1 |  | 654838 | 661646.5082 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 661646.5082 | 714092.6513 | -52446.1431 | -7.3444 | OK
13 | 11 kV South Chasara | 11 |  | 00000043 | 1 | 88911104 | 91543376 | 2632272 | 1 |  | 2632272 | 2659640.365 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2659640.365 | 2565218.7341 | 94421.6309 | 3.6808 | OK
14 | 11 kV Spare | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | 11 |  | 00000019 | 1 | 67159 | 96919 | 29760 | 1 |  | 29760 | 30069.4219 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 30069.4219 | 22516.8296 | 7552.5923 | 33.542 | OK
17 | 11 kV Spare | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | 11 |  | 00000173 | 1 | 3304592 | 4304069 | 999477 | 1 |  | 999477 | 1009868.8027 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1009868.8027 | 967617.4501 | 42251.3526 | 4.3665 | OK
20 | 11 kV Nitaigonj | 11 |  | 00000189 | 1 | 56636980 | 57402260 | 765280 | 1 |  | 765280 | 773236.8002 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 773236.8002 | 671875.6098 | 101361.1903 | 15.0863 | OK
21 | 11 kV Shahid Nagar | 11 |  | 00000020 | 1 | 54413388 | 55724624 | 1311236 | 1 |  | 1311236 | 1324869.236 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1324869.236 | 1256708.9709 | 68160.2651 | 5.4237 | OK
22 | 11 kV Bangla Bazar | 11 |  | 00000139 | 1 | 65980440 | 67598832 | 1618392 | 1 |  | 1618392 | 1635218.8108 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1635218.8108 | 1605498.2865 | 29720.5243 | 1.8512 | OK
23 | 11 kV Vogoban Gonj | 11 |  | 00000181 | 1 | 1465156 | 1911915 | 446759 | 1 |  | 446759 | 451404.0608 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 451404.0608 | 442440.5963 | 8963.4645 | 2.0259 | OK
24 | 11 kV Tanbazar | 11 |  | 00000138 | 1 | 46679968 | 47659964 | 979996 | 1 |  | 979996 | 990185.2541 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 990185.2541 | 977004.8332 | 13180.4209 | 1.3491 | OK
25 | 11 kV SS Road | 11 |  | 00000175 | 1 | 62559048 | 63912244 | 1353196 | 1 |  | 1353196 | 1367265.5042 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1367265.5042 | 1304240.0244 | 63025.4798 | 4.8324 | OK
26 | 11 kV Spare | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 | 0.415 |  |  | 1 | 2333.07 | 2413.05 | 79.98 | 100 |  | 7998 | 8081.1571 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 8081.1571 | 8402.5235 | -321.3664 | -3.8246 | OK
28 | 33/0.415 kV Auxiliary-2 | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15577849.9749 | 15417550 | 15577849.9749 | 1.0397
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1324869.236
[5 empty] | N.Gonj (East) | at 33 KV level |  | 5417450.9259
[5 empty] | N.Gonj (West) | at 33 KV level |  | 8835529.8131
[5 empty] | Total = |  |  | 15577849.9749 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 98984.656 | 108788.348 | 9803.692 | 1000 | 0 | 9803692 | 9812552.2159
0 | 34 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9619.053 | 9673.683 | 54.63 | 180000 | 0 | 9833400 | 9842287.0649
| MATUAIL 33 KV SIDE | [7 empty] | Total |  | 9803692 | 9812552.2159
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 55353.737 | 59915.41 | 4561.673 | 1000 | 0 | 4561673 | 4593162.3776
0 | 0 | 33 | P. Cell | 08993580 | 1.5 | 1313.084 | 1330.064 | 16.98 | 180000 | 0 | 4584600 | 4616247.6435
[9 empty] | Total | 0 | 4561673 | 4593162.3776
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) | [7 empty] | Total |  | 14365365 | 14405714.5935
3 | 33 kV Matuail Feeder | 33 | Digital | ABB03910 | 1 | 79891.7347 | 80771.768 | 880.0333 | 4000 | 3520133.08
6 | 33 kV Shitalakhya Feeder | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  | 33 | New | DHKA2199 | 1 | 4034.087 | 4085.7267 | 51.6397 | 180000 | 9295146
[7 empty] | 0 |  | Total | 3520133.08 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| NARAYANGONJ BSCIC 33 KV SIDE | [5 empty] | 0
5 | 33/11 kV, 20/28 MVA Transformer-3 | 33 | Old | HA021100524-02 | 1 |  | 0 | 0 | 1000 |  | 0
|  | 33 | New | DHKA2200 | 1 | 4246.9223 | 4271.1911 | 24.2688 | 180000 |  | 4368384
7 | 33/11 kV, 10/14 MVA Transformer-2 | 33 | Old | HA030800199-03 | 1 | 29604.1 | 34464.969 | 4860.869 | 1000 |  | 4860869
|  | 33 | New | DHKA2195 | 1 | 4374.8683 | 4424.2755 | 49.4072 | 90000 |  | 4446648
8 | 33/11 kV, 10/14 MVA Transformer-1 | 33 | Digital | ABB03909 | 1 | 415710.129 | 420502.76 | 4792.631 | 1000 |  | 4792631.01
[9 empty] | Total |  | 14021884.01 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 9812552.2159 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 14405714.5935
| MATUAIL 33 KV SIDE |  | 4593162.3776 |  | 33 KV NET IMPORT |  |  | 14405714.5935 |  | 33 KV TX HV SIDE |  | 14021884.01
[10 empty] | LOSS UNITS=> |  | 383830.5835
[10 empty] | LOSS % IN => |  | 2.664%
| TOTAL IMPORT |  | 14405714.5935
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming | 11 |  | 51426632 | 1 | 3618652 | 3672086 | 53434 | 90 | 4809060 |  | 4898423.6919
16 | 33/11 kV Transformer, T-1 Incoming | 11 |  | DHKA2192 | 1 | 3735.4904 | 3789.2958 | 53.8054 | 90000 | 4842486 |  | 4932470.8259
22 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426630 | 1 | 3927014 | 3976918 | 49904 | 90 | 4491360 |  | 4574820.0756
[7 empty] | 0 |  | Total | 14142906 |  | 14405714.5935
| NARAYANGONJ BSCIC 11 KV SIDE | [5 empty] | 0
10 | 11 kV Masdair Feeder (F-8) | 11 |  | XA575914 | 1 | 206799.9 | 209842.6 | 3042.7 | 1000 |  | 3042700 | 3086175.0273 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 3086175.0273 | 3077099.4263 | 9075.601 | 0.29494 | OK
11 | 11 kV Narayangonj (F-7) | 11 |  | XA575915 | 1 | 163077.6 | 164247.4 | 1169.8 | 1000 |  | 1169800 | 1186514.4598 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1186514.4598 | 1307443.1804 | -120928.7206 | -9.2493 | OK
12 | 11 kV Nearest Feeder (F-6) | 11 |  | XA575927 | 1 | 103832.5 | 104635.5 | 803 | 1000 |  | 803000 | 814473.5094 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 814473.5094 | 997748.2737 | -183274.7643 | -18.3688 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 |  | XA575916 | 1 | 113848.2 | 115029.2 | 1181 | 1000 |  | 1181000 | 1197874.4889 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1197874.4889 | 1341268.5888 | -143394.0999 | -10.6909 | OK
14 | 11 kV Abonti Color Tex. (F-4) | 11 |  | XA575912 | 1 | 53493 | 54099.1 | 606.1 | 1000 |  | 606100 | 614760.142 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 614760.142 | 701320.2188 | -86560.0768 | -12.3424 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 |  | DHK66615 | 1 | 165.1511 | 180.4877 | 15.3365 | 60000 |  | 920191.92 | 933339.9033 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 933339.9033 | 1045632.3523 | -112292.4489 | -10.7392 | OK
17 | 11 kV Shasongaon Feeder (F-2) | 11 |  | XA575920 | 1 | 229950 | 230751.7 | 801.7 | 1000 |  | 801700 | 813154.9346 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 813154.9346 | 1189560.6195 | -376405.6849 | -31.6424 | OK
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 |  | XA575929 | 1 | 17828 | 19036.6 | 1208.6 | 1000 |  | 1208600 | 1225868.8461 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1225868.8461 | 1274022.8667 | -48154.0206 | -3.7797 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 |  | HA021100913-02 | 1 | 37746.076 | 38386.576 | 640.5 | 1000 |  | 640500 | 649651.6597 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 649651.6597 | 916096.371 | -266444.7113 | -29.0848 | OK
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 |  | HA021100682-02 | 1 | 55419.839 | 57586.384 | 2166.545 | 1000 |  | 2166545 | 2197501.257 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2197501.257 | 2366722.3025 | -169221.0456 | -7.15 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 |  | HA021100455-02 | 1 | 51349.693 | 53001.889 | 1652.196 | 1000 |  | 1652196 | 1675803.0813 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1675803.0813 | 1827353.8856 | -151550.8043 | -8.2935 | OK
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3691.2 | 3753.3 | 62.1 | 160 |  | 9936 | 10077.9686 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 10077.9686 | 6902.8139 | 3175.1547 | 45.998 | FAULT
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4098.1 | 4101.3 | 3.2 | 160 |  | 512 | 519.3156 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 519.3156 | 421.2985 | 98.0171 | 23.2655 | OK
[9 empty] | Grand Total | 14405714.5935 | 14202780.92 | 14405714.5935 | 1.4288
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 813154.9346
[5 empty] | N.Gonj (West) | at 33 KV level |  | 13592559.659
[5 empty] | Total = |  |  | 14405714.5935 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  | IMPORT | 42627811 | 1 | 235.539 | 247.775 | 12.236 | 960000 | 0 | 11746560
| Madonganj to Charsyedpur-2 |  |  | 42627824 | 1 | 144.939 | 159.043 | 14.104 | 960000 | 0 | 13539840
[8 empty] | Total Import/Export |  | 0 | 25286400 | 0
[9 empty] | Net Total | 25286400
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 | 132 |  | 041808902821 | 1 | 195.94 | 205.73 | 9.79 | 1200000 | 11748000
|  | 132 |  | 041808904222 | 3 | 64.67 | 67.94 | 3.27 | 1200000 | 11772000
| 132 kV Madanganj Circuit-2 | 132 |  | 041808902865 | 1 | 115.71 | 127.26 | 11.55 | 1200000 | 13860000
|  | 132 |  | 041808904240 | 1 | 115.75 | 127.3 | 11.55 | 1200000 | 13860000
[7 empty] | 0 | Total Import/Export |  | 25608000 | 0 | 0
[7 empty] | 0 | Net Total |  | 25608000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| CHAR SYEDPUR 132 KV SIDE | [5 empty] | 0
4 | 132/33 kV, 80/120 MVA GT-1 | 132 | EXPORT | 041808902864 | 1 | 146.13 | 155.92 | 9.79 | 1200000 | 11748000 | 11748000
|  | 132 |  | 041808904224 | 1 | 146.03 | 155.82 | 9.79 | 1200000 | 11748000 | 11748000
7 | 132/33 kV, 80/120 MVA GT-2 | 132 |  | 041808902848 | 1 | 165.49 | 177.03 | 11.54 | 1200000 | 13848000 | 13848000
|  | 132 |  | 041808904244 | 1 | 165.59 | 177.11 | 11.52 | 1200000 | 13824000 | 13824000
[9 empty] | Total |  | 25596000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 25286400 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 25596000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 25596000 |  | 132/33 KV LV SIDE |  | 25452000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 144000
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5626%
| 132 KV TOTAL IMPORT |  | 25286400
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902859 | 1 | 241.98 | 258.18 | 16.2 | 720000 | 11664000 |  | 11729991.5134
|  | 33 | Backup | 041808904285 | 1 | 241.98 | 258.18 | 16.2 | 720000 | 11664000 |  | 11729991.5134
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902812 | 1 | 274.52 | 293.67 | 19.15 | 720000 | 13788000 |  | 13866008.4866
|  | 33 | Backup | 041808904276 | 1 | 274.57 | 293.69 | 19.12 | 720000 | 13766400 |  | 13844286.2801
[7 empty] | 0 |  | Total | 25452000 |  | 25596000
| CHAR SYEDPUR 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902875 | 1 | 190.56 | 200.92 | 10.36 | 240000 |  | 2486400 | 2501282.1097 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2501282.1097 | 2723906.2656 | -222624.1559 | -8.173 | OK
|  | 33 | Backup | 041808904241 | 1 | 190.5 | 200.86 | 10.36 | 240000 |  | 2486400 | 2501282.1097 |  |  |  |  | 0 | 2501282.1097 | 2721499.988 | -220217.8783 | -8.0918 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902844 | 3 | 53.76 | 56.7 | 2.94 | 240000 |  | 2116800 | 2129469.9042 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 2129469.9042 | 1891334.2091 | 238135.695 | 12.5909 | OK
|  | 33 | Backup | 041808904259 | 3 | 53.76 | 56.7 | 2.94 | 240000 |  | 2116800 | 2129469.9042 |  |  |  |  | 0 | 2129469.9042 | 1898553.042 | 230916.8622 | 12.1628 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 4603200 | 4630752.0138 |  |  |  |  | 33 KV Feeders | 4630752.0138 | 4615240.4747 | 15511.5391 | 0.33609 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 269.79 | 288.61 | 18.82 | 360000 |  | 6775200 | 6815752.3123 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 6815752.3123 | 6616060.3155 | 199691.9968 | 3.0183 | OK
|  | 33 | Backup | 041808904221 | 1 | 269.81 | 288.74 | 18.93 | 360000 |  | 6814800 | 6855589.3343 |  |  |  |  | 0 | 6855589.3343 | 6583575.5677 | 272013.7666 | 4.1317 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 87.04 | 93.75 | 6.71 | 360000 |  | 2415600 | 2430058.343 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2430058.343 | 2458012.5886 | -27954.2456 | -1.1373 | OK
|  | 33 | Backup | 041808904237 | 1 | 87.04 | 93.75 | 6.71 | 360000 |  | 2415600 | 2430058.343 |  |  |  |  | 0 | 2430058.343 | 2479669.0872 | -49610.7442 | -2.0007 | OK
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 39.89 | 42.67 | 2.78 | 360000 |  | 1000800 | 1006790.1928 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 1006790.1928 | 1108090.8439 | -101300.6511 | -9.1419 | OK
|  | 33 | Backup | 041808904232 | 1 | 39.92 | 42.69 | 2.77 | 360000 |  | 997200 | 1003168.6453 |  |  |  |  | 0 | 1003168.6453 | 1111700.2603 | -108531.615 | -9.7627 | OK
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 405.16 | 434.74 | 29.58 | 360000 |  | 10648800 | 10712537.375 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 10712537.375 | 10817421.0397 | -104883.6646 | -0.96958 | OK
|  | 33 | Backup | 041808904242 | 1 | 405.19 | 434.78 | 29.59 | 360000 |  | 10652400 | 10716158.9225 |  |  |  |  | 0 | 10716158.9225 | 10817421.0397 | -101262.1172 | -0.9361 | OK
| 33/0.415 kV Transformer AT-1 |  |  |  | 1 | 1372.11 | 1481.22 | 109.11 | 1 |  | 109.11 | 109.7631 | [5 empty] | 109.7631 | 98.7376
[9 empty] | Total |  | 20840509.11 | 20965247.9862 |  |  |  |  | 0 | 20965247.9862 | 20999683.5253 | -34435.5391 | -0.16398 | OK
[8 empty] | Grand Total |  | 25596000 | 25443709.11 | 25596000 | 0.59854
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902756 | 1 | 182.1 | 192 | 9.9 | 250000 | 2475000 |  | 3205187.9955
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902778 | 1.72 | 112.66 | 115.22 | 2.56 | 250000 | 1100800 |  | 1425564.0183
[7 empty] | 0 |  | Total | 3575800 |  | 4630752.0138
| CHAR SYEDPUR 11 kV SIDE | [5 empty] | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 |  | 041808902749 | 1 | 360.83 | 381.72 | 20.89 | 60000 |  | 1253400 | 1256317.0074 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 1256317.0074 | 1308593.1901 | -52276.1827 | -3.9948 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 |  | 041808902759 | 1 | 398.23 | 418.63 | 20.4 | 60000 |  | 1224000 | 1226848.5855 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1226848.5855 | 1401162.4833 | -174313.8978 | -12.4407 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | 11 |  | 041808902786 | 1 | 229.07 | 252.09 | 23.02 | 60000 |  | 1381200 | 1384414.4332 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1384414.4332 | 1059738.0772 | 324676.356 | 30.6374 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 |  | 041808902789 | 1 | 151.39 | 164.08 | 12.69 | 60000 |  | 761400 | 763171.9877 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 763171.9877 | 845746.7241 | -82574.7364 | -9.7635 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907976 | 1 | 1372.11 | 1481.22 | 109.11 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4630752.0138 | 4620000 | 4630752.0138 | 0.23273
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 25595890.2369
[5 empty] | Total = |  |  | 25595890.2369 | 20965138.2231
33 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FROM MADERTEK 33 KV SIDE
3 | Amulia | 33 | Export | SIEM0505 | 1 | 34124 | 35220 | 1096 | 6000 | 0 | 6576000 | 6565126.6501
[9 empty] | Total |  | 6576000 | 6565126.6501
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving | 33 |  |  | 1 | 1217.99 | 1254.53 | 36.54 | 180000 | 6577200
0
0
[7 empty] | 0 |  | Total | 6577200 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| AMULIA 33 KV SIDE | [5 empty] | 0
3 | 33/11 kV Transformer, T-1 | 33 |  | DHKA2194 | 1 | 325.7547 | 339.3168 | 13.5621 | 240000 |  | 3254904
4 | 33/11 kV Transformer, T-2 | 33 |  | DHKA2198 | 1 | 502.0763 | 515.8374 | 13.7611 | 240000 |  | 3302664
[9 empty] | Total |  | 6557568 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 6565126.6501 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 6565126.6501
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 6565126.6501 |  | 33 KV TX HV SIDE |  | 6557568
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 7558.6501
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1151%
| TOTAL IMPORT |  | 6565126.6501
11 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming | 11 |  | HA021100461-02 | 1 | 10126071 | 13429981 | 3303910 | 1 | 3303910 |  | 3359032.1899
11 | 33/11 kV Transformer, T-1 Incoming | 11 |  | HA021100478-02 | 1 | 80972706 | 84126188 | 3153482 | 1 | 3153482 |  | 3206094.4602
[7 empty] | 0 |  | Total | 6457392 |  | 6565126.6501
| AMULIA 11 KV SIDE | [5 empty] | 0
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 68696773 | 69350978 | 654205 | 1 |  | 654205 | 655997.4572 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 655997.4572 | 731782.37 | -75784.9127 | -10.3562 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 11388468 | 12677425 | 1288957 | 1 |  | 1288957 | 1292488.6152 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1292488.6152 | 1242034.7233 | 50453.8919 | 4.0622 | OK
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 67318225 | 67815676 | 497451 | 1 |  | 497451 | 498813.9667 | Demra | Grid Provided Reading 67481532 | Last Reading Collected From Grid Before Reset 67504359 |  | 11 kV Paity Feeder | 498813.9667 | 550647.0061 | -51833.0393 | -9.4131 | OK
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 59259140 | 61396460 | 2137320 | 1 |  | 2137320 | 2143176.0462 | Demra | Opening Reading (at 15/06/2023) After Reset | 20265 |  | 11 kV Bamuil Feeder | 2143176.0462 | 2258006.7634 | -114830.7172 | -5.0855 | OK
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 12956256 | 13507195 | 550939 | 1 |  | 550939 | 552448.5186 | Mugdapara | Closing Reading (at 30/06/2023) After Reset | 331582 |  | 11 kV Ali Ahmed School Feeder | 552448.5186 | 1045691.8176 | -493243.299 | -47.1691 | CHECK
13 | 11 kV Amulia Model Town Feeder | 11 | Demra |  | 1 | 51323114 | 51481502 | 158388 | 1 |  | 158388 | 158821.9675 | Demra | Difference | 311317 |  | 11 kV Amulia Model Town Feeder | 158821.9675 | 145542.9861 | 13278.9815 | 9.1238 | OK
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 8420622 | 9680550 | 1259928 | 1 |  | 1259928 | 1263380.0786 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1263380.0786 | 1242709.7581 | 20670.3205 | 1.6633 | OK
15 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 6565126.6501 | 6547188 | 6565126.6501 | 0.27324
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Mugdapara | at 33 KV level |  | 1208445.9758
[5 empty] | Demra | at 33 KV level |  | 5356680.6743
[5 empty] | Total = |  |  | 6565126.6501 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| MOGBAZAR T&T 11 KV SIDE | [8 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder | 33 |  | 8993841 | 1 | 39195.806 | 39285.417 | 89.611 | 36000 | 733 | 3225996 | 3226729 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 3226729 | 3058393 | 168336 | 5.5041 | OK
13 | 33 kV Mondol Para (Premire cement) Feeder | 33 |  | 8993842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total |  | 3225996 | 3226729 | 0.022722
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 3226729
[5 empty] | Total = |  |  | 3226729 | 0

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 | 132 | IMPORT | 50147584 | 1 | 3087.962 | 3134.038 | 46.076 | 1920000 | 0 | 88465920
| Maniknagar-2 | 132 |  | 50147585 | 1 | 3081.57 | 3127.49 | 45.92 | 1920000 | 0 | 88166400
[8 empty] | Total Import/Export |  | 0 | 176632320
[9 empty] | Net Total | 176632320
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 176632320
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 | 132 | EXPORT | 06604331 | 1 | 8792.35 | 8833.87 | 41.52 | 480000 |  | 19929600
| 132 kV Narinda Circuit-2 | 132 |  | 06604334 | 1 | 8800.57 | 8842.46 | 41.89 | 480000 |  | 20107200
| 132kV Motijheel Circuit-1 | 132 |  | 06604332 | 1 | 1797.51 | 1809.31 | 11.8 | 1440000 |  | 16992000
| 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1609.68 | 1619.13 | 9.45 | 1440000 |  | 13608000 |  |  | METER PROBLEM
| 132 kV Kazla Circuit-1 | 132 |  | ABB03905 | 1 | 681650 | 714735 | 33085 | 1000 |  | 33085000
| 132 kV Kazla Circuit-2 | 132 |  | ABB03904 | 1 | 514116 | 536435 | 22319 | 1000 |  | 22319000
[7 empty] | 0 |  | Total |  | 126040800
| MANIKNAGAR 132 KV SIDE | [5 empty] | 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 25049000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) | 132 | Export | ABB03903 | 1 | 258899 | 284234 | 25335 | 1000 |  | 25335000 |  |  | 50384000
[9 empty] | Total |  | 50384000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 176632320 |  | EXPORT TO OTHER S/S |  |  | 126040800 |  | 132 KV NET IMPORT |  | 50591520
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 50591520 |  | 33 KV NET IMPORT |  | 50416000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 175520
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3469%
| 132 KV TOTAL IMPORT |  | 176632320
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) | 33 | Digital | ABB03907 | 1 | 998995 | 1024044 | 25049 | 1000 | 25049000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) | 33 | Digital | ABB03906 | 1 | 165892 | 191259 | 25367 | 1000 | 25367000
[7 empty] | 0 |  | Total | 50416000 |  | 0
| Maniknagar 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 10745414.8989 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK00121 | 2 | 9651.2 | 10067.8 | 416.6 | 4444 |  | 3702740.8 | 3717504.4134 |  |  |  |  | 0 | 3717504.4134 | 4118977.441 | -401473.0277 | -9.7469 | OK
7 | 33 kV 20/28 MVA Transformer-2 | 33 | Digital | ABB03913 | 1 | 374709 | 378209 | 3500 | 2000 |  | 7000000 | 7027910.4855 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 7027910.4855 | 6955998.2234 | 71912.2622 | 1.0338 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 10702740.8 | 10745414.8989 |  |  |  |  | 33 KV Feeders | 10745414.8989 | 11074975.6644 | -329560.7655 | -2.9757 | OK
2 |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 12821719.8898 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder | 33 |  | DHK86054 | 1 | 2401.75 | 2425.39 | 23.64 | 270000 |  | 6382800 | 6408249.5782 |  |  |  |  | 33kV Motijheel-1 Feeder | 6408249.5782 | 6487859.5429 | -79609.9648 | -1.2271 | OK
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | Estimated | 9372512 | 9409882.1944 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 9409882.1944 | 9571276.435 | -161394.2407 | -1.6862 | OK
|  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 18847361.9892 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder | 33 | Digital | ABB03918 | 1 | 288011 | 292711 | 4700 | 2000 |  | 9400000 | 9437479.7949 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 9437479.7949 | 9375300.8462 | 62178.9487 | 0.66322 | OK
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 263791 | 267046 | 3255 | 2000 |  | 6510000 | 6535956.7515 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 6535956.7515 | 6321987.9686 | 213968.7829 | 3.3845 | OK
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 274454 | 277648 | 3194 | 2000 |  | 6388000 | 6413470.3117 |  | 6535956.7515 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 6413470.3117 | 5528971.9675 | 884498.3442 | 15.9975 | OK
12 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20118 | 20647 | 529 | 2000 |  | 1058000 | 1062218.4705 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 1062218.4705 | 1155307.5753 | -93089.1048 | -8.0575 | OK
[9 empty] | Total |  | 39111312 | 39267257.1011 |  |  |  |  | 0 | 39267257.1011 | 38440704.3356 | 826552.7655 | 2.1502 | OK
[8 empty] | Grand Total |  | 50012672 | 49814052.8 | 50012672 | 0.39872
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 1062218.4705
[5 empty] | Total = |  |  | 1062218.4705 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 | 11 | Import | 6604357 | 1 | 5335.14 | 5378.73 | 43.59 | 160000 | 6974400 |  | 7018997.2273
9 | 11kV 10/14 MVA Transformer T-1 | 11 | Import | DHK00121 | 2 | 9651.2 | 10067.8 | 416.6 | 4444 | 3702740.8 |  | 3726417.6716 |  | Converted to 30 days
[7 empty] | 0 |  | Total | 10677140.8 |  | 10745414.8989
| MOGBAZAR 11 kV SIDE | [5 empty] | 0
1 | 11 kV Nearest Feeder | 11 |  | HA021101060-02 | 1 | 72108037 | 73698434 | 1590397 | 1 |  | 1590397 | 1589546.8433 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1589546.8433 | 1558145.6337 | 31401.2096 | 2.0153 | OK
2 | 11kV Spare | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | 11 |  | HA021100937-02 | 1 | 75407218 | 76283711 | 876493 | 1 |  | 876493 | 876024.4652 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 876024.4652 | 849393.0553 | 26631.4098 | 3.1353 | OK
4 | 11 kV R K Mission Road Feeder | 11 |  | HA021101035-02 | 1 | 10974303 | 12539189 | 1564886 | 1 |  | 1564886 | 1564049.4804 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1564049.4804 | 1502639.6704 | 61409.8099 | 4.0868 | OK
5 | 11 kV Janapath Feeder | 11 |  | HA021100864-02 | 1 | 23326754 | 25420957 | 2094203 | 1 |  | 2094203 | 2093083.5306 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 2093083.5306 | 2005205.5254 | 87878.0052 | 4.3825 | OK
6 | 11 kV Dhalpur Feeder | 11 |  | HA021100851-02 | 1 | 84442992 | 85288108 | 845116 | 1 |  | 845116 | 844664.2379 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 844664.2379 | 860069.6023 | -15405.3643 | -1.7912 | OK
7 | 11kV WTP | 11 |  | X0599387 | 1 | 1406.5 | 1406.5 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11kV WTP | 0 | 145877.5724 | -145877.5724 | -100 | CHECK
10 | 11kV Kamalapur Water pumping | 11 |  | HA021100474-02 | 2 | 7628319 | 7638435 | 10116 | 1 | PT Missing From 14/06/23 | 20232 | 20221.1849 | Maniknagar | Converted to 30 days |  |  | 11kV Kamalapur Water pumping | 20221.1849 | 24456.8935 | -4235.7086 | -17.3191 | OK
11 | 11 kV Wasa Road Feeder | 11 |  | HA021001011-02 | 2 | 24448123 | 25380490 | 932367 | 1 | PT Missing From 14/06/23 | 1864734 | 1863737.1947 | Maniknagar | Converted to 30 days |  |  | 11 kV Wasa Road Feeder | 1863737.1947 | 2040994.3579 | -177257.1631 | -8.6848 | OK
12 | 11kV Sutikhalpar Feeder | 11 |  | HA021101047-02 | 2 | 78965769 | 79907658 | 941889 | 1 | PT Missing From 14/06/23 | 1883778 | 1882771.0147 | Maniknagar | Converted to 30 days |  |  | 11kV Sutikhalpar Feeder | 1882771.0147 | 2076315.0532 | -193544.0385 | -9.3215 | OK
13 | 11kV Spare | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 | 0.415 |  | AH14044078 | 1 | 391339 | 397817.5 | 6478.5 | 1 |  | 6478.5 | 6475.0369 | Maniknagar |  |  |  | Axuxilary -1 | 6475.0369 | 7064.9445 | -589.9076 | -8.3498 | OK
| Axuxilary -2 | 0.415 |  | AH14044072 | 1 | 364399.6 | 369244.1 | 4844.5 | 1 |  | 4844.5 | 4841.9103 | Maniknagar |  |  |  | Axuxilary -2 | 4841.9103 | 4813.3558 | 28.5545 | 0.59323 | OK
13 | AT-1 | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 10745414.8989 | 10751162 | 10745414.8989 | -0.053456
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 10745414.8989
[5 empty] | Total = |  |  | 10745414.8989 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder | 33 | 0 | DHK86054 | 1 | 2401.75 | 2425.39 | 23.64 | 270000 | 0 | 6382800 | 6408249.5782
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 274454 | 277648 | 3194 | 2000 | 0 | 6388000 | 6413470.3117
[9 empty] | Total | 0 | 12770800 | 12821719.8898
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 | 33 | Import | DHK86054 | 1 | 2401.75 | 2425.39 | 23.64 | 270000 | 6382800 |  |  |  | Reading Mismatch
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) | 33 | Import | DHK68120 | 1 | 2296.33 | 2322.11 | 25.78 | 270000 | 6960600
[7 empty] | 0 |  | Total | 13343400 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
1 | 33kV Biddyut Bhaban Circuit | 33 | Import |  | 1 | 0 | 0 | 0 | 600 | 0
|  | 33 | Export |  | 1 | 458833 | 476568 | 17735 | 600 | Estimated | 5563563.3 |  |  | From Remote End
[7 empty] | 0 |  | Total |  | 5563563.3
0
| Motijheel 33 KV SIDE | [5 empty] | 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK86053 | 1 | 2908.29 | 2935.58 | 27.29 | 180000 |  | 4912200
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) | 33 | Export | DHK86055 | 1 | 2290.59 | 2290.59 | 0 | 180000 |  | 0
[9 empty] | Total |  | 4912200 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 12821719.8898 |  | EXPORT TO OTHER S/S |  |  | 5563563.3 |  | 33 KV NET IMPORT |  | 7258156.5898
[5 empty] | 33 KV NET IMPORT |  |  | 7258156.5898 |  | 33 KV TX HV SIDE |  | 4912200
[10 empty] | LOSS UNITS=> |  | 2345956.5898
[10 empty] | LOSS % IN => |  | 32.32%
| TOTAL IMPORT |  | 12821719.8898
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 | 11 | Import | DHK86059 | 1 | 3289.14 | 3319.16 | 30.02 | 160000 | 4803200 |  | 4414300.2598 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 | 11 | Import | DHK86057 | 1 | 2553.12 | 2572.46 | 19.34 | 160000 | 3094400 |  | 2843856.33
[7 empty] | 0 |  | Total | 7897600 |  | 7258156.5898
| MOTIJHEEL 11 KV SIDE | [5 empty] | 0
6 | 11kV Fakirapul Panir Tank Feeder | 11 |  | DHK86058 | 1 | 1662.02 | 1678.29 | 16.27 | 60000 |  | 976200 | 1040852.4821 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 1040852.4821 | 913140.3988 | 127712.0833 | 13.986 | OK
7 | 11kV Station Road Feeder | 11 |  | DHK86075 | 1 | 2373.12 | 2374.67 | 1.55 | 60000 |  | 93000 | 99159.2715 | Motijheel |  |  |  | 11kV Station Road Feeder | 99159.2715 | 121832.4707 | -22673.1992 | -18.6101 | OK
8 | 11kV Box Culvert Road Feeder | 11 |  | DHK86071 | 1 | 3101.12 | 3125.25 | 24.13 | 60000 |  | 1447800 | 1543685.9492 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1543685.9492 | 1996966.8828 | -453280.9336 | -22.6985 | OK
9 | 11kV Mohamedan Club Feeder | 11 |  | DHK86062 | 1 | 1643.91 | 1662.49 | 18.58 | 60000 |  | 1114800 | 1188631.7835 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 1188631.7835 | 731597.9549 | 457033.8286 | 62.4706 | FAULT
10 | 11kV Amina Ahmed Co. | 11 |  | DHK95754 | 1 | 97956 | 104040 | 6084 | 60 |  | 365040 | 389216.1341 | Motijheel |  |  |  | 11kV Amina Ahmed Co. | 389216.1341 | 139323.2709 | 249892.8632 | 179.3619 | FAULT
11 | 11kV Bangabhaban -1 | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | 11 |  | DHK95753 | 1 | 43302 | 50590 | 7288 | 60 |  | 437280 | 466240.4972 | Motijheel |  |  |  | 11kV Sonali Bank | 466240.4972 | 345775.0268 | 120465.4704 | 34.8393 | OK
15 | 11kV NCC Bank Feeder | 11 |  | DHK68123 | 1 | 309.54 | 316.13 | 6.59 | 60000 |  | 395400 | 421586.8382 | Motijheel |  |  |  | 11kV NCC Bank Feeder | 421586.8382 | 147163.9744 | 274422.8637 | 186.4742 | FAULT
16 | 11kV IFIC BANK Feeder | 11 |  | DHK68116 | 1 | 383.41 | 389.19 | 5.78 | 60000 |  | 346800 | 369768.1221 | Ramna |  |  |  | 11kV IFIC BANK Feeder | 369768.1221 | 554880.5594 | -185112.4373 | -33.3608 | OK
17 | 11kV Arambagh Feeder | 11 |  | DHK68117 | 1 | 3354.56 | 3354.56 | 0 | 60000 | Estimated | 57982.68 | 61822.799 | Motijheel | 7 days Consumption |  |  | 11kV Arambagh Feeder | 61822.799 | 488536.1447 | -426713.3457 | -87.3453 | CHECK
18 | 11kV Nikotborti Feeder | 11 |  | DHK68114 | 1 | 1396.51 | 1410.57 | 14.06 | 60000 |  | 843600 | 899470.5531 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 899470.5531 | 655000.3125 | 244470.2406 | 37.3237 | OK
19 | 11kV Agrani Bank Feeder | 11 |  | DHK95756 | 1 | 357283 | 363305 | 6022 | 60 |  | 361320 | 385249.7632 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 385249.7632 | 144691.1372 | 240558.626 | 166.2566 | FAULT
20 | 11kV Bangladesh Bank-2 | 11 |  | DHK95755 | 1 | 515 | 521 | 6 | 60000 |  | 360000 | 383842.3413 | Motijheel |  |  |  | 11kV Bangladesh Bank-2 | 383842.3413 | 180939.3128 | 202903.0284 | 112.1387 | FAULT
21 | 11kV PDB Design Feeder 14 | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT | 0.415 |  | ELIC5429 | 1 | 397502 | 405596 | 8094 | 1 |  | 8094 | 8630.0553 | Motijheel |  |  |  | 11/0.4 kV AT | 8630.0553 | 3518.2644 | 5111.7909 | 145.293 | FAULT
[9 empty] | Grand Total | 7258156.5898 | 6807316.68 | 7258156.5898 | 6.6229
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 6888388.4677
[5 empty] | Ramna | at 33 KV level |  | 369768.1221
[5 empty] | Total = |  |  | 7258156.5898 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 | 132 | 0 | 06604332 | 1 | 1797.51 | 1809.31 | 11.8 | 1440000 | 0 | 16992000
2 | 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1609.68 | 1619.13 | 9.45 | 1440000 | 0 | 13608000
[8 empty] | Total Import/Export |  | 0 | 30600000
[9 empty] | Net Total | 30600000
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 | 132 | Imp/Main | 41812909527 | 1 | 285.51 | 299.67 | 14.16 | 1200000 | 16992000
|  | 132 | Imp/Backup | 41812909575 | 1 | 285.57 | 299.74 | 14.17 | 1200000 | 17004000
5 | 132 kV Mniknagar Circuit-2 | 132 | Imp/Main | 41812909512 | 1 | 107.49 | 118.86 | 11.37 | 1200000 | 13644000
|  | 132 | Imp/Backup | 41812909591 | 1 | 107.51 | 118.88 | 11.37 | 1200000 | 13644000
[7 empty] | 0 | Total Import/Export |  | 30636000 | 0
[7 empty] | 0 | Net Total |  | 30636000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 32.12 | 34.19 | 2.07 | 1200000 |  | 2484000
|  | 132 | Exp/Backup | 41812909570 | 1 | 32.1 | 34.17 | 2.07 | 1200000 |  | 2484000
7 | 132 kV Bangabhaban Circuit-2 | 132 | Exp/Main | 41812909559 | 1 | 80.49 | 83.53 | 3.04 | 1200000 |  | 3648000
|  | 132 | Exp/Backup | 41812909569 | 1 | 80.49 | 83.53 | 3.04 | 1200000 |  | 3648000
[7 empty] | 0 |  | Total |  | 6132000
| MOTIJHEEL 132 KV SIDE | [5 empty] | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41812909509 | 1 | 181.88 | 193.98 | 12.1 | 1200000 |  | 14520000
|  | 132 | Exp/Backup | 41812909594 | 1 | 181.88 | 193.98 | 12.1 | 1200000 |  | 14520000
6 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41812909508 | 1 | 98.54 | 106.87 | 8.33 | 1200000 |  | 9996000
|  | 132 | Exp/Backup | 41812909592 | 1 | 98.51 | 106.84 | 8.33 | 1200000 |  | 9996000
[9 empty] | Total |  | 24516000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 30600000 |  | EXPORT TO OTHER S/S |  |  | 6132000 |  | 132 KV NET IMPORT |  | 24468000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 24468000 |  | 33 KV NET IMPORT |  | 24379200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 88800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3629%
| 132 KV TOTAL IMPORT |  | 30600000
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41812909543 | 1 | 300.89 | 320.98 | 20.09 | 720000 | 14464800
|  | 33 | Backup | 41812909617 | 1 | 301.1 | 321.2 | 20.1 | 720000 | 14472000
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41812909468 | 1 | 162.34 | 176.11 | 13.77 | 720000 | 9914400
|  | 33 | Backup | 41812909600 | 1 | 162.31 | 176.08 | 13.77 | 720000 | 9914400
[7 empty] | 0 |  | Total | 24379200 |  | 0
| MOTIJHEEL 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) | 33 | Main | 41812909546 | 1 | 96.73 | 105.03 | 8.3 | 240000 |  | 1992000 | 1989186.2453 |  | 4210843.6543 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1989186.2453 | 1842469.3233 | 146716.9221 | 7.9631 | OK
|  | 33 | Backup | 41812909616 | 1 | 96.7 | 105 | 8.3 | 240000 |  | 1992000 | 1989186.2453 |  |  |  |  | 0 | 1989186.2453 | 1842469.3233 | 146716.9221 | 7.9631 | OK
17 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41812909482 | 1 | 178.97 | 188.24 | 9.27 | 240000 |  | 2224800 | 2221657.4089 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2221657.4089 | 2664272.9356 | -442615.5267 | -16.613 | OK
|  | 33 | Backup | 42003953371 | 1 | 179.01 | 188.28 | 9.27 | 240000 |  | 2224800 | 2221657.4089 |  |  |  |  | 0 | 2221657.4089 | 2664272.9356 | -442615.5267 | -16.613 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 4216800 | 4210843.6543 |  |  |  |  | 33 KV Feeders | 4210843.6543 | 4506742.2589 | -295898.6046 | -6.5657 | OK
10 | 33 kV Spare Feeder 1 | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 387.88 | 405.36 | 17.48 | 360000 |  | 6292800 | 6283911.2473 |  | 10662517.597 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 6283911.2473 | 5883203.4113 | 400707.836 | 6.811 | OK
|  | 33 | Backup | 41812909610 | 1 | 388.02 | 405.51 | 17.49 | 360000 |  | 6296400 | 6287506.1622 |  |  |  |  | 0 | 6287506.1622 | 5886797.3047 | 400708.8575 | 6.8069 | OK
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 174.02 | 191.2 | 17.18 | 360000 |  | 6184800 | 6176063.8003 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 6176063.8003 | 5753823.2508 | 422240.5495 | 7.3384 | OK
|  | 33 | Backup | 41812909595 | 1 | 174.09 | 191.27 | 17.18 | 360000 |  | 6184800 | 6176063.8003 |  | 9479790.5945 | Kamlapur Railway 33/11 kv ss |  | 0 | 6176063.8003 | 5753823.2508 | 422240.5495 | 7.3384 | OK
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 57.18 | 66.37 | 9.19 | 360000 |  | 3308400 | 3303726.7942 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 3303726.7942 | 2652293.2911 | 651433.5031 | 24.5611 | OK
|  | 33 | Backup | 41621865733 | 1 | 57.19 | 66.38 | 9.19 | 360000 |  | 3308400 | 3303726.7942 |  |  |  |  | 0 | 3303726.7942 | 2652293.2911 | 651433.5031 | 24.5611 | OK
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 123.9 | 136.08 | 12.18 | 360000 |  | 4384800 | 4378606.3497 |  |  |  |  | 33 kV P & T - 2 Feeder | 4378606.3497 | 4434864.3919 | -56258.0423 | -1.2685 | OK
|  | 33 | Backup | 41812909598 | 1 | 123.87 | 136.04 | 12.17 | 360000 |  | 4381200 | 4375011.4348 |  |  |  |  | 0 | 4375011.4348 | 4434864.3919 | -59852.9572 | -1.3496 | OK
20 | 33 kV Spare Feeder 9 | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) | 0.415 |  |  | 1 | 953.35 | 1040.3 | 86.95 | 300 |  | 26085 | 26048.1542 | [5 empty] | 26048.1542 | 25073.3959
[9 empty] | Total |  | 20196885 | 20168356.3457 |  |  |  |  | 0 | 20168356.3457 | 18749257.7411 | 1419098.6046 | 7.5688 | OK
[8 empty] | Grand Total |  | 24379200 | 24413685 | 24379200 | -0.14125
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) | 11 |  | 41812909493 | 1 | 92.1 | 100.03 | 7.93 | 250000 | 1982500 |  | 1993551.6524
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) | 11 |  | 41812909496 | 1 | 171.03 | 179.85 | 8.82 | 250000 | 2205000 |  | 2217292.0018
[7 empty] | 0 |  | Total | 4187500 |  | 4210843.6543
| MOTIJHEEL 11 kV SIDE | [5 empty] | 0
2 | 11 kV Central Weman | 11 |  | 41812909492 | 1 | 126.75 | 136.75 | 10 | 60000 |  | 600000 | 602582.0913 | Motijheel |  |  |  | 11 kV Central Weman | 602582.0913 | 559727.7485 | 42854.3429 | 7.6563 | OK
3 | 11 kV Spare Feeder 2 | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len | 11 |  | 41812909499 | 1 | 217.11 | 233.82 | 16.71 | 60000 |  | 1002600 | 1006914.6746 | Swamibag |  |  |  | 11 kV K. M. Das Len | 1006914.6746 | 933883.7569 | 73030.9178 | 7.8201 | OK
5 | 11 kV Gopibag | 11 |  | 41812909517 | 1 | 31.43 | 34.11 | 2.68 | 60000 |  | 160800 | 161492.0005 | Motijheel |  |  |  | 11 kV Gopibag | 161492.0005 | 148216.3898 | 13275.6107 | 8.9569 | OK
6 | 11kV SPICE TV | 11 |  | 41812909518 | 1 | 7.5 | 11.09 | 3.59 | 60000 |  | 215400 | 216326.9708 | Narinda |  |  |  | 11kV SPICE TV | 216326.9708 | 196416.8418 | 19910.129 | 10.1367 | OK
7 | 11 kV Spare Feeder 6 | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | 11 |  | 41812909473 | 1 | 358.82 | 367.96 | 9.14 | 60000 |  | 548400 | 550760.0315 | Motijheel |  |  |  | 11 kV South Kamlapur | 550760.0315 | 1048359.8303 | -497599.7988 | -47.4646 | CHECK
14 | 11 kV Spare Feeder 11 | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | 11 |  | 41812909514 | 1 | 153.52 | 166.1 | 12.58 | 60000 |  | 754800 | 758048.2709 | Motijheel |  |  |  | 11 kV Answer Camp | 758048.2709 | 729031.836 | 29016.4349 | 3.9801 | OK
16 | 11 kV Shapla Chattar | 11 |  | 41812909516 | 1 | 116.51 | 126.45 | 9.94 | 60000 |  | 596400 | 598966.5988 | Motijheel |  |  |  | 11 kV Shapla Chattar | 598966.5988 | 591058.0422 | 7908.5565 | 1.338 | OK
17 | 11 kV Sayedabad | 11 |  | 41812909497 | 1 | 84.55 | 89.79 | 5.24 | 60000 |  | 314400 | 315753.0159 | Swamibag |  |  |  | 11 kV Sayedabad | 315753.0159 | 300047.8135 | 15705.2024 | 5.2342 | OK
22 | 33/0.4 kV Aux Transformer | 0.415 |  | 41901920686 | 1 | 953.35 | 1040.3 | 86.95 | 1 |  |  | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4210843.6543 | 4192800 | 4210843.6543 | 0.43035
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 2671848.993
[6 empty] | Swamibag | at 33 KV level |  | 1322667.6905
[6 empty] | Narinda | at 33 KV level |  | 216326.9708
[6 empty] | Total = |  |  | 4210843.6543 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 33 KV SIDE
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 387.88 | 405.36 | 17.48 | 360000 | 0 | 6292800 | 6283911.2473
0 | 0 | 33 | Backup | 41812909610 | 1 | 388.02 | 405.51 | 17.49 | 360000 | 0 | 6296400 | 6287506.1622
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 123.9 | 136.08 | 12.18 | 360000 | 0 | 4384800 | 4378606.3497
0 | 0 | 33 | Backup | 41812909598 | 1 | 123.87 | 136.04 | 12.17 | 360000 | 0 | 4381200 | 4375011.4348
[9 empty] | Total | 0 | 10681200 | 10666112.5119
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
5 | 33 kV Bidyut Bhaban Circuit | 33 | Import | BD017079 | 1 | 15736.93 | 15736.93 | 0 | 1000 | 0
|  | 33 | Export | BD017079 | 1 |  | 0 | 0 | 1000 |  | 0
7 | 33 kV Motijheel Circuit-1 | 33 | Import | BD017081 | 1 | 132983 | 132983 | 0 | 1000 | 0
8 | 33 kV Motijheel Circuit-2 | 33 | Import | BD017082 | 1 | 21371.33 | 21371.33 | 0 | 1000 | 4384800
11 | 33 kV Kamlapur Circuit | 33 | Import | BD017085 | 1 |  | 0 | 0 | 1000 | 0
|  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
[7 empty] | 0 |  | Total | 4384800 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| MOGBAZAR T&T 33 KV SIDE | [5 empty] | 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | BD017080 | 1 | 30305 | 37374 | 7069 | 888.88 |  | 6283492.72 |  |  | % diffn betn 33 kV Impt & 11 kV Impt=
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | BD017084 | 1 | 94924 | 99683 | 4759 | 888.88 |  | 4230179.92
[9 empty] | Total |  | 10513672.64 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MOTIJHEEL 33 KV SIDE |  | 10666112.5119 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10666112.5119
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 10666112.5119 |  | 33 KV TX HV SIDE |  | 10513672.64
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 152439.8719
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.429%
| TOTAL IMPORT |  | 10666112.5119
11 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR T&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 | 11 | Import | BD014056 | 1 | 77487.94 | 77487.94 | 0 | 1000 | 6283492.72 |  | 10666112.5119 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | BD014057 | 1 | 83870 | 83870 | 0 | 1000 | 0 |  | 0
[6 empty] | 0 | 0 |  | Total | 6283492.72 |  | 10666112.5119
| MOGBAZAR T&T 11 KV SIDE |  |  |  |  | 0 | 0
12 | Inner Circular Road Feeder | 11 |  | BD014042 | 1 | 37233 | 39265 | 2032 | 1000 |  | 2032000 | 2044037.2926 | Motijheel |  |  |  | Inner Circular Road Feeder | 2044037.2926 | 2028898.6132 | 15138.6794 | 0.74615 | OK
13 | NSI New Building Expres Feeder | 11 |  | BD013982 | 1 | 8779 | 9206 | 427 | 1000 |  | 427000 | 429529.4901 | Ramna |  |  |  | NSI New Building Expres Feeder | 429529.4901 | 413128.6457 | 16400.8445 | 3.9699 | OK
14 | Police Hospital RMU Feeder | 11 |  | BD014044 | 1 | 3030 | 3211 | 181 | 1000 |  | 181000 | 182072.2195 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 182072.2195 | 167833.5123 | 14238.7072 | 8.4838 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | 11 |  | BD014013 | 1 | 29424 | 30996 | 1572 | 1000 |  | 1572000 | 1581312.3149 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1581312.3149 | 1420129.7195 | 161182.5955 | 11.3499 | OK
17 | Nayapalton Overhead Feeder | 11 |  | BD014014 | 1 | 21639 | 22642 | 1003 | 1000 |  | 1003000 | 1008941.636 | Ramna |  |  |  | Nayapalton Overhead Feeder | 1008941.636 | 976215.0449 | 32726.5911 | 3.3524 | OK
18 | Masjid Gali Over Head Feeder | 11 |  | BD014016 | 1 | 11857 | 12776 | 919 | 1000 |  | 919000 | 924444.0314 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 924444.0314 | 878891.4697 | 45552.5617 | 5.183 | OK
19 | Spare Feeder (Feeder-8) | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) | 11 |  | BD013988 | 1 | 12.18 | 12.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | 11 |  | BD014015 | 1 | 19862 | 20857 | 995 | 1000 |  | 995000 | 1000894.2451 | Ramna |  |  |  | Mid Way Over Head Feeder | 1000894.2451 | 972242.6541 | 28651.591 | 2.947 | OK
24 | Palton Thana Over Head Feeder | 11 |  | BD014033 | 1 | 19551 | 20890 | 1339 | 1000 |  | 1339000 | 1346932.0545 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1346932.0545 | 1294006.3108 | 52925.7437 | 4.0901 | OK
25 | Police Hospital (South) U/G Feeder 7 | 11 |  | BD014034 | 1 | 11851 | 12022 | 171 | 1000 |  | 171000 | 172012.9808 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 172012.9808 | 167833.5123 | 4179.4685 | 2.4902 | OK
26 | China Town Express Feeder | 11 |  | BD013943 | 1 | 5536 | 5830 | 294 | 1000 |  | 294000 | 295741.6161 | Ramna |  |  |  | China Town Express Feeder | 295741.6161 | 284025.9439 | 11715.6723 | 4.1249 | OK
27 | Fakirapul Bazar O/H Feeder | 11 |  | BD014032 | 1 | 25196 | 26543 | 1347 | 1000 |  | 1347000 | 1354979.4454 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1354979.4454 | 1402253.9607 | -47274.5153 | -3.3713 | OK
28 | PWD Ouarter (RMU) | 11 |  | BD013937 | 1 | 1861 | 2011 | 150 | 1000 |  | 150000 | 150888.5797 | Motijheel |  |  |  | PWD Ouarter (RMU) | 150888.5797 | 145985.3628 | 4903.2169 | 3.3587 | OK
29 | Postal Quarter RMU | 11 |  | BD013945 | 1 | 2327 | 2500 | 173 | 1000 |  | 173000 | 174024.8285 | Motijheel |  |  |  | Postal Quarter RMU | 174024.8285 | 164854.2192 | 9170.6094 | 5.5629 | OK
30 | 11/0.4 kV AT-1 | 0.415 |  | DHKH4409 | 1 | 1313 | 1316 | 3 | 100 |  | 300 | 301.7772 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 301.7772 | 0 | 301.7772 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV AT-2 | 0.415 |  | DHKH4411 | 1 | 454 | 454 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 0 | 5362.7276 | -5362.7276 | -100 | CHECK
[9 empty] | Grand Total | 10666112.5119 | 10603300 | 10666112.5119 | 0.59239
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 3723930.1462
[5 empty] | Ramna | at 33 KV level |  | 3659551.0189
[5 empty] | Rajarbag | at 33 KV level |  | 3282631.3469
[5 empty] | Total = |  |  | 10666112.5119 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 174.02 | 191.2 | 17.18 | 360000 | 0 | 6184800 | 6176063.8003
0 | 0 | 33 | Backup | 41812909595 | 1 | 174.09 | 191.27 | 17.18 | 360000 | 0 | 6184800 | 6176063.8003
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 57.18 | 66.37 | 9.19 | 360000 | 0 | 3308400 | 3303726.7942
0 | 0 | 33 | Backup | 41621865733 | 1 | 57.19 | 66.38 | 9.19 | 360000 | 0 | 3308400 | 3303726.7942
[9 empty] | Total | 0 | 9493200 | 9479790.5945
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
2 | 33 kV Motijheel Circuit-1 | 33 | Import | 101 | 1 | 231.8 | 254.6 | 22.8 | 270000 | 6156000
3 | 33 kV P&T Circuit | 33 | Import | 102 | 1 | 0 | 0 | 0 | 270000 | 0
6 | 33 kV Motijheel Circuit-2 | 33 | Import | 113 | 1 | 76.2 | 88.4 | 12.2 | 270000 | 3294000
[7 empty] | 0 |  | Total | 9450000 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
0
0
[7 empty] | 0 |  | Total | 0 | 0
0
| MOGBAZAR T&T 33 KV SIDE | [5 empty] | 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | 103 | 1 | 253.6 | 279.3 | 25.7 | 240000 |  | 6168000 |  |  | #VALUE!
4 | 33 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | 104 | 1 | 92.7 | 106.5 | 13.8 | 240000 |  | 3312000 |  |  | #VALUE!
[9 empty] | Total |  | 9480000 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 9479790.5945 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9479790.5945
[5 empty] | 33 KV NET IMPORT |  |  | 9479790.5945 |  | 33 KV TX HV SIDE |  | 9480000
[10 empty] | LOSS UNITS=> |  | -209.4055
[10 empty] | LOSS % IN => |  | -0.002209%
| TOTAL IMPORT |  | 9479790.5945
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | 42 | 1 | 301.8 | 332.5 | 30.7 | 200000 | 6140000 |  | 6165880.7468 |  | 0
10 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | 64 | 1 | 109.2 | 125.7 | 16.5 | 200000 | 3300000 |  | 3313909.8477 |  | 8704000
[7 empty] | 0 |  | Total | 9440000 |  | 9479790.5945
| KAMALAPUR RAILWAY 11 KV SIDE | [5 empty] | 0
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 315.7 | 349.8 | 34.1 | 40000 |  | 1364000 | 1381038.2208 | Rajarbag |  |  |  | Amtola O/H Feeder | 1381038.2208 | 1302977.567 | 78060.6538 | 5.9909 | OK
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 53.6 | 58.9 | 5.3 | 40000 |  | 212000 | 214648.1692 | Rajarbag |  |  |  | Police Telecom | 214648.1692 | 201076.785 | 13571.3842 | 6.7494 | OK
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 221 | 242.4 | 21.4 | 40000 |  | 856000 | 866692.6078 | Rajarbag |  |  |  | Railway Colony O/H | 866692.6078 | 735941.0332 | 130751.5746 | 17.7666 | OK
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 562.4 | 617 | 54.6 | 40000 |  | 2184000 | 2211281.1394 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 2211281.1394 | 2079133.9572 | 132147.1822 | 6.3559 | OK
5 | 11 KV Majar Feeder | 11 |  | 96 | 1 | 22.1 | 32 | 9.9 | 40000 |  | 396000 | 400946.5802 | Motijheel |  |  |  | 11 KV Majar Feeder | 400946.5802 | 382045.8916 | 18900.6887 | 4.9472 | OK
7 | 11 kV Feeder-6 | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 278.1 | 304.8 | 26.7 | 40000 |  | 1068000 | 1081340.777 | Rajarbag |  |  |  | Momenbagh O/H | 1081340.777 | 1001362.3894 | 79978.3875 | 7.987 | OK
9 | 11 kV Feeder-8 | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 190.2 | 198.6 | 8.4 | 40000 |  | 336000 | 340197.0984 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 340197.0984 | 337808.9988 | 2388.0995 | 0.70694 | OK
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 198.7 | 209.5 | 10.8 | 40000 |  | 432000 | 437396.2693 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 437396.2693 | 402153.5701 | 35242.6993 | 8.7635 | OK
13 | 11 kV Feeder-11 | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 48 | 53.5 | 5.5 | 40000 |  | 220000 | 222748.1001 | Motijheel |  |  |  | Dhaka Railway | 222748.1001 | 217162.9278 | 5585.1723 | 2.5719 | OK
15 | Jasimuddin Feeder-13 | 11 |  | 91 | 1 | 71.8 | 112.7 | 40.9 | 40000 |  | 1636000 | 1656435.8718 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1656435.8718 | 1097879.2463 | 558556.6256 | 50.876 | FAULT
16 | Police Box Feeder-14 | 11 |  | 18 | 1 | 36.4 | 52.8 | 16.4 | 40000 |  | 656000 | 664194.3349 | Motijheel |  |  |  | Police Box Feeder-14 | 664194.3349 | 643445.7121 | 20748.6228 | 3.2246 | OK
17 | 11 kV Feeder-15 | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) | 0.415 |  | DHKF 7632 | 1 | 787.87 | 816.23 | 28.36 | 100 |  | 2836 | 2871.4255 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 2871.4255 | 5128.4634 | -2257.0379 | -44.01 | CHECK
20 | Auxiliary -1 (AT-2 ) | 0.415 |  | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 9479790.5945 | 9362836 | 9479790.5945 | 1.2491
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Rajarbag | at 33 KV level |  | 6535465.7074
[5 empty] | Motijheel | at 33 KV level |  | 2944324.8871
[5 empty] | Total = |  |  | 9479790.5945 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 32.12 | 34.19 | 2.07 | 1200000 | 0 | 2484000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 | 132 |  | 41812909559 | 1 | 80.49 | 83.53 | 3.04 | 1200000 | 0 | 3648000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
[9 empty] | Total | 0 | 6132000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
[9 empty] | Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
BANGABHABAN 33 KV SIDE
|  | 132 | NET IMPORT | [7 empty] | 0
|  | 132 | [8 empty] | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 6132000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 6132000
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 6132000 |  | 33 KV TX HV SIDE |  | 6132000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 6132000
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) | 11 | Import | 4150744 | 1 | 1509378.4 | 1513142.4 | 3764 | 1000 | 3764000 |  | 3033281.8167
12 | 11 kV 28/35 MVA Transformer (GT-1) | 11 | Import | 4150742 | 1 | 1433418 | 1437263.2 | 3845.2 | 1000 | 3845200 |  | 3098718.1833
[7 empty] | 0 |  | Total | 7609200 |  | 6132000
| BANGABHABAN 11 KV SIDE | [5 empty] | 0
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 212943.22 | 214079.71 | 1136.49 | 1000 | Estimated | 788651.64 | 793502.3098 | Motijheel | 67 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 793502.3098 | 860468.6016 | -66966.2919 | -7.7825 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 23966.99 | 24049.87 | 82.88 | 1000 |  | 82880 | 83389.7606 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 83389.7606 | 79020.0597 | 4369.7009 | 5.5299 | OK
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 240728.715 | -240728.715 | -100 | CHECK
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33826.28 | 33840.33 | 14.05 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 20212.3186 | -20212.3186 | -100 | CHECK
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 706255.2 | 710599.0834 | Motijheel | 60 | Meter Bad |  | 11 kV Modhumita via Ovisar | 710599.0834 | 737544.5157 | -26945.4323 | -3.6534 | OK
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15661.1 | 15730.83 | 69.73 | 1000 |  | 69730 | 70158.8804 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 70158.8804 | 76837.1293 | -6678.2489 | -8.6914 | OK
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 244322.7 | 245496.9 | 1174.2 | 1000 |  | 1174200 | 1181422.0182 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1181422.0182 | 1217478.907 | -36056.8889 | -2.9616 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14139.81 | 14313.16 | 173.35 | 1000 |  | 173350 | 174416.2041 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 174416.2041 | 171420.6744 | 2995.5297 | 1.7475 | OK
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94891.92 | 94938.39 | 46.47 | 1000 | Estimated | 235418.4 | 236866.3611 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 236866.3611 | 245848.1719 | -8981.8108 | -3.6534 | OK
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163076.15 | 163401.03 | 324.88 | 1000 |  | 324880 | 326878.2024 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 326878.2024 | 270087.1078 | 56791.0946 | 21.027 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20481.33 | 20538.85 | 57.52 | 1000 | Estimated | 235418.4 | 236866.3611 | Motijheel | 20 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 236866.3611 | 245848.1719 | -8981.8108 | -3.6534 | OK
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 329585.76 | 331612.9056 | Motijheel | 28 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 331612.9056 | 368772.2578 | -37159.3523 | -10.0765 | OK
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122251.69 | 122597.98 | 346.29 | 1000 |  | 346290 | 348419.8864 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 348419.8864 | 313139.3465 | 35280.5399 | 11.2667 | OK
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 271490.95 | 272305.38 | 814.43 | 1000 |  | 814430 | 819439.2218 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 819439.2218 | 796304.7174 | 23134.5044 | 2.9052 | OK
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 79642.9 | 80121.74 | 478.84 | 1000 |  | 478840 | 481785.1466 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 481785.1466 | 474463.9677 | 7321.1789 | 1.543 | OK
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192345.5 | 192447.87 | 102.37 | 1000 | Estimated | 329585.76 | 331612.9056 | Motijheel | 28 | Meter Bad |  | 11 kV BCIC Feeder | 331612.9056 | 368772.2578 | -37159.3523 | -10.0765 | OK
23 | 11/0.4 kV AT-1 | 0.415 |  | 63412931 | 1 | 63258 | 63258 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV AT-2 | 0.415 |  | 63403117 | 1 | 13772 | 13772 | 0 | 1 | Estimated | 5000 | 5030.7529 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5030.7529 | 5053.0797 | -22.3267 | -0.44184 | OK
[9 empty] | Grand Total | 6132000 | 6094515.16 | 6132000 | 0.61506
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 0
[5 empty] | Ramna | at 33 KV level |  | 0
[5 empty] | Swamibag | at 33 KV level |  | 0
[5 empty] | Motijheel | at 33 KV level |  | 6132000
[5 empty] | Total = |  |  | 6132000 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 132 KV SIDE
1 | 132 kV Maniknagar Circuit-1 at Maniknagar | 132 | Import | 06604331 | 1 | 8792.35 | 8833.87 | 41.52 | 480000 | 19929600
2 | 132 kV Maniknagar Circui-2 at Maniknagar | 132 | Import | 06604334 | 1 | 8800.57 | 8842.46 | 41.89 | 480000 | 20107200
[8 empty] | Total Import/Export |  | 40036800 | 0
[9 empty] | Net Total | 40036800
NARINDA 132 KV SIDE (RECEIVING)
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 40036800
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 40036800
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 40036800 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 40036800
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 40036800 |  | 33 KV NET IMPORT |  | 40233600
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -196800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.4915%
| 132 KV TOTAL IMPORT |  | 40036800
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming | 33 | Import | 06604301 | 1 | 9167 | 9208.93 | 41.93 | 480000 | 20126400
7 | 132/33 kV 50/75 MVA GT-2 Incoming | 33 | Import | 06604304 | 1 | 8991.14 | 9033.03 | 41.89 | 480000 | 20107200
[7 empty] | 0 |  | Total | 40233600 |  | 0
| NARINDA 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 | 33 | Export | 06604300 | 1 | 9620.96 | 9670.71 | 49.75 | 180000 |  | 8955000 | 8996666.7386 |  | 17928231.9691 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 8996666.7386 | 8311261.3129 | 685405.4256 | 8.2467 | OK
8 | 33 kV 20/28 MVA Transformer T-4 | 33 | Export | 06604303 | 1 | 9750.28 | 9799.67 | 49.39 | 180000 |  | 8890200 | 8931565.2305 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 8931565.2305 | 8266228.471 | 665336.7596 | 8.0489 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 17845200 | 17928231.9691 |  |  |  |  | 33 KV Feeders | 17928231.9691 | 16577489.7839 | 1350742.1852 | 8.1481 | OK
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1513800 | 1520843.5632 |  | 1520843.5632 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1520843.5632 | 1558036.6112 | -37193.048 | -2.3872 | OK
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 10281481.1676 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5618.07 | 5643.19 | 25.12 | 180000 |  | 4521600 | 4542638.5623 |  |  |  |  | 33 kV Kumertully-1 Feeder | 4542638.5623 | 4539310.47 | 3328.0923 | 0.073317 | OK
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5474.62 | 5507.58 | 32.96 | 180000 |  | 5932800 | 5960404.7378 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 5960404.7378 | 5803832.6724 | 156572.0654 | 2.6977 | OK
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 10233864 | 10281481.1676 |  | 10503043.3 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 10281481.1676 | 9460530.4625 | 820950.7051 | 8.6776 | OK
[9 empty] | Total |  | 22202064 | 22305368.0309 |  |  |  |  | 0 | 22305368.0309 | 21361710.2161 | 943657.8148 | 4.4175 | OK
[8 empty] | Grand Total |  | 40233600 | 40047264 | 40233600 | 0.46529
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming | 11 | Import | 06604351 | 1 | 10819.45 | 10875.13 | 55.68 | 160000 | 8908800 |  | 9008608.9346
9 | 33/11 kV 20/28 MVA T-4 Incoming | 11 | Import | 06604295 | 1 | 11151.06 | 11206.19 | 55.13 | 160000 | 8820800 |  | 8919623.0345
[7 empty] | 0 |  | Total | 17729600 |  | 17928231.9691
| NARINDA 11 kV SIDE | [5 empty] | 0
1 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24474.94 | 24616.19 | 141.25 | 8000 |  | 1130000 | 1139801.4532 | Narinda |  |  |  | 11 kV Bonogram Feeder | 1139801.4532 | 1096395.2732 | 43406.18 | 3.959 | OK
2 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16557.29 | 16642.26 | 84.97 | 8000 |  | 679760 | 685656.1379 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 685656.1379 | 629657.0471 | 55999.0908 | 8.8936 | OK
3 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 471.15 | 487.34 | 16.19 | 40000 |  | 647600 | 653217.1868 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 653217.1868 | 492385.8425 | 160831.3443 | 32.6637 | OK
4 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5473.81 | 5501.64 | 27.83 | 40000 |  | 1113200 | 1122855.7324 | Narinda |  |  |  | 11 kV Manashi Feeder | 1122855.7324 | 1066634.3599 | 56221.3726 | 5.2709 | OK
5 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3323.44 | 3373.76 | 50.32 | 40000 |  | 2012800 | 2030258.73 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 2030258.73 | 1913892.8816 | 116365.8484 | 6.0801 | OK
6 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8477.29 | 8518.25 | 40.96 | 40000 |  | 1638400 | 1652611.2397 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1652611.2397 | 1532808.0158 | 119803.2239 | 7.8159 | OK
7 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7223.58 | 7262.99 | 39.41 | 40000 |  | 1576400 | 1590073.4608 | Narinda |  |  |  | 11 kV Narinda Feeder | 1590073.4608 | 1585232.3889 | 4841.072 | 0.30539 | OK
10 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5932.66 | 5965.54 | 32.88 | 40000 |  | 1315200 | 1326607.8506 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1326607.8506 | 1271895.9437 | 54711.9069 | 4.3016 | OK
11 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 4979.47 | 5006.32 | 26.85 | 40000 |  | 1074000 | 1083315.7174 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 1083315.7174 | 1015016.5156 | 68299.2018 | 6.7289 | OK
12 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7734.95 | 7762.22 | 27.27 | 40000 |  | 1090800 | 1100261.4381 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 1100261.4381 | 886375.1694 | 213886.2688 | 24.1304 | OK
13 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6319.72 | 6347.36 | 27.64 | 40000 |  | 1105600 | 1115189.8112 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 1115189.8112 | 1101315.099 | 13874.7122 | 1.2598 | OK
14 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 22163.2 | 26064.5 | 3901.3 | 444.44 |  | 1733893.772 | 1748933.3106 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1748933.3106 | 1624153.5662 | 124779.7444 | 7.6828 | OK
16 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 374036 | 384194 | 10158 | 80 |  | 812640 | 819688.7194 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 819688.7194 | 775800.0686 | 43888.6508 | 5.6572 | OK
17 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 29470.6 | 31907.7 | 2437.1 | 444.44 |  | 1083144.724 | 1092539.7614 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 1092539.7614 | 1048880.237 | 43659.5244 | 4.1625 | OK
18 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 35683.5 | 36247.2 | 563.7 | 1000 |  | 563700 | 568589.4506 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 568589.4506 | 537047.3757 | 31542.0749 | 5.8732 | OK
1 | 11/0.4 kV Aux Transformer-1 | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17729600 | 17577138.496 | 17729600 | 0.86739
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Narinda | at 33 KV level |  | 11365009.206
[5 empty] | Maniknagar | at 33 KV level |  | 653217.1868
[5 empty] | Swamibag | at 33 KV level |  | 5711373.6072
[5 empty] | Total = |  |  | 17729600 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5618.07 | 5643.19 | 25.12 | 180000 | 0 | 4521600 | 4542638.5623
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5474.62 | 5507.58 | 32.96 | 180000 | 0 | 5932800 | 5960404.7378
| MITFORD 33 KV SIDE | [9 empty] | 10454400 | 10503043.3
1 | Kumartuly Circuit-1 | 33 | 0 | DHK-66493 | 1 | 1284426 | 1285151 | 725 | 180 | 0 | 130500 | 130500
6 | Kumartuly Circuit-2 | 33 | 0 | DHK-60914 | 1 | 759468.5 | 759469.7 | 1.2 | 180 | 0 | 216 | 216
[9 empty] | Total |  | 130716 | 130716
| KUMERTULY 33 KV SIDE (RECEIVING) | [9 empty] | 10585116 | 10633759.3
5 | 33 kV Mitford Circuit-1 | 33 | Import | DHK60965 | 1 | 278764.4 | 279488 | 723.6 | 180 | 130248
6 | 33 kV Narinda Circuit-1 | 33 | Import | DHK60959 | 1 | 965418 | 973808 | 8390 | 540 | 4530600
9 | 33 kV Mitford Circuit-2 | 33 | Import | DHK86072 | 1 | 1760.52 | 1760.52 | 0 | 180000 | 0
10 | 33 kV Narinda Circuit-2 | 33 | Import | DHK60957 | 1 | 871496.3 | 882448.2 | 10951.9 | 540 | 5914026
[7 empty] | 0 |  | Total | 10574874 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| KUMERTULY 33 KV SIDE | [5 empty] | 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK60960 | 1 | 70252 | 96076.8 | 25824.8 | 180 |  | 4648464
8 | 33/11 kV 20/28 MVA Transformer (T-2) | 33 | Export | DHK60958 | 1 | 228896.8 | 261765.4 | 32868.6 | 180 |  | 5916348
[9 empty] | Total |  | 10564812 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 10503043.3 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10633759.3
| MITFORD 33 KV SIDE |  | 130716 |  | 33 KV NET IMPORT |  |  | 10633759.3 |  | 33 KV TX HV SIDE |  | 10574874
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 58885.3
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5538%
| TOTAL IMPORT |  | 10633759.3
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming | 11 | Import | 06604403 | 1 | 7218.92 | 7219.28 | 0.36 | 160000 | 57600 |  | 102796.8139 |  | 0
20 | 33/11 kV 20/28 MVA T-2 Incoming | 11 | Import | 06604410 | 1 | 6592.14 | 6629.02 | 36.88 | 160000 | 5900800 |  | 10530962.4862 |  |  | PT Damage
[7 empty] | 0 |  | Total | 5958400 |  | 10633759.3
| KUMERTULY 11 KV SIDE | [5 empty] | 0 | [7 empty] | 85
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62100 | 62362.9 | 262.9 | 2222.22 | Estimated | 470836.8 | 476949.7245 | Banglabazar | 40 | 20 |  | 11kV Babubazar Feeder | 476949.7245 | 555416.4351 | -78466.7106 | -14.1275 | OK
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4531.4 | 4560.66 | 29.26 | 40000 | Estimated | 1412510.4 | 1430849.1736 | Banglabazar | 120 | 65 |  | 11kV Islampur Feeder | 1430849.1736 | 1481110.4937 | -50261.32 | -3.3935 | OK
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  | 21.6667 |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5121.51 | 5132.38 | 10.87 | 40000 | Estimated | 529691.4 | 536568.4401 | Banglabazar | 45 | 41.6667 |  | 11kV Majar O/H Feeder | 536568.4401 | 493703.4979 | 42864.9422 | 8.6823 | OK
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5393.48 | 5420.2 | 26.72 | 40000 | Estimated | 1200633.84 | 1216221.7976 | Banglabazar | 102 |  |  | 11kV Sadarghat Feeder | 1216221.7976 | 1419397.5564 | -203175.7588 | -14.3142 | OK
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | Estimated | 39563.37 | 40077.0255 | Bangshal | 220 |  |  | 11kV Mitford Hospital Feeder | 40077.0255 | 0 | 40077.0255 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4023.81 | 4052.11 | 28.3 | 40000 | Estimated | 823964.4 | 834662.018 | Banglabazar | 70 |  |  | 11kV Zindabahar Feeder | 834662.018 | 740555.2468 | 94106.7711 | 12.7076 | OK
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1130008.32 | 1144679.3389 | Banglabazar | 96 |  |  | 11kV Police fari Feeder | 1144679.3389 | 925694.0585 | 218985.2804 | 23.6563 | OK
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5853.24 | 5878.45 | 25.21 | 40000 |  | 1008400 | 1021492.1651 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 1021492.1651 | 1019206.2302 | 2285.9349 | 0.22429 | OK
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8098.57 | 8147.67 | 49.1 | 40000 |  | 1964000 | 1989498.8221 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1989498.8221 | 1947085.7372 | 42413.085 | 2.1783 | OK
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3736.6 | 3746.74 | 10.14 | 40000 |  | 405600 | 410865.9482 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 410865.9482 | 427409.0643 | -16543.1161 | -3.8706 | OK
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7172.56 | 7200.1 | 27.54 | 40000 | Estimated | 1235946.6 | 1251993.0269 | Banglabazar | 105 |  |  | 11kV Dholaikhal Feeder | 1251993.0269 | 1073805.1079 | 178187.919 | 16.5941 | OK
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3572.31 | 3579.1 | 6.79 | 40000 |  | 271600 | 275126.2119 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 275126.2119 | 281286.3072 | -6160.0954 | -2.19 | OK
27 | 11/0.4 kV AT-1 | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 | 0.415 |  | 05378636 | 1 | 163007.6 | 165364.8 | 2357.2 | 2 |  | 4714.4 | 4775.6076 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 4775.6076 | 4915.4072 | -139.7996 | -2.8441 | OK
[9 empty] | Grand Total | 10633759.3 | 10497469.53 | 10633759.3 | 1.2983
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 40077.0255
[5 empty] | Banglabazar | at 33 KV level |  | 10593682.2746
[5 empty] | Total = |  |  | 10633759.3 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 10233864 | 10281481.1676
[9 empty] | Total | 0 | 10233864 | 10281481.1676
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 | 33 | Import | Mat-152447/1191738/007 | 1 | 111908100 | 114810700 | 2902600 | 1 | 2902600
5 | 33 kV Narinda Circuit-2 | 33 | Import | Mat-152447/1191738/002 | 1 | 221969900 | 229270900 | 7301000 | 1 | 7301000
[7 empty] | 0 |  | Total | 10203600 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| MOGBAZAR T&T 33 KV SIDE | [5 empty] | 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) | 33 | Export | Mat-152447/1191738/009 | 1 | 119054000 | 121964700 | 2910700 | 1 |  | 2910700 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) | 33 | Export | Mat-152447/1191738/004 | 1 | 219485000 | 226792500 | 7307500 | 1 |  | 7307500 |  |  | #VALUE!
[9 empty] | Total |  | 10218200 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 10281481.1676 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10281481.1676
[5 empty] | 33 KV NET IMPORT |  |  | 10281481.1676 |  | 33 KV TX HV SIDE |  | 10218200
[10 empty] | LOSS UNITS=> |  | 63281.1676
[10 empty] | LOSS % IN => |  | 0.6155%
| TOTAL IMPORT |  | 10281481.1676
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 | 11 | Import | 340180016886 | 1 | 119075109 | 121982461 | 2907352 | 1 | 2907352 |  | 2920879.6243 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 | 11 | Import | 340180012685 | 1 | 222771288 | 230097800 | 7326512 | 1 | 7326512 |  | 7360601.5433
[7 empty] | 0 |  | Total | 10233864 |  | 10281481.1676
| BANGSHAL 11 KV SIDE | [5 empty] | 0
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 36815436 | 37591630 | 776194 | 1 |  | 776194 | 778854.3109 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 778854.3109 | 716311.3918 | 62542.919 | 8.7312 | OK
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 46867285 | 48292149 | 1424864 | 1 |  | 1424864 | 1429747.5487 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1429747.5487 | 1353751.6158 | 75995.933 | 5.6137 | OK
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 19159807 | 19895217 | 735410 | 1 |  | 735410 | 737930.5287 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 737930.5287 | 715455.6721 | 22474.8566 | 3.1413 | OK
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 43501879 | 45156791 | 1654912 | 1 |  | 1654912 | 1660584.0104 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1660584.0104 | 1409457.3709 | 251126.6395 | 17.8173 | OK
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 59902495 | 61068329 | 1165834 | 1 |  | 1165834 | 1169829.7548 | Bangshal |  |  |  | 11 kV French Road Feeder | 1169829.7548 | 1127796.6211 | 42033.1336 | 3.727 | OK
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 27364546 | 28992386 | 1627840 | 1 |  | 1627840 | 1633419.2244 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 1633419.2244 | 1486833.0286 | 146586.1958 | 9.859 | OK
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 59668688 | 61260126 | 1591438 | 1 |  | 1591438 | 1596892.4609 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1596892.4609 | 1498407.2378 | 98485.2231 | 6.5727 | OK
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 47860599 | 49123470 | 1262871 | 1 |  | 1262871 | 1267199.3373 | Narinda |  |  |  | 11 kV Suritolla Feeder | 1267199.3373 | 1145519.8164 | 121679.521 | 10.6222 | OK
13 | AT-1 | 0.415 |  | DHK-4415 | 1 | 685.05 | 727.72 | 42.67 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 | 0.415 |  | DHK-4410 | 1 | 658.98 | 659.01 | 0.03 | 100 |  | 7000 | 7023.9917 | Bangshal |  |  |  | AT-2 | 7023.9917 | 6997.7081 | 26.2836 | 0.3756 | OK
[9 empty] | Grand Total | 10281481.1676 | 10246363 | 10281481.1676 | 0.34274
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 7584534.2816
[5 empty] | Banglabazar | at 33 KV level |  | 1429747.5487
[5 empty] | Narinda | at 33 KV level |  | 1267199.3373
[5 empty] | Total = |  |  | 10281481.1676 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDING)
1 | 132kV Kazla Circuit-1 at Maniknagar | 132 | Import | ABB03905 | 1 | 681650 | 714735 | 33085 | 1000 | 33085000 |  |  |  | 132 kV line Loss=
2 | 132kV Kazla Circuit-2 at Maniknagar | 132 | Import | ABB03904 | 1 | 514116 | 536435 | 22319 | 1000 | 22319000 |  |  |  | 100
[7 empty] | 0 | Total Import/Export |  | 55404000 | 0
[7 empty] | 0 |  | Net Total | 55404000
| KAZLA 132 KV SIDE (RECEIVING) | [5 empty] | 0
3 | 132kV Maniknagar Circuit-1 | 132 | Main | 41812909505 | 1 | 568.24 | 595.84 | 27.6 | 1200000 | 33120000
|  | 132 | Backup | 41812909603 | 1 | 568.22 | 595.82 | 27.6 | 1200000 | 33120000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 | 132 | Main | 41812909540 | 1 | 427.53 | 446.1 | 18.57 | 1200000 | 22284000
|  | 132 | Backup | 41812909587 | 1 | 427.54 | 446.12 | 18.58 | 1200000 | 22296000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
[7 empty] | 0 | Total Import/Export |  | 55404000 | 0
[7 empty] | 0 | Net Total |  | 55404000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| KAZLA 132 KV SIDE | [5 empty] | 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Main | 41812909542 | 1 | 568.57 | 596.18 | 27.61 | 1200000 |  | 33132000 |  |  | #DIV/0!
|  | 132 | Backup | 41812909589 | 1 | 568.9 | 596.53 | 27.63 | 1200000 |  | 33156000
7 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Main | 41812909501 | 1 | 427.37 | 445.95 | 18.58 | 1200000 |  | 22296000 |  |  | 100
|  | 132 | Backup | 41812909606 | 1 | 427.32 | 445.89 | 18.57 | 1200000 |  | 22284000
[9 empty] | Total |  | 55428000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 55404000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 55404000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 55404000 |  | 33 KV NET IMPORT |  | 55224000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 180000
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3249%
| 132 KV TOTAL IMPORT |  | 55404000
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) | 33 | Main | 41812909533 | 1 | 943.91 | 989.76 | 45.85 | 720000 | 33012000
|  | 33 | Backup | 41812909582 | 1 | 943.98 | 989.83 | 45.85 | 720000 | 33012000
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) | 33 | Main | 41812909479 | 1 | 709.98 | 740.83 | 30.85 | 720000 | 22212000
|  | 33 | Backup | 41812909622 | 1 | 709.89 | 740.73 | 30.84 | 720000 | 22204800
[7 empty] | 0 |  | Total | 55224000 |  | 0
| KAZLA 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 | 33 | Main | 41812909465 | 1 | 942.09 | 990.49 | 48.4 | 240000 |  | 11616000 | 11609794.9909 |  | 38938388.8611 | Kazla 33/11 kv ss | 1.6006 | 33/11 kV 20/28 MVA T-1 | 11609794.9909 | 11426857.287 | 182937.7039 | 1.6009 | OK
|  | 33 | Backup | 41812909596 | 1 | 941.85 | 990.24 | 48.39 | 240000 |  | 11613600 | 11607396.273 |  |  |  |  | 0 | 11607396.273 | 11424454.6677 | 182941.6052 | 1.6013 | OK
13 | 33/11 kV 28/35 MVA T-5 | 33 | Main | 41812909536 | 1 | 94.27 | 104.99 | 10.72 | 360000 |  | 3859200 | 3857138.5011 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 3857138.5011 | 2648887.7542 | 1208250.7469 | 45.6135 | FAULT
|  | 33 | Backup | 41812909578 | 1 | 94.28 | 105 | 10.72 | 360000 |  | 3859200 | 3857138.5011 |  |  |  |  | 0 | 3857138.5011 | 2648887.7542 | 1208250.7469 | 45.6135 | FAULT
14 | 33/11 kV 20/28 MVA T-2 | 33 | Main | 41812909554 | 1 | 953.56 | 996.99 | 43.43 | 240000 |  | 10423200 | 10417632.1582 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 10417632.1582 | 10396133.6167 | 21498.5415 | 0.20679 | OK
|  | 33 | Backup | 41812909613 | 1 | 952.62 | 996.01 | 43.39 | 240000 |  | 10413600 | 10408037.2863 |  |  |  |  | 0 | 10408037.2863 | 10381717.901 | 26319.3853 | 0.25352 | OK
17 | 33/11 kV 20/28 MVA T-3 | 33 | Main | 41812909544 | 1 | 836.01 | 869.25 | 33.24 | 240000 |  | 7977600 | 7973338.5434 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 7973338.5434 | 7916630.5216 | 56708.0218 | 0.71632 | OK
|  | 33 | Backup | 41812909614 | 1 | 836.04 | 869.27 | 33.23 | 240000 |  | 7975200 | 7970939.8254 |  |  |  |  | 0 | 7970939.8254 | 7919033.1409 | 51906.6845 | 0.65547 | OK
22 | 33/11 kV 10/14 MVA T-4 | 33 | Main | 41812909506 | 1 | 428.08 | 449.26 | 21.18 | 240000 |  | 5083200 | 5080484.6675 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 5080484.6675 | 5807130.7954 | -726646.1278 | -12.513 | OK
|  | 33 | Backup | 41812909602 | 1 | 428.14 | 449.4 | 21.26 | 240000 |  | 5102400 | 5099674.4113 |  |  |  |  | 0 | 5099674.4113 | 5797520.3182 | -697845.9069 | -12.037 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 38959200 | 38938388.8611 |  |  |  |  | 33 KV Feeders | 38938388.8611 | 38195639.9748 | 742748.8863 | 1.9446 | OK
10 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 531.04 | 550.9 | 19.86 | 360000 |  | 7149600 | 7145780.8426 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 7145780.8426 | 8991802.6486 | -1846021.806 | -20.5301 | OK
|  | 33 | Backup | 41812909580 | 1 | 531 | 550.86 | 19.86 | 360000 |  | 7149600 | 7145780.8426 |  |  |  |  | 0 | 7145780.8426 | 8991802.6486 | -1846021.806 | -20.5301 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Spare Feeder 7 | 33 | Main | 41812909523 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909565 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 577.58 | 602.93 | 25.35 | 360000 |  | 9126000 | 9121125.0936 | Kazla |  |  |  | 33 kV Zahir Steel | 9121125.0936 | 10343275.9926 | -1222150.899 | -11.8159 | OK
|  | 33 | Backup | 41812909563 | 1 | 577.77 | 603.14 | 25.37 | 360000 |  | 9133200 | 9128321.2475 |  |  |  |  | 0 | 9128321.2475 | 10343275.9926 | -1214954.745 | -11.7463 | OK
| Auxiliary Transformer-3 (AT-3) | 0.415 |  |  | 1 | 2173.65 | 2290.62 | 116.97 | 160 |  | 18715.2 | 18705.2028 | [5 empty] | 18705.2028 | 18881.384
[9 empty] | Total |  | 16294315.2 | 16285611.1389 |  |  |  |  | 0 | 16285611.1389 | 19353960.0252 | -3068348.8863 | -15.8539 | OK
[8 empty] | Grand Total |  | 55224000 | 55253515.2 | 55224000 | -0.053418
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | KAZLA at 33 KV level |  |  | 16266905.9361
[6 empty] | Kazla 33/11 KV Substation |  |  | 38938388.8611
[8 empty] | Total = | 55205294.7972 | -18705.2028
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK-61009 | 1 | 7704264 | 7767478 | 63214 | 180 | 11378520 |  | 11609794.9909
30 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK-61124 | 1 | 696229.7 | 752227.8 | 55998.1 | 180 | 10079658 |  | 10417632.1582
24 | 33/11 kV 20/28 MVA T-3 Incoming | 11 |  | DHK-61015 | 1 | 349719.9 | 393834.4 | 44114.5 | 180 | 7940610 |  | 7973338.5434
39 | 33/11 kV 10/14 MVA T-4 Incoming | 11 |  | 8L55984 | 1 | 25488.7 | 26726 | 1237.3 | 4000 | 4949200 |  | 5080484.6675
42 | 33/11 kv 28/35 MVA T-5 Incomer | 11 |  | DHK00112 | 1 | 96519.7 | 100858.5 | 4338.8 | 888.8 | 3856325.44 |  | 3857138.5011
[7 empty] | 0 |  | Total | 38204313.44 |  | 38938388.8611
| KAZLA 11 kV SIDE | [5 empty] | 0
17 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 783779.8 | 813181.6 | 29401.8 | 60 |  | 1764108 | 1792344.292 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1792344.292 | 1710856.4639 | 81487.8281 | 4.763 | OK
18 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1883347.2 | 1913492.0332 | Kazla | 160 |  |  | 11 kV Madrasa Bazar Feeder | 1913492.0332 | 1855425.2355 | 58066.7977 | 3.1296 | OK
19 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 3001584.6 | 3049627.928 | Kazla | 255 |  |  | 11 kV Kazla Feeder | 3049627.928 | 2968680.3768 | 80947.5512 | 2.7267 | OK
20 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963851 | 36963854 | 3 | 1000 | Estimated | 1059382.8 | 1076339.2687 | Maniknagar | 90 |  |  | 11 kV Sayedabad Feeder | 1076339.2687 | 556627.5706 | 519711.698 | 93.3679 | FAULT
21 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 110052.4 | 112225.6 | 2173.2 | 1000 |  | 2173200 | 2207984.2138 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 2207984.2138 | 2092993.2394 | 114990.9743 | 5.4941 | OK
23 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 41024544 | 0 | 1 | Estimated | 1706783.4 | 1734102.1551 | Kazla | 145 |  |  | 11 kV Matuail Feeder | 1734102.1551 | 1855425.2355 | -121323.0804 | -6.5388 | OK
25 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 647129.1 | 684518.2 | 37389.1 | 60 |  | 2243346 | 2279252.9698 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2279252.9698 | 2232712.5636 | 46540.4062 | 2.0845 | OK
26 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 579724.6 | 602385.9 | 22661.3 | 60 |  | 1359678 | 1381440.9902 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1381440.9902 | 1371332.0993 | 10108.8909 | 0.73716 | OK
27 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 947647 | 986124.4 | 38477.4 | 60 |  | 2308644 | 2345596.1288 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2345596.1288 | 2459477.0573 | -113880.9285 | -4.6303 | OK
28 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 178496.3 | 212446.1 | 33949.8 | 60 |  | 2036988 | 2069592.0061 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 2069592.0061 | 1962979.7252 | 106612.2809 | 5.4311 | OK
31 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 33062 | 73285.9 | 40223.9 | 60 |  | 2413434 | 2452063.3964 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 2452063.3964 | 2370251.5382 | 81811.8581 | 3.4516 | OK
32 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 249904.8 | 290452 | 40547.2 | 60 |  | 2432832 | 2471771.8805 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 2471771.8805 | 3092469.9692 | -620698.0887 | -20.0713 | OK
33 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 362270.4 | 383226.2 | 20955.8 | 60 |  | 1257348 | 1277473.0974 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 1277473.0974 | 837095.6004 | 440377.497 | 52.6078 | FAULT
34 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1912724 | 1945817 | 33093 | 60 |  | 1985580 | 2017361.1702 | Jurain |  |  |  | 11 kV Donia Feeder | 2017361.1702 | 1952856.964 | 64504.2062 | 3.3031 | OK
35 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 26329191 | 27937314 | 1608123 | 1 |  | 1608123 | 1633862.5979 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1633862.5979 | 1591423.3402 | 42439.2577 | 2.6667 | OK
36 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 25278265 | 25965046 | 686781 | 1 |  | 686781 | 697773.6086 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 697773.6086 | 686441.9856 | 11331.623 | 1.6508 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 2894.5 | 3086.1 | 191.6 | 10000 |  | 1916000 | 1946667.4736 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1946667.4736 | 1703398.1226 | 243269.351 | 14.2814 | OK
38 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 808.3 | 814.2 | 5.9 | 4000 |  | 23600 | 23977.7413 | Kazla | From 01-07-2023 17:25 No Load (Shifted to Jenith) |  |  | 11 kV Dharmik Para | 23977.7413 | 1140208.9403 | -1116231.199 | -97.8971 | CHECK
41 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 12649 | 13448.4 | 799.4 | 4000 |  | 3197600 | 3248780.7482 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 3248780.7482 | 3103743.9224 | 145036.8258 | 4.673 | OK
43 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 19756.3 | 20321.3 | 565 | 1000 |  | 565000 | 574043.3834 | Kazla |  |  |  | 11 kV Jenith Feeder | 574043.3834 | 0 | 574043.3834 | #DIV/0! | #DIV/0!
45 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 16523.9 | 17160.4 | 636.5 | 2000 |  | 1273000 | 1293375.6231 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1293375.6231 | 1288887.6302 | 4487.9929 | 0.34821 | OK
46 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 34893.9 | 35605.2 | 711.3 | 2000 |  | 1422600 | 1445370.1189 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 1445370.1189 | 1356006.601 | 89363.518 | 6.5902 | OK
47 | 33/0.4 kV AT-1 | 0.415 |  | 503043 | 1 | 96204 | 96204 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-1 | 0 | 244.069 | -244.069 | -100 | CHECK
48 | 33/0.4 kV AT-2 | 0.415 |  | 503044 | 1 | 92456 | 93292 | 836 | 10 |  | 6000 | 6096.0359 | Kazla |  |  |  | 33/0.4 kV AT-2 | 6096.0359 | 6101.7246 | -5.6887 | -0.093231 | OK
23 | Auxiliary Transformer | 0.415 |  | 41901920685 | 1 | 2173.65 | 2290.62 | 116.97 | 160 |  |  | 0 | Kazla |  |  |  | Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 38938388.8611 | 38324960 | 38938388.8611 | 1.6006
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 1277473.0974
[5 empty] | Jurain | at 33 KV level |  | 8956661.7502
[5 empty] | Swamibag | at 33 KV level |  | 2069592.0061
[5 empty] | Maniknagar | at 33 KV level |  | 2521709.3876
[5 empty] | Shyampur | at 33 KV level |  | 2471771.8805
[5 empty] | Kazla | at 33 KV level |  | 21641180.7393
[5 empty] | Total = |  |  | 38938388.8611 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT | 132 |  | 8993532 | 1 | 2226.297 | 2227.617 | 1.32 | 960000 | 0 | 1267200
|  | 132 |  |  | 1 | 666.114 | 666.456 | 0.342 | 960000 | 328320 | 0
1 | Tranformer - 1 at Shyampur 230/132 | 132 |  | 38992560 | 1 | 1376.368 | 1408.991 | 32.623 | 1920000 | 0 | 62636160
|  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  | 132 |  | 38992559 | 1 | 1467.736 | 1500.185 | 32.449 | 1920000 | 0 | 62302080
| Aggrekko 100 MW (Brammhongao) | 132 |  | PN-1711A04601 | 1 | 363.871 | 363.871 | 0 | 960000 | 0 | 0
|  | 132 |  |  | 1 | 5.419 | 5.419 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Exp | 132 |  | 38992544 | 1 | 32.177 | 32.177 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Imp | 132 |  | 38992544 | 1 | 18.041 | 18.041 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 328320 | 126205440
[9 empty] | Net Total | 125877120
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) | 132 | Import | 08993727 | 1 | 8945.468 | 9008.629 | 63.161 | 720000 | 45475920
|  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) | 132 | Import | 08993726 | 1 | 6705.919 | 6766.127 | 60.208 | 720000 | 43349760
|  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
[7 empty] | 0 | Total Import/Export |  | 88825680 | 0
[7 empty] | 0 | Net Total |  | 88825680
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
|  | 132 |  |  |  | 0 | 0
|  | 132 |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[7 empty] | 0 |  | Total |  | 37068000
| SHYAMPUR 132 KV SIDE | [5 empty] | 0
5 | 132 kV 80/120 MVA ( GT-1) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) | 132 | Export | ABB3902 | 1 | 1735597.5 | 1883170.2 | 147572.7 | 1300 |  | 191844510
[9 empty] | Total |  | 51757680
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 125877120 |  | EXPORT TO OTHER S/S |  |  | 37068000 |  | 132 KV NET IMPORT |  | 88809120
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 88809120 |  | 33 KV NET IMPORT |  | 88672752
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 136368
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1536%
| 132 KV TOTAL IMPORT |  | 125877120
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) | 33 | Import | BD001826 | 1 | 3292.028 | 3337.1699 | 45.1419 | 480000 | 21668112
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) | 33 | Import | BD001850 | 1 | 3348.8759 | 3394.1149 | 45.239 | 480000 | 21714720
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) | 33 | Import | BD001835 | 1 | 2834.593 | 2881.364 | 46.771 | 480000 | 22450080
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) | 33 | Import | BD001831 | 1 | 3713.1411 | 3760.7241 | 47.583 | 480000 | 22839840
[7 empty] | 0 |  | Total | 88672752
| SHYAMPUR 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) | 33 | Export | BD001808 | 1 | 2056.104 | 2087.2119 | 31.1079 | 240000 | From Downstream | 7443328 | 7447912.9078 |  | 25512201.2172 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7447912.9078 | 7973517.1986 | -525604.2908 | -6.5919 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) | 33 | Export | BD001834 | 1 | 1868.6779 | 1894.634 | 25.9561 | 240000 | From Downstream | 7412528 | 7417093.9357 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7417093.9357 | 7943090.0392 | -525996.1034 | -6.6221 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) | 33 | Export | BD001846 | 1 | 1374.781 | 1398.6889 | 23.9079 | 240000 |  | 5737896 | 5741430.4034 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 5741430.4034 | 6651296.9787 | -909866.5752 | -13.6795 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) | 33 | Export | BD001847 | 1 | 1240.6878 | 1261.1159 | 20.4281 | 240000 |  | 4902744 | 4905763.9703 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 4905763.9703 | 3663702.2377 | 1242061.7326 | 33.9018 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 25496496 | 25512201.2172 |  |  |  |  | 33 KV Feeders | 25512201.2172 | 26231606.4542 | -719405.237 | -2.7425 | OK
1 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 705.0729 | 715.3204 | 10.2475 | 240000 |  | 2459400 | 2460914.9302 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 2460914.9302 | 3061628.8242 | -600713.894 | -19.6207 | OK
2 | 33 kV Postogola Feeder-1. | 33 | Export | BD001804 | 1 | 1564.54 | 1564.541 | 0.001 | 240000 |  | 240 | 240.1478 |  | 720.4435 | Postogola 33/11 kv s/s |  | 33 kV Postogola Feeder-1. | 240.1478 | 0 | 240.1478 | #DIV/0! | #DIV/0!
5 | 33 kV Prime Textile Feeder. | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1218.187 | 1248.0069 | 29.8199 | 240000 | From Downstream | 7156776 | 7161184.3988 |  | 12893297.0663 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 7161184.3988 | 7117136.7895 | 44047.6093 | 0.6189 | OK
7 | 33 kV Nondolalpur -2 feeder | 33 | Export | BD001807 | 1 | 1061.5839 | 1085.453 | 23.8691 | 240000 |  | 5728584 | 5732112.6675 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 5732112.6675 | 6069017.2331 | -336904.5656 | -5.5512 | OK
8 | 33 kV Postogola Feeder-2. | 33 | Export | BD001830 | 1 | 2131.892 | 2131.894 | 0.002 | 240000 |  | 480 | 480.2957 |  |  |  |  | 33 kV Postogola Feeder-2. | 480.2957 | 2762225.5754 | -2761745.2798 | -99.9826 | CHECK
11 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 619.8515 | 629.3505 | 9.499 | 240000 |  | 2279760 | 2281164.2763 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2281164.2763 | 2550860.9103 | -269696.634 | -10.5728 | OK
12 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1058.144 | 1102.925 | 44.781 | 240000 |  | 10747440 | 10754060.1599 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 10754060.1599 | 11226204.5625 | -472144.4026 | -4.2057 | OK
13 | 33 kV Fatullah Feeder-2. | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 674551.2513 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2476.4919 | 2510.5759 | 34.084 | 240000 |  | 8343763.2 | 8348902.7538 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8348902.7538 | 8159147.373 | 189755.3808 | 2.3257 | OK
17 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 669.723 | 672.5319 | 2.8089 | 240000 | Prime Textile | 674136 | 674551.2513 | Fatullah | 17489649.7641 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 674551.2513 | 553357.9299 | 121193.3214 | 21.9014 | OK
18 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 123.986 | 129.9924 | 6.0064 | 240000 |  | 1441536 | 1442423.9509 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1442423.9509 | 1281447.8263 | 160976.1246 | 12.5621 | OK
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 |  | 0 | 0 |  | 0 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 0 | 240.2144 | -240.2144 | -100 | CHECK
20 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1461.395 | 1488.4699 | 27.0749 | 240000 |  | 6497976 | 6501978.5941 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 6501978.5941 | 5773073.0719 | 728905.5222 | 12.626 | OK
23 | 33 kV Shyampur BSCIC-2. | 33 | Export | BD001827 | 1 | 2385.1049 | 2423.1679 | 38.063 | 240000 |  | 9135120 | 9140747.0102 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 9140747.0102 | 9808915.4837 | -668168.4734 | -6.8118 | OK
24 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2295.02 | 2331.0006 | 35.9806 | 240000 |  | 8635344 | 8640663.1605 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 8640663.1605 | 8425760.8734 | 214902.287 | 2.5505 | OK
23 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 337.075 | 341.169 | 4.094 | 2400 |  | 10071.24 | 10071.24 | Fatullah
24 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 82.99 | 87.479 | 4.489 | 2400 |  | 11042.94 | 11042.94 | Fatullah
[9 empty] | Total |  | 63121669.38 | 63160537.7769 |  |  |  |  | 0 | 63160537.7769 | 66810662.2076 | -3650124.4307 | -5.4634 | OK
[8 empty] | Grand Total |  | 88672752 | 88618165.38 | 88672738.9942 | 0.061583
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 32081205.0719
[5 empty] | Fatullah | at 33 KV level |  | 695665.4313
[6 empty] | Export to Other SS |  | 55895868.4911
[5 empty] | Total = |  |  | 88672738.9942 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | BD001926 | 1 | 2773.52 | 2820.0408 | 46.5208 | 160000 | 7443328 |  | 7459869.064 |  | 7443328
16 | 11 kV 20/28 MVA Transformer-2 | 11 |  | BD001952 | 1 | 2786.63 | 2832.9583 | 46.3283 | 160000 | 7412528 |  | 7429000.6182
27 | 11 kV20/28 MVA Transformer-3 | 11 |  | BD001927 | 1 | 1927.01 | 1962.7445 | 35.7345 | 160000 | 5717520 |  | 5730225.8574 |  | 1327456
36 | 11 kV 20/28 MVA Transformer-4 | 11 |  | BD001927 | 1 | 1856.84 | 1887.3541 | 30.5141 | 160000 | 4882256 |  | 4893105.6776 |  | 1327456
[7 empty] | 0 |  | Total | 25455632 |  | 25512201.2172
| SHYAMPUR 11 kV SIDE | [5 empty] | 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur |  | 1 | 546.49 | 579.6764 | 33.1864 | 40000 |  | 1327456 | 1329002.2614 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1329002.2614 | 1796570.0888 | -467567.8275 | -26.0256 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | 11 |  | BD001943 | 1 | 1013.14 | 1030.3488 | 17.2088 | 40000 |  | 688352 | 689153.8135 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 689153.8135 | 726162.1684 | -37008.3549 | -5.0964 | OK
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1490.83 | 1510.017 | 19.187 | 40000 |  | 767480 | 768373.9842 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 768373.9842 | 842780.9272 | -74406.943 | -8.8287 | OK
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1383.34 | 1400.2733 | 16.9333 | 40000 |  | 677332 | 678120.977 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 678120.977 | 664045.6474 | 14075.3297 | 2.1196 | OK
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1259.97 | 1286.4505 | 26.4805 | 40000 |  | 1059220 | 1060453.8119 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 1060453.8119 | 1011898.1651 | 48555.6467 | 4.7985 | OK
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3181.56 | 3240.1803 | 58.6203 | 40000 |  | 2344812 | 2347543.3088 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2347543.3088 | 2415731.5404 | -68188.2316 | -2.8227 | OK
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2064.33 | 2102.0425 | 37.7125 | 40000 |  | 1508500 | 1510257.147 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1510257.147 | 1400226.6095 | 110030.5375 | 7.8581 | OK
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 481.32 | 484.1231 | 2.8031 | 40000 |  | 112124 | 112254.6055 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 112254.6055 | 96981.9232 | 15272.6823 | 15.748 | OK
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3028.5 | 3076.6439 | 48.1439 | 40000 |  | 1925756 | 1927999.1795 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1927999.1795 | 1824622.7112 | 103376.4683 | 5.6656 | OK
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1879.48 | 1921.3681 | 41.8881 | 40000 |  | 1675524 | 1677475.7016 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1677475.7016 | 1601003.2355 | 76472.4661 | 4.7765 | OK
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1372.48 | 1406.4167 | 33.9367 | 40000 |  | 1357468 | 1359049.2203 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1359049.2203 | 1887540.7358 | -528491.5155 | -27.9989 | OK
20 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 793.62 | 807.729 | 14.109 | 40000 |  | 564360 | 565017.3838 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 565017.3838 | 552636.6613 | 12380.7225 | 2.2403 | OK
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1274.85 | 1294.1832 | 19.3332 | 40000 |  | 773328 | 774228.7961 | Shyampur |  |  |  | 11 kV Delpara Feeder | 774228.7961 | 1030332.7456 | -256103.9494 | -24.8564 | OK
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2850.41 | 2914.5187 | 64.1087 | 40000 |  | 2564348 | 2567335.031 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2567335.031 | 2104748.1835 | 462586.8475 | 21.9783 | OK
24 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1090.91 | 1098.2827 | 7.3727 | 40000 |  | 294908 | 295251.5179 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 295251.5179 | 251271.3464 | 43980.1715 | 17.5031 | OK
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1882.3 | 1916.4054 | 34.1054 | 40000 |  | 1364216 | 1365805.0805 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1365805.0805 | 1428279.2319 | -62474.1513 | -4.3741 | OK
28 | 11 kV Spare Feeder | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1321.48 | 1335.0577 | 13.5777 | 40000 |  | 543108 | 543740.6288 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 543740.6288 | 732574.1964 | -188833.5676 | -25.7767 | OK
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1273.64 | 1300.6173 | 26.9773 | 40000 |  | 1079092 | 1080348.9594 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 1080348.9594 | 971021.4868 | 109327.4726 | 11.259 | OK
31 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2161.1 | 2199.2196 | 38.1196 | 40000 |  | 1524784 | 1526560.1151 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1526560.1151 | 1250345.4555 | 276214.6595 | 22.0911 | OK
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 168.36 | 170.7545 | 2.3945 | 40000 |  | 95780 | 95891.5675 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 95891.5675 | 84558.6189 | 11332.9485 | 13.4025 | OK
37 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1150.73 | 1172.4449 | 21.7149 | 40000 |  | 868596 | 869607.7672 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 869607.7672 | 875642.5706 | -6034.8034 | -0.68919 | OK
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3585.78 | 3633.3532 | 47.5732 | 40000 |  | 1902928 | 1905144.5888 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 1905144.5888 | 2092324.8793 | -187180.2905 | -8.946 | OK
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1064.5 | 1076.0762 | 11.5762 | 40000 |  | 463046.4 | 463585.7706 | Shyampur |  |  |  | 11 kV Igloo Feeder | 463585.7706 | 590307.3256 | -126721.555 | -21.467 | OK
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 62985.9 | 63432.6 | 446.7 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 |  |  | 1 | 578955 | 586899 | 7944 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 25512201.2172 | 25482518.4 | 25512201.2172 | 0.11648
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 1172708.4173
[5 empty] | Shyampur | at 33 KV level |  | 24339492.7999
[5 empty] | Total = |  |  | 25512201.2172 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2476.4919 | 2510.5759 | 34.084 | 240000 | 0 | 8343763.2 | 8348902.7538
23 | 33 kV Shyampur BSCIC-2. | 33 |  | BD001827 | 1 | 2385.1049 | 2423.1679 | 38.063 | 240000 | 0 | 9135120 | 9140747.0102
[9 empty] | Total | 0 | 17478883.2 | 17489649.7641
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 | 33 | Import | DHK61071 | 1 | 857567.5 | 887930.8 | 30363.3 | 270 | 8198091
5 | 33 kV Shyampur Circuit-2 | 33 | Import | DHK61067 | 1 | 642122.8 | 676108.4 | 33985.6 | 270 | 9176112
[7 empty] | 0 |  | Total | 17374203 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| SHYAMPUR BISIC 33 KV SIDE | [5 empty] | 0
2 | 33 kV 20/28 MVA Transformer-1 | 33 | Export | DHK61068 | 1 | 799750 | 845345.2 | 45595.2 | 180 |  | 8207136
3 | 33 kV 20/28 MVA Transformer-2 | 33 | Export | DHK61066 | 1 | 457508.2 | 508484 | 50975.8 | 180 |  | 9175644
[9 empty] | Total |  | 17382780 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 17489649.7641 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 17489649.7641
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 17489649.7641 |  | 33 KV TX HV SIDE |  | 17382780
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 106869.7641
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.611%
| TOTAL IMPORT |  | 17489649.7641
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK61019 | 1.05 | 929250.4 | 959640.9 | 30390.5 | 180 | 5743804.5 |  | 6792096.1175 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK61018 | 1 | 581500 | 631758.3 | 50258.3 | 180 | 9046494 |  | 10697553.6466
[7 empty] | 0 |  | Total | 14790298.5 |  | 17489649.7641
| SHYAMPUR BISIC 11 KV SIDE | [5 empty] | 0
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 33561211 | 35723650 | 2162439 | 1 |  | 2162439 | 2098065.1104 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 2098065.1104 | 2051822.5774 | 46242.533 | 2.2537 | OK
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 19777200 | 20537911 | 760711 | 1 |  | 760711 | 738065.3088 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 738065.3088 | 731764.9753 | 6300.3335 | 0.86098 | OK
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 377188.5 | 410183.5 | 32995 | 60 |  | 1979700 | 1920766.0882 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1920766.0882 | 1940683.7189 | -19917.6307 | -1.0263 | OK
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 550150 | 575495.8 | 25345.8 | 60 |  | 1520748 | 1475476.6819 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1475476.6819 | 1381608.0185 | 93868.6634 | 6.7942 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 570335.4 | 594888.2 | 24552.8 | 60 |  | 1473168 | 1429313.0963 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1429313.0963 | 1378277.4296 | 51035.6666 | 3.7029 | OK
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 320655.9 | 337050 | 16394.1 | 60 |  | 983646 | 954363.7317 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 954363.7317 | 1019394.7492 | -65031.0175 | -6.3794 | OK
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511384.5 | 511525.1 | 140.6 | 60 |  | 8436 | 8184.8678 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 8184.8678 | 8596.203 | -411.3353 | -4.7851 | OK
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 778535.8 | 824930.4 | 46394.6 | 60 |  | 2783676 | 2700808.4363 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2700808.4363 | 2561826.8196 | 138981.6167 | 5.4251 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 214982.3 | 236095.8 | 21113.5 | 60 |  | 1266810 | 1229098.1908 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1229098.1908 | 1284557.7074 | -55459.5166 | -4.3174 | OK
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 435544 | 443790.5 | 8246.5 | 60 |  | 494790 | 480060.5409 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 480060.5409 | 1215195.8482 | -735135.3073 | -60.4952 | CHECK
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 439242.7 | 482640.9 | 43398.2 | 60 |  | 2603892 | 2526376.4464 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2526376.4464 | 2465450.8355 | 60925.611 | 2.4712 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 833590.5 | 845435.7 | 11845.2 | 60 |  | 710712 | 689554.7346 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 689554.7346 | 725640.3272 | -36085.5926 | -4.9729 | OK
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 917620.2 | 938845.6 | 21225.4 | 60 |  | 1273524 | 1235612.3209 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1235612.3209 | 1199610.0995 | 36002.2214 | 3.0012 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB7380 | 1 | 600880 | 604904 | 4024 | 1 |  | 4024 | 3904.2091 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3904.2091 | 3633.5474 | 270.6617 | 7.449 | OK
[9 empty] | Grand Total | 17489649.7641 | 18026276 | 17489649.7641 | -2.9769
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5521043.5629
[5 empty] | Jurain | at 33 KV level |  | 11968606.2012
[5 empty] | Total = |  |  | 17489649.7641 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1218.187 | 1248.0069 | 29.8199 | 240000 | From Downstream | 7156776 | 7161184.3988
7 | 33 kV Nondolalpur -2 feeder | 33 |  | BD001807 | 1 | 1061.5839 | 1085.453 | 23.8691 | 240000 | 0 | 5728584 | 5732112.6675
[9 empty] | Total | 0 | 12885360 | 12893297.0663
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) | 33 | Import | 00000084 | 1 | 292336064 | 292336064 | 0 | 1 | 0
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) | 33 | Import | 00000070 | 1 | 275297536 | 275297536 | 0 | 1 | 0
[9 empty] | Total | 0 | 0 | 0
NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[9 empty] | Total |  | 0
NANDALALPUR 33 KV SIDE
4 | 33 kV, 28/35 MVA T-1 | 33 | Export | 00000086 | 1 | 292542016 | 292542016 | 0 | 1 |  | 0
5 | 33 kV, 28/35 MVA T-2 | 33 | Export | 00000083 | 1 | 274750112 | 274750112 | 0 | 1 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 12893297.0663 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 12893297.0663
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 12893297.0663 |  | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 12893297.0663
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 12893297.0663
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. | 11 |  | 00000036 | 1 | 290754528 | 297872160 | 7117632 | 1 | 7117632 |  | 7157075.8139 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000033 | 1 | 273555328 | 279259936 | 5704608 | 1 | 5704608 |  | 5736221.2523
[7 empty] | 0 |  | Total | 12822240 |  | 12893297.0663
| NANDALALPUR 11 KV SIDE | [5 empty] | 0 | [7 empty] | 80
8 | 11 kV Spare | 11 |  | 00000090 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  | 40 |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | 11 |  | 00000026 | 1 | 4014750 | 4686068 | 671318 | 1 |  | 671318 | 676115.2751 | Fatullah |  | 40 |  | 11 kV Khaza Moinuddin | 676115.2751 | 672821.6526 | 3293.6225 | 0.48952 | OK
10 | 11 kV Chitashal | 11 |  | 00000027 | 1 | 31727122 | 32447880 | 720758 | 1 |  | 720758 | 725908.576 | Shyampur |  | 13.3333 |  | 11 kV Chitashal | 725908.576 | 676035.0889 | 49873.4871 | 7.3774 | OK
11 | 11 kV Local Feeder | 11 |  | 00000157 | 1.5 | 18012236 | 18223956 | 211720 | 1 | Estimated | 647400.6 | 652026.96 | Shyampur | 55 | 53.3333 |  | 11 kV Local Feeder | 652026.96 | 610908.7086 | 41118.2515 | 6.7307 | OK
12 | 11 kV Rasel Germants | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 |  | 00000121 | 1 | 68316432 | 70737224 | 2420792 | 1 |  | 2420792 | 2438091.1118 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2438091.1118 | 2521439.5722 | -83348.4603 | -3.3056 | OK
14 | 11 kV Nandalalpur | 11 |  | 00000010 | 1 | 82071400 | 82993360 | 921960 | 1 |  | 921960 | 928548.3765 | Fatullah |  |  |  | 11 kV Nandalalpur | 928548.3765 | 892208.2473 | 36340.1292 | 4.0731 | OK
15 | 11 kV Sharif Bagh | 11 |  | 00000132 | 1 | 68478392 | 70183192 | 1704800 | 1 |  | 1704800 | 1716982.5939 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1716982.5939 | 1682233.437 | 34749.1569 | 2.0657 | OK
18 | 11 kV Spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | 11 |  | 00000158 | 1 | 62900248 | 64037524 | 1137276 | 1 |  | 1137276 | 1145403.0364 | Fatullah |  |  |  | 11 KV Nayamati | 1145403.0364 | 1037983.1413 | 107419.8951 | 10.3489 | OK
20 | 11 kV Pulpar | 11 |  | 00000160 | 1 | 6177345 | 6979983 | 802638 | 1 |  | 802638 | 808373.695 | Fatullah |  |  |  | 11 kV Pulpar | 808373.695 | 916555.6279 | -108181.933 | -11.8031 | OK
21 | 11 kV Shahi Bazar | 11 |  | 00000170 | 1 | 39279104 | 40057984 | 778880 | 1 |  | 778880 | 784445.919 | Shyampur |  |  |  | 11 kV Shahi Bazar | 784445.919 | 785444.6114 | -998.6924 | -0.12715 | OK
22 | 11 kV Pagla Bazar | 11 |  | 00000060 | 1 | 48692680 | 49521320 | 828640 | 1 |  | 828640 | 834561.5067 | Fatullah |  |  |  | 11 kV Pagla Bazar | 834561.5067 | 783154.3223 | 51407.1844 | 6.5641 | OK
23 | 11 kV Delpara bazar | 11 |  | 00000063 | 1 | 76134976 | 77632408 | 1497432 | 1 |  | 1497432 | 1508132.7308 | Shyampur |  |  |  | 11 kV Delpara bazar | 1508132.7308 | 1527622.8486 | -19490.1178 | -1.2758 | OK
24 | 11 kV Bhuighor (Board mill) | 11 |  | 00000146 | 1 | 42387696 | 43051416 | 663720 | 1 |  | 663720 | 668462.9794 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 668462.9794 | 1074021.0416 | -405558.0622 | -37.7607 | OK
25 | 11 kV Spare | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 | 11 |  | 7803 | 1 | 2309 | 2371 | 62 | 100 |  | 6200 | 6244.3055 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 6244.3055 | 5725.7228 | 518.5827 | 9.0571 | OK
27 | 33/0.415 kV, 200 kVA AT-2 | 11 |  | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 12893297.0663 | 12801814.6 | 12893297.0663 | 0.71461
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5393741.0854
[5 empty] | Fatullah | at 33 KV level |  | 4393001.8897
[5 empty] | Matuail | at 33 KV level |  | 3106554.0912
[5 empty] | Total = |  |  | 12893297.0663 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 | 132 | Import | 42627826 | 1 | 231.085 | 260.441 | 29.356 | 960000 | 0 | 28181760
[5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 | 132 |  | 42627815 | 1 | 117.004 | 125.28 | 8.276 | 960000 | 0 | 7944960
2 |  |  |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 36126720
[9 empty] | Net Total | 36126720
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 | 132 | Main | 41808902823 | 1 | 184.09 | 208.22 | 24.13 | 1200000 | 28956000
|  | 132 | Backup | 41808904269 | 1 | 184.09 | 208.22 | 24.13 | 1200000 | 28956000
4 | 132kV Hasnabad Circuit-2 | 132 | Imp/Main | 41808902845 | 1 | 93.51 | 100.14 | 6.63 | 1200000 | 7956000
|  | 132 | Imp/Backup | 41808904256 | 1 | 93.51 | 100.14 | 6.63 | 1200000 | 7956000
[7 empty] | 0 | Total Import/Export |  | 36912000 | 0
[7 empty] | 0 | Net Total |  | 36912000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
| POSTOGOLA 132 KV SIDE | [5 empty] | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41808902871 | 1 | 195.88 | 219.39 | 23.51 | 1200000 |  | 28212000
|  | 132 | Exp/Backup | 41808904257 | 1 | 195.88 | 219.39 | 23.51 | 1200000 |  | 28212000
5 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41808902846 | 1 | 82.23 | 88.86 | 6.63 | 1200000 |  | 7956000
|  | 132 | Exp/Backup | 41808904243 | 1 | 82.23 | 88.86 | 6.63 | 1200000 |  | 7956000
[9 empty] | Total |  | 36168000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 36126720 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 36126720
[5 empty] | 132 KV NET IMPORT |  |  | 36126720 |  | 33 KV NET IMPORT |  | 36043200
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 83520
[10 empty] | LOSS % IN => |  | 0.2312%
| 132 KV TOTAL IMPORT |  | 36126720
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| POSTOGOLA 33 KV SIDE | [7 empty] | Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41808902807 | 1 | 325.26 | 364.32 | 39.06 | 720000 | 28123200
|  | 33 | Backup | 41808904286 | 1 | 325.26 | 364.32 | 39.06 | 720000 | 28123200
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41808902869 | 1 | 136.08 | 147.08 | 11 | 720000 | 7920000
|  | 33 | Backup | 41808904268 | 1 | 136.08 | 147.08 | 11 | 720000 | 7920000
[7 empty] | 0 |  | Total | 36043200 |  | 0
| POSTOGOLA 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss |  | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 335.74 | 363.42 | 27.68 | 360000 |  | 9964800 | 9957837.8681 |  | 17886694.3208 | IG Gate 33/11 kv ss |  | 33 kV IG Gate Ckt-2 | 9957837.8681 | 9802531.8108 | 155306.0573 | 1.5843 | OK
|  | 33 | Backup | 41808904225 | 1 | 335.74 | 363.42 | 27.68 | 360000 |  | 9964800 | 9957837.8681 |  |  |  |  | 0 | 9957837.8681 | 9802531.8108 | 155306.0573 | 1.5843 | OK
8 | 33 kV Spare Feeder 2 | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 | 33 | Main | 41808902810 | 1 | 315.39 | 365.86 | 50.47 | 360000 |  | 18169200 | 18156505.6792 |  |  |  |  | 33kV Postogola circuit-1 | 18156505.6792 | 15234393.4747 | 2922112.2045 | 19.181 | OK
|  | 33 | Backup | 41808904252 | 1 | 315.39 | 365.86 | 50.47 | 360000 |  | 18169200 | 18156505.6792 |  |  |  |  | 0 | 18156505.6792 | 15234393.4747 | 2922112.2045 | 19.181 | OK
14 | 31 kV Spare Feeder 4 | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 271.63 | 293.67 | 22.04 | 360000 |  | 7934400 | 7928856.4527 |  |  |  |  | 33 kV IG Gate Ckt-1 | 7928856.4527 | 8039874.7145 | -111018.2618 | -1.3808 | OK
|  | 33 | Backup | 41812909573 | 1 | 271.63 | 293.67 | 22.04 | 360000 |  | 7934400 | 7928856.4527 |  |  |  |  | 0 | 7928856.4527 | 8039874.7145 | -111018.2618 | -1.3808 | OK
[9 empty] | Total |  | 36068400 | 36043200 |  |  |  |  | 0 | 36043200 | 33076800 | 2966400 | 8.9682 | OK
[8 empty] | Grand Total |  | 36043200 | 36068400 | 36043200 | -0.069867
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola | 33 | Import | BD001804 | 1 | 315.39 | 365.86 | 50.47 | 360000 | 18169200 |  | 18156505.6792
2 | 33 kV Postogola Circuit-2 at Shyampur | 33 | Import | BD001830 | 1 | 2131.892 | 2131.894 | 0.002 | 240000 | 480 |  | 480.2957
[7 empty] | 0 |  | Total | 18169680 |  | 18156985.9749
| POSTOGOLA 33 KV SIDE (RECEIVING) | [5 empty] | 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
[7 empty] | 0 |  | Total | 0
| POSTOGOLA 33 KV SIDE | [5 empty] | 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK61027 | 1 | 156623 | 200581.5 | 43958.5 | 180 |  | 7912530 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60870 | 1 | 559287.3 | 616186 | 56898.7 | 180 |  | 10241766
[7 empty] | 0 |  | Total |  | 18154296
| POSTOGOLA 11 KV SIDE | [5 empty] | 0
8 | 11 kV 20/28 MVA T-1 Incoming. | 11 |  | DHK61005 | 1.165 | 759820.5 | 799441.5 | 39621 | 180 | 8308523.7 |  | 8178471.0434 |  | 36308592
9 | 11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK60861 | 1.165 | 794200.3 | 842541.7 | 48341.4 | 180 | 10137191.58 |  | 9978514.9314
[7 empty] | 0 |  | Total | 18445715.28 |  | 18156985.9749
| POSTOGOLA 11 kV SIDE | [5 empty] | 0
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 59733520 | 61037936 | 1304416 | 1 |  | 1304416 | 1307497.2614 | Postogola |  |  |  | 11 kV Station Road Feeder | 1307497.2614 | 1269812.3426 | 37684.9189 | 2.9678 | OK
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 6981957 | 8339686 | 1357729 | 1 |  | 1357729 | 1360936.1962 | Jurain |  |  |  | 11 kV Samon & Sons Feeder. | 1360936.1962 | 1367079.5822 | -6143.386 | -0.44938 | OK
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 23055333 | 23596442 | 541109 | 1 |  | 541109 | 542387.1952 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 542387.1952 | 435813.5436 | 106573.6517 | 24.454 | OK
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 71243020 | 72786262 | 1543242 | 1 |  | 1543242 | 1546887.4107 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1546887.4107 | 1509702.7057 | 37184.705 | 2.463 | OK
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 407058.9 | 418110.9 | 11052 | 60 |  | 663120 | 664686.4068 | Postogola |  |  |  | 11 kV Cyca Feeder | 664686.4068 | 678488.3278 | -13801.921 | -2.0342 | OK
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 824597.3 | 845528 | 20930.7 | 60 |  | 1255842 | 1258808.5211 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 1258808.5211 | 1186933.4512 | 71875.0698 | 6.0555 | OK
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 706742.8 | 727154.9 | 20412.1 | 60 |  | 1224726 | 1227619.0196 | Postogola |  |  |  | 11 kV Munshi Bari | 1227619.0196 | 1164704.2052 | 62914.8144 | 5.4018 | OK
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 515784.4 | 517862.7 | 2078.3 | 60 |  | 124698 | 124992.5587 | Postogola |  |  |  | 11 kV Cantonment Feeder | 124992.5587 | 126222.4118 | -1229.8531 | -0.97435 | OK
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 797566.5 | 819569.4 | 22002.9 | 60 |  | 1320174 | 1323292.4846 | Postogola |  |  |  | 11 kV DIT Feeder. | 1323292.4846 | 1331811.5849 | -8519.1002 | -0.63966 | OK
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 243241.8 | 283639 | 40397.2 | 60 |  | 2423832 | 2429557.5202 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 2429557.5202 | 2393972.4885 | 35585.0316 | 1.4864 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 34480101 | 36547113 | 2067012 | 1 |  | 2067012 | 2071894.6482 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 2071894.6482 | 1933992.5359 | 137902.1123 | 7.1304 | OK
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 3547.1 | 5929.5 | 2382.4 | 1000 |  | 2382400 | 2388027.6504 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2388027.6504 | 2351667.7366 | 36359.9138 | 1.5461 | OK
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 52807093 | 54442479 | 1635386 | 1 |  | 1635386 | 1639249.0712 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1639249.0712 | 1571920.5306 | 67328.5406 | 4.2832 | OK
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52708936 | 52971025 | 262089 | 1 |  | 262089 | 262708.1006 | Postogola |  |  |  | 11 kV Rajabari Feeder. | 262708.1006 | 303872.8913 | -41164.7907 | -13.5467 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 |  | ELIB67385 | 1 | 243.19 | 314.92 | 71.73 | 80 |  | 5738.4 | 5751.9551 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 5751.9551 | 4375.6621 | 1376.293 | 31.4534 | OK
[9 empty] | Total | 18154296 | 18111513.4 | 18154296 | 0.23622
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Postogola | at 33 KV level |  | 9361492.7898
[5 empty] | Jurain | at 33 KV level |  | 8792803.2102
[5 empty] | Total = |  |  | 18154296 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 | 0 | 0 | 0
| Postogola 33 KV SIDE | [7 empty] | Total | 0 | 0 | 0
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 335.74 | 363.42 | 27.68 | 360000 | 0 | 9964800 | 9957837.8681
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 271.63 | 293.67 | 22.04 | 360000 | 0 | 7934400 | 7928856.4527
[9 empty] | Total | 0 | 17899200 | 17886694.3208
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 | 33 | Import | DHK60973 | 1 | 235334.2 | 249925.3 | 14591.1 | 540 | 7879194
6 | 33 kV Postogola Incoming Feeder-2 | 33 | Import | DHK60966 | 1 | 406797.9 | 425158.5 | 18360.6 | 540 | 9914724
[7 empty] | 0 |  | Total | 17793918 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| IG GATE 33 KV SIDE | [5 empty] | 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK60893 | 1 | 670808.2 | 714538.2 | 43730 | 180 |  | 7871400
5 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60975 | 1 | 254166.6 | 309221.7 | 55055.1 | 180 |  | 9909918
[9 empty] | Total |  | 17781318 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 17886694.3208 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 17886694.3208
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 17886694.3208 |  | 33 KV TX HV SIDE |  | 17781318
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 105376.3208
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5891%
| TOTAL IMPORT |  | 17886694.3208
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month June-2023 |  |  | Name of Feeders. | Month June-2023 | Month May-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK68139 | 1 | 3612.62 | 3655.67 | 43.05 | 180000 | 7749000 |  | 8052098.6146 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK68137 | 1 | 4215.89 | 4268.47 | 52.58 | 180000 | 9464400 |  | 9834595.7062
[7 empty] | 0 |  | Total | 17213400 |  | 17886694.3208
| IG GATE 11 KV SIDE | [5 empty] | 0
1 | 11 kV Feeder-1 | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | 11 |  | DHK60970 | 1 | 158004.4 | 190281.3 | 32276.9 | 60 |  | 1936614 | 1942348.072 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 1942348.072 | 1890634.7965 | 51713.2755 | 2.7352 | OK
4 | 11 kV Alom Gonj | 11 |  | DHK60894 | 1 | 460143.7 | 469945.6 | 9801.9 | 60 |  | 588114 | 589855.3321 | Postogola |  |  |  | 11 kV Alom Gonj | 589855.3321 | 589628.102 | 227.23 | 0.038538 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 |  | DHK60895 | 1 | 475941.2 | 505725.6 | 29784.4 | 60 |  | 1787064 | 1792355.2732 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1792355.2732 | 1711977.4089 | 80377.8642 | 4.695 | OK
6 | 11 kV Farashgonj Feeder (F-6) | 11 |  | DHK68133 | 1 | 3530.25 | 3559.31 | 29.06 | 60000 |  | 1743600 | 1748762.5817 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1748762.5817 | 1815572.1775 | -66809.5958 | -3.6798 | OK
7 | 11 kV Doyaganj | 11 |  | DHK68134 | 1 | 2322.27 | 2352.51 | 30.24 | 60000 |  | 1814400 | 1819772.2117 | Swamibag |  |  |  | 11 kV Doyaganj | 1819772.2117 | 1955417.8504 | -135645.6388 | -6.9369 | OK
10 | 11 kV Faridabad | 11 |  | DHK68140 | 1 | 730.03 | 751.51 | 21.48 | 60000 |  | 1288800 | 1292615.9757 | Postogola |  |  |  | 11 kV Faridabad | 1292615.9757 | 1233789.9626 | 58826.0131 | 4.7679 | OK
11 | 11 kV Gandaria | 11 |  | DHK60969 | 1 | 300077.81 | 336244.2 | 36166.39 | 60 |  | 2169983.4 | 2176408.4497 | Postogola |  |  |  | 11 kV Gandaria | 2176408.4497 | 2008723.2675 | 167685.1822 | 8.3478 | OK
12 | 11 kV Walter Road | 11 |  | DHK68136 | 1 | 926.56 | 950.44 | 23.88 | 60000 |  | 1432800 | 1437042.3417 | Banglabazar |  |  |  | 11 kV Walter Road | 1437042.3417 | 1402694.4766 | 34347.8651 | 2.4487 | OK
13 | 11 kV Murgitola Feeder (F-11) | 11 |  | DHK68138 | 1 | 3813.73 | 3852.58 | 38.85 | 60000 |  | 2331000 | 2337901.7997 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2337901.7997 | 2438521.0841 | -100619.2844 | -4.1262 | OK
14 | 11 kV Feeder-12 | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | 11 |  | DHK60899 | 1 | 609124.4 | 638057.1 | 28932.7 | 60 |  | 1735962 | 1741101.9665 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1741101.9665 | 1809148.9629 | -68046.9963 | -3.7613 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | 11 |  | DHK60967 | 1 | 132216.8 | 148948.3 | 16731.5 | 60 |  | 1003890 | 1006862.3928 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 1006862.3928 | 984580.1304 | 22282.2625 | 2.2631 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB2774 | 1 | 276011 | 277674 | 1663 | 1 |  | 1663 | 1667.9239 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1667.9239 | 1718.3058 | -50.3818 | -2.9321 | OK
[9 empty] | Grand Total | 17886694.3208 | 17833890.4 | 17886694.3208 | 0.29609
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Swamibag | at 33 KV level |  | 5898775.9779
[5 empty] | Banglabazar | at 33 KV level |  | 5128152.9955
[5 empty] | Postogola | at 33 KV level |  | 6859765.3474
[5 empty] | Total = |  |  | 17886694.3208 | 0
Swamibagh
Banglabazr
Postogola
Note on I385: No Reading Due to PT Out
Note on K385: Reading From Higher Side
Note on I644: No Reading due to PT Open
Note on L644: Energy From Bangshal SS End
Note on L649: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Linked_11KV
SL | Feeder_Name | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | May23_Consumption
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 3920074 | 5173196 | 1253122 | 1 | 0 | 1253122 | 1257653.9222 | Paribag | Dhanmondi 33/11KV S/S | 1137299.4891
5 | 11 kV Mogbazar O/H | 11 | 0 | HA021100463-02 | 1 | 44616340 | 46129640 | 1513300 | 1 | 0 | 1513300 | 1518772.8573 | Paribag | Dhanmondi 33/11KV S/S | 1477894.3769
6 | 11 kV Panthopath Feeder | 11 | 0 | HA021101078-02 | 1 | 56931817 | 59070322 | 2138505 | 1 | 0 | 2138505 | 2146238.9144 | Paribag | Dhanmondi 33/11KV S/S | 2162610.3185
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 | 0 | DHK60882 | 1 | 201916.09 | 208836.3 | 6920.21 | 60 | 0 | 415212.6 | 416714.2185 | Paribag | Dhanmondi 33/11KV S/S | 395540.6076
8 | 11 kV P G Hospital Feeder | 11 | 0 | DHK60889 | 1 | 275542.83 | 279161.7 | 3618.87 | 60 | 0 | 217132.2 | 217917.4597 | Paribag | Dhanmondi 33/11KV S/S | 226732.9713
9 | 11 kV Abdul Monem Ltd | 11 | 0 | DHK60890 | 1 | 684.97 | 691.92 | 6.95 | 60000 | 0 | 417000 | 418508.0827 | Paribag | Dhanmondi 33/11KV S/S | 415788.2923
10 | 11 kV Surjasen Hall Feeder | 11 | 0 | DHK60880 | 1 | 526282.72 | 538943.6 | 12660.88 | 60 | 0 | 759652.8 | 762400.0883 | Ramna | Dhanmondi 33/11KV S/S | 500947.7604
11 | 11 kV Azimpur-1 Feeder | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0
12 | 11 kV TSC Feeder | 11 | 0 | DHK60873 | 1 | 910191.77 | 918512 | 8320.23 | 60 | 0 | 499213.8 | 501019.2093 | Ramna | Dhanmondi 33/11KV S/S | 594864.6942
13 | 11 kV SCADA Bhaban | 11 | 0 | DHK60883 | 1 | 27965.2 | 28074.3 | 109.1 | 60 | 0 | 6546 | 6569.6736 | Paribag | Dhanmondi 33/11KV S/S | 7038.2714
14 | 11 kV DPH Sw/S-2 | 11 | 0 | DHK60871 | 1 | 455579.68 | 474478.5 | 18898.82 | 60 | 0 | 1133929.2 | 1138030.0608 | Paribag | Dhanmondi 33/11KV S/S | 1225995.769
17 | 11 kV New Elephant Road Feeder | 11 | 0 | DHK60981 | 1 | 38853.86 | 61120.9 | 22267.04 | 60 | 0 | 1336022.4 | 1340854.1319 | Paribag | Dhanmondi 33/11KV S/S | 1236853.2667
18 | 11 kV Dhanmondi O/H Feeder | 11 | 0 | DHK61110 | 1 | 356765.96 | 380880.9 | 24114.94 | 60 | 0 | 1446896.4 | 1452129.1083 | Paribag | Dhanmondi 33/11KV S/S | 1368507.5074
19 | 11 kV Sonargaon Feeder | 11 | 0 | DHK61115 | 1 | 283945.16 | 312180.8 | 28235.64 | 60 | 0 | 1694138.4 | 1700265.2603 | Paribag | Dhanmondi 33/11KV S/S | 1714907.3622
20 | 11 kV Museum Feeder | 11 | 0 | DHK61107 | 1 | 542994.77 | 545315.1 | 2320.33 | 60 | 0 | 139219.8 | 139723.2891 | Ramna | Dhanmondi 33/11KV S/S | 145373.4466
21 | 11 kV Shanta property | 11 | 0 | DHK61112 | 1 | 334966.62 | 338664.1 | 3697.48 | 60 | 0 | 221848.8 | 222651.1173 | Paribag | Dhanmondi 33/11KV S/S | 196910.1041
22 | 11 kV BIRDEM RMU Feeder | 11 | 0 | DHK61108 | 1 | 672823.56 | 685561.8 | 12738.24 | 60 | 0 | 764294.4 | 767058.4747 | Kakrail | Dhanmondi 33/11KV S/S | 1048103.4598
23 | 11 kV Azimpur-2 Feeder | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0
24 | 11 kV DPH Sw/S-1 | 11 | 0 | DHK60978 | 1 | 751590.62 | 767608.4 | 16017.78 | 60 | 0 | 961066.8 | 964542.5031 | Kakrail | Dhanmondi 33/11KV S/S | 717844.627
6 | WASA Bhaban | 11 | 0 | 8536188 | 1.14 | 2089.7 | 2288.8 | 199.1 | 1000 | 986040 | 986040 | 992894.4687 | Shere b.nagar | Kawranbazar 33/11KV S/S | 967717.4567
7 | Sangsad Bhaban | 11 | 0 | 8536178 | 1.14 | 567782 | 568300 | 518 | 44 | 0 | 25982.88 | 26163.5003 | Shere b.nagar | Kawranbazar 33/11KV S/S | 291323.9838
8 | Air Port Road (West) | 11 | 0 | 8536182 | 1.14 | 99649.5 | 100568.1 | 918.6 | 1000 | 0 | 1047204 | 1054483.651 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1142492.7318
9 | ICC (PM Office) | 11 | 0 | 8536193 | 1.14 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0
10 | (UTC) Tower | 11 | 0 | DHK00183 | 1.14 | 14511.4 | 15079.3 | 567.9 | 444.44 | 0 | 287733.1226 | 289733.3028 | Shere b.nagar | Kawranbazar 33/11KV S/S | 306081.9435
11 | Sonargaon Hotel | 11 | 0 | 8536190 | 1.14 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Kawranbazar 33/11KV S/S | 0
12 | Panthopath | 11 | 0 | 8536184 | 1.14 | 33415.5 | 34310.5 | 895 | 1000 | 0 | 1020300 | 1027392.6275 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1044641.4249
13 | Titas Bhaban | 11 | 0 | DHK00190 | 1.14 | 55090.4 | 55463.3 | 372.9 | 444.44 | 0 | 188934.1106 | 190247.4883 | Kakrail | Kawranbazar 33/11KV S/S | 258497.9936
16 | Green Road Dormatory s/s | 11 | 0 | DHK00021 | 1.14 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 0
26 | Aux. Transformer, AT-1 | 11 | 0 | 85-12906 | 1.14 | 67959 | 68255 | 296 | 10 | 0 | 3374.4 | 3397.8572 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0
27 | Aux. Transformer, AT-2 | 11 | 0 | 85-12909 | 1.14 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0
4 | Police Bhaban | 11 | 0 | DHK 00005 | 1 | 72836.6 | 73101.3 | 264.7 | 444.44 | 0 | 117643.268 | 121013.0538 | Ramna | New Ramna 33/11KV S/S | 111715.2077
5 | Water Works | 11 | 0 | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Lalbag | New Ramna 33/11KV S/S | 0
6 | GPO | 11 | 0 | DHK 00060 | 1 | 97306.6 | 97916.8 | 610.2 | 444.44 | 0 | 271197.288 | 278965.4908 | Ramna | New Ramna 33/11KV S/S | 233730.721
7 | Culvert Road | 11 | 0 | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 65 | 765109.8 | 787025.6832 | Ramna | New Ramna 33/11KV S/S | 769934.2629
8 | Secretariat (East) | 11 | 0 | DHK00059 | 1 | 81714.5 | 81719.4 | 4.9 | 444.44 | 0 | 2177.756 | 2240.1359 | Ramna | New Ramna 33/11KV S/S | 29358.1395
9 | Siddik Bazar | 11 | 0 | DHK00076 | 1 | 27275.4 | 29231.2 | 1955.8 | 444.44 | 0 | 869235.752 | 894134.2296 | Bangshal | New Ramna 33/11KV S/S | 765262.7858
10 | Bokshi Bazar | 11 | 0 | DHK 00206 | 1 | 84325 | 85464 | 1139 | 444.44 | 0 | 506217.16 | 520717.296 | Ramna | New Ramna 33/11KV S/S | 447450.7163
11 | Ramna 11 kV Sw/S Circuit-1 | 11 | 0 | DHK00198 | 1 | 44281.1 | 46597.3 | 2316.2 | 444.44 | 0 | 1029411.928 | 1058898.5083 | Ramna | New Ramna 33/11KV S/S | 1085933.5304
12 | TNT RMU | 11 | 0 | DHK 00207 | 1 | 59418.3 | 60351.5 | 933.2 | 444.44 | 0 | 414751.408 | 426631.5896 | Ramna | New Ramna 33/11KV S/S | 435698.3854
13 | DIT 11 kV Sw/S Circuit-1 | 11 | 0 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 35665.375
16 | Secretariat (West) | 11 | 0 | DHK 00006 | 1 | 67064.7 | 67894.2 | 829.5 | 444.44 | 0 | 368662.98 | 379223 | Ramna | New Ramna 33/11KV S/S | 77048.1002
17 | Ramna 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00197 | 1 | 84761.5 | 84763.4 | 1.9 | 444.44 | 0 | 844.436 | 868.6241 | Ramna | New Ramna 33/11KV S/S | 952.8917
18 | Sayed Nazrul Islam Road | 11 | 0 | DHK00186 | 1 | 21662.7 | 24569.9 | 2907.2 | 444.44 | 0 | 1292075.968 | 1329086.3239 | Ramna | New Ramna 33/11KV S/S | 1287356.6852
19 | Gulistan Complex | 11 | 0 | DHK00030 | 1 | 53974.5 | 54446.3 | 471.8 | 444.44 | 0 | 209686.792 | 215693.0819 | Ramna | New Ramna 33/11KV S/S | 200288.7599
20 | Mohanagor Nattomanso | 11 | 0 | DHK 00008 | 1 | 99681.5 | 99840.8 | 159.3 | 444.44 | 0 | 70799.292 | 72827.2741 | Ramna | New Ramna 33/11KV S/S | 40429.8335
21 | DIT 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00196 | 1 | 23893.8 | 24947 | 1053.2 | 444.44 | 0 | 468084.208 | 481492.0598 | Motijheel | New Ramna 33/11KV S/S | 701782.0483
22 | Jail | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 0
23 | Kosturi Bazar | 11 | 0 | HA021100713-02 | 1 | 75857044 | 75962552 | 105508 | 1 | 0 | 105508 | 108530.1819 | Ramna | New Ramna 33/11KV S/S | 101993.6695
24 | Kaptan Bazar | 11 | 0 | HA021101251-02 | 1 | 5820909 | 6236867 | 415958 | 1 | 0 | 415958 | 427872.7434 | Narinda | New Ramna 33/11KV S/S | 409490.3581
25 | G.T.V | 11 | 0 | HA-021101054-02 | 1 | 70498299 | 71120147 | 621848 | 1 | 0 | 621848 | 639660.2776 | Ramna | New Ramna 33/11KV S/S | 603518.518
26 | Kazi Alauddin Road | 11 | 0 | HA021100951-02 | 1 | 5667944 | 6043531 | 375587 | 1 | 0 | 375587 | 386345.3523 | Bangshal | New Ramna 33/11KV S/S | 300171.4873
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 | 0 | 2436 | 1 | 67423 | 67423 | 0 | 10 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 10.2097
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 | 0 | 2437 | 1 | 88090 | 88447 | 357 | 10 | 0 | 3570 | 3672.2594 | Ramna | New Ramna 33/11KV S/S | 3624.4279
7 | Pioneer | 11 | 0 | 06604395 | 1 | 23641.25 | 23746.79 | 105.54 | 8000 | 0 | 844320 | 859758.1646 | Ramna | Kakrail 33/11KV S/S | 826396.2524
8 | Pir Saheber Goli | 11 | 0 | DHK-00102 | 1 | 76172.5 | 79643 | 3470.5 | 444.444 | 0 | 1542442.902 | 1570646.0565 | Rajarbag | Kakrail 33/11KV S/S | 1456807.534
9 | Montri Para | 11 | 0 | DHK-00110 | 1 | 12504.9 | 12608.2 | 103.3 | 2222.22 | 0 | 229555.326 | 233752.6835 | Kakrail | Kakrail 33/11KV S/S | 183436.8651
10 | Baily Road 11 kV Sw/S-2 | 11 | 0 | 9119865 | 1 | 60588.9 | 62936.7 | 2347.8 | 1000 | 0 | 2347800 | 2390728.8929 | Kakrail | Kakrail 33/11KV S/S | 2272508.865
11 | Jamuna U/G 11 KV Jonaki O/H | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 0
12 | High Court | 11 | 0 | 1025651 | 1 | 28699 | 28975.9 | 276.9 | 1000 | 0 | 276900 | 281963.0422 | Ramna | Kakrail 33/11KV S/S | 304725.5352
13 | Secretaiat | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 0
16 | Shanti Nagar Bazar | 11 | 0 | 06604402 | 1 | 5592.5 | 5631.51 | 39.01 | 40000 | 0 | 1560400 | 1588931.4952 | Rajarbag | Kakrail 33/11KV S/S | 1455327.1248
17 | Tottho Bhovon | 11 | 0 | 9119867 | 1 | 31865.1 | 32076 | 210.9 | 1000 | 0 | 210900 | 214756.2499 | Kakrail | Kakrail 33/11KV S/S | 266523.7033
18 | Central Police Hospital/ PNT (Circuit House) | 11 | 0 | DHK00199 | 1 | 78080.07 | 78368.5 | 288.43 | 2222.22 | 0 | 640954.9146 | 652674.6032 | Kakrail | Kakrail 33/11KV S/S | 659362.3521
19 | Baily Road 11 kV Sw/S-1 | 11 | 0 | DHK00027 | 1 | 54773.6 | 55235.8 | 462.2 | 2222.22 | 0 | 1027110.084 | 1045890.5162 | Kakrail | Kakrail 33/11KV S/S | 1203453.6068
20 | Bijoy Nagar | 11 | 0 | D1025656 | 1 | 64877.9 | 65886.7 | 1008.8 | 1000 | 0 | 1008800 | 1027245.6372 | Ramna | Kakrail 33/11KV S/S | 1033096.3518
21 | Shilpakala Academy | 11 | 0 | D0086137 | 1 | 24493.9 | 25394.3 | 900.4 | 1000 | 0 | 900400 | 916863.5723 | Ramna | Kakrail 33/11KV S/S | 907912.3538
22 | Judges Complex | 11 | 0 | 06604344 | 1 | 667.77 | 670.94 | 3.17 | 40000 | 0 | 126800 | 129118.504 | Kakrail | Kakrail 33/11KV S/S | 137005.2472
23 | Auxiliary Transformer, AT-1 | 11 | 0 | 39333 | 1 | 492441 | 492441 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 0
24 | Auxiliary Transformer, AT-2 | 11 | 0 | 39254 | 1 | 1195010 | 1195010 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 0
8 | 11 kV Jamuna (F1) | 11 | 0 | BD017073 | 1 | 0.3512 | 0.3625 | 0.0113 | 2000 | 0 | 22.6 | 22.8027 | Kakrail | BSMMU 33/11KV S/S | 22.5473
9 | 11 kV Pukur Par (F2) | 11 | 0 | BD017074 | 1 | 2883.64 | 2906.26 | 22.62 | 2000 | 0 | 45240 | 45645.6695 | Kakrail | BSMMU 33/11KV S/S | 45879.8149
10 | 11 kV BSMMU Convention center (F3) | 11 | 0 | BD017075 | 1 | 1695.63 | 1714.95 | 19.32 | 2000 | 0 | 38640 | 38986.4869 | Kakrail | BSMMU 33/11KV S/S | 53187.5695
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 | 0 | BD017076 | 1 | 2841.69 | 2929.26 | 87.57 | 2000 | 0 | 175140 | 176710.4897 | Kakrail | BSMMU 33/11KV S/S | 172426.7726
12 | 11 kV Holi Family Feeder (F5) | 11 | 0 | BD017077 | 1 | 13664.28 | 14032.26 | 367.98 | 2000 | 0 | 735960 | 742559.3925 | Kakrail | BSMMU 33/11KV S/S | 663133.437
13 | 11 kV Navy House Feeder (F6) | 11 | 0 | BD017078 | 1 | 25982.79 | 26311.05 | 328.26 | 2000 | 0 | 656520 | 662407.0498 | Kakrail | BSMMU 33/11KV S/S | 617092.5697
14 | 11 kV Paribagh Feeder (F7) | 11 | 0 | BD017079 | 1 | 30291.6 | 31129.75 | 838.15 | 2000 | 0 | 1676300 | 1691331.4714 | Paribag | BSMMU 33/11KV S/S | 1532172.4233
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 | 0 | BD017080 | 1 | 5957.89 | 6172.02 | 214.13 | 2000 | 0 | 428260 | 432100.2302 | Paribag | BSMMU 33/11KV S/S | 400577.6906
18 | 11 kV Oncology Bhaban (F9) | 11 | 0 | BD017083 | 1 | 2161.63 | 2225.09 | 63.46 | 2000 | 0 | 126920 | 128058.0984 | Paribag | BSMMU 33/11KV S/S | 129888.7959
19 | Rupayan Trade Center | 11 | 0 | BD017084 | 1 | 928.49 | 1068.48 | 139.99 | 2000 | 0 | 279980 | 282490.5956 | Kakrail | BSMMU 33/11KV S/S | 277634.2814
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 | 0 | BD017085 | 1 | 1996.69 | 2058.21 | 61.52 | 2000 | 0 | 123040 | 124143.3062 | Kakrail | BSMMU 33/11KV S/S | 110824.2128
21 | 11 kV BSMMU RMU (F12) | 11 | 0 | BD017086 | 1 | 1881.92 | 1965.52 | 83.6 | 2000 | 0 | 167200 | 168699.2913 | Paribag | BSMMU 33/11KV S/S | 166467.8321
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 | 0 | BD017087 | 1 | 3915.28 | 4032.7 | 117.42 | 2000 | 0 | 234840 | 236945.8228 | Paribag | BSMMU 33/11KV S/S | 229298.4167
23 | 11 kV BCS Academy RMU (F14) | 11 | 0 | BD017088 | 1 | 965.83 | 995.07 | 29.24 | 2000 | 0 | 58480 | 59004.3933 | Paribag | BSMMU 33/11KV S/S | 75292.0174
24 | Spare | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 0
25 | BSMMU Super Specialist Hospital RMU | 11 | 0 | BD017090 | 1 | 971.62 | 1147.96 | 176.34 | 2000 | 0 | 352680 | 355842.5004 | Paribag | BSMMU 33/11KV S/S | 253677.7304
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKD4418 | 1 | 2460.23 | 2605.78 | 145.55 | 100 | 0 | 14555 | 14685.5155 | Paribag | BSMMU 33/11KV S/S | 15087.5942
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 0
3 | Chata Mosjid | 11 | 0 | 0 | 1 | 167272.9 | 169591.28 | 2318.38 | 1000 | 0 | 2318380 | 2319503.7751 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 2426211.3577
4 | AC mosjid | 11 | 0 | 0 | 1 | 4071.8 | 5346.4008 | 1274.6008 | 1000 | 0 | 1274600.8 | 1275218.63 | Lalbag | LALBAGH New 33/11 KV S/S | 1340177.0113
5 | Kazi Reaz Uddin Road | 11 | 0 | 0 | 1 | 16630.49 | 18853.63 | 2223.14 | 1000 | 0 | 2223140 | 2224217.61 | Lalbag | LALBAGH New 33/11 KV S/S | 2267338.6868
6 | Nazimuddin | 11 | 0 | 0 | 1 | 4214.292 | 4214.292 | 0 | 1000 | Estimated | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 0
7 | Kamal Bagh | 11 | 0 | 0 | 1 | 117683.69 | 13296.26 | -104387.43 | 1000 | Estimated | 1589074.2 | 1589844.4629 | Lalbag | LALBAGH New 33/11 KV S/S | 1583845.5588
8 | Rahamatganj | 11 | 0 | 0 | 1 | 37932 | 8699.95 | -29232.05 | 1000 | Estimated | 2471893.2 | 2473091.3867 | Lalbag | LALBAGH New 33/11 KV S/S | 2558519.7488
9 | Water Works 11kV Sw/S-1 | 11 | 0 | 0 | 1 | 18780.18 | 20641.601 | 1861.421 | 1000 | 0 | 1861421 | 1862323.276 | Lalbag | LALBAGH New 33/11 KV S/S | 1854345.8684
12 | City Colony | 11 | 0 | 0 | 1 | 20434.814 | 22484.11 | 2049.296 | 1000 | 0 | 2049296 | 2050289.3435 | Lalbag | LALBAGH New 33/11 KV S/S | 2080353.5364
13 | Water Works 11kV Sw/S-2 | 11 | 0 | 0 | 1 | 29754.25 | 32750 | 2995.75 | 1000 | 0 | 2995750 | 2997202.1128 | Lalbag | LALBAGH New 33/11 KV S/S | 3092062.2371
14 | Chun Goli | 11 | 0 | 0 | 1 | 5535.3348 | 6376.308 | 840.9732 | 1000 | 0 | 840973.2 | 841380.8401 | Lalbag | LALBAGH New 33/11 KV S/S | 894878.3402
15 | Alir Ghat | 11 | 0 | 0 | 1 | 117703.2 | 119606.4 | 1903.2 | 1000 | 0 | 1903200 | 1904122.5273 | Lalbag | LALBAGH New 33/11 KV S/S | 2096766.6729
16 | Club Ghat | 11 | 0 | 0 | 1 | 11435.815 | 13974.46 | 2538.645 | 1000 | 0 | 2538645 | 2539875.5429 | Lalbag | LALBAGH New 33/11 KV S/S | 2741271.1594
17 | Debidas Ghat | 11 | 0 | 0 | 1 | 21794.4 | 26831.902 | 5037.502 | 1000 | Estimated | 2436580.44 | 2437761.5097 | Lalbag | LALBAGH New 33/11 KV S/S | 2619436.8857
18 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 0
15 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
16 | Sowari Ghat | 11 | 0 | 8838019 | 1 | 72291.8 | 74886.8 | 2595 | 1000 | 0 | 2595000 | 2612060.995 | Lalbag | Lalbagh Old 33/11KV S/S | 2829205.9908
17 | Novo Kumar (Kara Odidoptor) | 11 | 0 | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 117709.2 | 118483.0867 | Lalbag | Lalbagh Old 33/11KV S/S | 132959.886
19 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
20 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
22 | Eidgah | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1294801.2 | 1303313.9541 | Lalbag | Lalbagh Old 33/11KV S/S | 1329598.8604
23 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
24 | Modumoti | 11 | 0 | 0 | 1 | 82497.9 | 87070.4 | 4572.5 | 444.44 | Estimated | 1942201.8 | 1954970.9311 | Lalbag | Lalbagh Old 33/11KV S/S | 2054834.6025
25 | Lalbagh O/H | 11 | 0 | 61389152 | 1 | 439667 | 440314 | 647 | 1000 | Estimated | 1059382.8 | 1066347.7806 | Lalbag | Lalbagh Old 33/11KV S/S | 1087853.6131
26 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
29 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
30 | Water Works 11 kV Sw/S-2 | 11 | 0 | 61389109 | 1 | 399921 | 400866 | 945 | 1000 | 0 | 945000 | 951212.9635 | Lalbag | Lalbagh Old 33/11KV S/S | 980831.1601
31 | Islambagh | 11 | 0 | 61389186 | 1 | 498372 | 499228 | 856 | 1000 | 0 | 856000 | 861627.8273 | Lalbag | Lalbagh Old 33/11KV S/S | 876487.4197
32 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
33 | WASA Low Lift Pump | 11 | 0 | 61389202 | 1 | 15416 | 15477 | 61 | 1000 | 0 | 61000 | 61401.0484 | Lalbag | Lalbagh Old 33/11KV S/S | 45712.4958
34 | Shahi Mosjid | 11 | 0 | 06604459 | 1 | 35388.6 | 35606.2 | 217.6 | 8000 | 0 | 1740800 | 1752245.002 | Azimpur | Lalbagh Old 33/11KV S/S | 1250534.8854
35 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
36 | 33/0.4 kV Auxiliary Transformer | 0.415 | 0 | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0
7 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0
8 | Spare | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0
9 | Chawk Bazar | 11 | 0 | DHK-60904 | 1 | 954595.7 | 963274.2 | 8678.5 | 60 | 0 | 520710 | 522405.3875 | Lalbag | Mitford 33/11 kV | 508276.2976
10 | Spare | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0
11 | Chatrabas | 11 | 0 | DHK-66485 | 1 | 782736 | 795411 | 12675 | 60 | 0 | 760500 | 762976.1234 | Bangshal | Mitford 33/11 kV | 353557.5482
12 | Begum Bazar | 11 | 0 | DHK-66481 | 1 | 3586533 | 3626756 | 40223 | 60 | 0 | 2413380 | 2421237.7604 | Bangshal | Mitford 33/11 kV | 2357293.0663
13 | SCC ROAD | 11 | 0 | DHK-60901 | 1 | 21576.1 | 48991.1 | 27415 | 60 | 0 | 1644900 | 1650255.6547 | Bangshal | Mitford 33/11 kV | 1574186.7645
16 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0
17 | Armanitola | 11 | 0 | DHK-61104 | 1 | 652439.3 | 668332.7 | 15893.4 | 60 | 0 | 953604 | 956708.8537 | Bangshal | Mitford 33/11 kV | 952602.7371
18 | Mitford Hospital (RMU) | 11 | 0 | DHK-61101 | 1 | 374512.4 | 383048.6 | 8536.2 | 60 | 0 | 512172 | 513839.5885 | Bangshal | Mitford 33/11 kV | 528540.0121
19 | Emamganj | 11 | 0 | DHK-68130 | 1 | 1435.73 | 1447.92 | 12.19 | 60000 | 0 | 731400 | 733781.3763 | Bangshal | Mitford 33/11 kV | 1159712.4523
20 | Kamal Dho Road | 11 | 0 | DHK-68129 | 1 | 1205.82 | 1216.26 | 10.44 | 60000 | 0 | 626400 | 628439.5052 | Lalbag | Mitford 33/11 kV | 594724.3345
21 | Spare | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0
22 | Panghat | 11 | 0 | DHK-68127 | 1 | 1481.94 | 1505.39 | 23.45 | 60000 | 0 | 1407000 | 1411581.0725 | Bangshal | Mitford 33/11 kV | 1500768.6523
23 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | U0004460 | 1 | 5513.28 | 5554.67 | 41.39 | 100 | 0 | 4139 | 4152.4762 | Bangshal | Mitford 33/11 kV | 4434.1352
7 | Chadni chwok | 11 | 0 | DHK60916 | 1 | 386413 | 399421 | 13008 | 60 | 0 | 780480 | 792142.0147 | Paribag | Azimpur 33/11 KV | 648152.1238
8 | BGB | 11 | 0 | DHK61090 | 1 | 661190 | 665574 | 4384 | 60 | 0 | 263040 | 266970.3715 | Jigatola | Azimpur 33/11 KV | 253340.1998
9 | Pari Bibi Mazar | 11 | 0 | DHK61091 | 1 | 708482 | 745025 | 36543 | 60 | 0 | 2192580 | 2225341.7622 | Azimpur | Azimpur 33/11 KV | 2144033.6462
10 | Azimpur | 11 | 0 | DHK61086 | 1 | 264194 | 282859 | 18665 | 60 | 0 | 1119900 | 1136633.6642 | Azimpur | Azimpur 33/11 KV | 1104066.6214
11 | Aazd | 11 | 0 | DHK61089 | 1 | 938971 | 960626 | 21655 | 60 | 0 | 1299300 | 1318714.278 | Azimpur | Azimpur 33/11 KV | 1257709.9294
12 | Dayra Sharif | 11 | 0 | DHK61088 | 1 | 482306 | 498851 | 16545 | 60 | 0 | 992700 | 1007533.0284 | Azimpur | Azimpur 33/11 KV | 980271.2172
13 | Naya palton | 11 | 0 | DHK86065 | 1 | 1842.39 | 1871.03 | 28.64 | 60000 | 0 | 1718400 | 1744076.5145 | Azimpur | Azimpur 33/11 KV | 1689342.4234
16 | Viqarunnisa Noon School | 11 | 0 | DHK66477 | 1 | 1560667 | 1584644 | 23977 | 60 | 0 | 1438620 | 1460116.0121 | Azimpur | Azimpur 33/11 KV | 1388906.1459
17 | Subal Das Lane | 11 | 0 | DHK66480 | 1 | 3964091 | 3981086 | 16995 | 60 | 0 | 1019700 | 1034936.4652 | Azimpur | Azimpur 33/11 KV | 1287496.6695
18 | Lalbagh | 11 | 0 | DHK61093 | 1 | 646194 | 685659 | 39465 | 60 | 0 | 2367900 | 2403281.4122 | Azimpur | Azimpur 33/11 KV | 2365446.3751
19 | Zahrul Haque Hall | 11 | 0 | DHK66497 | 1 | 1217962 | 1228090 | 10128 | 60 | 0 | 607680 | 616760.0188 | Ramna | Azimpur 33/11 KV | 675859.2968
20 | Eden College | 11 | 0 | DHK60917 | 1 | 918378 | 925859 | 7481 | 60 | 0 | 448860 | 455566.9136 | Azimpur | Azimpur 33/11 KV | 455119.369
21 | Nilkhet/ PWD-01 | 11 | 0 | DHK60918 | 1 | 456044 | 466773 | 10729 | 60 | 0 | 643740 | 653358.8311 | Azimpur | Azimpur 33/11 KV | 648152.1238
22 | BUET | 11 | 0 | DHK66496 | 1 | 937828 | 949620 | 11792 | 60 | 0 | 707520 | 718091.8386 | Ramna | Azimpur 33/11 KV | 902348.6159
23 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIG2780 | 1 | 381002 | 385337 | 4335 | 1 | 0 | 4335 | 4399.774 | Azimpur | Azimpur 33/11 KV | 2203.9333
4 | Rasulpur | 11 | 0 | HA-021101042-02 | 1 | 89078209 | 90531613 | 1453404 | 1 | 0 | 1453404 | 1475786.882 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1248201.2259
5 | Bheribadh | 11 | 0 | HA-021101105-02 | 1 | 59737086 | 62150594 | 2413508 | 1 | 0 | 2413508 | 2450676.7878 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2398606.8547
7 | Panna Tower 11 KV Faridpur Tower Express | 11 | 0 | 30799521 | 1 | 2623.32 | 2629.31 | 5.99 | 60000 | 0 | 359400 | 364934.8739 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 488122.7019
8 | Panna Battery Express | 11 | 0 | DHK15431 | 1 | 5243.73 | 5261.14 | 17.41 | 60000 | 0 | 1044600 | 1060687.1709 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1118589.0702
9 | Eidgah | 11 | 0 | 30799460 | 1 | 5297.07 | 5334.36 | 37.29 | 60000 | 0 | 2237400 | 2271856.6688 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2848456.9491
10 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 0
12 | Huzur Para | 11 | 0 | HA-021101055-02 | 1 | 97687286 | 99557723 | 1870437 | 1 | 0 | 1870437 | 1899242.3224 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1901795.8946
13 | Kamrangirchar | 11 | 0 | HA-021101015-02 | 1 | 17588896 | 19388783 | 1799887 | 1 | 0 | 1799887 | 1827605.83 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1737567.1439
14 | Munshihati | 11 | 0 | HA-021100854-02 | 1 | 48912982 | 50206769 | 1293787 | 1 | 0 | 1293787 | 1313711.7297 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1205376.9608
15 | Jhawchar | 11 | 0 | HA-021101028-02 | 1 | 97420106 | 98824125 | 1404019 | 1 | 0 | 1404019 | 1425641.3374 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1328999.0751
16 | RMU Express | 11 | 0 | HA-021101248-02 | 1 | 4693909 | 5318135 | 624226 | 1 | 0 | 624226 | 633839.2782 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 704501.3661
17 | Koyla Ghat | 11 | 0 | HA-021101259-02 | 1 | 14045899 | 15254118 | 1208219 | 1 | ESTIMATED | 2189391.12 | 2223108.4368 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1816011.9444
18 | Muslimbagh | 11 | 0 | HA-021100908-02 | 1 | 22904364 | 24575572 | 1671208 | 1 | 0 | 1671208 | 1696945.1326 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1737474.4882
19 | Noyagaon | 11 | 0 | HA-021101087-02 | 1 | 516458 | 3217494 | 2701036 | 1 | 0 | 2701036 | 2742632.8101 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2660587.4202
20 | Nurbagh | 11 | 0 | HA-021100982-02 | 1 | 19118491 | 21245035 | 2126544 | 1 | 0 | 2126544 | 2159293.4513 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2300317.433
21 | Ali Nagar | 11 | 0 | HA-021101022-02 | 1 | 17434438 | 19758728 | 2324290 | 1 | 0 | 2324290 | 2360084.8023 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2402380.2856
12 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
13 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
14 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
15 | Nababgonj Park | 11 | 0 | 0 | 1 | 6757988 | 8188769 | 1430781 | 1 | 0 | 1430781 | 1444952.9565 | Azimpur | BGB 33/11 KV S/S | 1573011.5868
16 | Kholamura Ghat | 11 | 0 | 0 | 1 | 72049102 | 74784480 | 2735378 | 1 | 0 | 2735378 | 2762472.0542 | Kamrangirchar | BGB 33/11 KV S/S | 2841690.4191
17 | Khalpar | 11 | 0 | 0 | 1 | 81615032 | 82977184 | 1362152 | 1 | 0 | 1362152 | 1375644.1828 | Kamrangirchar | BGB 33/11 KV S/S | 1437529.7992
18 | Shahidnagar | 11 | 0 | 0 | 1 | 12336427 | 14195510 | 1859083 | 1 | 0 | 1859083 | 1877497.3089 | Azimpur | BGB 33/11 KV S/S | 1808709.9159
19 | BGB 1 No Gate | 11 | 0 | 0 | 1 | 29847534 | 31209790 | 1362256 | 1 | 0 | 1362256 | 1375749.2129 | Azimpur | BGB 33/11 KV S/S | 1318685.5995
21 | Ganaktuli | 11 | 0 | 0 | 1 | 21869943 | 22588480 | 718537 | 1 | 0 | 718537 | 725654.1445 | Jigatola | BGB 33/11 KV S/S | 693078.4919
22 | Thana | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
23 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 28102896 | 30156751 | 2053855 | 1 | 0 | 2053855 | 2074198.5352 | Jigatola | BGB 33/11 KV S/S | 1909183.4664
24 | Sikder Medical | 11 | 0 | 0 | 1 | 33392224 | 34515480 | 1123256 | 1 | 0 | 1123256 | 1134381.9061 | Jigatola | BGB 33/11 KV S/S | 1138392.2283
25 | Gas Field | 11 | 0 | 0 | 1 | 49867262 | 51908120 | 2040858 | 1 | 0 | 2040858 | 2061072.7993 | Kamrangirchar | BGB 33/11 KV S/S | 1985612.1672
26 | Hazaribagh | 11 | 0 | 0 | 1 | 36947488 | 38417940 | 1470452 | 1 | 0 | 1470452 | 1485016.8997 | Jigatola | BGB 33/11 KV S/S | 1465699.7946
27 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
28 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 0 | 1 | 1998.58 | 2056.85 | 58.27 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 0
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 0 | 1 | 1590.01 | 1644.21 | 54.2 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 0
0 | Salek Garden | 11 | 0 | 2761 | 1 | 506.46 | 549.1 | 42.64 | 60000 | 0 | 2558400 | 2562123.5191 | Jigatola | Jigatola New 33/11 KV S/S | 2460950.9042
4 | Jigatola Local | 11 | 0 | 2850 | 1 | 408.27 | 438.35 | 30.08 | 60000 | 0 | 1804800 | 1807426.7227 | Jigatola | Jigatola New 33/11 KV S/S | 1737565.9216
6 | City College | 11 | 0 | 2784 | 1 | 450.2 | 479.78 | 29.58 | 60000 | 0 | 1774800 | 1777383.0604 | Jigatola | Jigatola New 33/11 KV S/S | 2346194.6487
7 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0
8 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0
10 | Post Office | 11 | 0 | 2836 | 1 | 330.76 | 358.58 | 27.82 | 60000 | 0 | 1669200 | 1671629.3692 | Jigatola | Jigatola New 33/11 KV S/S | 1589764.671
11 | Leather Institute | 11 | 0 | 2835 | 1 | 54.22 | 57.38 | 3.16 | 60000 | 0 | 189600 | 189875.9456 | Jigatola | Jigatola New 33/11 KV S/S | 195265.8799
12 | Mina Bazar | 11 | 0 | 2853 | 1 | 169.47 | 181.89 | 12.42 | 60000 | 0 | 745200 | 746284.571 | Jigatola | Jigatola New 33/11 KV S/S | 706562.076
13 | Mitali | 11 | 0 | 2852 | 1 | 278.85 | 330.42 | 51.57 | 60000 | 0 | 3094200 | 3098703.3274 | Jigatola | Jigatola New 33/11 KV S/S | 2956625.83
14 | Road-2 | 11 | 0 | 2839 | 1 | 546.35 | 584.66 | 38.31 | 60000 | 0 | 2298600 | 2301945.4038 | Jigatola | Jigatola New 33/11 KV S/S | 2450136.1786
15 | SS-2 | 11 | 0 | 2838 | 1 | 253.56 | 272.32 | 18.76 | 60000 | 0 | 1125600 | 1127238.2087 | Jigatola | Jigatola New 33/11 KV S/S | 1112715.1061
16 | Spare | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0
17 | Bou Bazar | 11 | 0 | 2843 | 1 | 440.65 | 471.44 | 30.79 | 60000 | 0 | 1847400 | 1850088.7231 | Jigatola | Jigatola New 33/11 KV S/S | 1774816.6433
18 | BGB | 11 | 0 | 2764 | 1 | 152.88 | 169.64 | 16.76 | 60000 | 0 | 1005600 | 1007063.5596 | Jigatola | Jigatola New 33/11 KV S/S | 934872.9509
19 | Dhamondi-12 | 11 | 0 | 2763 | 1 | 354.88 | 375.07 | 20.19 | 60000 | 0 | 1211400 | 1213163.0828 | Dhanmondi | Jigatola New 33/11 KV S/S | 1602982.669
0 | Mitali Road | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
7 | Bou Bazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
8 | Mina Bazar | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
10 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
11 | Simanto Square | 11 | 0 | DHK60946 | 1 | 1111.52 | 1125.53 | 14.01 | 60000 | 0 | 840600 | 852145.3731 | Jigatola | Jigatola Old 33/11KV S/S | 901151.3428
12 | Post Office | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
13 | Hazaribagh Sw/S-2 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
14 | Green Road Via Park | 11 | 0 | DHK61070 | 1 | 3394.83 | 3415.05 | 20.22 | 60000 | 0 | 1213200 | 1229862.9154 | Jigatola | Jigatola Old 33/11KV S/S | 476757.7712
15 | PWD Quarters 11 kV Saleq Grand | 11 | 0 | DHK61028 | 1 | 3628.17 | 3629.4 | 1.23 | 60000 | 0 | 73800 | 74813.6195 | Jigatola | Jigatola Old 33/11KV S/S | 63933.0345
18 | Road No.-2 | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
19 | Hzaribagh O/H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
20 | B.G.B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
21 | 11 kV City College | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
23 | Jigatala Local | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 243284 | 1 | 83536 | 83791 | 255 | 10 | 0 | 2550 | 2585.0234 | Jigatola | Jigatola Old 33/11KV S/S | 3440.2061
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 412277 | 1 | 38966 | 39498 | 532 | 10 | 0 | 5320 | 5393.0685 | Jigatola | Jigatola Old 33/11KV S/S | 0
7 | Spare | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0
0 | D Block dhaka uddyan | 11 | 0 | BD014031 | 1 | 48238.67 | 48613.5 | 374.83 | 1000 | 0 | 374830 | 376392.0985 | Adabor | Dhaka Uddyan 33/11 KV S/S | 356370.9019
8 | Dill Mohammad O/H | 11 | 0 | BD014027 | 1 | 13971.54 | 15908.7 | 1937.16 | 1000 | 0 | 1937160 | 1945233.0858 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1925614.3584
9 | Turag O/H | 11 | 0 | BD014028 | 1 | 24750.51 | 25472.56 | 722.05 | 1000 | 0 | 722050 | 725059.1327 | Adabor | Dhaka Uddyan 33/11 KV S/S | 419185.0275
10 | Nabadoy O/H | 11 | 0 | BD014025 | 1 | 34037.39 | 34907.65 | 870.26 | 1000 | 0 | 870260 | 873886.7957 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1264712.0241
11 | Chandrima O/H | 11 | 0 | BD014024 | 1 | 2884.39 | 3855 | 970.61 | 1000 | 0 | 970610 | 974655.0029 | Adabor | Dhaka Uddyan 33/11 KV S/S | 879754.0777
12 | Shyamoli Housing Project-2 | 11 | 0 | BD014029 | 1 | 23461.67 | 24761.38 | 1299.71 | 1000 | 0 | 1299710 | 1305126.5223 | Adabor | Dhaka Uddyan 33/11 KV S/S | 2226602.9518
13 | Spare | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0
16 | Spare | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0
17 | Spare | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0
18 | U Lab | 11 | 0 | BD013959 | 1 | 33037.97 | 35792.66 | 2754.69 | 1000 | 0 | 2754690 | 2766170.13 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2585824.4138
19 | Akota | 11 | 0 | BD014020 | 1 | 5038.54 | 5565.65 | 527.11 | 1000 | 0 | 527110 | 529306.7232 | Adabor | Dhaka Uddyan 33/11 KV S/S | 494561.9781
20 | Burigonga O/H | 11 | 0 | BD014019 | 1 | 3859.78 | 4279.01 | 419.23 | 1000 | 0 | 419230 | 420977.1349 | Adabor | Dhaka Uddyan 33/11 KV S/S | 372374.7602
21 | Garden City | 11 | 0 | BD014021 | 1 | 78655.82 | 81041.07 | 2385.25 | 1000 | 0 | 2385250 | 2395190.4943 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2278829.2831
22 | Avenue O/H | 11 | 0 | BD014017 | 1 | 11015.72 | 11977.96 | 962.24 | 1000 | 0 | 962240 | 966250.121 | Adabor | Dhaka Uddyan 33/11 KV S/S | 894892.5874
23 | Chand Uddyan | 11 | 0 | BD014018 | 1 | 6743.1 | 7472.53 | 729.43 | 1000 | 0 | 729430 | 732469.8888 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 645275.1572
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4416 | 1 | 1720.85 | 1760.35 | 39.5 | 100 | 0 | 3950 | 3966.4616 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1513.851
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 2409.7413
16 | Lalmatia O/H | 11 | 0 | DHK61042 | 1 | 3104.91 | 3125.6 | 20.69 | 60000 | 0 | 1241400 | 1240075.1783 | Satmasjid | Satmasjid 33/11KV S/S | 1343819.1874
16 | Asad Avenue (South) | 11 | 0 | DHK 60999 | 1 | 2892.58 | 2895.94 | 3.36 | 60000 | 0 | 201600 | 201384.8525 | Satmasjid | Satmasjid 33/11KV S/S | 143036.2105
17 | Madrasha Road | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 0
18 | Bashbari | 11 | 0 | DHK61002 | 1 | 2314.11 | 2340.79 | 26.68 | 60000 | 0 | 1600800 | 1599091.6268 | Satmasjid | Satmasjid 33/11KV S/S | 1533732.8114
19 | Road-27 | 11 | 0 | DHK61001 | 1 | 1430.55 | 1432.05 | 1.5 | 60000 | 0 | 90000 | 89903.952 | Satmasjid | Satmasjid 33/11KV S/S | 435118.5562
20 | Boishakhi O/H | 11 | 0 | DHK61024 | 1 | 3992.78 | 4043.27 | 50.49 | 60000 | 0 | 3029400 | 3026167.0253 | Dhanmondi | Satmasjid 33/11KV S/S | 2814447.7883
21 | Katasur O/H | 11 | 0 | DHK61003 | 1 | 3557.69 | 3581.57 | 23.88 | 60000 | 0 | 1432800 | 1431270.9163 | Satmasjid | Satmasjid 33/11KV S/S | 1334804.3002
22 | Nurjahan Road | 11 | 0 | DHK61000 | 1 | 1769.35 | 1793.34 | 23.99 | 60000 | 0 | 1439400 | 1437863.8728 | Shyamoli | Satmasjid 33/11KV S/S | 1376873.7739
25 | polpar over head | 11 | 0 | DHK61003 | 1 | 1725.79 | 1761.42 | 35.63 | 60000 | 0 | 2137800 | 2135518.5405 | Dhanmondi | Satmasjid 33/11KV S/S | 2016930.7661
26 | Satmosjid Housing | 11 | 0 | DHK61043 | 1 | 2792.38 | 2792.38 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 0
27 | Physical College | 11 | 0 | DHK61041 | 1 | 3172.69 | 3216.68 | 43.99 | 60000 | 0 | 2639400 | 2636583.2332 | Satmasjid | Satmasjid 33/11KV S/S | 2184607.6683
28 | Asad Avenue (North) | 11 | 0 | DHK61022 | 1 | 2725.31 | 2725.31 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 0
29 | Spare Feeder | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 0
30 | Ghraphic artch college | 11 | 0 | DHK61023 | 1 | 1015.9 | 1042.11 | 26.21 | 60000 | 0 | 1572600 | 1570921.7218 | Dhanmondi | Satmasjid 33/11KV S/S | 1701409.7136
31 | Mohammadpur O/H | 11 | 0 | DHK61025 | 1 | 2104.86 | 2132.57 | 27.71 | 60000 | 0 | 1662600 | 1660825.6738 | Shyamoli | Satmasjid 33/11KV S/S | 1343218.1949
32 | Bosila Feeder | 11 | 0 | DHK60997 | 1 | 3970.07 | 4018.46 | 48.39 | 60000 | 0 | 2903400 | 2900301.4925 | Satmasjid | Satmasjid 33/11KV S/S | 3015179.277
33 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIB 7375 | 1 | 5415.28 | 5560.3 | 145.02 | 60 | 0 | 8701.2 | 8691.9141 | Satmasjid | Satmasjid 33/11KV S/S | 0
5 | Dhaka Uddyan | 11 | 0 | DHK86067 | 1 | 3249.24 | 3249.81 | 0.57 | 60000 | 0 | 34200 | 34177.6075 | Adabor | Japan Garden 33/11 KV | 0
0 | Shia Mosjid | 11 | 0 | DHK60950 | 1 | 3353.91 | 3392.62 | 38.71 | 60000 | 0 | 2322600 | 2321079.2736 | Shyamoli | Japan Garden 33/11 KV | 1677029.4105
6 | Shekhar Tek | 11 | 0 | DHK60977 | 1 | 2275.45 | 2311.48 | 36.03 | 60000 | 0 | 2161800 | 2160384.5576 | Adabor | Japan Garden 33/11 KV | 1966584.1503
7 | Madrasha Road | 11 | 0 | DHK61083 | 1 | 1925.96 | 1945.1 | 19.14 | 60000 | 0 | 1148400 | 1147648.0831 | Shyamoli | Japan Garden 33/11 KV | 1148666.6379
8 | Baitul Aman Housing | 11 | 0 | DHK668115 | 1 | 3971.87 | 4021.57 | 49.7 | 60000 | 0 | 2982000 | 2980047.5303 | Adabor | Japan Garden 33/11 KV | 2714650.3131
11 | Shyamoli Square | 11 | 0 | DHK86063 | 1 | 446.82 | 452.52 | 5.7 | 30000 | 0 | 171000 | 170888.0374 | Shyamoli | Japan Garden 33/11 KV | 163284.9924
12 | Mohammadi Housing | 11 | 0 | DHK60948 | 1 | 3719.11 | 3751.71 | 32.6 | 60000 | 0 | 1956000 | 1954719.3056 | Adabor | Japan Garden 33/11 KV | 1343295.1846
13 | Chand Housing | 11 | 0 | DHK60867 | 1 | 2131.68 | 2147.7 | 16.02 | 60000 | 0 | 961200 | 960570.6526 | Satmasjid | Japan Garden 33/11 KV | 891350.9825
14 | PC Culture Housing | 11 | 0 | DHK60979 | 1 | 3977.85 | 4021.99 | 44.14 | 60000 | 0 | 2648400 | 2646665.9554 | Adabor | Japan Garden 33/11 KV | 2456140.6176
15 | Mehedibagh | 11 | 0 | DHK68121 | 1 | 2158.29 | 2208.55 | 50.26 | 60000 | 0 | 3015600 | 3013625.5306 | Adabor | Japan Garden 33/11 KV | 2845397.7111
16 | 33/11 kV Incoming (Spare) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 0
17 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | 0 | 1 | 636966 | 642363 | 5397 | 1 | 0 | 5397 | 5393.4663 | Adabor | Japan Garden 33/11 KV | 0
0 | Mokarom Bhabon | 11 | 0 | 2761 | 1 | 44.12 | 46.92 | 2.8 | 60000 | 0 | 168000 | 168036.2342 | Ramna | Dhaka University 33/11 KV S/S | 191876.7922
4 | 11 kV Shaid Minar RMU | 11 | 0 | 2850 | 1 | 105.12 | 110.73 | 5.61 | 60000 | 0 | 336600 | 336672.5979 | Ramna | Dhaka University 33/11 KV S/S | 339844.4752
5 | 11 kV Shaidulla Hall | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0
6 | Spare | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
7 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
8 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
10 | MBA Bhabon | 11 | 0 | 2836 | 1 | 81.98 | 86.15 | 4.17 | 60000 | 0 | 250200 | 250253.9631 | Ramna | Dhaka University 33/11 KV S/S | 301348.8178
11 | Suprime Court | 11 | 0 | 2835 | 1 | 39.19 | 44.16 | 4.97 | 60000 | 0 | 298200 | 298264.3158 | Ramna | Dhaka University 33/11 KV S/S | 306762.2696
12 | Karjon Hall | 11 | 0 | 2853 | 1 | 45.01 | 50.23 | 5.22 | 60000 | 0 | 313200 | 313267.551 | Ramna | Dhaka University 33/11 KV S/S | 333228.0341
13 | Spare | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
14 | Swimming Pool | 11 | 0 | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0
15 | Spare | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
16 | Police Head Quarter RMU | 11 | 0 | 2772 | 1 | 54.79 | 62.93 | 8.14 | 60000 | 0 | 488400 | 488505.3381 | Ramna | Dhaka University 33/11 KV S/S | 444504.5437
17 | Spare | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
18 | Spare | 11 | 0 | 2764 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
19 | Spare | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0
6 | Segunbagicha | 11 | 0 | DHK-C9360 | 1 | 61185.99 | 71954 | 10768.01 | 60 | 0 | 646080.6 | 648570.0837 | Ramna | Biddyut Bhaban 33/11 KV | 628132.1417
0 | Secretariat RMU | 11 | 0 | DHK-C9379 | 1 | 66319.31 | 68931.7 | 2612.39 | 60 | 0 | 156743.4 | 157347.3651 | Ramna | Biddyut Bhaban 33/11 KV | 189151.3106
7 | NBR RMU | 11 | 0 | DHK-C9319 | 1 | 35791.29 | 43622.4 | 7831.11 | 60 | 0 | 469866.6 | 471677.0943 | Ramna | Biddyut Bhaban 33/11 KV | 454185.7713
8 | Ramna 11 kV Sw/S-2 | 11 | 0 | DHK-C9364 | 1 | 81944.91 | 99344.1 | 17399.19 | 60 | 0 | 1043951.4 | 1047973.9631 | Ramna | Biddyut Bhaban 33/11 KV | 1309281.295
11 | Ramna 11 kV Sw/S-1 | 11 | 0 | DHK-C9375 | 1 | 30061.75 | 30685.5 | 623.75 | 60 | 0 | 37425 | 37569.2064 | Ramna | Biddyut Bhaban 33/11 KV | 3932.094
12 | Family Planning | 11 | 0 | DHK-C9378 | 1 | 33829.12 | 41466 | 7636.88 | 60 | 0 | 458212.8 | 459978.3897 | Ramna | Biddyut Bhaban 33/11 KV | 450311.5022
13 | Muktijuddho Montranalaya | 11 | 0 | DHK-C9376 | 1 | 9833.69 | 26269.1 | 16435.41 | 60 | 0 | 986124.6 | 989924.3443 | Ramna | Biddyut Bhaban 33/11 KV | 925250.3935
14 | Purana Palton | 11 | 0 | DHK-C9318 | 1 | 38036.29 | 43328.3 | 5292.01 | 60 | 0 | 317520.6 | 318744.0733 | Ramna | Biddyut Bhaban 33/11 KV | 328976.7665
15 | Tip Top Feeder | 11 | 0 | DHK-C9318 | 1 | 42816.99 | 66509.6 | 23692.61 | 60 | 0 | 1421556.6 | 1427034.1549 | Kakrail | Biddyut Bhaban 33/11 KV | 1299449.2529
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 | 0 | DHKD3784 | 1 | 331579 | 336257 | 4678 | 1 | 0 | 4678 | 4696.0253 | Ramna | Biddyut Bhaban 33/11 KV | 4800.6724
6 | Nearest O/H | 11 | 0 | 00000126 | 1 | 6865423 | 7074262 | 208839 | 1 | 0 | 208839 | 210729.7741 | Ramna | DMC 33/11 KV SS | 229906.9253
0 | Jagannath Hall | 11 | 0 | 00000002 | 1 | 2433494 | 2545753.8 | 112259.8 | 1 | 0 | 112259.8 | 113276.1711 | Ramna | DMC 33/11 KV SS | 96242.8599
7 | Samsun Nahar Hall | 11 | 0 | 00000024 | 1 | 8763059 | 9054018 | 290959 | 1 | 0 | 290959 | 293593.2672 | Ramna | DMC 33/11 KV SS | 312413.2678
8 | Spare, 4L | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0
9 | Board Office O/H, (5L) | 11 | 0 | 00000023 | 1 | 20238430 | 20726990 | 488560 | 1 | 0 | 488560 | 492983.2953 | Lalbag | DMC 33/11 KV SS | 466712.6927
10 | OT- Complex | 11 | 0 | 00000167 | 1 | 5287027 | 5711026 | 423999 | 1 | 0 | 423999 | 427837.7768 | Ramna | DMC 33/11 KV SS | 405707.0733
11 | Alia Mdrasha O/H, (7L) | 11 | 0 | 00000148 | 1 | 9243737 | 9318217 | 74480 | 1 | 0 | 74480 | 75154.3226 | Lalbag | DMC 33/11 KV SS | 71193.4446
12 | Majed Sordar Road | 11 | 0 | 00000164 | 1 | 51746392 | 53489908 | 1743516 | 1 | 0 | 1743516 | 1759301.3409 | Bangshal | DMC 33/11 KV SS | 1689289.8138
15 | Chankharpool, 9L | 11 | 0 | 00000001 | 1 | 44457492 | 45648168 | 1190676 | 1 | 0 | 1190676 | 1201456.0712 | Bangshal | DMC 33/11 KV SS | 1157798.1959
16 | Shahidullah College O/H, (10L) | 11 | 0 | 00000003 | 1 | 12322570 | 12584169 | 261599 | 1 | 0 | 261599 | 263967.4494 | Lalbag | DMC 33/11 KV SS | 265403.8751
17 | Ananda Bazar | 11 | 0 | 00000111 | 1 | 14499445 | 14714284 | 214839 | 1 | 0 | 214839 | 216784.0965 | Ramna | DMC 33/11 KV SS | 169141.9631
18 | Hosseni Dalan O/H, (12L) | 11 | 0 | 0 | 1 | 4.6 | 23.41 | 18.81 | 60000 | 0 | 1614720 | 1629339.2554 | Lalbag | DMC 33/11 KV SS | 1651805.4359
19 | Badrun Nessa College | 11 | 0 | 00000006 | 1 | 18502514 | 19009274 | 506760 | 1 | 0 | 506760 | 511348.0734 | Lalbag | DMC 33/11 KV SS | 487810.3149
20 | Dhaka Medical College, Unit-II | 11 | 0 | 00000125 | 1 | 11041413 | 11353372 | 311959 | 1 | 0 | 311959 | 314783.3957 | Ramna | DMC 33/11 KV SS | 318669.3545
21 | Spare, 15L | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0
22 | Sheikh Hasina National Burn Institute | 11 | 0 | 00000127 | 1 | 19088354 | 19677112 | 588758 | 1 | 0 | 588758 | 594088.462 | Ramna | DMC 33/11 KV SS | 527600.9918
23 | Aux. Transformer, AT-1 | 0.415 | 0 | DHKF-7804 | 1 | 2469.39 | 2551.19 | 81.8 | 100 | 0 | 8180 | 8254.0596 | Ramna | DMC 33/11 KV SS | 7320.9952
24 | Aux. Transformer, AT-2 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 0
6 | Secratariet East | 11 | 0 | BD 013966 | 1 | 3164.56 | 3406.54 | 241.98 | 1000 | 0 | 241980 | 245293.0009 | Ramna | BB Aveneu 33/11 KV S/S | 245463.3743
0 | Taher Bag O/H | 11 | 0 | BD 014045 | 1 | 16925.42 | 17659.83 | 734.41 | 1000 | 0 | 734410 | 744464.9674 | Narinda | BB Aveneu 33/11 KV S/S | 740283.3012
7 | Al Raji Complex | 11 | 0 | BD 013983 | 1 | 12207.81 | 12982.02 | 774.21 | 1000 | 0 | 774210 | 784809.8778 | Ramna | BB Aveneu 33/11 KV S/S | 793405.3649
8 | Raduni | 11 | 0 | BD 013999 | 1 | 25230.43 | 26506.32 | 1275.89 | 1000 | 0 | 1275890 | 1293358.488 | Ramna | BB Aveneu 33/11 KV S/S | 1280815.0384
9 | Sundor Bon Square O/H | 11 | 0 | BD 013954 | 1 | 11796.22 | 12263.75 | 467.53 | 1000 | 0 | 467530 | 473931.0551 | Narinda | BB Aveneu 33/11 KV S/S | 515871.5523
10 | Shromo Bhobon O/H | 11 | 0 | BD 013985 | 1 | 11614.06 | 12112.38 | 498.32 | 1000 | 0 | 498320 | 505142.6077 | Ramna | BB Aveneu 33/11 KV S/S | 521299.6391
11 | Nawabpur Road | 11 | 0 | BD 013953 | 1 | 17725.04 | 18556.72 | 831.68 | 1000 | 0 | 831680 | 843066.7121 | Narinda | BB Aveneu 33/11 KV S/S | 849749.7199
12 | Spair | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0
15 | Spare | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0
16 | Ahad Police Box | 11 | 0 | BD 013984 | 1 | 9842.75 | 10306.68 | 463.93 | 1000 | 0 | 463930 | 470281.7667 | Ramna | BB Aveneu 33/11 KV S/S | 423970.1788
17 | Nearest O/H | 11 | 0 | BD 013997 | 1 | 2274.44 | 2390.76 | 116.32 | 1000 | 0 | 116320 | 117912.5625 | Ramna | BB Aveneu 33/11 KV S/S | 115595.8875
18 | Natab Bhaban | 11 | 0 | BD 014000 | 1 | 4442.04 | 4625.24 | 183.2 | 1000 | 0 | 183200 | 185708.2311 | Ramna | BB Aveneu 33/11 KV S/S | 177165.0302
19 | Spare | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0
20 | Awami League Party Office | 11 | 0 | BD 013956 | 1 | 1395.25 | 1404.54 | 9.29 | 1000 | 0 | 9290 | 9417.1914 | Ramna | BB Aveneu 33/11 KV S/S | 9250.1106
21 | Khaddar Bazar | 11 | 0 | BD 014012 | 1 | 8928.66 | 9317.61 | 388.95 | 1000 | 0 | 388950 | 394275.1992 | Ramna | BB Aveneu 33/11 KV S/S | 392631.6173
22 | Bangobondu National Stidium | 11 | 0 | BD 014008 | 1 | 5862.17 | 6146.93 | 284.76 | 1000 | 0 | 284760 | 288658.7112 | Ramna | BB Aveneu 33/11 KV S/S | 290128.194
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4418 | 1 | 1124.63 | 1124.63 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 1718.8942
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 41.9 | 41.9 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 387.2849
0 | 11 KV Ring Road Feeder | 11 | 0 | 77816675 | 1 | 41632.55 | 41775.56 | 143.01 | 8000 | 0 | 1144080 | 1172682 | Adabor | Kallyanpur 33/11KV S/S | 1124384
0 | 11 KV Gano Bhavan RMU | 11 | 0 | DHK14997 | 1 | 995.68 | 995.71 | 0.03 | 40000 | 0 | 1200 | 1230 | Shere b.nagar | Kallyanpur 33/11KV S/S | 1230
0 | 11 KV Adabor O/H | 11 | 0 | DHK14957 | 1 | 4319.26 | 4371.7 | 52.44 | 40000 | 0 | 2097600 | 2150040 | Adabor | Kallyanpur 33/11KV S/S | 2995460
0 | 11 KV Goidertek (DPDC) | 11 | 0 | DHK14996 | 1 | 9341.2 | 9355.62 | 14.42 | 40000 | 0 | 576800 | 591220 | Adabor | Kallyanpur 33/11KV S/S | 558420
0 | 11 KV Beribandh Feeder. | 11 | 0 | DHK14960 | 1 | 9633.08 | 9640.43 | 7.35 | 40000 | 0 | 294000 | 301350 | Adabor | Kallyanpur 33/11KV S/S | 184500
0 | 11 KV Sewarage Pump | 11 | 0 | DHK14959 | 1 | 1991.3 | 2054.75 | 63.45 | 40000 | 0 | 2538000 | 2601450 | Adabor | Kallyanpur 33/11KV S/S | 535870
0 | 11 KV Technical School (DPDC) | 11 | 0 | DHK15019 | 1 | 8076.21 | 8133.47 | 57.26 | 40000 | 0 | 2290400 | 2347660 | Adabor | Kallyanpur 33/11KV S/S | 2184890
0 | 11 KV Mansurabad | 11 | 0 | 77816681 | 1 | 51326.05 | 51616.27 | 290.22 | 8000 | 0 | 2321760 | 2379804 | Adabor | Kallyanpur 33/11KV S/S | 2220888
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40402.7 | 40404.3 | 1.6 | 1000 | 0 | 1600 | 1691.4448 | Moghbazar | Moghbazar 33/11KV S/S | 1119.369
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 79796.2 | 80555.5 | 759.3 | 1000 | 0 | 759300 | 802696.2793 | Tejgaon | Moghbazar 33/11KV S/S | 1023306.7911
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 1589911.0287
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 118798.7 | 119107.7 | 309 | 1000 | 0 | 309000 | 326660.2796 | Tejgaon | Moghbazar 33/11KV S/S | 342221.6327
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 115816.3 | 117632.1 | 1815.8 | 1000 | 0 | 1815800 | 1919578.4326 | Kakrail | Moghbazar 33/11KV S/S | 1819483.4353
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 120528.2 | 122850.8 | 2322.6 | 1000 | 0 | 2322600 | 2455343.5773 | Moghbazar | Moghbazar 33/11KV S/S | 1989016.959
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 141604.5 | 142744.5 | 1140 | 1000 | 0 | 1140000 | 1205154.4296 | Tejgaon | Moghbazar 33/11KV S/S | 1055666.7314
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8294.9 | 8423.8 | 128.9 | 1000 | 0 | 128900 | 136267.0228 | Tejgaon | Moghbazar 33/11KV S/S | 122011.2214
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9327.8 | 9488.7 | 160.9 | 1000 | 0 | 160900 | 170095.919 | Tejgaon | Moghbazar 33/11KV S/S | 154167.6401
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 118443.2 | 120465.9 | 2022.7 | 1000 | 0 | 2022700 | 2138303.3901 | Kakrail | Moghbazar 33/11KV S/S | 1962152.1029
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 81467.2 | 82976.9 | 1509.7 | 1000 | 0 | 1509700 | 1595983.8968 | Tejgaon | Moghbazar 33/11KV S/S | 78254.0694
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 171354 | 172255.3 | 901.3 | 1000 | 0 | 901300 | 952812.0065 | Tejgaon | Moghbazar 33/11KV S/S | 1869447.9972
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 122407.2 | 122785.5 | 378.3 | 1000 | 0 | 378300 | 399920.9831 | Moghbazar | Moghbazar 33/11KV S/S | 690345.3929
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 111507.7 | 112406.9 | 899.2 | 1000 | 0 | 899200 | 950591.9851 | Kakrail | Moghbazar 33/11KV S/S | 944645.6784
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43325.7 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Moghbazar 33/11KV S/S | 323294.1205
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 | 13055099.6465 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0
1 | 11 kV TCB Feeder | 11 | T-4 | 0 | 1 | 33653.6 | 34661.4 | 1007.8 | 1000 | 0 | 1007800 | 1058026.2525 | Kakrail | Moghbazar 33/11KV S/S | 587067.814
2 | 11 kV Tejgaon SS-2 | 11 | T-4 | 0 | 1 | 27179.6 | 28639.4 | 1459.8 | 1000 | 0 | 1459800 | 1532552.8114 | Tejgaon | Moghbazar 33/11KV S/S | 1481122.0985
3 | Holy Day Inn | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 497820 | 522630.1141 | Tejgaon | Moghbazar 33/11KV S/S | 493817.3233
4 | Polly Bhabon-2 | 11 | T-4 | 0 | 1 | 18301.8 | 18322 | 20.2 | 1000 | Consumer meter damaged, 12 months average | 28632 | 30058.9479 | Kakrail | Moghbazar 33/11KV S/S | 29444.1053
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 | 0 | 1 | 11538.8 | 13294.2 | 1755.4 | 1000 | 0 | 1755400 | 1842884.7823 | Kakrail | Moghbazar 33/11KV S/S | 1860061.7445
6 | 11 kV Tejturibazar | 11 | T-4 | 0 | 1 | 129174.3 | 129914.1 | 739.8 | 1000 | 0 | 739800 | 776669.7972 | Kakrail | Moghbazar 33/11KV S/S | 731592.6735
7 | Songsad | 11 | T-4 | 0 | 1 | 1949 | 2467.7 | 518.7 | 1000 | 0 | 518700 | 544550.7215 | Shere b.nagar | Moghbazar 33/11KV S/S | 126381.9385
0 | Chennel 24 | 11 | T-4 | 0 | 1 | 7307.13 | 7308.75 | 1.62 | 1000 | 0 | 1620 | 1700.7368 | Moghbazar | Moghbazar 33/11KV S/S | 1164.858
8 | Sonargaon | 11 | T-4 | 0 | 1 | 38114.9 | 38919 | 804.1 | 1000 | 0 | 804100 | 844174.3497 | Kakrail | Moghbazar 33/11KV S/S | 839625.5215
0 | AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 7215.9345
0 | AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 7153248.5134 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 109708 | 133254 | 23546 | 60 | 0 | 1412760 | 1413099.3422 | Kakrail | T&T 33/11 KV | 1314936.3633
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 374779 | 399215 | 24436 | 60 | 0 | 1466160 | 1466512.1688 | Kakrail | T&T 33/11 KV | 1363050.3594
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 931981 | 938252 | 6271 | 60 | 0 | 376260 | 376350.3769 | Moghbazar | T&T 33/11 KV | 416269.8468
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1912434 | 1927455 | 15021 | 60 | 0 | 901260 | 901476.4809 | Moghbazar | T&T 33/11 KV | 862940.0791
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 532.55 | 561.01 | 28.46 | 60000 | 0 | 1707600 | 1708010.1623 | Moghbazar | T&T 33/11 KV | 1630130.9123
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 864753 | 874964 | 10211 | 60 | 0 | 612660 | 612807.1598 | Kakrail | T&T 33/11 KV | 591251.5937
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 434155 | 452115 | 17960 | 60 | 0 | 1077600 | 1077858.8375 | Moghbazar | T&T 33/11 KV | 1046359.7284
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 642051 | 669487 | 27436 | 60 | 0 | 1646160 | 1646555.4045 | Khilgaon | T&T 33/11 KV | 1662984.8723
4 | 11 kv Sherebangla | 11 | 0 | DHK60915 | 1 | 645233 | 668842 | 23609 | 60 | 0 | 1416540 | 1416880.2502 | Moghbazar | T&T 33/11 KV | 1438632.4204
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 297424 | 308967 | 11543 | 60 | 0 | 692580 | 692746.3564 | Moghbazar | T&T 33/11 KV | 708065.6738
6 | Auxiliary | 0 | Export | U0004461 | 1 | 7968.46 | 8028.17 | 59.71 | 60 | 0 | 3582.6 | 3583.4605 | Moghbazar | T&T 33/11 KV | 3045.4245
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1118237.4 | 1138226.0536 | Moghbazar | Ullon local 33/11KV S/S | 978294.9507
2 | Ullon | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1589074.2 | 1617479.1288 | Moghbazar | Ullon local 33/11KV S/S | 1406298.9916
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1647928.8 | 1677385.7633 | Moghbazar | Ullon local 33/11KV S/S | 1345155.5572
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1294801.2 | 1317945.9568 | Moghbazar | Ullon local 33/11KV S/S | 1100581.8195
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1530219.6 | 1557572.4944 | Moghbazar | Ullon local 33/11KV S/S | 1345155.5572
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1353655.8 | 1377852.5912 | Moghbazar | Ullon local 33/11KV S/S | 1222868.6883
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0
4 | AT-1 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0
5 | AT-2 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 6677.95 | 8495.5256 | 1817.5756 | 1000 | 0 | 1817575.6 | 1887459.924 | Mugdapara | Madarteck 33/11KV S/S | 1753548.1446
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 95560.9 | 97494.4 | 1933.5 | 1000 | 0 | 1933500 | 2007841.5243 | Mugdapara | Madarteck 33/11KV S/S | 1858521.5132
3 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 5644.71 | 7021.7968 | 1377.0868 | 1000 | 0 | 1377086.8 | 1430034.683 | Mugdapara | Madarteck 33/11KV S/S | 1264456.5681
0 | Goran | 11 | 0 | X1390296 | 1 | 24684 | 26638.6 | 1954.6 | 1000 | 0 | 1954600 | 2029752.8023 | Bashabo | Madarteck 33/11KV S/S | 1851494.7743
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 6722.86 | 8205.6192 | 1482.7592 | 1000 | 0 | 1482759.2 | 1539770.102 | Mugdapara | Madarteck 33/11KV S/S | 2039169.8043
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 79376.5 | 79747.1 | 370.6 | 1000 | 0 | 370600 | 384849.2728 | Maniknagar | Madarteck 33/11KV S/S | 881499.2996
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 282.33 | 510.4637 | 228.1337 | 1000 | 0 | 228133.68 | 236905.237 | Mugdapara | Madarteck 33/11KV S/S | 209712.5124
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 1799.56 | 2474.7662 | 675.2062 | 1000 | 0 | 675206.2 | 701167.3368 | Mugdapara | Madarteck 33/11KV S/S | 331641.7074
2 | Mugdapara | 11 | 0 | X0854272 | 1 | 3507.9 | 3786.4 | 278.5 | 1000 | 0 | 278500 | 289208.1016 | Maniknagar | Madarteck 33/11KV S/S | 256934.2344
0 | Singapur | 11 | 0 | X1390302 (N) | 1 | 28808.4 | 31151.7 | 2343.3 | 1000 | 0 | 2343300 | 2433398.0056 | Banosree | Madarteck 33/11KV S/S | 2200082.1244
0 | Trimohony | 11 | 0 | X1390308 | 1 | 22519.4 | 24527.3 | 2007.9 | 1000 | 0 | 2007900 | 2085102.1446 | Banosree | Madarteck 33/11KV S/S | 1604947.893
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 8633.04 | 10561.687 | 1928.647 | 1000 | 0 | 1928647 | 2002801.9303 | Mugdapara | Madarteck 33/11KV S/S | 1839386.3794
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 3107.93 | 3952.1608 | 844.2308 | 1000 | 0 | 844230.8 | 876690.7972 | Mugdapara | Madarteck 33/11KV S/S | 596386.824
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 702966 | 712365 | 9399 | 200 | 0 | 1879800 | 1952076.8023 | Mugdapara | Madarteck 33/11KV S/S | 480873.3471
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 739373 | 746576 | 7203 | 200 | 0 | 1440600 | 1495989.9146 | Mugdapara | Madarteck 33/11KV S/S | 298789.1572
1 | Nakhal Para Feeder | 11 | 0 | DHK60950 | 1 | 176336.6 | 201859.3 | 25522.7 | 60 | 0 | 1531362 | 1545202.0376 | Tejgaon | Tejgoan 33/11KV S/S | 1536369.5556
2 | Badda-Meghna Feeder | 11 | 0 | DHK60979 | 1 | 876525.4 | 888283.6 | 11758.2 | 60 | 0 | 705492 | 711868.0468 | Tejgaon | Tejgoan 33/11KV S/S | 842649.7133
3 | Rasulbagh Feeder | 11 | 0 | DHK60948 | 1 | 931276.3 | 961752.1 | 30475.8 | 60 | 0 | 1828548 | 1845073.9247 | Tejgaon | Tejgoan 33/11KV S/S | 1902151.6741
4 | Lukas | 11 | 0 | 8A021100948-02 | 1 | 62085526 | 64421346 | 2335820 | 1 | 0 | 2335820 | 2356930.5125 | Tejgaon | Tejgoan 33/11KV S/S | 2345545.782
5 | PWD RMU | 11 | 0 | 0 | 1 | 650851.8 | 652660.7 | 1808.9 | 1 | 0 | 1808.9 | 1825.2484 | Tejgaon | Tejgoan 33/11KV S/S | 1757.0539
1 | Civil Aviation Feeder | 11 | 0 | DHK60977 | 1 | 744587.4 | 791561.7 | 46974.3 | 60 | 0 | 2818458 | 2843930.4649 | Tejgaon | Tejgoan 33/11KV S/S | 2795399.6317
2 | Ahasanullah Eng. | 11 | 0 | DHK60867 | 1 | 848834.7 | 859374.2 | 10539.5 | 60 | 0 | 632370 | 638085.1899 | Tejgaon | Tejgoan 33/11KV S/S | 673101.4258
3 | New GMG Feeder | 11 | 0 | DHK61106 | 1 | 970375 | 1007264.2 | 36889.2 | 60 | 0 | 2213352 | 2233355.6797 | Tejgaon | Tejgoan 33/11KV S/S | 2281871.6214
4 | Shikajo | 11 | 0 | HA021101036-02 | 1 | 61878821 | 62704679 | 825858 | 1 | 0 | 825858 | 833321.8823 | Tejgaon | Tejgoan 33/11KV S/S | 756034.1648
5 | Kahinur | 11 | 0 | 0 | 1 | 475997.5 | 496661.5 | 20664 | 60 | 0 | 1239840 | 1251045.3402 | Tejgaon | Tejgoan 33/11KV S/S | 1294083.2246
6 | Link road | 11 | 0 | 8A021100380-02 | 1 | 63506551 | 63919556 | 413005 | 1 | 0 | 413005 | 416737.628 | Tejgaon | Tejgoan 33/11KV S/S | 435428.3198
7 | Shanta | 11 | 0 | 0 | 1 | 289500.3 | 299552.9 | 10052.6 | 60 | 0 | 603156 | 608607.1616 | Tejgaon | Tejgoan 33/11KV S/S | 630895.3248
1 | Karnafuly Feeder | 11 | 0 | DHK61084 | 1 | 33015.5 | 33696.3 | 680.8 | 1000 | 0 | 680800 | 686952.8872 | Tejgaon | Tejgoan 33/11KV S/S | 738300.0364
2 | Butex | 11 | 0 | 0 | 1 | 803.1 | 892.3 | 89.2 | 1000 | 0 | 89200 | 90006.1656 | Tejgaon | Tejgoan 33/11KV S/S | 91610.1416
3 | OriON LAB | 11 | 0 | 0 | 1 | 7919755 | 8007550 | 87795 | 1 | 0 | 87795 | 88588.4676 | Tejgaon | Tejgoan 33/11KV S/S | 248723.2522
4 | Nina kabbo | 11 | 0 | 201101025-2 | 1 | 16283296 | 16563888 | 280592 | 1 | 0 | 280592 | 283127.915 | Tejgaon | Tejgoan 33/11KV S/S | 99489.3009
5 | Satrong | 11 | 0 | HA021100515-2 | 1 | 88090387 | 89639487 | 1549100 | 1 | 0 | 1549100 | 1563100.3489 | Tejgaon | Tejgoan 33/11KV S/S | 1367977.887
6 | South East RMU | 11 | 0 | 0 | 1 | 464.1 | 601.9 | 137.8 | 1000 | 0 | 137800 | 139045.3993 | Tejgaon | Tejgoan 33/11KV S/S | 149070.967
7 | Rangs Bhaban | 11 | 0 | HA021100939-2 | 1 | 121073 | 270974 | 149901 | 1 | 0 | 149901 | 151255.7649 | Tejgaon | Tejgoan 33/11KV S/S | 161670.1139
8 | Babli | 11 | 0 | 0 | 1 | 51912.4 | 54005.3 | 2092.9 | 1000 | 0 | 2092900 | 2111815.0669 | Tejgaon | Tejgoan 33/11KV S/S | 1541422.4274
0 | SPL | 11 | 0 | 0 | 1 | 3055.8 | 3461.1 | 405.3 | 1000 | 0 | 405300 | 408962.9923 | Tejgaon | Tejgoan 33/11KV S/S | 372268.4438
9 | DNCC Hospital | 11 | 0 | 0 | 1 | 12507.9 | 13491.4 | 983.5 | 1000 | 0 | 983500 | 992388.6083 | Tejgaon | Tejgoan 33/11KV S/S | 965076.0343
0 | 11/.415 kv Local transformer | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 6000 | 6054.2264 | Tejgaon | Tejgoan 33/11KV S/S | 6134.6077
1 | Gonobhaban | 11 | 0 | DHKC9332 | 1 | 65439.13 | 69014.8 | 3575.67 | 60 | 0 | 214540.2 | 216875.2359 | Shere b.nagar | Asad Gate 33/11 KV S/S | 216836.1836
2 | Rapa Plaza Feeder | 11 | 0 | DHKC9339 | 1 | 36328.06 | 56103.84 | 19775.78 | 60 | 0 | 1186546.8 | 1199461.0668 | Dhanmondi | Asad Gate 33/11 KV S/S | 1170856.0696
3 | Shukrabad/ South Plaza | 11 | 0 | DHKC9324 | 1 | 77512.2 | 95989.52 | 18477.32 | 60 | 0 | 1108639.2 | 1120705.5276 | Shere b.nagar | Asad Gate 33/11 KV S/S | 1130327.1946
4 | Wasa O/H | 11 | 0 | DHKC9333 | 1 | 43612.07 | 78543.28 | 34931.21 | 60 | 0 | 2095872.6 | 2118683.8855 | Satmasjid | Asad Gate 33/11 KV S/S | 1049087.4751
5 | Bangabandhu Memorial Museum | 11 | 0 | DHKC9334 | 1 | 14682.59 | 15026.42 | 343.83 | 60 | 0 | 20629.8 | 20854.3329 | Dhanmondi | Asad Gate 33/11 KV S/S | 20897.995
6 | Iqbal Road O/H | 11 | 0 | DHKC9330 | 1 | 16028.77 | 43449.53 | 27420.76 | 60 | 0 | 1645245.6 | 1663152.3025 | Shyamoli | Asad Gate 33/11 KV S/S | 1601413.1174
7 | Town Hall | 11 | 0 | DHKC9351 | 1 | 29046.8 | 64380.78 | 35333.98 | 60 | 0 | 2120038.8 | 2143113.1083 | Shyamoli | Asad Gate 33/11 KV S/S | 2338946.2013
8 | Post Office | 11 | 0 | DHKC9331 | 1 | 14408.51 | 39135.17 | 24726.66 | 60 | 0 | 1483599.6 | 1499746.9623 | Shyamoli | Asad Gate 33/11 KV S/S | 1492441.2314
9 | Shangshad Bhaban | 11 | 0 | DHKC9370 | 1 | 98850.73 | 106671.66 | 7820.93 | 60 | 0 | 469255.8 | 474363.1372 | Shere b.nagar | Asad Gate 33/11 KV S/S | 422562.5169
10 | Jakir Hossain Road | 11 | 0 | DHKC9373 | 1 | 52169.33 | 81724.89 | 29555.56 | 60 | 0 | 1773333.6 | 1792634.4006 | Satmasjid | Asad Gate 33/11 KV S/S | 1277863.2905
11 | New Colony O/H Feeder | 11 | 0 | DHKC9369 | 1 | 69251.43 | 69251.43 | 0 | 60 | 0 | 0 | 0 | Satmasjid | Asad Gate 33/11 KV S/S | 1328527.8719
12 | Aurangzeb Feeder | 11 | 0 | DHKC9321 | 1 | 12056.46 | 42513.02 | 30456.56 | 60 | 0 | 1827393.6 | 1847282.7847 | Shyamoli | Asad Gate 33/11 KV S/S | 2012075.4293
13 | Asadgate Local Feeder | 11 | 0 | DHKC9338 | 1 | 93460.16 | 132726.29 | 39266.13 | 60 | 0 | 2355967.8 | 2381609.9379 | Satmasjid | Asad Gate 33/11 KV S/S | 1832840.2298
14 | Sonarbangla Road | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 0
15 | Humayun Road | 11 | 0 | DHKC9366 | 1 | 42688.17 | 47034.27 | 4346.1 | 60 | 0 | 260766 | 263604.1533 | Shyamoli | Asad Gate 33/11 KV S/S | 1670349.266
16 | NHA | 11 | 0 | DHKC9374 | 1 | 52311.92 | 52748.02 | 436.1 | 60 | 0 | 26166 | 26450.7883 | Shyamoli | Asad Gate 33/11 KV S/S | 221861.5773
17 | Auxiliary transformer | 0.415 | 0 | 0 | 1 | 626701 | 633994 | 7293 | 1 | 0 | 7293 | 7372.3763 | Satmasjid | Asad Gate 33/11 KV S/S | 6148.5505
1 | Angur Jora | 11 | 0 | 141 | 1 | 1717760 | 3861980 | 2144220 | 1 | Grid Provided the Reading of 00:00 hour of 30.06.23 instead of 01.07.23 | 2144220 | 2168323.5267 | Banosree | Banasree 33/11 SS | 1879685.8324
2 | Block F-G Avenue | 11 | 0 | 68 | 1 | 2777480 | 5519540 | 2742060 | 1 | 0 | 2742060 | 2772883.9436 | Banosree | Banasree 33/11 SS | 2653782.5782
3 | Banasree Main Road(Monpura) | 11 | 0 | 168 | 1 | 2694560 | 4446260 | 1751700 | 1 | 0 | 1751700 | 1771391.1453 | Banosree | Banasree 33/11 SS | 1640446.1666
4 | Baitul Kuddus | 11 | 0 | 62 | 1 | 5086120 | 7309220 | 2223100 | 1 | 0 | 2223100 | 2248090.2296 | Banosree | Banasree 33/11 SS | 2090165.4312
5 | Ideal | 11 | 0 | 0 | 1 | 6710680 | 7487660 | 776980 | 1 | 0 | 776980 | 785714.1589 | Banosree | Banasree 33/11 SS | 730886.4987
6 | Central Mosque | 11 | 0 | 46 | 1 | 5624400 | 7813780 | 2189380 | 1 | #REF! | 2189380 | 2213991.1776 | Banosree | Banasree 33/11 SS | 2027033.5767
7 | Larive | 11 | 0 | 47 | 1 | 7265440 | 8407420 | 1141980 | 1 | 0 | 1141980 | 1154817.1834 | Banosree | Banasree 33/11 SS | 1075325.8802
8 | Bank Colony | 11 | 0 | 0 | 1 | 3178720 | 3914160 | 735440 | 1 | 0 | 735440 | 743707.201 | Khilgaon | Banasree 33/11 SS | 684269.1356
9 | Salambagh | 11 | 0 | 0 | 1 | 1440440 | 2367500 | 927060 | 1 | 0 | 927060 | 937481.2326 | Khilgaon | Banasree 33/11 SS | 1234217.735
10 | Titas Road | 11 | 0 | 0 | 1 | 1526120 | 1963420 | 437300 | 1 | 0 | 437300 | 442215.7606 | Khilgaon | Banasree 33/11 SS | 461564.0031
11 | AT-1 | 0.415 | 0 | 7734 | 1 | 3113.136 | 3257.088 | 143.952 | 1 | 0 | 143.952 | 145.5702 | Banosree | Banasree 33/11 SS | 0
12 | AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 0
1 | Meradia | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estimated | 0 | 0 | Banosree | Goran 33/11KV S/S | 0
2 | Shipahibagh | 11 | 0 | HA-021001030-02 | 1 | 35007828 | 36289191 | 1281363 | 1 | 0 | 1281363 | 1292900.8718 | Bashabo | Goran 33/11KV S/S | 1411235.5236
3 | Farazi Hospital | 11 | 0 | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0
4 | West Bansree | 11 | 0 | New Meter | 1 | 89182268 | 91131594 | 1949326 | 1 | 0 | 1949326 | 1966878.4605 | Banosree | Goran 33/11KV S/S | 1837316.4777
5 | Model School(Nearest) | 11 | 0 | HA-030701099-03 | 1 | 12612480 | 15066081 | 2453601 | 1 | 0 | 2453601 | 2475694.1412 | Banosree | Goran 33/11KV S/S | 2316464.2537
6 | Bhuiyan Para | 11 | 0 | HA-021100508-02 | 1 | 50569666 | 53101375 | 2531709 | 1 | 0 | 2531709 | 2554505.4549 | Banosree | Goran 33/11KV S/S | 2408712.741
7 | Bonobithi (Ideal) School | 11 | 0 | HA-021100879-02 | 1 | 12579186 | 14133451 | 1554265 | 1 | 0 | 1554265 | 1568260.1835 | Banosree | Goran 33/11KV S/S | 1428642.8767
8 | AT-01 | 0.415 | 0 | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0
9 | AT-02 | 0.415 | 0 | 3043146 | 1 | 4637.2 | 4704.4 | 67.2 | 80 | 0 | 5376 | 5424.4075 | Banosree | Goran 33/11KV S/S | 4669.3803
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1412510.4 | 1418643.1678 | Dhanmondi | Lalmatia 33/11KV S/S | 1399733.2864
2 | Bangabobondhu museum | 11 | Export | 0 | 1 | 627449 | 627449 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 76132438 | 78185685 | 2053247 | 1 | 0 | 2053247 | 2062161.6863 | Dhanmondi | Lalmatia 33/11KV S/S | 2160918.3029
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 96836903 | 99151250 | 2314347 | 1 | 0 | 2314347 | 2324395.3174 | Dhanmondi | Lalmatia 33/11KV S/S | 2181617.4346
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25242.7 | 25444.9 | 202.2 | 3333.33 | 0 | 673999.326 | 676925.663 | Dhanmondi | Lalmatia 33/11KV S/S | 643438.6457
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 68865.4 | 69354.4 | 489 | 3333.33 | 0 | 1629998.37 | 1637075.4163 | Dhanmondi | Lalmatia 33/11KV S/S | 1478674.7103
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 76765.7 | 77227.8 | 462.1 | 3333.33 | 0 | 1540331.793 | 1547019.5294 | Dhanmondi | Lalmatia 33/11KV S/S | 1459995.3095
0 | Road 25 | 11 | Export | 0 | 1 | 69416.1 | 69810.6 | 394.5 | 3333.3 | 0 | 1314986.85 | 1320696.1949 | Dhanmondi | Lalmatia 33/11KV S/S | 1108412.3257
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37575.5 | 37703.6 | 128.1 | 3333.33 | 0 | 426999.573 | 428853.4986 | Dhanmondi | Lalmatia 33/11KV S/S | 403274.921
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 57291365 | 59045605 | 1754240 | 1 | 0 | 1754240 | 1761856.4725 | Dhanmondi | Lalmatia 33/11KV S/S | 924073.8841
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 64955658 | 67161693 | 2206035 | 1 | 0 | 2206035 | 2215613.0537 | Dhanmondi | Lalmatia 33/11KV S/S | 2070071.1797
1 | Lab aid/local RMU | 11 | 0 | 3C65883 | 1 | 48899 | 54004 | 5105 | 300 | 0 | 1531500 | 1536617.643 | Paribag | Green Road 33/11KV S/S | 1422394.5672
2 | Green View | 11 | 0 | DHK000151 | 1 | 66511.6 | 66871.1 | 359.5 | 3333.33 | 0 | 1198332.135 | 1202336.4681 | Paribag | Green Road 33/11KV S/S | 1154869.3417
3 | Central Road | 11 | 0 | 65943 | 1 | 9730 | 15582 | 5852 | 300 | 0 | 1755600 | 1761466.4931 | Paribag | Green Road 33/11KV S/S | 1692090.5953
4 | New Market | 11 | 0 | DHK000194 | 1 | 45899.3 | 46255.4 | 356.1 | 3333.33 | 0 | 1186998.813 | 1190965.2748 | Jigatola | Green Road 33/11KV S/S | 1011316.673
5 | DPH Feeder | 11 | 0 | HA-021100459 | 1 | 41350 | 41476.6 | 126.6 | 1 | 20 | 235418.4 | 236205.0715 | Paribag | Green Road 33/11KV S/S | 247670.0176
6 | Dhanmondi Rd 4(md Banglo | 11 | 0 | 6604464 | 1 | 4450.58 | 4476.72 | 26.14 | 60000 | 0 | 1568400 | 1573640.9477 | Jigatola | Green Road 33/11KV S/S | 1319464.1465
1 | Green Road East | 11 | 0 | HA-021101050 | 1 | 92229088 | 93757224 | 1528136 | 1 | 0 | 1528136 | 1533242.4019 | Paribag | Green Road 33/11KV S/S | 1471624.0188
2 | North Road | 11 | 0 | HA-021100884 | 1 | 76809718 | 78525314 | 1715596 | 1 | 0 | 1715596 | 1721328.8161 | Paribag | Green Road 33/11KV S/S | 1634915.8518
3 | Green road SS | 11 | 0 | DHK00135 | 1 | 16023524 | 17244056 | 1220532 | 1 | 0 | 1220532 | 1224610.5159 | Paribag | Green Road 33/11KV S/S | 1315498.6273
4 | Plane Moszid | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 80 | 941673.6 | 944820.2858 | Paribag | Green Road 33/11KV S/S | 990680.0705
5 | Malancha | 11 | 0 | HA-021100953 | 1 | 30602490 | 31976092 | 1373602 | 1 | 0 | 1373602 | 1378192.0129 | Paribag | Green Road 33/11KV S/S | 1148505.9825
0 | AT -1 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5016.7079 | Paribag | Green Road 33/11KV S/S | 5090.5253
1 | North Dhanmondi | 11 | 0 | BD 014039 | 1 | 21702.59 | 21956.7 | 254.11 | 2000 | 0 | 508220 | 504079.3978 | Paribag | Green Road Dormatory 33/11 SS | 452285.2955
2 | Lake circus | 11 | 0 | BD 014047 | 1 | 33605.68 | 34637.48 | 1031.8 | 2000 | 0 | 2063600 | 2046787.3073 | Paribag | Green Road Dormatory 33/11 SS | 1887308.9386
3 | Bashir Uddin | 11 | 0 | BD 014037 | 1 | 13668.5 | 14070.93 | 402.43 | 2000 | 0 | 804860 | 798302.5936 | Paribag | Green Road Dormatory 33/11 SS | 740604.9957
4 | Raza Bazar | 11 | 0 | BD 013939 | 1 | 19945.29 | 20615.43 | 670.14 | 2000 | 0 | 1340280 | 1329360.3858 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1277085.001
5 | Rasel Squar | 11 | 0 | BD 013970 | 1 | 30409.89 | 31411.16 | 1001.27 | 2000 | 0 | 2002540 | 1986224.7792 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1860400.7233
6 | Bow Bazar | 11 | 0 | BD 013967 | 1 | 22875.2 | 23561.5 | 686.3 | 2000 | 0 | 1372600 | 1361417.0663 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1195690.6937
7 | BRB Hospital | 11 | 0 | BD 014003 | 1 | 12053.73 | 12424.41 | 370.68 | 2000 | 0 | 741360 | 735319.9448 | Shere b.nagar | Green Road Dormatory 33/11 SS | 733624.2823
8 | Green Road North | 11 | 0 | BD 013969 | 1 | 14142.63 | 14760.23 | 617.6 | 2000 | 0 | 1235200 | 1225136.5003 | Paribag | Green Road Dormatory 33/11 SS | 1163648.4072
1 | Water Bhaban | 11 | 0 | BD 014004 | 1 | 4730.78 | 4898.2 | 167.42 | 2000 | 0 | 334840 | 332111.9703 | Shere b.nagar | Green Road Dormatory 33/11 SS | 301428.8307
2 | Alamin Road | 11 | 0 | BD 014006 | 1 | 17886.83 | 18211.68 | 324.85 | 2000 | 0 | 649700 | 644406.723 | Paribag | Green Road Dormatory 33/11 SS | 578607.7993
3 | Katal Bagan | 11 | 0 | 0 | 1 | 5394.19 | 6635.26 | 1241.07 | 2000 | 0 | 2482140 | 2461917.3517 | Paribag | Green Road Dormatory 33/11 SS | 1880307.9323
4 | Eastern Pantho chaya | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 0
5 | Kalabagan | 11 | 0 | BD 014005 | 1 | 5394.19 | 5575.77 | 181.58 | 2000 | 0 | 363160 | 360201.2398 | Paribag | Green Road Dormatory 33/11 SS | 320179.3518
6 | Univer Hospital | 11 | 0 | BD 013963 | 1 | 606.64 | 745.38 | 138.74 | 2000 | 0 | 277480 | 275219.2974 | Paribag | Green Road Dormatory 33/11 SS | 258266.1053
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 | 0 | BD 013971 | 1 | 9267.96 | 9523.65 | 255.69 | 2000 | 0 | 511380 | 507213.6524 | Paribag | Green Road Dormatory 33/11 SS | 520651.6433
1 | Matir Masjid | 11 | 0 | DHK00170 | 1 | 17730 | 20154.5 | 2424.5 | 888.8889 | 0 | 2155111.1111 | 2177028.2382 | Khilgaon | Taltola 33/11KV S/S | 2023352.6919
2 | Hajipara | 11 | 0 | DHK-00108 | 1 | 1596.3 | 2631.3 | 1035 | 2222.2222 | 0 | 2300000 | 2323390.6234 | Khilgaon | Taltola 33/11KV S/S | 1505682.5673
3 | Nearest Feeder | 11 | 0 | DHK-00106 | 1 | 90788.1 | 90788.1 | 0 | 2222.222 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 102528.7436
4 | Reazbagh | 11 | 0 | DHK-00109 | 1 | 94301.5 | 95125.7 | 824.2 | 2222.222 | 0 | 1831555.3724 | 1850181.9906 | Khilgaon | Taltola 33/11KV S/S | 1693614.7124
5 | Chowdhury Para | 11 | 0 | DHK-00107 | 1 | 51884.4 | 52175.6 | 291.2 | 2222.222 | 0 | 647111.0464 | 653692.0598 | Khilgaon | Taltola 33/11KV S/S | 575139.5465
6 | Model Colleg | 11 | 0 | 9122392 | 1 | 2456.34 | 2474.25 | 17.91 | 40000 | 0 | 716400 | 723685.6707 | Khilgaon | Taltola 33/11KV S/S | 1038453.9207
1 | East Rampura | 11 | 0 | DHK-00181 | 1 | 97163 | 97687.4 | 524.4 | 2222.222 | 0 | 1165333.2168 | 1177184.4648 | Khilgaon | Taltola 33/11KV S/S | 1381135.5698
2 | Adarshabagh | 11 | 0 | DHK-00090 | 1 | 47488.7 | 48490.9 | 1002.2 | 2222.222 | 0 | 2227110.8884 | 2249760.2414 | Bashabo | Taltola 33/11KV S/S | 2012766.0076
3 | Khailgaon Govt Colony | 11 | 0 | DHK00167 | 1 | 73598.82 | 74331.4 | 732.58 | 2222.222 | 0 | 1627955.3928 | 1644511.4325 | Khilgaon | Taltola 33/11KV S/S | 1548206.2687
4 | TV Road | 11 | 0 | 6604434 | 1 | 4998.51 | 5034.04 | 35.53 | 40000 | 0 | 1421200 | 1435653.3713 | Khilgaon | Taltola 33/11KV S/S | 1278251.1059
5 | Tilpa Para | 11 | 0 | 06604476 | 1 | 6526.36 | 6549.26 | 22.9 | 40000 | 0 | 916000 | 925315.57 | Bashabo | Taltola 33/11KV S/S | 631719.4629
1 | Navana | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0
7 | Shantipur | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 232625.2878
2 | AT-01 | 0.415 | 0 | 9187958 | 1 | 283.22 | 288.03 | 4.81 | 80 | 0 | 384.8 | 388.7134 | Bashabo | Taltola 33/11KV S/S | 5004.1149
3 | AT-02 | 0.415 | 0 | 9187959 | 1 | 0 | 123.08 | 123.08 | 10 | 0 | 1230.8 | 1243.317 | Bashabo | Taltola 33/11KV S/S | 0
1 | Sher-e-Banglanagar Local | 11 | 0 | DHK 66503 | 1 | 73849 | 76044 | 2195 | 60 | 0 | 131700 | 130259.0089 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 137740.1655
2 | Mirpur Road East | 11 | 0 | DHK 60961 | 1 | 805750 | 815519 | 9769 | 60 | 0 | 586140 | 579726.769 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 591320.8565
3 | Gonobhaban school | 11 | 0 | DHK 66492 | 1 | 519667 | 523059 | 3392 | 60 | 0 | 203520 | 201293.1928 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 178100.36
4 | Babor Road | 11 | 0 | DHK 66489 | 1 | 688132 | 727817 | 39685 | 60 | 0 | 2381100 | 2355047.2749 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 1531864.2685
5 | College Gate | 11 | 0 | DHK 66487 | 1 | 2552998 | 2587196 | 34198 | 60 | 0 | 2051880 | 2029429.4244 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 1693179.314
6 | Parade ground | 11 | 0 | DHK 66490 | 1 | 938217 | 938247 | 30 | 60 | 0 | 1800 | 1780.3054 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S
7 | Hospital RMU | 11 | 0 | DHK 66491 | 1 | 873509 | 882954 | 9445 | 60 | 0 | 566700 | 560499.4711 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 544171.0965
1 | Shamoly Square | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 0
2 | Gonobhaban RMU | 11 | 0 | DHK 60964 | 1 | 189395.3 | 191126.8 | 1731.5 | 60 | 0 | 103890 | 102753.2911 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 81921.1363
3 | Krishi University | 11 | 0 | DHK 60963 | 1 | 330598.6 | 340100.1 | 9501.5 | 60 | 0 | 570090 | 563852.3796 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 574020.0379
4 | NEC | 11 | 0 | DHK 86073 | 1 | 25.3 | 29.93 | 4.63 | 60000 | 0 | 277800 | 274760.4607 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 284784.5503
5 | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 323.21 | 342.41 | 19.2 | 60000 | 0 | 472320 | 467152.1267 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 453385.8053
5 | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 323.21 | 342.41 | 19.2 | 60000 | 0 | 679680 | 672243.3043 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 652433.232
6 | Netor | 11 | 0 | DHK 60962 | 1 | 92954.2 | 103402.9 | 10448.7 | 60 | 0 | 626922 | 620062.5542 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 596532.4766
7 | BICC | 11 | 0 | 0 | 1 | 26.67 | 29.93 | 3.26 | 60000 | 0 | 195600 | 193459.8492 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 69152.9813
8 | Auxiliary | 0.415 | 0 | 0 | 1 | 5090.45 | 5156.09 | 65.64 | 60 | 0 | 3938.4 | 3895.3081 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 5642.8833
1 | City Corporation | 11 | 0 | 93 | 1 | 38782904 | 39720584 | 937680 | 1 | 0 | 937680 | 951549.8845 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 660250.7383
2 | Bot tola | 11 | 0 | 0 | 1 | 49052840 | 51317676 | 2264836 | 1 | 0 | 2264836 | 2298336.7826 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 2240795.0697
3 | Jhilpar | 11 | 0 | 145 | 1 | 32593720 | 33590076 | 996356 | 1 | 0 | 996356 | 1011093.8025 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1160185.3486
4 | Central Bashaboo | 11 | 0 | 128 | 1 | 34044596 | 35782472 | 1737876 | 1 | 0 | 1737876 | 1763582.1465 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1733572.9987
5 | Kadamtala | 11 | 0 | 8 | 1.5 | 17533438 | 17980396 | 446958 | 1 | 0 | 670437 | 680353.9053 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1958904.8441
6 | Ansar VDP | 11 | 0 | 119 | 1 | 17300398 | 18412676 | 1112278 | 1 | 0 | 1112278 | 1128730.4864 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 727503.1317
7 | Mugda Hospital Express-01 | 11 | 0 | 0 | 1 | 5309707 | 5599066 | 289359 | 1 | 0 | 289359 | 293639.1125 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 272764.3875
8 | Boro Masjid | 11 | 0 | 7 | 1.22 | 45410408 | 46545848 | 1135440 | 1 | 0 | 1385236.8 | 1405726.812 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1342757.2732
1 | Anandodhara | 11 | 0 | 120 | 1 | 44960492 | 45910688 | 950196 | 1 | 0 | 950196 | 964251.0175 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 915566.0508
2 | Culvert | 11 | 0 | 117 | 1 | 34952276 | 36749792 | 1797516 | 1 | 0 | 1797516 | 1824104.3237 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1912589.1389
3 | Mugda Hospital Express-02 | 11 | 0 | 97 | 1 | 4845548 | 4845548 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0
4 | Jhor Pukur | 11 | 0 | 98 | 1 | 23101984 | 24721380 | 1619396 | 1 | 0 | 1619396 | 1643349.6255 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1429146.8866
5 | T&T | 11 | 0 | 99 | 1 | 22071346 | 22630184 | 558838 | 1 | 0 | 558838 | 567104.166 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 852556.8368
6 | Haider Ali | 11 | 0 | 9 | 1 | 62774928 | 64773440 | 1998512 | 1 | 0 | 1998512 | 2028073.3969 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 1439434.5953
0 | 11kv Tilpapara | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 2150000 | 2181802.1625 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 2151612.2434
7 | AT-01 | 11 | 0 | 0 | 1 | 2782 | 2875 | 93 | 1 | 0 | 93 | 94.3756 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0
8 | AT-02 | 11 | 0 | 0 | 1 | 17 | 17 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 8.4563
1 | Shantinagar s/s-1 | 11 | 0 | DHK60932 | 1 | 232427 | 277582 | 45155 | 60 | 0 | 2709300 | 2755360.6206 | Rajarbag | Khillgaon 33/11KV S/S | 2616486.0095
2 | Gulbagh | 11 | 0 | DHK60934 | 1 | 111867 | 117195 | 5328 | 60 | 0 | 319680 | 325114.8574 | Rajarbag | Khillgaon 33/11KV S/S | 314880.9114
3 | Rampura BTV | 11 | 0 | DHK60933 | 1 | 14053 | 14073 | 20 | 60 | 0 | 1200 | 1220.4011 | Khilgaon | Khillgaon 33/11KV S/S | 241.3343
4 | West Shantibag | 11 | 0 | DHK60926 | 1 | 490108 | 505382 | 15274 | 60 | 0 | 916440 | 932020.3326 | Rajarbag | Khillgaon 33/11KV S/S | 912726.2746
1 | East Malibagh | 11 | 0 | DHK60929 | 1 | 537667 | 560235 | 22568 | 60 | 0 | 1354080 | 1377100.6198 | Rajarbag | Khillgaon 33/11KV S/S | 1289630.0978
2 | Police Line | 11 | 0 | DHK60930 | 1 | 545249 | 555020 | 9771 | 60 | 0 | 586260 | 596226.9654 | Rajarbag | Khillgaon 33/11KV S/S | 576125.2774
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 | 0 | DHK61017 | 1 | 187933 | 190385 | 2452 | 60 | 0 | 147120 | 149621.1769 | Rajarbag | Khillgaon 33/11KV S/S | 146188.2445
4 | Benjir Bagan | 11 | 0 | DHK60985 | 1 | 157675 | 160865 | 3190 | 60 | 0 | 191400 | 194653.9781 | Rajarbag | Khillgaon 33/11KV S/S | 180699.0476
6 | AT-1 & AT-2 | 0.415 | 0 | ELIB 7374 | 1 | 1628.18 | 1864.68 | 236.5 | 60 | 0 | 14190 | 14431.2432 | Rajarbag | Khillgaon 33/11KV S/S | 0
1 | Spare | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 0
2 | Monipuripara west | 11 | 0 | BD013947 | 1 | 28604.46 | 29462.81 | 858.35 | 1000 | 0 | 858350 | 886112.5599 | Shere b.nagar | Monipuripara 33/11 KV S/S | 873090.4062
3 | Biggan College | 11 | 0 | BD013949 | 1 | 16491.07 | 17308.18 | 817.11 | 1000 | 0 | 817110 | 843538.6891 | Kakrail | Monipuripara 33/11 KV S/S | 853994.1863
4 | Green Road South | 11 | 0 | BD013948 | 1 | 26639.32 | 27673.13 | 1033.81 | 1000 | 0 | 1033810 | 1067247.656 | Shere b.nagar | Monipuripara 33/11 KV S/S | 986346.7996
5 | BARC Building O/H | 11 | 0 | BD014010 | 1 | 11567.27 | 12194.37 | 627.1 | 1000 | 0 | 627100 | 647382.9863 | Shere b.nagar | Monipuripara 33/11 KV S/S | 632910.7169
6 | Green Road North | 11 | 0 | BD014036 | 1 | 53150.66 | 55063.73 | 1913.07 | 1000 | 0 | 1913070 | 1974946.5311 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1871294.3358
7 | Chundrima Uddan | 11 | 0 | BD014035 | 1 | 26974.49 | 28003.9 | 1029.41 | 1000 | 0 | 1029410 | 1062705.342 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1015615.1889
8 | RMU-1 Feeder | 11 | 0 | BD013940 | 1 | 0 | 146.76 | 146.76 | 1000 | 0 | 146760 | 151506.8204 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0
1 | Spare-03 | 11 | 0 | BD013946 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0
2 | kawran Bazar North | 11 | 0 | BD013964 | 1 | 40112.39 | 40142.51 | 30.12 | 1000 | 0 | 30120 | 31094.2044 | Kakrail | Monipuripara 33/11 KV S/S | 0
3 | NAM Bhanan RMU | 11 | 0 | BD013950 | 1 | 13253.69 | 14281.17 | 1027.48 | 1000 | 0 | 1027480 | 1060712.9179 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1013545.3917
4 | Novo Theater | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0
5 | Monipuripara Nearest | 11 | 0 | BD013962 | 1 | 35872.57 | 36592.1 | 719.53 | 1000 | 0 | 719530 | 742802.5517 | Tejgaon | Monipuripara 33/11 KV S/S | 733061.8614
6 | Holy Cross | 11 | 0 | BD013965 | 1 | 33881.78 | 35046.94 | 1165.16 | 1000 | 0 | 1165160 | 1202846.0538 | Tejgaon | Monipuripara 33/11 KV S/S | 1126874.592
7 | Honda Goli | 11 | 0 | BD014011 | 1 | 11371.49 | 12339.97 | 968.48 | 1000 | 0 | 968480 | 999804.6158 | Tejgaon | Monipuripara 33/11 KV S/S | 953126.0337
8 | Navy Quarter | 11 | 0 | BD013941 | 1 | 4780.31 | 4964.2 | 183.89 | 1000 | 0 | 183890 | 189837.7569 | Tejgaon | Monipuripara 33/11 KV S/S | 175339.91
9 | AT-01 | 0.415 | 0 | 0 | 1 | 1762.39 | 1834.42 | 72.03 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0
10 | AT-02 | 0.415 | 0 | 0 | 1 | 585.48 | 585.48 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0
1 | Doctor Goli | 11 | 0 | BD013944 | 1 | 5839.76 | 6792.09 | 952.33 | 1000 | 0 | 952330 | 958270.3835 | Moghbazar | Ispahani 33/11 KV SS | 898591.0283
2 | Ispahani | 11 | 0 | BD013947 | 1 | 6529.14 | 7580.78 | 1051.64 | 1000 | 0 | 1051640 | 1058199.8531 | Moghbazar | Ispahani 33/11 KV SS | 999582.0108
3 | BTCL | 11 | 0 | BD013949 | 1 | 3442.04 | 3962.52 | 520.48 | 1000 | 0 | 520480 | 523726.617 | Kakrail | Ispahani 33/11 KV SS | 532492.3633
4 | Vikarunnesa | 11 | 0 | BD013948 | 1 | 2973.78 | 4102.97 | 1129.19 | 1000 | 0 | 1129190 | 1136233.5895 | Kakrail | Ispahani 33/11 KV SS | 1092064.7445
5 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
6 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
7 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
8 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
1 | Wireless | 11 | 0 | 0 | 1 | 4695.65 | 5737.24 | 1041.59 | 1000 | 0 | 1041590 | 1048087.1638 | Moghbazar | Ispahani 33/11 KV SS | 896344.5253
2 | Kazir Goli | 11 | 0 | 0 | 1 | 3648.07 | 4903.55 | 1255.48 | 1000 | 0 | 1255480 | 1263311.3532 | Kakrail | Ispahani 33/11 KV SS | 1182067.1763
3 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
4 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
5 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
6 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
7 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
8 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
9 | AT-01 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
10 | AT-02 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 207823.5 | 210341.9 | 2518.4 | 1000 | 0 | 2518400 | 2549641.8301 | Siddirgonj | Siddhirganj 33/11KV S/S | 2438789.3271
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16587.7 | 16731.5 | 143.8 | 1000 | 0 | 143800 | 145583.9006 | Siddirgonj | Siddhirganj 33/11KV S/S | 138711.8093
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 105223.6 | 106740.6 | 1517 | 1000 | 0 | 1517000 | 1535819.0344 | Siddirgonj | Siddhirganj 33/11KV S/S | 1523513.0022
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 164769.1 | 167267.3 | 2498.2 | 1000 | 0 | 2498200 | 2529191.2405 | Siddirgonj | Siddhirganj 33/11KV S/S | 2405949.7847
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6907.4 | 6948.3 | 40.9 | 1000 | 0 | 40900 | 41407.382 | Siddirgonj | Siddhirganj 33/11KV S/S | 36566.7297
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 71952.3 | 73247.9 | 1295.6 | 1000 | 0 | 1295600 | 1311672.4727 | Siddirgonj | Siddhirganj 33/11KV S/S | 1337959.5143
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 141739.7 | 144040.1 | 2300.4 | 1000 | 0 | 2300400 | 2328937.4468 | Siddirgonj | Siddhirganj 33/11KV S/S | 2238024.8856
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 64.2821 | 71.4752 | 7.1931 | 40000 | 0 | 287724 | 291293.3394 | Matuail | Siddhirganj 33/11KV S/S | 424399.7103
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 12873.4 | 13546.5 | 673.1 | 1000 | 0 | 673100 | 681450.0937 | Siddirgonj | Siddhirganj 33/11KV S/S | 758130.0486
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 140787.7 | 143559.8 | 2772.1 | 1000 | 0 | 2772100 | 2806489.0873 | Siddirgonj | Siddhirganj 33/11KV S/S | 2820775.6603
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 | 0 | HA021101013-02 | 1 | 41495960 | 43772221 | 2276261 | 1 | 0 | 2276261 | 2312393.5546 | Matuail | Demra 33/11KV S/S | 2206583.7096
12 | 11 kV DND (WASA) Feeder. | 11 | 0 | HA021100992-02 | 1 | 5288520 | 5367438 | 78918 | 1 | 0 | 78918 | 80170.7162 | Siddirgonj | Demra 33/11KV S/S | 6927.7253
13 | 11 kV Local Feeder | 11 | 0 | HA021100794-02 | 1 | 6636120 | 8692106 | 2055986 | 1 | 0 | 2055986 | 2088621.9879 | Siddirgonj | Demra 33/11KV S/S | 1417684.9395
14 | 11 kV Mouchak Feeder | 11 | 0 | DHK60888 | 1 | 817710.4 | 855586.5 | 37876.1 | 60 | 0 | 2272566 | 2308639.9015 | Siddirgonj | Demra 33/11KV S/S | 2074135.4747
15 | 11 kV Overhead-1 Feeder | 11 | 0 | HA021100829-02 | 1 | 75894360 | 76972401 | 1078041 | 1 | 0 | 1078041 | 1095153.438 | Siddirgonj | Demra 33/11KV S/S | 1095304.9401
16 | 11 kV Provati Steel Feeder | 11 | 0 | DHK60874 | 1 | 544937.6 | 544937.6 | 0 | 60 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 0
17 | 11 kV Islambagh Feeder. | 11 | 0 | DHKA2190 | 1 | 950.6676 | 999.9264 | 49.2588 | 60000 | 0 | 2955528 | 3002442.9965 | Matuail | Demra 33/11KV S/S | 2983539.0327
20 | 11 kV Taj Jute Feeder. | 11 | 0 | DHK61062 | 1 | 563396.8 | 590904.5 | 27507.7 | 60 | 0 | 1650462 | 1676660.8446 | Siddirgonj | Demra 33/11KV S/S | 1675376.4941
21 | 11 kV Al-Aksa Steel Feeder | 11 | 0 | DHK61061 | 1 | 708770.6 | 732963.2 | 24192.6 | 60 | 0 | 1451556 | 1474597.4818 | Siddirgonj | Demra 33/11KV S/S | 1597579.1906
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 | 0 | DHKA2189 | 1 | 905.2486 | 945.7312 | 40.4826 | 60000 | 0 | 2428956 | 2467512.3805 | Siddirgonj | Demra 33/11KV S/S | 2370283.5934
23 | 11 kV Over Head Feeder-2. | 11 | 0 | HA021100488-02 | 1 | 22702980 | 24800709 | 2097729 | 1 | 0 | 2097729 | 2131027.6013 | Demra | Demra 33/11KV S/S | 2071443.4949
24 | 11 kV Shimrail Express Feeder. | 11 | 0 | HA021100511-02 | 1 | 8067222 | 8095991 | 28769 | 1 | 0 | 28769 | 29225.6688 | Siddirgonj | Demra 33/11KV S/S | 0
25 | 11 kV Sarder & Khadem Steel Feeder | 11 | 0 | HA021100413-02 | 1 | 79767340 | 80407905 | 640565 | 1 | 0 | 640565 | 650733.1002 | Demra | Demra 33/11KV S/S | 409613.9007
26 | 11 kV Siddhirgonj Mazar Feeder | 11 | 0 | HA021100393-02 | 1 | 21884266 | 22161663 | 277397 | 1 | 0 | 277397 | 281800.301 | Siddirgonj | Demra 33/11KV S/S | 832832.3648
27 | 11 kV AST Beverage Feeder | 11 | 0 | 0 | 1 | 19198420 | 20233737 | 1035317 | 1 | 0 | 1035317 | 1051751.2525 | Siddirgonj | Demra 33/11KV S/S | 1163750.6238
28 | 11 kV Karim Market Feeder | 11 | 0 | 0 | 1 | 53529387 | 53935137 | 405750 | 1 | Previous Meter Details Below | 2039919 | 2072299.946 | Matuail | Demra 33/11KV S/S | 2089377.8867
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 0
8 | 11 kV Dayagonj Feeder (=L11) | 11 | 0 | 2007755114 | 1 | 5681.21 | 5723.87 | 42.66 | 60000 | 0 | 2559600 | 2648546.8605 | Demra | Sarulia 33/11KV S/S | 3036942.6611
9 | 11 kV Karim Jute Feeder (=L12) | 11 | 0 | 30799484 | 1 | 20.9002 | 21.1189 | 0.2187 | 60000 | 0 | 13122 | 13577.9934 | Demra | Sarulia 33/11KV S/S | 12817.0467
11 | 11 kV Konapara (=L13) **** | 11 | 0 | DHKA2191 | 1 | 1949.7345 | 2005.823 | 56.0885 | 60000 | 0 | 3365310 | 3482255.5223 | Demra | Sarulia 33/11KV S/S | 2467003.1131
12 | 11 kV Sanarpar Feeder (=L14) | 11 | 0 | 575926 | 1 | 45987.8 | 48458.1 | 2470.3 | 1000 | 0 | 2470300 | 2556143.6589 | Matuail | Sarulia 33/11KV S/S | 2386518.0767
13 | 11 kV Latif Bawani Feeder (=L15) | 11 | 0 | 30799450 | 1 | 1800.14 | 1804.9 | 4.76 | 60000 | 0 | 285600 | 295524.6849 | Demra | Sarulia 33/11KV S/S | 302404.9427
14 | 11 kV Tengra Feeder (=L16) | 11 | 0 | 30799145 | 1 | 5390.98 | 5426.47 | 35.49 | 60000 | 0 | 2129400 | 2203397.2826 | Demra | Sarulia 33/11KV S/S | 3315319.3041
16 | 11 kV Police Line Feeder (=L17) | 11 | 0 | 30799480 | 1 | 3276.53 | 3297.43 | 20.9 | 60000 | 0 | 1254000 | 1297576.8726 | Demra | Sarulia 33/11KV S/S | 1183247.2468
17 | 11 kV Demra Bazar Feeder (=L18) | 11 | 0 | 30799119 | 1 | 1621.73 | 1630.73 | 9 | 60000 | 0 | 540000 | 558765.1604 | Demra | Sarulia 33/11KV S/S | 495803.4526
18 | 11 kV Spare Feeder (=F9) | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0
19 | 11 kV Boxnagar Feeder (=F10) | 11 | 0 | HA021100493-02 | 1 | 74707530 | 77608653 | 2901123 | 1 | 0 | 2901123 | 3001937.8862 | Demra | Sarulia 33/11KV S/S | 2753359.8865
21 | 11 kV Baser Pool Feeder (=L11) | 11 | 0 | HA021100518-02 | 1 | 50715102 | 50867999 | 152897 | 1 | 0 | 152897 | 158210.2162 | Demra | Sarulia 33/11KV S/S | 30254.1689
22 | 11 kV Dip-Pur Feeder (=L12) | 11 | 0 | HA021100697-02 | 1 | 18260443 | 20487902 | 2227459 | 1 | 0 | 2227459 | 2304863.862 | Demra | Sarulia 33/11KV S/S | 2171918.011
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0
12 | 11 kV Khanpur Feeder | 11 | 0 | DHKC 9348 | 1 | 86157.18 | 116751.32 | 30594.14 | 60 | 0 | 1835648.4 | 1858439.2031 | N.Gonj (East) | Khanpur 33/11KV S/S | 1689432.0922
13 | 11 kV Mission Para Feeder. | 11 | 0 | DHKC 9347 | 1 | 76552.26 | 103983.86 | 27431.6 | 60 | 0 | 1645896 | 1666330.9001 | N.Gonj (East) | Khanpur 33/11KV S/S | 1591097.4109
14 | 11 kV Esha Kha Feeder | 11 | 0 | DHKC 9311 | 1 | 49376.9 | 64482.72 | 15105.82 | 60 | 0 | 906349.2 | 917602.1317 | N.Gonj (East) | Khanpur 33/11KV S/S | 1040108.3114
15 | 11 kV New Hazigonj Feeder | 11 | 0 | DHKC 9314 | 1 | 100.41 | 134.23 | 33.82 | 60000 | 0 | 2029200 | 2054393.8757 | N.Gonj (East) | Khanpur 33/11KV S/S | 2135156.6373
16 | 11 kV Spare Feeder. | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
19 | 11 kV Hospital RMU Feeder. | 11 | 0 | 6604412 | 1 | 2.82 | 3.83 | 1.01 | 60000 | 0 | 60600 | 61352.3895 | N.Gonj (East) | Khanpur 33/11KV S/S | 59949.0945
20 | 11 kV Old Hajiganj Feeder. | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 0
21 | 11 kV Siraj-ud-daullah Feeder. | 11 | 0 | 06604389 | 1 | 62961.9 | 84767.18 | 21805.28 | 60 | 0 | 1308316.8 | 1324560.4284 | N.Gonj (East) | Khanpur 33/11KV S/S | 1260578.6756
22 | 11 kV Spare Feeder. | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
25 | 11 kV B. B. Road West Feeder. | 11 | 0 | 6604415 | 1 | 140.58 | 186.02 | 45.44 | 40000 | 0 | 1817600 | 1840166.7201 | N.Gonj (West) | Khanpur 33/11KV S/S | 1800087.6245
26 | 11 kV Mondalpara Feeder. | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
27 | 11 kV B. B. Road East Feeder. | 11 | 0 | 06604392 | 1 | 109.7 | 145.84 | 36.14 | 40000 | 0 | 1445600 | 1463548.0912 | N.Gonj (East) | Khanpur 33/11KV S/S | 1396793.7162
28 | 11 kV Bishaw Road Feeder. | 11 | 0 | 06604393 | 1 | 147.19 | 191.13 | 43.94 | 40000 | 0 | 1757600 | 1779421.78 | N.Gonj (East) | Khanpur 33/11KV S/S | 1969640.6189
29 | 11 kV Chasara Feeder. | 11 | 0 | 06604391 | 1 | 152.29 | 204.54 | 52.25 | 40000 | 0 | 2090000 | 2115948.7484 | N.Gonj (West) | Khanpur 33/11KV S/S | 2048765.3497
31 | 11 kV Pathan Tully Feeder. | 11 | 0 | 06604388 | 1 | 32.71 | 32.71 | 0 | 40000 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 0
32 | 11 kV Spare Feeder. | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
33 | 11 kV Nayamati Feeder. | 11 | 0 | 6604289 | 1 | 107.18 | 139.69 | 32.51 | 40000 | 0 | 1300400 | 1316545.3361 | N.Gonj (East) | Khanpur 33/11KV S/S | 1343505.6323
34 | 11 kV Spare Feeder. | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
35 | 11 kV Spare Feeder. | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
36 | 11 kV Spare Feeder. | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 | 0 | 412109 | 1 | 9109.5 | 9109.5 | 0 | 10 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 0
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 | 0 | 243285 | 1 | 6388.1 | 6388.1 | 0 | 10 | 0 | 3000 | 3037.247 | N.Gonj (East) | Khanpur 33/11KV S/S | 3027.732
0 | 11 kV Link Road Feeder | 11 | 0 | HA021100475-02 | 1 | 83653.744 | 85577.974 | 1924.23 | 1000 | 0 | 1924230 | 1951841.3049 | N.Gonj (East) | Matuail 33/11KV S/S | 1877540.2045
4 | 11 kV Lamapara Express Feeder | 11 | 0 | HA021100928-03 | 1 | 75563.19 | 76566.376 | 1003.186 | 1000 | 0 | 1003186 | 1017580.9915 | N.Gonj (East) | Matuail 33/11KV S/S | 1063497.0225
5 | 11 kV Kutubpur Feeder*** | 11 | 0 | DHK66616 | 1 | 17315.9 | 17507.52 | 191.62 | 8000 | 0 | 1532960 | 1554956.8642 | N.Gonj (East) | Matuail 33/11KV S/S | 1703285.4205
6 | 11 kV Ramarbagh Feeder (F1) | 11 | 0 | DHK66625 | 1 | 3463.92 | 3485.92 | 22 | 60000 | 0 | 1320000 | 1338941.0426 | Fatullah | Matuail 33/11KV S/S | 835792.1765
0 | 0 | 11 | Backup | 0 | 1 | 8395.82 | 8395.82 | 0 | 1000 | 0 | 0 | 0 | Fatullah | Matuail 33/11KV S/S | 837818.9826
7 | 11 kV Tushardhara Feeder (F2) | 11 | 0 | DHK66623 | 1 | 3701.54 | 3746.82 | 45.28 | 60000 | 0 | 2716800 | 2755784.1096 | Matuail | Matuail 33/11KV S/S | 2760297.6743
8 | 11 kV Matuail Medical Feeder (F3) | 11 | 0 | DHK66627 | 1 | 3258.78 | 3271.85 | 13.07 | 60000 | 0 | 784200 | 795452.7012 | Matuail | Matuail 33/11KV S/S | 696897.8308
0 | 0 | 11 | Backup | 0 | 1 | 63825.371 | 63825.371 | 0 | 1000 | 0 | 0 | 0 | Matuail | Matuail 33/11KV S/S | 0
9 | 11 kV Rupayan Town Feeder (F4) | 11 | 0 | HA021101044-02 | 1 | 64851.309 | 65208.095 | 356.786 | 1000 | 0 | 356786 | 361905.6203 | Matuail | Matuail 33/11KV S/S | 323912.9361
12 | 11 kV Shibu Market Feeder (F7) | 11 | 0 | DHK66624 | 1 | 2356.06 | 2362.42 | 6.36 | 60000 | 0 | 381600 | 387075.6832 | Fatullah | Matuail 33/11KV S/S | 615623.4101
13 | 11 kV Soma-Sagar Steel (F6) | 11 | 0 | HA060300286-03 | 1 | 75021.472 | 76206.462 | 1184.99 | 1000 | 0 | 1184990 | 1201993.7471 | Fatullah | Matuail 33/11KV S/S | 1110650.3388
14 | 11 kV Jhalkuri Feeder (F8) | 11 | 0 | DHK66626 | 1 | 4291.01 | 4334.87 | 43.86 | 60000 | 0 | 2631600 | 2669361.5514 | Matuail | Matuail 33/11KV S/S | 2690547.2387
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 | 0 | 0 | 0 | Matuail | Matuail 33/11KV S/S | 0
0 | 0 | 11 | 0 | DHK6622 | 1 | 4144.98 | 4168.25 | 23.27 | 60000 | 0 | 1396200 | 1416234.4574 | Matuail | Matuail 33/11KV S/S | 1374993.3702
16 | 11 kV Rajmahal Feeder (F10) | 11 | 0 | DHKA2187 | 1 | 104.4696 | 108.4909 | 4.0213 | 60000 | 0 | 241278 | 244740.1643 | Shyampur | Matuail 33/11KV S/S | 218634.2568
17 | 11 kV Bhuighor Bazar | 11 | 0 | HA021100861-02 | 1 | 73094.967 | 74536.429 | 1441.462 | 1000 | 0 | 1441462 | 1462145.9342 | Matuail | Matuail 33/11KV S/S | 1034107.8281
18 | 11 kV Tokkar Math Feeder | 11 | 0 | HA021200298-02 | 1 | 78743.932 | 79511.406 | 767.474 | 1000 | 0 | 767474 | 778486.6953 | Fatullah | Matuail 33/11KV S/S | 733095.2742
19 | 11 kV Osmani Stadium Feeder***** | 11 | 0 | XA575922 | 1 | 170.9 | 184 | 13.1 | 1000 | 0 | 13100 | 13287.9755 | Fatullah | Matuail 33/11KV S/S | 64493.8811
16 | 33/0.415 KV Transformer, AT-1 | 0.415 | 0 | 2001123043119 | 1 | 7194 | 7271 | 77 | 160 | 0 | 12320 | 12496.7831 | Shyampur | Matuail 33/11KV S/S | 11807.0303
17 | 33/0.415 KV Transformer, AT-2 | 0.415 | 0 | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 129.3921
1 | 11 kV Godnail (F16) | 11 | 0 | 00000109 | 1 | 21004948 | 22845784 | 1840836 | 1 | 0 | 1840836 | 1848814.9706 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1869406.9017
2 | 11 kV M. Circus (F15) | 11 | 0 | 00000123 | 1 | 103491504 | 105458624 | 1967120 | 1 | 0 | 1967120 | 1975646.3394 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 2135882.0516
3 | 11 kV Wapderpool (F14) | 11 | 0 | 00000190 | 1 | 55179144 | 55796344 | 617200 | 1 | 0 | 617200 | 619875.2088 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 595303.4365
4 | 11 kV Chowdhury Bari (F13) | 11 | 0 | 00000191 | 1 | 94163728 | 96441288 | 2277560 | 1 | 0 | 2277560 | 2287431.9192 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 2194488.2982
5 | 11 kV Ailpara (F12) | 1 | 0 | 00000192 | 1 | 46804564 | 49107040 | 2302476 | 1 | 0 | 2302476 | 2312455.9158 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 2506620.5244
6 | 11 kV Spare (F11) | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0
7 | 11 kV Spare (F10) | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0
8 | 11 kV Spare (F9) | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0
9 | 11 kV Spare (F8) | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0
10 | 11 kV Zulfiqur Steel | 11 | 0 | 00000197 | 1 | 13020328 | 14248885 | 1228557 | 1 | 0 | 1228557 | 1233882.0915 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1248729.4855
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 | 0 | 00000198 | 1 | 3985110 | 3997630 | 12520 | 1 | 0 | 12520 | 12574.267 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 42071.0581
12 | 11 kV Lucky Bazar (F5) | 11 | 0 | 00000199 | 1 | 85797352 | 87124224 | 1326872 | 1 | 0 | 1326872 | 1332623.2308 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1392661.9878
13 | 11 kV Enayetnagar (F4) | 11 | 0 | 00000200 | 1 | 27625972 | 29163608 | 1537636 | 1 | 0 | 1537636 | 1544300.7721 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1576051.8888
14 | 11 kV Bhuiyapara (F3) | 11 | 0 | 00000201 | 1 | 60310572 | 62323408 | 2012836 | 1 | 0 | 2012836 | 2021560.4921 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1949356.1666
15 | 11 kV Arambagh (F2) | 11 | 0 | 00000202 | 1 | 5922585 | 6951863 | 1029278 | 1 | 0 | 1029278 | 1033739.3311 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1073358.7436
16 | 11 kV Spare (F1) | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 0
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 | 0 | 00000204 | 1 | 1532.1 | 1577 | 44.9 | 100 | 0 | 4490 | 4509.4616 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 4713.1396
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 | 0 | 00000205 | 1 | 60.71 | 60.71 | 0 | 100 | 0 | 0 | 0 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 0
14 | 11 kV Minan Steel Feeder | 11 | New | 0 | 1 | 74349258 | 74957542 | 608284 | 1 | 0 | 608284 | 608736.535 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 686221.5647
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 86574371 | 87261856 | 687485 | 1 | 0 | 687485 | 687996.4568 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 904286.638
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 83099.6 | 105562.1 | 22462.5 | 60 | 0 | 1347750 | 1348752.6633 | Fatullah | Fatullah OLD 33/11KV S/S | 1520277.0648
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 275685 | 291780 | 16095 | 60 | 0 | 965700 | 966418.4358 | Fatullah | Fatullah OLD 33/11KV S/S | 973413.7301
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 906898.46 | 938604.3 | 31705.84 | 60 | 0 | 1902350.4 | 1903765.6601 | Fatullah | Fatullah OLD 33/11KV S/S | 1898489.4903
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 37019.5 | 48136.4 | 11116.9 | 60 | 0 | 667014 | 667510.2274 | Fatullah | Fatullah OLD 33/11KV S/S | 661387.5474
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 588771.6 | 602547.3 | 13775.7 | 60 | 0 | 826542 | 827156.9088 | Fatullah | Fatullah OLD 33/11KV S/S | 863427.9271
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 466043.56 | 486964.4 | 20920.84 | 60 | 0 | 1255250.4 | 1256184.2479 | Fatullah | Fatullah OLD 33/11KV S/S | 1130265.9765
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 855908.3 | 860387.5 | 4479.2 | 60 | 0 | 268752 | 268951.939 | Fatullah | Fatullah OLD 33/11KV S/S | 461817.7457
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 487049.3 | 501840.9 | 14791.6 | 60 | 0 | 887496 | 888156.2557 | Fatullah | Fatullah OLD 33/11KV S/S | 505747.1466
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 98802056 | 99488328 | 686272 | 1 | 0 | 686272 | 686782.5544 | Sytalakhya | Fatullah OLD 33/11KV S/S | 645276.6941
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24231901 | 24567287 | 335386 | 1 | 0 | 335386 | 335635.5116 | Sytalakhya | Fatullah OLD 33/11KV S/S | 326421.8579
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14466321 | 14795210 | 328889 | 1 | 0 | 328889 | 329133.6781 | Sytalakhya | Fatullah OLD 33/11KV S/S | 311868.8913
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 26912795 | 27036113 | 123318 | 1 | 0 | 123318 | 123409.7429 | Fatullah | Fatullah OLD 33/11KV S/S | 535601.4665
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 9716958 | 11860750 | 2143792 | 1 | 0 | 2143792 | 2145386.8814 | Fatullah | Fatullah OLD 33/11KV S/S | 2599917.6327
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 875390 | 2718344 | 1842954 | 1 | 0 | 1842954 | 1844325.072 | Fatullah | Fatullah OLD 33/11KV S/S | 1788794.6263
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 823.84 | 855.85 | 32.01 | 60000 | 0 | 1920600 | 1925513.8961 | Sytalakhya | Fatullah New 33/11 KV SS | 2018573.5941
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 366.25 | 390.79 | 24.54 | 60000 | 0 | 1472400 | 1476167.1668 | Sytalakhya | Fatullah New 33/11 KV SS | 1492878.3256
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 506.79 | 518.47 | 11.68 | 60000 | 0 | 700800 | 702593.0118 | Sytalakhya | Fatullah New 33/11 KV SS | 691704.3007
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1118.86 | 1147.26 | 28.4 | 60000 | 0 | 1704000 | 1708359.7204 | Sytalakhya | Fatullah New 33/11 KV SS | 1811062.3039
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 116.01 | 135.99 | 19.98 | 60000 | 0 | 1198800 | 1201867.1554 | Sytalakhya | Fatullah New 33/11 KV SS | 1168078.0452
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 48.55 | 58.08 | 9.53 | 60000 | 0 | 571800 | 573262.9625 | Sytalakhya | Fatullah New 33/11 KV SS | 566596.0446
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1045.24 | 1064.3 | 19.06 | 60000 | 0 | 1143600 | 1146525.925 | Sytalakhya | Fatullah New 33/11 KV SS | 1680540.7098
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1234.36 | 1275.93 | 41.57 | 60000 | 0 | 2494200 | 2500581.4639 | Sytalakhya | Fatullah New 33/11 KV SS | 2536449.5967
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0
11 | 11 kV Katherpol Feeder | 11 | 0 | 00000031 | 1 | 59742536 | 61558008 | 1815472 | 1 | 0 | 1815472 | 1825325.1091 | Fatullah | Dapa 33/11 kV | 2095256.7912
12 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
13 | 11 kV Union Parishad Feeder | 11 | 0 | 00000032 | 1 | 61871328 | 63039328 | 1168000 | 1 | 0 | 1168000 | 1174339.0851 | Fatullah | Dapa 33/11 kV | 1364658.7564
14 | 11 kV Shiachar Feeder | 11 | 0 | 00000030 | 1 | 61991488 | 63888724 | 1897236 | 1 | 0 | 1897236 | 1907532.8668 | Fatullah | Dapa 33/11 kV | 1901950.2285
15 | 11 kV Sastapur Feeder | 11 | 0 | 00000106 | 1 | 67891392 | 69229072 | 1337680 | 1 | 0 | 1337680 | 1344939.9892 | Fatullah | Dapa 33/11 kV | 1492863.3157
17 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
18 | 11 kV Jalal Ahmed Express | 11 | 0 | 00000172 | 1 | 4889120 | 4960188 | 71068 | 1 | 0 | 71068 | 71453.7073 | Fatullah | Dapa 33/11 kV | 791901.0884
19 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
21 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
22 | 11 kV Lalpur Feeder | 11 | 0 | 00000044 | 1 | 74945536 | 76099056 | 1153520 | 1 | 0 | 1153520 | 1159780.4978 | Fatullah | Dapa 33/11 kV | 373576.7292
23 | 11 kV Kotaler Bag Feeder | 11 | 0 | 00000050 | 1 | 79654888 | 81048560 | 1393672 | 1 | 0 | 1393672 | 1401235.8745 | Fatullah | Dapa 33/11 kV | 1515181.1462
24 | 11 kV Idrakpur Feeder | 11 | 0 | 00000021 | 1 | 73516904 | 74625056 | 1108152 | 1 | 0 | 1108152 | 1114166.2721 | Fatullah | Dapa 33/11 kV | 1068664.5804
25 | 11 kV Isdair Feeder | 11 | 0 | 00000029 | 1 | 38441108 | 39230944 | 789836 | 1 | 0 | 789836 | 794122.676 | Fatullah | Dapa 33/11 kV | 792940.801
26 | 11 kV Shah Fateullah Express | 11 | 0 | 0000051 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0
27 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
28 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 | 0 | DHKF 7522 | 1 | 2900 | 2955 | 55 | 100 | 0 | 5500 | 5529.8501 | Fatullah | Dapa 33/11 kV | 5198.5629
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0
3 | 11 kV Bholail Feeder (F-3) | 11 | 0 | DHK 9335 | 1 | 17557.5729 | 68294.86 | 50737.2871 | 60 | 0 | 3044237.226 | 3046734.2178 | Sytalakhya | Sitalakhya 33/11KV S/S | 2464743.5384
4 | 11 kV Crony Apparels (F-2) | 11 | 0 | DHK 9336 | 1 | 10186.2566 | 28231.2805 | 18045.0239 | 60 | 0 | 1082701.434 | 1083589.5043 | Sytalakhya | Sitalakhya 33/11KV S/S | 1409860.9795
5 | 11 kV Baburail Feeder (F-5) | 11 | 0 | DHK 9322 | 1 | 14240.3356 | 48193.1576 | 33952.822 | 60 | 0 | 2037169.32 | 2038840.2789 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 1960329.6227
6 | 11 kV Goghchar Feeder (F-1) | 11 | 0 | DHK 9323 | 1 | 68546.5464 | 90249.8775 | 21703.3311 | 60 | 0 | 1302199.866 | 1303267.9767 | Sytalakhya | Sitalakhya 33/11KV S/S | 1261095.5642
7 | 11 kV Norshinghopur (F-2) | 11 | 0 | DHK 9365 | 1 | 47651.0611 | 70175.942 | 22524.8809 | 60 | 0 | 1351492.854 | 1352601.3966 | Sytalakhya | Sitalakhya 33/11KV S/S | 1471201.0567
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 | 0 | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 33/11KV S/S | 554462.5713
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 | 0 | H/A030701125-03 | 1 | 72602.239 | 72836.303 | 234.064 | 1000 | 0 | 234064 | 234255.9876 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 224598.6372
12 | 11 kV Kashipur Feeder (F-7) | 11 | 0 | H/A030800169-03 | 1 | 31592.82 | 33256.036 | 1663.216 | 1000 | 0 | 1663216 | 1664580.229 | Sytalakhya | Sitalakhya 33/11KV S/S | 1652181.4751
13 | 11 kV Spare Feeder (F-6) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 0
14 | 11 kV Paikpara Feeder (F-8) | 11 | 0 | H/A030701098-03 | 1 | 76031.283 | 77120.905 | 1089.622 | 1000 | 0 | 1089622 | 1090515.7468 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 1082731.082
15 | 11 kV B. K. Road Feeder (F-9) | 11 | 0 | H/A030800205-03 | 1 | 93037 | 93822.411 | 785.411 | 1000 | 0 | 785411 | 786055.2221 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 765048.1281
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 | 0 | H/A030701091-03 | 1 | 51115.194 | 52130.183 | 1014.989 | 1000 | 0 | 1014989 | 1015821.5301 | Sytalakhya | Sitalakhya 33/11KV S/S | 958950.0681
9 | 11 kV River View | 11 | 0 | 00000061 | 1 | 4718732 | 5548248 | 829516 | 1 | 0 | 829516 | 838140.6773 | N.Gonj (East) | Mondalpara 33/11KV S/S | 803073.4017
10 | 11 kV Railgate B.B. Road | 11 | 0 | 00000191 | 1 | 21484788 | 22140866 | 656078 | 1 | 0 | 656078 | 662899.4007 | N.Gonj (East) | Mondalpara 33/11KV S/S | 611819.3181
11 | 11 kV DIT | 11 | 0 | 00000174 | 1 | 130377160 | 133509912 | 3132752 | 1 | 0 | 3132752 | 3165323.9759 | N.Gonj (West) | Mondalpara 33/11KV S/S | 2992837.0935
12 | 11 kV Dalpatti | 11 | 0 | 00000182 | 1 | 2382434 | 3037272 | 654838 | 1 | 0 | 654838 | 661646.5082 | N.Gonj (East) | Mondalpara 33/11KV S/S | 714092.6513
13 | 11 kV South Chasara | 11 | 0 | 00000043 | 1 | 88911104 | 91543376 | 2632272 | 1 | 0 | 2632272 | 2659640.365 | N.Gonj (West) | Mondalpara 33/11KV S/S | 2565218.7341
14 | 11 kV Spare | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0
16 | 11 kV NCC Express | 11 | 0 | 00000019 | 1 | 67159 | 96919 | 29760 | 1 | 0 | 29760 | 30069.4219 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22516.8296
17 | 11 kV Spare | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0
18 | 11 kV Masuya Bazar | 11 | 0 | 00000173 | 1 | 3304592 | 4304069 | 999477 | 1 | 0 | 999477 | 1009868.8027 | N.Gonj (East) | Mondalpara 33/11KV S/S | 967617.4501
20 | 11 kV Nitaigonj | 11 | 0 | 00000189 | 1 | 56636980 | 57402260 | 765280 | 1 | 0 | 765280 | 773236.8002 | N.Gonj (East) | Mondalpara 33/11KV S/S | 671875.6098
21 | 11 kV Shahid Nagar | 11 | 0 | 00000020 | 1 | 54413388 | 55724624 | 1311236 | 1 | 0 | 1311236 | 1324869.236 | Sytalakhya | Mondalpara 33/11KV S/S | 1256708.9709
22 | 11 kV Bangla Bazar | 11 | 0 | 00000139 | 1 | 65980440 | 67598832 | 1618392 | 1 | 0 | 1618392 | 1635218.8108 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1605498.2865
23 | 11 kV Vogoban Gonj | 11 | 0 | 00000181 | 1 | 1465156 | 1911915 | 446759 | 1 | 0 | 446759 | 451404.0608 | N.Gonj (East) | Mondalpara 33/11KV S/S | 442440.5963
24 | 11 kV Tanbazar | 11 | 0 | 00000138 | 1 | 46679968 | 47659964 | 979996 | 1 | 0 | 979996 | 990185.2541 | N.Gonj (East) | Mondalpara 33/11KV S/S | 977004.8332
25 | 11 kV SS Road | 11 | 0 | 00000175 | 1 | 62559048 | 63912244 | 1353196 | 1 | 0 | 1353196 | 1367265.5042 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1304240.0244
26 | 11 kV Spare | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0
27 | 33/0.415 kV Auxiliary-1 | 0.415 | 0 | 0 | 1 | 2333.07 | 2413.05 | 79.98 | 100 | 0 | 7998 | 8081.1571 | N.Gonj (West) | Mondalpara 33/11KV S/S | 8402.5235
28 | 33/0.415 kV Auxiliary-2 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 0
10 | 11 kV Masdair Feeder (F-8) | 11 | 0 | XA575914 | 1 | 206799.9 | 209842.6 | 3042.7 | 1000 | 0 | 3042700 | 3086175.0273 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 3077099.4263
11 | 11 kV Narayangonj (F-7) | 11 | 0 | XA575915 | 1 | 163077.6 | 164247.4 | 1169.8 | 1000 | 0 | 1169800 | 1186514.4598 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1307443.1804
12 | 11 kV Nearest Feeder (F-6) | 11 | 0 | XA575927 | 1 | 103832.5 | 104635.5 | 803 | 1000 | 0 | 803000 | 814473.5094 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 997748.2737
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 | 0 | XA575916 | 1 | 113848.2 | 115029.2 | 1181 | 1000 | 0 | 1181000 | 1197874.4889 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1341268.5888
14 | 11 kV Abonti Color Tex. (F-4) | 11 | 0 | XA575912 | 1 | 53493 | 54099.1 | 606.1 | 1000 | 0 | 606100 | 614760.142 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 701320.2188
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 | 0 | DHK66615 | 1 | 165.1511 | 180.4877 | 15.3365 | 60000 | 0 | 920191.92 | 933339.9033 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1045632.3523
17 | 11 kV Shasongaon Feeder (F-2) | 11 | 0 | XA575920 | 1 | 229950 | 230751.7 | 801.7 | 1000 | 0 | 801700 | 813154.9346 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 1189560.6195
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 | 0 | XA575929 | 1 | 17828 | 19036.6 | 1208.6 | 1000 | 0 | 1208600 | 1225868.8461 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1274022.8667
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 | 0 | HA021100913-02 | 1 | 37746.076 | 38386.576 | 640.5 | 1000 | 0 | 640500 | 649651.6597 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 916096.371
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 | 0 | HA021100682-02 | 1 | 55419.839 | 57586.384 | 2166.545 | 1000 | 0 | 2166545 | 2197501.257 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 2366722.3025
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 | 0 | HA021100455-02 | 1 | 51349.693 | 53001.889 | 1652.196 | 1000 | 0 | 1652196 | 1675803.0813 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1827353.8856
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3691.2 | 3753.3 | 62.1 | 160 | 0 | 9936 | 10077.9686 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 6902.8139
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4098.1 | 4101.3 | 3.2 | 160 | 0 | 512 | 519.3156 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 421.2985
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 | 0 | 041808902749 | 1 | 360.83 | 381.72 | 20.89 | 60000 | 0 | 1253400 | 1256317.0074 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1308593.1901
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 | 0 | 041808902759 | 1 | 398.23 | 418.63 | 20.4 | 60000 | 0 | 1224000 | 1226848.5855 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1401162.4833
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
13 | 11 kV Mokterpur Feeder (=F8) | 11 | 0 | 041808902786 | 1 | 229.07 | 252.09 | 23.02 | 60000 | 0 | 1381200 | 1384414.4332 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1059738.0772
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 | 0 | 041808902789 | 1 | 151.39 | 164.08 | 12.69 | 60000 | 0 | 761400 | 763171.9877 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 845746.7241
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
21 | 33/0.415 kV Transformer AT-1 | 0.415 | 0 | 041811907976 | 1 | 1372.11 | 1481.22 | 109.11 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 0
22 | 33/0.415 kV Transformer AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 68696773 | 69350978 | 654205 | 1 | 0 | 654205 | 655997.4572 | Mugdapara | Amulia 33/11 kv | 731782.37
6 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 11388468 | 12677425 | 1288957 | 1 | 0 | 1288957 | 1292488.6152 | Demra | Amulia 33/11 kv | 1242034.7233
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 67318225 | 67815676 | 497451 | 1 | 0 | 497451 | 498813.9667 | Demra | Amulia 33/11 kv | 550647.0061
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 59259140 | 61396460 | 2137320 | 1 | 0 | 2137320 | 2143176.0462 | Demra | Amulia 33/11 kv | 2258006.7634
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 12956256 | 13507195 | 550939 | 1 | 0 | 550939 | 552448.5186 | Mugdapara | Amulia 33/11 kv | 1045691.8176
13 | 11 kV Amulia Model Town Feeder | 11 | Demra | 0 | 1 | 51323114 | 51481502 | 158388 | 1 | 0 | 158388 | 158821.9675 | Demra | Amulia 33/11 kv | 145542.9861
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 8420622 | 9680550 | 1259928 | 1 | 0 | 1259928 | 1263380.0786 | Demra | Amulia 33/11 kv | 1242709.7581
15 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0
16 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0
17 | 33/0.415 kV Transformer, AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0
1 | 11 kV Nearest Feeder | 11 | 0 | HA021101060-02 | 1 | 72108037 | 73698434 | 1590397 | 1 | 0 | 1590397 | 1589546.8433 | Maniknagar | Maniknagar 33/11 KV SS | 1558145.6337
2 | 11kV Spare | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0
3 | 11 kV City Palli Feeder | 11 | 0 | HA021100937-02 | 1 | 75407218 | 76283711 | 876493 | 1 | 0 | 876493 | 876024.4652 | Maniknagar | Maniknagar 33/11 KV SS | 849393.0553
4 | 11 kV R K Mission Road Feeder | 11 | 0 | HA021101035-02 | 1 | 10974303 | 12539189 | 1564886 | 1 | 0 | 1564886 | 1564049.4804 | Maniknagar | Maniknagar 33/11 KV SS | 1502639.6704
5 | 11 kV Janapath Feeder | 11 | 0 | HA021100864-02 | 1 | 23326754 | 25420957 | 2094203 | 1 | 0 | 2094203 | 2093083.5306 | Maniknagar | Maniknagar 33/11 KV SS | 2005205.5254
6 | 11 kV Dhalpur Feeder | 11 | 0 | HA021100851-02 | 1 | 84442992 | 85288108 | 845116 | 1 | 0 | 845116 | 844664.2379 | Maniknagar | Maniknagar 33/11 KV SS | 860069.6023
7 | 11kV WTP | 11 | 0 | X0599387 | 1 | 1406.5 | 1406.5 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 145877.5724
10 | 11kV Kamalapur Water pumping | 11 | 0 | HA021100474-02 | 2 | 7628319 | 7638435 | 10116 | 1 | PT Missing From 14/06/23 | 20232 | 20221.1849 | Maniknagar | Maniknagar 33/11 KV SS | 24456.8935
11 | 11 kV Wasa Road Feeder | 11 | 0 | HA021001011-02 | 2 | 24448123 | 25380490 | 932367 | 1 | PT Missing From 14/06/23 | 1864734 | 1863737.1947 | Maniknagar | Maniknagar 33/11 KV SS | 2040994.3579
12 | 11kV Sutikhalpar Feeder | 11 | 0 | HA021101047-02 | 2 | 78965769 | 79907658 | 941889 | 1 | PT Missing From 14/06/23 | 1883778 | 1882771.0147 | Maniknagar | Maniknagar 33/11 KV SS | 2076315.0532
13 | 11kV Spare | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0
14 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0
15 | 11kV Spare | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0
16 | 11kV Spare | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0
17 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0
13 | AT-1 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0
6 | 11kV Fakirapul Panir Tank Feeder | 11 | 0 | DHK86058 | 1 | 1662.02 | 1678.29 | 16.27 | 60000 | 0 | 976200 | 1040852.4821 | Motijheel | Motijheel old 33/11 kV | 913140.3988
7 | 11kV Station Road Feeder | 11 | 0 | DHK86075 | 1 | 2373.12 | 2374.67 | 1.55 | 60000 | 0 | 93000 | 99159.2715 | Motijheel | Motijheel old 33/11 kV | 121832.4707
8 | 11kV Box Culvert Road Feeder | 11 | 0 | DHK86071 | 1 | 3101.12 | 3125.25 | 24.13 | 60000 | 0 | 1447800 | 1543685.9492 | Motijheel | Motijheel old 33/11 kV | 1996966.8828
9 | 11kV Mohamedan Club Feeder | 11 | 0 | DHK86062 | 1 | 1643.91 | 1662.49 | 18.58 | 60000 | 0 | 1114800 | 1188631.7835 | Motijheel | Motijheel old 33/11 kV | 731597.9549
10 | 11kV Amina Ahmed Co. | 11 | 0 | DHK95754 | 1 | 97956 | 104040 | 6084 | 60 | 0 | 365040 | 389216.1341 | Motijheel | Motijheel old 33/11 kV | 139323.2709
11 | 11kV Bangabhaban -1 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0
12 | 11kV Sonali Bank | 11 | 0 | DHK95753 | 1 | 43302 | 50590 | 7288 | 60 | 0 | 437280 | 466240.4972 | Motijheel | Motijheel old 33/11 kV | 345775.0268
15 | 11kV NCC Bank Feeder | 11 | 0 | DHK68123 | 1 | 309.54 | 316.13 | 6.59 | 60000 | 0 | 395400 | 421586.8382 | Motijheel | Motijheel old 33/11 kV | 147163.9744
16 | 11kV IFIC BANK Feeder | 11 | 0 | DHK68116 | 1 | 383.41 | 389.19 | 5.78 | 60000 | 0 | 346800 | 369768.1221 | Ramna | Motijheel old 33/11 kV | 554880.5594
17 | 11kV Arambagh Feeder | 11 | 0 | DHK68117 | 1 | 3354.56 | 3354.56 | 0 | 60000 | Estimated | 57982.68 | 61822.799 | Motijheel | Motijheel old 33/11 kV | 488536.1447
18 | 11kV Nikotborti Feeder | 11 | 0 | DHK68114 | 1 | 1396.51 | 1410.57 | 14.06 | 60000 | 0 | 843600 | 899470.5531 | Motijheel | Motijheel old 33/11 kV | 655000.3125
19 | 11kV Agrani Bank Feeder | 11 | 0 | DHK95756 | 1 | 357283 | 363305 | 6022 | 60 | 0 | 361320 | 385249.7632 | Motijheel | Motijheel old 33/11 kV | 144691.1372
20 | 11kV Bangladesh Bank-2 | 11 | 0 | DHK95755 | 1 | 515 | 521 | 6 | 60000 | 0 | 360000 | 383842.3413 | Motijheel | Motijheel old 33/11 kV | 180939.3128
21 | 11kV PDB Design Feeder 14 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0
22 | 11kV Bangabhaban-2 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0
23 | 11/0.4 kV AT | 0.415 | 0 | ELIC5429 | 1 | 397502 | 405596 | 8094 | 1 | 0 | 8094 | 8630.0553 | Motijheel | Motijheel old 33/11 kV | 3518.2644
2 | 11 kV Central Weman | 11 | 0 | 41812909492 | 1 | 126.75 | 136.75 | 10 | 60000 | 0 | 600000 | 602582.0913 | Motijheel | Motijheel 33/11 KV SS (new) | 559727.7485
3 | 11 kV Spare Feeder 2 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
4 | 11 kV K. M. Das Len | 11 | 0 | 41812909499 | 1 | 217.11 | 233.82 | 16.71 | 60000 | 0 | 1002600 | 1006914.6746 | Swamibag | Motijheel 33/11 KV SS (new) | 933883.7569
5 | 11 kV Gopibag | 11 | 0 | 41812909517 | 1 | 31.43 | 34.11 | 2.68 | 60000 | 0 | 160800 | 161492.0005 | Motijheel | Motijheel 33/11 KV SS (new) | 148216.3898
6 | 11kV SPICE TV | 11 | 0 | 41812909518 | 1 | 7.5 | 11.09 | 3.59 | 60000 | 0 | 215400 | 216326.9708 | Narinda | Motijheel 33/11 KV SS (new) | 196416.8418
7 | 11 kV Spare Feeder 6 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
8 | 11 kV Spare Feeder 7 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
9 | 11 kV BPT-1 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
10 | 11 kV BPT-2 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
11 | 10 kV Spare Feeder 8 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
12 | 11 kV Spare Feeder 9 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
13 | 11 kV South Kamlapur | 11 | 0 | 41812909473 | 1 | 358.82 | 367.96 | 9.14 | 60000 | 0 | 548400 | 550760.0315 | Motijheel | Motijheel 33/11 KV SS (new) | 1048359.8303
14 | 11 kV Spare Feeder 11 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0
15 | 11 kV Answer Camp | 11 | 0 | 41812909514 | 1 | 153.52 | 166.1 | 12.58 | 60000 | 0 | 754800 | 758048.2709 | Motijheel | Motijheel 33/11 KV SS (new) | 729031.836
16 | 11 kV Shapla Chattar | 11 | 0 | 41812909516 | 1 | 116.51 | 126.45 | 9.94 | 60000 | 0 | 596400 | 598966.5988 | Motijheel | Motijheel 33/11 KV SS (new) | 591058.0422
17 | 11 kV Sayedabad | 11 | 0 | 41812909497 | 1 | 84.55 | 89.79 | 5.24 | 60000 | 0 | 314400 | 315753.0159 | Swamibag | Motijheel 33/11 KV SS (new) | 300047.8135
22 | 33/0.4 kV Aux Transformer | 0.415 | 0 | 41901920686 | 1 | 953.35 | 1040.3 | 86.95 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new) | 0
12 | Inner Circular Road Feeder | 11 | 0 | BD014042 | 1 | 37233 | 39265 | 2032 | 1000 | 0 | 2032000 | 2044037.2926 | Motijheel | P & T 33/11 KV SS | 2028898.6132
13 | NSI New Building Expres Feeder | 11 | 0 | BD013982 | 1 | 8779 | 9206 | 427 | 1000 | 0 | 427000 | 429529.4901 | Ramna | P & T 33/11 KV SS | 413128.6457
14 | Police Hospital RMU Feeder | 11 | 0 | BD014044 | 1 | 3030 | 3211 | 181 | 1000 | 0 | 181000 | 182072.2195 | Rajarbag | P & T 33/11 KV SS | 167833.5123
16 | Jonaki O/H Feeder | 11 | 0 | BD014013 | 1 | 29424 | 30996 | 1572 | 1000 | 0 | 1572000 | 1581312.3149 | Rajarbag | P & T 33/11 KV SS | 1420129.7195
17 | Nayapalton Overhead Feeder | 11 | 0 | BD014014 | 1 | 21639 | 22642 | 1003 | 1000 | 0 | 1003000 | 1008941.636 | Ramna | P & T 33/11 KV SS | 976215.0449
18 | Masjid Gali Over Head Feeder | 11 | 0 | BD014016 | 1 | 11857 | 12776 | 919 | 1000 | 0 | 919000 | 924444.0314 | Ramna | P & T 33/11 KV SS | 878891.4697
19 | Spare Feeder (Feeder-8) | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 0
23 | Mid Way Over Head Feeder | 11 | 0 | BD014015 | 1 | 19862 | 20857 | 995 | 1000 | 0 | 995000 | 1000894.2451 | Ramna | P & T 33/11 KV SS | 972242.6541
24 | Palton Thana Over Head Feeder | 11 | 0 | BD014033 | 1 | 19551 | 20890 | 1339 | 1000 | 0 | 1339000 | 1346932.0545 | Rajarbag | P & T 33/11 KV SS | 1294006.3108
25 | Police Hospital (South) U/G Feeder 7 | 11 | 0 | BD014034 | 1 | 11851 | 12022 | 171 | 1000 | 0 | 171000 | 172012.9808 | Rajarbag | P & T 33/11 KV SS | 167833.5123
26 | China Town Express Feeder | 11 | 0 | BD013943 | 1 | 5536 | 5830 | 294 | 1000 | 0 | 294000 | 295741.6161 | Ramna | P & T 33/11 KV SS | 284025.9439
27 | Fakirapul Bazar O/H Feeder | 11 | 0 | BD014032 | 1 | 25196 | 26543 | 1347 | 1000 | 0 | 1347000 | 1354979.4454 | Motijheel | P & T 33/11 KV SS | 1402253.9607
28 | PWD Ouarter (RMU) | 11 | 0 | BD013937 | 1 | 1861 | 2011 | 150 | 1000 | 0 | 150000 | 150888.5797 | Motijheel | P & T 33/11 KV SS | 145985.3628
29 | Postal Quarter RMU | 11 | 0 | BD013945 | 1 | 2327 | 2500 | 173 | 1000 | 0 | 173000 | 174024.8285 | Motijheel | P & T 33/11 KV SS | 164854.2192
30 | 11/0.4 kV AT-1 | 0.415 | 0 | DHKH4409 | 1 | 1313 | 1316 | 3 | 100 | 0 | 300 | 301.7772 | Rajarbag | P & T 33/11 KV SS | 0
31 | 11/0.4 kV AT-2 | 0.415 | 0 | DHKH4411 | 1 | 454 | 454 | 0 | 100 | 0 | 0 | 0 | Rajarbag | P & T 33/11 KV SS | 5362.7276
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 315.7 | 349.8 | 34.1 | 40000 | 0 | 1364000 | 1381038.2208 | Rajarbag | Kamalapur Railway 33/11 KV SS | 1302977.567
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 53.6 | 58.9 | 5.3 | 40000 | 0 | 212000 | 214648.1692 | Rajarbag | Kamalapur Railway 33/11 KV SS | 201076.785
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 221 | 242.4 | 21.4 | 40000 | 0 | 856000 | 866692.6078 | Rajarbag | Kamalapur Railway 33/11 KV SS | 735941.0332
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 562.4 | 617 | 54.6 | 40000 | 0 | 2184000 | 2211281.1394 | Rajarbag | Kamalapur Railway 33/11 KV SS | 2079133.9572
5 | 11 KV Majar Feeder | 11 | 0 | 96 | 1 | 22.1 | 32 | 9.9 | 40000 | 0 | 396000 | 400946.5802 | Motijheel | Kamalapur Railway 33/11 KV SS | 382045.8916
7 | 11 kV Feeder-6 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 278.1 | 304.8 | 26.7 | 40000 | 0 | 1068000 | 1081340.777 | Rajarbag | Kamalapur Railway 33/11 KV SS | 1001362.3894
9 | 11 kV Feeder-8 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 190.2 | 198.6 | 8.4 | 40000 | 0 | 336000 | 340197.0984 | Rajarbag | Kamalapur Railway 33/11 KV SS | 337808.9988
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 198.7 | 209.5 | 10.8 | 40000 | 0 | 432000 | 437396.2693 | Rajarbag | Kamalapur Railway 33/11 KV SS | 402153.5701
13 | 11 kV Feeder-11 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 48 | 53.5 | 5.5 | 40000 | 0 | 220000 | 222748.1001 | Motijheel | Kamalapur Railway 33/11 KV SS | 217162.9278
15 | Jasimuddin Feeder-13 | 11 | 0 | 91 | 1 | 71.8 | 112.7 | 40.9 | 40000 | 0 | 1636000 | 1656435.8718 | Motijheel | Kamalapur Railway 33/11 KV SS | 1097879.2463
16 | Police Box Feeder-14 | 11 | 0 | 18 | 1 | 36.4 | 52.8 | 16.4 | 40000 | 0 | 656000 | 664194.3349 | Motijheel | Kamalapur Railway 33/11 KV SS | 643445.7121
17 | 11 kV Feeder-15 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0
18 | 11 kV Feeder-16 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0
19 | Auxiliary -1 (AT-1 ) | 0.415 | 0 | DHKF 7632 | 1 | 787.87 | 816.23 | 28.36 | 100 | 0 | 2836 | 2871.4255 | Rajarbag | Kamalapur Railway 33/11 KV SS | 5128.4634
20 | Auxiliary -1 (AT-2 ) | 0.415 | 0 | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS | 0
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 212943.22 | 214079.71 | 1136.49 | 1000 | Estimated | 788651.64 | 793502.3098 | Motijheel | Bangabhaban 132/11KV S/S | 860468.6016
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 23966.99 | 24049.87 | 82.88 | 1000 | 0 | 82880 | 83389.7606 | Motijheel | Bangabhaban 132/11KV S/S | 79020.0597
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 0
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 240728.715
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33826.28 | 33840.33 | 14.05 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 20212.3186
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 706255.2 | 710599.0834 | Motijheel | Bangabhaban 132/11KV S/S | 737544.5157
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15661.1 | 15730.83 | 69.73 | 1000 | 0 | 69730 | 70158.8804 | Motijheel | Bangabhaban 132/11KV S/S | 76837.1293
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 244322.7 | 245496.9 | 1174.2 | 1000 | 0 | 1174200 | 1181422.0182 | Motijheel | Bangabhaban 132/11KV S/S | 1217478.907
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14139.81 | 14313.16 | 173.35 | 1000 | 0 | 173350 | 174416.2041 | Motijheel | Bangabhaban 132/11KV S/S | 171420.6744
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94891.92 | 94938.39 | 46.47 | 1000 | Estimated | 235418.4 | 236866.3611 | Motijheel | Bangabhaban 132/11KV S/S | 245848.1719
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163076.15 | 163401.03 | 324.88 | 1000 | 0 | 324880 | 326878.2024 | Motijheel | Bangabhaban 132/11KV S/S | 270087.1078
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20481.33 | 20538.85 | 57.52 | 1000 | Estimated | 235418.4 | 236866.3611 | Motijheel | Bangabhaban 132/11KV S/S | 245848.1719
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 329585.76 | 331612.9056 | Motijheel | Bangabhaban 132/11KV S/S | 368772.2578
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122251.69 | 122597.98 | 346.29 | 1000 | 0 | 346290 | 348419.8864 | Motijheel | Bangabhaban 132/11KV S/S | 313139.3465
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 271490.95 | 272305.38 | 814.43 | 1000 | 0 | 814430 | 819439.2218 | Motijheel | Bangabhaban 132/11KV S/S | 796304.7174
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 79642.9 | 80121.74 | 478.84 | 1000 | 0 | 478840 | 481785.1466 | Motijheel | Bangabhaban 132/11KV S/S | 474463.9677
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192345.5 | 192447.87 | 102.37 | 1000 | Estimated | 329585.76 | 331612.9056 | Motijheel | Bangabhaban 132/11KV S/S | 368772.2578
23 | 11/0.4 kV AT-1 | 0.415 | 0 | 63412931 | 1 | 63258 | 63258 | 0 | 1 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0
24 | 11/0.4 kV AT-2 | 0.415 | 0 | 63403117 | 1 | 13772 | 13772 | 0 | 1 | Estimated | 5000 | 5030.7529 | Motijheel | Bangabhaban 132/11KV S/S | 5053.0797
1 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24474.94 | 24616.19 | 141.25 | 8000 | 0 | 1130000 | 1139801.4532 | Narinda | Narinda 33/11KV S/S | 1096395.2732
2 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16557.29 | 16642.26 | 84.97 | 8000 | 0 | 679760 | 685656.1379 | Swamibag | Narinda 33/11KV S/S | 629657.0471
3 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 471.15 | 487.34 | 16.19 | 40000 | 0 | 647600 | 653217.1868 | Maniknagar | Narinda 33/11KV S/S | 492385.8425
4 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5473.81 | 5501.64 | 27.83 | 40000 | 0 | 1113200 | 1122855.7324 | Narinda | Narinda 33/11KV S/S | 1066634.3599
5 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3323.44 | 3373.76 | 50.32 | 40000 |  | 2012800 | 2030258.73 | Swamibag | Narinda 33/11KV S/S | 1913892.8816
6 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8477.29 | 8518.25 | 40.96 | 40000 | 0 | 1638400 | 1652611.2397 | Narinda | Narinda 33/11KV S/S | 1532808.0158
7 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7223.58 | 7262.99 | 39.41 | 40000 | 0 | 1576400 | 1590073.4608 | Narinda | Narinda 33/11KV S/S | 1585232.3889
10 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5932.66 | 5965.54 | 32.88 | 40000 | 0 | 1315200 | 1326607.8506 | Swamibag | Narinda 33/11KV S/S | 1271895.9437
11 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 4979.47 | 5006.32 | 26.85 | 40000 | 0 | 1074000 | 1083315.7174 | Narinda | Narinda 33/11KV S/S | 1015016.5156
12 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7734.95 | 7762.22 | 27.27 | 40000 | 0 | 1090800 | 1100261.4381 | Swamibag | Narinda 33/11KV S/S | 886375.1694
13 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6319.72 | 6347.36 | 27.64 | 40000 | 0 | 1105600 | 1115189.8112 | Narinda | Narinda 33/11KV S/S | 1101315.099
14 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0
15 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 22163.2 | 26064.5 | 3901.3 | 444.44 | 0 | 1733893.772 | 1748933.3106 | Narinda | Narinda 33/11KV S/S | 1624153.5662
16 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 374036 | 384194 | 10158 | 80 | 0 | 812640 | 819688.7194 | Narinda | Narinda 33/11KV S/S | 775800.0686
17 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 29470.6 | 31907.7 | 2437.1 | 444.44 | 0 | 1083144.724 | 1092539.7614 | Narinda | Narinda 33/11KV S/S | 1048880.237
18 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 35683.5 | 36247.2 | 563.7 | 1000 | 0 | 563700 | 568589.4506 | Swamibag | Narinda 33/11KV S/S | 537047.3757
1 | 11/0.4 kV Aux Transformer-1 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0
2 | 11/0.4 kV Aux Transformer-2 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62100 | 62362.9 | 262.9 | 2222.22 | Estimated | 470836.8 | 476949.7245 | Banglabazar | Kumertuly 33/11KV S/S | 555416.4351
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4531.4 | 4560.66 | 29.26 | 40000 | Estimated | 1412510.4 | 1430849.1736 | Banglabazar | Kumertuly 33/11KV S/S | 1481110.4937
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 0
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5121.51 | 5132.38 | 10.87 | 40000 | Estimated | 529691.4 | 536568.4401 | Banglabazar | Kumertuly 33/11KV S/S | 493703.4979
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 0
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5393.48 | 5420.2 | 26.72 | 40000 | Estimated | 1200633.84 | 1216221.7976 | Banglabazar | Kumertuly 33/11KV S/S | 1419397.5564
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | Estimated | 39563.37 | 40077.0255 | Bangshal | Kumertuly 33/11KV S/S | 0
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4023.81 | 4052.11 | 28.3 | 40000 | Estimated | 823964.4 | 834662.018 | Banglabazar | Kumertuly 33/11KV S/S | 740555.2468
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1130008.32 | 1144679.3389 | Banglabazar | Kumertuly 33/11KV S/S | 925694.0585
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5853.24 | 5878.45 | 25.21 | 40000 | 0 | 1008400 | 1021492.1651 | Banglabazar | Kumertuly 33/11KV S/S | 1019206.2302
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8098.57 | 8147.67 | 49.1 | 40000 | 0 | 1964000 | 1989498.8221 | Banglabazar | Kumertuly 33/11KV S/S | 1947085.7372
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3736.6 | 3746.74 | 10.14 | 40000 | 0 | 405600 | 410865.9482 | Banglabazar | Kumertuly 33/11KV S/S | 427409.0643
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7172.56 | 7200.1 | 27.54 | 40000 | Estimated | 1235946.6 | 1251993.0269 | Banglabazar | Kumertuly 33/11KV S/S | 1073805.1079
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3572.31 | 3579.1 | 6.79 | 40000 | 0 | 271600 | 275126.2119 | Banglabazar | Kumertuly 33/11KV S/S | 281286.3072
27 | 11/0.4 kV AT-1 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 0
28 | 11/0.4 kV AT-2 | 0.415 | 0 | 05378636 | 1 | 163007.6 | 165364.8 | 2357.2 | 2 | 0 | 4714.4 | 4775.6076 | Banglabazar | Kumertuly 33/11KV S/S | 4915.4072
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 36815436 | 37591630 | 776194 | 1 | 0 | 776194 | 778854.3109 | Bangshal | Banshal 33/11KV S/S | 716311.3918
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 46867285 | 48292149 | 1424864 | 1 | 0 | 1424864 | 1429747.5487 | Banglabazar | Banshal 33/11KV S/S | 1353751.6158
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 19159807 | 19895217 | 735410 | 1 | 0 | 735410 | 737930.5287 | Bangshal | Banshal 33/11KV S/S | 715455.6721
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 43501879 | 45156791 | 1654912 | 1 | 0 | 1654912 | 1660584.0104 | Bangshal | Banshal 33/11KV S/S | 1409457.3709
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 59902495 | 61068329 | 1165834 | 1 | 0 | 1165834 | 1169829.7548 | Bangshal | Banshal 33/11KV S/S | 1127796.6211
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 27364546 | 28992386 | 1627840 | 1 | 0 | 1627840 | 1633419.2244 | Bangshal | Banshal 33/11KV S/S | 1486833.0286
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 59668688 | 61260126 | 1591438 | 1 | 0 | 1591438 | 1596892.4609 | Bangshal | Banshal 33/11KV S/S | 1498407.2378
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 47860599 | 49123470 | 1262871 | 1 | 0 | 1262871 | 1267199.3373 | Narinda | Banshal 33/11KV S/S | 1145519.8164
13 | AT-1 | 0.415 | 0 | DHK-4415 | 1 | 685.05 | 727.72 | 42.67 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0
14 | AT-2 | 0.415 | 0 | DHK-4410 | 1 | 658.98 | 659.01 | 0.03 | 100 | 0 | 7000 | 7023.9917 | Bangshal | Banshal 33/11KV S/S | 6997.7081
17 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 783779.8 | 813181.6 | 29401.8 | 60 | 0 | 1764108 | 1792344.292 | Kazla | Kazla 33/11KV S/S | 1710856.4639
18 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1883347.2 | 1913492.0332 | Kazla | Kazla 33/11KV S/S | 1855425.2355
19 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 3001584.6 | 3049627.928 | Kazla | Kazla 33/11KV S/S | 2968680.3768
20 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963851 | 36963854 | 3 | 1000 | Estimated | 1059382.8 | 1076339.2687 | Maniknagar | Kazla 33/11KV S/S | 556627.5706
21 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0
22 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 110052.4 | 112225.6 | 2173.2 | 1000 | 0 | 2173200 | 2207984.2138 | Jurain | Kazla 33/11KV S/S | 2092993.2394
23 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 41024544 | 0 | 1 | Estimated | 1706783.4 | 1734102.1551 | Kazla | Kazla 33/11KV S/S | 1855425.2355
25 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 647129.1 | 684518.2 | 37389.1 | 60 | 0 | 2243346 | 2279252.9698 | Jurain | Kazla 33/11KV S/S | 2232712.5636
26 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 579724.6 | 602385.9 | 22661.3 | 60 | 0 | 1359678 | 1381440.9902 | Kazla | Kazla 33/11KV S/S | 1371332.0993
27 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 947647 | 986124.4 | 38477.4 | 60 | 0 | 2308644 | 2345596.1288 | Kazla | Kazla 33/11KV S/S | 2459477.0573
28 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0
29 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 178496.3 | 212446.1 | 33949.8 | 60 | 0 | 2036988 | 2069592.0061 | Swamibag | Kazla 33/11KV S/S | 1962979.7252
31 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 33062 | 73285.9 | 40223.9 | 60 | 0 | 2413434 | 2452063.3964 | Jurain | Kazla 33/11KV S/S | 2370251.5382
32 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 249904.8 | 290452 | 40547.2 | 60 | 0 | 2432832 | 2471771.8805 | Shyampur | Kazla 33/11KV S/S | 3092469.9692
33 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 362270.4 | 383226.2 | 20955.8 | 60 | 0 | 1257348 | 1277473.0974 | Matuail | Kazla 33/11KV S/S | 837095.6004
34 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1912724 | 1945817 | 33093 | 60 | 0 | 1985580 | 2017361.1702 | Jurain | Kazla 33/11KV S/S | 1952856.964
35 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 26329191 | 27937314 | 1608123 | 1 | 0 | 1608123 | 1633862.5979 | Kazla | Kazla 33/11KV S/S | 1591423.3402
36 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 25278265 | 25965046 | 686781 | 1 | 0 | 686781 | 697773.6086 | Kazla | Kazla 33/11KV S/S | 686441.9856
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 2894.5 | 3086.1 | 191.6 | 10000 | 0 | 1916000 | 1946667.4736 | Kazla | Kazla 33/11KV S/S | 1703398.1226
38 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0
40 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 808.3 | 814.2 | 5.9 | 4000 | 0 | 23600 | 23977.7413 | Kazla | Kazla 33/11KV S/S | 1140208.9403
41 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 12649 | 13448.4 | 799.4 | 4000 | 0 | 3197600 | 3248780.7482 | Kazla | Kazla 33/11KV S/S | 3103743.9224
43 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0
44 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 19756.3 | 20321.3 | 565 | 1000 | 0 | 565000 | 574043.3834 | Kazla | Kazla 33/11KV S/S | 0
45 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 16523.9 | 17160.4 | 636.5 | 2000 | 0 | 1273000 | 1293375.6231 | Kazla | Kazla 33/11KV S/S | 1288887.6302
46 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 34893.9 | 35605.2 | 711.3 | 2000 | 0 | 1422600 | 1445370.1189 | Maniknagar | Kazla 33/11KV S/S | 1356006.601
47 | 33/0.4 kV AT-1 | 0.415 | 0 | 503043 | 1 | 96204 | 96204 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 244.069
48 | 33/0.4 kV AT-2 | 0.415 | 0 | 503044 | 1 | 92456 | 93292 | 836 | 10 | 0 | 6000 | 6096.0359 | Kazla | Kazla 33/11KV S/S | 6101.7246
23 | Auxiliary Transformer | 0.415 | 0 | 41901920685 | 1 | 2173.65 | 2290.62 | 116.97 | 160 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur | 0 | 1 | 546.49 | 579.6764 | 33.1864 | 40000 | 0 | 1327456 | 1329002.2614 | Shyampur | Shyampur 33/11KV S/S | 1796570.0888
6 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
7 | 11 kV Road No.-21 Feeder | 11 | 0 | BD001943 | 1 | 1013.14 | 1030.3488 | 17.2088 | 40000 | 0 | 688352 | 689153.8135 | Shyampur | Shyampur 33/11KV S/S | 726162.1684
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1490.83 | 1510.017 | 19.187 | 40000 | 0 | 767480 | 768373.9842 | Shyampur | Shyampur 33/11KV S/S | 842780.9272
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1383.34 | 1400.2733 | 16.9333 | 40000 | 0 | 677332 | 678120.977 | Shyampur | Shyampur 33/11KV S/S | 664045.6474
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1259.97 | 1286.4505 | 26.4805 | 40000 | 0 | 1059220 | 1060453.8119 | Fatullah | Shyampur 33/11KV S/S | 1011898.1651
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3181.56 | 3240.1803 | 58.6203 | 40000 | 0 | 2344812 | 2347543.3088 | Shyampur | Shyampur 33/11KV S/S | 2415731.5404
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2064.33 | 2102.0425 | 37.7125 | 40000 | 0 | 1508500 | 1510257.147 | Shyampur | Shyampur 33/11KV S/S | 1400226.6095
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 481.32 | 484.1231 | 2.8031 | 40000 | 0 | 112124 | 112254.6055 | Fatullah | Shyampur 33/11KV S/S | 96981.9232
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3028.5 | 3076.6439 | 48.1439 | 40000 | 0 | 1925756 | 1927999.1795 | Shyampur | Shyampur 33/11KV S/S | 1824622.7112
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1879.48 | 1921.3681 | 41.8881 | 40000 | 0 | 1675524 | 1677475.7016 | Shyampur | Shyampur 33/11KV S/S | 1601003.2355
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1372.48 | 1406.4167 | 33.9367 | 40000 | 0 | 1357468 | 1359049.2203 | Shyampur | Shyampur 33/11KV S/S | 1887540.7358
20 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 793.62 | 807.729 | 14.109 | 40000 | 0 | 564360 | 565017.3838 | Shyampur | Shyampur 33/11KV S/S | 552636.6613
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1274.85 | 1294.1832 | 19.3332 | 40000 | 0 | 773328 | 774228.7961 | Shyampur | Shyampur 33/11KV S/S | 1030332.7456
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2850.41 | 2914.5187 | 64.1087 | 40000 | 0 | 2564348 | 2567335.031 | Shyampur | Shyampur 33/11KV S/S | 2104748.1835
24 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1090.91 | 1098.2827 | 7.3727 | 40000 | 0 | 294908 | 295251.5179 | Shyampur | Shyampur 33/11KV S/S | 251271.3464
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1882.3 | 1916.4054 | 34.1054 | 40000 | 0 | 1364216 | 1365805.0805 | Shyampur | Shyampur 33/11KV S/S | 1428279.2319
28 | 11 kV Spare Feeder | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1321.48 | 1335.0577 | 13.5777 | 40000 | 0 | 543108 | 543740.6288 | Shyampur | Shyampur 33/11KV S/S | 732574.1964
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1273.64 | 1300.6173 | 26.9773 | 40000 | 0 | 1079092 | 1080348.9594 | Shyampur | Shyampur 33/11KV S/S | 971021.4868
31 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
32 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
33 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2161.1 | 2199.2196 | 38.1196 | 40000 | 0 | 1524784 | 1526560.1151 | Shyampur | Shyampur 33/11KV S/S | 1250345.4555
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 168.36 | 170.7545 | 2.3945 | 40000 | 0 | 95780 | 95891.5675 | Shyampur | Shyampur 33/11KV S/S | 84558.6189
37 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1150.73 | 1172.4449 | 21.7149 | 40000 | 0 | 868596 | 869607.7672 | Shyampur | Shyampur 33/11KV S/S | 875642.5706
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3585.78 | 3633.3532 | 47.5732 | 40000 | 0 | 1902928 | 1905144.5888 | Shyampur | Shyampur 33/11KV S/S | 2092324.8793
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1064.5 | 1076.0762 | 11.5762 | 40000 | 0 | 463046.4 | 463585.7706 | Shyampur | Shyampur 33/11KV S/S | 590307.3256
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 62985.9 | 63432.6 | 446.7 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 | 0 | 0 | 1 | 578955 | 586899 | 7944 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 33561211 | 35723650 | 2162439 | 1 | 0 | 2162439 | 2098065.1104 | Shyampur | Shyampur BISIC 33/11KV S/S | 2051822.5774
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 19777200 | 20537911 | 760711 | 1 | 0 | 760711 | 738065.3088 | Jurain | Shyampur BISIC 33/11KV S/S | 731764.9753
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 0
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 0
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 377188.5 | 410183.5 | 32995 | 60 | 0 | 1979700 | 1920766.0882 | Jurain | Shyampur BISIC 33/11KV S/S | 1940683.7189
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 550150 | 575495.8 | 25345.8 | 60 | 0 | 1520748 | 1475476.6819 | Jurain | Shyampur BISIC 33/11KV S/S | 1381608.0185
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 570335.4 | 594888.2 | 24552.8 | 60 | 0 | 1473168 | 1429313.0963 | Jurain | Shyampur BISIC 33/11KV S/S | 1378277.4296
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 320655.9 | 337050 | 16394.1 | 60 | 0 | 983646 | 954363.7317 | Shyampur | Shyampur BISIC 33/11KV S/S | 1019394.7492
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511384.5 | 511525.1 | 140.6 | 60 | 0 | 8436 | 8184.8678 | Jurain | Shyampur BISIC 33/11KV S/S | 8596.203
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 778535.8 | 824930.4 | 46394.6 | 60 | 0 | 2783676 | 2700808.4363 | Jurain | Shyampur BISIC 33/11KV S/S | 2561826.8196
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 214982.3 | 236095.8 | 21113.5 | 60 | 0 | 1266810 | 1229098.1908 | Shyampur | Shyampur BISIC 33/11KV S/S | 1284557.7074
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 435544 | 443790.5 | 8246.5 | 60 | 0 | 494790 | 480060.5409 | Jurain | Shyampur BISIC 33/11KV S/S | 1215195.8482
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 439242.7 | 482640.9 | 43398.2 | 60 | 0 | 2603892 | 2526376.4464 | Jurain | Shyampur BISIC 33/11KV S/S | 2465450.8355
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 833590.5 | 845435.7 | 11845.2 | 60 | 0 | 710712 | 689554.7346 | Jurain | Shyampur BISIC 33/11KV S/S | 725640.3272
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 917620.2 | 938845.6 | 21225.4 | 60 | 0 | 1273524 | 1235612.3209 | Shyampur | Shyampur BISIC 33/11KV S/S | 1199610.0995
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB7380 | 1 | 600880 | 604904 | 4024 | 1 | 0 | 4024 | 3904.2091 | Shyampur | Shyampur BISIC 33/11KV S/S | 3633.5474
8 | 11 kV Spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0
9 | 11 kV Khaza Moinuddin | 11 | 0 | 00000026 | 1 | 4014750 | 4686068 | 671318 | 1 | 0 | 671318 | 676115.2751 | Fatullah | Nandalalpur 33/11 kV | 672821.6526
10 | 11 kV Chitashal | 11 | 0 | 00000027 | 1 | 31727122 | 32447880 | 720758 | 1 | 0 | 720758 | 725908.576 | Shyampur | Nandalalpur 33/11 kV | 676035.0889
11 | 11 kV Local Feeder | 11 | 0 | 00000157 | 1.5 | 18012236 | 18223956 | 211720 | 1 | Estimated | 647400.6 | 652026.96 | Shyampur | Nandalalpur 33/11 kV | 610908.7086
12 | 11 kV Rasel Germants | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 0
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 | 0 | 00000121 | 1 | 68316432 | 70737224 | 2420792 | 1 | 0 | 2420792 | 2438091.1118 | Matuail | Nandalalpur 33/11 kV | 2521439.5722
14 | 11 kV Nandalalpur | 11 | 0 | 00000010 | 1 | 82071400 | 82993360 | 921960 | 1 | 0 | 921960 | 928548.3765 | Fatullah | Nandalalpur 33/11 kV | 892208.2473
15 | 11 kV Sharif Bagh | 11 | 0 | 00000132 | 1 | 68478392 | 70183192 | 1704800 | 1 | 0 | 1704800 | 1716982.5939 | Shyampur | Nandalalpur 33/11 kV | 1682233.437
18 | 11 kV Spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0
19 | 11 KV Nayamati | 11 | 0 | 00000158 | 1 | 62900248 | 64037524 | 1137276 | 1 | 0 | 1137276 | 1145403.0364 | Fatullah | Nandalalpur 33/11 kV | 1037983.1413
20 | 11 kV Pulpar | 11 | 0 | 00000160 | 1 | 6177345 | 6979983 | 802638 | 1 | 0 | 802638 | 808373.695 | Fatullah | Nandalalpur 33/11 kV | 916555.6279
21 | 11 kV Shahi Bazar | 11 | 0 | 00000170 | 1 | 39279104 | 40057984 | 778880 | 1 | 0 | 778880 | 784445.919 | Shyampur | Nandalalpur 33/11 kV | 785444.6114
22 | 11 kV Pagla Bazar | 11 | 0 | 00000060 | 1 | 48692680 | 49521320 | 828640 | 1 | 0 | 828640 | 834561.5067 | Fatullah | Nandalalpur 33/11 kV | 783154.3223
23 | 11 kV Delpara bazar | 11 | 0 | 00000063 | 1 | 76134976 | 77632408 | 1497432 | 1 | 0 | 1497432 | 1508132.7308 | Shyampur | Nandalalpur 33/11 kV | 1527622.8486
24 | 11 kV Bhuighor (Board mill) | 11 | 0 | 00000146 | 1 | 42387696 | 43051416 | 663720 | 1 | 0 | 663720 | 668462.9794 | Matuail | Nandalalpur 33/11 kV | 1074021.0416
25 | 11 kV Spare | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0
26 | 33/0.415 kV, 200 kVA AT-1 | 11 | 0 | 7803 | 1 | 2309 | 2371 | 62 | 100 | 0 | 6200 | 6244.3055 | Shyampur | Nandalalpur 33/11 kV | 5725.7228
27 | 33/0.415 kV, 200 kVA AT-2 | 11 | 0 | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur | Nandalalpur 33/11 kV | 0
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 59733520 | 61037936 | 1304416 | 1 | 0 | 1304416 | 1307497.2614 | Postogola | Postogola 33/11KV S/S | 1269812.3426
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 6981957 | 8339686 | 1357729 | 1 | 0 | 1357729 | 1360936.1962 | Jurain | Postogola 33/11KV S/S | 1367079.5822
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 23055333 | 23596442 | 541109 | 1 | 0 | 541109 | 542387.1952 | Jurain | Postogola 33/11KV S/S | 435813.5436
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 71243020 | 72786262 | 1543242 | 1 | 0 | 1543242 | 1546887.4107 | Postogola | Postogola 33/11KV S/S | 1509702.7057
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 407058.9 | 418110.9 | 11052 | 60 | 0 | 663120 | 664686.4068 | Postogola | Postogola 33/11KV S/S | 678488.3278
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 824597.3 | 845528 | 20930.7 | 60 | 0 | 1255842 | 1258808.5211 | Postogola | Postogola 33/11KV S/S | 1186933.4512
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 706742.8 | 727154.9 | 20412.1 | 60 | 0 | 1224726 | 1227619.0196 | Postogola | Postogola 33/11KV S/S | 1164704.2052
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 515784.4 | 517862.7 | 2078.3 | 60 | 0 | 124698 | 124992.5587 | Postogola | Postogola 33/11KV S/S | 126222.4118
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 797566.5 | 819569.4 | 22002.9 | 60 | 0 | 1320174 | 1323292.4846 | Postogola | Postogola 33/11KV S/S | 1331811.5849
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 243241.8 | 283639 | 40397.2 | 60 | 0 | 2423832 | 2429557.5202 | Jurain | Postogola 33/11KV S/S | 2393972.4885
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 34480101 | 36547113 | 2067012 | 1 | 0 | 2067012 | 2071894.6482 | Jurain | Postogola 33/11KV S/S | 1933992.5359
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 3547.1 | 5929.5 | 2382.4 | 1000 | 0 | 2382400 | 2388027.6504 | Jurain | Postogola 33/11KV S/S | 2351667.7366
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 52807093 | 54442479 | 1635386 | 1 | 0 | 1635386 | 1639249.0712 | Postogola | Postogola 33/11KV S/S | 1571920.5306
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52708936 | 52971025 | 262089 | 1 | 0 | 262089 | 262708.1006 | Postogola | Postogola 33/11KV S/S | 303872.8913
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 | 0 | ELIB67385 | 1 | 243.19 | 314.92 | 71.73 | 80 | 0 | 5738.4 | 5751.9551 | Postogola | Postogola 33/11KV S/S | 4375.6621
1 | 11 kV Feeder-1 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0
2 | 11 kV Feeder-2 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0
3 | 11 kV Dholaikal RMU | 11 | 0 | DHK60970 | 1 | 158004.4 | 190281.3 | 32276.9 | 60 | 0 | 1936614 | 1942348.072 | Banglabazar | IG Gate GIS 33/11 kV | 1890634.7965
4 | 11 kV Alom Gonj | 11 | 0 | DHK60894 | 1 | 460143.7 | 469945.6 | 9801.9 | 60 | 0 | 588114 | 589855.3321 | Postogola | IG Gate GIS 33/11 kV | 589628.102
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 | 0 | DHK60895 | 1 | 475941.2 | 505725.6 | 29784.4 | 60 | 0 | 1787064 | 1792355.2732 | Postogola | IG Gate GIS 33/11 kV | 1711977.4089
6 | 11 kV Farashgonj Feeder (F-6) | 11 | 0 | DHK68133 | 1 | 3530.25 | 3559.31 | 29.06 | 60000 | 0 | 1743600 | 1748762.5817 | Banglabazar | IG Gate GIS 33/11 kV | 1815572.1775
7 | 11 kV Doyaganj | 11 | 0 | DHK68134 | 1 | 2322.27 | 2352.51 | 30.24 | 60000 | 0 | 1814400 | 1819772.2117 | Swamibag | IG Gate GIS 33/11 kV | 1955417.8504
10 | 11 kV Faridabad | 11 | 0 | DHK68140 | 1 | 730.03 | 751.51 | 21.48 | 60000 | 0 | 1288800 | 1292615.9757 | Postogola | IG Gate GIS 33/11 kV | 1233789.9626
11 | 11 kV Gandaria | 11 | 0 | DHK60969 | 1 | 300077.81 | 336244.2 | 36166.39 | 60 | 0 | 2169983.4 | 2176408.4497 | Postogola | IG Gate GIS 33/11 kV | 2008723.2675
12 | 11 kV Walter Road | 11 | 0 | DHK68136 | 1 | 926.56 | 950.44 | 23.88 | 60000 | 0 | 1432800 | 1437042.3417 | Banglabazar | IG Gate GIS 33/11 kV | 1402694.4766
13 | 11 kV Murgitola Feeder (F-11) | 11 | 0 | DHK68138 | 1 | 3813.73 | 3852.58 | 38.85 | 60000 | 0 | 2331000 | 2337901.7997 | Swamibag | IG Gate GIS 33/11 kV | 2438521.0841
14 | 11 kV Feeder-12 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0
15 | 11 kV Begumgonj Feeder (F-13) | 11 | 0 | DHK60899 | 1 | 609124.4 | 638057.1 | 28932.7 | 60 | 0 | 1735962 | 1741101.9665 | Swamibag | IG Gate GIS 33/11 kV | 1809148.9629
16 | 11 kV Lohar Pool Feeder (F-14) | 11 | 0 | DHK60967 | 1 | 132216.8 | 148948.3 | 16731.5 | 60 | 0 | 1003890 | 1006862.3928 | Postogola | IG Gate GIS 33/11 kV | 984580.1304
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB2774 | 1 | 276011 | 277674 | 1663 | 1 | 0 | 1663 | 1667.9239 | Postogola | IG Gate GIS 33/11 kV | 1718.3058
1 | Nizambag | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1000528.2 | 1008260.1492 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 972380.6635
2 | Merry Stopes | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 353127.6 | 355856.5232 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 364642.7488
3 | Mujibur Ghat | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1294801.2 | 1304807.2519 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1337023.4124
4 | Madrasa | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1530219.6 | 1542044.934 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1701666.1612
5 | Thana | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1412510.4 | 1423426.093 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1337023.4124
6 | Al-Hera | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0
7 | Waz Uddin School | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 823964.4 | 830331.8876 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 972380.6635
8 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0
10 | Bashundhara City | 33 | 0 | 660434 | 1 | 739.39 | 753.18 | 13.79 | 180000 | 0 | 2482200 | 2480389.347 | Shere b.nagar | Moghbazar 132/33/11KV S/S | 2161081.9864
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4469.84 | 4500.27 | 30.43 | 240000 | 0 | 7303200 | 7317548.4229 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 5615154.9463
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 353746.5 | 357772.9 | 4026.4 | 2000 | 0 | 8052800 | 8068621.1441 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 8850787.3005
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1006.87 | 1008.73 | 1.86 | 240000 | 0 | 446400 | 446400 | Siddirgonj | Demra 33/11KV S/S | 0
11 | 33 kV ACI Pharmacuticles Feeder | 33 | 0 | DHKC4791 | 1 | 874.23 | 885.85 | 11.62 | 90000 | 0 | 1045800 | 1045800 | N.Gonj (East) | Khanpur 33/11KV S/S | 0
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC | 0 | 1 | 9902.221 | 9902.222 | 0.001 | 1000 | From Customer End | 10962.5847 | 11038.2598 | Matuail | Matuail 132/33 KV S/S | 10991.7418
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 36660.866 | 37583.454 | 922.588 | 1000 | 0 | 922588 | 923421.8011 | Sytalakhya | Sitalakhya 132/33KV S/S | 1229303.7954
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S | 0
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4621.1 | 4646.3 | 25.2 | 160 | 0 | 4032 | 4035.644 | Sytalakhya | Sitalakhya 132/33KV S/S | 2848.7249
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 269.79 | 288.61 | 18.82 | 360000 | 0 | 6775200 | 6815752.3123 | Sytalakhya | Char Syedpur 132/33KV S/S | 6616060.3155
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 87.04 | 93.75 | 6.71 | 360000 | 0 | 2415600 | 2430058.343 | Sytalakhya | Char Syedpur 132/33KV S/S | 2458012.5886
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 39.89 | 42.67 | 2.78 | 360000 | 0 | 1000800 | 1006790.1928 | Sytalakhya | Char Syedpur 132/33KV S/S | 1108090.8439
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 405.16 | 434.74 | 29.58 | 360000 | 0 | 10648800 | 10712537.375 | Sytalakhya | Char Syedpur 132/33KV S/S | 10817421.0397
1 | 11 KV Shahidbagh Feeder | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 35808 | 36416.7693 | Rajarbag | Santinagar Switching S/S | -3994.0825
2 | 11 Fortune(MogBazar)-new | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 125532 | 127666.1608 | Moghbazar | Santinagar Switching S/S | 126229.899
3 | Centerpoint-Kakrail | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 80400 | 81766.8748 | Kakrail | Santinagar Switching S/S | 80846.9863
1 | 11 KV Shyamoli O/H | 11 | 0 | DHK-15026 | 1 | 9151.97 | 9164.92 | 12.95 | 40000 | 0 | 518000 | 530950 | Shere b.nagar | Agargaon 33/11 KV S/S
2 | 11 KV Nearest RMU | 11 | 0 | DHK-15027 | 1 | 3855.49 | 3859.52 | 4.03 | 40000 | 0 | 161200 | 165230 | Shere b.nagar | Agargaon 33/11 KV S/S
3 | 11 KV Sher-e-bangla Nagar | 11 | 0 | DHK-15025 | 1 | 3975.03 | 3976.15 | 1.12 | 40000 | 0 | 44800 | 45920 | Shere b.nagar | Agargaon 33/11 KV S/S
| Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13837.5 | -13837.5 | Shere b.nagar | Agargaon 33/11 KV S/S
| 33/0.4 kV, 500 kVA AT-1 | 0.4 | 0 | 84.2659 | 1 | 311229 | 313699 | 2470 | 10 | 0 | 24700 | 24707.6715 | Paribag | Dhanmondi 33/11KV S/S
| 33/0.4 kV, 1000 kVA AT-2 | 0.4 | 0 | 84.2673 | 1 | 478688 | 478688 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S
| 33 KV Japan Genden City | 33 | 0 | DHK15681 | 1 | 273.18 | 358.27 | 85.09 | 18000 | 0 | 1531620 | 1531620 | Adabor | Japan Garden 33/11 KV
| 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKE6223 | 1 | 42637.18 | 42845.32 | 208.14 | 120 | 0 | 24976.8 | 25361.4506 | Kamrangirchar | Kamrangirchar 33/11KV S/S
| 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar 33/11KV S/S
| AT-1 | 0.415 | 0 | 0 | 1 | 238.06 | 357.37 | 119.31 | 80 | 0 | 9544.8 | 9911.7899 | Mugdapara | Madarteck 33/11KV S/S
| AT-2 | 0.415 | 0 | 63394003 | 1 | 89.44 | 157.43 | 67.99 | 80 | 0 | 5439.2 | 5648.3329 | Mugdapara | Madarteck 33/11KV S/S
7 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 531.04 | 550.9 | 19.86 | 360000 | 0 | 7149600 | 7145780.8426 | Kazla | Kazla 132/133 KV SS
8 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 577.58 | 602.93 | 25.35 | 360000 | 0 | 9126000 | 9121125.0936 | Kazla | Kazla 132/133 KV SS
44 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20118 | 20647 | 529 | 2000 | 0 | 1058000 | 1062218.4705 | Maniknagar | Maniknagar 132/33 KV SS
| Axuxilary -1 | 0.415 | 0 | AH14044078 | 1 | 391339 | 397817.5 | 6478.5 | 1 | 0 | 6478.5 | 6475.0369 | Maniknagar | Maniknagar 132/33/11KV S/S
| Axuxilary -2 | 0.415 | 0 | AH14044072 | 1 | 364399.6 | 369244.1 | 4844.5 | 1 | 0 | 4844.5 | 4841.9103 | Maniknagar | Maniknagar 132/33/11KV S/S
1 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 705.0729 | 715.3204 | 10.2475 | 240000 | 0 | 2459400 | 2460914.9302 | Shyampur | Shyampur 132/33KV S/S
11 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 619.8515 | 629.3505 | 9.499 | 240000 | 0 | 2279760 | 2281164.2763 | Shyampur | Shyampur 132/33KV S/S
12 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1058.144 | 1102.925 | 44.781 | 240000 | 0 | 10747440 | 10754060.1599 | Shyampur | Shyampur 132/33KV S/S
18 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 123.986 | 129.9924 | 6.0064 | 240000 | 0 | 1441536 | 1442423.9509 | Shyampur | Shyampur 132/33KV S/S
20 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1461.395 | 1488.4699 | 27.0749 | 240000 | 0 | 6497976 | 6501978.5941 | Shyampur | Shyampur 132/33KV S/S
24 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2295.02 | 2331.0006 | 35.9806 | 240000 | 0 | 8635344 | 8640663.1605 | Shyampur | Shyampur 132/33KV S/S
17 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 669.723 | 672.5319 | 2.8089 | 240000 | Prime Textile | 674136 | 674551.2513 | Fatullah | Shyampur 132/33KV S/S
23 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 337.075 | 341.169 | 4.094 | 2400 | 0 | 10071.24 | 10071.24 | Fatullah | Shyampur 132/33KV S/S
24 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 82.99 | 87.479 | 4.489 | 2400 | 0 | 11042.94 | 11042.94 | Fatullah | Shyampur 132/33KV S/S
1 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 237.068 | 256.333 | 19.265 | 480000 |  | 9239520 | 9239520 | Sytalakhya | MI CEMENT 132/33 kV
12 | 33 kV Shah Cement Feeder | 33 | 0 | 8993841 | 1 | 39195.806 | 39285.417 | 89.611 | 36000 | 733 | 3225996 | 3226729 | Sytalakhya | Madonganj 132/33 KV SS
13 | 33 kV Mondol Para (Premire cement) Feeder | 33 | 0 | 8993842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS
| RMU-1 Feeder | 11 | 0 | BD013940 | 1 | 0 | 146.76 | 146.76 | 1000 | 0 | 146760 | 151506.8204 | Shere b.nagar | Monipuripara 33/11 KV S/S

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month June-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month June-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.07.2023 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 9560287.9373 | 20208348.1599 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 7244852.759 |  | North | 308071159.3022 | Tejgaon | 59880815.8004 | Tejgaon | 32859668.0006 | 33009538.7975 | -149870.7969 | -0.45402 | North | 308071159.3022 | 274698202.36 | 10.8329 | Tejgaon | 59880815.8004 | 56363916 | 5.8732 | Tejgaon | 32859668.0006 | 31707881 | 3.5052 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 544550.7215 | [5 empty] | Kakrail | 27021147.7998 | 26094458.147 | 926689.6528 | 3.5513 | [8 empty] | Kakrail | 27021147.7998 | 24656035 | 8.7528 | 2 | Tejgaon | 31707881 | 158656 | 31866537 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | -1007536.639
|  |  |  | Maghbazar | 2858656.742 |  |  |  | Moghbazar | 37799486.5534 | Moghbazar | 20914248.216 | 19191663.6958 | 1722584.5202 | 8.9757 |  |  |  |  | Moghbazar | 37799486.5534 | 32799837 | 13.2268 | Moghbazar | 20914248.216 | 18182320 | 13.0625 | 3 | Kakrail | 24656035 | 171692 | 24827727 | A1 | Motijheel | 21032591 | 180512 | 21213103
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 14308442.6387 |  |  |  |  | Khilgaon | 16885238.3373 | 15814616.5953 | 1070621.742 | 6.7698 | [8 empty] | Khilgaon | 16885238.3373 | 14617517 | 13.4302 | 4 | Moghbazar | 18182320 | 108541 | 18290861 | A2 | Khilgaon | 14617517 | 126930 | 14744447
|  |  |  | Jigatola | 2764606.2224 |  |  |  | Satmasjid | 48516990.4852 | Satmosjid | 23263785.2371 | 21874027.2652 | 1389757.9719 | 6.3535 |  |  |  |  | Satmasjid | 48516990.4852 | 42580912 | 12.2351 | Satmosjid | 23263785.2371 | 20586218 | 11.5096 | 5 | Khilgaon | 14617517 | 126930 | 14744447 | A3 | Lalbag | 32348524 | 29808 | 32378332
|  |  |  | Paribagh | 11543836.4163 | [5 empty] | Sherebanglanagar | 25253205.2481 | 23841857.0802 | 1411348.1679 | 5.9196 | [8 empty] | Sherebangla nagar | 25253205.2481 | 21994694 | 12.9034 | 6 | Satmosjid | 20586218 | 69986 | 20656204 | A4 | Kazla | 40348198 | 83854 | 40432052
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 15393240 |  |  | Dhanmondi | 53314716.2602 | Dhanmondi | 24559325.7701 | 23157735.0016 | 1401590.7685 | 6.0524 |  |  |  |  | Dhanmondi | 53314716.2602 | 48713574.98 | 8.6302 | Dhanmondi | 24559325.7701 | 22565841 | 8.117 | 7 | Sherebanglanagar | 21994694 | 177417 | 22172111 | A5 | Postogola | 14337348 | 103284 | 14440632
[11 empty] | Jhigatala | 28755390.4901 | 27497787.9591 | 1257602.531 | 4.5735 | [8 empty] | Jhigatala | 28755390.4901 | 26147733.98 | 9.0684 | 8 | Dhanmondi | 22565841 | 85074 | 22650915 | A6 | Banglabazar | 15581064 | 53984 | 15635048
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 56001325.4318 | Azimpur | 19894403.1357 | 19273690.4419 | 620712.6939 | 3.2205 |  |  |  |  | Azimpur | 56001325.4318 | 49311265.38 | 11.9463 | Azimpur | 19894403.1357 | 17615715 | 11.4539 | 9 | Jhigatala | 26147733.98 | 242541.6706 | 26390275.6506 | A7 | N.Gonj (West) | 29979099 | 162575 | 30141674
|  |  |  | Dhanmondi | 15393240 | [5 empty] | Paribagh | 36106922.2961 | 33925839.4802 | 2181082.8159 | 6.429 | [8 empty] | Paribagh | 36106922.2961 | 31695550.38 | 12.2175 | 10 | Azimpur | 17615715 | 84677 | 17700392 | A8 | Siddirgonj | 45619403 | 359101 | 45978504
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 21807280.959 | 21807280.959 |  |  | Shamoly | 52557824.7712 | Shyamoli | 18566131.7394 | 18283221.4148 | 282910.3246 | 1.5474 |  |  |  |  | Shamoly | 52557824.7712 | 44928697 | 14.5157 | Shyamoli | 18566131.7394 | 16718023 | 9.9542 | 11 | Paribagh | 31695550.38 | 255283.5864 | 31950833.9664 | A9 | Bashabo | 12611121 | 37574 | 12648695
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 14995756.0431 |  |  |  |  | Adabor | 33991693.0318 | 31334492.2359 | 2657200.7959 | 8.4801 | [8 empty] | Adabor | 33991693.0318 | 28210674 | 17.0072 | 12 | Shyamoli | 16718023 | 72417 | 16790440 | B1 | Narinda | 13913312 | 133778 | 14047090
|  |  |  | RAMNA | 1403142.5867 |  | Central | 274821069.637 | Lalbagh | 76163211.7323 | Lalbagh | 35248383.1173 | 36512406.1293 | -1264023.012 | -3.4619 | Central | 274821069.637 | 246642439.82 | 10.2534 | Lalbagh | 76163211.7323 | 71827948 | 5.6921 | Lalbagh | 35248383.1173 | 32348524 | 8.2269 | 13 | Adabor | 28210674 | 352167 | 28562841 | B2 | Maniknagar | 17973194 | 150970 | 18124164
|  |  |  | Kakrail | 1731600.9777 | [5 empty] | Kamrangirchar | 40914828.615 | 41297895.4236 | -383066.8086 | -0.92757 | [8 empty] | Kamrangirchar | 40914828.615 | 39479424 | 3.5083 | 14 | Lalbagh | 32348524 | 29808 | 32378332 | B3 | Jurain | 27240834 | 329722 | 27570556
|  |  |  | Paribagh | 11861012.4787 |  |  |  | Ramna | 47622503.1358 | Ramna | 28263881.9666 | 27950585.9269 | 313296.0397 | 1.1209 |  |  |  |  | Ramna | 47622503.1358 | 42102875 | 11.5904 | Ramna | 28263881.9666 | 25224461 | 10.7537 | 15 | Kamrangirchar | 39479424 | 109154 | 39588578 | B4 | Shyampur | 69895627 | 289766 | 70185393
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 3584312.8959 |  |  |  |  | Rajarbagh | 19358621.1692 | 18065624.986 | 1292996.1832 | 7.1572 | [8 empty] | Rajarbagh | 19358621.1692 | 16878414 | 12.8119 | 16 | Ramna | 25224461 | 474835 | 25699296 | B5 | Swamibag | 13215953.82 | 23775 | 13239728.82
|  |  |  | Kakrail | 190247.4883 |  |  |  | Bashabo | 41068369.3915 | Bashabo | 14863749.6586 | 14134545.9205 | 729203.7381 | 5.159 |  |  |  |  | Bashabo | 41068369.3915 | 34702046 | 15.5018 | Bashabo | 14863749.6586 | 12611121 | 15.1552 | 17 | Rajarbagh | 16878414 | 82496 | 16960910 | B6 | Bangshal | 17387477 | 73977 | 17461454
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 26204619.7329 | 23898161.7109 | 2306458.022 | 9.6512 | [8 empty] | Bonossri | 26204619.7329 | 22090925 | 15.6984 | 18 | Bashabo | 12611121 | 37574 | 12648695 | B7 | N.Gonj (East) | 29106385 | 385947 | 29492332
|  |  |  | Shere Bangla Nagar | 3394065.4076 |  |  |  | Motijheel | 42154741.0779 | Motijheel | 22841984.5538 | 22370326.0361 | 471658.5177 | 2.1084 |  |  |  |  | Motijheel | 42154741.0779 | 37911764 | 10.0652 | Motijheel | 22841984.5538 | 21032591 | 7.9214 | 19 | Bnossri | 22090925 | 70927 | 22161852 | B8 | Fateullah | 31615717 | 560066 | 32175783
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1280479.5819 | 8134897.1655 |  |  |  |  | Mughdapara | 19312756.5241 | 18048010.2028 | 1264746.3213 | 7.0077 | [8 empty] | Mughdapara | 19312756.5241 | 16879173 | 12.6009 | 20 | Motijheel | 21032591 | 180512 | 21213103 | B9 | Mugdapara | 16879173 | 58942 | 16938115
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 37471964.0256 | Banglabazar | 17151582.8188 | 16832238.2088 | 319344.61 | 1.8972 |  |  |  |  | Banglabazar | 37471964.0256 | 32968541 | 12.0181 | Banglabazar | 17151582.8188 | 15581064 | 9.1567 | 21 | Mughdapara | 16879173 | 58942 | 16938115 | C1 | Tejgaon | 31707881 | 158656 | 31866537
|  |  |  | Narinda | 427872.7434 | [5 empty] | Bongshal | 20320381.2069 | 19304876.681 | 1015504.5258 | 5.2604 | [8 empty] | Bongshal | 20320381.2069 | 17387477 | 14.4333 | 22 | Banglabazar | 15581064 | 53984 | 15635048 | C2 | Satmasjid | 20586218 | 69986 | 20656204
|  |  |  | Motijheel | 481492.0598 |  |  |  | Narinda | 30340280.2738 | Narinda | 15337870.9921 | 14569881.1136 | 767989.8785 | 5.2711 |  |  |  |  | Narinda | 30340280.2738 | 27129265.82 | 10.5833 | Narinda | 15337870.9921 | 13913312 | 9.2879 | 23 | Bongshal | 17387477 | 73977 | 17461454 | C3 | Paribagh | 31695550.38 | 255283.5864 | 31950833.9664
|  |  |  | RAMNA | 5945052.7804 | [5 empty] | Swamibagh | 15002409.2817 | 14638867.6103 | 363541.6714 | 2.4834 | [8 empty] | Swamibagh | 15002409.2817 | 13215953.82 | 11.9078 | 24 | Narinda | 13913312 | 133778 | 14047090 | C6 | Kakrail | 24656035 | 171692 | 24827727
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 433060827.1342 | Kazla | 58855365.1907 | Kazla | 37908086.6755 | 41076724.8443 | -3168638.1688 | -7.714 | South | 433060827.1342 | 413467981 | 4.5243 | Kazla | 58855365.1907 | 58321392 | 0.90726 | Kazla | 37908086.6755 | 40348198 | -6.4369 | 25 | Swamibagh | 13215953.82 | 23775 | 13239728.82 | D1 | Moghbazar | 18182320 | 108541 | 18290861
|  | Khillgaon 33/11KV S/S |  | Kakrail | 81766.8748 | 6591600 |  |  |  |  | Maniknagar | 20947278.5152 | 20369532.5037 | 577746.0115 | 2.8363 | [8 empty] | Maniknagar | 20947278.5152 | 17973194 | 14.198 | 26 | Kazla | 40348198 | 83854 | 40432052 | D2 | Dhanmondi | 22565841 | 85074 | 22650915
|  |  |  | Khilgaon | 1220.4011 |  |  |  | Shyampur | 94155014.6658 | Shyampur | 70064491.3479 | 71611732.1812 | -1547240.8333 | -2.1606 |  |  |  |  | Shyampur | 94155014.6658 | 90489911 | 3.8926 | Shyampur | 70064491.3479 | 69895627 | 0.24101 | 27 | Maniknagar | 17973194 | 150970 | 18124164 | D3 | Ramna | 25224461 | 474835 | 25699296
| 9 |  |  | Maghbazaar | 127666.1608 | [5 empty] | Matuail | 24090523.3179 | 23414723.2501 | 675800.0678 | 2.8862 | [8 empty] | Matuail | 24090523.3179 | 20594284 | 14.5129 | 28 | Shyampur | 69895627 | 289766 | 70185393 | D4 | Shyamoli | 16718023 | 72417 | 16790440
|  |  |  | Rajarbagh | 6380946.5633 |  |  |  | Postogola | 45939329.2988 | Postogola | 16221258.1373 | 15678261.2905 | 542996.8468 | 3.4634 |  |  |  |  | Postogola | 45939329.2988 | 41578182 | 9.4933 | Postogola | 16221258.1373 | 14337348 | 11.6138 | 29 | Matuail | 20594284 | 253556 | 20847840 | D5 | Shere b.nagar | 21994694 | 177417 | 22172111
| 10 | Goran 33/11KV S/S |  | Bashabo | 1292900.8718 | 9863663.5193 |  |  |  |  | Jurain | 29718071.1615 | 29540384.3679 | 177686.7936 | 0.6015 | [8 empty] | Jurain | 29718071.1615 | 27240834 | 8.3358 | 30 | Postogola | 14337348 | 103284 | 14440632 | D6 | Rajarbag | 16878414 | 82496 | 16960910
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 62554890.3913 | Narayangonj-West | 30810293.9579 | 31820650.1222 | -1010356.1643 | -3.1752 |  |  |  |  | Narayangonj | 62554890.3913 | 59085484 | 5.5462 | Narayangonj- West | 30810293.9579 | 29979099 | 2.6978 | 31 | Jurain | 27240834 | 329722 | 27570556 | D8 | Jhigatala | 26147733.98 | 242541.6706 | 26390275.6506
|  |  |  | Banosree | 8570762.6475 | [5 empty] | Narayangonj-East | 31744596.4334 | 32234510.966 | -489914.5326 | -1.5198 | [8 empty] | Narayangonj- East | 31744596.4334 | 29106385 | 8.3107 | 32 | Narayangonj-West | 29979099 | 162575 | 30141674 | D9 | Azimpur | 17615715 | 84677 | 17700392
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 11985327.8512 | 15162035.693 |  |  | Demra | 75355983.9902 | Demra | 24103097.7168 | 23689068.4661 | 414029.2508 | 1.7478 |  |  |  |  | Demra | 75355983.9902 | 66822396 | 11.3244 | Demra | 24103097.7168 | 21202993 | 12.0321 | 33 | Narayangonj-East | 29106385 | 385947 | 29492332 | E1 | Demra | 21202993 | 145204 | 21348197
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 51252886.2733 | 49889071.0956 | 1363815.1777 | 2.7337 | [8 empty] | Siddhirgonj | 51252886.2733 | 45619403 | 10.9915 | 34 | Damra | 21202993 | 145204 | 21348197 | E2 | Matuail | 20594284 | 253556 | 20847840
|  |  |  | Bashabo | 3176707.8418 |  |  |  | Fatullah | 96200243.5974 | Fatulla | 33019604.8442 | 33687593.9843 | -667989.1401 | -1.9829 |  |  |  |  | Fatullah | 96200243.5974 | 97170616 | -1.0087 | Fatulla | 33019604.8442 | 31615717 | 4.2517 | 35 | Siddhirgonj | 45619403 | 359101 | 45978504 | E3 | Sytalakha | 65554899 | 304905 | 65859804
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 19938600 |  |  |  |  | Shitalakha | 63180638.7532 | 66193265.9901 | -3012627.2369 | -4.5513 | [8 empty] | Sytalakhya | 63180638.7532 | 65554899 | -3.7579 | 36 | Fatulla | 31615717 | 560066 | 32175783 | F1 | Kamrangirchar | 39479424 | 109154 | 39588578
|  |  |  | Shyamoli | 3098689.5466 |  | TOTAL=> | 1015953056.0733 | TOTAL=> | 1015953056.0733 | TOTAL=> | 1015953056.0733 | 1000127867.1263 | 15825188.947 | 1.5823 |  | 1015953056.0733 | 934808623.18 |  | TOTAL=> | 1015953056.0733 | 934808623.18 |  | Total=> | 1015953056.0733 | 934808623.18 | 7.987 | 37 | Shitalokko | 65554899 | 304905 | 65859804 | F2 | Banosree | 22090925 | 70927 | 22161852
|  |  |  | Shere Bangla Nagar | 0 | [23 empty] | Total => | 934808623.18 | 6364094.257 | 941172717.437 | G1 | Adabor | 28210674 | 352167 | 28562841
|  |  |  | Satmosjid | 10107303.1657 | [14 empty] | 132KV Import => |  |  |  |  | 1020742121.6706 | [8 empty] | Total => | 934808623.18 | 6364094.257 | 941172717.437
|  |  |  | Dhanmondi NOCS | 6732607.2877 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 1020742121.6706 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 1015953056.0733
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 1015953056.0733 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.46917
| 13 | Japan garden Building |  | Adabor | 1531620 | 1531620 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.46917 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 934808623.18
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 4789065.5973 | [8 empty] | System loss at 132kv level => |  |  |  |  | 8.4187
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 2164800 | 2164800
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 11544206 | 12273698.5
| 16 |  |  | Shere Bangla Nagar | 729492.5
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 25931408.9648 | 25931408.9648
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1752245.002 | 10681663.5887
|  |  |  | Lalbagh | 8929418.5867
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 8686461.9883
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 8686461.9883
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 3085830.4163 | 10912329.4176
|  |  |  | Rajarbaghl | 3159577.5517
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 4666921.4496 | 4666921.4496
|  | Banshal 33/11 KV S/S |  | Bangshal | 7584534.2816 | 10281481.1676
|  |  |  | Banglabazar | 1429747.5487
|  |  |  | Narinda | 1267199.3373
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 12795013.9533 | 17395200
|  |  |  | Shamoly | 3639615.3941
|  |  |  | Satmosjit | 960570.6526
|  | Azimpur 33/11 KV |  | jigatola | 266970.3715 | 15837922.8991
|  |  |  | Azimpur | 13443958.6555
|  |  |  | RAMNA | 1334851.8575
|  |  |  | Paribagh | 792142.0147
|  | T&T 33/11 KV |  | Kakrail | 3492418.6708 | 11315880
|  |  |  | Mogbazar | 6176905.9247
|  |  |  | Khilgaon | 1646555.4045
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 3697714.4114 | 8756214.7204
|  |  |  | Shamoly | 4384476.6993
|  |  |  | Tejgaon | 672243.3043
|  |  |  | Satmosjit | 1780.3054
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 22195327.2417 | 24514831.0168
|  |  |  | Kamrangirchar | 2319503.7751
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 4136480.5451 | 5563514.7
|  |  |  | Kakrail | 1427034.1549
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1220315.3996
|  |  |  | Shere Bangla Nagar | 1811943.9007
|  |  |  | Shamoly | 7443350.0993
|  |  |  | Satmosjit | 6300300.6004
|  | Banasree 33/11SS |  | Khilgaon | 2123404.1942
|  |  |  | Bansree | 13115356.9352 | 13115356.9352
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 1128730.4864 | 18741792
|  |  |  | Bashabo | 8364388.1427
|  |  |  | Mugdapara | 3958012.174
|  |  |  | Maniknagor | 5290661.197
|  | DMC |  | Bangshal | 2960757.4121
|  |  |  | RAMNA | 2179347.0029 | 5152139.399
|  |  |  | Lalbagh | 2972792.3961
|  | Green Road Dormatory |  | Paribagh | 8823264.0632
|  |  |  | Shere Bangla Nagar | 5744434.1464
|  | BSMMU 33/11KV S/S |  | Kakrail | 2072965.793
|  |  |  | Paribagh | 3086667.3232
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 8120853.0785
|  |  |  | Satmasjid | 5893830.5131
|  | Dhaka University 33/11 KV SS |  | RAMNA | 1855000
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 6850614.8135
|  |  |  | Kakrail | 874632.8935
|  |  |  | Tejgaon | 3135290.9782
|  | BGB 33/11 KV SS |  | Kamrangirchar | 6199189.0362
|  |  |  | Jigatola | 5419251.4855
|  |  |  | Azimpur | 4698199.4783
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2480389.347
|  | BB Avenue 33/11 KV SS |  | Narinda | 2061462.7346
|  |  |  | Ramna | 4294857.6367
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 18139762.4107
|  |  |  | Dhanmondi | 1213163.0828
|  | Ispahani 33/11 KV SS |  | Moghbazar | 3064557.4003
|  |  |  | Kakrail | 2923271.5598
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 6464726.8389
|  |  |  | Total=> | 478120948.5918 | 314938610.7875
NORTH ZONE TOTAL=>
|  | NOCS |  | 478120948.5918 |  | 200857461
|  | diff |  |  | -478120948.5918
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 6132000
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 6132000
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 653217.1868 | 17729600
|  |  |  | Swamibagh | 5711373.6072
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 11365009.206
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 10633759.3
|  |  |  | Bangshall | 40077.0255
|  |  |  | Banglabazar | 10593682.2746
| 4 | Maderteck 33/11KV S/S |  | Banosree | 4518500.1502 | 21368608.7012
|  |  |  | Bashabo | 2029752.8023
|  |  |  | Maniknagar | 674057.3744
|  |  |  | Mugdapara | 14146298.3743
| 5 | Kazla 33/11KV S/S |  | Matual | 1277473.0974 | 38938388.8611
|  |  |  | Jurain | 8956661.7502
|  |  |  | Swamibagh | 2069592.0061
|  |  |  | Maniknagar | 2521709.3876
|  |  |  | Shyampur | 2471771.8805
|  |  |  | Kazla | 21641180.7393
|  | Shyampur 132/11KV S/S |  | Shyampur | 32081205.0719 | 32776870.5031
|  |  |  | Fatullah. | 695665.4313
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 25512201.2172
|  |  |  | Fatullah | 1172708.4173
|  |  |  | Shyampur | 24339492.7999
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 5521043.5629 | 17489649.7641
|  |  |  | Jurain | 11968606.2012
| 8 | Postogola 33/11KV S/S |  | Jurain | 8792803.2102 | 18154296
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 9361492.7898
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 12240018.0342 | 13591569.7783
|  |  |  | Narayanganj (West) | 1296732.9918
|  |  |  | Shitalakhy | 1351551.7441
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 1020311.2097 | 14543719.535
|  |  |  | Shitalakhy | 9466594.8546
|  |  |  | Narayanganj (West) | 3129356.0257
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 927457.445
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 813154.9346
| 11 |  |  | Narayanganj (West) | 13592559.659 | 14405714.5935
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 15386169.567 | 15386169.567
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 13930192.4881 | 13930192.4881
|  |  |  | Matuail | 291293.3394
| 14 | Sarulia 33/11KV S/S |  | Demra | 15964656.3411 | 18520800
|  |  |  | Matuail | 2556143.6589
|  | Demra 33/11KV S/S |  | Matuail | 7387136.4971 | 23169431.1714
| 15 |  |  | Demra | 2781760.7015
|  |  |  | Siddhirganj | 13000533.9728
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1324869.236
| 16 |  |  | Narayanganj (East) | 5417450.9259 | 14252980.7389
|  |  |  | Narayanganj (West) | 8835529.8131
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 3956115.4685 | 17447146.8512
|  |  |  | Narayanganj (East) | 13491031.3827
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 4524379.1606 | 17973323.8856
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 257236.9474
|  |  |  | Fatullah | 3719785.1437
|  |  |  | Matuail | 9471922.6339
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 3226729 | 3226729
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 1062218.4705
|  |  |  | Maniknagar | 10745414.8989 | 10745414.8989
|  | IG Gate 33/11 kv |  | Swamibagh | 5898775.9779 | 17886694.3208
|  |  |  | Banglabazr | 5128152.9955
|  |  |  | Postogola | 6859765.3474
|  | Motijil 33/11kv |  | kamlapur | 6888388.4677 | 7258156.5898
|  |  |  | RAMNA | 369768.1221
|  | Mitford 33/11kv |  | Banshal | 8454532.9058 | 9605377.7985
|  |  |  | Lalbagh | 1150844.8928
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 5393741.0854 | 12893297.0663
|  |  |  | Fatullah | 4393001.8897
|  |  |  | Matuail | 3106554.0912
|  | MI CEMENT |  | Shitalakhy | 9239520 | 9239520
|  | Dapa 33/11 kV |  | Fatullah | 10798425.928 | 10798425.928
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7291423.7545 | 16227414
|  |  |  | Siddhirganj | 8935990.2455
|  | Amulia 33/11 KV SS |  | Mugdapara | 1208445.9758 | 6565126.6501
|  |  |  | Demra | 5356680.6743
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 11234871.3019
|  | P&T 33/11 KV SS |  | Motijeel | 3723930.1462
|  |  |  | RAMNA | 3659551.0189
|  |  |  | Rajarbagh | 3282631.3469
|  | Kazla 132/33 KV SS |  | Kazla | 16266905.9361
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 6535465.7074
|  |  |  | Motijeel | 2944324.8871
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 25595890.2369
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 2671848.993
|  |  |  | Swamibagh | 1322667.6905
|  |  |  | Narinda | 216326.9708
|  |  |  | Total=> | 537832107.4815 | 422811612.63
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 537832107.4815
| Diff zone&Nocs |  |  |  | -25232865.1564
|  |  |  | Diff= | 0

## Sheet2
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2184.48 | 2210.16 | 25.68 | 720000 | 18489600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2158.72 | 2179.89 | 21.17 | 720000 | 15242400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1864.35 | 1898.61 | 34.26 | 720000 | 24667200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1762.32 | 1780.89 | 18.57 | 480000 | 8913600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2024.03 | 2052.39 | 28.36 | 240000 | 0 | 6806400 | 6808513.9804 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2315.96 | 2349.96 | 34 | 240000 | 0 | 8160000 | 8162534.3912 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1435.41 | 1451.13 | 15.72 | 240000 | 0 | 3772800 | 3773971.7832 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 782.32 | 804.13 | 21.81 | 240000 | 0 | 5234400 | 5236025.7374 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1811.32 | 1826.25 | 14.93 | 240000 | 0 | 3583200 | 3584312.8959 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1164.56 | 1176.39 | 11.83 | 240000 | 0 | 2839200 | 2840081.8191 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 377.52 | 391.38 | 13.86 | 240000 | 0 | 3326400 | 3327433.1371 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2031.88 | 2059.78 | 27.9 | 240000 | 0 | 6696000 | 6698079.6916 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1565.51 | 1589.15 | 23.64 | 240000 | 0 | 5673600 | 5675362.1473 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 679.62 | 694.88 | 15.26 | 240000 | 0 | 3662400 | 3663537.4944 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1906.63 | 1942.41 | 35.78 | 240000 | 0 | 8587200 | 8589867.074 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1804.37 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 139.74 | 145.23 | 5.49 | 240000 | 0 | 1317600 | 1318009.2296 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1347.73 | 1379.43 | 31.7 | 240000 | 0 | 7608000 | 7610362.9471 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2184.48 | 2210.16 | 25.68 | 720000 | 18489600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2158.72 | 2179.89 | 21.17 | 720000 | 15242400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1864.35 | 1898.61 | 34.26 | 720000 | 24667200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1762.32 | 1780.89 | 18.57 | 480000 | 8913600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2024.03 | 2052.39 | 28.36 | 240000 | 0 | 6806400 | 6808513.9804 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2315.96 | 2349.96 | 34 | 240000 | 0 | 8160000 | 8162534.3912 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1435.41 | 1451.13 | 15.72 | 240000 | 0 | 3772800 | 3773971.7832 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 782.32 | 804.13 | 21.81 | 240000 | 0 | 5234400 | 5236025.7374 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1811.32 | 1826.25 | 14.93 | 240000 | 0 | 3583200 | 3584312.8959 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1164.56 | 1176.39 | 11.83 | 240000 | 0 | 2839200 | 2840081.8191 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 377.52 | 391.38 | 13.86 | 240000 | 0 | 3326400 | 3327433.1371 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2031.88 | 2059.78 | 27.9 | 240000 | 0 | 6696000 | 6698079.6916 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1565.51 | 1589.15 | 23.64 | 240000 | 0 | 5673600 | 5675362.1473 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 679.62 | 694.88 | 15.26 | 240000 | 0 | 3662400 | 3663537.4944 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1906.63 | 1942.41 | 35.78 | 240000 | 0 | 8587200 | 8589867.074 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1804.37 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 139.74 | 145.23 | 5.49 | 240000 | 0 | 1317600 | 1318009.2296 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1347.73 | 1379.43 | 31.7 | 240000 | 0 | 7608000 | 7610362.9471 | 0 | Dhanmondi 132/33/11KV S/S