## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month December-2023 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 766 | 1 | 960000 | 2234.461 | 2234.461 | 0 |  | 0 | 1951.095 | 1951.095 | 0 |  | 0 | 0 | 0 | 0.95 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 667.558 | 667.558 | 0 | 0 |  | 379.591 | 379.591 | 0 | 0 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 402.926 | 421.365 | 18.439 |  | 17701440 | 181.302 | 189.851 | 8.549 |  | 8207040 | 17701440 | 8207040 | 0.91 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 165.737 | 170.689 | 4.952 |  | 4753920 | 55.775 | 56.966 | 1.191 |  | 1143360 | 4753920 | 1143360 | 0.97 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | HASNABAD –FATULLAH (New) |  | 132 | Exp | 5972 3848 | 1 | 960000 | 6.982 | 11.904 | 4.922 |  | 4725120 | 6.834 | 15.633 | 8.799 |  | 8447040 | 2925120 | 7080000 | 0.95 |  | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 0.242 | 2.117 | 1.875 | 1800000 |  | 0.142 | 1.566 | 1.424 | 1367040 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 1800000 | 27180480 |  |  | Total=> | 1367040 | 17797440 | 25380480 | 16430400 | 0.84 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 8993 624 | 1 | 960000 | 4885.436 | 4892.631 | 7.195 |  | 6907200 | 2405.774 | 2408.028 | 2.254 |  | 2163840 | 6907200 | 2163840 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 11.083 | 11.083 | 0 | 0 |  | 7.816 | 7.816 | 0 | 0 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 6907200 |  |  | Total=> | 0 | 2163840 | 6907200 | 2163840 | 0.95 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 8993 518 | 1 | 960000 | 1188.499 | 1202.084 | 13.585 |  | 13041600 | 786.614 | 790.862 | 4.248 |  | 4078080 | 13041600 | 4074240 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 70.101 | 70.101 | 0 | 0 |  | 141.182 | 141.186 | 0.004 | 3840 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 366.009 | 379.667 | 13.658 |  | 13111680 | 141.385 | 145.634 | 4.249 |  | 4079040 | 13111680 | 3962880 | 0.96 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.408 | 4.408 | 0 | 0 |  | 30.499 | 30.62 | 0.121 | 116160
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 0 | 26153280 |  |  | Total=> | 120000 | 8157120 | 26153280 | 8037120 | 0.96
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 2986.08 | 3017.096 | 31.016 |  | 14887680 | 1210.475 | 1220.42 | 9.945 |  | 4773600 | 14887680 | 4773600 | 0.95 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8576.821 | 8605.814 | 28.993 |  | 13916640 | 5014.301 | 5028.562 | 14.261 |  | 6845280 | 13916640 | 6845280 | 0.9 | 0 | 0
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8529.331 | 8558.906 | 29.575 |  | 14196000 | 4973.939 | 4988.481 | 14.542 |  | 6980160 | 14196000 | 6980160 | 0.9 | 0 | 0
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 375.942 | 400.476 | 24.534 |  | 11776320 | 71.576 | 76.066 | 4.49 |  | 2155200 | 11776320 | 2155200 | 0.98 | 0 | 0
[10 empty] | Total=> | 0 | 54776640 |  |  | Total=> | 0 | 20754240 | 54776640 | 20754240 | 0.94
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 8993 683 | 1 | 960000 | 8481.316 | 8508.189 | 26.873 |  | 25798080 | 4712.021 | 4723.799 | 11.778 |  | 11306880 | 25798080 | 11306880 | 0.92 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 8993 682 | 1 | 960000 | 8470.688 | 8497.485 | 26.797 |  | 25725120 | 4706.454 | 4718.257 | 11.803 |  | 11330880 | 25725120 | 11330880 | 0.92 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 59723527 | 1 | 1440000 | 0 | 3.198 | 3.198 |  | 13439520 | 1389.481 | 1390.225 | 0.744 |  | 1071360 | 13439520 | 1071360 | 1 | 0 | 0 |  | Old Meter 8834400 Units Added
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 59723528 | 1 | 1440000 | 0 | 0 | 0 |  | 0 | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | New Meter
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 8993 555 | 1 | 1440000 | 2894.06 | 2917.64 | 23.58 |  | 33955200 | 1345.175 | 1354.413 | 9.238 |  | 13302720 | 33955200 | 13302720 | 0.93 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 771.699 | 771.699 | 0 | 0 |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 0 | 98917920 |  |  | Total=> | 0 | 37011840 | 98917920 | 37011840 | 0.94 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993 631 | 1 | 960000 | 5948.831 | 5970.835 | 22.004 |  | 21123840 | 3028.686 | 3037.274 | 8.588 |  | 8244480 | 21123840 | 8244480 | 0.93 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993 659 | 1 | 960000 | 5064.126 | 5080.769 | 16.643 |  | 15977280 | 2567.33 | 2573.683 | 6.353 |  | 6098880 | 15977280 | 6098880 | 0.93 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4448.367 | 4458.841 | 10.474 |  | 10055040 | 1774.761 | 1775.791 | 1.03 |  | 988800 | 10055040 | 988800 | 1 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.561 | 1.561 | 0 | 0 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993 660 | 1 | 960000 | 4130.91 | 4140.621 | 9.711 |  | 9322560 | 1638.966 | 1640.126 | 1.16 |  | 1113600 | 9322560 | 1104960 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.33 | 1.33 | 0 | 0 |  | 5.269 | 5.278 | 0.009 | 8640 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 5014 6667 | 1 | 960000 | 1886.879 | 1904.258 | 17.379 |  | 16683840 | 693.714 | 699.922 | 6.208 |  | 5959680 | 16683840 | 5959680 | 0.94 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 5014 6668 | AMR | 960000 | 1680.527 | 1697.667 | 17.14 |  | 16454400 | 718.856 | 725.022 | 6.166 |  | 5919360 | 16454400 | 5919360 | 0.94 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 4262 7810 | 1 | 960000 | 214.859 | 232.688 | 17.829 |  | 17115840 | 3.91 | 4.431 | 0.521 |  | 500160 | 17115840 | 500160 | 1 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 70.933 | 72.286 | 1.353 | 1298880 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 4262 7812 | 1 | 960000 | 217.013 | 235.042 | 18.029 |  | 17307840 | 2.775 | 3.118 | 0.343 |  | 329280 | 17307840 | 329280 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 75.351 | 76.984 | 1.633 | 1567680
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 0 | 124040640 |  |  | Total=> | 2875200 | 29154240 | 124040640 | 26279040 | 0.98 |  | 0
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3356.292 | 3386.62 | 30.328 |  | 58229760 | 1679.108 | 1688.977 | 9.869 |  | 18948480 | 58229760 | 18948480 | 0.95 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3347.682 | 3377.577 | 29.895 |  | 57398400 | 1675.926 | 1685.657 | 9.731 |  | 18683520 | 57398400 | 18683520 | 0.95 | 0 | 0
[10 empty] | Total=> |  | 115628160 |  |  | Total=> | 0 | 37632000 | 115628160 | 37632000 | 0.95
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1593.217 | 1632.528 | 39.311 |  | 75477120 | 772.967 | 786.653 | 13.686 |  | 26277120 | 75477120 | 26277120 | 0.95 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
|  |  | Calculated Unit for 230/132kV T-1 due to R-phase PT Missing | [8 empty] | 0 |  |  |  |  | 0
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1683.807 | 1722.931 | 39.124 |  | 75118080 | 813.34 | 827.085 | 13.745 |  | 26390400 | 75118080 | 26390400 | 0.95 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 150595200 |  |  | Total=> | 0 | 52667520 | 150595200 | 52667520 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 1025.378 | 1052.817 | 27.439 |  | 39512160 | 216.288 | 220.551 | 4.263 |  | 6138720 | 39512160 | 5927040 | 0.99 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.021 | 0 | 0 |  | 0.894 | 1.041 | 0.147 | 211680
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 752.493 | 780.158 | 27.665 |  | 39837600 | 320.715 | 332.699 | 11.984 |  | 17256960 | 39837600 | 17256960 | 0.92 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.838 | 0.838 | 0 | 0 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 0 | 79349760 |  |  | Total=> | 211680 | 23395680 | 79349760 | 23184000 | 0.96
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 306.632 | 317.589 | 10.957 |  | 10518720 | 78.091 | 80.348 | 2.257 |  | 2166720 | 10518720 | 2166720 | 0.98 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 237.944 | 256.733 | 18.789 |  | 18037440 | 54.336 | 58.838 | 4.502 |  | 4321920 | 18037440 | 4321920 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 33.859 | 34.145 | 0.286 |  | 274560 | 16.247 | 16.299 | 0.052 |  | 49920 | -37701120 | -20037120 | 0.95 | 0 | 0 | Loop PFC is Considered
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 105.155 | 144.713 | 39.558 | 37975680 |  | 88.645 | 109.569 | 20.924 | 20087040
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[10 empty] | Total=> | 37975680 | 28830720 |  |  | Total=> | 20087040 | 6538560 | -9144960 | -13548480 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 39775680 | 712380000 |  |  |  | 24660960 | 235272480
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 672604320 |  |  |  |  | 210611520 | 672604320 | 210611520 | 0.95 |  | 0 |  | 0.95431
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC Unit
[8 empty] | 672604320 |  | 210611520 |  | 0.95 | 0
[8 empty] | PDB (Unit+PFC) |  | 672604320 |  | KWH
[8 empty] | PGCB Unit |  | 672604320 |  | KWH
33 KV LEVEL | [10 empty] | Month December-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
4 | Shah Cement | Madanganj 132/33 kV | 33 | Exp | 8993 841 | 1 | 36000 | 39602.522 | 39602.522 | 0 |  | 0 | 10453.354 | 10453.354 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1484
| Shah Cement (new) |  | 33 | Exp | 5050 1238 | 1 | 36000 | 17.275 | 41.562 | 24.287 |  | 874332 | 3.716 | 11.132 | 7.416 |  | 266976 | 874332 | 266976 | 0.95641 | 0 | 0 | 1484
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 874332 |  |  | Total=> | 0 | 266976 | 874332 | 266976 | 0.95641 |  | 0 | 1484
6 | Jigatala (JP garden) | Kallyanpur
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.459 | 1.52 | 0.061 |  | 10980 | 0.104 | 0.104 | 0 |  | 0 | 10980 | 0 | 0 | 0 | 0 | 8
| Shere Bangla |  | 33 | Exp | 59723 485 | 1 | 180000 | 0.107 | 1.39 | 1.283 |  | 230940 | 0.003 | 0.003 | 0 |  | 0 | 230940 | 0 | 0 | 0 | 0 | 162
| Satmosjid-1 |  | 33 | Exp | 59723 483 | 1 | 180000 | 3.32 | 8.53 | 5.21 |  | 937800 | 0.44 | 1.107 | 0.667 |  | 120060 | 937800 | 120060 | 0.9919 | 0 | 0 | 658
| Satmosjid-2 |  | 33 | Exp | 59723 851 | 1 | 180000 | 12.822 | 33.168 | 20.346 |  | 3662280 | 4.877 | 12.771 | 7.894 |  | 1420920 | 3662280 | 1420920 | 0.93229 | 0 | 0 | 2568
| Kallayanpur T3 |  | 33 | Exp | 59723 486 | 1 | 180000 | 19.616 | 39.89 | 20.274 |  | 3649320 | 8.668 | 17.858 | 9.19 |  | 1654200 | 3649320 | 1654200 | 0.9108 | 0 | 0 | 2559
| Kallayanpur T4 |  | 33 | Exp | 59723 875 | 1 | 180000 | 18.01 | 55.454 | 37.444 |  | 6739920 | 7.905 | 22.803 | 14.898 |  | 2681640 | 6739920 | 2681640 | 0.92916 | 0 | 0 | 4727
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 184.069 | 185.464 | 1.395 |  | 251100 | 52.275 | 52.654 | 0.379 |  | 68220 | 251100 | 68220 | 0.96502 | 0 |  | 176 | T-5 has been used by DESCO
| Exp to Desco at 11 KV |  | 33 | Exp |  | 1 |  |  |  |  | 2950885 |  |  |  |  | 434731.2 |  | -2950885 | -434731.2 | 0 | 0 | 0
| Lalmatia |  | 33 | Exp | 59723 850 | 1 | 180000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
[10 empty] | Total=> | 2950885 | 15482340 |  |  | Total=> | 434731.2 | 5945040 | 12531455 | 5510308.8 | 0.91541 |  | 0 | 10858
SATMOSJID 132/33KV SS | [17 empty] | 15482340 | 5945040
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3308.169 | 3333.384 | 25.215 |  | 18911250 | 1646.116 | 1659.892 | 13.776 |  | 10332000 | 18911250 | 10332000 | 0.87757 | 0.01 | 189112.5 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 2950.394 | 2976.109 | 25.715 |  | 19286250 | 1443.211 | 1457.242 | 14.031 |  | 10523250 | 19286250 | 10523250 | 0.87783 | 0.01 | 192862.5 | 0
[10 empty] | Total=> | 0 | 38197500 |  |  | Total=> | 0 | 20855250 | 38197500 | 20855250 | 0.8777 | 0.01 | 381975 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1 | 180000 | 1999.239 | 2013.229 | 13.99 |  | 2518200 | 660.982 | 663.703 | 2.721 |  | 489780 | 2518200 | 489780 | 0.98161 | 0 | 0 | 12354.54
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1 | 180000 | 720.775 | 730.562 | 9.787 |  | 1761660 | 50.696 | 50.78 | 0.084 |  | 15120 | 1761660 | 15120 | 0.99996 | 0 | 0 | 8642.88
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1 | 180000 | 110.267 | 110.934 | 0.667 |  | 120060 | 4.16 | 4.16 | 0 |  | 0 | 120060 | 0 | 0 | 0 | 0 | 589.03
19 | Monipuripara-1 |  |  |  |  | 1 | 180000 | 1182.108 | 1186.857 | 4.749 |  | 854820 | 487.279 | 488.766 | 1.487 |  | 267660 | 854820 | 267660 | 0.95431 | 0 | 0 | 4193.83
20 | Monipuripara-2 |  |  |  |  | 1 | 180000 | 869.027 | 895.777 | 26.75 |  | 4815000 | 309.804 | 318.319 | 8.515 |  | 1532700 | 4815000 | 1532700 | 0.95289 | 0 | 0 | 23622.86
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 10069740 |  |  | Total=> | 0 | 2305260 | 10069740 | 2305260 | 0.97478 |  | 0 | 49403.14
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 424443.4 | 427058.1 | 2614.7 |  | 2680.0675 | 272257.6 | 274595.5 | 2337.9 |  | 2396.3475 | 2680.0675 | 2396.3475 | 0.74546 | 0.165 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 392725.7 | 397392.3 | 4666.6 |  | 4783.265 | 137792.8 | 138932.7 | 1139.9 |  | 1168.3975 | 4783.265 | 1168.3975 | 0.97144 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 7463.3325 |  |  | Total=> | 0 | 3564.745 | 7463.3325 | 3564.745 | 0.90235 |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 351.425 | 353.505 | 2.08 |  | 5116.8 | 255.48 | 257.244 | 1.764 |  | 4339.44 | 5116.8 | 4339.44 | 0.76266 | 0.15 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 124.447 | 129.438 | 4.991 |  | 12277.86 | 67.846 | 71.782 | 3.936 |  | 9682.56 | 12277.86 | 9682.56 | 0.78521 | 0.105 | 0 | 0
[10 empty] | Total=> | 0 | 17394.66 |  |  | Total=> | 0 | 14022 | 17394.66 | 14022 | 0.77854 |  | 0 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 2950885 | 64648769.9925 |  |  |  | 434731.2 | 29390112.745 | [5 empty] | 61745.14 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 61697884.9925 |  |  |  |  | 28955381.545 | 61697884.9925 | 28955381.545 | 0.90526 |  | 381975 |  | Total PFC Unit
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 512910 |  |  | 62210794.9925
33 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 61697884.9925 |  | 28955381.545 |  | 0.90526 | 381975
[8 empty] | PDB (Unit+PFC) |  | 62079859.9925 |  | KWH
[8 empty] | PGCB Unit |  | 61697884.9925 |  | KWH
11 KV LEVEL | [10 empty] | Month December-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [9 empty] | Total=> |  | 0 |  |  |  |  | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 1502 6 | 1 | 40000 | 9229.09 | 9236.31 | 7.22 |  | 288800 | 3477.86 | 3480.91 | 3.05 |  | 122000 | 296020 | 125050 | 0.92118 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 1502 7 | 1 | 40000 | 3878 | 3880.96 | 2.96 |  | 118400 | 1263.75 | 1263.79 | 0.04 |  | 1600 | 121360 | 1640 | 0.99991 | 1
3a | PD Betar |  | 11 | Imp | 2612 100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612 100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 1502 5 | 1 | 40000 | 3984.04 | 3986.34 | 2.3 |  | 92000 | 1894.36 | 1896.8 | 2.44 |  | 97600 | 94300 | 100040 | 0.68592 | 1.3121
5 | BICC - U/G |  | 11 | Exp | 1502 4 | 1 | 40000 | 1038.9 | 1038.93 | 0.03 |  | 1200 | 297.34 | 297.34 | 0 |  | 0 | 1230 | 0 | 0 | 1
6 | NEC |  | 11 | Exp | 1502 3 | 1 | 40000 | 431.67 | 431.67 | 0 |  | 0 | 56.31 | 56.32 | 0.01 |  | 400 | 0 | 410 | #DIV/0! | #DIV/0!
7 | Manikmia Avenue |  | 11 | Exp | 7602 6327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 500400 |  |  |  | 0 | 221600 | 512910 | 227140 | 0.91435
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 500400 |  |  |  | 0 | 221600
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 500400 |  |  |  |  | 221600
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 512910 |  |  |  |  | 227140 | 512910 | 227140 | 0.91435 |  | 0 |  | 0.91435
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 512910 |  | 227140 |  | 0.91435 | 0
[8 empty] | PDB (Unit + PFC) |  | 512910 |  | KWH
[8 empty] | PGCB Unit |  | 512910 |  | KWH

## PDB SUM AMR (hidden)
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE Month December-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 672604320 | 8.1335 | 5470627237 |  |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 672604320 | 672604320 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 5470627237 | 5470627237 | 0
2a | 33kv | 61697884.9925 | 8.22 | 507156615 |  |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 61697884.9925 | 61697884.9925 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 507156615 | 507156615 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 512910 | 8.22 | 4216120 |  |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 512910 | 512910 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 4216120 | 4216120 | 0
2c | Bus Loss Units (33kv) | 61745.14 | 8.22 | 507547 |  |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 61745.14 | 61745.14 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 507547 | 507547 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 62272540.1325 |  | 511880282 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 62272540.1325 | 62272540.1325 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 511880282 | 511880282 | 0
4 | TOTAL 132kv & 33kv (1+3) | 734876860.1325 |  | 5982507519 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 734876860.1325 | 734876860.1325 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 5982507519 | 5982507519 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 381975 | 8.22 | 3139835 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 381975 | 381975 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 3139835 | 3139835 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 381975 |  | 3139835 |  |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 381975 | 381975 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 3139835 | 3139835 | 0
8 | TOTAL Billed Amount => (4+7) | 735258835.1325 |  | 5985647354 |  | 5985647354 |  | 10 | সর্বমোট (৬+৯) | 735258835.1325 | 735258835.1325 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 5985647354 | 5985647354 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 359138841 | Source Tax | [10 empty] | 11 | উৎস কর (মোট বিলের উপর ৬%) | 359138841 | 359138841 | -
10 | NET BILL TOTAL => (8-9) |  |  | 5626508513 |  | 7755732645 | , কমা চেইঞ্জার | [8 empty] | 12 | কর পরবর্তী মোট পরিশোধ যোগ্য বিল (১০-১১) | 5626508513 | 5626508513 | -
11*** | 24th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  |  | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 5626508513
"In word: Taka Six Hundred Sixty Five Crore Sixty One Lac Ninety Two Thousand Fifty"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | 31683869.1762 | 2021-10-01
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid | 30306309.6468 | 2021-11-01
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid | 28928750.1174 | 2021-12-01
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid | 27551190.588 | 2022-01-01
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid | 26173631.0586 | 2022-02-01
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid | 24796071.5292 | 2022-03-01
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid | 23418511.9998 | 2022-04-01
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid | 22040952.4704 | 2022-05-01
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid | 20663392.941 | 2022-06-01
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid | 19285833.4116 | 2022-07-01
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid | 17908273.8822 | 2022-08-01
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid | 16530714.3528 | 2022-09-01
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid | 15153154.8234 | 2022-10-01
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid | 13775595.294 | 2022-11-01
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid | 12398035.7646 | 2022-12-01
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid | 11020476.2352 | 2023-01-01
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid | 9642916.7058 | 2023-02-01
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid | 8265357.1764 | 2023-03-01
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid | 6887797.647 | 2023-04-01 |  | 366430834.8204
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid | 5510238.1176 | 2023-05-01 |  | 20971130269.73
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid | 4132678.5882 | 2023-06-01
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Paid | 2755119.0588 | 2023-07-01
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94 | Paid | 1377559.5294 | 2023-08-01 |  | 20604699434.9096
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0 | Certified For Payment | 380206430.1144
| Total | 3306142870.56
20984905865.024
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | 0 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [9 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[12 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE Month December-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 672604320 | 0.2886 | 194113606.752 |  | 293050922 | , কমা চেইঞ্জার | 1 | 132 †Kwf (GbvwR©) | 672604320 | 672604320 | 672604320 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 5470627237 | 194113606.752 | 194113606.752 | 0
2a | 33kv Level | 61697884.9925 | 0.2944 | 18163857.3418 |  |  |  | 2 | 33 †Kwf (GbvwR©) | 61697884.9925 | 61697884.9925 | 61697884.9925 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 507156615 | 18163857.3418 | 18163857.3418 | 0 |  | 33KV Amount (2+3+4) => | 18333036.155
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 512910 | 0.2944 | 151000.704 |  |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 512910 | 512910 | 512910 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 4216120 | 151000.704 | 151000.704 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 61745.14 | 0.2944 | 18178.1092 |  |  |  | 4 | 33 ‡Kwf evm jm | 61745.14 | 61745.14 | 61745.14 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 507547 | 18178.1092 | 18178.1092 | 0 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 62272540.1325 | 0.2944 | 18333036.155 |  |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 62272540.1325 | 62272540.1325 | 62272540.1325 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 511880282 | 18333036.155 | 18333036.155 | 0
4 | TOTAL=> (1+3) | 734876860.1325 |  | 212446642.907 |  |  |  | 6 | me©‡gvU (1+5) | 734876860.1325 | 734876860.1325 | 734876860.1325 | 0 |  |  | 6 | me©‡gvU (1+5) | 5982507519 | 212446642.907 | 212446642.907 | 0
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000 | [12 empty] | 298330160 | , কমা চেইঞ্জার
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 14th Installment ) |  |  | 25993419.79 |  |  |  | ‡gvU (GbvwR©) |  | 734815114.9925 | 734815114.9925 | 734815114.9925 | 0 |  |  | ‡gvU (GbvwR©) |  | 5981999972 | 212428464.7978 | 18333036.155 | 194095428.6428
7 | Grand TOTAL=> (4-5+6) |  |  | 236940062.697
| CERTIFIED UNITS |  |  | 734876860.1325 |  | 251429633 | , কমা চেইঞ্জার
| CERTIFIED TAKA |  |  | 212446642.907
| CERTIFIED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 14th Installment of Wheeling Charge Due) |  |  | 236940062.697
evsjv
In word: Taka Twenty Seven Crore Fifty Nine Lac Twenty Three Thousand Fifty Three
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Paid
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Paid
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06 | Paid
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27 | Paid
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48 | Paid
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69 | Paid
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9 | Certified For Payment
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check
[6 empty] | Month December-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 115836594.66 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 115441056 | Fatullah Grid | 30470400 | 395538.66 | 0.3415%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 0 |  |  |  | Shyampur Grid | 84970656
|  |  | 132 | Import |  | 0 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 17701440 | 22455360 | Postogola 132/33 KV Grid | 22455360 | Postogola Grid | 22455360 | 0 | 0%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 4753920
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 4725120 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 1800000 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 1800000 | 27180480
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 6907200 | 74148000 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 73639960.6 | Ullon Grid | 19132655 | 508039.4 | 0.6852%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 46635305.6
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 6907200 |  |  |  | DU Grid | 7872000
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 13041600 | 105503040 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 104481083 | Lalbagh Grid | 39719483 | 1021957 | 0.9687%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 26155200
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 13111680 |  |  |  | Jigatola Grid | 38606400
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 26153280
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 14887680 | 43000320 | Sitalakhya 132/33 KV Grid | 42911963 | Sitalakhya Grid | 42911963 | 88357 | 0.2055%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 13916640
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 14196000
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 11776320 | 11776320 | Sitalakhya NOCS | 11776320 | Sitalakhya NOCS | 11776320 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 54776640
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 25798080 | 51523200 | Siddirganj 132/33 KV Grid | 51317107.2 | Siddirganj Grid | 51317107.2 | 206092.8 | 0.4%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 25725120
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 13439520 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 33955200 | 33955200 | Matuail 132/33 KV Grid | 33955265 | Matuail Grid | 33955265 | -65 | -0.0001914%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 98917920
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 21123840 | 37101120 | Moghbazar 132/33 KV Grid | 36721459.2 | Moghbazar Gird | 36721459.2 | 379660.8 | 1.023%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 15977280
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 10055040 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 9322560
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 16683840 | 33138240 | Madartek 132/33 KV Grid | 33105101.76 | Madartek Grid | 33105101.76 | 33138.24 | 0.1%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 16454400
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 17115840 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 17307840
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 124040640
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 58229760 | 115628160 | Maniknagar 132/33 KV Grid | 115976560 | Kazla Grid | 43660800 | -348400 | -0.3013%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 57398400 |  |  |  | Motijheel Grid | 14896800
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 115628160 |  |  |  | Narinda Grid | 24403200
[11 empty] | Bangabhaban Grid | 4436400
[11 empty] | Maniknagar Grid | 28564000
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 75477120 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid |  | Metro Rail | 15360
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 75118080
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 150595200
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 39512160 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 39837600
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 79349760
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 10518720 | 28556160 | Charsyedpur 132/33 KV Grid | 28488000 | Charsyedpur Grid | 28488000 | 68160 | 0.2387%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 18037440
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 274560 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 37975680 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 37975680 | 28830720 | 672621714.66 |  | 670269235.76 |  | 670269235.76 | 2352478.9 | 0.3497%
[9 empty] | 33 KV Transmission Loss |  | 61449550.3325 | 61728262.047 | -278711.7145 | -0.4536%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 512910 | 517420 | -4510 | -0.8793%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 734584174.9925 | 732514917.807 | 2069257.1855 | 0.2817%
[9 empty] | From Summary Sheet |  |  |  | 4752374.5411 | 0.6467%
[9 empty] | Mismatch in KWH |  |  |  | -2683117.3556
| 33 KV LEVEL |  |  |  |  | Month December-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | #REF! | #REF!
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 874332 | 874332 | Sitalakhya NOCS | 875816 | Sitalakhya NOCS | 875816 | -1484 | -0.1697%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 874332
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 10980 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 10980 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 10980
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 230940
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 937800 | 42797580 | Shatmasjid 132/33 KV Grid | 43112769.9144 | Asadgate SS | 7978569.9144 | -315189.9144 | -0.7365%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 3662280 |  |  |  | Lalmatia SS | 8315280
[11 empty] | Japan Garden SS | 8426700
[11 empty] | Jigatola Old SS | 1303200
[11 empty] | Shatmasjid SS | 14857740
[11 empty] | BGB SS | 2231280
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 3649320 | 7689455 | Adabor NOCS | 7825752 | Adabor NOCS | 7825752 | -136297 | -1.773%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 6739920
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 251100
| Export to Desco at 11 KV |  |  |  |  | 2950885 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 0 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 2950885 | 15482340
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 18911250 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 19286250
AGARGAON 132/33KV SS | [5 empty] | 0 | 38197500
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 2518200 | 4399920 | Sherebanglanagar 33/11 KV SS | 4208901.6297 | Sherebanglanagar SS | 4208901.6297 | 191018.3703 | 4.341%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 1761660
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 120060
19 | Monipuripara-1 |  |  |  |  | 0 | 854820 | 5669820 | Monipuripara 33/11 KV SS | 5697636.69 | Monipuripara SS | 5697636.69 | -27816.69 | -0.4906%
20 | Monipuripara-2 |  |  |  |  | 0 | 4815000
| Maniknagar 230/132 kv |  |  |  |  | 0 | 10069740
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 2680.0675 | 7463.3325 | Maniknagar 33/11 KV SS | 7385.8129 | Maniknagar 33/11 KV SS | 7385.8129 | 77.5196 | 1.039%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 4783.265
Shyampur 230/132 kv | [5 empty] | 0 | 7463.3325
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 5116.8 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 12277.86
[6 empty] | 0 | 17394.66
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 2950885 | 64648769.9925 | 61449550.3325 |  | 61728262.047 |  | 61728262.047 | -278711.7145 | -0.4536%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 288800 | 512910 | Sherebanglanagar NOCS | 517420 | Sherebanglanagar NOCS | 517420 | -4510 | -0.8793%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 118400
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 92000
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 1200
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 500400
TOTAL => | [5 empty] | 0 | 500400 | 512910 |  | 517420 |  | 517420 | -4510 | -0.8793%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 185.464 | 184.069 |  | 1.395 | 180000 | 251100 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 55.454 | 18.01 |  | 37.444 | 180000 | 6739920 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 996.01 | #REF!
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 39.89 | 19.616 |  | 20.274 | 180000 | 3649320 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9678.27 | #REF!
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4662.01 | #REF!
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 4445.7 | 4419.5 |  | 26.855 | 8000 | 214840 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 53140.44 | #REF!
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 42542.57 | #REF!
03 |  | 11 KV Bashir Uddin |  | 74819925 | 935.309 | 934.477 |  | 0.8528 | 16000 | 13644.8 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 2404.55 | #REF!
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8432.58 | #REF!
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1135.27 | 1131.24 |  | 4.1307 | 40000 | 165230 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9438.88 | #REF!
05 |  | 11 KV Lalkuthy |  | DHK15018 | 1059.42 | 1031.06 |  | 29.069 | 40000 | 1162760 | 0 | 1 |  |  |  |  | 0 |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9828.4 | 9794.39 |  | 34.8603 | 40000 | 1394410 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [5 empty] | #REF!
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 53140.44 | 52970.34 |  | 174.3525 | 8000 | 1394820 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  | #REF!
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8432.58 | 8401.63 |  | 31.7238 | 40000 | 1268950 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  | #REF!
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2404.55 | 2350.06 |  | 55.8523 | 40000 | 2234090 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  | #REF!
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  | #REF!
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.705 | 3273.705 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  | #REF!
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9678.27 | 9673.06 |  | 5.3403 | 40000 | 213610 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  | #REF!
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9438.88 | 9431.09 |  | 7.9847 | 40000 | 319390 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  | #REF!
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4662.01 | 4620.87 |  | 42.1685 | 40000 | 1686740 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  | #REF!
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 996.01 | 995.9 |  | 0.11275 | 40000 | 4510 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 42542.57 | 42456.21 |  | 88.519 | 8000 | 708152 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 2950884.8 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 7689455.2 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48 | 48 | 48 | 48 | 48 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41 | 41 | 41 | 41 | 41 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [138 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | 89 | 89 | 89 | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [178 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[141 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | December-2023 % of Loss | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.32457 | 0.15752 | 0.36993 | 0.1982 | 0.22066 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.5014 | 2.8235 | 3.3831 | 4.7675 | 6.4099 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 0.8681 | 1.8104 | 1.4562 | 0.087826 | 1.0278 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.90072 | 1.7413 | 0.57703 | 0.73688 | 0.95024 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.4757 | 0.58489 | 1.028 | 0.51858 | 1.0269 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.0456 | 1.0112 | -1.6675 | -0.51228 | -0.14892 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.1464 | 0.11776 | 0.40506 | 0.59878 | 0.032224 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | -0.22179 | -0.0059747 | 0.78672 | 0.71164 | 0.1718 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.042288 | -0.22661 | 0.090354 | 1.8004 | 0.72315 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.3399 | -0.34635 | 1.7093 | 1.2924 | 1.7957 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0 | 0.078999 | 0.012837 | 0.076849 | 0.070408 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.94329 | 0.71194 | 0.42244 | 0.67755 | 0.74731 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 1.6183 | 0.39893 | -0.035562 | 1.3133 | 1.1413 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.4872 | 0.23283 | 0.31121 | 1.418 | 1.5 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 0.081362 | 1.6403 | 0.39586 | 0.22128 | 3.0565 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.29485 | 1.1177 | 0.22363 | -0.15783 | 0.36408 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | 1.8414 | -0.75805 | 0.86271 | -0.5535 | -0.24021 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 1.1299 | -0.36418 | 0.10052 | -0.025203 | 0.21781 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.42032 | -0.086911 | -0.2611 | 0.97617 | -0.13914 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.5345 | 1.8667 | 1.1968 | 2.1342 | 2.1711 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.1395 | 0.31895 | 0.16255 | -0.50074 | 0.12321 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.48586 | 0.11321 | 0.07333 | 0.10551 | 0.1185 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | 0.93209 | -0.53789 | -0.043971 | -0.075665 | -0.064901 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.8143 | 1.8226 | 1.1357 | 2.0237 | 1.9508 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 1.8269 | 0.93812 | 0.5119 | 0.40513 | -1.985 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.11727 | 0.21759 | 0.14868 | 0.41233 | 0.10871 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 2.2403 | -0.06039 | 1.5455 | 1.2197 | 1.7549 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 2.5706 | 0.85 | 0.85 | 1 | 1 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | 1.6282 | -2.4815 | 2.0082 | -2.831 | -2.6717 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.2091 | 1.3444 | 1.2163 | 0.86585 | 1.5712 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | 1.0212 | -0.32329 | 1.3885 | 1.3864 | 1.1808 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | 0.85829 | -0.09904 | 0.15826 | 0.3214 | 0.74913 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.66098 | -0.86776 | 1.3314 | 0.41255 | 0.56541 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.5443 | 0.6468 | -0.78277 | 1.757 | 1.2174 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | -0.01484 | 0.39969 | 1.2104 | 0.54824 | 0.90308 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | -0.53825 | 0.30898 | 0.026513 | 0.047491 | -0.25931 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 0.40161 | -0.15046 | 0.063822 | 1.034 | -0.81695 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.67176 | 0.54646 | 1.0407 | 0.334 | 0.41807 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.71763 | 0.27825 | 0.23578 | 1.0938 | 1.7781 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 1.1187 | -0.40364 | 0.31408 | 0.18399 | 1.0713 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.074543 | -0.26271 | -0.092639 | -0.05005 | 0.074283 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.26105 | 0.62337 | 0.24412 | 0.051628 | -0.13885 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.73163 | 0.92584 | 1.2666 | 0.69212 | 0.34882 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.50247 | 0.26743 | 0.070914 | 0.3138 | 0.22403 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | December-2023 % of Loss | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.41839 | 0.65358 | 0.15556 | 0.20112 | 0.95272 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.64336 | 0.22332 | 0.15665 | 0.20537 | 0.20884 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.5241 | 1.0652 | 1.1157 | 1.2591 | 1.2584 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.69983 | 0.53762 | 0.77964 | 0.65402 | 1.444 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 0.27555 | -0.32773 | 0.17832 | 0.31771 | 1.0687 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 1.4354 | -0.2497 | 0.24297 | 0.17031 | 0.10378 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.14854 | 0.0012825 | 0.10878 | -0.085961 | 0.041539 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.57978 | 0.71204 | 0.43536 | 0.43971 | 1.0708 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.66344 | 0.14942 | -0.13156 | -0.4174 | 0.13595 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 0.32549 | 1.1659 | 1.3565 | 2.1519 | 1.211 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.032147 | 0.014741 | -0.031653 | -0.01844 | 0.010028 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.11183 | 0.22189 | 0.79245 | 0.12531 | -0.42556 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | 0 | -0.8 | -0.48244 | 0 | -1.9122 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | 0.46062 | -0.24353 | -1.0495e-13 | -0.04852 | -0.048314 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 2.1067 | 1.3882 | 1.8683 | 1.573 | 0.29445 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 1.4502 | 1.1022 | 0.43069 | 0.068963 | -0.86273 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.077152 | -0.02899 | -0.023304 | 0.076622 | 0.064233 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.18042 | 0.23889 | 0.18888 | 0.15171 | 0.25381 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | -0.35882 | 0.12376 | 1.5174 | 2.7774 | 1.2284 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.48827 | -0.078372 | -0.48766 | 0.66641 | -0.41499 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 1.1371 | 0.57715 | 0.64916 | 0.88184 | 0.57602 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.73689 | 0.2689 | 0.32352 | 0.80196 | -0.26653 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.64818 | 0.56141 | 0.25534 | 0.44829 | 1.0739 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.0581 | 0.9012 | 1.0829 | 1.112 | 1.1039 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | -0.55219 | 0.21493 | 0.33276 | 0.71435 | 0.23019 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 1.1068 | 0.79088 | 1.0512 | 1.0599 | 0.74837 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.8988 | 1.095 | 1.1333 | 1.4904 | 1.4865 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 2.5 | 0 | 1.4383 | 2.0408 | 0.18209 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 0.46563 | 1.1359 | 1.4766 | 0.10496 | 0.096193 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | 1.1327 | 0.3109 | 1.2474 | -0.24532 | -0.64219 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.96474 | 0.49417 | 0.28876 | -0.62244 | 1.8284 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.60032 | 0.22815 | 0.24367 | 0.46773 | 0.16433 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | 0.8586 | 2.1521 | 0.66653 | 0.56513 | -0.8103 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | -0.037198 | 1.347 | 1.4676 | 1.9489 | 1.3703 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | 0.054939 | 0.45149 | 1.3208 | 0.33477 | -0.12622 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.031496 | -0.073934 | -0.057847 | -0.086839 | 0.038802 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.42912 | 0.23243 | 0.22785 | 0.18163 | 1.4646 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | 2.165 | 1.7361 | 1.179 | 0.4914 | 1.1051 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | 0.91042 | -0.025332 | -0.044529 | -0.040721 | -0.12694 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 1.7823 | 0.5041 | -2.2501 | 3.468 | 0.40336 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 2.0579 | 0.35988 | 1.5164 | 1.7985 | 0.80075 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | -0.12595 | 0.096563 | 0.12007 | 0.27405 | 0.15019 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | 0.49516 | -0.40379 | -0.18029 | -0.41785 | -0.72448 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0.16973 | 0 | 0 | 0 | 0 | 0 | 0.033974

## ALL SS Loss History (hidden)
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68
|  | DPDC TOTAL SS | 89 | 89
NORTH
[7 empty] | HV Side |  |  |  | LV Side |  |  | % LOSS
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export / Import | XFR-Sending | XFR-Receiving | Feeder Total | Corrected Feeder Total | S_FT | R_FT | XS_FT | XR_FT
[7 empty] | S | R | EI | XS | XR | FT | CFT | %S | %R | %XS | %XR
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.32457 | 132 | 33 | 37101120 | 37303200 | 0 | 37303200 | 37017600 | 36602657.2 | 36721459.2 | 1.3618 | 1.9139 | 1.9139 | 1.1336
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.5014 | 33 | 11 |  |  |  | 12453088.4812 | 12336300 | 11779678.4 | 12074336.4406 | -100 | -100 | 5.7167 | 4.7253
N-2 | 3 | Green Road 33/11KV S/S | 3 | 0.8681 | 33 | 11 | 8806474.08 | 0 | 0 | 0 | 9303300 | 8730683.357 | 8806474.08 | 0.8681 | -100 | -100 | 6.5587
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.90072 | 33 | 11 | 8450667.1052 | 0 | 0 | 0 | 8315280 | 8241051.413 | 8315280 | 2.5436 | -100 | -100 | 0.90072
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.4757 | 33 | 11 | 13793023.4657 | 0 | 0 | 14931459 | 6912702 | 13592435.8 | 13793023.4657 | 1.4757 | -100 | 9.8512 | -49.143
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.0456 | 33 | 11 | 6715063.5869 | 7879680 | 0 | 24795540 | 6640200 | 6645575.4 | 6715063.5869 | 1.0456 | 18.5703 | 273.1135 | -0.080887
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.1464 | 132 | 33 | 0 | 46868000 | 26590000 | 46832000 | 46593600 | 46567130 | 46635305.6 | -100 | 0.6461 | 0.56879 | 0.056843
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | -0.22179 | 33 | 11 |  |  |  | 8662263.2599 | 8619442.2 | 8681518 | 8662263.2599 | -100 | -100 | -0.22179 | -0.71503
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.042288 | 33 | 11 | 2619829.8982 | 2575800 | 0 | 2588400 | 2579000 | 2618722.48 | 2619829.8982 | 0.042288 | -1.6391 | -1.1579 | -1.5169
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.3399 | 33 | 11 | 5620693.7884 | 0 | 0 | 0 | 5546800 | 5546379.751 | 5620693.7884 | 1.3399 | -100 | -100 | 0.007577
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0 | 132 | 33 | 39724320 | 0 | 20278000 | 19446320 | 19035744 | 19132655 | 19132655 | 107.6258 | -100 | 1.6394 | -0.50652
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.94329 | 33 | 11 |  |  |  | 4669608 | 4669608 | 4625971.56 | 4669608 | -100 | -100 | 0.94329 | 0.94329
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 1.6183 | 33 | 11 | 6330855.0018 | 5482800 | 0 | 0 | 6155556.325 | 6230033.3376 | 6330855.0018 | 1.6183 | -11.9941 | -100 | -1.1955
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.4872 | 33 | 11 | 4644569.5282 | 25707164.4 | 0 | 4608360 | 4519800 | 4586016.78 | 4608360 | 1.2768 | 460.5554 | 0.4872 | -1.4439
N-2 | 15 | Goran 33/11KV S/S | 15 | 0.081362 | 33 | 11 | 7421006.8986 | 48091008 | 0 | 7410000 | 7421021 | 7414988 | 7421021 | 0.081172 | 548.5649 | -0.067269 | 0.081362
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.29485 | 33 | 11 | 8966904 | 0 | 0 | 0 | 8808000 | 8940542.9942 | 8966904 | 0.29485 | -100 | -100 | -1.4825
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | 1.8414 | 33 | 11 |  |  |  | 15099649.642 | 14857740 | 14589090.6 | 14857740 | -100 | -100 | 3.4996 | 1.8414
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 1.1299 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.42032 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.5345 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.1395 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.48586 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 24 | Japan Garden 33/11 KV, | 24 | 0.93209 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.8143 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 1.8269 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.11727 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 2.2403 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 2.5706 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | 1.6282 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 31 | Banasree 33/11 SS | 31 | 1.2091 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 32 | Mugdhapara Hospital | 32 | 1.0212 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 33 | DMC | 33 | 0.85829 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.66098 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.5443 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | -0.01484 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | -0.53825 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 0.40161 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.67176 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.71763 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 1.1187 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.074543 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.26105 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.73163 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.50247 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
|  | SOUTH |  |  |  |  | S: HV Side; XR: LV Side
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export | XFR-Sending | XFR-Receiving | Feeder Total | Feeder Total
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.41839 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.64336 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.5241 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.69983 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 0.27555 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 1.4354 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.14854 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.57978 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.66344 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 10 | Kazla 33/11KV S/S | 8 | 0.32549 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.032147 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.11183 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | 0 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 14 | Postogola 132/33 KV S/S | 43 | 0.46062 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 15 | Postogola 33/11KV S/S | 12 | 2.1067 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 1.4502 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.077152 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.18042 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | -0.35882 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.48827 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 1.1371 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.73689 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.64818 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.0581 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 25 | Matuail 132/33 KV S/S | 24 | -0.55219 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 26 | Matuail 33/11KV S/S | 23 | 1.1068 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.8988 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 2.5 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 0.46563 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Mitford 33/11 kV | 29 | 1.1327 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.96474 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.60032 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 33 | Dapa 33/11 kV | 32 | 0.8586 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | -0.037198 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 35 | Amulia 33/11 kv | 34 | 0.054939 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.031496 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.42912 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 38 | P & T 33/11 KV SS | 37 | 2.165 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 39 | Motijheel 132/33 KV SS | 38 | 0.91042 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 1.7823 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 2.0579 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | -0.12595 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | 0.49516 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0.16973 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Feeder Code | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) |  | 3: 132; 4: IMPORT; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000
| 132 KV DHANMONDI-3 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 10: Net Total | 46868000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 |  | 132 |  | SIEM0480 | 1 | 1632768 | 1632768 | 0 | 1000 | 0
| 132 kV Dhaka University |  | 132 |  | SIEM0480 | 1 | 133950 | 160540 | 26590 | 1000 | 26590000
3 | 132 kV Dhaka University |  | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 |  | 132 |  | SIEM0481 | 1 | 2235495 | 2245585 | 10090 | 1000 | 10090000
8 | 132 kV Ullon Circuit-3 |  | 132 |  | SIEM0484 | 1 | 2991477 | 3001665 | 10188 | 1000 | 10188000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 46868000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 46868000
| DHANMONDI 132 KV SIDE (EXPORT To / IMPORT From OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhaka University (Export) |  | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) |  | 132 |  |  | 1 | 133950 | 160540 | 26590 | 1000 |  | 26590000
|  |  | 7: 0; 8: 0; 10: Total |  | 26590000
| DHANMONDI 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) |  | 132 | NET IMPORT | SIEM0487 | 1 | 921073 | 932267 | 11194 | 1000 |  | 11194000
5 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | SIEM0496 | 1 | 1496532 | 1501580 | 5048 | 2000 |  | 10096000
9 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | SIEM0493 | 1 | 1366335 | 1371417 | 5082 | 2000 |  | 10164000
10 | 132/33kV, 80/120 MVA GT-3 (HV) |  | 132 |  | SIEM0497 | 1 | 1339435 | 1347124 | 7689 | 2000 |  | 15378000
|  |  | 10: Total |  | 46832000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 4: 46832000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 46832000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 46832000 | 132/33 kv GT LV Side |  | 46593600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 238400
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.5091%
| 132 KV TOTAL IMPORT |  | 4: 46832000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming |  | 33 | IMPORT | BD001860 | 1 | 2324.72 | 2338.66 | 13.94 | 720000 | 10036800
12 | 132/33 kV GT-2 Incoming |  | 33 |  | BD001818 | 1 | 2292.58 | 2306.73 | 14.15 | 720000 | 10188000
17 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001863 | 1 | 2046.44 | 2067.67 | 21.23 | 720000 | 15285600
24 | 132/33 kV GT-4 Incoming |  | 33 |  | BD001916 | 1 | 1909.93 | 1933.02 | 23.09 | 480000 | 11083200
|  |  | 7: 0; 8: 0; 10: Total | 46593600 |  | 0
| DHANMONDI 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 |  |  |  |  | 8662263.2599 | Dhanmondi 33/11 kv ss | -0.22179 |  | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 |  | 33 |  | BD001861 | 1 | 2191.32 | 2208.94 | 17.62 | 240000 |  | 4228800 | 4234991.0832 | [5 empty] | 33/11 kV 20/28 MVA T-1 | 4234991.0832 | 5024309.5707 | -789318.4875 | -15.71 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 |  | BD001892 | 1 | 2497.75 | 2516.17 | 18.42 | 240000 |  | 4420800 | 4427272.1767 | [5 empty] | 33/11 kV 20/28 MVA T-2 | 4427272.1767 | 5442401.3284 | -1015129.1517 | -18.6522 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8649600 | 8662263.2599 | [5 empty] | 33 KV Feeders | 8662263.2599 | 10466710.8991 | -1804447.6392 | -17.2399 | OK
5 | New Ramna Circuit-1 |  | 33 |  | BD001919 | 1 | 1527.47 | 1539.9 | 12.43 | 240000 |  | 2983200 | 2987567.4895 |  | 4631570.8385 | New Ramna 33/11 kv ss | 1.3399 |  | New Ramna Circuit-1 | 2987567.4895 | 3505723.4164 | -518155.9269 | -14.7803 | OK
8 | Kakrail Circuit-1 |  | 33 |  | BD001825 | 1 | 900.82 | 907.43 | 6.61 | 240000 |  | 1586400 | 1588722.5346 | [5 empty] | Kakrail Circuit-1 | 1588722.5346 | 2534981.6342 | -946259.0996 | -37.328 | OK
9 | Kawran Bazar Circuit-1 |  | 33 |  | BD001820 | 1 | 1904.37 | 1914.8 | 10.43 | 240000 |  | 2503200 | 2506864.7558 |  | 6330855.0018 | Kakrail 33/11 kv ss | 1.6183 |  | Kawran Bazar Circuit-1 | 2506864.7558 | 3332719.9304 | -825855.1746 | -24.7802 | OK
10 | New Ramna Circuit-2 |  | 33 |  | BD001816 | 1 | 1246.56 | 1253.4 | 6.84 | 240000 |  | 1641600 | 1644003.349 | [5 empty] | New Ramna Circuit-2 | 1644003.349 | 2530175.9818 | -886172.6328 | -35.0242 | OK
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.44 | 462.91 | 0.47 | 240000 |  | 112800 | 112965.1424 |  | 2619829.8982 | Kawran Bazar 33/11 kv ss | 0.042288 |  | Kawran BazarCircuit-2 | 112965.1424 | 2402.8262 | 110562.3162 | 4601.3447 | FAULT
13 | DMC Hospital Feeder |  | 33 |  | BD001840 | 1 | 464.63 | 475.63 | 11 | 240000 |  | 2640000 | 2643865.0349 | [5 empty] | DMC Hospital Feeder | 2643865.0349 | 4308267.365 | -1664402.3301 | -38.6328 | OK
15 | Green Road Circuit-2 (U/G) |  | 33 |  | BD001918 | 1 | 2193.69 | 2210.47 | 16.78 | 240000 |  | 4027200 | 4033095.9351 |  | 2643865.0349 | DMC Hospital 33/11 kv ss | 0.85829 |  | Green Road Circuit-2 (U/G) | 4033095.9351 | 5086783.0517 | -1053687.1166 | -20.7142 | OK
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1696.22 | 1715.95 | 19.73 | 240000 |  | 4735200 | 4742132.4672 | [5 empty] | Kakrail Circuit-2 | 4742132.4672 | 4675899.7726 | 66232.6946 | 1.4165 | OK
18 | BSMMU Hospital Circuit-1 |  | 33 |  | BD001920 | 1 | 766.57 | 774.65 | 8.08 | 240000 |  | 1939200 | 1942039.0438 |  | 8806474.08 | Green Road 33/11 kv ss | 0.8681 |  | BSMMU Hospital Circuit-1 | 1942039.0438 | 2683956.8582 | -741917.8143 | -27.6427 | OK
19 | Azimpur Circuit-1 |  | 33 |  | BD001822 | 1 | 2072.37 | 2091.42 | 19.05 | 240000 |  | 4572000 | 4578693.5378 | [5 empty] | Azimpur Circuit-1 | 4578693.5378 | 3592225.1593 | 986468.3784 | 27.4612 | OK
20 | Azimpur Circuit-2 |  | 33 |  | BD001857 | 1 | 1885.43 | 1904.68 | 19.25 | 240000 | From Downstream R Phase CT Problem | 5434560 | 5442516.3501 |  | 2901040.9974 | BSMMU 33/11 kv ss | 0.5443 |  | Azimpur Circuit-2 | 5442516.3501 | 4301058.8864 | 1141457.4636 | 26.539 | OK
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 175.9 | 179.89 | 3.99 | 240000 |  | 957600 | 959001.9536 | [5 empty] | BSMMU Hospital Circuit-2 | 959001.9536 | 1256678.0992 | -297676.1456 | -23.6875 | OK
23 | Green Road Circuit-1 |  | 33 |  | BD001865 | 1 | 1526.05 | 1545.91 | 19.86 | 240000 |  | 4766400 | 4773378.1449 |  | 10021209.8878 | Azimpur 33/11 kv ss | 1.8143 |  | Green Road Circuit-1 | 4773378.1449 | 5754768.7335 | -981390.5887 | -17.0535 | OK
26 | 33/0.4 kV, 500 kVA AT-1 |  | 0.4 |  | 84.2659 | 1 | 325367 | 327184 | 1817 | 10 |  | 18170 | 18196.6014 | Paribag |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 18196.6014 | 19032.3858 | -835.7844 | -4.3914 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 |  | 0.4 |  | 84.2673 | 1 | 478776 | 478776 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 8: 0; 10: Total |  | 37917530 | 37973042.3401 | [6 empty] | 37973042.3401 | 43584674.1009 | -5611631.7608 | -12.8752 | OK
|  |  | 9=8-7: Grand Total | 46635305.6 | 46567130 | 46635305.6 | 0.1464
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming |  | 11 | IMPORT | DHK60884 | 1 | 42187.28 | 66728.26 | 24540.98 | 180 | 4417376.4 |  | 4439321.7574
16 | 33/11 kV Transformer-1 Incoming |  | 11 |  | DHK60976 | 1 | 639368.63 | 662713.44 | 23344.81 | 180 | 4202065.8 |  | 4222941.5025
|  |  | 7: 0; 8: 0; 10: Total | 8619442.2 |  | 8662263.2599
| DHANMONDI 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 11634850 | 12489127 | 854277 | 1 |  | 854277 | 852382.2989 | Paribag |  |  |  |  | 11 kV Balaka Feeder | 852382.2989 | 1117275.2423 | -264892.9434 | -23.7088 | OK
5 | 11 kV Mogbazar O/H | C301M | 11 |  | HA021100463-02 | 1 | 53414203 | 54398317 | 984114 | 1 |  | 984114 | 981931.3334 | Paribag |  |  |  |  | 11 kV Mogbazar O/H | 981931.3334 | 1079510.4987 | -97579.1653 | -9.0392 | OK
6 | 11 kV Panthopath Feeder | C3011 | 11 |  | HA021101078-02 | 1 | 67706878 | 68510069 | 803191 | 1 |  | 803191 | 801409.6026 | Paribag |  |  |  |  | 11 kV Panthopath Feeder | 801409.6026 | 967771.1752 | -166361.5726 | -17.1902 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 |  | DHK60882 | 1 | 242194.26 | 247026.69 | 4832.43 | 60 |  | 289945.8 | 289302.7292 | Paribag |  |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 289302.7292 | 325387.5579 | -36084.8288 | -11.0898 | OK
8 | 11 kV P G Hospital Feeder | C301P | 11 |  | DHK60889 | 1 | 296567.58 | 299102.92 | 2535.34 | 60 |  | 152120.4 | 151783.0121 | Paribag |  |  |  |  | 11 kV P G Hospital Feeder | 151783.0121 | 122058.3971 | 29724.6151 | 24.3528 | OK
9 | 11 kV Abdul Monem Ltd |  | 11 |  | DHK60890 | 1 | 726.52 | 731.24 | 4.72 | 60000 |  | 283200 | 282571.8907 | Paribag |  |  |  |  | 11 kV Abdul Monem Ltd | 282571.8907 | 343779.459 | -61207.5683 | -17.8043 | OK
10 | 11 kV Surjasen Hall Feeder | D301H | 11 |  | DHK60880 | 1 | 581064.2 | 584988.43 | 3924.23 | 60 |  | 235453.8 | 234931.587 | Ramna |  |  |  |  | 11 kV Surjasen Hall Feeder | 234931.587 | 287616.8148 | -52685.2278 | -18.3179 | OK
11 | 11 kV Azimpur-1 Feeder |  | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | D301U | 11 |  | DHK60873 | 1 | 963916.78 | 969708.1 | 5791.32 | 60 |  | 347479.2 | 346708.5258 | Ramna |  |  |  |  | 11 kV TSC Feeder | 346708.5258 | 436581.914 | -89873.3882 | -20.5857 | OK
13 | 11 kV SCADA Bhaban | C301S | 11 |  | DHK60883 | 1 | 28971.13 | 29139.32 | 168.19 | 60 |  | 10091.4 | 10069.0183 | Paribag |  |  |  |  | 11 kV SCADA Bhaban | 10069.0183 | 10788.5554 | -719.5371 | -6.6694 | OK
14 | 11 kV DPH Sw/S-2 |  | 11 |  | DHK60871 | 1 | 563612.73 | 574627.71 | 11014.98 | 60 |  | 660898.8 | 659432.9925 | Paribag |  |  |  |  | 11 kV DPH Sw/S-2 | 659432.9925 | 837287.7716 | -177854.7792 | -21.2418 | OK
17 | 11 kV New Elephant Road Feeder | C301E | 11 |  | DHK60981 | 1 | 143677.95 | 154561.42 | 10883.47 | 60 |  | 653008.2 | 651559.893 | Paribag |  |  |  |  | 11 kV New Elephant Road Feeder | 651559.893 | 749226.2334 | -97666.3404 | -13.0356 | OK
18 | 11 kV Dhanmondi O/H Feeder | C301D | 11 |  | DHK61110 | 1 | 501237.66 | 518925.19 | 17687.53 | 60 |  | 1061251.8 | 1058898.0495 | Paribag |  |  |  |  | 11 kV Dhanmondi O/H Feeder | 1058898.0495 | 1248319.0123 | -189420.9629 | -15.1741 | OK
19 | 11 kV Sonargaon Feeder |  | 11 |  | DHK61115 | 1 | 449664.26 | 467590.06 | 17925.8 | 60 |  | 1075548 | 1073162.5419 | Paribag |  |  |  |  | 11 kV Sonargaon Feeder | 1073162.5419 | 1368467.8334 | -295305.2915 | -21.5793 | OK
20 | 11 kV Museum Feeder | D301M | 11 |  | DHK61107 | 1 | 556021.54 | 557180.75 | 1159.21 | 60 |  | 69552.6 | 69398.3393 | Ramna |  |  |  |  | 11 kV Museum Feeder | 69398.3393 | 102971.2474 | -33572.9081 | -32.6042 | OK
21 | 11 kV Shanta property |  | 11 |  | DHK61112 | 1 | 354429.92 | 356318.61 | 1888.69 | 60 |  | 113321.4 | 113070.0644 | Paribag |  |  |  |  | 11 kV Shanta property | 113070.0644 | 143833.6059 | -30763.5414 | -21.3883 | OK
22 | 11 kV BIRDEM RMU Feeder | C601R | 11 |  | DHK61108 | 1 | 756877.47 | 764862.93 | 7985.46 | 60 |  | 479127.6 | 478064.9428 | Kakrail |  |  |  |  | 11 kV BIRDEM RMU Feeder | 478064.9428 | 635092.6529 | -157027.7101 | -24.7252 | OK
23 | 11 kV Azimpur-2 Feeder |  | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 |  | 11 |  | DHK60978 | 1 | 838049.17 | 848198.12 | 10148.95 | 60 |  | 608937 | 607586.4385 | Kakrail |  |  |  |  | 11 kV DPH Sw/S-1 | 607586.4385 | 690742.9278 | -83156.4892 | -12.0387 | OK
|  |  | 10: Total | 8662263.2599 | 8681518 | 8662263.2599 | -0.22179
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Paribag at 33 KV level |  |  | 6943770.0278
[7 empty] | Azimpur at 33 KV level |  |  | 0
[7 empty] | Ramna at 33 KV level |  |  | 651038.4521
[7 empty] | Kakrail at 33 KV level |  |  | 1085651.3814
|  |  | 7: Total =; 10: 8680459.8613 | 2.1828e-10
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 |  | 33 | 0 | BD001820 | 1 | 1904.37 | 1914.8 | 10.43 | 240000 | 0 | 2503200 | 2506864.7558
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.44 | 462.91 | 0.47 | 240000 | 0 | 112800 | 112965.1424
|  |  | 10: Total | 0 | 2616000 | 2619829.8982
MOGBAZAR 33 KV SIDE
17 | 33KV Karwan Bazar |  | 33 | 0 | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAWRANBAZAR 33 KV SIDE (RECEIVING) | [10 empty] | 2616000 | 2619829.8982
1 | 33 kV Dhanmondi Circuit-1 |  | 33 |  | DHK61036 | 1 | 3474.8 | 3484.34 | 9.54 | 270000 | 2575800
5 | 33 kV Dhanmondi Circuit-2 |  | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar |  | 33 |  | DHK 61038 | 1 | 1061.95 | 1061.95 | 0 | 270000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 2575800 | 0 | 2619829.8982
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | DHK61039 | 1 | 5220.3 | 5234.68 | 14.38 | 180000 |  | 2588400
3 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 2588400
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4: 2619829.8982; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 2619829.8982
| MOGBAZAR 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 2619829.8982 | 33 KV TX HV SIDE |  | 2588400
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 31429.8982
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.2%
| TOTAL IMPORT |  | 4: 2619829.8982
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK00182 | 1 | 15558.9 | 15816.8 | 257.9 | 10000 | 2579000 |  | 2619829.8982
15 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 2579000 | 2588400 | 2619829.8982
| KAWRANBAZAR 11 KV SIDE |  | 7: 0; 8: 0
6 | WASA Bhaban | C605M | 11 |  | 8536188 | 1.4 | 271216 | 271216 | 0 | 1000 | 897180 | 897180 | 897559.4039 | Shere b.nagar | From Customer End | 90 |  |  | WASA Bhaban | 897559.4039 | 933040.8402 | -35481.4363 | -3.8028 | OK
7 | Sangsad Bhaban |  | 11 |  | 8536178 | 1.4 | 586004 | 587512 | 1508 | 44 |  | 92892.8 | 92932.083 | Shere b.nagar |  | 30 | 5 | 80 | Sangsad Bhaban | 92932.083 | 218864.9052 | -125932.8223 | -57.5391 | CHECK
8 | Air Port Road (West) | D505A | 11 |  | 8536182 | 1.4 | 4761.7 | 5005.7 | 244 | 1000 |  | 341600 | 341744.4575 | Shere b.nagar |  | 60 | 30 | 90 | Air Port Road (West) | 341744.4575 | 711222.6426 | -369478.1851 | -51.9497 | CHECK
9 | ICC (PM Office) | C172C | 11 |  | 8536193 | 1.4 | 32421.4 | 32437.1 | 15.7 | 1000 |  | 21980 | 21989.295 | Shere b.nagar |  | 20 |  |  | ICC (PM Office) | 21989.295 | 0 | 21989.295 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | D505U | 11 |  | DHK00183 | 1.4 | 18092.4 | 18493.7 | 401.3 | 444.44 |  | 249695.2808 | 249800.8732 | Shere b.nagar |  | 50 |  |  | (UTC) Tower | 249800.8732 | 276538.0329 | -26737.1598 | -9.6685 | OK
11 | Sonargaon Hotel | C605O | 11 |  | 8536190 | 1.4 | 51744.1 | 51744.1 | 0 | 1000 | 20 | 54930.96 | 54954.1895 | Kakrail | Estimated |  |  |  | Sonargaon Hotel | 54954.1895 | 46976.984 | 7977.2055 | 16.9811 | OK
12 | Panthopath | D505P | 11 |  | 8536184 | 1.4 | 39056.5 | 39621.9 | 565.4 | 1000 |  | 791560 | 791894.7388 | Shere b.nagar |  |  |  |  | Panthopath | 791894.7388 | 929616.6174 | -137721.8786 | -14.8149 | OK
13 | Titas Bhaban | C605N | 11 |  | DHK00190 | 1.4 | 57494.3 | 57763 | 268.7 | 444.44 |  | 167189.4392 | 167260.1411 | Kakrail |  |  |  |  | Titas Bhaban | 167260.1411 | 217096.7452 | -49836.6041 | -22.9559 | OK
16 | Green Road Dormatory s/s |  | 11 |  | DHK00021 | 1.4 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | [5 empty] | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 |  | 11 |  | 85-12906 | 1.4 | 69426 | 69547 | 121 | 10 |  | 1694 | 1694.7164 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-1 | 1694.7164 | 1765.989 | -71.2726 | -4.0358 | OK
27 | Aux. Transformer, AT-2 |  | 11 |  | 85-12909 | 1.4 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 2619829.8982 | 2618722.48 | 2619829.8982 | 0.042288
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail at 33 KV level |  |  | 222214.3306
[6 empty] | Shere b.nagar at 33 KV level |  |  | 2397615.5677
[6 empty] | Total = |  |  | 2619829.8982 | 0
|  |  | 9=8-7: Customer Name; 10: Customer Number | Feeder name | Consumption | OMF
|  |  | 9=8-7: Square Hospital; 10: 27529489 | Wasa Bhaban | 897180 | 6000
|  |  | 9=8-7: NOCS Name; 10: Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
|  |  | 9=8-7: ShereBangla Nagar; 10: 2984.58 | 3091.29 | 1176.17 | 1218.99
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 |  | 33 | 0 | BD001919 | 1 | 1527.47 | 1539.9 | 12.43 | 240000 | 0 | 2983200 | 2987567.4895
10 | New Ramna Circuit-2 |  | 33 | 0 | BD001816 | 1 | 1246.56 | 1253.4 | 6.84 | 240000 | 0 | 1641600 | 1644003.349
|  |  | 10: Total | 0 | 4624800 | 4631570.8385
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 982800 | 989122.95
|  |  | 10: Total | 0 | 982800 | 989122.95
| NEW RAMNA 33 KV SIDE (RECEIVING) | [10 empty] | 5607600 | 5620693.7884
|  |  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 10: Total |  | 0 | 5620693.7884
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 9=8-7: 0 |  | 0
| Feeder No.2 |  | 3: 33; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.3. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 5620693.7884 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 4631570.8385; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5620693.7884
| NARINDA 33 KV SIDE |  | 4: 989122.95; 6: 33 KV NET IMPORT; 9=8-7: 5620693.7884 | 33 KV TX HV SIDE |  | 5620693.7884
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 5620693.7884
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK 00002 | 1 | 26743.5 | 27037.1 | 293.6 | 10000 | 2936000 |  | 2975113.0315
15 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK 00007 | 1 | 14836 | 14998.8 | 162.8 | 10000 | 1628000 |  | 1649688.0161
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming |  | 11 |  | DHKA2182 | 3 | 629.31 | 631.13 | 1.82 | 180000 | 982800 |  | 995892.7409 |  | PT Missing
|  |  | 7: 0; 8: 0; 10: Total | 5546800 |  | 5620693.7884
| NEW RAMNA 11 KV SIDE |  | 7: 0; 8: 0
4 | Police Bhaban | D315I | 11 | T-1 | DHK 00005 | 1 | 74352.7 | 74521.9 | 169.2 | 444.44 |  | 75199.248 | 76206.8169 | Ramna |  |  |  |  | Police Bhaban | 76206.8169 | 98323.9544 | -22117.1375 | -22.4941 | OK
5 | Baitul Mukarram (OLD Water Works) |  | 11 | T-1 | DHK 00010 | 1 | 17723.4 | 17725.1 | 1.7 | 444.44 |  | 755.548 | 765.6713 | Ramna |  |  |  |  | Baitul Mukarram (OLD Water Works) | 765.6713 | 301881.114 | -301115.4427 | -99.7464 | CHECK
6 | GPO | D3157 | 11 | T-1 | DHK 00060 | 1 | 681.6 | 1138.7 | 457.1 | 444.44 |  | 203153.524 | 205875.5083 | Ramna |  |  |  |  | GPO | 205875.5083 | 264367.4251 | -58491.9168 | -22.1252 | OK
7 | Culvert Road | D315C | 11 | T-1 | 8536184 | 1 | 40342.5 | 40530.9 | 188.4 | 444.44 | 304292.984 | 304292.984 | 308370.1012 | Ramna | T-1 - (Sum of All feeders Under T-1) |  |  |  | Culvert Road | 308370.1012 | 586507.5886 | -278137.4875 | -47.4227 | CHECK
8 | Secretariat (East) | D315E | 11 | T-1 | DHK00059 | 1 | 81748.6 | 81751 | 2.4 | 444.44 |  | 1066.656 | 1080.9478 | Ramna |  |  |  |  | Secretariat (East) | 1080.9478 | 7972.2125 | -6891.2648 | -86.4411 | CHECK
9 | Siddik Bazar | B615S | 11 | T-1 | DHK00076 | 1 | 45245.7 | 47897.2 | 2651.5 | 444.44 |  | 1178432.66 | 1194222.0745 | Bangshal |  |  |  |  | Siddik Bazar | 1194222.0745 | 1547982.2206 | -353760.1461 | -22.853 | OK
10 | Bokshi Bazar | D315X | 11 | T-1 | DHK 00206 | 1 | 91450.6 | 92431.2 | 980.6 | 444.44 |  | 435817.864 | 441657.2379 | Ramna |  |  |  |  | Bokshi Bazar | 441657.2379 | 530285.0026 | -88627.7648 | -16.7132 | OK
11 | Ramna 11 kV Sw/S Circuit-1 |  | 11 | T-1 | DHK00198 | 1 | 51162 | 51950.5 | 788.5 | 444.44 |  | 350440.94 | 355136.3778 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 355136.3778 | 406494.2583 | -51357.8805 | -12.6343 | OK
12 | TNT RMU | D315Z | 11 | T-1 | DHK 00207 | 1 | 64922.1 | 65792.5 | 870.4 | 444.44 |  | 386840.576 | 392023.72 | Ramna |  |  |  |  | TNT RMU | 392023.72 | 391967.1155 | 56.6046 | 0.014441 | OK
13 | DIT 11 kV Sw/S Circuit-1 |  | 11 | T-1 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | D315W | 11 | T-2 | DHK 00006 | 1.44 | 73143.7 | 73404.3 | 260.6 | 444.44 |  | 166782.3322 | 169016.9913 | Ramna | Sum of Feeder Under T2= 1128389 CF= (1628000/1128389)=1.44 |  |  |  | Secretariat (West) | 169016.9913 | 331909.7812 | -162892.7898 | -49.0774 | CHECK
17 | Ramna 11 kV Sw/S Circuit-2 |  | 11 | T-2 | DHK00197 | 1.44 | 89232.8 | 89265.4 | 32.6 | 444.44 |  | 20863.7914 | 21143.3381 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 21143.3381 | 3897.5261 | 17245.812 | 442.481 | FAULT
18 | Sayed Nazrul Islam Road | D315A | 11 | T-2 | DHK00186 | 1.44 | 38231 | 39861.5 | 1630.5 | 444.44 |  | 1043509.5648 | 1057491.1911 | Ramna |  |  |  |  | Sayed Nazrul Islam Road | 1057491.1911 | 977526.1249 | 79965.0662 | 8.1804 | OK
19 | Gulistan Complex | D3153 | 11 | T-2 | DHK00030 | 1.44 | 56794.4 | 57092.1 | 297.7 | 444.44 |  | 190526.0947 | 193078.8884 | Ramna |  |  |  |  | Gulistan Complex | 193078.8884 | 172686.9812 | 20391.9073 | 11.8086 | OK
20 | Mohanagor Nattomanso | D3152 | 11 | T-2 | DHK 00008 | 1.44 | 564 | 615.7 | 51.7 | 444.44 |  | 33087.6691 | 33530.9994 | Ramna |  |  |  |  | Mohanagor Nattomanso | 33530.9994 | 53280.9537 | -19749.9542 | -37.0676 | OK
21 | DIT 11 kV Sw/S Circuit-2 |  | 11 | T-2 | DHK00196 | 1.44 | 29843.6 | 30109.4 | 265.8 | 444.44 |  | 170110.2989 | 172389.5484 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-2 | 172389.5484 | 335231.5364 | -162841.988 | -48.576 | CHECK
22 | Jail | B678Z | 11 | T-2 | DHK00009 | 1.44 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | D315K | 11 | T-3 | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 | 44349 | 44349 | 44943.217 | Ramna | T-3 - (Sum of All feeder Under T-3) |  |  |  | Kosturi Bazar | 44943.217 | 0 | 44943.217 | #DIV/0! | #DIV/0!
24 | Kaptan Bazar | B124K | 11 | T-3 | HA021101251-02 | 1 | 8299757 | 8567076 | 267319 | 1 |  | 267319 | 270900.7155 | Narinda |  |  |  |  | Kaptan Bazar | 270900.7155 | 367694.0766 | -96793.3611 | -26.3244 | OK
25 | G.T.V | D315G | 11 | T-3 | HA-021101054-02 | 1 | 73968193 | 74336827 | 368634 | 1 |  | 368634 | 373573.2004 | Ramna |  |  |  |  | G.T.V | 373573.2004 | 423322.7388 | -49749.5384 | -11.7522 | OK
26 | Kazi Alauddin Road | B615K | 11 | T-3 | HA021100951-02 | 1 | 8159834 | 8462332 | 302498 | 1 |  | 302498 | 306551.0668 | Bangshal |  |  |  |  | Kazi Alauddin Road | 306551.0668 | 320999.3644 | -14448.2976 | -4.501 | OK
28 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.4 | T-3 | 2436 | 1 | 67991 | 68252 | 261 | 10 |  | 2610 | 2644.9705 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 2644.9705 | 2870.0252 | -225.0547 | -7.8416 | OK
29 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.4 | T-3 | 2437 | 1 | 90000 | 90009 | 9 | 10 |  | 90 | 91.2059 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 91.2059 | 0 | 91.2059 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5620693.7884 | 5546379.751 | 5620693.7884 | 1.3399
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 3676630.3833
[6 empty] | Lalbag | at 33 KV level
[6 empty] | Bangshal | at 33 KV level |  | 1500773.1413
[6 empty] | Motijheel | at 33 KV level |  | 172389.5484
[6 empty] | Narinda | at 33 KV level |  | 270900.7155
[6 empty] | Total = |  |  | 5620693.7884 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 |  | 33 | 0 | BD001825 | 1 | 900.82 | 907.43 | 6.61 | 240000 | 0 | 1586400 | 1588722.5346
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1696.22 | 1715.95 | 19.73 | 240000 | 0 | 4735200 | 4742132.4672
|  |  | 10: Total | 0 | 6321600 | 6330855.0018
ULLON 33 KV SIDE
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder.(import) |  | 33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAKRAIL 33 KV SIDE (RECEIVING) | [10 empty] | 6321600 | 6330855.0018
5 | 33 kV Dhanmondi-2 |  | 33 |  | 06604376 | 1 | 5396.96 | 5423.02 | 26.06 | 180000 | 4690800
2 | 33 kV Dhanmondi-1 |  | 33 |  | 06604375 | 1 | 2122.61 | 2127.01 | 4.4 | 180000 | 792000
| 33 KV Kakrail From ULLON |  | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola |  | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
|  |  | 10: Total | 5482800
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 4: 6330855.0018; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KAKRAIL 33 KV NET IMPORT |  | 6330855.0018
| ULLON 33 KV SIDE |  | 4: 0; 6: KAKRAIL 33 KV NET IMPORT; 9=8-7: 6330855.0018 | KAKRAIL KV NET IMPORT |  | 6155556.325
| Taltola 33 KV SIDE |  | 4: 0 | LOSS UNITS=> |  | 175298.6768
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.769%
| TOTAL IMPORT |  | 4: 6330855.0018
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK00017 | 1 | 20985.2 | 21155 | 169.8 | 8888.89 | 1509333.522 |  | 1552316.5044
15 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK00018 | 1 | 7933.3 | 8456 | 522.7 | 8888.89 | 4646222.803 |  | 4778538.4974
|  |  | 7: 0; 8: 0; 10: Total | 6155556.325 |  | 6330855.0018
| KAKRAIL 11 KV SIDE |  | 7: 0; 8: 0
7 | Pioneer | D304P | 11 |  | 06604395 | 1 | 24231.18 | 24289.89 | 58.71 | 8000 |  | 469680 | 477280.9094 | Ramna |  |  |  |  | Pioneer | 477280.9094 | 570908.4836 | -93627.5741 | -16.3998 | OK
8 | Pir Saheber Goli | D604L | 11 |  | DHK-00102 | 1 | 95296.1 | 97162 | 1865.9 | 444.444 |  | 829288.0596 | 842708.566 | Rajarbag |  |  |  |  | Pir Saheber Goli | 842708.566 | 1050082.5289 | -207373.9629 | -19.7483 | OK
9 | Montri Para | C604B | 11 |  | DHK-00110 | 1 | 12973.5 | 13024.5 | 51 | 2222.22 |  | 113333.22 | 115167.3103 | Kakrail |  |  |  |  | Montri Para | 115167.3103 | 51314.9581 | 63852.3523 | 124.4322 | FAULT
10 | Baily Road 11 kV Sw/S-2 |  | 11 |  | 9119865 | 1 | 73065.6 | 73065.6 | 0 | 1000 |  | 0 | 0 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-2 | 0 | 684720.7122 | -684720.7122 | -100 | CHECK
11 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | D3046 | 11 |  | 1025651 | 1 | 30191.9 | 30298.4 | 106.5 | 1000 |  | 106500 | 108223.5072 | Ramna |  |  |  |  | High Court | 108223.5072 | 181822.4648 | -73598.9576 | -40.4785 | CHECK
13 | Secretaiat |  | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | D604N | 11 |  | 06604402 | 1 | 5809.98 | 5832.19 | 22.21 | 40000 |  | 888400 | 902777.1248 | Rajarbag |  |  |  |  | Shanti Nagar Bazar | 902777.1248 | 1155190.1048 | -252412.98 | -21.8503 | OK
17 | Tottho Bhovon |  | 11 |  | 9119867 | 1 | 33058.1 | 33187 | 128.9 | 1000 |  | 128900 | 130986.0101 | Kakrail |  |  |  |  | Tottho Bhovon | 130986.0101 | 77638.4937 | 53347.5165 | 68.7127 | FAULT
18 | Central Police Hospital/ PNT (Circuit House) |  | 11 |  | DHK00199 | 1 | 79666.3 | 79852.8 | 186.5 | 2222.22 |  | 414444.03 | 421151.0466 | Kakrail |  |  |  |  | Central Police Hospital/ PNT (Circuit House) | 421151.0466 | 183819.1042 | 237331.9424 | 129.1117 | FAULT
19 | Baily Road 11 kV Sw/S-1 |  | 11 |  | DHK00027 | 1 | 58241 | 59278.4 | 1037.4 | 2222.22 |  | 2305331.028 | 2342638.5829 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-1 | 2342638.5829 | 1933413.755 | 409224.8279 | 21.1659 | OK
20 | Bijoy Nagar | D304B | 11 |  | D1025656 | 1 | 70601.3 | 71184.1 | 582.8 | 1000 |  | 582800 | 592231.5492 | Ramna |  |  |  |  | Bijoy Nagar | 592231.5492 | 791846.372 | -199614.8228 | -25.2088 | OK
21 | Shilpakala Academy | D304F | 11 |  | D0086137 | 1 | 27773.3 | 28085.4 | 312.1 | 1000 |  | 312100 | 317150.7661 | Ramna |  |  |  |  | Shilpakala Academy | 317150.7661 | 438773.4499 | -121622.6838 | -27.7188 | OK
22 | Judges Complex | C604JC | 11 |  | 06604344 | 1 | 686.38 | 688.26 | 1.88 | 40000 |  | 75200 | 76416.9741 | Kakrail |  |  |  |  | Judges Complex | 76416.9741 | 88351.0596 | -11934.0855 | -13.5076 | OK
23 | Auxiliary Transformer, AT-1 |  | 11 |  | 39333 | 1 | 499183 | 499707 | 524 | 1 |  | 524 | 532.48 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-1 | 532.48 | 2999.9201 | -2467.4401 | -82.2502 | CHECK
24 | Auxiliary Transformer, AT-2 |  | 11 |  | 39254 | 1 | 1228762 | 1232295 | 3533 | 1 |  | 3533 | 3590.1751 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-2 | 3590.1751 | 0 | 3590.1751 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6330855.0018 | 6230033.3376 | 6330855.0018 | 1.6183
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1494886.732
[6 empty] | Rajarbag | at 33 KV level |  | 1745485.6908
[6 empty] | Kakrail | at 33 KV level |  | 3090482.5791
[6 empty] | Total = |  |  | 6330855.0018 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 |  | 33 | 0 | BD001920 | 1 | 766.57 | 774.65 | 8.08 | 240000 | 0 | 1939200 | 1942039.0438
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 175.9 | 179.89 | 3.99 | 240000 | 0 | 957600 | 959001.9536
|  |  | 10: Total |  | 2896800 | 2901040.9974 | 0.1464
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 |  | 33 |  | BD017073 | 1 | 81207.61 | 83155.73 | 1948.12 | 1000 | 1948120
4 | 33 kV Dhanmondi Incoming Circuit-2 |  | 33 |  | BD017074 | 1 | 42162.3 | 43117.42 | 955.12 | 1000 | 955120
| 33 KV Ullon-1 Feeder |  | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 2903240 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0 |  | Total
[7 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017072 | 1 | 11748.6 | 13947.66 | 2199.06 | 888.89 |  | 1954722.4434
6 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017076 | 1 | 40308.75 | 41386.94 | 1078.19 | 888.89 |  | 958392.3091
|  |  | 10: Total |  | 2913114.7525
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 2901040.9974; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 2901040.9974
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 2901040.9974 | 33/11 KV XF HV SIDE |  | 2913114.7525
[11 empty] | LOSS UNITS=> |  | -12073.7551
[11 empty] | LOSS % IN => |  | -0.4162%
| TOTAL IMPORT |  | 4: 2901040.9974
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD017081 | 1 | 86969.48 | 88901.37 | 1931.89 | 1000 | 1931890 |  | 1948168.8308
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD017082 | 1 | 34894.17 | 35839.08 | 944.91 | 1000 | 944910 |  | 952872.1666
|  |  | 7: 0; 8: 0; 10: Total | 2876800 |  | 2901040.9974
| BSMMU HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Jamuna (F1) | C6101JG | 11 |  | BD017073 | 1 | 0.4177 | 0.4288 | 0.0111 | 2000 |  | 22.2 | 22.3208 | Kakrail |  |  |  |  | 11 kV Jamuna (F1) | 22.3208 | 20.9345 | 1.3863 | 6.6221 | OK
9 | 11 kV Pukur Par (F2) | C6101PP | 11 |  | BD017074 | 1 | 3012.43 | 3027.97 | 15.54 | 2000 |  | 31080 | 31249.1675 | Kakrail |  |  |  |  | 11 kV Pukur Par (F2) | 31249.1675 | 40077.555 | -8828.3875 | -22.0283 | OK
10 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 |  | BD017075 | 1 | 1878.4 | 1901.41 | 23.01 | 2000 |  | 46020 | 46270.4855 | Kakrail |  |  |  |  | 11 kV BSMMU Convention center (F3) | 46270.4855 | 47907.8759 | -1637.3905 | -3.4178 | OK
11 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 |  | BD017076 | 1 | 3350.25 | 3398.96 | 48.71 | 2000 |  | 97420 | 97950.2541 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 97950.2541 | 144186.603 | -46236.3489 | -32.067 | OK
12 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 |  | BD017077 | 1 | 15660.41 | 15821.61 | 161.2 | 2000 |  | 322400 | 324154.8134 | Kakrail |  |  |  |  | 11 kV Holi Family Feeder (F5) | 324154.8134 | 500335.3629 | -176180.5495 | -35.2125 | OK
13 | 11 kV Navy House Feeder (F6) | C6101NH | 11 |  | BD017078 | 1 | 27893.89 | 28087.2 | 193.31 | 2000 |  | 386620 | 388724.3609 | Kakrail |  |  |  |  | 11 kV Navy House Feeder (F6) | 388724.3609 | 492746.5943 | -104022.2334 | -21.1107 | OK
14 | 11 kV Paribagh Feeder (F7) | C31016 | 11 |  | BD017079 | 1 | 34847.13 | 35288.67 | 441.54 | 2000 |  | 883080 | 887886.5777 | Paribag |  |  |  |  | 11 kV Paribagh Feeder (F7) | 887886.5777 | 1159088.7861 | -271202.2084 | -23.3979 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 |  | BD017080 | 1 | 7150.9 | 7242.66 | 91.76 | 2000 |  | 183520 | 184518.8938 | Paribag |  |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 184518.8938 | 291332.2219 | -106813.3281 | -36.6638 | OK
18 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 |  | BD017083 | 1 | 2558.44 | 2605.46 | 47.02 | 2000 |  | 94040 | 94551.8569 | Paribag |  |  |  |  | 11 kV Oncology Bhaban (F9) | 94551.8569 | 114173.7278 | -19621.8709 | -17.186 | OK
19 | Rupayan Trade Center | C6101RT | 11 |  | BD017084 | 1 | 1722.15 | 1801.76 | 79.61 | 2000 |  | 159220 | 160086.6296 | Kakrail |  |  |  |  | Rupayan Trade Center | 160086.6296 | 211841.3807 | -51754.7511 | -24.4309 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 |  | BD017085 | 1 | 2325.72 | 2367.58 | 41.86 | 2000 |  | 83720 | 84175.6854 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 84175.6854 | 86093.2711 | -1917.5857 | -2.2273 | OK
21 | 11 kV BSMMU RMU (F12) | C3101RM | 11 |  | BD017086 | 1 | 2390.79 | 2411.92 | 21.13 | 2000 |  | 42260 | 42490.0199 | Paribag |  |  |  |  | 11 kV BSMMU RMU (F12) | 42490.0199 | 182774.5854 | -140284.5655 | -76.7528 | CHECK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 |  | BD017087 | 1 | 4595.64 | 4656.67 | 61.03 | 2000 |  | 122060 | 122724.3689 | Paribag |  |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 122724.3689 | 185834.2481 | -63109.8792 | -33.9603 | OK
23 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 |  | BD017088 | 1 | 1140.23 | 1159.47 | 19.24 | 2000 |  | 38480 | 38689.4455 | Paribag |  |  |  |  | 11 kV BCS Academy RMU (F14) | 38689.4455 | 46559.2088 | -7869.7633 | -16.9027 | OK
24 | Spare |  | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | C310113 | 11 |  | BD017090 | 1 | 2367.14 | 2560.35 | 193.21 | 2000 |  | 386420 | 388523.2723 | Paribag |  |  |  |  | BSMMU Super Specialist Hospital RMU | 388523.2723 | 426621.648 | -38098.3756 | -8.9302 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKD4418 | 1 | 3035.81 | 3122.06 | 86.25 | 100 |  | 8625 | 8671.9456 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 8671.9456 | 7126.7998 | 1545.1458 | 21.6808 | OK
27 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 1915.93 | 1919.42 | 3.49 | 100 |  | 349 | 350.8996 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 350.8996 | 3914.154 | -3563.2544 | -91.0351 | CHECK
|  |  | 10: Grand Total | 2901040.9974 | 2885336.2 | 2901040.9974 | 0.5443
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 1132633.7173
[6 empty] | Paribag | at 33 KV level |  | 1768407.2801
[6 empty] | Total = |  |  | 2901040.9974 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 |  | 132 |  | 8993518 | 1 | 1188.499 | 1202.084 | 13.585 | 960000 | 0 | 13041600
|  |  | 132 |  |  | 1 | 70.101 | 70.101 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 |  | 132 |  | 5014660 | 1 | 366.009 | 379.667 | 13.658 | 960000 | 0 | 13111680
|  |  | 132 |  |  | 1 | 4.408 | 4.408 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 |  | 132 |  | 38992597 | 1 | 752.493 | 780.158 | 27.665 | 1440000 | 0 | 39837600
|  |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 65990880
|  |  | 10: Net Total | 65990880
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 |  | 132 | RECEIVE | 6604452 | 1 | 340574 | 353173 | 12599 | 1000 | 12599000
|  |  | 132 |  |  | 1 | 6797 | 6797 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) |  | 132 |  |  | 1 | 4584458 | 4624269 | 39811 | 1000 | 39811000
|  |  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar |  | 132 |  |  | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  |  | 1 | 645542 | 645583 | 41 | 1000 |  | 41000
| Kallyanpur-2 |  | 132 |  | 6604428 | 1 | 437971 | 450374 | 12403 | 1000 | 12403000
|  |  | 132 |  |  | 1 | 7153 | 7156 | 3 | 1000 |  | 3000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 64813000 | 44000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 64769000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
6 | Kamrangirchar |  | 132 |  | SIEM491 | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  | SIEM491 | 1 | 645542 | 645583 | 41 | 1000 | From Kamrangirchar | 24940800
|  |  | 7: 0; 8: 0; 10: Total |  | 24940800
| LALBAGH 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 | NET IMPORT | SIEM494 | 1 | 2299916 | 2319760 | 19844 | 1000 |  | 19844000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | SIEM499 | 1 | 2411035 | 2431004 | 19969 | 1000 |  | 19969000
|  |  | 10: Total |  | 39813000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 65990880; 6: EXPORT TO OTHER S/S; 9=8-7: 24940800 | 132 KV NET IMPORT |  | 41050080
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 41050080 | 132/33 KV GT LV SIDE |  | 39839000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1211080
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.95%
| 132 KV TOTAL IMPORT |  | 4: 65990880
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | SIEM0517 | 1 | 2299099 | 2318936 | 19837 | 1000 | 19837000
16 | 132/33 kV GT-2 Incoming (LV) |  | 33 |  | SIEM0518 | 1 | 2385093 | 2405095 | 20002 | 1000 | 20002000
|  |  | 7: 0; 8: 0; 10: Total | 39839000 |  | 0
| LALBAGH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SIEM0502 | 1 | 863359 | 868903 | 5544 | 2000 |  | 11088000 | 11101003.1555 |  | 22306128.2741 | Lalbagh New 33/11 kv ss | 2.2403 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 11101003.1555 | 12877960.4874 | -1776957.3319 | -13.7984 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SIEM0501 | 1 | 857191 | 862787 | 5596 | 2000 |  | 11192000 | 11205125.1187 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 11205125.1187 | 12891990.9502 | -1686865.8315 | -13.0846 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 22280000 | 22306128.2741 | [5 empty] | 33 KV Feeders | 22306128.2741 | 25769951.4376 | -3463823.1634 | -13.4413 | OK
9 | Spare |  | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 4981835.4709 | Mitford 33/11 kv ss | 1.1327 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 |  | 33 |  | SIEM0513 | 1 | 328991 | 330557 | 1566 | 2000 |  | 3132000 | 3135672.9692 | [5 empty] | Mitford Circuit-1 | 3135672.9692 | 3545698.3817 | -410025.4124 | -11.564 | OK
12 | Azimpur Circuit-1 |  | 33 |  | SIEM0503 | 1 | 76611 | 77848 | 1237 | 2000 |  | 2474000 | 2476901.3173 |  | 2538974.0262 | Azimpur 33/11 kv ss | 1.8143 |  | Azimpur Circuit-1 | 2476901.3173 | 4040773.2829 | -1563871.9656 | -38.7023 | OK
15 | Azimpur Circuit-2 |  | 33 |  | SIEM0507 | 1 | 91012 | 91043 | 31 | 2000 |  | 62000 | 62072.7088 | [5 empty] | Azimpur Circuit-2 | 62072.7088 | 1880082.0136 | -1818009.3047 | -96.6984 | CHECK
17 | Lalbagh old |  | 33 |  | SIEM0509 | 1 | 244897 | 249834 | 4937 | 2000 |  | 9874000 | 9885579.4694 |  | 9885579.4694 | Lalbagh old 33/11 kv ss | 0.1395 |  | Lalbagh old | 9885579.4694 | 10879621.716 | -994042.2466 | -9.1367 | OK
18 | Mitford Circuit-2 |  | 33 |  | SIEM0511 | 1 | 364401 | 365323 | 922 | 2000 |  | 1844000 | 1846162.5017 | [5 empty] | Mitford Circuit-2 | 1846162.5017 | 2649753.1151 | -803590.6134 | -30.327 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKC7982 | 1 | 7621.11 | 7679.09 | 57.98 | 120 |  | 6957.6 | 6965.7593 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-1 | 6965.7593 | 7179.5882 | -213.8289 | -2.9783 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHU02670 | 1 | 27106.6 | 27106.6 | 0 | 120 |  | 0 | 0 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 2056.465 | -2056.465 | -100 | CHECK
|  |  | 10: Total |  | 17392957.6 | 17413354.7259 | [5 empty] | 0 | 17413354.7259 | 23005164.5624 | -5591809.8366 | -24.3068 | OK
|  |  | 9=8-7: Grand Total | 39719483 | 39672957.6 | 39719483 | 0.11727
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK98833 | 1 | 615022.5 | 620534.9 | 5512.4 | 2000 | 11024800 |  | 11105167.5117
11 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK98832 | 1 | 611856.25 | 617416.2 | 5559.95 | 2000 | 11119900 |  | 11200960.7624
|  |  | 7: 0; 8: 0; 10: Total | 22144700 |  | 22306128.2741
| LALBAGH 11 kV SIDE |  | 7: 0; 8: 0
3 | Chata Mosjid |  | 11 |  |  | 1 | 182187.1 | 184283.1 | 2096 | 1000 |  | 2096000 | 2142956.195 | Kamrangirchar |  |  |  |  | Chata Mosjid | 2142956.195 | 3224151.7427 | -1081195.5476 | -33.5343 | OK
4 | AC mosjid | A3109X | 11 |  |  | 1 | 11622.59 | 12645 | 1022.41 | 1000 |  | 1022410 | 1045314.8108 | Lalbag |  |  |  |  | AC mosjid | 1045314.8108 | 1227807.0733 | -182492.2626 | -14.8633 | OK
5 | Kazi Reaz Uddin Road | A3109K | 11 |  |  | 1 | 29.8902 | 1763.086 | 1733.1958 | 1000 |  | 1733195.792 | 1772024.1697 | Lalbag |  |  |  |  | Kazi Reaz Uddin Road | 1772024.1697 | 2150154.7266 | -378130.5569 | -17.5862 | OK
6 | Nazimuddin | A3109M | 11 |  |  | 1 | 7907.4712 | 8409.7048 | 502.2336 | 1000 |  | 502233.6 | 513485.0212 | Lalbag |  |  |  |  | Nazimuddin | 513485.0212 | 619180.2481 | -105695.2269 | -17.0702 | OK
7 | Kamal Bagh | A3109U | 11 |  |  | 1 | 21.7349 | 1189.24 | 1167.5051 | 1000 | 110 | 1337961.24 | 1367935.271 | Lalbag | Estimated |  |  |  | Kamal Bagh | 1367935.271 | 1559969.3577 | -192034.0868 | -12.3101 | OK
8 | Rahamatganj | A3109B | 11 |  |  | 1 | 20350.666 | 22490 | 2139.334 | 1000 |  | 2139334 | 2187260.9964 | Lalbag |  |  |  |  | Rahamatganj | 2187260.9964 | 2312778.458 | -125517.4615 | -5.4271 | OK
9 | Water Works 11kV Sw/S-1 |  | 11 |  |  | 1 | 6144.4552 | 7433.728 | 1289.2728 | 1000 |  | 1289272.8 | 1318156.0753 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-1 | 1318156.0753 | 1695142.4767 | -376986.4014 | -22.2392 | OK
12 | City Colony | A3109J | 11 |  |  | 1 | 3450.24 | 5297.59 | 1847.35 | 1000 |  | 1847350 | 1888735.7476 | Lalbag |  |  |  |  | City Colony | 1888735.7476 | 1983609.3649 | -94873.6173 | -4.7829 | OK
13 | Water Works 11kV Sw/S-2 |  | 11 |  |  | 1 | 10455.924 | 12227.5 | 1771.576 | 1000 |  | 1771576 | 1811264.2005 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-2 | 1811264.2005 | 2752272.8848 | -941008.6843 | -34.1902 | OK
14 | Chun Goli | A3109H | 11 |  |  | 1 | 2584.3304 | 3396.59 | 812.2596 | 1000 |  | 812259.6 | 830456.4608 | Lalbag |  |  |  |  | Chun Goli | 830456.4608 | 905187.2228 | -74730.762 | -8.2558 | OK
15 | Alir Ghat | A3109L | 11 |  |  | 1 | 129316.3 | 131133.1 | 1816.8 | 1000 |  | 1816800 | 1857501.3431 | Lalbag |  |  |  |  | Alir Ghat | 1857501.3431 | 1968110.7302 | -110609.3872 | -5.6201 | OK
16 | Club Ghat | A3109C | 11 |  |  | 1 | 27337.512 | 30001.5 | 2663.988 | 1000 |  | 2663988 | 2723668.6966 | Lalbag |  |  |  |  | Club Ghat | 2723668.6966 | 2705806.9627 | 17861.7339 | 0.66013 | OK
17 | Debidas Ghat | A3109V | 11 |  |  | 1 | 4371.9 | 6998.987 | 2627.087 | 1000 |  | 2627087 | 2685941.0122 | Lalbag |  |  |  |  | Debidas Ghat | 2685941.0122 | 2625728.7516 | 60212.2606 | 2.2932 | OK
18 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 22144700 | 21659468.032 | 22144700 | 2.2403
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 2142956.195
[6 empty] | Lalbag | at 33 KV level |  | 20001743.805
[6 empty] | Total = |  |  | 22144700 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old |  | 33 | 0 | SIEM0509 | 1 | 244897 | 249834 | 4937 | 2000 | 0 | 9874000 | 9885579.4694
|  |  | 10: Total |  | 9874000 | 9885579.4694 | 0.11727
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 |  | 33 | 0 | 30799098 | 1 | 1760.74 | 1761.57 | 0.83 | 240000 | 0 | 199200 | 198362.7193
|  |  | 10: Total |  | 199200 | 198362.7193
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming |  | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0 | 10083942.1887
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 4: 9885579.4694; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALBAGH OLD 33 KV NET IMPORT |  | 10083942.1887
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 198362.7193; 6: LALBAGH OLD 33 KV NET IMPORT; 9=8-7: 10083942.1887 | 33 KV TX HV SIDE |  | 10083942.1887
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 10083942.1887
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) |  | 11 |  | 8838010 | 1 | 88171.7 | 88171.7 | 0 | 1000 | 0 |  | 0
27 | 33/11 kV T1 Incoming (LV) |  | 11 |  | 06604426 | 1 | 36460.24 | 36643.04 | 182.8 | 16000 | 2924800 |  | 7020927.9455
28 | 33/11 kV T2 Incoming (LV) |  | 11 |  |  | 1 | 610761 | 612037 | 1276 | 1000 | 1276000 |  | 3063014.2432
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 4200800 |  | 10083942.1887
| LALBAGH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [6 empty] | 250
15 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  | 230 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | A319R | 11 |  | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2921891.112 | 2925967.2197 | Lalbag | 235 |  | 20 |  | Sowari Ghat | 2925967.2197 | 2836655.3487 | 89311.871 | 3.1485 | OK
17 | Novo Kumar (Kara Odidoptor) | A3202 | 11 |  | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 621678.96 | 622546.217 | Lalbag | 50 |  | 6.6667 |  | Novo Kumar (Kara Odidoptor) | 622546.217 | 543189.3221 | 79356.8949 | 14.6094 | OK
19 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | A320A | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1616365.296 | 1618620.1641 | Lalbag | 130 |  |  |  | Eidgah | 1618620.1641 | 1207087.3824 | 411532.7817 | 34.093 | OK
23 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | A3201 | 11 |  |  | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 1367693.712 | 1369601.6773 | Lalbag | 110 |  |  |  | Modumoti | 1369601.6773 | 2052048.5501 | -682446.8728 | -33.2569 | OK
25 | Lalbagh O/H | A320Y | 11 |  | 61389152 | 1 | 443210 | 443574 | 364 | 1000 | Estimated | 994686.336 | 996073.9471 | Lalbag | 80 |  |  |  | Lalbagh O/H | 996073.9471 | 965669.9059 | 30404.0412 | 3.1485 | OK
26 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | A320G | 11 |  | 61389109 | 1 | 405569 | 406689 | 1120 | 1000 |  | 1120000 | 1121562.4267 | Lalbag |  |  |  |  | Water Works 11 kV Sw/S-2 | 1121562.4267 | 955036.4181 | 166526.0086 | 17.4366 | OK
31 | Islambagh | A320D | 11 |  | 61389186 | 1 | 503360 | 504200 | 840 | 1000 |  | 840000 | 841171.82 | Lalbag |  |  |  |  | Islambagh | 841171.82 | 869765.3094 | -28593.4893 | -3.2875 | OK
32 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | A320F | 11 |  | 61389202 | 1 | 15746 | 15795 | 49 | 1000 |  | 49000 | 49068.3562 | Lalbag |  |  |  |  | WASA Low Lift Pump | 49068.3562 | 57181.8023 | -8113.4462 | -14.1889 | OK
34 | Shahi Mosjid | D920M | 11 |  | 06604459 | 1 | 36593.61 | 36660.02 | 66.41 | 8000 |  | 531280 | 532021.1483 | Azimpur |  |  |  |  | Shahi Mosjid | 532021.1483 | 1405027.1069 | -873005.9586 | -62.1345 | CHECK
35 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer |  | 0.415 |  | 5395822 | 1 | 67756.97 | 75056 | 7299.03 | 1 |  | 7299.03 | 7309.2123 | Lalbag |  |  |  |  | 33/0.4 kV Auxiliary Transformer | 7309.2123 | 7143.8831 | 165.3292 | 2.3143 | OK
|  |  | 10: Grand Total | 10083942.1887 | 10069894.446 | 10083942.1887 | 0.1395
33/0.4 kV Auxiliary Transformer meter change at 30 April 2023
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Lalbag | at 33 KV level |  | 9551921.0405
[6 empty] | Azimpur | at 33 KV level |  | 532021.1483
[6 empty] | Total = |  |  | 10083942.1887 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 |  | 33 | 0 | SIEM0513 | 1 | 328991 | 330557 | 1566 | 2000 | 0 | 3132000 | 3135672.9692
18 | Mitford Circuit-2 |  | 33 | 0 | SIEM0511 | 1 | 364401 | 365323 | 922 | 2000 | 0 | 1844000 | 1846162.5017
|  |  | 10: Total | 0 | 4976000 | 4981835.4709
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 1267.61 | 1273.62 | 6.01 | 540000 |  | 3245400
| Lalbagh Circuit-2 |  | 33 |  | DHK68131 | 1 | 1310.98 | 1313.28 | 2.3 | 540000 |  | 1242000
|  |  | 7: 0; 8: 0; 10: Total |  | 4487400
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
1 | Kumartuly Circuit-1 |  | 33 |  | DHK-66493 | 1 | 1304145 | 1305659 | 1514 | 180 |  | 132570 |  |  | From Kumertully End
6 | Kumartuly Circuit-2 |  | 33 |  | DHK-60914 | 1.1 | 786422.9 | 792788.8 | 6365.9 | 180 |  | 1271160 |  |  | From Kumertully End
|  |  | 7: 0; 8: 0; 10: Total |  | 1403730
[7 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-66494 | 1 | 3027889 | 3056740 | 28851 | 180 | From Downstream | 3211313.4
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHKA-2193 | 1 | 655.1572 | 669.48 | 14.3228 | 180000 |  | 2578104
|  |  | 10: Total |  | 5789417.4
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 4: 4981835.4709; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5789417.4
| IMPORT-2 |  | 4: 1403730; 6: 33 KV NET IMPORT; 9=8-7: 5789417.4 | 33 KV TX HV SIDE |  | 5789417.4
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 6385565.4709
11 KV SIDE of___MIDFORT 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK-66484 | 1 | 2859740 | 2877061 | 17321 | 180 | 3117780 |  | 3198982.32
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK-66476 | 1 | 2138177 | 2152203 | 14026 | 180 | 2524680 |  | 2590435.08
|  |  | 7: 0; 8: 0; 10: Total | 5642460 |  | 5789417.4
| MIDFORT 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | A319Z | 11 |  | DHK-60904 | 1 | 1004599.4 | 1005415 | 815.6 | 60 | 25 | 304082.1 | 307526.3862 | Lalbag | Estimated |  |  |  | Chawk Bazar | 307526.3862 | 440824.2804 | -133297.8941 | -30.2383 | OK
10 | Spare |  | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | B688D | 11 |  | DHK-66485 | 1 | 867960 | 871687 | 3727 | 60 |  | 223620 | 226152.9057 | Bangshal |  |  |  |  | Chatrabas | 226152.9057 | 282876.7415 | -56723.8358 | -20.0525 | OK
12 | Begum Bazar | B678G | 11 |  | DHK-66481 | 1 | 3818719 | 3843354 | 24635 | 60 |  | 1478100 | 1494842.1873 | Bangshal |  |  |  |  | Begum Bazar | 1494842.1873 | 1874630.1846 | -379787.9972 | -20.2594 | OK
13 | SCC ROAD | B688R | 11 |  | DHK-60901 | 1 | 179474.4 | 198202.9 | 18728.5 | 60 |  | 1123710 | 1136438.0721 | Bangshal |  |  |  |  | SCC ROAD | 1136438.0721 | 1342334.3996 | -205896.3275 | -15.3387 | OK
16 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | B619A | 11 |  | DHK-61104 | 1 | 745406.5 | 754499.2 | 9092.7 | 60 |  | 545562 | 551741.488 | Bangshal |  |  |  |  | Armanitola | 551741.488 | 743803.3265 | -192061.8385 | -25.8216 | OK
18 | Mitford Hospital (RMU) |  | 11 |  | DHK-61101 | 1 | 425420.5 | 430089.5 | 4669 | 60 |  | 280140 | 283313.0981 | Bangshal |  |  |  |  | Mitford Hospital (RMU) | 283313.0981 | 415582.0452 | -132268.947 | -31.8274 | OK
19 | Emamganj | B688I | 11 |  | DHK-68130 | 1 | 1494.26 | 1506.36 | 12.1 | 60000 |  | 726000 | 734223.2785 | Bangshal |  |  |  |  | Emamganj | 734223.2785 | 961780.9211 | -227557.6426 | -23.66 | OK
20 | Kamal Dho Road | A319T | 11 |  | DHK-68129 | 1 | 1226.83 | 1226.83 | 0 | 60000 |  | 0 | 0 | Lalbag |  |  |  |  | Kamal Dho Road | 0 | 601.8654 | -601.8654 | -100 | CHECK
21 | Spare |  | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | B688P | 11 |  | DHK-68127 | 1 | 1617.63 | 1634.95 | 17.32 | 60000 |  | 1039200 | 1050970.8417 | Bangshal |  |  |  |  | Panghat | 1050970.8417 | 1225999.835 | -175028.9933 | -14.2764 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | U0004460 | 1 | 5760.29 | 5801.91 | 41.62 | 100 |  | 4162 | 4209.1423 | Bangshal |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4209.1423 | 4259.2009 | -50.0586 | -1.1753 | OK
|  |  | 10: Grand Total | 5789417.4 | 5724576.1 | 5789417.4 | 1.1327
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 5481891.0138
[6 empty] | Lalbag | at 33 KV level |  | 307526.3862
[6 empty] | Total = |  |  | 5789417.4 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 |  | 33 | 0 | SIEM0503 | 1 | 76611 | 77848 | 1237 | 2000 | 0 | 2474000 | 2476901.3173
15 | Azimpur Circuit-2 |  | 33 | 0 | SIEM0507 | 1 | 91012 | 91043 | 31 | 2000 | 0 | 62000 | 62072.7088
|  |  | 10: Total | 0 | 2536000 | 2538974.0262
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 |  | 33 | 0 | BD001822 | 1 | 2072.37 | 2091.42 | 19.05 | 240000 | 0 | 4572000 | 4578693.5378
20 | Azimpur Circuit-2 |  | 33 | 0 | BD001857 | 1 | 1885.43 | 1904.68 | 19.25 | 240000 | From Downstream R Phase CT Problem | 5434560 | 5442516.3501
|  |  | 10: Total | 0 | 10006560 | 10021209.8878
|  |  | 10: GRAND TOTAL |  | 12542560 | 12560183.914
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 850372 | 864115 | 13743 | 180 |  | 2473740
| Dhanmondi Circuit-1 |  | 33 |  | DHK68131 | 1 | 1227584 | 1236105 | 8521 | 540 |  | 4601340
| Dhanmondi Circuit-2 |  | 33 |  |  | 1 | 169233 | 179297 | 10064 | 540 |  | 5434560
| Lalbagh Circuit-2 |  | 33 |  | DHK68132 | 1 | 9914 | 10259 | 345 | 180 |  | 62100
|  |  | 7: 0; 8: 0; 10: Total |  | 12571740
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 |  | 3: 33; 6: 1; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK61094 | 1 | 479842 | 519179 | 39337 | 180 |  | 7080660
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK60919 | 1 | 577452 | 608013 | 30561 | 180 |  | 5500980
|  |  | 10: Total |  | 12581640 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 4: 2538974.0262; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | AZIMPUR 33 KV NET IMPORT |  | 12560183.914
| DHANMONDI 33 kV SIDE |  | 4: 10021209.8878; 6: AZIMPUR 33 KV NET IMPORT; 9=8-7: 12560183.914 | 33 KV TX HV SIDE |  | 12581640
[11 empty] | LOSS UNITS=> |  | -21456.086
[11 empty] | LOSS % IN => |  | -0.1708%
| TOTAL IMPORT |  | 4: 12560183.914
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) |  | 11 |  | DHK60909 | 1 | 482949 | 522350 | 39401 | 180 | 7092180 |  | 7063008.3548
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK60902 | 1 | 593423 | 624089 | 30666 | 180 | 5519880 |  | 5497175.5592
|  |  | 7: 0; 8: 0; 10: Total | 12612060 |  | 12560183.914
| AZIMPUR 11 KV SIDE |  | 7: 0; 8: 0
7 | Chadni chwok |  | 11 |  | DHK60916 | 1 | 454152 | 464674 | 10522 | 60 |  | 631320 | 642773.9991 | Paribag |  |  |  |  | Chadni chwok | 642773.9991 | 585337.5096 | 57436.4896 | 9.8125 | OK
8 | BGB |  | 11 |  | DHK61090 | 1 | 716307 | 720083 | 3776 | 60 |  | 226560 | 230670.4639 | Jigatola |  |  |  |  | BGB | 230670.4639 | 138499.1268 | 92171.337 | 66.5501 | FAULT
9 | Pari Bibi Mazar | D920P | 11 |  | DHK61091 | 1 | 919902 | 951531 | 31629 | 60 |  | 1897740 | 1932170.5777 | Azimpur |  |  |  |  | Pari Bibi Mazar | 1932170.5777 | 1912839.727 | 19330.8507 | 1.0106 | OK
10 | Azimpur | D901P | 11 |  | DHK61086 | 1 | 383398 | 407809 | 24411 | 60 |  | 1464660 | 1491233.2344 | Azimpur |  |  |  |  | Azimpur | 1491233.2344 | 1631381.6426 | -140148.4081 | -8.5908 | OK
11 | Aazd | D901Z | 11 |  | DHK61089 | 1 | 64260 | 77569 | 13309 | 60 |  | 798540 | 813027.8611 | Azimpur |  |  |  |  | Aazd | 813027.8611 | 1025333.4123 | -212305.5512 | -20.706 | OK
12 | Dayra Sharif | D966D | 11 |  | DHK61088 | 1 | 579254 | 589162 | 9908 | 60 |  | 594480 | 605265.6133 | Azimpur |  |  |  |  | Dayra Sharif | 605265.6133 | 772833.6808 | -167568.0675 | -21.6823 | OK
13 | Naya palton | D966U | 11 |  | DHK86065 | 1 | 2006.64 | 2026.6 | 19.96 | 60000 |  | 1197600 | 1219327.9816 | Azimpur |  |  |  |  | Naya palton | 1219327.9816 | 1424702.0899 | -205374.1082 | -14.4152 | OK
16 | Viqarunnisa Noon School | D966V | 11 |  | DHK66477 | 1 | 1696824 | 1710480 | 13656 | 60 |  | 819360 | 834225.5971 | Azimpur |  |  |  |  | Viqarunnisa Noon School | 834225.5971 | 1008349.3994 | -174123.8023 | -17.2682 | OK
17 | Subal Das Lane | D966W | 11 |  | DHK66480 | 1 | 4107768 | 4138344 | 30576 | 60 |  | 1834560 | 1867844.3069 | Azimpur |  |  |  |  | Subal Das Lane | 1867844.3069 | 1712147.3443 | 155696.9627 | 9.0937 | OK
18 | Lalbagh | D920L | 11 |  | DHK61093 | 1 | 874634 | 898839 | 24205 | 60 |  | 1452300 | 1478648.9877 | Azimpur |  |  |  |  | Lalbagh | 1478648.9877 | 1848324.9154 | -369675.9276 | -20.0006 | OK
19 | Zahrul Haque Hall | D366J | 11 |  | DHK66497 | 1 | 1281591 | 1287059 | 5468 | 60 |  | 328080 | 334032.3348 | Ramna |  |  |  |  | Zahrul Haque Hall | 334032.3348 | 483616.7128 | -149584.378 | -30.9304 | OK
20 | Eden College | D966E | 11 |  | DHK60917 | 1 | 962562 | 967289 | 4727 | 60 |  | 283620 | 288765.6999 | Azimpur |  |  |  |  | Eden College | 288765.6999 | 308522.5366 | -19756.8368 | -6.4037 | OK
21 | Nilkhet/ PWD-01 | D902N | 11 |  | DHK60918 | 1 | 519580 | 526604 | 7024 | 60 |  | 421440 | 429086.1595 | Azimpur |  |  |  |  | Nilkhet/ PWD-01 | 429086.1595 | 527298.6165 | -98212.4571 | -18.6256 | OK
22 | BUET | D366BU | 11 |  | DHK66496 | 1 | 1015739 | 1022142 | 6403 | 60 |  | 384180 | 391150.1536 | Ramna |  |  |  |  | BUET | 391150.1536 | 431931.5513 | -40781.3976 | -9.4416 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIG2780 | 1 | 404836 | 406762 | 1926 | 1 |  | 1926 | 1960.9433 | Azimpur |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 1960.9433 | 3021.0771 | -1060.1338 | -35.0913 | OK
|  |  | 10: Grand Total | 12560183.914 | 12336366 | 12560183.914 | 1.8143
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 642773.9991
[6 empty] | Jigatola | at 33 KV level |  | 230670.4639
[6 empty] | Azimpur | at 33 KV level |  | 10961556.9626
[6 empty] | Ramna | at 33 KV level |  | 725182.4885
[6 empty] | Total = |  |  | 12560183.914 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar |  | 132 |  | 38992596 | 1 | 1025.378 | 1052.817 | 27.439 | 1440000 | 0 | 39512160
|  |  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 39512160
|  |  | 10: Net Total | 39512160
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj |  | 132 | RECEIVE |  | 1 | 5899.76 | 5941.03 | 41.27 | 960000 | 39619200
|  |  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh |  | 132 |  |  | 1 | 3181.25 | 3207.23 | 25.98 | 960000 | 24940800
|  |  | 132 |  |  | 1 | 7.84 | 7.84 | 0 | 960000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 64560000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 64560000
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
5 | 132 kV Jigatola-1 |  | 132 |  | 42003953362 | 1 | 278.28 | 291.67 | 13.39 | 1440000 |  | 19281600
6 | 132 kV Jigatola-2 |  | 132 |  | 42003953364 | 1 | 271.97 | 284.99 | 13.02 | 1440000 |  | 18748800
|  |  | 7: 0; 8: 0; 10: Total |  | 38030400
| KAMRANGIRCHAR 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | 30799138 | 1 | 3428.7 | 3436.67 | 7.97 | 960000 |  | 7651200
2 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 |  | 30799148 | 1 | 3406.36 | 3413.59 | 7.23 | 960000 |  | 6940800
7 | 132/33 kV, 50/75 MVA GT-3 (HV) |  | 132 |  | BD001910 | 1 | 1208.83 | 1217.24 | 8.41 | 960000 |  | 8073600
|  |  | 10: Total |  | 22665600 | 60696000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 4: 39512160; 6: EXPORT TO OTHER S/S; 9=8-7: 38030400 | 132 KV NET IMPORT |  | 26422560
| FROM LALBAGH 132/33 KV GRID |  | 4: 24940800; 6: 132 KV NET IMPORT; 9=8-7: 26422560 | 33 KV NET IMPORT |  | 26155200
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 267360
[11 empty] | LOSS % IN => |  | 1.012%
| 132 KV TOTAL IMPORT |  | 4: 64452960
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001914 | 1 | 2432.43 | 2451.36 | 18.93 | 480000 | 9086400 |  | 9179281.7177
14 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | 30799094 | 1 | 6957.76 | 6975.64 | 17.88 | 480000 | 8582400 |  | 8670129.8
19 | 132/33 kV GT-2 Incoming |  | 33 |  | 30799150 | 1 | 6857 | 6874.68 | 17.68 | 480000 | 8486400 |  | 8573148.4823
|  |  | 7: 0; 8: 0; 10: Total | 26155200 |  | 26422560
| KAMRANGIRCHAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) |  | 33 |  | 30799129 | 1 | 6986.34 | 7014.79 | 28.45 | 240000 |  | 6828000 | 6799300.4386 |  | 20949971.0526 | Kamrangir Char 33/11 kv ss | 1.5345 |  | 33/11 kV, 20/28 MVA T31 (HV) | 6799300.4386 | 8471830.6275 | -1672530.1889 | -19.7423 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) |  | 33 |  | 30799110 | 1 | 6881.97 | 6910.32 | 28.35 | 240000 |  | 6804000 | 6775401.3158 | [5 empty] | 33/11 kV, 20/28 MVA T32 (HV) | 6775401.3158 | 8409484.8601 | -1634083.5443 | -19.4314 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) |  | 33 |  | 30799137 | 1 | 4028.92 | 4059.78 | 30.86 | 240000 |  | 7406400 | 7375269.2982 | [5 empty] | 33/11 kV, 20/28 MVA T-33 (HV) | 7375269.2982 | 9371048.4269 | -1995779.1287 | -21.2973 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 21038400 | 20949971.0526 | [5 empty] | 33 KV Feeders | 20949971.0526 | 26252363.9145 | -5302392.8618 | -20.1978 | OK
8 | Dhaka Uddyan 2 |  | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | -0.01484 |  | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 |  | 33 |  | BD001912 | 1 | 428.24 | 428.24 | 0 | 240000 |  | 0 | 0 | [5 empty] | Dhaka Uddyan 1 | 0 | 2397.9141 | -2397.9141 | -100 | CHECK
10 | Spare Feeder -2 |  | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) |  | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 |  | 33 |  | 30799098 | 1 | 1760.74 | 1761.57 | 0.83 | 240000 |  | 199200 | 198362.7193 |  | 5205228.9474 | Kamrangir Char-2 33/11 kv ss | 0.50247 |  | Lalbagh Circuit-1 | 198362.7193 | 19183.3131 | 179179.4062 | 934.0379 | FAULT
16 | Zigatola Circuit-1 (BGB-1) |  | 33 |  | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 |  | 0 | 0 | [5 empty] | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 |  | 33 |  | 30799147 | 1 | 1603.45 | 1624.4 | 20.95 | 240000 |  | 5028000 | 5006866.2281 |  | 0 | BGB 33/11 kv ss | 0.71763 |  | Kamrangir Char-2 | 5006866.2281 | 1316454.8583 | 3690411.3697 | 280.3295 | FAULT
22 | Zigatola Circuit-2 (BGB-2) |  | 33 |  | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Grid Has No Reading | Zigatola Circuit-2 (BGB-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 5227200 | 5205228.9474 | [5 empty] | 0 | 5205228.9474 | 1338036.0855 | 3867192.8618 | 289.0201 | FAULT
|  |  | 9=8-7: Grand Total | 26155200 | 26265600 | 26155200 | -0.42032
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 6807600 |  | 6836129.3945
11 | 33/11 kV T-32 Incoming |  | 11 |  | 6604433 | 1 | 7767.12 | 7804.94 | 37.82 | 180000 | 6807600 |  | 6836129.3945
22 | 33/11 kV T-33 Incoming |  | 11 |  | DHK 95817 | 1 | 4747297 | 4787560 | 40263 | 180 | 7247340 |  | 7277712.2636
|  |  | 7: 0; 8: 0; 10: Total | 20862540 |  | 20949971.0526
| KAMRANGIRCHAR 11 kV SIDE |  | 7: 0; 8: 0
4 | Rasulpur | F120R | 11 |  | HA-021101042-02 | 1 | 97733809 | 98581922 | 848113 | 1 |  | 848113 | 861127.0146 | Kamrangirchar |  | 226 |  |  | Rasulpur | 861127.0146 | 1135070.1317 | -273943.1171 | -24.1345 | OK
5 | Bheribadh | F120B | 11 |  | HA-021101105-02 | 1 | 74035356 | 75856137 | 1820781 | 1 |  | 1820781 | 1848720.2846 | Kamrangirchar |  | 100 |  |  | Bheribadh | 1848720.2846 | 2165499.7281 | -316779.4435 | -14.6285 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 |  | 30799521 | 1 | 2655.72 | 2661.25 | 5.53 | 60000 |  | 331800 | 336891.3617 | Kamrangirchar |  | 126 |  |  | Panna Tower 11 KV Faridpur Tower Express | 336891.3617 | 271984.1018 | 64907.2599 | 23.8644 | OK
8 | Panna Battery Express | F140E | 11 |  | DHK15431 | 1 | 5345.3 | 5361.41 | 16.11 | 60000 |  | 966600 | 981432.1586 | Kamrangirchar |  | 42 |  |  | Panna Battery Express | 981432.1586 | 963251.5607 | 18180.5979 | 1.8874 | OK
9 | Eidgah | F140I | 11 |  | 30799460 | 1 | 5523.86 | 5556.72 | 32.86 | 60000 |  | 1971600 | 2001853.5525 | Kamrangirchar |  | 142 |  |  | Eidgah | 2001853.5525 | 2214989.6293 | -213136.0768 | -9.6224 | OK
10 | Bot Tola Mazar | D840L | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | F140H | 11 |  | HA-021101055-02 | 1 | 9989092 | 11777481 | 1788389 | 1 |  | 1788389 | 1815831.2401 | Kamrangirchar |  |  |  |  | Huzur Para | 1815831.2401 | 2641114.3542 | -825283.1141 | -31.2475 | OK
13 | Kamrangirchar | F103K | 11 |  | HA-021101015-02 | 1 | 29348087 | 30547592 | 1199505 | 1 |  | 1199505 | 1217911.0091 | Kamrangirchar |  |  |  |  | Kamrangirchar | 1217911.0091 | 2380775.6541 | -1162864.645 | -48.8439 | CHECK
14 | Munshihati | F140T | 11 |  | HA-021100854-02 | 1 | 56404546 | 57165112 | 760566 | 1 |  | 760566 | 772236.6347 | Kamrangirchar |  |  |  |  | Munshihati | 772236.6347 | 990193.2667 | -217956.632 | -22.0115 | OK
15 | Jhawchar | F140J | 11 |  | HA-021101028-02 | 1 | 6004029 | 6932632 | 928603 | 1 |  | 928603 | 942852.1071 | Kamrangirchar |  |  |  |  | Jhawchar | 942852.1071 | 1224855.4453 | -282003.3381 | -23.0234 | OK
16 | RMU Express | F140D | 11 |  | HA-021101248-02 | 1 | 8590513 | 9219291 | 628778 | 1 |  | 628778 | 638426.3913 | Kamrangirchar |  |  |  |  | RMU Express | 638426.3913 | 630223.836 | 8202.5553 | 1.3015 | OK
17 | Koyla Ghat | F140C | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2036133.7416 | 2067377.5431 | Kamrangirchar | 162 |  |  |  | Koyla Ghat | 2067377.5431 | 2106357.2232 | -38979.6801 | -1.8506 | OK
18 | Muslimbagh | F140M | 11 |  | HA-021100908-02 | 1 | 34050945 | 35892134 | 1841189 | 1 |  | 1841189 | 1869441.4387 | Kamrangirchar |  |  |  |  | Muslimbagh | 1869441.4387 | 2918215.2206 | -1048773.7819 | -35.9389 | OK
19 | Noyagaon | F140Y | 11 |  | HA-021101087-02 | 1 | 16193892 | 18030958 | 1837066 | 1 |  | 1837066 | 1865255.1726 | Kamrangirchar |  |  |  |  | Noyagaon | 1865255.1726 | 2290171.3321 | -424916.1595 | -18.5539 | OK
20 | Nurbagh | F140N | 11 |  | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2136683.556 | 2169470.2613 | Kamrangirchar | 170 |  |  |  | Nurbagh | 2169470.2613 | 2292212.2723 | -122742.011 | -5.3547 | OK
21 | Ali Nagar | F140A | 11 |  | HA-021101022-02 | 1 | 30998173 | 32604402 | 1606229 | 1 |  | 1606229 | 1630876.0549 | Kamrangirchar |  |  |  |  | Ali Nagar | 1630876.0549 | 2028577.6342 | -397701.5793 | -19.6049 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKE6223 | 1 | 43796.79 | 43873.75 | 76.96 | 120 |  | 9235.2 | 9376.9111 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 9376.9111 | 21708.6097 | -12331.6986 | -56.8056 | CHECK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHK37495 | 1 | 45593.9 | 45670.4 | 76.5 | 120 |  | 9180 | 9320.8641 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 9320.8641 | 0 | 9320.8641 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 21038400 | 20720451.4976 | 21038400 | 1.5345
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 21038400
[6 empty] | Jigatola | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 21038400 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: TOTAL |  | 0 | 0
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old |  | 33 | 0 | 43998033 | 1 | 287.849 | 296.113 | 8.264 | 270000 |  | 2231280 | 2267609.0881
|  |  | 10: TOTAL |  | 2231280 | 2231280
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 |  | 33 | 0 | 0 | 1 | 79.33 | 79.33 | 0 | 360000 | 0 | 0 | 0
11 | BGB-2 |  | 33 | 0 | 0 | 1 | 326.06 | 345.7 | 19.64 | 360000 | 0 | 7070400 | 7065129.4819
|  |  | 10: Total | 0 | 7070400 | 7065129.4819
|  |  | 10: GRAND TOTAL |  | 9301680 | 9296409.4819
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 |  | 33 |  | 43998032 | 1 | 1047.72 | 1047.72 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old |  | 33 |  | 43998033 | 1 | 287.849 | 296.113 | 8.264 | 270000 | 2231280
| 33 kV Zigatola-1 |  | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 |  | 33 |  | 43998027 | 1 | 781.12 | 781.12 | 0 | 270000 | 0
| 33 kV Zigatola-2 |  | 33 |  | 43998031 | 1 | 433.992 | 460.079 | 26.087 | 270000 | 7043490
|  |  | 7: 0; 8: 0; 10: Total | 9274770 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BGB 33 KV SIDE |  | 7: 0; 8: 0
6 | 33/11 kV T1 |  | 33 |  | 43998028 | 1 | 867.256 | 869.446 | 2.19 | 270000 |  | 591300
9 | 33/11 kV T2 |  | 33 |  | 43998029 | 1 | 882.002 | 914.056 | 32.054 | 270000 |  | 8654580
11 | 33/11 kV T3 |  | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 9245880
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 4: 9296409.4819; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BGB 33 KV NET IMPORT |  | 9296409.4819
|  |  | 6: BGB 33 KV NET IMPORT; 9=8-7: 9296409.4819 | 33 KV TX HV SIDE |  | 9245880
[11 empty] | LOSS UNITS=> |  | 50529.4819
[11 empty] | LOSS % IN => |  | 0.5435%
| TOTAL IMPORT |  | 4: 9296409.4819
11 KV SIDE of___BGB 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming |  | 11 |  |  | 1 | 32273270 | 32882240 | 608970 | 1 | 608970 |  | 613136.5444
29 | 33/11 kV T-2 Incoming |  | 11 |  |  | 1 | 36010820 | 44584900 | 8574080 | 1 | 8574080 |  | 8632743.4556
30 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 9183050 |  | 9245880
| BGB 11 KV SIDE |  | 7: 0; 8: 0
12 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | D920K | 11 |  |  | 1 | 12523740 | 12523740 | 0 | 1 |  | 0 | 0 | Azimpur |  |  |  |  | Nababgonj Park | 0 | 257344.0613 | -257344.0613 | -100 | CHECK
16 | Kholamura Ghat | F1104O | 11 |  |  | 1 | 88803750 | 91668720 | 2864970 | 1 |  | 2864970 | 2885529.8072 | Kamrangirchar |  |  |  |  | Kholamura Ghat | 2885529.8072 | 2905973.3033 | -20443.4961 | -0.7035 | OK
17 | Khalpar | F1104L | 11 |  |  | 1 | 91426620 | 92741032 | 1314412 | 1 |  | 1314412 | 1323844.5795 | Kamrangirchar |  |  |  |  | Khalpar | 1323844.5795 | 2032339.2009 | -708494.6214 | -34.861 | OK
18 | Shahidnagar | D920S | 11 |  |  | 1 | 23321150 | 24739150 | 1418000 | 1 |  | 1418000 | 1428175.9553 | Azimpur |  |  |  |  | Shahidnagar | 1428175.9553 | 1591215.1991 | -163039.2438 | -10.2462 | OK
19 | BGB 1 No Gate | D9104G | 11 |  |  | 1 | 37153410 | 37153410 | 0 | 1 |  | 0 | 0 | Azimpur |  |  |  |  | BGB 1 No Gate | 0 | 345681.1733 | -345681.1733 | -100 | CHECK
21 | Ganaktuli | D8104J | 11 |  |  | 1 | 26868220 | 27397800 | 529580 | 1 |  | 529580 | 533380.4107 | Jigatola |  |  |  |  | Ganaktuli | 533380.4107 | 706109.2655 | -172728.8548 | -24.4621 | OK
22 | Thana |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | D8104L | 11 |  |  | 1 | 39081811 | 39081811 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 521511.0545 | -521511.0545 | -100 | CHECK
24 | Sikder Medical | D8104K | 11 |  |  | 1 | 40142320 | 40845832 | 703512 | 1 |  | 703512 | 708560.5942 | Jigatola |  |  |  |  | Sikder Medical | 708560.5942 | 897177.4288 | -188616.8346 | -21.0234 | OK
25 | Gas Field | F1104G | 11 |  |  | 1 | 62157430 | 63617728 | 1460298 | 1 |  | 1460298 | 1470777.4973 | Kamrangirchar |  |  |  |  | Gas Field | 1470777.4973 | 1717515.6493 | -246738.152 | -14.366 | OK
26 | Hazaribagh | D8104H | 11 |  |  | 1 | 45430730 | 46318840 | 888110 | 1 |  | 888110 | 894483.3199 | Jigatola |  |  |  |  | Hazaribagh | 894483.3199 | 1109528.647 | -215045.3271 | -19.3817 | OK
27 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  |  | 1 | 2337.12 | 2389.78 | 52.66 | 10 |  | 526.6 | 530.379 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-1 | 530.379 | 413.4472 | 116.9318 | 28.2822 | OK
32 | 11/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  |  | 1 | 1909.01 | 1968.33 | 59.32 | 10 |  | 593.2 | 597.457 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-2 | 597.457 | 421.5697 | 175.8872 | 41.722 | FAULT
|  |  | 10: Grand Total | 9245880 | 9180001.8 | 9245880 | 0.71763
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Azimpur | at 33 KV level |  | 1429303.7913
[6 empty] | Kamrangirchar | at 33 KV level |  | 5680151.8839
[6 empty] | Jigatola | at 33 KV level |  | 2136424.3249
[6 empty] | Total = |  |  | 9245880 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 |  | 132 | 0 | 42003953362 | 1 | 278.28 | 291.67 | 13.39 | 1440000 | 0 | 19281600 | 0
6 | 132 kV Jigatola-2 |  | 132 | 0 |  | 1 | 271.97 | 284.99 | 13.02 | 1440000 | 0 | 18748800 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 38030400
|  |  | 10: Net Total | 38030400
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 |  | 132 | RECEIVE | 6604452 | 1 | 333.89 | 350.27 | 16.38 | 1200000 | 19656000
| 132 kV Kamrangirchar 2 |  | 132 |  |  | 1 | 326.11 | 342.03 | 15.92 | 1200000 | 19104000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 38760000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 38760000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| JIGATOLA 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  |  | 1 | 278.04 | 294.29 | 16.25 | 1200000 |  | 19500000
3 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  |  | 1 | 382.22 | 398.28 | 16.06 | 1200000 |  | 19272000
|  |  | 10: Total |  | 38772000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 38030400; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 38030400
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 38030400 | 33 KV NET IMPORT |  | 38606400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -576000
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.515%
| 132 KV TOTAL IMPORT |  | 4: 38030400
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  |  | 1 | 461.23 | 488.21 | 26.98 | 720000 | 19425600
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  |  | 1 | 634.01 | 660.65 | 26.64 | 720000 | 19180800
|  |  | 7: 0; 8: 0; 10: Total | 38606400 |  | 0
| JIGATOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  |  | 1 | 653.96 | 676.27 | 22.31 | 240000 |  | 5354400 | 5350408.647 |  | 13792111.2188 | JIGATOLA NEW 3/11 KV SS | 0.26105 |  | 33/11 kV 28/35 MVA T-1 | 5350408.647 | 6589841.9352 | -1239433.2881 | -18.8082 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  |  | 1 | 525.07 | 541.22 | 16.15 | 240000 |  | 3876000 | 3873110.697 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 3873110.697 | 4792177.0992 | -919066.4023 | -19.1785 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  |  | 1 | 432.2 | 451.25 | 19.05 | 240000 |  | 4572000 | 4568591.8748 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 4568591.8748 | 4995641.1619 | -427049.2871 | -8.5484 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 13802400 | 13792111.2188 | [5 empty] | 33 KV Feeders | 13792111.2188 | 16377660.1963 | -2585548.9775 | -15.787 | OK
2 | BGB-1 |  | 33 |  |  | 1 | 79.33 | 79.33 | 0 | 360000 |  | 0 | 0 |  | 7065129.4819 | BGB 33/11 kv ss | 0.71763 |  | BGB-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Spair |  | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 |  | 33 |  |  | 1 | 257.91 | 271.13 | 13.22 | 360000 |  | 4759200 | 4755652.3295 | [5 empty] | Dhaka Uddyan-1 | 4755652.3295 | 5066255.1601 | -310602.8306 | -6.1308 | OK
4 | Green Road -1 |  | 33 |  |  | 1 | 54 | 66.69 | 12.69 | 360000 |  | 4568400 | 4564994.5583 |  | 8727089.6757 | Dhaka Uddan 33/11 kv ss | -0.01484 |  | Green Road -1 | 4564994.5583 | 7209808.9025 | -2644814.3442 | -36.6836 | OK
9 | Green Road -2 |  | 33 |  |  | 1 | 88.88 | 97.49 | 8.61 | 360000 |  | 3099600 | 3097289.4521 | [5 empty] | Green Road -2 | 3097289.4521 | 4150666.8782 | -1053377.4261 | -25.3785 | OK
10 | Dhaka Uddyan-2 |  | 33 |  |  | 1 | 273.28 | 284.32 | 11.04 | 360000 |  | 3974400 | 3971437.3463 | [5 empty] | Dhaka Uddyan-2 | 3971437.3463 | 4402004.8379 | -430567.4917 | -9.7812 | OK
11 | BGB-2 |  | 33 |  |  | 1 | 326.06 | 345.7 | 19.64 | 360000 |  | 7070400 | 7065129.4819 |  | 1359785.6131 | Jigatla Old 33/11 kv ss | 1.1299 |  | BGB-2 | 7065129.4819 | 9475441.0826 | -2410311.6007 | -25.4375 | OK
12 | Jigatola Old |  | 33 |  |  | 1 | 38.94 | 42.72 | 3.78 | 360000 |  | 1360800 | 1359785.6131 | [5 empty] | Jigatola Old | 1359785.6131 | 1608562.9424 | -248777.3293 | -15.4658 | OK
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 24832800 | 24814288.7812 | [5 empty] | 0 | 24814288.7812 | 31912739.8037 | -7098451.0225 | -22.2433 | OK
|  |  | 9=8-7: Grand Total | 38606400 | 38635200 | 38606400 | -0.074543
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 221.38 | 242.72 | 21.34 | 250000 | 5335000 |  | 5359134.2573
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 245.15 | 260.61 | 15.46 | 250000 | 3865000 |  | 3882484.3307
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 181.88 | 200 | 18.12 | 250000 | 4530000 |  | 4550492.6308
|  |  | 7: 0; 8: 0; 10: Total | 13730000 |  | 13792111.2188
| JIGATOLA 11 kV SIDE |  | 7: 0; 8: 0
| Salek Garden |  | 11 |  | 2761 | 1 | 749.07 | 773.21 | 24.14 | 60000 |  | 1448400 | 1452181.1176 | Jigatola |  |  |  |  | Salek Garden | 1452181.1176 | 1864953.454 | -412772.3364 | -22.1331 | OK
4 | Jigatola Local |  | 11 |  | 2850 | 1 | 578.8 | 596.45 | 17.65 | 60000 |  | 1059000 | 1061764.5702 | Jigatola |  |  |  |  | Jigatola Local | 1061764.5702 | 1304682.5555 | -242917.9853 | -18.6189 | OK
5 | Modina Rayer Bazar |  | 11 |  | 2851 | 1 | 662.99 | 692.25 | 29.26 | 60000 |  | 1755600 | 1760183.0779 | Switching |  |  |  |  | Modina Rayer Bazar | 1760183.0779 | 2081696.183 | -321513.1052 | -15.4448 | OK
6 | City College |  | 11 |  | 2784 | 1 | 617.99 | 635.88 | 17.89 | 60000 |  | 1073400 | 1076202.1621 | Jigatola |  |  |  |  | City College | 1076202.1621 | 1313738.6584 | -237536.4963 | -18.081 | OK
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office |  | 11 |  | 2836 | 1 | 488.7 | 506.21 | 17.51 | 60000 |  | 1050600 | 1053342.6416 | Jigatola |  |  |  |  | Post Office | 1053342.6416 | 1284759.1292 | -231416.4876 | -18.0124 | OK
11 | Leather Institute |  | 11 |  | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Leather Institute | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Mina Bazar |  | 11 |  | 2853 | 1 | 237.44 | 244.3 | 6.86 | 60000 |  | 411600 | 412674.5015 | Jigatola |  |  |  |  | Mina Bazar | 412674.5015 | 509556.7223 | -96882.2208 | -19.013 | OK
13 | Mitali |  | 11 |  | 2852 | 1 | 536.6 | 549.65 | 13.05 | 60000 |  | 783000 | 785044.059 | Switching |  |  |  |  | Mitali | 785044.059 | 1032999.469 | -247955.41 | -24.0034 | OK
14 | Road-2 |  | 11 |  | 2839 | 1 | 774.77 | 801.77 | 27 | 60000 |  | 1620000 | 1624229.0876 | Jigatola |  |  |  |  | Road-2 | 1624229.0876 | 1929553.6546 | -305324.567 | -15.8236 | OK
15 | SS-2 |  | 11 |  | 2838 | 1 | 387.95 | 424.49 | 36.54 | 60000 |  | 2192400 | 2198123.3652 | Jigatola |  |  |  |  | SS-2 | 2198123.3652 | 2140258.9817 | 57864.3835 | 2.7036 | OK
16 | Spare |  | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar |  | 11 |  | 2843 | 1 | 620.73 | 639.85 | 19.12 | 60000 |  | 1147200 | 1150194.8205 | Jigatola |  |  |  |  | Bou Bazar | 1150194.8205 | 1453202.6428 | -303007.8223 | -20.851 | OK
18 | BGB |  | 11 |  | 2764 | 1 | 214.64 | 222.92 | 8.28 | 60000 |  | 496800 | 498096.9202 | Jigatola |  |  |  |  | BGB | 498096.9202 | 766146.304 | -268049.3838 | -34.9867 | OK
19 | Dhamondi-12 |  | 11 |  | 2763 | 1 | 499.01 | 510.98 | 11.97 | 60000 |  | 718200 | 720074.8955 | Dhanmondi |  |  |  |  | Dhamondi-12 | 720074.8955 | 696112.4417 | 23962.4538 | 3.4423 | OK
|  |  | 10: Total | 13792111.2188 | 13756200 | 13792111.2188 | 0.26105
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Jigatola | at 33 KV level |  | 12218383.7448 | Including Switching
[6 empty] | Dhanmondi | at 33 KV level |  | 1573727.474
[6 empty] | Total = |  |  | 13792111.2188 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [14 empty] | Month December-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | 4: CF; 5: Number; 7: 2023-04-01; 8: 2023-04-01 | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar |  | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 29.26 | 60000 | 0 | 1755600 | 1760183.0779 |  | 0
13 | Mitali |  | 11 | 0 | 2852 | 1 | 536.6 | 549.65 | 13.05 | 60000 | 0 | 783000 | 785044.059 |  | 95
|  |  | 10: Total |  | 2538600 | 2545227.1369
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 851429.88 | 853652.5785 | Dhanmondi
3 | 11 kV Madina Masjid Feeder |  | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1155511.98 | 1158528.4994 | Jigatola
3 | 11 kV Mitali |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 531658.14 | 533046.059 | Jigatola | Switching Total - Madina - Rayer Bazar
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit |  | 33 | 0 | 214393/37-2711 | 1 | 38.183 | 40.3944 | 2.2114 | 1000 | Estimated | 1644300 | 1671072.041
|  |  | 10: Total |  | 1644300 | 1671072.041
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  |  | 3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 | NET IMPORT | DHK61073 | 1 | 4048.77 | 4054.2 | 5.43 | 240000 |  | 1303200
2 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
|  |  | 10: Total |  | 1303200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 1671072.041
| Satmasjid 33 KV SIDE |  | 4: 1671072.041; 6: 33 KV NET IMPORT; 9=8-7: 1671072.041 | ZIGATOLA OLD 11 KV NET IMPORT |  | 1303200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 367872.041
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 22.01%
| TOTAL IMPORT |  | 4: 1671072.041
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0
16 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0
17 | 33/11 kV T-1 Incoming |  | 11 |  | DHK61028 | 1.32 | 1879.77 | 1884.95 | 5.18 | 180000 | 1230768
|  |  | 7: 0; 8: 0; 10: Total | 1230768 |  | 1303200
| ZIGATOLA OLD 11 KV SIDE |  | 7: 0; 8: 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | D803D | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | D803E | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | D803I | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | D803R | 11 |  | DHK60946 | 1 | 1199.27 | 1209.99 | 10.72 | 60000 |  | 643200 | 650467.3454 | Jigatola |  |  |  |  | Simanto Square | 650467.3454 | 732323.3006 | -81855.9551 | -11.1776 | OK
12 | Post Office | D803P | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | D803S | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | D803G | 11 |  | DHK61070 | 1 | 3506.97 | 3516.73 | 9.76 | 60000 |  | 585600 | 592216.5384 | Jigatola |  |  |  |  | Green Road Via Park | 592216.5384 | 824386.8012 | -232170.2628 | -28.1628 | OK
15 | PWD Quarters 11 kV Saleq Grand | D803A | 11 |  | DHK61028 | 1 | 3635.35 | 3636.29 | 0.94 | 60000 |  | 56400 | 57037.2486 | Jigatola |  |  |  |  | PWD Quarters 11 kV Saleq Grand | 57037.2486 | 62770.5686 | -5733.32 | -9.1338 | OK
18 | Road No.-2 | D803T | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | D803H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | D803B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | D803C | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | D803M | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | D803Z | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  | 243284 | 1 | 85569 | 85913 | 344 | 10 |  | 3440 | 3478.8676 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 3478.8676 | 2919.3296 | 559.538 | 19.1667 | OK
25 | 33/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  | 412277 | 1 | 39890 | 39890 | 0 | 10 |  | 0 | 0 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 1303200 | 1288640 | 1303200 | 1.1299
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Jigatola | at 33 KV level |  | 1303200
[6 empty] | Total = |  |  | 1303200 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) |  | 33 | 0 | BD001912 | 1 | 428.24 | 428.24 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 |  | 33 | 0 | 0 | 1 | 257.91 | 271.13 | 13.22 | 360000 | 0 | 4759200 | 4755652.3295
10 | Dhaka Uddyan-2 |  | 33 | 0 | 0 | 1 | 273.28 | 284.32 | 11.04 | 360000 | 0 | 3974400 | 3971437.3463
|  |  | 10: Total | 0 | 8733600 | 8727089.6757
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | RECEIVE | BD017107 | 1 | 90469.3 | 90471.49 | 2.19 | 1125 |  | 2463.75
| 33 kV Jigatala Incoming Circuit-1 |  | 33 |  | BD017098 | 1 | 82191.3 | 86300.03 | 4108.73 | 1125 |  | 4622321.25
| 33 kV Jigatala Incoming Circuit-2 |  | 33 |  | BD017097 | 1 | 87149.2 | 90570.07 | 3420.87 | 1125 |  | 3848478.75
| 33 kV Kamrangirchar Circuit-2 (O/H) |  | 33 |  | BD017108 | 1 | 73739.05 | 73739.06 | 0.01 | 1125 |  | 11.25
|  |  | 7: 0; 8: 0; 10: Total |  | 8473275 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017100 | 1 | 95037.2 | 99677.23 | 4640.03 | 1000 |  | 4640030
3 | 33/11 kV, 28/35 MVA T-3 (Future) |  | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017109 | 1 | 81579.7 | 85440.16 | 3860.46 | 1000 |  | 3860460
|  |  | 10: Total |  | 8500490 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8500490
| JIGATOLA 33 KV SIDE |  | 4: 8727089.6757; 6: 33 KV NET IMPORT; 9=8-7: 8500490 | 33 KV TX HV |  | 8500490
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 8727089.6757
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD014060 | 1 | 93929.02 | 98545.03 | 4616.01 | 1000 | 4616010 |  | 4636918.5698
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD014061 | 1 | 80850.06 | 84696.21 | 3846.15 | 1000 | 3846150 |  | 3863571.4302
|  |  | 7: 0; 8: 0; 10: Total | 8462160 |  | 8500490
| DHAKA UDDYAN 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | G1103L | 11 |  | BD014031 | 1 | 50391.3 | 50616.29 | 224.99 | 1000 |  | 224990 | 224956.6107 | Adabor |  |  |  |  | D Block dhaka uddyan | 224956.6107 | 285235.5277 | -60278.917 | -21.133 | OK
8 | Dill Mohammad O/H | G1103DM | 11 |  | BD014027 | 1 | 25238.4 | 26373.57 | 1135.17 | 1000 |  | 1135170 | 1135001.5369 | Adabor |  |  |  |  | Dill Mohammad O/H | 1135001.5369 | 1518244.1569 | -383242.6201 | -25.2425 | OK
9 | Turag O/H | G1103U | 11 |  | BD014028 | 1 | 28864.7 | 29356.45 | 491.75 | 1000 |  | 491750 | 491677.0226 | Adabor |  |  |  |  | Turag O/H | 491677.0226 | 590651.3937 | -98974.3711 | -16.7568 | OK
10 | Nabadoy O/H | G1103N | 11 |  | BD014025 | 1 | 39575.1 | 41099.31 | 1524.21 | 1000 |  | 1524210 | 1523983.802 | Adabor |  |  |  |  | Nabadoy O/H | 1523983.802 | 1125982.5565 | 398001.2455 | 35.347 | OK
11 | Chandrima O/H | G1103CH | 11 |  | BD014024 | 1 | 8643.05 | 9266.86 | 623.81 | 1000 |  | 623810 | 623717.4245 | Adabor |  |  |  |  | Chandrima O/H | 623717.4245 | 752545.8986 | -128828.4741 | -17.119 | OK
12 | Shyamoli Housing Project-2 | G1103SH | 11 |  | BD014029 | 1 | 31988.5 | 32602.26 | 613.76 | 1000 |  | 613760 | 613668.9159 | Adabor |  |  |  |  | Shyamoli Housing Project-2 | 613668.9159 | 919460.3881 | -305791.4722 | -33.2577 | OK
13 | Spare |  | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare |  | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare |  | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | C2103U | 11 |  | BD013959 | 1 | 45500.4 | 46153.52 | 653.12 | 1000 |  | 653120 | 653023.0747 | Satmasjid |  |  |  |  | U Lab | 653023.0747 | 694263.8768 | -41240.8021 | -5.9402 | OK
19 | Akota | G1103AK | 11 |  | BD014020 | 1 | 8078.5 | 8424.99 | 346.49 | 1000 |  | 346490 | 346438.5797 | Adabor |  |  |  |  | Akota | 346438.5797 | 380615.236 | -34176.6563 | -8.9793 | OK
20 | Burigonga O/H | G1103BU | 11 |  | BD014019 | 1 | 6149.5 | 6461.38 | 311.88 | 1000 |  | 311880 | 311833.7159 | Adabor |  |  |  |  | Burigonga O/H | 311833.7159 | 278809.9473 | 33023.7686 | 11.8445 | OK
21 | Garden City | C2103G | 11 |  | BD014021 | 1 | 94056.2 | 95724.67 | 1668.47 | 1000 |  | 1668470 | 1668222.3933 | Satmasjid |  |  |  |  | Garden City | 1668222.3933 | 1892735.0117 | -224512.6183 | -11.8618 | OK
22 | Avenue O/H | G1103AV | 11 |  | BD014017 | 1 | 16683.5 | 17346.12 | 662.62 | 1000 |  | 662620 | 662521.6649 | Adabor |  |  |  |  | Avenue O/H | 662521.6649 | 749985.7064 | -87464.0415 | -11.6621 | OK
23 | Chand Uddyan | C2103D | 11 |  | BD014018 | 1 | 10938.7 | 11142.1 | 203.4 | 1000 |  | 203400 | 203369.8147 | Satmasjid |  |  |  |  | Chand Uddyan | 203369.8147 | 512239.2335 | -308869.4187 | -60.2979 | CHECK
24 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4416 | 1 | 1917.01 | 1954.47 | 37.46 | 100 |  | 3746 | 3745.4441 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3745.4441 | 2862.3952 | 883.0488 | 30.85 | OK
25 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4412 | 1 | 284.73 | 284.73 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 168.6715 | -168.6715 | -100 | CHECK
|  |  | 10: Grand Total | 8462160 | 8463416 | 8462160 | -0.01484
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 5937544.7172
[6 empty] | Satmasjid | at 33 KV level |  | 2524615.2828
[6 empty] | Total = |  |  | 8462160 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
#REF! | #REF! |  | #REF! | IMPORT | #REF! | 1 | 3.32 | 8.53 | 5.21 | 180000 | 0 | 937800
#REF! | #REF! |  | #REF! |  | #REF! | 1 | 12.822 | 33.168 | 20.346 | 180000 | 0 | 3662280
#REF! | #REF! |  | #REF! |  |  | 1 | 0 | 0 | 0 | 180000 | 0 | 0
14 | Transformer-1 |  | 33 |  | 50147586E | 1 | 3308.169 | 3333.384 | 25.215 | 750000 | 0 | 18911250
15 | Transformer-2 |  | 33 |  | 50148569E | 1 | 2950.394 | 2976.109 | 25.715 | 750000 | 0 | 19286250
|  |  | 9=8-7: Total Import/Export | 0 | 42797580
|  |  | 10: Net Total | 42797580
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | 4: RECEIVE; 6: 1; 9=8-7: 0
| 33 KV GT-2 Incomming |  | 6: 1; 9=8-7: 0
| 33 KV Satmosjid-1 Incomming |  | 6: 1; 9=8-7: 0
Total Import/Export
|  |  | 9=8-7: Net Total | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 4: EXPORT |  | 0
| Feeder No.2 | [10 empty] | 0
|  |  | 10: Total |  | 0
SATMOSJID 132 KV SIDE
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 4: 42797580; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 42797580
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 42797580 | 33 KV NET IMPORT |  | 42797580
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 42797580
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming |  | 33 |  | 50147586 | 1 | 3232.217 | 3232.217 | 0 | 750000 | 0
10 | 132/33 kV, 80/120 MVA GT-2 Incoming |  | 33 |  | 50148569 | 1 | 2873.592 | 2873.592 | 0 | 750000 | 0
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 42797580
| SATMOSJID 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SICAM | 1 | 4214 | 4214 | 0 | 1000 | From Downstream | 7367940 | 7487902.7755 |  | 1.8414 | Satmasjid 3/11 kv ss | 15099649.642 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 7487902.7755 | 8116129.0541 | -628226.2786 | -7.7405 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SICAM | 1 | 4298 | 4298 | 0 | 1000 | From Downstream | 7489800 | 7611746.8665 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 7611746.8665 | 8313252.8495 | -701505.9829 | -8.4384 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 14857740 | 15099649.642 | [5 empty] | 33 KV Feeders | 15099649.642 | 16429381.9035 | -1329732.2615 | -8.0936 | OK
6 | BGB |  | 33 |  | 214393/40-2711 | 1 | 8456.954 | 8456.954 | 0 | 1000 | From Downstream | 2231280 | 2267609.0881 |  | 0.71763 | BGB 33/11 KV SS | 2267609.0881 |  | BGB | 2267609.0881 | 2624835.8633 | -357226.7751 | -13.6095 | OK
| Asad Gate Circuit-1 |  | 33 |  | 214393/44-2711 | 1 | 4308.85 | 7383.4 | 3074.55 | 1000 | Estimated | 3088418.4 | 3138703.1801 |  | 2.5706 | ASADGATE 33/11 KV SS | 8132439.0118 |  | Asad Gate Circuit-1 | 3138703.1801 | 6393333.7849 | -3254630.6048 | -50.9066 | CHECK
8 | Lalmatia Circuit-2 |  | 33 |  | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 8315280 | 8450667.1052 |  | 0.90072 | LALMATIA 33/11 KV SS | 8450667.1052 |  | Lalmatia Circuit-2 | 8450667.1052 | 10242362.8329 | -1791695.7277 | -17.493 | OK
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 4913731.8 | 4993735.8316 |  | 1.1299 | JIGATOLA OLD 33/11 KV SS | 1671072.041 |  | Asad Gate Circuit-2 | 4993735.8316 | 5300077.8433 | -306342.0117 | -5.78 | OK
13 | Jigatola U/G Circuit |  | 33 |  | 214393/37-2711 | 1 | 38.183 | 40.3944 | 2.2114 | 1000 | Estimated | 1644300 | 1671072.041 |  | 0.93209 | JAPAN GARDEN 33/11 KV SS | 7176143.112 |  | Jigatola U/G Circuit | 1671072.041 | 1603495.878 | 67576.163 | 4.2143 | OK
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 7061175 | 7176143.112 | [5 empty] | Japan Garden City-2 | 7176143.112 | 9726031.8942 | -2549888.7822 | -26.2172 | OK
|  |  | 10: Total |  | 27254185.2 | 27697930.358 | [5 empty] | 0 | 27697930.358 | 35890138.0965 | -8192207.7385 | -22.8258 | OK
|  |  | 9=8-7: Grand Total | 42797580 | 42111925.2 | 42797580 | 1.6282
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming |  | 11 |  | DHK60998 | 1 | 5013.107 | 5054.04 | 40.933 | 180000 | 7367940 |  | 7487902.7755
24 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61044 | 1 | 5105.79 | 5147.4 | 41.61 | 180000 | 7489800 |  | 7611746.8665
|  |  | 7: 0; 8: 0; 10: Total | 14857740 |  | 15099649.642
| SATMOSJID 11 kV SIDE |  | 7: 0; 8: 0
16 | Lalmatia O/H | C209M | 11 |  | DHK61042 | 1 | 3220.42 | 3232.99 | 12.57 | 60000 |  | 754200 | 768088.1431 | Satmasjid |  |  |  |  | Lalmatia O/H | 768088.1431 | 970586.2531 | -202498.1101 | -20.8635 | OK
16 | Asad Avenue (South) | C209C | 11 |  | DHK 60999 | 1 | 2949.71 | 2960.26 | 10.55 | 60000 |  | 633000 | 644656.3174 | Satmasjid |  |  |  |  | Asad Avenue (South) | 644656.3174 | 816364.2657 | -171707.9483 | -21.0333 | OK
17 | Madrasha Road |  | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | C209H | 11 |  | DHK61002 | 1 | 2461.86 | 2477.67 | 15.81 | 60000 |  | 948600 | 966067.9031 | Satmasjid |  |  |  |  | Bashbari | 966067.9031 | 1190903.3781 | -224835.475 | -18.8794 | OK
19 | Road-27 | C209A | 11 |  | DHK61001 | 1 | 1479.65 | 1483.48 | 3.83 | 60000 |  | 229800 | 234031.6299 | Satmasjid |  |  |  |  | Road-27 | 234031.6299 | 326307.5256 | -92275.8957 | -28.2788 | OK
20 | Boishakhi O/H | D209O | 11 |  | DHK61024 | 1 | 4253.99 | 4274.92 | 20.93 | 60000 |  | 1255800 | 1278924.8078 | Dhanmondi |  |  |  |  | Boishakhi O/H | 1278924.8078 | 1623796.756 | -344871.9482 | -21.2386 | OK
21 | Katasur O/H | C209K | 11 |  | DHK61003 | 1 | 3692.06 | 3705.25 | 13.19 | 60000 |  | 791400 | 805973.1589 | Satmasjid |  |  |  |  | Katasur O/H | 805973.1589 | 1044422.2626 | -238449.1037 | -22.8307 | OK
22 | Nurjahan Road | D409I | 11 |  | DHK61000 | 1 | 1912.62 | 1926.3 | 13.68 | 60000 |  | 820800 | 835914.5423 | Shyamoli |  |  |  |  | Nurjahan Road | 835914.5423 | 1604146.8503 | -768232.3079 | -47.8904 | CHECK
25 | polpar over head | D209W | 11 |  | DHK61003 | 1 | 1928.75 | 1949.28 | 20.53 | 60000 |  | 1231800 | 1254482.8621 | Dhanmondi |  |  |  |  | polpar over head | 1254482.8621 | 1581519.6861 | -327036.8239 | -20.6786 | OK
26 | Satmosjid Housing | C209S | 11 |  | DHK61043 | 1 | 2852.16 | 2870.9 | 18.74 | 60000 |  | 1124400 | 1145105.1552 | Satmasjid |  |  |  |  | Satmosjid Housing | 1145105.1552 | 1396334.2108 | -251229.0556 | -17.992 | OK
27 | Physical College | C209P | 11 |  | DHK61041 | 1 | 3423.91 | 3449.62 | 25.71 | 60000 |  | 1542600 | 1571006.0587 | Satmasjid |  |  |  |  | Physical College | 1571006.0587 | 1952486.0884 | -381480.0296 | -19.5382 | OK
28 | Asad Avenue (North) | D409V | 11 |  | DHK61022 | 1 | 2730.21 | 2741 | 10.79 | 60000 |  | 647400 | 659321.4848 | Shyamoli |  |  |  |  | Asad Avenue (North) | 659321.4848 | 0 | 659321.4848 | #DIV/0! | #DIV/0!
29 | Spare Feeder |  | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | D209Z | 11 |  | DHK61023 | 1 | 1170.56 | 1188.33 | 17.77 | 60000 |  | 1066200 | 1085833.4369 | Dhanmondi |  |  |  |  | Ghraphic artch college | 1085833.4369 | 1330834.525 | -245001.0881 | -18.4096 | OK
31 | Mohammadpur O/H | D409W | 11 |  | DHK61025 | 1 | 2252.68 | 2284.77 | 32.09 | 60000 |  | 1925400 | 1960855.0924 | Shyamoli |  |  |  |  | Mohammadpur O/H | 1960855.0924 | 652019.5995 | 1308835.4929 | 200.7356 | FAULT
32 | Bosila Feeder | C209V | 11 |  | DHK60997 | 1 | 4231.8 | 4258.71 | 26.91 | 60000 |  | 1614600 | 1644331.8958 | Satmasjid |  |  |  |  | Bosila Feeder | 1644331.8958 | 2353225.0751 | -708893.1793 | -30.1243 | OK
33 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIB 7375 | 1 | 6168.9 | 6220.41 | 51.51 | 60 |  | 3090.6 | 3147.5116 | Satmasjid |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 3147.5116 | 4513.5238 | -1366.0122 | -30.2649 | OK
|  |  | 10: Total | 14857740 | 14589090.6 | 14857740 | 1.8414
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Satmasjid | at 33 KV level |  | 7782407.7736
[6 empty] | Shyamoli | at 33 KV level |  | 3456091.1195
[6 empty] | Dhanmondi | at 33 KV level |  | 3619241.1069
[6 empty] | Total = |  |  | 14857740 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 |  | 33 |  | 38992490 (new) | 1 | 1.459 | 1.52 | 0.061 | 180000 | 0 | 10980 | 10980
| Kallyanpur to Japangarden-2 |  | 33 |  | 8993669E | 1 | 0.107 | 1.39 | 1.283 | #REF! | 0 | 230940 | 230940
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 7061175 | 7176143.112
|  |  | 10: Total | 0 | 7303095 | 7418063.112
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G |  | 33 | RECEIVE | DHK86051 | 1 | 3076.8 | 3094.43 | 17.63 | 270000 |  | 4760100
| kallyanpur U/G-2 |  | 33 |  | DHK61100 | 1 | 2950.85 | 2964.43 | 13.58 | 270000 |  | 3666600
|  |  | 7: 0; 8: 0; 10: Total |  | 8426700
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33 KV Japan Genden City |  | 33 |  | DHK15681 | 1 | 750.68 | 804.83 | 54.15 | 18000 |  | 974700 | 974700 | Adabor | Customer Number:- 27111298
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 974700
[7 empty] | 0 | 0
| JAPAN GERDEN CITY 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61080 | 1 | 4399.31 | 4419.69 | 20.38 | 180000 |  | 3668400
3 | 33/11 kV 20/28 MVA T-1 (HV) |  | 33 |  | 86052 | 1 | 5196.91 | 5203.94 | 7.03 | 180000 |  | 4771800 | 7027200 |  | Check Meter
|  |  | 10: Total |  | 8440200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 4: 9414900; 6: Adabor NOCS; 9=8-7: 974700 | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 8440200
| IMPORT-2 |  | 6: JAPAN GERDEN CITY 33 KV NET IMPORT; 9=8-7: 8440200 | 33 KV TX HV SIDE |  | 8440200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9414900
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK61079 | 1 | 5841.01 | 5870.16 | 29.15 | 160000 | 4664000 |  | 4719582.3902
10 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK61082 | 1 | 4897.74 | 4920.72 | 22.98 | 160000 | 3676800 |  | 3720617.6098
|  |  | 7: 0; 8: 0; 10: Total | 8340800 | 8426700 | 8440200
| JAPAN GERDEN CITY 11 KV SIDE |  | 7: 0; 8: 0
5 | Dhaka Uddyan | G186D | 11 |  | DHK86067 | 1 | 3254.34 | 3254.98 | 0.64 | 60000 |  | 38400 | 38757.9222 | Adabor |  |  |  |  | Dhaka Uddyan | 38757.9222 | 90112.6747 | -51354.7525 | -56.9895 | CHECK
| Shia Mosjid | D409H | 11 |  | DHK60950 | 1 | 3569.61 | 3592.79 | 23.18 | 60000 |  | 1390800 | 1403763.4936 | Shyamoli |  |  |  |  | Shia Mosjid | 1403763.4936 | 1651270.0056 | -247506.5121 | -14.9889 | OK
6 | Shekhar Tek | G186S | 11 |  | DHK60977 | 1 | 2464.44 | 2472.47 | 8.03 | 60000 |  | 481800 | 486290.8047 | Adabor |  |  |  |  | Shekhar Tek | 486290.8047 | 1243674.2652 | -757383.4605 | -60.8989 | CHECK
7 | Madrasha Road | D434D | 11 |  | DHK61083 | 1 | 2092.58 | 2108.17 | 15.59 | 60000 |  | 935400 | 944118.7603 | Shyamoli |  |  |  |  | Madrasha Road | 944118.7603 | 1646495.8242 | -702377.0638 | -42.6589 | CHECK
8 | Baitul Aman Housing | G186B | 11 |  | DHK668115 | 1 | 4242.38 | 4269.31 | 26.93 | 60000 |  | 1615800 | 1630860.6938 | Adabor |  |  |  |  | Baitul Aman Housing | 1630860.6938 | 2021865.8399 | -391005.1461 | -19.3388 | OK
11 | Shyamoli Square | D486G | 11 |  | DHK86063 | 1 | 480.53 | 484.66 | 4.13 | 30000 |  | 123900 | 125054.8582 | Shyamoli |  |  |  |  | Shyamoli Square | 125054.8582 | 139346.4208 | -14291.5625 | -10.2561 | OK
12 | Mohammadi Housing | G186E | 11 |  | DHK60948 | 1 | 3887.07 | 3887.07 | 0 | 60000 |  | 0 | 0 | Adabor |  |  |  |  | Mohammadi Housing | 0 | 796094.7552 | -796094.7552 | -100 | CHECK
13 | Chand Housing | C286H | 11 |  | DHK60867 | 1 | 2223.07 | 2233.74 | 10.67 | 60000 |  | 640200 | 646167.2337 | Satmasjid |  |  |  |  | Chand Housing | 646167.2337 | 578272.7269 | 67894.5067 | 11.7409 | OK
14 | PC Culture Housing |  | 11 |  | DHK60979 | 1 | 4222.72 | 4245.93 | 23.21 | 60000 |  | 1392600 | 1405580.2712 | Adabor |  |  |  |  | PC Culture Housing | 1405580.2712 | 1788527.722 | -382947.4509 | -21.4113 | OK
15 | Mehedibagh | G186H | 11 |  | DHK68121 | 1 | 2445.54 | 2474.33 | 28.79 | 60000 |  | 1727400 | 1743500.9051 | Adabor |  |  |  |  | Mehedibagh | 1743500.9051 | 2209252.4615 | -465751.5564 | -21.0819 | OK
16 | 33/11 kV Incoming (Spare) |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 |  | 0 | 0 | Adabor |  |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer |  | 11 |  |  | 1 | 665030 | 667611 | 2581 | 1 |  | 2581 | 2605.0572 | Adabor |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 2605.0572 | 3087.304 | -482.2468 | -15.6203 | OK
|  |  | 10: Grand Total | 8426700 | 8348881 | 8426700 | 0.93209
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Adabor | at 33 KV level |  | 5307595.6542
[6 empty] | Shyamoli | at 33 KV level |  | 2472937.1122
[6 empty] | Satmasjid | at 33 KV level |  | 646167.2337
[6 empty] | Total = |  |  | 8426700 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) |  | 132 |  | 42627810 | 1 | 214.859 | 232.688 | 17.829 | 960000 | 0 | 17115840
2 | Dhaka University-1 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) |  | 132 |  | 42627812 | 1 | 217.013 | 235.042 | 18.029 | 960000 | 0 | 17307840
3 | Dhaka University-2 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 34423680
|  |  | 10: Net Total | 34423680
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 |  | 132 |  | 2877 | 1 | 171.97 | 186.23 | 14.26 | 1200000 |  | 17112000
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 |  | 132 |  | 2811 | 1 | 173.6 | 188.01 | 14.41 | 1200000 |  | 17292000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 34404000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 34404000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhanmondi |  | 132 | 0 | SIEM0480 | 1 | 133950 | 160540 | 26590 | 1000 |  | 26590000
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 26590000
| DHAKA UNIVERSITY 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | 2752 | 1 | 224.83 | 228.11 | 3.28 | 1200000 |  | 3936000
4 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | 2867 | 1 | 242.82 | 246.1 | 3.28 | 1200000 |  | 3936000
|  |  | 10: Total | 34462000 | 7872000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 34423680; 6: EXPORT TO OTHER S/S; 9=8-7: 26590000 | 132 KV NET IMPORT |  | 7872000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 7872000 | 33 KV NET IMPORT |  | 7783200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 88800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.128%
| 132 KV TOTAL IMPORT |  | 4: 34423680
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  | 2769 | 1 | 371.83 | 377.24 | 5.41 | 720000 | 3895200
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  | 2830 | 1 | 401.15 | 406.55 | 5.4 | 720000 | 3888000
|  |  | 7: 0; 8: 0; 10: Total | 7783200 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  | 2751 | 1 | 39.91 | 40.68 | 0.77 | 240000 |  | 184800 | 183805.3218 |  | 0.40161 | DHAKA UNIVERSITY 33/11 KV SS | 988251.99 |  | 33/11 kV 28/35 MVA T-1 | 183805.3218 | 250371.2207 | -66565.8989 | -26.5869 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  | 4253 | 1 | 65.91 | 67.97 | 2.06 | 240000 |  | 494400 | 491738.9129 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 491738.9129 | 739076.5842 | -247337.6713 | -33.4658 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  | 2808 | 1 | 26.32 | 27.63 | 1.31 | 240000 |  | 314400 | 312707.7553 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 312707.7553 | 385186.4934 | -72478.7381 | -18.8165 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 993600 | 988251.99 | [5 empty] | 33 KV Feeders | 988251.99 | 1374634.2983 | -386382.3083 | -28.108 | OK
2 | Spare |  | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 |  | 33 |  | 2804 | 1.5 | 181.85 | 187.29 | 5.44 | 360000 |  | 2937600 | 2921788.4922 |  | 1.1187 | BB AVENUE 33/11 KV SS | 4328973.3909 |  | BB Avenue-1 | 2921788.4922 | 3981263.5215 | -1059475.0294 | -26.6115 | OK
3 | DMC Circuit-1 |  | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 | [5 empty] | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 |  | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | 0.85829 | DMC 33/11 KV SS | 2518968.3875 |  | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 |  | 33 |  | 2753 | 1 | 431.54 | 431.64 | 0.1 | 360000 |  | 36000 | 35806.2315 | [5 empty] | Biddyut Bhaban Circuit-2 | 35806.2315 | 1834450.6748 | -1798644.4432 | -98.0481 | CHECK
10 | DMC Circuit-2 |  | 33 |  | 2803 | 1.05 | 333.41 | 340.11 | 6.7 | 360000 |  | 2532600 | 2518968.3875 |  | 0.96474 | BIDDYUT BHABAN 33/11 KV SS | 35806.2315 |  | DMC Circuit-2 | 2518968.3875 | 1453838.271 | 1065130.1165 | 73.2633 | FAULT
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 210.83 | 214.76 | 3.93 | 360000 |  | 1414800 | 1407184.8988 | [5 empty] | BB Avenue-2 | 1407184.8988 | 2090840.4344 | -683655.5356 | -32.6976 | OK
12 | Spare |  | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 6921000 | 6883748.01 | [5 empty] | 0 | 6883748.01 | 9360392.9017 | -2476644.8917 | -26.4588 | OK
|  |  | 9=8-7: Grand Total | 7872000 | 7914600 | 7872000 | -0.53825
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 50.61 | 51.67 | 1.06 | 250000 | 265000 |  | 249415.9784
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 61.67 | 63.6 | 1.93 | 250000 | 482500 |  | 454125.3192
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 24.3 | 25.51 | 1.21 | 250000 | 302500 |  | 284710.6924
|  |  | 7: 0; 8: 0; 10: Total | 1050000 |  | 988251.99
| DHAKA UNIVERSITY 11 kV SIDE |  | 7: 0; 8: 0
| Mokarom Bhabon | D3108MB | 11 |  | 2761 | 1 | 63.51 | 65.52 | 2.01 | 60000 |  | 120600 | 121084.3373 | Ramna |  |  |  |  | Mokarom Bhabon | 121084.3373 | 174337.3 | -53252.9626 | -30.5459 | OK
4 | 11 kV Shaid Minar RMU | D3108SM | 11 |  | 2850 | 1 | 146.61 | 149 | 2.39 | 60000 |  | 143400 | 143975.9036 | Ramna |  |  |  |  | 11 kV Shaid Minar RMU | 143975.9036 | 186918.3422 | -42942.4386 | -22.9739 | OK
5 | 11 kV Shaidulla Hall | D3108SH | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | D3108MA | 11 |  | 2836 | 1 | 106.63 | 108.47 | 1.84 | 60000 |  | 110400 | 110843.3735 | Ramna |  |  |  |  | MBA Bhabon | 110843.3735 | 176733.689 | -65890.3155 | -37.2823 | OK
11 | Suprime Court |  | 11 |  | 2835 | 1 | 70.7 | 73.79 | 3.09 | 60000 |  | 185400 | 186144.5783 | Ramna |  |  |  |  | Suprime Court | 186144.5783 | 281575.7078 | -95431.1295 | -33.8918 | OK
12 | Karjon Hall | D3108KH | 11 |  | 2853 | 1 | 76.92 | 79.81 | 2.89 | 60000 |  | 173400 | 174096.3855 | Ramna |  |  |  |  | Karjon Hall | 174096.3855 | 243233.4838 | -69137.0982 | -28.4242 | OK
13 | Spare |  | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | D3108SP | 11 |  | 2839 | 1 | 2.73 | 2.93 | 0.2 | 60000 |  | 12000 | 12048.1928 | Ramna |  |  |  |  | Swimming Pool | 12048.1928 | 23963.89 | -11915.6973 | -49.7236 | CHECK
15 | Spare |  | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU |  | 11 |  | 2772 | 1 | 98.89 | 103 | 4.11 | 60000 |  | 246600 | 247590.3614 | Ramna |  |  |  |  | Police Head Quarter RMU | 247590.3614 | 319318.8346 | -71728.4732 | -22.463 | OK
17 | Spare |  | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare |  | 11 |  | 2764 | 1 | 2.38 | 3.28 | 0.9 | 60000 |  | 54000 | 54216.8675 | Ramna |  |  |  |  | Spare | 54216.8675 | 53918.7526 | 298.1149 | 0.5529 | OK
19 | Spare |  | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 1050000 | 1045800 | 1050000 | 0.40161
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1050000
[6 empty] | Total = |  |  | 1050000 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 |  | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 |  | 33 | 0 | 2753 | 1 | 431.54 | 431.64 | 0.1 | 360000 | 0 | 36000 | 35806.2315
| Motijheel Old 33 KV Side (Sending) |  | 10: Total | 0 | 36000 | 35806.2315
| Motijheel Incoming |  | 33 | 0 | DHK-C9344 | 1 | 73648.71 | 78311.6 | 4662.89 | 270 | 0 | 1258980.3 |  | 0
P&T 33 KV Side (Sending)
| P&T Incoming |  | 33 | Export | BD017079 | 1 | 1533 | 3210 | 1677 | 1000 | 0 | 1677000
|  |  | 10: Total |  | 2971786.5315
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 73648.71 | 78311.6 | 4662.89 | 270 | 0 | 1258980.3
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 21216.28 | 21216.28 | 0 | 270 |  | 0
| Dhaka University Incoming-1 |  | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 | From P&T END | 1677000
| Dhaka University Incoming-2 |  | 33 |  | DHK-C9343 | 1 | 76502.64 | 76529.93 | 27.29 | 270 |  | 7368.3
|  |  | 7: 0; 8: 0; 10: Total |  | 2943348.6 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 |  | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-C9342 | 1 | 5607.26 | 10273.69 | 4666.43 | 270 |  | 1259936.1
3 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK-C9308 | 1 | 68327.02 | 74624.86 | 6297.84 | 270 |  | 1700416.8
|  |  | 10: Total |  | 2960352.9 | 2960352.9
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 4: 2971786.5315; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 2971786.5315
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 2971786.5315 | 33 KV TX HV SIDE |  | 2960352.9
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 11433.6315
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3847%
| TOTAL IMPORT |  | 4: 2971786.5315
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK-C9316 | 1 | 89297.15 | 94514.44 | 5217.29 | 240 | 1252149.6 |  | 1263668.7474
10 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK-C9377 | 1 | 25021.99 | 32074.27 | 7052.28 | 240 | 1692547.2 |  | 1708117.7841
|  |  | 7: 0; 8: 0; 10: Total | 2944696.8 |  | 2971786.5315
| BIDDYUT BHABAN 11 KV SIDE |  | 7: 0; 8: 0
6 | Segunbagicha | D394S | 11 |  | DHK-C9360 | 1 | 20686.9 | 26166.36 | 5479.46 | 60 |  | 328767.6 | 331939.36 | Ramna |  |  |  |  | Segunbagicha | 331939.36 | 443816.6143 | -111877.2543 | -25.208 | OK
| Secretariat RMU | D394FB | 11 |  | DHK-C9379 | 1 | 81663.25 | 83159.69 | 1496.44 | 60 |  | 89786.4 | 90652.6074 | Ramna |  |  |  |  | Secretariat RMU | 90652.6074 | 124236.116 | -33583.5087 | -27.032 | OK
7 | NBR RMU | D394NR | 11 |  | DHK-C9319 | 1 | 78532.8 | 82593.8 | 4061 | 60 |  | 243660 | 246010.691 | Ramna |  |  |  |  | NBR RMU | 246010.691 | 319447.2431 | -73436.552 | -22.9886 | OK
8 | Ramna 11 kV Sw/S-2 |  | 11 |  | DHK-C9364 | 1 | 64314.76 | 74109.1 | 9794.34 | 60 |  | 587660.4 | 593329.8083 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-2 | 593329.8083 | 847238.794 | -253908.9856 | -29.969 | OK
11 | Ramna 11 kV Sw/S-1 |  | 11 |  | DHK-C9375 | 1 | 57677.67 | 57712.71 | 35.04 | 60 |  | 2102.4 | 2122.6827 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-1 | 2122.6827 | 103793.1904 | -101670.5077 | -97.9549 | CHECK
12 | Family Planning | D394FP | 11 |  | DHK-C9378 | 1 | 77750.21 | 81981.71 | 4231.5 | 60 |  | 253890 | 256339.3842 | Ramna |  |  |  |  | Family Planning | 256339.3842 | 360288.4749 | -103949.0907 | -28.8516 | OK
13 | Muktijuddho Montranalaya | D394MJ | 11 |  | DHK-C9376 | 1 | 99696.86 | 107684.92 | 7988.06 | 60 |  | 479283.6 | 483907.4515 | Ramna |  |  |  |  | Muktijuddho Montranalaya | 483907.4515 | 671537.2027 | -187629.7512 | -27.9403 | OK
14 | Purana Palton | D394R | 11 |  | DHK-C9318 | 1 | 70819.4 | 74578.56 | 3759.16 | 60 |  | 225549.6 | 227725.5723 | Ramna |  |  |  |  | Purana Palton | 227725.5723 | 301353.4691 | -73627.8968 | -24.4324 | OK
15 | Tip Top Feeder |  | 11 |  | DHK-C9318 | 1 | 92552.33 | 104709.02 | 12156.69 | 60 |  | 729401.4 | 736438.2437 | Kakrail |  |  |  |  | Tip Top Feeder | 736438.2437 | 1345378.9377 | -608940.694 | -45.2616 | CHECK
16 | 11/0.4 kV Auxiliary Transformer, AT |  | 0.415 |  | DHKD3784 | 1 | 359859 | 363148 | 3289 | 1 |  | 3289 | 3320.7304 | Ramna |  |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 3320.7304 | 4689.0579 | -1368.3275 | -29.1813 | OK
|  |  | 10: Grand Total | 2971786.5315 | 2943390.4 | 2971786.5315 | 0.96474
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2235348.2879
[6 empty] | Kakrail | at 33 KV level |  | 736438.2437
[6 empty] | Total = |  |  | 2971786.5315 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 |  | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 |  | 33 | 0 | 2803 | 1.05 | 333.41 | 340.11 | 6.7 | 360000 | 0 | 2532600 | 2518968.3875
|  |  | 10: Total | 0 | 2532600 | 2518968.3875
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder |  | 33 | 0 | BD001840 | 1 | 464.63 | 475.63 | 11 | 240000 | 0 | 2640000 | 2643865.0349
|  |  | 10: Total |  | 2640000 | 2643865.0349
| DMCH 33 KV SIDE (RECEIVING) | [11 empty] | 5162833.4225
| 33 kV DU Incoming Circuit-1 |  | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming |  | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 |  | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0 | 0
| DMCH 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DMCH 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | 00000069 | 1 | 138244800 | 138244800 | 0 | 1 |  | 0
2 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 10: Total |  | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 4: 2518968.3875; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5162833.4225
| DHANMONDI 33 kV SIDE |  | 4: 2643865.0349; 6: 33 KV NET IMPORT; 9=8-7: 5162833.4225 | 33 KV TX HV SIDE |  | 5162833.4225
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 5162833.4225
11 KV SIDE of___DMCH 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000056 | 1 | 136910672 | 139558464 | 2647792 | 1 | 2647792 |  | 2724649.0141
14 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000034 | 1 | 165462480 | 167831888 | 2369408 | 1 | 2369408 |  | 2438184.4084
|  |  | 7: 0; 8: 0; 10: Total | 5017200 |  | 5162833.4225
| DMCH 11 KV SIDE |  | 7: 0; 8: 0
6 | Nearest O/H | D398NE | 11 |  | 00000126 | 1 | 8118980 | 8233620 | 114640 | 1 |  | 114640 | 115623.9439 | Ramna |  |  |  |  | Nearest O/H | 115623.9439 | 175545.4669 | -59921.523 | -34.1345 | OK
| Jagannath Hall | D398JA | 11 |  | 00000002 | 1 | 3050232 | 3117432.5 | 67200.5 | 1 |  | 67200.5 | 67777.2753 | Ramna |  |  |  |  | Jagannath Hall | 67777.2753 | 82037.8689 | -14260.5936 | -17.3829 | OK
7 | Samsun Nahar Hall | D398SN | 11 |  | 00000024 | 1 | 10524494 | 10689174 | 164680 | 1 |  | 164680 | 166093.4323 | Ramna |  |  |  |  | Samsun Nahar Hall | 166093.4323 | 229211.7629 | -63118.3307 | -27.5371 | OK
8 | Spare, 4L |  | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | A3983 | 11 |  | 00000023 | 1 | 23025144 | 23638862 | 613718 | 1 |  | 613718 | 618985.4813 | Lalbag |  |  |  |  | Board Office O/H, (5L) | 618985.4813 | 282360.0725 | 336625.4088 | 119.2185 | FAULT
10 | OT- Complex | D398OT | 11 |  | 00000167 | 1 | 7175302 | 7368582 | 193280 | 1 |  | 193280 | 194938.9033 | Ramna |  |  |  |  | OT- Complex | 194938.9033 | 340061.3683 | -145122.4651 | -42.6754 | CHECK
11 | Alia Mdrasha O/H, (7L) | A3984 | 11 |  | 00000148 | 1 | 9776616 | 9997056 | 220440 | 1 |  | 220440 | 222332.0149 | Lalbag |  |  |  |  | Alia Mdrasha O/H, (7L) | 222332.0149 | 101819.0581 | 120512.9567 | 118.3599 | FAULT
12 | Majed Sordar Road | B698J | 11 |  | 00000164 | 1 | 62242088 | 63519284 | 1277196 | 1 |  | 1277196 | 1288158.0478 | Bangshal |  |  |  |  | Majed Sordar Road | 1288158.0478 | 1959932.9522 | -671774.9044 | -34.2754 | OK
15 | Chankharpool, 9L | B698Q | 11 |  | 00000001 | 1 | 50750956 | 51452996 | 702040 | 1 |  | 702040 | 708065.5404 | Bangshal |  |  |  |  | Chankharpool, 9L | 708065.5404 | 416746.8435 | 291318.6969 | 69.903 | FAULT
16 | Shahidullah College O/H, (10L) | A3986 | 11 |  | 00000003 | 1 | 13802806 | 14004206 | 201400 | 1 |  | 201400 | 203128.5964 | Lalbag |  |  |  |  | Shahidullah College O/H, (10L) | 203128.5964 | 207912.8783 | -4784.2819 | -2.3011 | OK
17 | Ananda Bazar | D398AB | 11 |  | 00000111 | 1 | 15359723 | 15427242 | 67519 | 1 |  | 67519 | 68098.5089 | Ramna |  |  |  |  | Ananda Bazar | 68098.5089 | 103817.0773 | -35718.5684 | -34.4053 | OK
18 | Hosseni Dalan O/H, (12L) | A3985 | 11 |  |  | 1 | 65.91 | 67.97 | 2.06 | 60000 | Estimated | 688147.92 | 694054.226 | Lalbag | Estimated from Grid SAS Data |  |  |  | Hosseni Dalan O/H, (12L) | 694054.226 | 859332.9703 | -165278.7443 | -19.2334 | OK
19 | Badrun Nessa College | A398W | 11 |  | 00000006 | 1 | 21354548 | 21641708 | 287160 | 1 |  | 287160 | 289624.6661 | Lalbag |  |  |  |  | Badrun Nessa College | 289624.6661 | 354408.6447 | -64783.9786 | -18.2795 | OK
20 | Dhaka Medical College, Unit-II | D398DM | 11 |  | 00000125 | 1 | 12836569 | 13008288 | 171719 | 1 |  | 171719 | 173192.8473 | Ramna |  |  |  |  | Dhaka Medical College, Unit-II | 173192.8473 | 223818.1101 | -50625.2628 | -22.6189 | OK
21 | Spare, 15L |  | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | D398SH | 11 |  | 00000127 | 1 | 22395106 | 22744864 | 349758 | 1 |  | 349758 | 352759.9386 | Ramna |  |  |  |  | Sheikh Hasina National Burn Institute | 352759.9386 | 420023.595 | -67263.6564 | -16.0143 | OK
23 | Aux. Transformer, AT-1 |  | 0.415 |  | DHKF-7804 | 1 | 2923.68 | 2923.68 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-1 | 0 | 5076.9668 | -5076.9668 | -100 | CHECK
24 | Aux. Transformer, AT-2 |  | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5162833.4225 | 5118898.42 | 5162833.4225 | 0.85829
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1138484.8495
[6 empty] | Lalbag | at 33 KV level |  | 2028124.9847
[6 empty] | Bangshal | at 33 KV level |  | 1996223.5882
[6 empty] | Total = |  |  | 5162833.4225 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 |  | 33 | 0 | 2804 | 1.5 | 181.85 | 187.29 | 5.44 | 360000 | 0 | 2937600 | 2921788.4922
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 210.83 | 214.76 | 3.93 | 360000 | 0 | 1414800 | 1407184.8988
|  |  | 10: Total | 0 | 4352400 | 4328973.3909
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 |  | 33 |  | BD 017078 | 1 | 27939.19 | 30559.31 | 2620.12 | 1125 |  | 2947635
| 33 kV Dhaka University-2 |  | 33 |  | BD 017090 | 1 | 75816.77 | 77156.57 | 1339.8 | 1125 |  | 1507275
|  |  | 7: 0; 8: 0; 10: Total | 0 | 4454910 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD 017093 | 1 | 106526.14 | 106526.14 | 0 | 1000 |  | 0
3 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD 017094 | 1 | 61232.28 | 62575.2 | 1342.92 | 1000 |  | 1342920
|  |  | 10: Total |  | 1342920
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 4328973.3909; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BB AVENEU 33 KV NET IMPORT |  | 4328973.3909
|  |  | 6: BB AVENEU 33 KV NET IMPORT; 9=8-7: 4328973.3909 | 33 KV TX HV SIDE |  | 1342920
[11 empty] | LOSS UNITS=> |  | 2986053.3909
[11 empty] | LOSS % IN => |  | 68.98%
| TOTAL IMPORT |  | 4: 4328973.3909
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD 014052 | 1 | 106679.74 | 113577.48 | 6897.74 | 1000 | 6897740 |  | 3629502.2666
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD 014055 | 1 | 60655.42 | 61984.74 | 1329.32 | 1000 | 1329320 |  | 699471.1243
|  |  | 7: 0; 8: 0; 10: Total | 8227060 |  | 4328973.3909
| BB AVENEU 11 KV SIDE |  | 7: 0; 8: 0
6 | Secratariet East | D363BS | 11 |  | BD 013966 | 1 | 4544.19 | 4662.1 | 117.91 | 1000 |  | 117910 | 119229.0018 | Ramna |  |  |  |  | Secratariet East | 119229.0018 | 176076.397 | -56847.3952 | -32.2856 | OK
| Taher Bag O/H | B163G | 11 |  | BD 014045 | 1 | 21284.07 | 21741.99 | 457.92 | 1000 |  | 457920 | 463042.5281 | Narinda |  |  |  |  | Taher Bag O/H | 463042.5281 | 606900.3521 | -143857.8241 | -23.7037 | OK
7 | Al Raji Complex | D363AR | 11 |  | BD 013983 | 1 | 16656.82 | 17122.03 | 465.21 | 1000 |  | 465210 | 470414.0777 | Ramna |  |  |  |  | Al Raji Complex | 470414.0777 | 584839.7594 | -114425.6816 | -19.5653 | OK
8 | Raduni | D363RI | 11 |  | BD 013999 | 1 | 31732.57 | 32490.8 | 758.23 | 1000 |  | 758230 | 766711.9498 | Ramna |  |  |  |  | Raduni | 766711.9498 | 970925.0317 | -204213.0818 | -21.0328 | OK
9 | Sundor Bon Square O/H | B163D | 11 |  | BD 013954 | 1 | 14602.66 | 14944.13 | 341.47 | 1000 |  | 341470 | 345289.8586 | Narinda |  |  |  |  | Sundor Bon Square O/H | 345289.8586 | 413245.1984 | -67955.3398 | -16.4443 | OK
10 | Shromo Bhobon O/H | D363SB | 11 |  | BD 013985 | 1 | 14602.66 | 14888.74 | 286.08 | 1000 |  | 286080 | 289280.2377 | Ramna |  |  |  |  | Shromo Bhobon O/H | 289280.2377 | 470791.9727 | -181511.735 | -38.5546 | OK
11 | Nawabpur Road | B163P | 11 |  | BD 013953 | 1 | 22640.38 | 23160.37 | 519.99 | 1000 |  | 519990 | 525806.8749 | Narinda |  |  |  |  | Nawabpur Road | 525806.8749 | 713209.502 | -187402.6271 | -26.276 | OK
12 | Spair |  | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare |  | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | D363AP | 11 |  | BD 013984 | 1 | 12534.21 | 12968.49 | 434.28 | 1000 |  | 434280 | 439138.0789 | Ramna |  |  |  |  | Ahad Police Box | 439138.0789 | 488719.3167 | -49581.2378 | -10.1451 | OK
17 | Nearest O/H | D363NE | 11 |  | BD 013997 | 1 | 2970.68 | 3058.55 | 87.87 | 1000 |  | 87870 | 88852.9589 | Ramna |  |  |  |  | Nearest O/H | 88852.9589 | 103430.8152 | -14577.8563 | -14.0943 | OK
18 | Natab Bhaban | D363NB | 11 |  | BD 014000 | 1 | 5488.09 | 5613.02 | 124.93 | 1000 |  | 124930 | 126327.5311 | Ramna |  |  |  |  | Natab Bhaban | 126327.5311 | 141307.3092 | -14979.7782 | -10.6009 | OK
19 | Spare |  | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | D363AO | 11 |  | BD 013956 | 1 | 1452.23 | 1459.86 | 7.63 | 1000 |  | 7630 | 7715.3531 | Ramna |  |  |  |  | Awami League Party Office | 7715.3531 | 18136.4963 | -10421.1432 | -57.4595 | CHECK
21 | Khaddar Bazar | D363KB | 11 |  | BD 014012 | 1 | 11244.73 | 11528.62 | 283.89 | 1000 |  | 283890 | 287065.7392 | Ramna |  |  |  |  | Khaddar Bazar | 287065.7392 | 332552.2312 | -45486.492 | -13.678 | OK
22 | Bangobondu National Stidium | D363NS | 11 |  | BD 014008 | 1 | 11498.09 | 11887.08 | 388.99 | 1000 |  | 388990 | 393341.4417 | Ramna |  |  |  |  | Bangobondu National Stidium | 393341.4417 | 1044626.3348 | -651284.893 | -62.3462 | CHECK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4418 | 1 | 1481.27 | 1548.06 | 66.79 | 100 |  | 6679 | 6753.7147 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 6753.7147 | 7343.2393 | -589.5246 | -8.0281 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 48.11 | 48.15 | 0.04 | 100 |  | 4 | 4.0447 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 4.0447 | 0 | 4.0447 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4328973.3909 | 4281083 | 4328973.3909 | 1.1187
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2994834.1293
[6 empty] | Narinda | at 33 KV level |  | 1334139.2616
[6 empty] | Total = |  |  | 4328973.3909 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 |  | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
|  |  | 10: Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 |  | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 |  | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 |  | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 0
|  |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 0 | KALLYANPUR 11 KV NET IMPORT |  | 0
|  |  | 6: TOTAL EXPORT; 9=8-7: 0 | LOSS UNITS=> |  | 0
|  |  | 6: 132KV NET LOSS =>; 9=8-7: #DIV/0! | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 4: 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming |  | 11 |  | 74819926 | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  | 7: 0; 8: 0
A | From Kallyanpur S/S. |  | 7: 0; 8: 0
| 11 KV Gano Bhavan RMU | D534T | 11 |  | DHK14997 | 1 | 995.9 | 996.01 | 0.11 | 40000 |  | 4400 | 4510 | Shere b.nagar |  |  |  |  | 11 KV Gano Bhavan RMU | 4510 | 1230 | 3280 | 266.6667 | FAULT
| 11 KV Beribandh Feeder. | G134K | 11 |  | DHK14960 | 1 | 9673.06 | 9678.27 | 5.21 | 40000 |  | 208400 | 213610 | Adabor |  |  |  |  | 11 KV Beribandh Feeder. | 213610 | 230010 | -16400 | -7.1301 | OK
| 11 KV Adabor O/H | D434A | 11 |  | DHK14957 | 1 | 4620.87 | 4662.01 | 41.14 | 40000 |  | 1645600 | 1686740 | Adabor |  |  |  |  | 11 KV Adabor O/H | 1686740 | 1540370 | 146370 | 9.5023 | OK
| 11 KV Mansurabad | G134M | 11 |  | 77816681 | 1 | 52970.34 | 53140.44 | 170.1 | 8000 |  | 1360800 | 1394820 | Adabor |  |  |  |  | 11 KV Mansurabad | 1394820 | 1650496 | -255676 | -15.4909 | OK
| 11 KV Ring Road Feeder | G134R | 11 |  | 77816675 | 1 | 42456.21 | 42542.57 | 86.36 | 8000 |  | 690880 | 708152 | Adabor |  |  |  |  | 11 KV Ring Road Feeder | 708152 | 871742 | -163590 | -18.7659 | OK
| 11 KV Sewarage Pump | G134P | 11 |  | DHK14959 | 1 | 2350.06 | 2404.55 | 54.49 | 40000 |  | 2179600 | 2234090 | Adabor |  |  |  |  | 11 KV Sewarage Pump | 2234090 | 2206210 | 27880 | 1.2637 | OK
| 11 KV Technical School (DPDC) | G134T | 11 |  | DHK15019 | 1 | 8401.63 | 8432.58 | 30.95 | 40000 |  | 1238000 | 1268950 | Adabor |  |  |  |  | 11 KV Technical School (DPDC) | 1268950 | 1626470 | -357520 | -21.9813 | OK
| 11 KV Goidertek (DPDC) | G134G | 11 |  | DHK14996 | 1 | 9431.09 | 9438.88 | 7.79 | 40000 |  | 311600 | 319390 | Adabor |  |  |  |  | 11 KV Goidertek (DPDC) | 319390 | 663380 | -343990 | -51.8541 | CHECK
B | From Agargaon S/S. |  | 3: 11 |  |  | 0
| 11 KV P.C Culture Housing | G186C | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H |  | 11 |  | DHK-15026 | 1 | 9229.09 | 9236.31 | 7.22 | 40000 |  | 288800 | 296020 | Shere b.nagar
| 11 KV Nearest RMU |  | 11 |  | DHK-15027 | 1 | 3878 | 3880.96 | 2.96 | 40000 |  | 118400 | 121360 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar |  | 11 |  | DHK-15025 | 1 | 3984.04 | 3986.34 | 2.3 | 40000 |  | 92000 | 94300 | Shere b.nagar
| 11 KV BICC Feeder. |  | 11 |  | DHK-15024 | 1 | 1038.9 | 1038.93 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar
| 11 KV NEC Feeder. |  | 11 |  | DHK-15023 | 1 | 431.67 | 431.67 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV Manik Mia Feeder. |  | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
|  |  | 7: Export To Desco; 9=8-7: 0; 10: Grand Total |  | 8139680 | 8343172 | 2.5
DESCO | 11 kV Tolarbugh |  | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil |  | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy |  | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari |  | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H |  | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur |  | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S |  | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 0 | 0 | #DIV/0!
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 7825752
[6 empty] | Shere b.nagar | at 33 KV level |  | 517420
[6 empty] | Satmasjid | at 33 KV level
[6 empty] | DESCO | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 8343172 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 |  | 33 | 0 | 30799147 | 1 | 1603.45 | 1624.4 | 20.95 | 240000 | 0 | 5028000 | 5205228.9474
|  |  | 10: Total | 0 |  | 5205228.9474
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
|  |  | 10: Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming |  | 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
| Lalbagh Incoming |  | 3: 33; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 |  | 33 |  | BD017102 | 1 | 1531.16 | 1545.87 | 14.71 | 180000 |  | 2647800
1 | Transformer-02 |  | 33 |  | BD017105 | 1 | 2008.94 | 2021.95 | 13.01 | 180000 |  | 2341800
|  |  | 10: Total |  | 4989600 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 5205228.9474; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 5205228.9474
| IMPORT-2 |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 5205228.9474 | KALLYANPUR 11 KV NET IMPORT |  | 5205228.9474
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 5205228.9474
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month December-2023 |  |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 140
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 110
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 30
|  |  | 10: Total | 0 |  | 5205228.9474 |  |  | 10
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 120
1 | Nizambag | F1114Z | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 502225.92 | 504749.4737 | Kamrangirchar | 80 |  |  |  | Nizambag | 504749.4737 | 234080.9166 | 270668.557 | 115.6303 | FAULT
2 | Merry Stopes | F1114P | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 60816.42 | 61122.0066 | Kamrangirchar | 5 |  |  |  | Merry Stopes | 61122.0066 | 55077.8627 | 6044.1438 | 10.9738 | OK
3 | Mujibur Ghat | F1114V | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1344684.1447 | Kamrangirchar | 110 |  |  |  | Mujibur Ghat | 1344684.1447 | 275389.3137 | 1069294.831 | 388.2848 | FAULT
4 | Madrasa | F1114U | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 941673.6 | 946405.2632 | Kamrangirchar | 150 |  |  |  | Madrasa | 946405.2632 | 330467.1764 | 615938.0867 | 186.384 | FAULT
5 | Thana | F1114Q | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1520410.5 | 1528050.1645 | Kamrangirchar | 125 |  |  |  | Thana | 1528050.1645 | 247850.3823 | 1280199.7822 | 516.5212 | FAULT
6 | Al-Hera |  | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | F1114W | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 816117.12 | 820217.8947 | Kamrangirchar | 80 |  |  |  | Waz Uddin School | 820217.8947 | 192772.5196 | 627445.3752 | 325.4849 | FAULT
8 | 11/0.4 kV Auxiliary Transformer |  | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off |  | 10: Grand Total | 5205228.9474 | 5179204.8 | 5205228.9474 | 0.50247
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 5205228.9474
[6 empty] | Total = |  |  | 5205228.9474 | 0
Note on G935: User: Grid CF=1.5
Note on G1888: User: Grd CF = 3

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) |  | 132 | IMPORT | 8993631 | 1 | 5948.831 | 5970.835 | 22.004 | 960000 | 0 | 21123840
| 132 KV Mogbazar-2 CKT(EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) |  | 132 |  | 8993659 | 1 | 5064.126 | 5080.769 | 16.643 | 960000 | 0 | 15977280
| 132 KV Mogbazar-1 CKT(EXP) |  | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 37101120
|  |  | 10: Net Total | 37101120
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE | 6604452 | 1 | 9505.05 | 9534.47 | 29.42 | 720000 | 21182400
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  | 6604428 | 1 | 5734.05 | 5756.44 | 22.39 | 720000 | 16120800
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
|  |  | 9=8-7: Total Import/Export | 37303200 | 0
|  |  | 9=8-7: Net Total | 37303200 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0 |  |  | future Scope
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0 |  |  | No meter
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 37303200
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 37101120; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 37101120
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 37101120 | MOGBAZAR 33 KV NET IMPORT |  | 37017600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 83520
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2251%
| 132 KV TOTAL IMPORT |  | 4: 37101120
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming |  | 33 | IMPORT | 76026303 | 1 | 10094.56 | 10120.94 | 26.38 | 480000 | 12662400 |  | 12690969.2116
| 132/33 KV GT-2 Incomming |  | 33 |  | 76026307 | 1 | 10089.58 | 10115.58 | 26 | 480000 | 12480000 |  | 12508157.6763
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 8292.12 | 8316.86 | 24.74 | 480000 | 11875200 |  | 11901993.112
|  |  | 7: 0; 8: 0; 10: Total | 37017600 |  | 37101120
| MOGBAZAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. |  | 33 |  | 6604465 | 1 | 7038.34 | 7048.53 | 10.19 | 180000 |  | 1834200 | 1840153.3008 |  | 12453088.4812 | MOGBAZAR 33/11 KV SS | 2.5014 | 33/11 KV Transformer No.1. | 1840153.3008 | 2300417.8861 | -460264.5853 | -20.0079 | OK
| 33/11 KV Transformer No.2. |  | 33 |  | 202006985 | 1 | 35669075293 | 35672822403 | 3747110 | 3 | T2 Incomer side | 3224800 | 3235266.7999 |  |  |  |  | 33/11 KV Transformer No.2. | 3235266.7999 | 4477341.5517 | -1242074.7518 | -27.7413 | OK
| 33/11 KV Transformer No.3. |  | 33 |  | 6604338 | 1 | 7166.66 | 7186.67 | 20.01 | 180000 |  | 3601800 | 3613490.4366 |  |  |  |  | 33/11 KV Transformer No.3. | 3613490.4366 | 4903712.1082 | -1290221.6716 | -26.3111 | OK
| 33/11 KV Transformer No.4 |  | 33 |  |  | 1 | 1161118 | 1182071 | 20953 | 180000 | T4 Incomer side | 3752000 | 3764177.9438 |  |  |  |  | 33/11 KV Transformer No.4 | 3764177.9438 | 4653718.9419 | -889540.9981 | -19.1146 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 12412800 | 12453088.4812 |  |  |  |  | 33 KV Feeders | 12453088.4812 | 16335190.4879 | -3882102.0067 | -23.7653 | OK
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 |  | 76026300 | 1 | 6802.73 | 6816.66 | 13.93 | 360000 |  | 5014800 | 5031076.6399 |  | 13793023.4657 | Tejgoan 33/11 kv ss | 1.4757 | 33 kV Tejgaon U/G Feeder-1 | 5031076.6399 | 6205359.2193 | -1174282.5794 | -18.9237 | OK
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 |  | 06604453 | 1 | 6657.36 | 6681.62 | 24.26 | 360000 |  | 8733600 | 8761946.8258 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 8761946.8258 | 10236499.0259 | -1474552.2001 | -14.4048 | OK
10 | Bashundhara City |  | 33 |  | 660434 | 1 | 814.02 | 824.68 | 10.66 | 180000 |  | 1918800 | 1925027.8888 | Shere b.nagar | 3729064.3436 | Ispahani 33/11 kv ss | 0.73163 | Bashundhara City | 1925027.8888 | 1952470.6666 | -27442.7778 | -1.4055 | OK
11 | Ispahani-1 |  | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Ispahani-2 |  | 33 |  |  | 1 | 3982.57 | 4003.22 | 20.65 | 180000 |  | 3717000 | 3729064.3436 |  | 1200855.0302 | Green Road Dormatory 33/11 kv ss | 0.66098 | Ispahani-2 | 3729064.3436 | 4600835.7721 | -871771.4285 | -18.9481 | OK
13 | 33 kV Green Road Dormitory |  | 33 |  | 76026305 | 1 | 8111.66 | 8115.73 | 4.07 | 180000 | Reading From G. Dormitory Side | 1196970 | 1200855.0302 |  |  |  |  | 33 kV Green Road Dormitory | 1200855.0302 | 0 | 1200855.0302 | #DIV/0! | #DIV/0!
14 | 33 KV Khejurbagan |  | 33 |  |  | 1 | 6236.18 | 6236.83 | 0.65 | 180000 |  | 117000 | 117379.7493 | Shere b.nagar |  |  |  | 33 KV Khejurbagan
15 | 33 KV T&T-1 |  | 33 |  | 6604337 | 1.05 | 4673.82 | 4692.24 | 18.42 | 180000 |  | 3481380 | 3492679.5869 |  | 3492679.5869 | T&T 33/11 kv ss | 1.0456 | 33 KV T&T-1 | 3492679.5869 | 3636318.8685 | -143639.2816 | -3.9501 | OK
16 | 33 KV T&T-2 |  | 33 |  | 6604336 | 1 | 5758.86 | 5758.86 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 KV T&T-2 | 0 | 2404982.3354 | -2404982.3354 | -100 | CHECK
17 | 33KV Karwan Bazar |  | 33 |  | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.042288 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | AT-1 |  | 33 |  | 6603338 | 1 | 2724.99 | 2853.83 | 128.84 | 80 |  | 10307.2 | 10340.6543 |  |  |  |  | AT-1 | 10340.6543 | 12478.0243 | -2137.37 | -17.1291 | OK
19 | AT-2 |  | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 24189857.2 | 24268370.7188 |  |  |  |  | 0 | 24268370.7188 | 29048943.9121 | -4780573.1933 | -16.457 | OK
|  |  | 9=8-7: Grand Total | 36721459.2 | 36602657.2 | 36721459.2 | 0.32457
-0.3377
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2042407.6381
|  |  | 9=8-7: Total =; 10: 2042407.6381 | 117379.7493 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 |  | 11 | Import | 6604457 | 1 | 546486.3 | 548298 | 1811.7 | 1000 | 1811700 |  | 1828851.471
2 | 33/11 kV Transformer-2 |  | 11 | Import | 30/11009-1101 | 1 | 600993.7 | 604218.5 | 3224.8 | 1000 | 3224800 |  | 3255329.3722
3 | 33/11 kV Transformer-3 |  | 11 | Import | 6604454 | 1 | 597273.2 | 600821 | 3547.8 | 1000 | 3547800 |  | 3581387.2323
4 | 33/11 kV Transformer-4 |  | 11 | Import |  | 1 | 1153.2 | 1176.65 | 23.45 | 160000 | 3752000 |  | 3787520.4057
|  |  | 7: 0; 8: 0; 10: Total | 12336300 |  | 12453088.4812
| MOGBAZAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 41105.9 | 41136.9 | 31 | 1000 |  | 31000 | 31110.7192 | Kakrail |  |  |  | 11 kV Doctor's Lane | 31110.7192 | 140940.5878 | -109829.8687 | -77.9264 | CHECK
2 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 81024 | 81311.7 | 287.7 | 1000 |  | 287700 | 288727.5453 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 288727.5453 | 67586.7284 | 221140.8169 | 327.1956 | FAULT
3 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 |  | 11 | T-1 | 30/11004-1101 | 1 | 121092.2 | 121388.3 | 296.1 | 1000 |  | 296100 | 297157.5466 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 297157.5466 | 354627.9687 | -57470.422 | -16.2058 | OK
7 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 133873.6 | 135083.5 | 1209.9 | 1000 |  | 1209900 | 1214221.262 | Moghbazar |  |  |  | 11KV Ambagan | 1214221.262 | 1754826.6729 | -540605.411 | -30.8068 | OK
[7 empty] | 0 | 0
5 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 150222.7 | 151349.6 | 1126.9 | 1000 |  | 1126900 | 1130924.8203 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1130924.8203 | 1339188.5287 | -208263.7084 | -15.5515 | OK
3 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10241.6 | 10338.2 | 96.6 | 1000 |  | 96600 | 96945.0152 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 96945.0152 | 117467.3528 | -20522.3376 | -17.4707 | OK
4 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 130036 | 131183.1 | 1147.1 | 1000 |  | 1147100 | 1151196.9663 | Kakrail |  |  |  | 11 kV Bangla Motor | 1151196.9663 | 1495406.9549 | -344209.9885 | -23.0178 | OK
1 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 180854.9 | 181893.3 | 1038.4 | 1000 |  | 1038400 | 1042108.7349 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1042108.7349 | 1981464.8041 | -939356.0691 | -47.4072 | CHECK
[7 empty] | 0 | 0
6 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 125174.5 | 126081.4 | 906.9 | 1000 | Estimated | 1216328.4 | 1220672.6215 | Kakrail | 100 |  |  | 11 kV Iskaton | 1220672.6215 | 1548241.5645 | -327568.943 | -21.1575 | OK
5 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 90371.6 | 91408.5 | 1036.9 | 1000 |  | 1036900 | 1040603.3776 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1040603.3776 | 1298009.1897 | -257405.8122 | -19.8308 | OK
2 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124552.3 | 124790.9 | 238.6 | 1000 |  | 238600 | 239452.1804 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 239452.1804 | 307276.7877 | -67824.6073 | -22.0728 | OK
3 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 116794.1 | 117328.9 | 534.8 | 1000 |  | 534800 | 536710.0842 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 536710.0842 | 748310.5439 | -211600.4597 | -28.2771 | OK
4 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 45007.6 | 45319 | 311.4 | 1000 |  | 311400 | 312512.1919 | Kakrail |  |  |  | 11 kV BSRS Feeder | 312512.1919 | 397324.9737 | -84812.7818 | -21.3459 | OK
2 | 11 kV Vumi Bhaban |  | 11 | T-3 | 21101039 | 1 | 9098.9 | 9161.9 | 63 | 1000 |  | 63000 | 63225.0099 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 63225.0099 | 102897.7587 | -39672.7487 | -38.5555 | OK
5 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | check | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0 | 8665568.0754 | 8634728.4 | 8665568.0754 | 0.35716 |  |  |  |  | 8665568.0754 | 11653570.4165
1 | 11 kV TCB Feeder | C608P | 11 | T-4 |  | 1 | 37126.3 | 37210.6 | 84.3 | 1000 |  | 84300 | 91371.619 | Kakrail |  |  |  | 11 kV TCB Feeder | 91371.619 | 275835.9679 | -184464.3489 | -66.8747 | CHECK
2 | 11 kV Tejgaon SS-2 |  | 11 | T-4 |  | 1 | 35724.6 | 36834.7 | 1110.1 | 1000 |  | 1110100 | 1203222.2332 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1203222.2332 | 1541959.4958 | -338737.2626 | -21.968 | OK
3 | Holy Day Inn | C108HY | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 263640 | 285755.7964 | Tejgaon |  |  |  | Holy Day Inn | 285755.7964 | 328334.8182 | -42579.0218 | -12.9682 | OK
4 | Polly Bhabon-2 | C608PB | 11 | T-4 |  | 1 | 18385 | 18386 | 1 | 1000 | According to AMR meter reading | 9660 | 10470.3421 | Kakrail |  |  |  | Polly Bhabon-2 | 10470.3421 | 17302.438 | -6832.0959 | -39.4863 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 |  | 1 | 21533.5 | 22448.4 | 914.9 | 1000 |  | 914900 | 991647.6183 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 991647.6183 | 1456551.0784 | -464903.4601 | -31.9181 | OK
6 | 11 kV Tejturibazar | C608X | 11 | T-4 |  | 1 | 133302 | 133608 | 306 | 1000 |  | 306000 | 331669.222 | Kakrail |  |  |  | 11 kV Tejturibazar | 331669.222 | 405180.9614 | -73511.7394 | -18.1429 | OK
7 | Songsad |  | 11 | T-4 |  | 1 | 3864.8 | 3864.8 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Songsad | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Chennel 24 |  | 11 | T-4 |  | 1 | 7329.92 | 7333.57 | 3.65 | 1000 |  | 3650 | 3956.1852 | Moghbazar |  |  |  | Chennel 24 | 3956.1852 | 2657.627 | 1298.5581 | 48.8616 | FAULT
8 | Sonargaon | C608K | 11 | T-4 |  | 1 | 42568 | 43020.7 | 452.7 | 1000 |  | 452700 | 490675.349 | Kakrail |  |  |  | Sonargaon | 490675.349 | 653797.6846 | -163122.3356 | -24.95 | OK
| AT -1 |  | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 |  | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[11 empty] | 3408768.3652 | 3144950 | 3408768.3652 | 8.3886
|  |  | 10: Total | 12453088.4812 | 11779678.4 | 12074336.4406 | 2.5014
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH | [13 empty] | AMR Meter Information
|  |  | 6: Moghbazar; 7: at 33 KV level; 9=8-7: 1457629.6275 | [13 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
|  |  | 6: Tejgaon; 7: at 33 KV level; 9=8-7: 5448670.0794 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 52380 | 3000
|  |  | 6: Kakrail; 7: at 33 KV level; 9=8-7: 5168036.7336 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 211260 | 3000
|  |  | 6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 0 | [13 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 9660 | 300
[6 empty] | Total = |  |  | 12074336.4406 | 0
AMR Meter Information
[24 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[24 empty] | Shah Garments | 850.51 | 863.61 | 234.38 | 238.74
[24 empty] | Habib Hotel | 2852.4 | 2903.86 | 946.68 | 965.64
[24 empty] | The Joint Director BRDB | 1415.14 | 1441.99 | 269.48 | 274.83
[26 empty] | 863.61 | 238.74
[26 empty] | 2903.86 | 965.64
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [24 empty] | 1441.99 | 274.83
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
15 | 33 KV T&T-1 |  | 33 | 0 | 6604337 | 1.05 | 4673.82 | 4692.24 | 18.42 | 180000 | 0 | 3481380 | 3492679.5869
16 | 33 KV T&T-2 |  | 33 | 0 | 6604336 | 1 | 5758.86 | 5758.86 | 0 | 180000 | 0 | 0 | 0
0 | Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 343.3399 | 356.7665 | 13.4266 | 240000 | 0 | 3222384 | 3222384
|  |  | 10: Total | 0 | 6703764 | 6715063.5869
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder |  | 33 | Import | DHK60891 | 1 | 6947 | 19700 | 12753 | 360 | 4591080
2 | 33 kV Moghbazar-2 Feeder |  | 33 | Import | DHK68131 | 1 | 898200 | 898200 | 0 | 360 | 0
| 33 kV Ullon Feeder |  | 33 | Import | DHK68132 | 1 | 362.7 | 380.97 | 18.27 | 180000 | 3288600
|  |  | 7: 0; 8: 0; 10: Total | 7879680 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 31989 | 157578 | 125589 | 180 |  | 22606020
4 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 917708 | 929872 | 12164 | 180 |  | 2189520 |  |  | Meter Problem
|  |  | 10: Total |  | 24795540 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 6715063.5869; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6715063.5869
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 6715063.5869 | 33/11 KV XF LV SIDE |  | 6640200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 74863.5869
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.115%
| TOTAL IMPORT |  | 4: 6715063.5869
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 155985 | 174537 | 18552 | 180 | 3339360 |  | 3377008.9364 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 108144 | 126482 | 18338 | 180 | 3300840 |  | 3338054.6505 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 6640200 |  | 6715063.5869 | 1.1274 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 225815 | 240206 | 14391 | 60 |  | 863460 | 872488.6042 | Kakrail |  |  |  | 11 kV post office | 872488.6042 | 1045950.5553 | -173461.9511 | -16.5841 | OK
2 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 508205 | 521860 | 13655 | 60 |  | 819300 | 827866.8536 | Kakrail |  |  |  | 11 kV anarkoli | 827866.8536 | 1005950.1284 | -178083.2748 | -17.703 | OK
3 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 968143 | 971446 | 3303 | 60 |  | 198180 | 200252.2312 | Moghbazar |  |  |  | 11 kV sonalibagh | 200252.2312 | 266002.8385 | -65750.6073 | -24.718 | OK
4 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1999157 | 2007924 | 8767 | 60 |  | 526020 | 531520.2274 | Moghbazar |  |  |  | 11 Kv desh tv | 531520.2274 | 691583.1374 | -160062.91 | -23.1444 | OK
5 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 690.8 | 706.34 | 15.54 | 60000 |  | 932400 | 942149.4621 | Moghbazar |  |  |  | 11 Kv Btcl | 942149.4621 | 1206073.4761 | -263924.014 | -21.8829 | OK
1 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 923585 | 929471 | 5886 | 60 |  | 353160 | 356852.7499 | Kakrail |  |  |  | 11 kV century | 356852.7499 | 456065.4727 | -99212.7228 | -21.7541 | OK
2 | 11 kV cinema hall |  | 11 | Mogbazar | DHK60979 | 1 | 535968 | 546370 | 10402 | 60 |  | 624120 | 630645.9913 | Moghbazar |  |  |  | 11 kV cinema hall | 630645.9913 | 805584.354 | -174938.3627 | -21.7157 | OK
3 | 11 kV malibagh bazar |  | 11 | Khailgaon | DHK61106 | 1 | 803461 | 819498 | 16037 | 60 |  | 962220 | 972281.2692 | Khilgaon |  |  |  | 11 kV malibagh bazar | 972281.2692 | 1271165.0797 | -298883.8105 | -23.5126 | OK
4 | 11 kv Sherebangla | D1105G | 11 |  | DHK60915 | 1 | 782199 | 795455 | 13256 | 60 |  | 795360 | 803676.5296 | Moghbazar |  |  |  | 11 kv Sherebangla | 803676.5296 | 1035344.3815 | -231667.8519 | -22.3759 | OK
5 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 364525 | 374009 | 9484 | 60 |  | 569040 | 574990.0578 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 574990.0578 | 572490.9575 | 2499.1003 | 0.43653 | OK
6 | Auxiliary |  |  | Export | U0004461 | 1 | 8333.5 | 8372.09 | 38.59 | 60 |  | 2315.4 | 2339.6105 | Moghbazar |  |  |  | Auxiliary | 2339.6105 | 2704.2713 | -364.6607 | -13.4846 | OK
|  |  | 10: Grand Total | 6715063.5869 | 6645575.4 | 6715063.5869 | 1.0456
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 2057208.2077
[6 empty] | Moghbazar | at 33 KV level |  | 3685574.11
[6 empty] | Khilgaon | at 33 KV level |  | 972281.2692
[6 empty] | Total = |  |  | 6715063.5869 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 |  | 132 | IMPORT | 8993681 | 1 | 0 | 3.198 | 3.198 | 1440000 | 0 | 13439520
| Ullon-1 |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  | 8993680 | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 13439520
|  |  | 9=8-7: Net Total | 13439520
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) |  | 132 |  | 8993624 | 1 | 4885.436 | 4892.631 | 7.195 | 960000 | 0 | 6907200
| Maniknager-2 (new line to ullon) |  | 132 |  |  | 1 | 11.083 | 11.083 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 6907200
|  |  | 9=8-7: Net Total | 6907200
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 |  | 132 |  | 8993659 | 1 | 4448.367 | 4458.841 | 10.474 | 960000 | 0 | 10055040
| Ullon U/G-1 |  | 132 |  |  | 1 | 1.561 | 1.561 | 0 | 960000 | 0 | 0
| Ullon U/G-2 |  | 132 |  | 8993660 | 1 | 4130.91 | 4140.621 | 9.711 | 960000 | 0 | 9322560
| Ullon U/G-2 |  | 132 |  |  | 1 | 1.33 | 1.33 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 19377600
|  |  | 9=8-7: Net Total | 19377600
| ULLON 132 KV SIDE (RECEIVING) | [9 empty] | 39724320
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) |  | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 9=8-7: Total Import/Export | 0 | 0
Net Total
| EXPORT TO OTHERS 132/33 KV SS | [13 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 |  | 132 |  |  | 1 | 1632768 | 1632768 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 |  | 132 |  |  | 1 | 2235495 | 2245585 | 10090 | 1000 |  | 10090000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 |  | 132 |  |  | 1 | 2991477 | 3001665 | 10188 | 1000 |  | 10188000 |  |  | 132 kV Ullon CKT-3 | 31978000
|  |  | 10: Total |  | 20278000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 19446320
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 4: 13439520; 6: EXPORT TO OTHER S/S; 9=8-7: 20278000 | 132 KV NET IMPORT |  | 19446320
| HORIPUR 132 SIDE (TARIFF POINT) |  | 4: 6907200; 6: 132 KV Net EXPORT; 9=8-7: 19446320 | 132/33 KV GT LV Side |  | 19035744
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 19377600 | LOSS UNITS=>(132 HV-33 LV) |  | 410576
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.111%
| 132 KV TOTAL IMPORT |  | 4: 39724320
33 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | BD001812 | 1 | 2257.2727 | 2275.1704 | 17.8977 | 480000 | 8590896 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming |  | 33 | Import | BD001858 | 1 | 2177.0059 | 2194.5675 | 17.5616 | 480000 | 8429568 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming |  | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 2015280 |  |  |  | Estimated | [5 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 19035744 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1690.629 | 1706.6468 | 16.0178 | 240000 |  | 3844272 | 3844272 |  | 8966904 | Taltola 33/11 kv ss | 0.29485 | Taltala-1 | 3844272 | 5730923.8044 | -1886651.8044 | -32.9206 | OK
| Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 343.3399 | 356.7665 | 13.4266 | 240000 |  | 3222384 | 3222384 |  |  |  |  | Mgbazar T&T | 3222384 | 2317613.4485 | 904770.5515 | 39.0389 | OK
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 |  | 0 | 0 |  | 3222384 | Mgbazar T&T 33/11 kv ss | 1.0456 | Kakrail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Taltala-2 |  | 33 | Export | BD001837 | 1 | 2639.7785 | 2661.1228 | 21.3443 | 240000 |  | 5122632 | 5122632 |  |  |  |  | Taltala-2 | 5122632 | 7005129.6209 | -1882497.6209 | -26.8731 | OK
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 0 | Kakrail 33/11 kv ss | 1.6183 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 0.081362 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3331 | 79.3331 | 0 | 240000 | From Downstream | 2272050 | 2272050 |  | 0 | Tejgoan 33/11 kv ss | 1.4757 | Khailgaon | 2272050 | 2016872.053 | 255177.947 | 12.6522 | OK
4 | AT at GIS Building |  | 415 | Export | DHKE4577 | 1 | 157988 | 159697 | 1709 | 1 |  | 1709 | 1709 |  | 2272050 | Khilgoan 33/11 kv ss | 0.4872 | AT at GIS Building | 1709 | 2776.1914 | -1067.1914 | -38.4408 | OK
|  |  | 7: 0; 8: 0; 10: TOTAL= |  | 14463047 | 14463047 |  |  |  |  | 0 | 14463047 | 17073315.1183 | -2610268.1183 | -15.2886 | OK
| 33 KV Local Feeder -1 |  | 33 | NET IMPORT |  | 1 | 1200.8375 | 1212.1286 | 11.2911 | 240000 |  | 2709864 | 2709864 |  | 4669608 | Ullon 33/11 kv ss | 0.94329 | 33 KV Local Feeder -1 | 2709864 | 3170622.7862 | -460758.7862 | -14.5321 | OK
| 33KV Local Feeder- 2 |  | 33 |  |  | 1 | 927.2613 | 935.4269 | 8.1656 | 240000 |  | 1959744 | 1959744 |  |  |  |  | 33KV Local Feeder- 2 | 1959744 | 3088670.0955 | -1128926.0955 | -36.5506 | OK
|  |  | 10: TOTAL= |  | 4669608 | 4669608 |  |  |  |  | 0 | 4669608 | 6259292.8817 | -1589684.8817 | -25.3972 | OK
|  |  | 10: Grand Total | 19132655 | 19132655 | 19132655 | 0
11 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 64 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 38 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 4669608 |  | 4669608 |  |  | 26 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [14 empty] | 8.6667 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 588546 | 594097.7099 | Moghbazar | 50 | 46.6667 |  | West Malibagh | 594097.7099 | 711283.282 | -117185.5721 | -16.4752 | OK
2 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1059382.8 | 1069375.8779 | Moghbazar | 90 |  |  | Ullon | 1069375.8779 | 1304019.3504 | -234643.4725 | -17.9939 | OK
3 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 918131.76 | 926792.4275 | Moghbazar | 78 |  |  | Mohanagar | 926792.4275 | 1244745.7435 | -317953.316 | -25.5436 | OK
4 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 588546 | 594097.7099 | Moghbazar | 50 |  |  | Bagichartek | 594097.7099 | 924668.2666 | -330570.5567 | -35.7502 | OK
1 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 941673.6 | 950556.3359 | Moghbazar | 80 |  |  | Mirbagh | 950556.3359 | 1185472.1367 | -234915.8008 | -19.8162 | OK
2 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 529691.4 | 534687.9389 | Moghbazar | 45 |  |  | West Rampura | 534687.9389 | 889104.1025 | -354416.1636 | -39.8622 | OK
3 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 |  | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 |  | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4669608 | 4625971.56 | 4669608 | 0.94329
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 4669608
[6 empty] | Total = |  |  | 4669608 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 |  | 132 | Export | 50146667 | 1 | 1886.879 | 1904.258 | 17.379 | 960000 | 0 | 16683840
2 | Rampura to Madartek-2 |  | 132 | Export | 50146668 | 1 | 1680.527 | 1697.667 | 17.14 | 960000 | 0 | 16454400
|  |  | 9=8-7: Total Import/Export | 0 | 33138240
|  |  | 9=8-7: Net Total | 33138240
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 |  | 132 | Import | SIEM0492 | 1 | 1668805 | 1685446 | 16641 | 1000 | 16641000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 |  | 132 | Import | SIEM0489 | 1 | 1618218 | 1634743 | 16525 | 1000 | 16525000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 33166000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 33166000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| MADERTEK 132 KV SIDE |  | 7: 0; 8: 0
3 | 133 kV GT-1 |  | 132 | Export |  | 1 | 1505378 | 1522043 | 16665 | 1000 |  | 16665000
4 | 133 kV GT-2 |  | 132 | Export |  | 1 | 1493107 | 1509661 | 16554 | 1000 |  | 16554000
|  |  | 10: Total |  | 33219000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 33138240; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 33138240
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 33138240 | 33 KV NET IMPORT |  | 33238000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -99760
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.301%
| 132 KV TOTAL IMPORT |  | 4: 33138240
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0516 | 1 | 1654069 | 1670747 | 16678 | 1000 | 16678000 |  | 16627942.9183
2 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0515 | 3 | 549335 | 554855 | 5520 | 1000 | 16560000 |  | 16510297.0817
|  |  | 7: 0; 8: 0; 10: Total | 33238000 |  | 33138240
| MADERTEK 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kv Transforfers |  | 7: 0; 8: 0
1 | 33 kV T-1 |  | 33 | Import | SIEM0512 | 1 | 423836 | 426369 | 2533 | 2000 |  | 5066000 | 5073525.0943 |  | 12452469.6056 | Madartek 33/11 kv ss
2 | 33 kV T-3 |  | 33 | Export |  | 1 | 82436 | 83546 | 1110 | 2000 |  | 2220000 | 2223297.6134
2 | 33 kV T-2 |  | 33 | Export | SIEM0505 | 1 | 427002 | 429576 | 2574 | 2000 |  | 5148000 | 5155646.898
| 33 kv Feeders |  | 7: 0; 8: 0; 10: Total |  | 12434000 | 12452469.6056 |  | 7745488.1719 | Banasree 33/11 kv ss
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 118449 | 120532 | 2083 | 2000 |  | 4166000 | 4172188.224
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 370267 | 373972 | 3705 | 2000 |  | 7410000 | 7421006.8986 |  | 7421006.8986 | Goran 33/11 kv ss
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 39708 | 40621 | 913 | 6000 |  | 5478000 | 5486137.0838
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 103053 | 104837 | 1784 | 2000 |  | 3568000 | 3573299.948 |  | 5486137.0838 | Amulia 33/11 kv ss
|  |  | 10: Total |  | 20622000 | 20652632.1544
|  |  | 9=8-7: Grand Total | 33105101.76 | 33056000 | 33105101.76 | 0.14854
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | GJU 71154 | 1 | 396603.8 | 399125.2 | 2521.4 | 2000 | 5042800 |  | 5071745.8225 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | GJU 71155 | 1 | 399942.9 | 402507 | 2564.1 | 2000 | 5128200 |  | 5157636.0211 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming |  | 11 | Import | 6604399 | 1 | 4759.7 | 4771.98 | 12.28 | 180000 | 2210400 |  | 2223087.762 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 12381400 |  | 12452469.6056 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 17.0895 | 18.1608 | 1.0713 | 1000000 |  | 1071292 | 1077503.1322 | Mugdapara |  |  |  | Sobujbagh | 1077503.1322 | 1312980.8765 | -235477.7443 | -17.9346 | OK
2 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 106484.9 | 107601.2 | 1116.3 | 1000 |  | 1116300 | 1122772.0794 | Mugdapara |  |  |  | Madertek | 1122772.0794 | 1278337.9483 | -155565.8689 | -12.1694 | OK
3 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 7446.5 | 8767.9 | 1321.4 | 1000 |  | 1321400 | 1329061.2073 | Mugdapara |  |  |  | Rajarbagh | 1329061.2073 | 1227377.6551 | 101683.5522 | 8.2846 | OK
| Goran | A921G | 11 |  | X1390296 | 1 | 35532.5 | 36638.8 | 1106.3 | 1000 |  | 1106300 | 1112714.1015 | Bashabo |  |  |  | Goran | 1112714.1015 | 1214687.9378 | -101973.8364 | -8.3951 | OK
5 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 15256.78 | 16123.789 | 867.009 | 1000 |  | 867009 | 872035.7411 | Mugdapara |  |  |  | Dhakhingaon | 872035.7411 | 1038687.6018 | -166651.8607 | -16.0445 | OK
6 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | Manda | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1661.0999 | 1837.281 | 176.1811 | 1000 |  | 176181.1 | 177202.562 | Mugdapara |  |  |  | Green Model Town | 177202.562 | 183059.6459 | -5857.0838 | -3.1995 | OK
1 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 5343.364 | 5741.1932 | 397.8292 | 1000 |  | 397829.2 | 400135.7324 | Mugdapara |  |  |  | Biswa Road | 400135.7324 | 375481.886 | 24653.8464 | 6.5659 | OK
2 | Mugdapara | B921P | 11 |  | X0854272 | 1 | 4957.2 | 5114.1 | 156.9 | 1000 |  | 156900 | 157809.6742 | Maniknagar |  |  |  | Mugdapara | 157809.6742 | 277461.6755 | -119652.0014 | -43.1238 | CHECK
| Singapur | F221S | 11 |  | X1390302 (N) | 1 | 41999.2 | 43327 | 1327.8 | 1000 |  | 1327800 | 1335498.3132 | Banosree |  |  |  | Singapur | 1335498.3132 | 1578862.6815 | -243364.3683 | -15.4139 | OK
| Trimohony | F221T | 11 |  | X1390308 | 1 | 34398.2 | 35701.8 | 1303.6 | 1000 |  | 1303600 | 1311158.0066 | Banosree |  |  |  | Trimohony | 1311158.0066 | 1565165.8438 | -254007.8372 | -16.2288 | OK
5 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 19281.996 | 20389.554 | 1107.558 | 1000 |  | 1107558 | 1113979.3951 | Mugdapara |  |  |  | Mayakanon | 1113979.3951 | 1516431.2867 | -402451.8916 | -26.5394 | OK
6 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 7716.29 | 7952.16 | 235.87 | 1000 |  | 235870 | 237237.5261 | Mugdapara |  |  |  | Ahmedbagh | 237237.5261 | 554113.2234 | -316875.6973 | -57.1861 | CHECK
1 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 755370 | 761504 | 6134 | 200 |  | 1226800 | 1233912.7358 | Mugdapara |  |  |  | Wasa Road | 1233912.7358 | 1333024.5871 | -99111.8513 | -7.4351 | OK
2 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 783208 | 787992 | 4784 | 200 |  | 956800 | 962347.331 | Mugdapara |  |  |  | Nandipara | 962347.331 | 1198876.1472 | -236528.8163 | -19.7292 | OK
| AT-1 |  | 0.415 |  |  | 1 | 1021.24 | 1075.8 | 54.56 | 80 |  | 4364.8 | 4390.1062 | Mugdapara |  |  |  | AT-1 | 4390.1062 | 5672.1022 | -1281.996 | -22.6018 | OK
3 | AT-2 |  | 0.415 |  | 63394003 | 1 | 549.25 | 607.81 | 58.56 | 80 |  | 4684.8 | 4711.9615 | Mugdapara |  |  |  | AT-2 | 4711.9615 | 5966.9871 | -1255.0255 | -21.0328 | OK
|  |  | 10: Total | 12452469.6056 | 12380688.9 | 12452469.6056 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 12452469.6056 | 12380688.9 | 12452469.6056 | 0.57978
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 2646656.3198
[6 empty] | Bashabo | at 33 KV level |  | 1112714.1015
[6 empty] | Maniknagar | at 33 KV level |  | 157809.6742
[6 empty] | Mugdapara | at 33 KV level |  | 8535289.5103
[6 empty] | Total = |  |  | 12452469.6056 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 | 0 | 76026300 | 1 | 6802.73 | 6816.66 | 13.93 | 360000 | 0 | 5014800 | 5031076.6399
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 | 0 | 06604453 | 1 | 6657.36 | 6681.62 | 24.26 | 360000 | 0 | 8733600 | 8761946.8258
0 | Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 13748400 | 13793023.4657
TEJGOAN 33 KV SIDE (RECEIVING)
|  |  | 7: 0; 8: 0; 10: Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 783323.2 | 801892.3 | 18569.1 | 270 |  | 5013657
2 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 677710.6 | 710147.5 | 32436.9 | 180 |  | 5838642
3 | 33/11 kV Transfomer-3 (T3) |  | 33 | Export | BD001872 | 1 | 1328.9426 | 1351.6046 | 22.662 | 180000 |  | 4079160
|  |  | 10: Total |  | 14931459 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 13793023.4657; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TEJGOAN 33 KV NET IMPORT |  | 13793023.4657
| IMPORT-2 |  | 6: TEJGOAN 33 KV NET IMPORT; 9=8-7: 13793023.4657 | 33 KV TX HV Side |  | 14931459
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -1138435.5343
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -8.254%
| TOTAL IMPORT |  | 4: 13793023.4657
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 991694.1 | 1017157.3 | 25463.2 | 180 | 4583376 |  | 9145282.5133 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 893032.7 | 905973.4 | 12940.7 | 180 | 2329326 |  | 4647740.9524 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming |  | 11 | Import | BD001875 | 1 | 235650.9 | 235650.9 | 0 | 1000 | 0 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 6912702 |  | 13793023.4657 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | C110U | 11 |  | DHK60950 | 1 | 324180.3 | 338621.4 | 14441.1 | 60 |  | 866466 | 879252.6995 | Tejgaon |  |  |  | Nakhal Para Feeder | 879252.6995 | 1127439.9287 | -248187.2292 | -22.0133 | OK
2 | Badda-Meghna Feeder | C110N | 11 |  | DHK60979 | 1 | 952442.1 | 960822.6 | 8380.5 | 60 |  | 502830 | 510250.4136 | Tejgaon |  |  |  | Badda-Meghna Feeder | 510250.4136 | 710173.5747 | -199923.161 | -28.1513 | OK
3 | Rasulbagh Feeder | C110K | 11 |  | DHK60948 | 1 | 107045.9 | 127321.3 | 20275.4 | 60 |  | 1216524 | 1234476.6108 | Tejgaon |  |  |  | Rasulbagh Feeder | 1234476.6108 | 1507771.5116 | -273294.9008 | -18.1258 | OK
4 | Lukas | C171V | 11 |  | 8A021100948-02 | 1 | 75134351 | 76487313 | 1352962 | 1 |  | 1352962 | 1372928.0674 | Tejgaon |  |  |  | Lukas | 1372928.0674 | 1596720.7407 | -223792.6733 | -14.0158 | OK
5 | PWD RMU |  | 11 |  |  | 1 | 661501.9 | 662699.7 | 1197.8 | 1 |  | 1197.8 | 1215.4763 | Tejgaon |  |  |  | PWD RMU | 1215.4763 | 1463.309 | -247.8327 | -16.9365 | OK
1 | Civil Aviation Feeder |  | 11 |  | DHK60977 | 1 | 19068.7 | 47798.9 | 28730.2 | 60 |  | 1723812 | 1749250.8125 | Tejgaon |  |  |  | Civil Aviation Feeder | 1749250.8125 | 2103712.8393 | -354462.0269 | -16.8494 | OK
2 | Ahasanullah Eng. | C171L | 11 |  | DHK60867 | 1 | 908328.2 | 914459.3 | 6131.1 | 60 |  | 367866 | 373294.7093 | Tejgaon |  |  |  | Ahasanullah Eng. | 373294.7093 | 467019.6637 | -93724.9544 | -20.0687 | OK
3 | New GMG Feeder | C110M | 11 |  | DHK61106 | 1 | 180726.9 | 204440.4 | 23713.5 | 60 |  | 1422810 | 1443806.8354 | Tejgaon |  |  |  | New GMG Feeder | 1443806.8354 | 1745180.0137 | -301373.1783 | -17.2689 | OK
4 | Shikajo | C171Z | 11 |  | HA021101036-02 | 1 | 66732385 | 67251272 | 518887 | 1 |  | 518887 | 526544.3716 | Tejgaon |  |  |  | Shikajo | 526544.3716 | 677285.3335 | -150740.9618 | -22.2566 | OK
5 | Kahinur |  | 11 |  |  | 1 | 602529.6 | 616855.2 | 14325.6 | 60 |  | 859536 | 872220.4314 | Tejgaon |  |  |  | Kahinur | 872220.4314 | 1070076.3665 | -197855.9351 | -18.4899 | OK
6 | Link road | C171X | 11 |  | 8A021100380-02 | 1 | 66526725 | 66817451 | 290726 | 1 |  | 290726 | 295016.3311 | Tejgaon |  |  |  | Link road | 295016.3311 | 416288.669 | -121272.3379 | -29.1318 | OK
7 | Shanta | C110E | 11 |  |  | 1 | 350241.3 | 357200.4 | 6959.1 | 60 |  | 417546 | 423707.852 | Tejgaon |  |  |  | Shanta | 423707.852 | 526308.4207 | -102600.5687 | -19.4944 | OK
1 | Karnafuly Feeder | C110Y | 11 |  | DHK61084 | 1 | 37300.6 | 37764.9 | 464.3 | 1000 |  | 464300 | 471151.8148 | Tejgaon |  |  |  | Karnafuly Feeder | 471151.8148 | 622218.1242 | -151066.3094 | -24.2787 | OK
2 | Butex | C110BT | 11 |  |  | 1 | 1403 | 1478.6 | 75.6 | 1000 |  | 75600 | 76715.652 | Tejgaon |  |  |  | Butex | 76715.652 | 104608.2847 | -27892.6328 | -26.6639 | OK
3 | OriON LAB | C171A | 11 |  |  | 1 | 8454240 | 8514212 | 59972 | 1 |  | 59972 | 60857.0249 | Tejgaon |  |  |  | OriON LAB | 60857.0249 | 76732.1885 | -15875.1637 | -20.6891 | OK
4 | Nina kabbo | C171Y | 11 |  | 201101025-2 | 1 | 17854558 | 18027840 | 173282 | 1 |  | 173282 | 175839.1746 | Tejgaon |  |  |  | Nina kabbo | 175839.1746 | 208000.4981 | -32161.3235 | -15.4621 | OK
5 | Satrong | C171S | 11 |  | HA021100515-2 | 1 | 98397161 | 99276332 | 879171 | 1 |  | 879171 | 892145.191 | Tejgaon |  |  |  | Satrong | 892145.191 | 1231591.5581 | -339446.367 | -27.5616 | OK
6 | South East RMU |  | 11 |  |  | 1 | 1176.1 | 1238.1 | 62 | 1000 |  | 62000 | 62914.9527 | Tejgaon |  |  |  | South East RMU | 62914.9527 | 67794.2153 | -4879.2626 | -7.1972 | OK
7 | Rangs Bhaban |  | 11 |  | HA021100939-2 | 1 | 1006950 | 1105998 | 99048 | 1 |  | 99048 | 100509.6811 | Tejgaon |  |  |  | Rangs Bhaban | 100509.6811 | 126221.9657 | -25712.2845 | -20.3707 | OK
8 | Babli | C171R | 11 |  |  | 1 | 61327 | 62640.4 | 1313.4 | 1000 |  | 1313400 | 1332782.2391 | Tejgaon |  |  |  | Babli | 1332782.2391 | 926990.3383 | 405791.9008 | 43.7752 | FAULT
| SPL |  | 11 |  |  | 1 | 5708.6 | 6113.4 | 404.8 | 1000 |  | 404800 | 410773.7554 | Tejgaon |  |  |  | SPL | 410773.7554 | 403948.9148 | 6824.8406 | 1.6895 | OK
9 | DNCC Hospital |  | 11 |  |  | 1 | 18258.1 | 18777.8 | 519.7 | 1000 |  | 519700 | 527369.3693 | Tejgaon |  |  |  | DNCC Hospital | 527369.3693 | 724311.7867 | -196942.4174 | -27.1903 | OK
| 11/.415 kv Local transformer |  | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
|  |  | 10: Grand Total | 13793023.4657 | 13592435.8 | 13793023.4657 | 1.4757
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Tejgaon | at 33 KV level |  | 13793023.4657
[6 empty] | Total = |  |  | 13793023.4657 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 |  | 33 | 0 | 214393/44-2711 | 1 | 4308.85 | 7383.4 | 3074.55 | 1000 | Estimated | 3088418.4 | 3138703.1801
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 4913731.8 | 4993735.8316
|  |  | 10: Total |  | 8002150.2 | 8132439.0118
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 33 | Import | DHKC9350 | 1 | 30700.57 | 42129.56 | 11428.99 | 270 | 3085827.3
2 | Shatmasjid-2 |  | 33 | Import | DHKC9354 | 1 | 55611.4 | 73929.2 | 18317.8 | 270 | 4945806
|  |  | 7: 0; 8: 0; 10: Total | 8031633.3
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  | 7: 0; 8: 0
1 | Transfomer-1 (T1) |  | 33 | Export | DHKC9353 | 1 | 17157.52 | 34315.4 | 17157.88 | 180 |  | 3088418.4
2 | Transfomer-2 (T2) |  | 33 | Export | DHKC9305 | 1 | 96496.48 | 124040.35 | 27543.87 | 180 |  | 4957896.6
|  |  | 10: Total |  | 8046315 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 4: 8132439.0118; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | ASADGATE 33 KV NET IMPORT |  | 8132439.0118
| IMPORT-2 |  | 6: ASADGATE 33 KV NET IMPORT; 9=8-7: 8132439.0118 | ASADGATE 11 KV NET IMPORT |  | 7978569.9144
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 153869.0973
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.892%
| TOTAL IMPORT |  | 4: 8132439.0118
11 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHKC9371 | 1 | 59690.95 | 70955.41 | 11264.46 | 180 | 3088418.4 |  |  |  | From Upstream | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHKC9337 | 1 | 96200.99 | 123499.5 | 27298.51 | 180 | 4913731.8 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 8002150.2 |  | 8132439.0118 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | D570T | 11 | T-1 | DHKC9332 | 1 | 84785.44 | 86324.71 | 1539.27 | 60 | Previous Meter | 92356.2 | 94730.2684 | Shere b.nagar |  |  |  | Gonobhaban | 94730.2684 | 138463.2177 | -43732.9493 | -31.5845 | OK
2 | Town hall | D270R | 11 | T-1 | DHKC9339 | 1 | 48476.04 | 48476.4 | 0.36 | 60 | 292041.6 | 292063.2 | 299570.85 | Shyamoli | Feeder Swapped |  |  | Town hall | 299570.85 | 907389.807 | -607818.957 | -66.9854 | CHECK
3 | Post Office | D570S | 11 | T-1 | DHKC9324 | 1 | 85995.04 | 95416.99 | 9421.95 | 60 |  | 565317 | 579848.7937 | Shere b.nagar |  |  |  | Post Office | 579848.7937 | 881149.6455 | -301300.8518 | -34.1941 | OK
4 | Wasa O/H | C270W | 11 | T-1 | DHKC9333 | 1 | 70721.35 | 76278.95 | 5557.6 | 60 |  | 333456 | 342027.6753 | Satmasjid |  |  |  | Wasa O/H | 342027.6753 | 723429.7254 | -381402.0501 | -52.7214 | CHECK
5 | Bangabandhu Memorial Museum |  | 11 | T-1 | DHKC9334 | 1 | 16545.05 | 16631.31 | 86.26 | 60 |  | 5175.6 | 5308.6417 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 5308.6417 | 12869.2668 | -7560.6251 | -58.7495 | CHECK
6 | Iqbal Road O/H | D470Q | 11 | T-1 | DHKC9330 | 1 | 66650.02 | 70225.65 | 3575.63 | 60 |  | 214537.8 | 220052.6157 | Shyamoli |  |  |  | Iqbal Road O/H | 220052.6157 | 1111797.4278 | -891744.8121 | -80.2075 | CHECK
7 | Rapa Plaza Feeder | D470W | 11 | T-1 | DHKC9351 | 1 | 34396.36 | 46751.85 | 12355.49 | 60 | 146162.4 | 887491.8 | 910305.2794 | Dhanmondi | Feeder Swapped |  |  | Rapa Plaza Feeder | 910305.2794 | 1599081.4323 | -688776.1529 | -43.0732 | CHECK
8 | Sukrabad/South Plaza | D470P | 11 | T-1 | DHKC9331 | 1 | 50889.76 | 55736.63 | 4846.87 | 60 |  | 290812.2 | 298287.6923 | Shyamoli |  |  |  | Sukrabad/South Plaza | 298287.6923 | 1080300.7626 | -782013.0703 | -72.3885 | CHECK
9 | Shangshad Bhaban |  | 11 | T-2 | DHKC9370 | 1.05 | 24023.68 | 24136.05 | 112.37 | 60 |  | 7079.31 | 7261.2877 | Shere b.nagar | 33 Hours Load on T-1 Transformer but Energy was not recorded. So, CF Provided |  |  | Shangshad Bhaban | 7261.2877 | 0.6051 | 7260.6826 | 1199914.4888 | FAULT
10 | Jakir Hossain Road | C270J | 11 | T-2 | DHKC9373 | 1.05 | 83237.19 | 94960.21 | 11723.02 | 60 |  | 738550.26 | 757535.1127 | Satmasjid |  |  |  | Jakir Hossain Road | 757535.1127 | 934510.389 | -176975.2763 | -18.9378 | OK
11 | New Colony O/H Feeder | C270N | 11 | T-2 | DHKC9369 | 1.05 | 48198.28 | 61209.99 | 13011.71 | 60 |  | 819737.73 | 840809.5526 | Satmasjid |  |  |  | New Colony O/H Feeder | 840809.5526 | 1003963.767 | -163154.2144 | -16.251 | OK
12 | Aurangzeb Feeder | D470M | 11 | T-2 | DHKC9321 | 1 | 54002.53 | 69155.15 | 15152.62 | 60 |  | 909157.2 | 932527.6007 | Shyamoli |  | CF Corrected |  | Aurangzeb Feeder | 932527.6007 | 1156516.7382 | -223989.1375 | -19.3676 | OK
13 | Asadgate Local Feeder | C270E | 11 | T-2 | DHKC9338 | 1.05 | 52468.4 | 60842.91 | 8374.51 | 60 |  | 527594.13 | 541156.2359 | Satmasjid |  |  |  | Asadgate Local Feeder | 541156.2359 | 617884.5528 | -76728.3169 | -12.4179 | OK
14 | Sonarbangla Road | D470R | 11 | T-2 | DHKC9320 | 1.05 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | D470H | 11 | T-2 | DHKC9366 | 1 | 83086.82 | 115702.31 | 32615.49 | 60 |  | 1956929.4 | 2007233.3786 | Shyamoli |  | CF Corrected |  | Humayun Road | 2007233.3786 | 1566720.6843 | 440512.6943 | 28.1169 | OK
16 | NHA | D470B | 11 | T-2 | DHKC9374 | 1 | 68657.31 | 70893.51 | 2236.2 | 60 |  | 134172 | 137620.9673 | Shyamoli |  | CF Corrected |  | NHA | 137620.9673 | 169863.0669 | -32242.0996 | -18.9812 | OK
17 | Auxiliary transformer |  | 0.415 | T-2 |  | 1.05 | 672271 | 676258 | 3987 | 1 |  | 4186.35 | 4293.9625 | Satmasjid |  |  |  | Auxiliary transformer | 4293.9625 | 5219.996 | -926.0335 | -17.7401 | OK
|  |  | 10: Grand Total | 7978569.9144 | 7778616.18 | 7978569.9144 | 2.5706
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH |  |  |  | 2.5706
|  |  | 6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 681840.3498 | 681840.3498 | 0
|  |  | 6: Dhanmondi; 7: at 33 KV level; 9=8-7: 304879.4917 | 304879.4917 | 0
|  |  | 6: Satmasjid; 7: at 33 KV level; 9=8-7: 2485822.5391 | 2485822.5391 | 0
|  |  | 6: Shyamoli; 7: at 33 KV level; 9=8-7: 4506027.5339 | 4659896.6312 | -153869.0973
|  |  | 7: at 33 KV level |  | 0
|  |  | 6: Total =; 9=8-7: 7978569.9144; 10: 0 | 8132439.0118 | -153869.0973
33 KV SIDE of___ BANASREE 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 118449 | 120532 | 2083 | 2000 | 0 | 4166000 | 4172188.224
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 103053 | 104837 | 1784 | 2000 | 0 | 3568000 | 3573299.948
|  |  | 10: Total |  | 7734000 | 7745488.1719 | 0.14854
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import |  | 1 | 5435140 | 9581530 | 4146390 | 1 | 4146390
2 | Madertek Circuit-02 |  | 33 | Import |  | 1 | 5261020 | 8817460 | 3556440 | 1 | 3556440
3 | Ullon O/H |  | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
|  |  | 8: 0; 10: Total | 7702830 | 0 | 0
| BANASREE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| BANASREE 33 KV SIDE |  | 8: 0
1 | Transformer-01 |  | 33 | Export | 14 | 1 | 1472400 | 5620320 | 4147920 | 1 |  | 4147920
2 | Transformer-02 |  | 33 | Export | 74 | 1 | 2130960 | 5687520 | 3556560 | 1 |  | 3556560 |  |  | Meter Problem
|  |  | 10: Total |  | 7704480
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 4: 7745488.1719; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 7745488.1719
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 7745488.1719 | 33 KV TX HV SIDE |  | 7704480
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 41008.1719
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.5294%
| TOTAL IMPORT |  | 4: 7745488.1719
11 KV SIDE of___BANASREE 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 4147920 |  | 4169997.8841 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | 198 | 1 | 0 | 0 | 0 | 1 | 3556560 |  | 3575490.2878 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 7704480 |  | 7745488.1719 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | F292A | 11 |  | 141 | 1 | 3821920 | 5002480 | 1180560 | 1 |  | 1180560 | 1194834.4269 | Banosree |  |  |  | Angur Jora | 1194834.4269 | 1423037.4494 | -228203.0225 | -16.0363 | OK
2 | Block F-G Avenue | F299G | 11 |  | 68 | 1 | 6117160 | 6894840 | 777680 | 1 |  | 777680 | 787083.1107 | Banosree |  |  |  | Block F-G Avenue | 787083.1107 | 599512.8999 | 187570.2107 | 31.2871 | OK
3 | Banasree Main Road(Monpura) | F292P | 11 |  | 168 | 1 | 766400 | 1156280 | 389880 | 1 |  | 389880 | 394594.1302 | Banosree |  |  |  | Banasree Main Road(Monpura) | 394594.1302 | 496465.9196 | -101871.7894 | -20.5194 | OK
4 | Baitul Kuddus | F292Q | 11 |  | 62 | 1 | 7869640 | 9216840 | 1347200 | 1 |  | 1347200 | 1363489.3101 | Banosree |  |  |  | Baitul Kuddus | 1363489.3101 | 1686613.9505 | -323124.6404 | -19.1582 | OK
5 | Ideal | F214I | 11 |  |  | 1 | 1080480 | 1502200 | 421720 | 1 |  | 421720 | 426819.1151 | Banosree |  |  |  | Ideal | 426819.1151 | 548800.1649 | -121981.0498 | -22.2269 | OK
6 | Central Mosque | F292C | 11 |  | 46 | 1 | 7883600 | 9070960 | 1187360 | 1 |  | 1187360 | 1201716.6473 | Banosree |  |  |  | Central Mosque | 1201716.6473 | 1552150.2079 | -350433.5606 | -22.5773 | OK
7 | Larive | F299L | 11 |  | 47 | 1 | 3914200 | 4534040 | 619840 | 1 |  | 619840 | 627334.6303 | Banosree |  |  |  | Larive | 627334.6303 | 804309.6523 | -176975.0219 | -22.0033 | OK
8 | Bank Colony | A299K | 11 |  |  | 1 | 8610600 | 9186160 | 575560 | 1 |  | 575560 | 582519.2305 | Khilgaon |  |  |  | Bank Colony | 582519.2305 | 564812.5793 | 17706.6512 | 3.135 | OK
9 | Salambagh | A299G | 11 |  |  | 1 | 6829880 | 7514640 | 684760 | 1 |  | 684760 | 693039.5932 | Khilgaon |  |  |  | Salambagh | 693039.5932 | 454833.6424 | 238205.9509 | 52.3721 | FAULT
10 | Titas Road | A299T | 11 |  |  | 1 | 4913000 | 5381360 | 468360 | 1 |  | 468360 | 474023.0502 | Khilgaon |  |  |  | Titas Road | 474023.0502 | 281534.7278 | 192488.3224 | 68.3711 | FAULT
11 | AT-1 |  | 0.415 |  | 7734 | 1 | 3571.06 | 3605.57 | 34.51 | 1 |  | 34.51 | 34.9273 | Banosree |  |  |  | AT-1 | 34.9273 | 36.6867 | -1.7594 | -4.7958 | OK
12 | AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 7745488.1719 | 7652954.51 | 7745488.1719 | 1.2091
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 5995906.298
[6 empty] | Khilgaon | at 33 KV level |  | 1749581.874
[6 empty] | Total = |  |  | 7745488.1719 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 370267 | 373972 | 3705 | 2000 | 0 | 7410000 | 7421006.8986
ULLON 33 KV SIDE | bar: 4
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 7410000 | 7421006.8986
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import | HA-030701133-03 | 1 | 8926360 | 57017368 | 48091008 | 1 | 48091008
2 | Ullon O/H |  | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 48091008 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GORAN 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | HA-030800176-03 | 1 | 27106240 | 29660074 | 2553834 | 1 |  | 2553834
2 | Transformer-02 |  | 33 | Export | HA-030701133-03 | 1 | 94701270 | 97138822 | 2437552 | 1 |  | 2437552
3 | Transformer-03 |  | 33 | Export | DHK-57075 | 1 | 12413.92 | 12516.04 | 102.12 | 120000 |  | 2418614 |  |  | Problem
|  |  | 10: Total |  | 7410000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 4: 7421006.8986; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7421006.8986
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 7421006.8986 | 33 KV TX HV SIDE |  | 7410000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 11006.8986
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1483%
| TOTAL IMPORT |  | 4: 7421006.8986
11 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming |  | 11 | IMPORT |  | 1 | 67679970 | 70228669 | 2548699 | 1 | 2548699 |  | 2548694.157
| 33/11 kV Transfomer-2 Incoming |  | 11 |  |  | 1 | 2196020 | 4625634 | 2429614 | 1 | 2429614 |  | 2429609.3833
| 33/11 kV Transfomer-3 Incoming |  | 11 |  |  | 1 | 87118310 | 89561018 | 2442708 | 1 | 2442708 |  | 2442703.3584
|  |  | 7: 0; 8: 0; 10: Total | 7421021 |  | 7421006.8986
| GORAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Meradia | F214M | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estiimated by Grid | 1010556 | 1011378.211 | Banosree | 170 |  |  | Meradia | 1011378.211 | 2033879.5103 | -1022501.2993 | -50.2734 | CHECK
2 | Shipahibagh | A914S | 11 |  | HA-021001030-02 | 1 | 43252680 | 44110709 | 858029 | 1 |  | 858029 | 858727.1116 | Bashabo |  |  |  | Shipahibagh | 858727.1116 | 1201195.1008 | -342467.9892 | -28.5106 | OK
3 | Farazi Hospital | F214F | 11 |  | HA-030701081-03 | 1 | 52545470 | 53225584 | 680114 | 1 |  | 680114 | 680667.356 | Banosree |  |  |  | Farazi Hospital | 680667.356 | 834659.8902 | -153992.5342 | -18.4497 | OK
4 | West Bansree | F214W | 11 |  | New Meter | 1 | 99726960 | 100754861 | 1027901 | 1 |  | 1027901 | 1028737.3232 | Banosree |  |  |  | West Bansree | 1028737.3232 | 1344518.0725 | -315780.7492 | -23.4865 | OK
5 | Model School(Nearest) | F214D | 11 |  | HA-030701099-03 | 1 | 26588810 | 27983298 | 1394488 | 1 |  | 1394488 | 1395622.5866 | Banosree |  |  |  | Model School(Nearest) | 1395622.5866 | 1890153.6365 | -494531.0499 | -26.1635 | OK
6 | Bhuiyan Para | F214V | 11 |  | HA-021100508-02 | 1 | 64706638 | 64706638 | 0 | 1 | Estiimated by Grid | 1596000 | 1597298.5413 | Banosree |  |  |  | Bhuiyan Para | 1597298.5413 | 1593748.1926 | 3550.3487 | 0.22277 | OK
7 | Bonobithi (Ideal) School | F214B | 11 |  | HA-021100879-02 | 1 | 21242510 | 22088634 | 846124 | 1 |  | 846124 | 846812.4254 | Banosree |  |  |  | Bonobithi (Ideal) School | 846812.4254 | 1095885.5972 | -249073.1718 | -22.728 | OK
8 | AT-01 |  | 0.415 |  | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 |  | 0.415 |  | 3043146 | 1 | 5084.2 | 5106.4 | 22.2 | 80 |  | 1776 | 1777.445 | Banosree |  |  |  | AT-02 | 1777.445 | 0 | 1777.445 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 7421021 | 7414988 | 7421021 | 0.081362
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 6562293.8884
[6 empty] | Bashabo | at 33 KV level |  | 858727.1116
[6 empty] | Total = |  |  | 7421021 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 |  | 33 | 0 | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 8315280 | 8450667.1052
|  |  | 10: Total |  | 8315280 | 8450667.1052
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
2 | Shatmasjid-2 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
3 | Kallayanpur |  | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
|  |  | 10: Total | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 |  | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 |  | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 4: 8450667.1052; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALMATIA 33 KV NET IMPORT |  | 8450667.1052
| IMPORT-2 |  | 6: LALMATIA 33 KV NET IMPORT; 9=8-7: 8450667.1052 | LALMATIA 11 KV NET IMPORT |  | 8315280
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 135387.1052
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.602%
| TOTAL IMPORT |  | 4: 8450667.1052
11 KV SIDE of___LALMATIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | DHK000180 | 1 | 3046616 | 3079454 | 32838 | 90 | 2955420 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | DHK000177 | 1 | 3126003 | 3185557 | 59554 | 90 | 5359860 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 8315280 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 85 | 1033879.14 | 1043191.4697 | Dhanmondi | Estimated | 112 |  | Shankor O/H | 1043191.4697 | 1437106.4117 | -393914.942 | -27.4103 | OK
2 | Bangabobondhu museum | D207B | 11 | Export |  | 1 | 629342 | 630081 | 739 | 1 |  | 739 | 745.6563 | Dhanmondi |  | 68 |  | Bangabobondhu museum | 745.6563 | 0 | 745.6563 | #DIV/0! | #DIV/0!
3 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 87980510 | 89026265 | 1045755 | 1 |  | 1045755 | 1055174.2976 | Dhanmondi |  | 44 |  | Road No-13/A | 1055174.2976 | 1526974.093 | -471799.7954 | -30.8977 | OK
4 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 8383244 | 8967300 | 584056 | 1 |  | 584056 | 589316.6942 | Dhanmondi |  | 14.6667 |  | Jaforabad | 589316.6942 | 788052.4828 | -198735.7886 | -25.2186 | OK
5 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 82.6667 |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26317.7 | 26433.6 | 115.9 | 3333.33 |  | 386332.947 | 389812.7152 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 389812.7152 | 453765.7341 | -63953.0189 | -14.0938 | OK
1 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71326.8 | 71601.8 | 275 | 3333.33 |  | 916665.75 | 924922.3182 | Dhanmondi |  |  |  | Road No -15 | 924922.3182 | 1066926.0087 | -142003.6905 | -13.3096 | OK
2 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79310 | 79491.8 | 181.8 | 3333.33 |  | 605999.394 | 611457.7362 | Dhanmondi |  |  |  | Road No-27 South | 611457.7362 | 1026568.6676 | -415110.9314 | -40.4367 | CHECK
| Road 25 | D207C | 11 | Export |  | 1 | 71667.3 | 71863.3 | 196 | 3333.3 |  | 653326.8 | 659211.4284 | Dhanmondi |  |  |  | Road 25 | 659211.4284 | 941775.8615 | -282564.4331 | -30.0034 | OK
3 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38312.4 | 38377.8 | 65.4 | 3333.33 |  | 217999.782 | 219963.344 | Dhanmondi |  |  |  | Ibne Sina | 219963.344 | 311328.0598 | -91364.7157 | -29.3468 | OK
4 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 64469326 | 65735404 | 1266078 | 1 |  | 1266078 | 1277481.7853 | Dhanmondi |  |  |  | Road No-31 (PARI) | 1277481.7853 | 1297830.3074 | -20348.5221 | -1.5679 | OK
5 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | 130 | 1530219.6 | 1544002.5547 | Dhanmondi | Estimated |  |  | Satmoszid Road West | 1544002.5547 | 1652672.3734 | -108669.8187 | -6.5754 | OK
|  |  | 10: Grand Total | 8315280 | 8241051.413 | 8315280 | 0.90072
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Dhanmondi | at 33 KV level |  | 8315280
[6 empty] | Total = |  |  | 8315280 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) |  | 33 | 0 | BD001918 | 1 | 2193.69 | 2210.47 | 16.78 | 240000 | 0 | 4027200 | 4033095.9351
23 | Green Road Circuit-1 |  | 33 | 0 | BD001865 | 1 | 1526.05 | 1545.91 | 19.86 | 240000 | 0 | 4766400 | 4773378.1449
|  |  | 10: Total | 0 | 8793600 | 8806474.08
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory |  | 3: 33; 4: EXPORT |  | 0
| Green Road Dormatory |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0
| 33/11 KV Transformer No.2. |  | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 4: 8806474.08; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | Green Road 33 KV NET IMPORT |  | 8806474.08
| IMPORT-2 |  | 6: Green Road 33 KV NET IMPORT; 9=8-7: 8806474.08 | Green Road 11 KV NET IMPORT |  | 8806474.08
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 8806474.08 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 8806474.08
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | 150
| Green Road 11 KV X-F SIDE | [14 empty] | 22
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 00138 | 1 | 3328979 | 3381740 | 52761 | 100 | 5276100 |  |  |  |  | 128
2 | Transfomer-2 Incoming |  | 11 | Import | HA-021101496 | 1 | 6214.5824 | 6664.7868 | 450.2044 | 10000 | 4027200 |  |  |  |  | 42.6667
|  |  | 7: 0; 8: 0; 10: Total | 9303300 |  | 8806474.08 |  |  | 64.6667
| Green Road 11 KV SIDE |  | 7: 0; 8: 0
1 | Lab aid/local RMU | C302L | 11 |  | 3C65883 | 1 | 76794 | 80402 | 3608 | 300 |  | 1082400 | 1091796.2723 | Paribag |  |  |  | Lab aid/local RMU | 1091796.2723 | 1099246.4449 | -7450.1725 | -0.67775 | OK
2 | Green View | C302V | 11 |  | DHK000151 | 1 | 68593.9 | 68803.9 | 210 | 3333.33 |  | 699999.3 | 706075.9667 | Paribag |  |  |  | Green View | 706075.9667 | 952604.6387 | -246528.6719 | -25.8794 | OK
3 | Central Road | C302C | 11 |  | 65943 | 1 | 41167 | 44228 | 3061 | 300 |  | 918300 | 926271.7266 | Paribag |  |  |  | Central Road | 926271.7266 | 1084585.7532 | -158314.0266 | -14.5967 | OK
4 | New Market | D802N | 11 |  | DHK000194 | 1 | 48019.6 | 48318.5 | 298.9 | 3333.33 |  | 996332.337 | 1004981.4593 | Jigatola |  |  |  | New Market | 1004981.4593 | 1091745.3233 | -86763.864 | -7.9473 | OK
5 | DPH Feeder |  | 11 |  | HA-021100459 | 1 | 42140.3 | 42220.2 | 79.9 | 1 | 20 | 243265.68 | 245377.4599 | Paribag | Estimated |  |  | DPH Feeder | 245377.4599 | 299600.3974 | -54222.9375 | -18.0984 | OK
6 | Dhanmondi Rd 4(md Banglo | D802F | 11 |  | 6604464 | 1 | 4589.51 | 4602.53 | 13.02 | 60000 |  | 781200 | 787981.5668 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 787981.5668 | 976157.721 | -188176.1541 | -19.2772 | OK
1 | Green Road East | C302X | 11 |  | HA-021101050 | 1 | 777480 | 1597306 | 819826 | 1 |  | 819826 | 826942.8777 | Paribag |  |  |  | Green Road East | 826942.8777 | 1043123.4845 | -216180.6069 | -20.7244 | OK
2 | North Road | C302Z | 11 |  | HA-021100884 | 1 | 86548201 | 87580680 | 1032479 | 1 |  | 1032479 | 1041441.9101 | Paribag |  |  |  | North Road | 1041441.9101 | 1315225.9221 | -273784.012 | -20.8165 | OK
3 | Green road SS | C302W | 11 |  | DHK00135 | 1 | 23172245 | 23910038 | 737793 | 1 |  | 737793 | 744197.7524 | Paribag |  |  |  | Green road SS | 744197.7524 | 927434.3375 | -183236.5851 | -19.7574 | OK
4 | Plane Moszid | C302A | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 729797.04 | 736132.3797 | Paribag | Estimated |  |  | Plane Moszid | 736132.3797 | 719040.9537 | 17091.426 | 2.377 | OK
5 | Malancha | C302H | 11 |  | HA-021100953 | 1 | 39024399 | 39708690 | 684291 | 1 |  | 684291 | 690231.3036 | Paribag |  |  |  | Malancha | 690231.3036 | 1262646.9803 | -572415.6768 | -45.3346 | CHECK
| AT -1 |  | 7: 22891; 8: 22891; 9=8-7: 0; 10: 1 |  | 5000 | 5043.4048 | Paribag |  |  |  | AT -1 | 5043.4048 | 5090.5179 | -47.1131 | -0.92551 | OK
|  |  | 10: Grand Total | 8806474.08 | 8730683.357 | 8806474.08 | 0.8681
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 7013511.0538
[6 empty] | Jigatola | at 33 KV level |  | 1792963.0261
[6 empty] | Total = |  |  | 8806474.08 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory |  | 33 | 0 | 76026305 | 1 | 8111.66 | 8115.73 | 4.07 | 180000 | Reading From G. Dormitory Side | 1196970 | 1200855.0302
|  |  | 10: Total | 0 | 1196970 | 1200855.0302
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 |  | 33 | 0 | 0 | 1 | 54 | 66.69 | 12.69 | 360000 | 0 | 4568400 | 4564994.5583
9 | Green Road -2 |  | 33 | 0 | 0 | 1 | 88.88 | 97.49 | 8.61 | 360000 | 0 | 3099600 | 3097289.4521
|  |  | 10: Total | 0 | 7668000 | 7662284.0104
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [10 empty] | 8864970 | 8863139.0407
1 | Mogbazar Grid |  | 33 | Import | BD 017064 | 1 | 57264.79 | 58461.76 | 1196.97 | 1000 | 1196970
2 | Green Road SS |  | 33 | Import | BD 017070 | 1 | 32923.13 | 32923.13 | 0 | 1000 | 0
3 | Jigatola Ckt-1 |  | 33 | Import |  | 1 | 19368 | 23924.29 | 4556.29 | 1000 | 4556290
NEW | Jigatola Ckt-2 |  | 33 |  |  | 1 | 31940.13 | 35036.13 | 3096 | 1000 | 3096000 |  |  |  | NEW FOUND
|  |  | 7: 0; 8: 0; 10: Total | 8849260 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | BD 017065 | 1 | 8288.53 | 64577.15 | 56288.62 | 888.89 |  | 50034391.4318
2 | Transformer-02 |  | 33 | Export | BD 017069 | 1 | 5577.05 | 24554.86 | 18977.81 | 888.89 |  | 16869185.5309
|  |  | 10: Total |  | 66903576.9627 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 8863139.0407; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 8863139.0407
|  |  | 6: GREEN ROAD DORMITORY 33 KV NET IMPORT; 9=8-7: 8863139.0407 | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 8863139.0407
|  |  | 6: TOTAL EXPORT; 9=8-7: 8863139.0407 | LOSS UNITS=> |  | 0
|  |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 8863139.0407
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD 014050 | 1 | 124.44 | 22385.46 | 22261.02 | 1000 | 22261020
2 | Transformer-02 Incoming |  | 11 | Import | BD 014059 | 1 | 95155.39 | 98238.03 | 3082.64 | 1000 | 3082640
|  |  | 7: 0; 8: 0; 10: Total | 25343660 |  | 8863139.0407
| GREEN ROAD DORMITORY 11 KV SIDE |  | 7: 0; 8: 0
1 | North Dhanmondi | C31002 | 11 |  | BD 014039 | 1 | 23783.66 | 24137.31 | 353.65 | 2000 |  | 707300 | 711975.1234 | Paribag |  |  |  | North Dhanmondi | 711975.1234 | 970901.1912 | -258926.0678 | -26.6686 | OK
2 | Lake circus | C31004 | 11 |  | BD 014047 | 1 | 39176.51 | 39691.93 | 515.42 | 2000 |  | 1030840 | 1037653.6636 | Paribag |  |  |  | Lake circus | 1037653.6636 | 1359915.9406 | -322262.277 | -23.6972 | OK
3 | Bashir Uddin | C31003 | 11 |  | BD 014037 | 1 | 15830.71 | 16042.42 | 211.71 | 2000 |  | 423420 | 426218.7286 | Paribag |  |  |  | Bashir Uddin | 426218.7286 | 519195.2113 | -92976.4826 | -17.9078 | OK
4 | Raza Bazar | D5100R | 11 |  | BD 013939 | 1 | 23815.99 | 24260.81 | 444.82 | 2000 |  | 889640 | 895520.3575 | Shere b.nagar |  |  |  | Raza Bazar | 895520.3575 | 1203544.7399 | -308024.3825 | -25.5931 | OK
5 | Rasel Squar | D5100RS | 11 |  | BD 013970 | 1 | 35887.97 | 36460.54 | 572.57 | 2000 |  | 1145140 | 1152709.1657 | Shere b.nagar |  |  |  | Rasel Squar | 1152709.1657 | 1357853.9899 | -205144.8242 | -15.108 | OK
6 | Bow Bazar | D5100O | 11 |  | BD 013967 | 1 | 26716.98 | 27345.66 | 628.68 | 2000 |  | 1257360 | 1265670.9193 | Shere b.nagar |  |  |  | Bow Bazar | 1265670.9193 | 1309854.1577 | -44183.2384 | -3.3731 | OK
7 | BRB Hospital | D5100S | 11 |  | BD 014003 | 1 | 14382.67 | 14617.11 | 234.44 | 2000 |  | 468880 | 471979.2109 | Shere b.nagar |  |  |  | BRB Hospital | 471979.2109 | 608037.5277 | -136058.3168 | -22.3766 | OK
8 | Green Road North | C31008 | 11 |  | BD 013969 | 1 | 17616.03 | 17935.33 | 319.3 | 2000 |  | 638600 | 642821.029 | Paribag |  |  |  | Green Road North | 642821.029 | 876606.6014 | -233785.5724 | -26.6694 | OK
1 | Water Bhaban | D5100PB | 11 |  | BD 014004 | 1 | 5723.95 | 5811.58 | 87.63 | 2000 |  | 175260 | 176418.4365 | Shere b.nagar |  |  |  | Water Bhaban | 176418.4365 | 266368.3378 | -89949.9013 | -33.769 | OK
2 | Alamin Road | C31007 | 11 |  | BD 014006 | 1 | 19724.04 | 19878.23 | 154.19 | 2000 |  | 308380 | 310418.3353 | Paribag |  |  |  | Alamin Road | 310418.3353 | 564141.7704 | -253723.4351 | -44.9751 | CHECK
3 | Katal Bagan | C3100K | 11 |  |  | 1 | 11681.91 | 12283.55 | 601.64 | 2000 |  | 1203280 | 1211233.4604 | Paribag |  |  |  | Katal Bagan | 1211233.4604 | 1478597.0623 | -267363.6019 | -18.0822 | OK
4 | Eastern Pantho chaya | C310010 | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan |  | 11 |  | BD 014005 | 1 | 6367.44 | 6453.74 | 86.3 | 2000 |  | 172600 | 173740.8544 | Paribag |  |  |  | Kalabagan | 173740.8544 | 284172.4888 | -110431.6344 | -38.8608 | OK
6 | Univer Hospital | C310012 | 11 |  | BD 013963 | 1 | 1392.56 | 1482.8 | 90.24 | 2000 |  | 180480 | 181672.9397 | Paribag |  |  |  | Univer Hospital | 181672.9397 | 220053.7538 | -38380.814 | -17.4416 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 |  | BD 013971 | 1 | 10701.31 | 10803.19 | 101.88 | 2000 |  | 203760 | 205106.8163 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 205106.8163 | 341233.008 | -136126.1917 | -39.8924 | OK
|  |  | 10: Grand Total | 8863139.0407 | 8804940 | 8863139.0407 | 0.66098
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 4900840.9508
[6 empty] | Shere b.nagar | at 33 KV level |  | 3962298.0898
[6 empty] | Total = |  |  | 8863139.0407 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1690.629 | 1706.6468 | 16.0178 | 240000 | 0 | 3844272 | 3844272
2 | Taltala-2 |  | 33 |  | BD001837 | 1 | 2639.7785 | 2661.1228 | 21.3443 | 240000 | 0 | 5122632 | 5122632
|  |  | 10: Total | 0 | 8966904 | 8966904
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming |  | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 |  | 0
| 33 KV Ullon-ckt-2 incoming |  | 3: 33; 6: 1; 9=8-7: 0; 10: 1000 |  | 0
|  |  | 10: Total |  | 0 | 8966904
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) |  | 3: 33; 4: EXPORT |  | 0
| 33 KV Khilgaon Feeder(Import) |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
|  |  | 10: Total |  | 0 | 8966904 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 4: 8966904; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TALTOLA 33 KV NET IMPORT |  | 8966904
| IMPORT-2 |  | 6: TALTOLA 33 KV NET IMPORT; 9=8-7: 8966904 | TALTOLA 11 KV NET IMPORT |  | 8966904
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 8966904 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 8966904
11 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming |  | 11 | Import | 06604431 | 1 | 8728.02 | 8760.95 | 32.93 | 160000 | 5268800
2 | Transformer-02 Incoming |  | 11 | Import | 06604341 | 1 | 9450.92 | 9473.04 | 22.12 | 160000 | 3539200
3 | Transformer-03 Incoming |  | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 8808000 |  | 8966904
| TALTOLA 11 KV SIDE |  | 7: 0; 8: 0
1 | Matir Masjid | A229S | 11 |  | DHK00170 | 1 | 31256.8 | 32697.5 | 1440.7 | 888.8889 |  | 1280622.2222 | 1284398.1103 | Khilgaon |  |  |  | Matir Masjid | 1284398.1103 | 1604310.6045 | -319912.4942 | -19.9408 | OK
2 | Hajipara | A229P | 11 |  | DHK-00108 | 1 | 7020.3 | 7595.3 | 575 | 2222.2222 |  | 1277777.7778 | 1281545.2791 | Khilgaon |  |  |  | Hajipara | 1281545.2791 | 1799894.6638 | -518349.3847 | -28.7989 | OK
3 | Nearest Feeder | A929N | 11 |  | DHK-00106 | 1 | 92041.4 | 92278.7 | 237.3 | 2222.222 |  | 527333.2806 | 528888.1119 | Bashabo |  |  |  | Nearest Feeder | 528888.1119 | 952079.0172 | -423190.9054 | -44.4491 | CHECK
4 | Reazbagh | A229C | 11 |  | DHK-00109 | 1 | 98929.8 | 99412.2 | 482.4 | 2222.222 |  | 1071999.8928 | 1075160.6623 | Khilgaon |  |  |  | Reazbagh | 1075160.6623 | 1369807.3375 | -294646.6752 | -21.5101 | OK
5 | Chowdhury Para | A229F | 11 |  | DHK-00107 | 1 | 53518 | 53735.7 | 217.7 | 2222.222 |  | 483777.7294 | 485204.138 | Khilgaon |  |  |  | Chowdhury Para | 485204.138 | 558618.9372 | -73414.7992 | -13.1422 | OK
6 | Model Colleg | A229D | 11 |  | 9122392 | 1 | 2601.93 | 2615.34 | 13.41 | 40000 |  | 536400 | 537981.5643 | Khilgaon |  |  |  | Model Colleg | 537981.5643 | 695285.1522 | -157303.5879 | -22.6243 | OK
1 | East Rampura | A229B | 11 |  | DHK-00181 | 1 | 70 | 290.4 | 220.4 | 2222.222 |  | 489777.7288 | 491221.8283 | Khilgaon |  |  |  | East Rampura | 491221.8283 | 1083981.397 | -592759.5687 | -54.6836 | CHECK
2 | Adarshabagh | A929A | 11 |  | DHK-00090 | 1 | 53089.4 | 53626.6 | 537.2 | 2222.222 |  | 1193777.6584 | 1197297.4871 | Bashabo |  |  |  | Adarshabagh | 1197297.4871 | 1572716.7906 | -375419.3035 | -23.8708 | OK
3 | Khailgaon Govt Colony | A229K | 11 |  | DHK00167 | 1 | 77744.9 | 78176 | 431.1 | 2222.222 |  | 957999.9042 | 960824.5471 | Khilgaon |  |  |  | Khailgaon Govt Colony | 960824.5471 | 1228467.3088 | -267642.7617 | -21.7867 | OK
4 | TV Road | A214T | 11 |  | 6604434 | 1 | 5174.98 | 5190.73 | 15.75 | 40000 |  | 630000 | 631857.5419 | Khilgaon |  |  |  | TV Road | 631857.5419 | 1115125.7501 | -483268.2082 | -43.3376 | CHECK
5 | Post Office |  | 11 |  | 06604476 | 1 | 6654.54 | 6666.69 | 12.15 | 40000 |  | 486000 | 487432.9609 | Bashabo |  |  |  | Post Office | 487432.9609 | 755551.2881 | -268118.3272 | -35.4864 | OK
1 | Navana | A929V | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | A929P | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 |  | 0.415 |  | 9187958 | 1 | 790.37 | 853.83 | 63.46 | 80 |  | 5076.8 | 5091.7688 | Bashabo |  |  |  | AT-01 | 5091.7688 | 215.1784 | 4876.5904 | 2266.3009 | FAULT
3 | AT-02 |  | 0.415 |  | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 8966904 | 8940542.9942 | 8966904 | 0.29485
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Khilgaon | at 33 KV level |  | 6748193.6713
[6 empty] | Bashabo | at 33 KV level |  | 2218710.3287
[6 empty] | Total = |  |  | 8966904 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 |  | 33 | Import | 35786569 | 1 | 1999.239 | 2013.229 | 13.99 | 180000 | 0 | 2518200 | 12354.54
2 | Sher-e-Banglanagar Ckt-02 |  | 33 | Import | 35786575 | 1 | 720.775 | 730.562 | 9.787 | 180000 | 0 | 1761660 | 8642.88
|  |  | 10: Total | 0 | 4279860 | 20997.42
|  |  | 10: Net Total | 4300857.42
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | DHK 66505 | 1 |  | 0 | 0 | 540 | 0
2 | Agargaon Ckt-02 |  | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
|  |  | 8: 0; 10: Total | 0 | 0 | 0
| SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| SHER-E-BANGLANAGAR 33 KV SIDE |  | 8: 0
3 | Transformer-01 |  | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 |  | 33 | Export | DHK 66500 | 1 | 787774 | 797284 | 9510 | 180 |  | 1711800
|  |  | 10: Total |  | 1711800 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 4: 4300857.42; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 4300857.42
| IMPORT-2 |  | 6: SHER-E-BANGLANAGAR 33 KV NET IMPORT; 9=8-7: 4300857.42 | 33 KV TX HV SIDE |  | 4300857.42
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 4300857.42
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 66503 | 1 | 2273078 | 2286674 | 13596 | 180 | 2447280 |  | 2527859.9984
2 | Transfomer-2 Incoming |  | 11 | Import | DHK 66495 | 1 | 770405 | 779941 | 9536 | 180 | 1716480 |  | 1772997.4216
|  |  | 7: 0; 8: 0; 10: Total | 4163760 |  | 4300857.42
| SHER-E-BANGLANAGAR 11 KV SIDE |  | 7: 0; 8: 0
1 | Sher-e-Banglanagar Local |  | 11 |  | DHK 66503 | 1.45 | 85742 | 86523 | 781 | 60 | 11 kv bus-1 R Phase PT missing | 67947 | 69188.3162 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 69188.3162 | 109846.5171 | -40658.2009 | -37.0136 | OK
2 | Mirpur Road East | D550F | 11 |  | DHK 60961 | 1.45 | 854603 | 858191 | 3588 | 60 |  | 312156 | 317858.7434 | Shere b.nagar |  |  |  | Mirpur Road East | 317858.7434 | 395819.5598 | -77960.8164 | -19.696 | OK
3 | Gonobhaban school | D550E | 11 |  | DHK 66492 | 1.45 | 536080 | 537174 | 1094 | 60 |  | 95178 | 96916.7963 | Shere b.nagar |  |  |  | Gonobhaban school | 96916.7963 | 122017.2321 | -25100.4358 | -20.5712 | OK
4 | Babor Road | D450B | 11 |  | DHK 66489 | 1.3 | 798679 | 804063 | 5384 | 60 |  | 419952 | 427624.0566 | Shyamoli |  |  |  | Babor Road | 427624.0566 | 570860.7987 | -143236.7421 | -25.0914 | OK
5 | College Gate | D450K | 11 |  | DHK 66487 | 1.4 | 2718507 | 2732457 | 13950 | 60 |  | 1171800 | 1193207.4845 | Shyamoli |  |  |  | College Gate | 1193207.4845 | 1044976.0411 | 148231.4433 | 14.1852 | OK
6 | Parade ground |  | 11 |  | DHK 66490 | 1.45 | 938469 | 938503 | 34 | 60 |  | 2958 | 3012.0394 | Satmasjid |  |  |  | Parade ground | 3012.0394 | 3333.3805 | -321.3412 | -9.6401 | OK
7 | Hospital RMU | D550H | 11 |  | DHK 66491 | 1.45 | 927197 | 930854 | 3657 | 60 |  | 318159 | 323971.4115 | Shere b.nagar |  |  |  | Hospital RMU | 323971.4115 | 434269.7168 | -110298.3052 | -25.3986 | OK
1 | Shamoly Square |  | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | D550D | 11 |  | DHK 60964 | 1 | 198714.3 | 200013.1 | 1298.8 | 60 |  | 77928 | 79351.658 | Shere b.nagar |  |  |  | Gonobhaban RMU | 79351.658 | 75406.8335 | 3944.8245 | 5.2314 | OK
3 | Krishi University | D550V | 11 |  | DHK 60963 | 1 | 386593 | 392263 | 5670 | 60 |  | 340200 | 346415.0761 | Shere b.nagar |  |  |  | Krishi University | 346415.0761 | 461555.7137 | -115140.6376 | -24.9462 | OK
4 | NEC | D550X | 11 |  | DHK 86073 | 1 | 51.31 | 53.71 | 2.4 | 60000 |  | 144000 | 146630.7201 | Shere b.nagar |  |  |  | NEC | 146630.7201 | 204096.883 | -57466.163 | -28.1563 | OK
5 | Novo Theater/Army Musium | D550A | 11 |  | DHK 86074 | 1 | 432.4 | 444.74 | 12.34 | 60000 |  | 740400 | 753926.2856 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 753926.2856 | 879978.5491 | -126052.2635 | -14.3245 | OK
6 | Netor |  | 11 |  | DHK 60962 | 1 | 150829.4 | 155777.3 | 4947.9 | 60 |  | 296874 | 302297.5582 | Shere b.nagar |  |  |  | Netor | 302297.5582 | 451889.8792 | -149592.3209 | -33.1037 | OK
7 | BICC | D550VV | 11 |  |  | 1 | 51.31 | 53.71 | 2.4 | 60000 |  | 144000 | 146630.7201 | Shere b.nagar |  |  |  | BICC | 146630.7201 | 204096.883 | -57466.163 | -28.1563 | OK
8 | Auxiliary |  | 0.415 |  |  | 1 | 5439.49 | 5470.11 | 30.62 | 60 |  | 1837.2 | 1870.7636 | Shere b.nagar |  |  |  | Auxiliary | 1870.7636 | 2593.3022 | -722.5386 | -27.8617 | OK
|  |  | 10: Grand Total | 4208901.6297 | 4133389.2 | 4208901.6297 | 1.8269
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH |  |  |  | 1.8269
[6 empty] | Shere b.nagar | at 33 KV level |  | 2140241.5407 | Including 41% of Novo Theatre
[6 empty] | Shyamoli | at 33 KV level |  | 1620831.5411
[6 empty] | Satmasjid | at 33 KV level |  | 3012.0394
[6 empty] | Tejgaon | at 33 KV level |  | 444816.5085 | 59% of Novo Theatre
[6 empty] | Total = |  |  | 4208901.6297 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 5678656 | 5694303.573
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 |  | ABB03918 | 1 | 314865 | 317505 | 2640 | 2000 | 0 | 5280000 | 5294549.0739
|  |  | 10: Total | 0 | 10958656 | 10988852.6469
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 |  | 33 | Import | 38 | 1 | 325243072 | 330921728 | 5678656 | 1 | 5678656
2 | Maniknagor Incoming-02 |  | 33 | Import | 15 | 1 | 239893376 | 245157568 | 5264192 | 1 | 5264192
|  |  | 7: 0; 8: 0; 10: Total | 10942848 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | 16 | 1 | 313843456 | 319519680 | 5676224 | 1 |  | 5676224
4 | Transformer-02 |  | 33 | Export | 196 | 1 | 251151120 | 256416000 | 5264880 | 1 |  | 5264880
|  |  | 10: Total |  | 10941104 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 4: 10988852.6469; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10942848
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 10942848 | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 10941104
[11 empty] | LOSS UNITS=> |  | 1744
[11 empty] | LOSS % IN => |  | 0.01594%
| TOTAL IMPORT |  | 4: 10988852.6469
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | 192 | 1 | 311617152 | 317263168 | 5646016 | 1 | 5646016 |  | 5676634.8752
2 | Transformer-02 Incoming |  | 11 | Import | 118 | 1 | 249494320 | 254732128 | 5237808 | 1 | 5237808 |  | 5266213.1248
|  |  | 7: 0; 8: 0; 10: Total | 10883824 |  | 10942848
| MUGDAPARA HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
1 | City Corporation | A997Y | 11 |  | 93 | 1 | 44783932 | 45377608 | 593676 | 1 |  | 593676 | 599738.4197 | Bashabo |  |  |  | City Corporation | 599738.4197 | 776082.8806 | -176344.4609 | -22.7224 | OK
2 | Bot tola | B297L | 11 |  |  | 1 | 62504888 | 63949164 | 1444276 | 1 |  | 1444276 | 1459024.4609 | Maniknagar |  |  |  | Bot tola | 1459024.4609 | 1806337.3901 | -347312.9293 | -19.2275 | OK
3 | Jhilpar | B997J | 11 |  | 145 | 1 | 38598064 | 39421184 | 823120 | 1 |  | 823120 | 831525.4247 | Mugdapara |  |  |  | Jhilpar | 831525.4247 | 819817.0349 | 11708.3898 | 1.4282 | OK
4 | Central Bashaboo | A997C | 11 |  | 128 | 1 | 43766652 | 44810732 | 1044080 | 1 |  | 1044080 | 1054741.7939 | Bashabo |  |  |  | Central Bashaboo | 1054741.7939 | 1340049.7308 | -285307.9369 | -21.2908 | OK
5 | Kadamtala | B997L | 11 |  | 8 | 1.5 | 20429350 | 20678950 | 249600 | 1 |  | 374400 | 378223.2469 | Mugdapara |  |  |  | Kadamtala | 378223.2469 | 607566.4408 | -229343.1939 | -37.7478 | OK
6 | Ansar VDP | A297A | 11 |  | 119 | 1 | 21940426 | 22442506 | 502080 | 1 |  | 502080 | 507207.0721 | Khilgaon |  |  |  | Ansar VDP | 507207.0721 | 657824.4358 | -150617.3637 | -22.8963 | OK
7 | Mugda Hospital Express-01 | B997H | 11 |  |  | 1 | 7018583 | 7189702 | 171119 | 1 |  | 171119 | 172866.4097 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 172866.4097 | 206011.8286 | -33145.4189 | -16.0891 | OK
8 | Boro Masjid | B997Z | 11 |  | 7 | 1.22 | 52337832 | 52934072 | 596240 | 1 |  | 727412.8 | 734840.8949 | Mugdapara |  |  |  | Boro Masjid | 734840.8949 | 1191583.9793 | -456743.0844 | -38.3308 | OK
1 | Anandodhara | B297B | 11 |  | 120 | 1 | 50564636 | 51256316 | 691680 | 1 |  | 691680 | 698743.2036 | Maniknagar |  |  |  | Anandodhara | 698743.2036 | 685213.6028 | 13529.6008 | 1.9745 | OK
2 | Culvert | A997L | 11 |  | 117 | 1 | 45451008 | 46405368 | 954360 | 1 |  | 954360 | 964105.6034 | Bashabo |  |  |  | Culvert | 964105.6034 | 1368637.0118 | -404531.4084 | -29.5572 | OK
3 | Mugda Hospital Express-02 |  | 11 |  | 97 | 1 | 4870948 | 4870948 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 25317.8849 | -25317.8849 | -100 | CHECK
4 | Jhor Pukur | A997J | 11 |  | 98 | 1 | 29587808 | 29972006 | 384198 | 1 |  | 384198 | 388121.3008 | Bashabo |  | 145 |  | Jhor Pukur | 388121.3008 | 230851.2653 | 157270.0355 | 68.1261 | FAULT
5 | T&T | B997T | 11 |  | 99 | 1 | 25731818 | 26086056 | 354238 | 1 |  | 354238 | 357855.3593 | Mugdapara |  | 70 |  | T&T | 357855.3593 | 590205.7479 | -232350.3885 | -39.3677 | OK
6 | Haider Ali | B297H | 11 |  | 9 | 1 | 76603816 | 78155048 | 1551232 | 1 |  | 1551232 | 1567072.6596 | Maniknagar |  | 95 |  | Haider Ali | 1567072.6596 | 1855860.7678 | -288788.1082 | -15.5609 | OK
| 11kv Tilpapara | A929T | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 1216328.4 | 1228749.1366 | Bashabo | 100 |  |  | 11kv Tilpapara | 1228749.1366 | 1642601.2461 | -413852.1094 | -25.1949
7 | AT-01 |  | 11 |  |  | 1 | 3262 | 3294.68 | 32.68 | 1 |  | 32.68 | 33.0137 | Mugdapara |  |  |  | AT-01 | 33.0137 | 54.7524 | -21.7387 | -39.7036 | OK
8 | AT-02 |  | 11 |  |  | 1 | 17.34 | 17.34 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 10942848 | 10832232.88 | 10942848 | 1.0212
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bashabo | at 33 KV level |  | 4235456.2545
[6 empty] | Maniknagar | at 33 KV level |  | 3724840.3241
[6 empty] | Mugdapara | at 33 KV level |  | 2475344.3493
[6 empty] | Khilgaon | at 33 KV level |  | 507207.0721
[6 empty] | Total = |  |  | 10942848 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3331 | 79.3331 | 0 | 240000 | From Downstream | 2272050 | 2272050
MANKNAGAR 33 KV SIDE | bar: 4
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 280390 | 281573 | 1183 | 2000 | 0 | 2366000 | 2372519.5282
|  |  | 10: Total | 0 | 4638050 | 4644569.5282
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming |  | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming |  | 33 |  |  | 1 | 79378 | 87793 | 8415 | 270 |  | 2272050
| 33 kV Maniknagor Incoming |  | 33 |  |  | 1.08 | 7578 | 128129 | 120551 | 180 |  | 23435114.4
|  |  | 7: 0; 8: 0; 10: Total |  | 25707164.4
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KHILGOAN 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer -01 |  | 33 | Export | DHK60982 | 1 | 840895 | 853458 | 12563 | 180 |  | 2261340
4 | Transformer -02 |  | 33 | Export | DHK60947 | 1 | 865457 | 878496 | 13039 | 180 |  | 2347020
|  |  | 10: Total |  | 4608360 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 4: 4644569.5282; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4644569.5282
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 4644569.5282 | 33 KV TX HV SIDE |  | 4608360
[11 empty] | LOSS UNITS=> |  | 36209.5282
[11 empty] | LOSS % IN => |  | 0.7796%
| TOTAL IMPORT |  | 4: 4644569.5282
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | DHK60927 | 1 | 840290 | 852432 | 12142 | 180 | 2185560 |  | 2245892.601
2 | Transformer-02 Incoming |  | 11 | Import | DHK60928 | 1 | 23690 | 36658 | 12968 | 180 | 2334240 |  | 2398676.9272
|  |  | 7: 0; 8: 0; 10: Total | 4519800 |  | 4644569.5282
| KHILGOAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Shantinagar s/s-1 |  | 11 |  | DHK60932 | 1 | 430321 | 457519 | 27198 | 60 |  | 1631880 | 1639830.5714 | Rajarbag |  |  |  | Shantinagar s/s-1 | 1639830.5714 | 1995495.3946 | -355664.8232 | -17.8234 | OK
2 | Gulbagh | D606G | 11 |  | DHK60934 | 1 | 189715 | 200689 | 10974 | 60 |  | 658440 | 661647.9407 | Rajarbag |  |  |  | Gulbagh | 661647.9407 | 827221.5772 | -165573.6365 | -20.0156 | OK
3 | Rampura BTV | A206H | 11 |  | DHK60933 | 1 | 14076 | 14081 | 5 | 60 |  | 300 | 301.4616 | Khilgaon |  |  |  | Rampura BTV | 301.4616 | 180.4191 | 121.0425 | 67.0896 | FAULT
4 | West Shantibag | D606W | 11 |  | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 547347.78 | 550014.4758 | Rajarbag | 45 |  |  | West Shantibag | 550014.4758 | 707899.6007 | -157885.1248 | -22.3033 | OK
1 | East Malibagh | D606E | 11 |  | DHK60929 | 1 | 665295 | 678393 | 13098 | 60 |  | 785880 | 789708.8324 | Rajarbag |  |  |  | East Malibagh | 789708.8324 | 996093.8555 | -206385.0231 | -20.7194 | OK
2 | Police Line | D606S | 11 |  | DHK60930 | 1 | 601907 | 606946 | 5039 | 60 |  | 302340 | 303813.0101 | Rajarbag |  |  |  | Police Line | 303813.0101 | 464398.7655 | -160585.7553 | -34.5793 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 |  | DHK61017 | 1 | 201786 | 203304 | 1518 | 60 |  | 91080 | 91523.7447 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 91523.7447 | 111138.1661 | -19614.4214 | -17.6487 | OK
4 | Benjir Bagan | D662R | 11 |  | DHK60985 | 1 | 175954 | 177912 | 1958 | 60 |  | 117480 | 118052.3663 | Rajarbag |  |  |  | Benjir Bagan | 118052.3663 | 135073.7668 | -17021.4005 | -12.6016 | OK
5 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 892895 | 900339 | 7444 | 60 |  | 446640 | 448816.0443 | Switching |  |  |  | Shantinagar s/s-2 | 448816.0443 | 575657.211 | -126841.1666 | -22.0341 | OK
6 | AT-1 & AT-2 |  | 0.415 |  | ELIB 7374 | 1 | 2427 | 2504.15 | 77.15 | 60 |  | 4629 | 4651.5526 | Rajarbag |  |  |  | AT-1 & AT-2 | 4651.5526 | 5701.2436 | -1049.6909 | -18.4116 | OK
|  |  | 10: Grand Total | 4608360 | 4586016.78 | 4608360 | 0.4872
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Rajarbag | at 33 KV level |  | 4439022.9847 | Including Switching
[6 empty] | Khilgaon | at 33 KV level |  | 301.4616
[6 empty] | Moghbazar | at 33 KV level |  | 105125.6925
[6 empty] | Kakrail | at 33 KV level |  | 63909.8612
[6 empty] | Total = |  |  | 4608360 | 0
11 KV SIDE of___Santinagar Switching S/S | [14 empty] | Month December-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 892895 | 900339 | 7444 | 60 |  | 446640 | 448816.0443 | 0.4872
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder |  | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 278424 | 279780.4906 | Rajarbag
2 | 11 Fortune(MogBazar)-new |  | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 104616 | 105125.6925 | Moghbazar
3 | Centerpoint-Kakrail |  | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 63600 | 63909.8612 | Kakrail
[12 empty] | 446640 | 448816.0443 | 0.4872
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 |  | 33 | Import |  | 1 | 1182.108 | 1186.857 | 4.749 | 180000 | 0 | 854820 | 4193.83
2 | Sherebangla to Monipuripara-2 |  | 33 | Import |  | 1 | 869.027 | 895.777 | 26.75 | 180000 | 0 | 4815000 | 23622.86
|  |  | 10: Total | 0 | 5669820 | 27816.69
|  |  | 10: Net Total | 5697636.69
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | BD017103 | 1 | 49332.2 | 50093.49 | 761.29 | 1000 | 761290
2 | Agargaon Ckt-02 |  | 33 | Import | BD017104 | 1 | 38934.14 | 43223.87 | 4289.73 | 1000 | 4289730
|  |  | 7: 0; 8: 0; 10: Total | 5051020 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONIPURIPARA 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | BD017102 | 1 | 49332.2 | 50093.49 | 761.29 | 1000 |  | 761290 |  |  | OMF Corrected by Grid
4 | Transformer-02 |  | 33 | Export | BD017105 | 1 | 56887.35 | 61730.45 | 4843.1 | 1000 |  | 4843100 |  |  | OMF Corrected by Grid
|  |  | 10: Total |  | 5604390 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 4: 5697636.69; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5697636.69
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 5697636.69 | 33 KV TX HV SIDE |  | 5604390
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 93246.69
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.637%
| TOTAL IMPORT |  | 4: 5697636.69
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD014058 | 1 | 12724.35 | 12724.35 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import | BD014062 | 1 | 55879.87 | 60690 | 4810.13 | 1000 | 4810130 |  | 5697636.69
|  |  | 7: 0; 8: 0; 10: Total | 4810130 | 0 | 5697636.69
| MONIPURIPARA 11 KV SIDE |  | 7: 0; 8: 0
1 | Spare |  | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | D572W | 11 |  | BD013947 | 1 | 33710.12 | 34318.15 | 608.03 | 1000 |  | 608030 | 612114.5091 | Shere b.nagar |  |  |  | Monipuripara west | 612114.5091 | 935544.6228 | -323430.1137 | -34.5713 | OK
3 | Biggan College | C672BC | 11 |  | BD013949 | 1 | 21787.07 | 22412.2 | 625.13 | 1000 |  | 625130 | 629329.3802 | Kakrail |  |  |  | Biggan College | 629329.3802 | 983877.3078 | -354547.9275 | -36.0358 | OK
4 | Green Road South | D572G | 11 |  | BD013948 | 1 | 32252.24 | 32736.24 | 484 | 1000 |  | 484000 | 487251.3238 | Shere b.nagar |  |  |  | Green Road South | 487251.3238 | 613343.481 | -126092.1573 | -20.5582 | OK
5 | BARC Building O/H | D572B | 11 |  | BD014010 | 1 | 14613.61 | 14617.09 | 3.48 | 1000 |  | 3480 | 3503.3773 | Shere b.nagar |  |  |  | BARC Building O/H | 3503.3773 | 39283.5032 | -35780.1259 | -91.0818 | CHECK
6 | Indira Road (Green Road North) | D572NN | 11 |  | BD014036 | 1 | 63504.96 | 63986.61 | 481.65 | 1000 |  | 481650 | 484885.5374 | Shere b.nagar |  |  |  | Indira Road (Green Road North) | 484885.5374 | 964099.8184 | -479214.281 | -49.7059 | CHECK
7 | Chundrima Uddan | D572C | 11 |  | BD014035 | 1 | 32488.76 | 32997.64 | 508.88 | 1000 |  | 508880 | 512298.4579 | Shere b.nagar |  |  |  | Chundrima Uddan | 512298.4579 | 477595.7009 | 34702.7571 | 7.2661 | OK
8 | khamar bari RMU-1 Feeder |  | 11 |  | BD013940 | 1 | 1367.45 | 1648.58 | 281.13 | 1000 |  | 281130 | 283018.522 | Shere b.nagar |  |  |  | khamar bari RMU-1 Feeder | 283018.522 | 321406.8247 | -38388.3027 | -11.9438 | OK
1 | Farmgate foot over bridge RMU |  | 11 |  | BD013946 | 1 | 239.33 | 457.31 | 217.98 | 1000 |  | 217980 | 219444.3049 | Tejgaon |  |  |  | Farmgate foot over bridge RMU | 219444.3049 | 176700.3547 | 42743.9502 | 24.1901 | OK
2 | kawran Bazar North | C672K | 11 |  | BD013964 | 1 | 40517.44 | 40643.13 | 125.69 | 1000 |  | 125690 | 126534.3365 | Kakrail |  |  |  | kawran Bazar North | 126534.3365 | 61252.9055 | 65281.4311 | 106.5769 | FAULT
3 | NAM Bhanan RMU | D572NM | 11 |  | BD013950 | 1 | 18967.08 | 19600.71 | 633.63 | 1000 |  | 633630 | 637886.4799 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 637886.4799 | 770397.0568 | -132510.5769 | -17.2003 | OK
4 | Novo Theater |  | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | C172I | 11 |  | BD013962 | 1 | 40098.87 | 40333.1 | 234.23 | 1000 |  | 234230 | 235803.4661 | Tejgaon |  |  |  | Monipuripara Nearest | 235803.4661 | 446918.9749 | -211115.5089 | -47.238 | CHECK
6 | Holy Cross | C172HC | 11 |  | BD013965 | 1 | 40933.65 | 41628.74 | 695.09 | 1000 |  | 695090 | 699759.3443 | Tejgaon |  |  |  | Holy Cross | 699759.3443 | 1032893.7086 | -333134.3643 | -32.2525 | OK
7 | Honda Goli | C172HG | 11 |  | BD014011 | 1 | 17161.03 | 17805.97 | 644.94 | 1000 |  | 644940 | 649272.4561 | Tejgaon |  |  |  | Honda Goli | 649272.4561 | 812717.0632 | -163444.6071 | -20.1109 | OK
8 | Navy Quarter | C172NQ | 11 |  | BD013941 | 1 | 5981.54 | 6097.25 | 115.71 | 1000 |  | 115710 | 116487.2948 | Tejgaon |  |  |  | Navy Quarter | 116487.2948 | 259359.6022 | -142872.3074 | -55.0866 | CHECK
9 | AT-01 |  | 0.415 |  |  | 1 | 2170.58 | 2170.58 | 0 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 641.32 | 688.9 | 47.58 | 1 |  | 47.58 | 47.8996 | Shere b.nagar |  |  |  | AT-02 | 47.8996 | 56.1451 | -8.2455 | -14.6861 | OK
|  |  | 10: Grand Total | 5697636.69 | 5659617.58 | 5697636.69 | 0.67176
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 3021006.1071
[6 empty] | Kakrail | at 33 KV level |  | 755863.7168
[6 empty] | Tejgaon | at 33 KV level |  | 1920766.8661
[6 empty] | Total = |  |  | 5697636.69 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 |  | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 |  | 33 | 0 | 0 | 1 | 3982.57 | 4003.22 | 20.65 | 180000 | 0 | 3717000 | 3729064.3436
|  |  | 10: Total | 0 | 3717000 | 3729064.3436
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 |  | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 |  | 33 | Import |  | 1 | 48712.32 | 52428.58 | 3716.26 | 1000 | 3716260
|  |  | 8: 0; 10: Total | 3716260 | 0 | 0
| Ispahani 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| Ispahani 33 KV SIDE |  | 8: 0
3 | Transformer-01 |  | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 |  | 33 | Export |  | 1 | 49141.45 | 53320.42 | 4178.97 | 888.8889 |  | 3714640.0464
|  |  | 10: Total |  | 3714640.0464 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 4: 3729064.3436; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3729064.3436
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 3729064.3436 | 33 KV TX HV SIDE |  | 3714640.0464
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 14424.2972
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3868%
| TOTAL IMPORT |  | 4: 3729064.3436
11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import |  | 1 | 14251.82 | 15471.12 | 1219.3 | 1000 | 1219300 |  | 3729064.3436 |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 1219300 | 3714640.0464 | 3729064.3436
| Ispahani 11 KV SIDE |  | 7: 0; 8: 0
1 | Doctor Goli | D1113D | 11 |  | BD013944 | 1 | 11220.97 | 11738.94 | 517.97 | 1000 |  | 517970 | 521759.6267 | Moghbazar |  |  |  | Doctor Goli | 521759.6267 | 680371.3877 | -158611.761 | -23.3125 | OK
2 | Ispahani | D1113S | 11 |  | BD013947 | 1 | 12560.14 | 13161.92 | 601.78 | 1000 |  | 601780 | 606182.8062 | Moghbazar |  |  |  | Ispahani | 606182.8062 | 787241.7632 | -181058.957 | -22.9992 | OK
3 | BTCL | C6113BT | 11 |  | BD013949 | 1 | 6628.46 | 7159.42 | 530.96 | 1000 |  | 530960 | 534844.6655 | Kakrail |  |  |  | BTCL | 534844.6655 | 534614.2847 | 230.3807 | 0.043093 | OK
4 | Vikarunnesa | C6113VQ | 11 |  | BD013948 | 1 | 9308.85 | 9895.52 | 586.67 | 1000 |  | 586670 | 590962.2568 | Kakrail |  |  |  | Vikarunnesa | 590962.2568 | 754158.2718 | -163196.0149 | -21.6395 | OK
5 | OASIS |  | 11 |  |  | 1 | 424 | 546.82 | 122.82 | 1000 |  | 122820 | 123718.5886 | Kakrail |  |  |  | OASIS | 123718.5886 | 114056.2956 | 9662.2931 | 8.4715 | OK
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | D1113W | 11 |  |  | 1 | 10751.41 | 11429.01 | 677.6 | 1000 |  | 677600 | 682557.5285 | Moghbazar |  |  |  | Wireless | 682557.5285 | 776089.4575 | -93531.929 | -12.0517 | OK
2 | Kazir Goli | C6113KG | 11 |  |  | 1 | 10477.16 | 11127.02 | 649.86 | 1000 |  | 649860 | 654614.5742 | Kakrail |  |  |  | Kazir Goli | 654614.5742 | 954304.3117 | -299689.7375 | -31.404 | OK
3 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3714640.0464 | 3687660 | 3714640.0464 | 0.73163
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 1810499.9613
[6 empty] | Kakrail | at 33 KV level |  | 1904140.0851
[6 empty] | Total = |  |  | 3714640.0464 | 0
Note on K1229: User: Grid OMF = 1000
Note on K1230: User: Grid OMF = 1000

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 |  | 132 | IMPORT | 8993683 | 1 | 8481.316 | 8508.189 | 26.873 | 960000 | 0 | 25798080
| XFR- T2 |  | 132 |  | 8993682 | 1 | 8470.688 | 8497.485 | 26.797 | 960000 | 0 | 25725120
|  |  | 10: Total | 0 | 51523200
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** |  | 132 | P. Cell | 08993685 | 1 | 8481.208 | 8508.189 | 26.981 | 960000 | 25901760
| 132/33 kV Transformer-2(HV) ** |  | 132 | P. Cell | 08993684 | 1 | 8470.673 | 8497.485 | 26.812 | 960000 | 25739520
|  |  | 10: Total | 51641280
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 4: 51523200; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 51523200
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 51523200 | 33 KV NET IMPORT |  | 51540000
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 51523200 | LOSS UNITS=>(132 HV-33 LV) |  | -16800
| IMPORT-4 |  | 6: Loss Units=> (132 IMP-132 EXP); 9=8-7: 0 | LOSS % IN => |  | -0.03261%
| 132 KV TOTAL IMPORT |  | 4: 51523200; 6: 132 KV NET LOSS =>; 9=8-7: 0%
| 33 KV GT INCOMING-NOCS |  | 4: 51540000
| Loss Units=> (132 IMP-33 IMP) |  | 4: -16800
| LOSS % IN => |  | 4: -0.03261%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | 4: IMPORT
3 | 132/33 kV Transformer, T-1 (LV) |  | 33 | PGCB | J2002016494 | 1 | 22821.391 | 23000.595 | 179.204 | 144000 | 25805376
4 | 132/33 kV Transformer, T-2 (LV) |  | 33 | PGCB | J2002016859 | 1 | 32792.205 | 32970.94 | 178.735 | 144000 | 25737840
| DPDC |  | 7: 0; 8: 0; 10: Total | 51543216
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | DPDC | 07389553 | 1 | 1892.64 | 1946.6 | 53.96 | 480000 | 25900800
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | DPDC | 07389485 | 1.038 | 1256.79 | 1309.38 | 52.59 | 480000 | 26202441.6
| P.Cell |  | 7: 0; 8: 0; 10: Total | 52103241.6
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | P.Cell | 08993674 | 1 | 11157.639 | 11211.156 | 53.517 | 480000 | 25688160
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | P.Cell | 8993667 | 1 | 11065.518 | 11119.376 | 53.858 | 480000 | 25851840
|  |  | 7: 0; 8: 0; 10: Total | 51540000
| SIDDHIRGANJ 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) |  | 33 | DPDC | 07389555 | 1 | 5746.05 | 5749.06 | 3.01 | 240000 | From Downstream | 3945200 | 3964463.1236 |  | 8963955.401 | Siddhirganj 33/11 kv ss | 1.1371 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 3964463.1236 | 5503683.2922 | -1539220.1685 | -27.9671 | OK
|  |  | 33 | P.Cell | 08993675 | 1 | 5022.34 | 5022.34 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) |  | 33 | DPDC | 07389487 | 1 | 5928.34 | 5949.07 | 20.73 | 240000 |  | 4975200 | 4999492.2773 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 4999492.2773 | 6175156.635 | -1175664.3576 | -19.0386 | OK
|  |  | 33 | P.Cell | 08993666 | 1 | 5192.564 | 5213.314 | 20.75 | 240000 |  | 4980000 | 5004315.7142 |  |  |  |  | 0 | 5004315.7142 | 6168681.7135 | -1164365.9993 | -18.8754 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8920400 | 8963955.401 |  |  |  |  | 33 KV Feeders | 8963955.401 | 11678839.9272 | -2714884.5262 | -23.2462 | OK
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4401.053 | 4428.152 | 27.099 | 240000 |  | 6503760 | 6535515.7368 |  | 12169289.9577 | Sarulia 33/11 kv ss | 1.8988 | 33 kV Sarulia-1 Feeder | 6535515.7368 | 8017391.7134 | -1481875.9766 | -18.4833 | OK
|  |  | 33 | P.Cell | 08993679 | 1 | 4401.846 | 4428.942 | 27.096 | 240000 |  | 6503040 | 6534792.2213 |  |  |  |  | 0 | 6534792.2213 | 8010676.98 | -1475884.7587 | -18.424 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) |  | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss | 1.0581 | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6293.38 | 6323.29 | 29.91 | 240000 |  | 7178400 | 7213449.7837 |  |  |  |  | 33 kV Demra-1 Feeder | 7213449.7837 | 8381426.19 | -1167976.4063 | -13.9353 | OK
|  |  | 33 | P.Cell | 08993676 | 1 | 5938.92 | 5968.841 | 29.921 | 240000 |  | 7181040 | 7216102.6739 |  |  |  |  | 0 | 7216102.6739 | 8370155.0303 | -1154052.3564 | -13.7877 | OK
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5855.99 | 5895.83 | 39.84 | 240000 |  | 9561600 | 9608286.1712 |  | 16821735.9549 | Demra 33/11 kv ss | 0.73689 | 33 kV Demra-2 Feeder | 9608286.1712 | 11055328.9659 | -1447042.7947 | -13.0891 | OK
|  |  | 33 | P.Cell | 08993665 | 1 | 5564.146 | 5603.99 | 39.844 | 240000 |  | 9562560 | 9609250.8586 |  |  |  |  | 0 | 9609250.8586 | 11041180.0634 | -1431929.2048 | -12.969 | OK
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder |  | 33 | DPDC | 7389486 | 1 | 4616.75 | 4641.55 | 24.8 | 240000 |  | 5952000 | 5981061.6729 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 5981061.6729 | 5757883.9148 | 223177.758 | 3.876 | OK
|  |  | 33 | P.Cell | 08993678 | 1 | 3862.384 | 3887.194 | 24.81 | 240000 |  | 5954400 | 5983473.3913 |  |  |  |  | 0 | 5983473.3913 | 5749250.6861 | 234222.7052 | 4.074 | OK
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4094.6 | 4117.96 | 23.36 | 240000 |  | 5606400 | 5633774.2209 |  |  |  |  | 33 kV Sarulia-2 Feeder | 5633774.2209 | 6853824.3351 | -1220050.1142 | -17.801 | OK
|  |  | 33 | P.Cell | 08993663 | 1 | 3816.402 | 3839.766 | 23.364 | 240000 |  | 5607360 | 5634738.9082 |  |  |  |  | 0 | 5634738.9082 | 6843032.7992 | -1208293.891 | -17.6573 | OK
17 | 33 kV Adamjee EPZ Feeder |  | 33 | DPDC | ABB03919 | 1 | 380367.7 | 384040.3 | 3672.6 | 2000 |  | 7345200 | 7381064.2136 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 7381064.2136 | 9198984.9536 | -1817920.74 | -19.7622 | OK
|  |  | 10: Total | 51317107.2 | 51067760 | 51317107.2 | 0.48827
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 13362125.8865
[6 empty] | Total = |  |  | 13362125.8865 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | 4: IMPORT
8 | 33/11 kV Transformer-1 Incoming |  | 11 | New | XA587379 | 1 | 703843.3 | 707788.5 | 3945.2 | 1000 | 3945200 |  | 3992886.5458
9 | 33/11 kV Transformer-2 Incoming |  | 11 | New | DHKA9985 | 1 | 336869.4 | 341781.1 | 4911.7 | 1000 | 4911700 |  | 4971068.8551
|  |  | 7: 0; 8: 0; 10: Total | 8856900 |  | 8963955.401
| SIDDHIRGANJ 11 kV SIDE |  | 4: EXPORT; 7: 0; 8: 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1 | 221836.7 | 223150.6 | 1313.9 | 1000 |  | 1313900 | 1328840.997 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 1328840.997 | 1907566.3908 | -578725.3938 | -30.3384 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1 | 17327.3 | 17397.1 | 69.8 | 1000 |  | 69800 | 70593.7298 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 70593.7298 | 97801.2231 | -27207.4933 | -27.8192 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1 | 113678.5 | 114558.2 | 879.7 | 1000 |  | 879700 | 889703.4972 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 889703.4972 | 1253935.5917 | -364232.0945 | -29.0471 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1 | 179110.6 | 180686.4 | 1575.8 | 1000 |  | 1575800 | 1593719.1894 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 1593719.1894 | 2152733.2578 | -559014.0684 | -25.9676 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1 | 7300.2 | 7399.4 | 99.2 | 1000 |  | 99200 | 100328.0515 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 100328.0515 | 99239.4764 | 1088.5751 | 1.0969 | OK
10 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 79934 | 80921.6 | 987.6 | 1000 |  | 987600 | 998830.4807 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 998830.4807 | 1251179.7778 | -252349.2971 | -20.1689 | OK
11 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) |  | 11 | T2 |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 155175.3 | 156626.1 | 1450.8 | 1000 |  | 1450800 | 1467297.7535 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 1467297.7535 | 1794799.2873 | -327501.5338 | -18.2473 | OK
14 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 111.26 | 117.1198 | 5.8598 | 40000 |  | 234392 | 237057.3856 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 237057.3856 | 379449.435 | -142392.0494 | -37.526 | OK
15 | 11 kV Madrasha Road Feeder (F-11) |  | 11 | T2 | XA575919 | 1 | 2.5378 | 6.4972 | 3.9594 | 40000 |  | 158376 | 160176.9706 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 160176.9706 | 0 | 160176.9706 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 16870.9 | 17353.1 | 482.2 | 1000 |  | 482200 | 487683.3311 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 487683.3311 | 567556.8719 | -79873.5408 | -14.0732 | OK
17 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129895.9 | 129896 | 0.1 | 1000 |  | 100 | 101.1371 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 101.1371 | 0 | 101.1371 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 156958.2 | 158569.5 | 1611.3 | 1000 |  | 1611300 | 1629622.8772 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 1629622.8772 | 2174578.6154 | -544955.7381 | -25.0603 | OK
|  |  | 10: Total | 8963955.401 | 8863168 | 8963955.401 | 1.1371
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 8726898.0153
[6 empty] | Matuail | at 33 KV level |  | 237057.3856
[6 empty] | Total = |  |  | 8963955.401 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6293.38 | 6323.29 | 29.91 | 240000 | 0 | 7178400 | 7213449.7837
0 | 0 |  | 33 | P.Cell | 08993676 | 1 | 5938.92 | 5968.841 | 29.921 | 240000 | 0 | 7181040 | 7216102.6739
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5855.99 | 5895.83 | 39.84 | 240000 | 0 | 9561600 | 9608286.1712
0 | 0 |  | 33 | P.Cell | 08993665 | 1 | 5564.146 | 5603.99 | 39.844 | 240000 | 0 | 9562560 | 9609250.8586
|  |  | 10: Total | 0 | 16740000 | 16821735.9549
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 |  | 33 | Digital | DHK60885 | 3 | 425220.6 | 442060.4 | 16839.8 | 240 | 12124656
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) |  | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
|  |  | 7: 0; 8: 0; 10: Total | 12124656 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
10 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1022.36 | 1024.85 | 2.49 | 240000 |  | 597600 |  | Siddirgonj
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 597600
[7 empty] | 0 | 0
| DEMRA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60886 | 1 | 905180.8 | 935670.4 | 30489.6 | 240 |  | 7317504
8 | 33/11 kV, 10/14 MVA T-2 (HV) |  | 33 | Digital | 05002303 | 1 | 61.99 | 69.78 | 7.79 | 240000 |  | 1869600
9 | 33/11 kV, 20/28 MVA T-3 (HV) |  | 33 |  |  | 1 | 0 | 0 | 0 | 180 |  | 0
|  |  | 10: Total |  | 9187104 | 0
[6 empty] | 33 KV Export-Import |  |  | KWH
[6 empty] | Total Import |  |  | 16821735.9549
[6 empty] | Siddirgonj NOCS |  |  | 597600
[6 empty] | Net Import to Demra 33/11 KV SS |  |  | 16224135.9549
11 KV SIDE of___DEMRA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.01.2024 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK60881 | 1 | 499660.4 | 540240.6 | 40580.2 | 180 | 7304436 |  | 7446187.7352
19 | 33/11 kV, 20/28 MVA T-3 Incoming. |  | 11 |  | DHK60925 | 1 | 898930.8 | 935460.6 | 36529.8 | 180 | 6575364 |  | 6702967.1793
| 33/11 kV, 10/14 MVA T-2 Incoming. |  | 11 |  |  | 1 | 18314.98 | 20350.46 | 2035.48 | 1000 | 2035480 |  | 2074981.0405
|  |  | 7: 0; 8: 0; 10: Total | 15915280 |  | 16224135.9549
| DEMRA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 |  | HA021101013-02 | 1 | 57648360 | 59997998 | 2349638 | 1 |  | 2349638 | 2366952.3646 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2366952.3646 | 2709931.5892 | -342979.2246 | -12.6564 | OK
12 | 11 kV DND (WASA) Feeder. | A816B | 11 |  | HA021100992-02 | 1 | 6452560 | 6457730 | 5170 | 1 |  | 5170 | 5208.0975 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 5208.0975 | 4780.8214 | 427.2761 | 8.9373 | OK
13 | 11 kV Local Feeder | A816D | 11 |  | HA021100794-02 | 1 | 14233810 | 14945420 | 711610 | 1 |  | 711610 | 716853.8184 | Siddirgonj |  |  |  | 11 kV Local Feeder | 716853.8184 | 898962.87 | -182109.0516 | -20.2577 | OK
14 | 11 kV Mouchak Feeder | A816A | 11 |  | DHK60888 | 1 | 1047240.6 | 1077570.4 | 30329.8 | 60 |  | 1819788 | 1833197.9265 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 1833197.9265 | 2048559.8995 | -215361.973 | -10.5128 | OK
15 | 11 kV Overhead-1 Feeder | A816C | 11 |  | HA021100829-02 | 1 | 79937310 | 80343450 | 406140 | 1 |  | 406140 | 409132.8253 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 409132.8253 | 374998.6846 | 34134.1407 | 9.1025 | OK
16 | 11 kV Provati Steel Feeder | A816Z | 11 |  | DHK60874 | 1 | 609350.3 | 615326.2 | 5975.9 | 60 |  | 358554 | 361196.1665 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 361196.1665 | 473734.4777 | -112538.3112 | -23.7556 | OK
17 | 11 kV Islambagh Feeder. | E116I | 11 |  | DHKA2190 | 1 | 1212.637 | 1240.0398 | 27.4028 | 60000 |  | 1644168 | 1656283.7916 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 1656283.7916 | 1979061.5163 | -322777.7248 | -16.3096 | OK
20 | 11 kV Taj Jute Feeder. | A816E | 11 |  | DHK61062 | 1 | 702990.4 | 722690.8 | 19700.4 | 60 |  | 1182024 | 1190734.2756 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1190734.2756 | 1388752.4047 | -198018.1291 | -14.2587 | OK
21 | 11 kV Al-Aksa Steel Feeder | A816S | 11 |  | DHK61061 | 1 | 877240.8 | 906680.6 | 29439.8 | 60 |  | 1766388 | 1779404.4246 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1779404.4246 | 1746616.1362 | 32788.2884 | 1.8772 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 |  | DHKA2189 | 1 | 1151.187 | 1180.884 | 29.697 | 60000 |  | 1781820 | 1794950.1423 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 1794950.1423 | 2085198.1573 | -290248.015 | -13.9194 | OK
23 | 11 kV Over Head Feeder-2. | E116V | 11 |  | HA021100488-02 | 1 | 35111950 | 36458480 | 1346530 | 1 |  | 1346530 | 1356452.5121 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 1356452.5121 | 1697694.9376 | -341242.4255 | -20.1003 | OK
24 | 11 kV Shimrail Express Feeder. | A8164 | 11 |  | HA021100511-02 | 1 | 8254917 | 8256130 | 1213 | 1 |  | 1213 | 1221.9385 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 1221.9385 | 542.4548 | 679.4838 | 125.2609 | FAULT
25 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 |  | HA021100413-02 | 1 | 82521598 | 82686340 | 164742 | 1 |  | 164742 | 165955.9755 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 165955.9755 | 367927.7214 | -201971.7459 | -54.8944 | CHECK
26 | 11 kV Siddhirgonj Mazar Feeder |  | 11 |  | HA021100393-02 | 1 | 26893.78 | 27633.46 | 739.68 | 1000 |  | 739680 | 745130.6648 | Siddirgonj |  |  |  | 11 kV Siddhirgonj Mazar Feeder | 745130.6648 | 826630.8876 | -81500.2228 | -9.8593 | OK
27 | 11 kV AST Beverage Feeder | A816J | 11 |  |  | 1 | 23358696 | 23586810 | 228114 | 1 |  | 228114 | 229794.9606 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 229794.9606 | 294965.0476 | -65170.0869 | -22.0942 | OK
28 | 11 kV Karim Market Feeder | E216K | 11 |  |  | 1 | 64428.93 | 65722.21 | 1293.28 | 1000 |  | 1293280 | 1302810.1155 | Matuail |  |  |  | 11 kV Karim Market Feeder | 1302810.1155 | 1746397.55 | -443587.4345 | -25.4001 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 |  | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 15915280 | 15798859 | 15915280 | 0.73689
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 5326046.2717
[6 empty] | Demra | at 33 KV level |  | 1522408.4876
[6 empty] | Siddirgonj | at 33 KV level |  | 9066825.2407
[6 empty] | Total = |  |  | 15915280 | 0
33 KV SIDE of___ SARULIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4401.053 | 4428.152 | 27.099 | 240000 | 0 | 6503760 | 6535515.7368
0 | 0 |  | 33 | P.Cell | 08993679 | 1 | 4401.846 | 4428.942 | 27.096 | 240000 | 0 | 6503040 | 6534792.2213
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4094.6 | 4117.96 | 23.36 | 240000 | 0 | 5606400 | 5633774.2209
| 0 |  | 33 | P.Cell | 08993663 | 1 | 3816.402 | 3839.766 | 23.364 | 240000 | 0 | 5607360 | 5634738.9082
|  |  | 10: Total | 0 | 12110160 | 12169289.9577
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) |  | 33 |  | 30799103 | 1 | 4468.94 | 4492.18 | 23.24 | 240000 | 5577600
7 | 33 kV Siddhirgonj-1 Incoming (=L41) |  | 33 |  | 30799100 | 1 | 4418.41 | 4445.18 | 26.77 | 240000 | 6424800
|  |  | 7: 0; 8: 0; 10: Total | 12002400 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SARULIA 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV Transformer-1 (=T31) |  | 33 |  | 30799099 | 1 | 4826.03 | 4857.05 | 31.02 | 180000 |  | 5583600
5 | 33/11 kV Transformer-2 (=T32) |  | 33 |  | 30799139 | 1 | 4124.15 | 4142.66 | 18.51 | 180000 |  | 3331800
6 | 33/11 kV Transformer-3 (=T33) |  | 33 |  | 30799102 | 1 | 1827.2 | 1840.2 | 13 | 240000 |  | 3120000 |  |  | Meter Problem
|  |  | 10: Total |  | 12035400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 4: 12169289.9577; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 12169289.9577
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 12169289.9577 | 33 KV NET Receiving |  | 12002400
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 12169289.9577 | LOSS UNITS=> |  | 166889.9577
| IMPORT-4 |  | 6: 132KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 1.371%
| TOTAL IMPORT |  | 4: 12169289.9577
11 KV SIDE of___SARULIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) |  | 11 |  | 2007754972 | 1 | 9504.86 | 9539.83 | 34.97 | 160000 | 5595200 |  | 5664491.4117
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) |  | 11 |  | 30799500 | 1 | 8981.71 | 9023.03 | 41.32 | 80000 | 3305600 |  | 3346536.8192
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) |  | 11 |  | HA021100368-02 | 1 | 63076552 | 66196180 | 3119628 | 1 | 3119628 |  | 3158261.7268
|  |  | 7: 0; 8: 0; 10: Total | 12020428 |  | 12169289.9577
| SARULIA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 |  | 2007755114 | 1 | 5962.59 | 5999 | 36.41 | 60000 |  | 2184600 | 2226080.12 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 2226080.12 | 2656170.9356 | -430090.8156 | -16.1921 | OK
9 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 |  | 30799484 | 1 | 22.3065 | 22.573 | 0.2665 | 60000 |  | 15990 | 16293.6103 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 16293.6103 | 14090.6259 | 2202.9844 | 15.6344 | OK
11 | 11 kV Konapara (=L13) **** | E183KL | 11 |  | DHKA2191 | 1 | 2242.8601 | 2270.8758 | 28.0157 | 60000 |  | 1680942 | 1712858.9074 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 1712858.9074 | 2092594.4251 | -379735.5177 | -18.1466 | OK
12 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 |  | 575926 | 1 | 60597 | 62272 | 1675 | 1000 |  | 1675000 | 1706804.0836 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 1706804.0836 | 2044950.3572 | -338146.2736 | -16.5357 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 |  | 30799450 | 1 | 1829.83 | 1834.24 | 4.41 | 60000 |  | 264600 | 269624.0958 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 269624.0958 | 277809.1547 | -8185.0589 | -2.9463 | OK
14 | 11 kV Tengra Feeder (=L16) | E183T | 11 |  | 30799145 | 1 | 5648.31 | 5679.55 | 31.24 | 60000 |  | 1874400 | 1909990.1936 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 1909990.1936 | 2317704.7602 | -407714.5666 | -17.5913 | OK
16 | 11 kV Police Line Feeder (=L17) | E183PL | 11 |  | 30799480 | 1 | 3396.71 | 3410.21 | 13.5 | 60000 |  | 810000 | 825379.8852 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 825379.8852 | 1025710.2197 | -200330.3345 | -19.5309 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 |  | 30799119 | 1 | 1670.44 | 1675.8 | 5.36 | 60000 |  | 321600 | 327706.384 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 327706.384 | 385778.6515 | -58072.2675 | -15.0533 | OK
18 | 11 kV Spare Feeder (=F9) |  | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 |  | HA021100493-02 | 1 | 91722476 | 93505305 | 1782829 | 1 |  | 1782829 | 1816680.4881 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 1816680.4881 | 2264027.3407 | -447346.8526 | -19.7589 | OK
21 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 |  | HA021100518-02 | 1 | 50895377 | 50895377 | 0 | 1 |  | 0 | 0 | Demra | No Reading in Grid |  |  | 11 kV Baser Pool Feeder (=L11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 |  | HA021100697-02 | 1 | 31095860 | 32428430 | 1332570 | 1 |  | 1332570 | 1357872.1896 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 1357872.1896 | 1792379.5779 | -434507.3882 | -24.2419 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) |  | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) |  | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 12169289.9577 | 11942531 | 12169289.9577 | 1.8988
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Demra | at 33 KV level |  | 10462485.8741
[6 empty] | Matuail | at 33 KV level |  | 1706804.0836
[6 empty] | Total = |  |  | 12169289.9577 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 46039.096 | 51950.566 | 5911.47 | 1000 | 0 | 5911470 | 5916030.8292
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 537.5595 | 559.9832 | 22.4237 | 240000 | 0 | 5381688 | 5385840.0907
| Siddhirganj 33 KV SIDE |  | 10: Total |  | 11293158 | 11301870.9198
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) |  | 33 |  | 84663042 | 1 | 544.98 | 567.24 | 22.26 | 240000 | 5342400
6 | 33 kV Shitalakhya-2 Feeder (Old) |  | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 5911470 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 |  | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 |  | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 11253870 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
11 | 33 kV ACI Pharmacuticles Feeder |  | 33 |  | DHKC4791 | 1 | 960.83 | 971.93 | 11.1 | 90000 |  | 999000 |  | N.Gonj (East)
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 999000
[7 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  | 7: 0; 8: 0
9 | 33/11 kV, 20/28 MVA T1 Transformer |  | 33 |  | DHKC 9363 | 1 | 16865.34 | 33482.79 | 16617.45 | 240 |  | 3988188 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer |  | 33 |  | DHKC 9361 | 1 | 50295.81 | 63205.86 | 12910.05 | 240 |  | 3098412 |  |  | Meter Problem
|  |  | 10: Total |  | 10254870 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 11301870.9198; 6: EXPORT TO N.Gonj (East); 9=8-7: 999000 | 33 KV NET IMPORT |  | 10302870.9198
| SIDDIRGANJ 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 10302870.9198 | 33 KV TX HV SIDE |  | 10254870
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 48000.9198
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4659%
| TOTAL IMPORT |  | 4: 11301870.9198
11 KV SIDE of___KHANPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. |  | 11 |  | DHKC 9313 | 1 | 37858588.1 | 40568574.28 | 2709986.18 | 1 | 2709986.18 |  | 3406734.6359
18 | 33/11 kV Transformer-2 Incoming. |  | 11 |  | DHKC 9346 | 1 | 62167341.88 | 62301074.12 | 133732.24 | 1 | 133732.24 |  | 168115.3422
24 | 33/11 kV 20/28 MVA T4 Incoming |  | 11 |  | 06604325 | 1 | 199.96 | 212.75 | 12.79 | 240000 | 3069600 |  | 3858806.6299
30 | 33/11 kV 20/28 MVA T1 Incoming |  | 11 |  | 06604374 | 1 | 116.61 | 126.12 | 9.51 | 240000 | 2282400 |  | 2869214.312
|  |  | 7: 0; 8: 0; 10: Total | 8195718.42 |  | 10302870.9198
| KHANPUR 11 KV SIDE |  | 7: 0; 8: 0
12 | 11 kV Khanpur Feeder | B723B | 11 |  | DHKC 9348 | 1 | 55005.6 | 71759.65 | 16754.05 | 60 |  | 1005243 | 1015879.0626 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1015879.0626 | 1344397.4603 | -328518.3977 | -24.4361 | OK
13 | 11 kV Mission Para Feeder. | B723T | 11 |  | DHKC 9347 | 1 | 33948.22 | 50154.35 | 16206.13 | 60 |  | 972367.8 | 982656.0237 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 982656.0237 | 1274888.2401 | -292232.2164 | -22.9222 | OK
14 | 11 kV Esha Kha Feeder | B723M | 11 |  | DHKC 9311 | 1 | 42944.3 | 55179.5 | 12235.2 | 60 |  | 734112 | 741879.3371 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 741879.3371 | 807699.1496 | -65819.8125 | -8.1491 | OK
15 | 11 kV New Hazigonj Feeder | B723F | 11 |  | DHKC 9314 | 1 | 302.18 | 324.58 | 22.4 | 60000 |  | 1344000 | 1358220.3111 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 1358220.3111 | 1630966.9503 | -272746.6392 | -16.723 | OK
16 | 11 kV Spare Feeder. |  | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | B723H | 11 |  | 6604412 | 1 | 8.79 | 9.36 | 0.57 | 60000 |  | 34200 | 34561.8561 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 34561.8561 | 46010.9459 | -11449.0898 | -24.8834 | OK
20 | 11 kV Old Hajiganj Feeder. | B723E | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 |  | 06604389 | 1 | 85919.8 | 98494.55 | 12574.75 | 60 |  | 754485 | 762467.8954 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 762467.8954 | 948106.9996 | -185639.1042 | -19.58 | OK
22 | 11 kV Spare Feeder. |  | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming |  | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | A723A | 11 |  | 6604415 | 1 | 413.32 | 442.48 | 29.16 | 40000 |  | 1166400 | 1178741.1985 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1178741.1985 | 1517554.0047 | -338812.8062 | -22.3262 | OK
26 | 11 kV Mondalpara Feeder. |  | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | B723C | 11 |  | 06604392 | 1 | 323.08 | 347.28 | 24.2 | 40000 |  | 968000 | 978242.0098 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 978242.0098 | 1208392.7367 | -230150.727 | -19.046 | OK
28 | 11 kV Bishaw Road Feeder. | B723A | 11 |  | 06604393 | 1 | 332.61 | 350.11 | 17.5 | 40000 |  | 700000 | 707406.412 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 707406.412 | 953718.1152 | -246311.7032 | -25.8265 | OK
29 | 11 kV Chasara Feeder. | A723B | 11 |  | 06604391 | 1 | 449.6 | 479.56 | 29.96 | 40000 |  | 1198400 | 1211079.7774 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 1211079.7774 | 1572444.256 | -361364.4786 | -22.9811 | OK
31 | 11 kV Pathan Tully Feeder. | B723G | 11 |  | 06604388 | 1 | 78.12 | 87.97 | 9.85 | 40000 |  | 394000 | 398168.7519 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 398168.7519 | 528318.6681 | -130149.9162 | -24.6347 | OK
32 | 11 kV Spare Feeder. |  | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | B722J | 11 |  | 6604289 | 1 | 294.9 | 317.91 | 23.01 | 40000 |  | 920400 | 930138.3737 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 930138.3737 | 1139779.9227 | -209641.549 | -18.3932 | OK
34 | 11 kV Spare Feeder. |  | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. |  | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. |  | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 |  | 0.415 |  | 412109 | 1 | 9234.3 | 9273.7 | 39.4 | 10 |  | 394 | 398.1688 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 398.1688 | 305.7306 | 92.4381 | 30.2352 | OK
38 | 33/0.415 kV Auxiliary Transformer-2 |  | 0.415 |  | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 |  | 3000 | 3031.7418 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3031.7418 | 3027.0359 | 4.7059 | 0.15546 | OK
|  |  | 10: Grand Total | 10302870.9198 | 10195001.8 | 10302870.9198 | 1.0581
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (West) | at 33 KV level |  | 2389820.9759
[6 empty] | N.Gonj (East) | at 33 KV level |  | 7913049.9439
[6 empty] | Total = |  |  | 10302870.9198 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail |  | 132 | Impt | 8993555 | 1 | 2894.06 | 2917.64 | 23.58 | 1440000 | 0 | 33955200
|  |  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar |  | 3: 132; 4: Impt; 6: 1; 9=8-7: 0 | 0 | 0
|  |  | 3: 132; 4: Expt; 6: 1; 9=8-7: 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 33955200
|  |  | 10: Net Total | 33955200
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder |  | 132 | Impt |  | 1 | 0 | 0 | 0 | 1 | 0
|  |  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  |  | 132 | Expt |  | 1 | 9004370 | 9004435 | 65 | 1 | 65
|  |  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder |  | 132 | Impt | HA040700237-03 | 1 | 45393605 | 58096533 | 12702928 | 1
|  |  | 132 |  | 06604364 | 1 | 6108.75 | 6110.66 | 1.91 | 960000 | 1833600
|  |  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 1833665 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 1833665
| Matuail 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| Matuail 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 KV Transformer, GT-1 |  | 132 | DPDC | H/A040700240-03 | 1 | 656.262 | 36817.106 | 36160.844 | 1000 |  | 36160844
|  |  | 132 | P. Cell | 08993572 | 1 | 5051.982 | 5051.982 | 0 | 480000 |  | 0
5 | 132/33 KV Transformer, GT-2 |  | 132 | DPDC | H/A030700918-03 | 1 | 80918.411 | 97777.153 | 16858.742 | 1000 |  | 16858742
|  |  | 132 | P. Cell | 08993577 | 1 | 5182.088 | 5217.178 | 35.09 | 480000 |  | 16843200
|  |  | 10: Total |  | 53019586
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 4: 33955200; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 33955265
| 132 KV Sending From Maniknagar |  | 4: 65; 6: 132 KV NET IMPORT; 9=8-7: 33955265 | 132/33 KV GT LV Side |  | 34018945
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -63680
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.1875%
| 132 KV TOTAL IMPORT |  | 4: 33955265
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | 4: IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 11744.258 | 28932.368 | 17188.11 | 1000 | 17188110
|  |  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 32325.149 | 49155.984 | 16830.835 | 1000 | 16830835
|  |  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 34018945 |  | 0
| MATUAIL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 |  | 33 | DPDC | H/A060300287-03 | 1.45 | 87559.704 | 93264.112 | 5704.408 | 1000 | From Downstream | 8434620 | 8388045.0363 |  | 14610832.7526 | Matuail 33/11 kv ss | 1.1068 | 33/11 KV Transformer, T-3 | 8388045.0363 | 10294391.7589 | -1906346.7226 | -18.5183 | OK
|  |  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 |  | 33 | DPDC | H/A060300190-03 | 1 | 86159.232 | 92415.891 | 6256.659 | 1000 |  | 6256659 | 6222110.4767 |  |  |  |  | 33/11 KV Transformer, T-4 | 6222110.4767 | 7143701.1492 | -921590.6726 | -12.9007 | OK
|  |  | 33 | P. Cell | 08993581 | 1 | 6382.515 | 6417.278 | 34.763 | 180000 |  | 6257340 | 6222787.7163 |  |  |  |  | 0 | 6222787.7163 | 7134120.6018 | -911332.8855 | -12.7743 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 14691960 | 14610832.7526 |  |  |  |  | 33 KV Feeders | 14610832.7526 | 17428512.3607 | -2817679.6081 | -16.1671 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 7233760 | 12916480 | 5682720 | 1 |  | 5682720 | 5651340.6992 |  | 13585366.6949 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 5651340.6992 | 5966235.8306 | -314895.1313 | -5.278 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.26 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC |  | 1 | 9902.222 | 9905.803 | 3.581 | 1000 | From Customer End | 13605 | 13529.8748 | Matuail | Customer Number 35568341 | From AMR Reading |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 13529.8748 | 7215.4751 | 6314.3997 | 87.5119 | FAULT
|  |  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 0 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 88663.917 | 94441.355 | 5777.438 | 1000 |  | 5777438 | 5745535.6778 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 5745535.6778 | 6259426.6391 | -513890.9613 | -8.2099 | OK
|  |  | 33 | P. Cell | 08993580 | 1.5 | 1436.51 | 1457.985 | 21.475 | 180000 |  | 5798250 | 5766232.7564 |  |  |  |  | 0 | 5766232.7564 | 6247158.3271 | -480925.5708 | -7.6983 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 5745535.6778 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 | DPDC | 00000154 | 1 | 6792000 | 14770080 | 7978080 | 1 | From Downstream | 7978080 | 7934025.9956 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 7934025.9956 | 8707635.3306 | -773609.3349 | -8.8843 | OK
|  |  | 10: Total |  | 19451843 | 19344432.2474 |  |  |  |  | 0 | 19344432.2474 | 20940513.2753 | -1596081.0279 | -7.622 | OK
|  |  | 9=8-7: Grand Total | 33955265 | 34143803 | 33955265 | -0.55219
13620
[6 empty] | 33 KV EXPORT |  |  | KWH
[6 empty] | EXPORT TO Matuail |  |  | 13529.8748
[6 empty] | Total Export |  |  | 13529.8748 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426631 | 1 | 7933529 | 8027247 | 93718 | 90 | 8434620 |  | 8426812.379
11 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | 51426633 | 1 | 7558277 | 7627052 | 68775 | 90 | 6189750 |  | 6184020.3735
|  |  | 7: 0; 8: 0; 10: Total | 14624370 |  | 14610832.7526
| MATUAIL 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Link Road Feeder | B741N | 11 | Backup | DHK66629 | 1 | 25054.42 | 25282.82 | 228.4 | 8000 |  | 1827200 | 1847422.9764 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 1847422.9764 | 2909550.3778 | -1062127.4013 | -36.5049 | OK
|  |  | 11 |  | HA021100475-02 | 1 | 99970.287 | 101790.348 | 1820.061 | 1000 |  | 1820061 | 1840204.9638 | N.Gonj (East) |  |  |  | 0 | 1840204.9638 | 2900288.7042 | -1060083.7403 | -36.551 | OK
4 | 11 kV Lamapara Express Feeder | B723L | 11 |  | HA021100928-03 | 1 | 81154.775 | 82245.906 | 1091.131 | 1000 |  | 1091131 | 1103207.3553 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1103207.3553 | 980020.9332 | 123186.4221 | 12.5698 | OK
5 | 11 kV Kutubpur Feeder*** | B741Q | 11 |  | DHK66616 | 1 | 18505.85 | 18653.41 | 147.56 | 8000 |  | 1180480 | 1193545.2469 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1193545.2469 | 1740376.2153 | -546830.9684 | -31.4203 | OK
|  |  | 11 | Backup | XA575929 | 1 | 46952.4 | 48133 | 1180.6 | 1000 |  | 1180600 | 1193666.5751 | N.Gonj (East) |  |  |  | 0 | 1193666.5751 | 1737533.9126 | -543867.3375 | -31.3011 | OK
6 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 |  | DHK66625 | 1 | 3598.24 | 3616.61 | 18.37 | 60000 |  | 1102200 | 1114398.8642 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1114398.8642 | 1066770.6323 | 47628.2318 | 4.4647 | OK
|  |  | 11 | Backup |  | 1 | 8395.82 | 17738.538 | 9342.718 | 1000 |  | 9342718 | 9446120.7834 | Fatullah |  |  |  | 0 | 9446120.7834 | 0 | 9446120.7834 | #DIV/0! | #DIV/0!
7 | 11 kV Tushardhara Feeder (F2) | E241T | 11 |  | DHK66623 | 1 | 3975.1 | 4010.76 | 35.66 | 60000 |  | 2139600 | 2163280.5387 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2163280.5387 | 2634875.0823 | -471594.5436 | -17.8982 | OK
8 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 |  | DHK66627 | 1 | 3345.82 | 3357.9 | 12.08 | 60000 |  | 724800 | 732821.8987 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 732821.8987 | 826686.7655 | -93864.8668 | -11.3543 | OK
|  |  | 11 | Backup |  | 1 | 63825.371 | 80449.266 | 16623.895 | 1000 |  | 16623895 | 16807883.9649 | Matuail |  |  |  | 0 | 16807883.9649 | 0 | 16807883.9649 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 |  | HA021101044-02 | 1 | 66770.571 | 66954.672 | 184.101 | 1000 |  | 184101 | 186138.5822 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 186138.5822 | 243777.8524 | -57639.2702 | -23.6442 | OK
12 | 11 kV Shibu Market Feeder (F7) | B841B | 11 |  | DHK66624 | 1 | 2396.07 | 2398.8 | 2.73 | 60000 |  | 163800 | 165612.896 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 165612.896 | 311443.8071 | -145830.9111 | -46.8241 | CHECK
13 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 |  | HA060300286-03 | 1 | 6365.598 | 7639.081 | 1273.483 | 1000 |  | 1273483 | 1287577.5801 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 1287577.5801 | 1300740.5246 | -13162.9446 | -1.012 | OK
14 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 |  | DHK66626 | 1 | 4543.46 | 4574 | 30.54 | 60000 |  | 1832400 | 1852680.5287 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 1852680.5287 | 2054924.3814 | -202243.8527 | -9.8419 | OK
15 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK6622 | 1 | 4277.24 | 4295.85 | 18.61 | 60000 |  | 1116600 | 1128958.2396 | Matuail |  |  |  | 0 | 1128958.2396 | 1266941.3122 | -137983.0726 | -10.891 | OK
16 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 |  | DHKA2187 | 1 | 131.7799 | 137.5179 | 5.738 | 60000 |  | 344280 | 348090.4019 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 348090.4019 | 342400.7167 | 5689.6851 | 1.6617 | OK
17 | 11 kV Bhuighor Bazar |  | 11 |  | HA021100861-02 | 1 | 3332.199 | 4204.39 | 872.191 | 1000 |  | 872191 | 881844.1841 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 881844.1841 | 1074012.4568 | -192168.2727 | -17.8926 | OK
18 | 11 kV Tokkar Math Feeder | B8416 | 11 |  | HA021200298-02 | 1 | 83283.485 | 83870.096 | 586.611 | 1000 |  | 586611 | 593103.4586 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 593103.4586 | 658390.1923 | -65286.7337 | -9.9161 | OK
19 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 |  | XA575922 | 1 | 249.9 | 259.6 | 9.7 | 1000 |  | 9700 | 9807.3571 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 9807.3571 | 17235.2398 | -7427.8827 | -43.0971 | CHECK
16 | 33/0.415 KV Transformer, AT-1 |  | 0.415 |  | 2001123043119 | 1 | 7626.4 | 7684.5 | 58.1 | 160 |  | 9296 | 9398.8857 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 9398.8857 | 7772.9924 | 1625.8934 | 20.9172 | OK
17 | 33/0.415 KV Transformer, AT-2 |  | 0.415 |  | 2001123043157 | 1 | 4726.8 | 4727.8 | 1 | 160 |  | 160 | 161.7708 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 161.7708 | 1854.5521 | -1692.7813 | -91.2771 | CHECK
|  |  | 10: Total | 14610832.7526 | 14450894 | 14610832.7526 | 1.1068
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 4136957.5661
[6 empty] | Shyampur | at 33 KV level |  | 357651.0584
[6 empty] | Fatullah | at 33 KV level |  | 3170500.1559
[6 empty] | Matuail | at 33 KV level |  | 6945723.9721
[6 empty] | Total = |  |  | 14610832.7526 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 7233760 | 12916480 | 5682720 | 1 | 0 | 5682720 | 5651340.6992
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 |  | 00000154 | 1 | 6792000 | 14770080 | 7978080 | 1 | From Downstream | 7978080 | 7934025.9956
|  |  | 10: Total | 0 | 13660800 | 13585366.6949
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder |  | 33 |  | 00000079 | 1 | 363851200 | 371159552 | 7308352 | 1 | 7308352
7 | 33 kV Matuail-1 Feeder |  | 33 |  | 00000114 | 1 | 295190176 | 300832640 | 5642464 | 1 | 5642464
|  |  | 7: 0; 8: 0; 10: Total | 12950816 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000075 | 1 | 378491040 | 385883776 | 7392736 | 1 |  | 7392736
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000156 | 1 | 280624576 | 286184640 | 5560064 | 1 |  | 5560064
|  |  | 10: Total |  | 12952800
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 13585366.6949; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 13585366.6949
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 13585366.6949 | 33 KV TX HV Side |  | 12952800
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 632566.6949
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 4.656%
| TOTAL IMPORT |  | 4: 13585366.6949
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming |  | 11 |  | 00000144 | 1 | 377131200 | 384503584 | 7372384 | 1 | 7372384 |  | 7758118.9673
18 | 11 kV T-1 Incoming |  | 11 |  | 00000054 | 1 | 278964128 | 284501644 | 5537516 | 1 | 5537516 |  | 5827247.7276
|  |  | 7: 0; 8: 0; 10: Total | 12909900 |  | 13585366.6949
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Godnail (F16) | A8963 | 11 |  | 00000109 | 1 | 32205162 | 33556120 | 1350958 | 1 |  | 1350958 | 1350455.4719 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1350455.4719 | 1608130.1776 | -257674.7057 | -16.0232 | OK
2 | 11 kV M. Circus (F15) | B796C | 11 |  | 00000123 | 1 | 114200200 | 115576320 | 1376120 | 1 |  | 1376120 | 1375608.1121 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1375608.1121 | 1875844.4545 | -500236.3424 | -26.6673 | OK
3 | 11 kV Wapderpool (F14) | B723W | 11 |  | 00000190 | 1 | 59257536 | 60232292 | 974756 | 1 |  | 974756 | 974393.4111 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 974393.4111 | 927244.3035 | 47149.1076 | 5.0849 | OK
4 | 11 kV Chowdhury Bari (F13) | A896C | 11 |  | 00000191 | 1 | 107236336 | 109195976 | 1959640 | 1 |  | 1959640 | 1958911.0549 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 1958911.0549 | 2117617.9441 | -158706.8892 | -7.4946 | OK
5 | 11 kV Ailpara (F12) | B7966 | 1 |  | 00000192 | 1 | 61060412 | 62774568 | 1714156 | 1 |  | 1714156 | 1713518.3698 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 1713518.3698 | 2091231.2297 | -377712.8599 | -18.0617 | OK
6 | 11 kV Spare (F11) |  | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) |  | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) |  | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) |  | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | A8962H | 11 |  | 00000197 | 1 | 19720952 | 20884910 | 1163958 | 1 |  | 1163958 | 1163525.0319 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1163525.0319 | 1070830.7575 | 92694.2745 | 8.6563 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 |  | 00000198 | 1 | 4290309 | 4304189 | 13880 | 1 |  | 13880 | 13874.8369 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 13874.8369 | 49416.8148 | -35541.9779 | -71.9228 | CHECK
12 | 11 kV Lucky Bazar (F5) | B796Z | 11 |  | 00000199 | 1 | 93619848 | 94930648 | 1310800 | 1 |  | 1310800 | 1310312.4098 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1310312.4098 | 1175901.2838 | 134411.126 | 11.4305 | OK
13 | 11 kV Enayetnagar (F4) | A896Y | 11 |  | 00000200 | 1 | 36816152 | 37943668 | 1127516 | 1 |  | 1127516 | 1127096.5876 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1127096.5876 | 1294647.5791 | -167550.9915 | -12.9418 | OK
14 | 11 kV Bhuiyapara (F3) | A896V | 11 |  | 00000201 | 1 | 70774584 | 71863984 | 1089400 | 1 |  | 1089400 | 1088994.766 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1088994.766 | 1494739.0596 | -405744.2937 | -27.1448 | OK
15 | 11 kV Arambagh (F2) | B796D | 11 |  | 00000202 | 1 | 12144210 | 12975328 | 831118 | 1 |  | 831118 | 830808.8415 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 830808.8415 | 965266.6711 | -134457.8296 | -13.9296 | OK
16 | 11 kV Spare (F1) |  | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 |  | 0.415 |  | 00000204 | 1 | 1782.91 | 1806.93 | 24.02 | 100 |  | 2402 | 2401.1065 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 2401.1065 | 2999.8723 | -598.7658 | -19.9597 | OK
18 | 11/0.415 kV Aux. Transformer-2 |  | 0.415 |  | 00000205 | 1 | 61.17 | 61.17 | 0 | 100 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0 | 1.0135 | -1.0135 | -100 | CHECK
|  |  | 10: Grand Total | 12909900 | 12914704 | 12909900 | -0.037198
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 6220917.0877
[6 empty] | Siddirgonj | at 33 KV level |  | 6688982.9123
[6 empty] | Total = |  |  | 12909900 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.26 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side |  | 10: Total | 0 | 0 | 0
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 785.87 | 806.7 | 20.83 | 360000 | 0 | 7498800 | 7496438.1732
0 | 0 |  | 33 | Backup | 041808904262 | 1 | 785.88 | 806.72 | 20.84 | 360000 | 0 | 7502400 | 7500037.0394
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 530.58 | 538.24 | 7.66 | 360000 | 0 | 2757600 | 2756731.4646
0 | 0 |  | 33 | Backup | 041808904258 | 1 | 530.78 | 538.44 | 7.66 | 360000 | 0 | 2757600 | 2756731.4646
|  |  | 10: Total | 0 | 10256400 | 10253169.6378
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) |  | 33 | Digital | DHK60875 | 1 | 381161.7 | 412093.1 | 30931.4 | 240 | 7423536
9 | 33 kV New Fatulla-2 |  | 33 | Digital | DHK2186 | 1 | 375.0002 | 382.6497 | 7.6495 | 360000 | 2753820
|  |  | 7: 0; 8: 0; 10: Total | 10177356 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  | 7: 0; 8: 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60980 | 1 | 29151.7 | 47085.2 | 17933.5 | 240 |  | 4304040
13 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 | Digital | DHK60952 | 1 | 549175.1 | 562262.4 | 13087.3 | 240 |  | 7423536 |  |  | Meter Problem
|  |  | 10: Total |  | 11727576 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 10253169.6378
| New Fatullah 33 kv Side |  | 4: 10253169.6378; 6: 33 KV Net Import; 9=8-7: 10253169.6378 | 33 KV TX HV Side |  | 11727576
[11 empty] | LOSS UNITS=> |  | -1474406.3622
[11 empty] | LOSS % IN => |  | -14.38%
| TOTAL IMPORT |  | 4: 10253169.6378
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 | New | DHK61060 | 1 | 240545.7 | 263239.1 | 22693.4 | 180 | 4084812 |  | 4219700.7728 | [7 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 | New | DHK61054 | 1 | 450703.8 | 468149.2 | 17445.4 | 180 | 3140172 |  | 3243866.8451 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming |  | 11 | New | DHK60924 | 1.1 | 493401 | 499226.3 | 5825.3 | 180 | 1153409.4 |  | 1191497.3165 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming |  | 11 | New | DHK61051 | 1 | 29404.3 | 46593.4 | 17189.1 | 90 | 1547019 |  | 1598104.7034 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 9925412.4 |  | 10253169.6378 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | A717R | 11 | New |  | 1 | 78084808 | 78664998 | 580190 | 1 |  | 580190 | 588603.6575 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 588603.6575 | 632806.8774 | -44203.2199 | -6.9853 | OK
15 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 91204625 | 91785899 | 581274 | 1 |  | 581274 | 589703.3771 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 589703.3771 | 831073.3841 | -241370.0069 | -29.0432 | OK
16 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 228288.5 | 241520.1 | 13231.6 | 60 |  | 793896 | 805408.7269 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 805408.7269 | 1363029.7869 | -557621.06 | -40.9104 | CHECK
17 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 370704.6 | 381113.2 | 10408.6 | 60 |  | 624516 | 633572.4534 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 633572.4534 | 733183.1825 | -99610.7291 | -13.5861 | OK
19 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 94344.4 | 115281.3 | 20936.9 | 60 |  | 1256214 | 1274431.057 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1274431.057 | 1605474.9303 | -331043.8733 | -20.6197 | OK
20 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 102086.1 | 110638.4 | 8552.3 | 60 |  | 513138 | 520579.2992 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 520579.2992 | 625630.6419 | -105051.3427 | -16.7913 | OK
23 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 676359 | 688661.1 | 12302.1 | 60 |  | 738126 | 748829.9751 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 748829.9751 | 893996.3722 | -145166.397 | -16.2379 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 576544.9 | 596465.2 | 19920.3 | 60 |  | 1195218 | 1212550.5201 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1212550.5201 | 1055367.6461 | 157182.874 | 14.8937 | OK
25 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 882166.7 | 902017.3 | 19850.6 | 60 |  | 1191036 | 1208307.8746 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 1208307.8746 | 283482.5341 | 924825.3405 | 326.2372 | FAULT
26 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Dhaka Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 3152340 | 3643474 | 491134 | 1 |  | 491134 | 498256.2069 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 498256.2069 | 624571.0906 | -126314.8837 | -20.2243 | OK
28 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 26146252 | 26354730 | 208478 | 1 |  | 208478 | 211501.2553 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 211501.2553 | 266805.7231 | -55304.4678 | -20.7284 | OK
29 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 16501720 | 16948242 | 446522 | 1 |  | 446522 | 452997.2635 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 452997.2635 | 377407.5066 | 75589.7569 | 20.0287 | OK
30 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 18251948 | 18736168 | 484220 | 1 |  | 484220 | 491241.9432 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 491241.9432 | 609177.2667 | -117935.3235 | -19.3598 | OK
35 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 1166208 | 2168854.1 | 1002646.1 | 1 |  | 1002646.1 | 1017186.028 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1017186.028 | 997122.6577 | 20063.3704 | 2.0121 | OK
37 | 11 kV Spare Feeder |  | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 |  | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 10253169.6378 | 10106608.1 | 10253169.6378 | 1.4502
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 7912107.8774
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1178307.0346
[6 empty] | Sytalakhya | at 33 KV level |  | 1162754.7258
[6 empty] | Total = |  |  | 10253169.6378 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder |  | 132 | Export | 041808902770 | 1 | 126.99 | 126.99 | 0 | 1200000 |  | 0
|  |  | 132 |  | 041808904227 | 1 | 126.99 | 126.99 | 0 | 1200000 |  | 0
|  |  | 132 | Import | 041808902770 | 1 | 282.88 | 310.11 | 27.23 | 1200000 | 32676000
|  |  | 132 |  | 041808904227 | 1 | 282.84 | 310.07 | 27.23 | 1200000 | 32676000
3 | 132 kV Haripur Feeder |  | 132 | Export | 041808902766 | 1 | 122.48 | 154.26 | 31.78 | 1200000 |  | 38136000
|  |  | 132 |  | 041808904230 | 1 | 122.53 | 154.32 | 31.79 | 1200000 |  | 38148000
|  |  | 132 | Import | 041808902766 | 1 | 720.75 | 720.98 | 0.23 | 1200000 | 276000
|  |  | 132 |  | 041808904230 | 1 | 721 | 721.23 | 0.23 | 1200000 | 276000
4 | 132 kV Aggreko Feeder |  | 132 | Export | 041808902768 | 1 | 31.37 | 32.9 | 1.53 | 1200000 |  | 1836000
|  |  | 132 |  | 041808904219 | 1 | 31.37 | 32.9 | 1.53 | 1200000 |  | 1836000
|  |  | 132 | Import | 041808902768 | 1 | 268.85 | 272.78 | 3.93 | 1200000 | 4716000
|  |  | 132 |  | 041808904219 | 1 | 268.85 | 272.78 | 3.93 | 1200000 | 4716000
6 | 132 kV Shyampur-2 Feeder |  | 132 | Export | 041808902793 | 1 | 120.76 | 120.76 | 0 | 1200000 |  | 0
|  |  | 132 |  | 041808904278 | 1 | 120.78 | 120.78 | 0 | 1200000 |  | 0
|  |  | 132 | Import | 041808902793 | 1 | 275.62 | 303.07 | 27.45 | 1200000 | 32940000
|  |  | 132 |  | 041808904278 | 1 | 275.68 | 303.13 | 27.45 | 1200000 | 32940000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 70608000 | 39972000
|  |  | 7: 0; 8: 0; 10: Net Total | 30636000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| FATULLAH 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | Export | 041808902767 | 1 | 648.14 | 662.29 | 14.15 | 1200000 |  | 16980000
|  |  | 132 | Export | 041808904228 | 1 | 647.97 | 662.12 | 14.15 | 1200000 |  | 16980000
5 | 132/33 kV, 80/120 MVA GT-2 |  | 132 | Export | 041808902792 | 1 | 501.51 | 512.88 | 11.37 | 1200000 |  | 13644000
|  |  | 132 | Export | 041808904251 | 1 | 501.32 | 512.68 | 11.36 | 1200000 |  | 13632000
|  |  | 10: Total |  | 30624000
| 132 KV IMPORT |  | 4: KWH | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 4: 30636000 | 132 KV NET IMPORT |  | 30636000
| IMPORT-2 | [9 empty] | 132/33 KV GT LV Side |  | 30470400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 165600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.5405%
| 132 KV TOTAL IMPORT |  | 4: 30636000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902796 | 1 | 1075.17 | 1098.63 | 23.46 | 720000 | 16891200
|  |  | 33 | Backup | 041808904255 | 1 | 1075.17 | 1098.63 | 23.46 | 720000 | 16891200
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902802 | 1 | 832.28 | 851.14 | 18.86 | 720000 | 13579200
|  |  | 33 | Backup | 041808904281 | 1 | 832.07 | 850.92 | 18.85 | 720000 | 13572000
|  |  | 7: 0; 8: 0; 10: Total | 30470400 |  | 0
| FATULLAH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902868 | 1 | 857.74 | 875.26 | 17.52 | 240000 |  | 4204800 | 4203475.6535 |  | 8762039.4331 | New Fatullah 33/11 kv ss | 0.42912 | 33/11 kV, 28/35 MVA T-1 (=H5) | 4203475.6535 | 5278494.5321 | -1075018.8786 | -20.366 | OK
|  |  | 33 | Backup | 041808904277 | 1 | 857.19 | 874.69 | 17.5 | 240000 |  | 4200000 | 4198677.1654 |  |  |  |  | 0 | 4198677.1654 | 5276096.3065 | -1077419.1412 | -20.4208 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902824 | 1 | 763.13 | 782.13 | 19 | 240000 |  | 4560000 | 4558563.7795 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 4558563.7795 | 6098687.6852 | -1540123.9057 | -25.2534 | OK
|  |  | 33 | Backup | 041808904267 | 1 | 763 | 782.01 | 19.01 | 240000 |  | 4562400 | 4560963.0236 |  |  |  |  | 0 | 4560963.0236 | 6096289.4596 | -1535326.436 | -25.1846 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8764800 | 8762039.4331 |  |  |  |  | 33 KV Feeders | 8762039.4331 | 11377182.2174 | -2615142.7843 | -22.9859 | OK
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 820.3 | 834.74 | 14.44 | 360000 |  | 5198400 | 5196762.7087 |  | 11455190.9291 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 5196762.7087 | 6622699.9775 | -1425937.2688 | -21.5311 | OK
|  |  | 33 | Backup | 041808904220 | 1 | 819.89 | 834.33 | 14.44 | 360000 |  | 5198400 | 5196762.7087 |  |  |  |  | 0 | 5196762.7087 | 6619102.6391 | -1422339.9304 | -21.4884 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) |  | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 785.87 | 806.7 | 20.83 | 360000 |  | 7498800 | 7496438.1732 |  | 10253169.6378 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 7496438.1732 | 7968104.5357 | -471666.3624 | -5.9194 | OK
|  |  | 33 | Backup | 041808904262 | 1 | 785.88 | 806.72 | 20.84 | 360000 |  | 7502400 | 7500037.0394 |  |  |  |  | 0 | 7500037.0394 | 7964507.1973 | -464470.1579 | -5.8318 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 600.23 | 617.62 | 17.39 | 360000 |  | 6260400 | 6258428.2205 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 6258428.2205 | 7986091.2276 | -1727663.0071 | -21.6334 | OK
|  |  | 33 | Backup | 041808904219 | 1 | 600.6 | 617.99 | 17.39 | 360000 |  | 6260400 | 6258428.2205 |  |  |  |  | 0 | 6258428.2205 | 7993285.9044 | -1734857.6839 | -21.7039 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 530.58 | 538.24 | 7.66 | 360000 |  | 2757600 | 2756731.4646 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 2756731.4646 | 3349122.0419 | -592390.5773 | -17.6879 | OK
|  |  | 33 | Backup | 041808904258 | 1 | 530.78 | 538.44 | 7.66 | 360000 |  | 2757600 | 2756731.4646 |  |  |  |  | 0 | 2756731.4646 | 3349122.0419 | -592390.5773 | -17.6879 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) |  | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 21715200 | 21708360.5669 |  |  |  |  | 0 | 21708360.5669 | 25926017.7826 | -4217657.2157 | -16.268 | OK
|  |  | 9=8-7: Grand Total | 30470400 | 30480000 | 30470400 | -0.031496
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902832 | 1 | 821.16 | 837.92 | 16.76 | 250000 | 4190000 |  | 4198164.1194
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902765 | 1 | 730.45 | 748.67 | 18.22 | 250000 | 4555000 |  | 4563875.3136
|  |  | 7: 0; 8: 0; 10: Total | 8745000 |  | 8762039.4331
| FATULLAH 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) |  | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 1032.15 | 1055.91 | 23.76 | 60000 |  | 1425600 | 1431717.6049 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 1431717.6049 | 1967161.5939 | -535443.989 | -27.2191 | OK
7 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 519.22 | 535.1 | 15.88 | 60000 |  | 952800 | 956888.7023 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 956888.7023 | 1278564.8268 | -321676.1246 | -25.1592 | OK
8 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 572.34 | 579.48 | 7.14 | 60000 |  | 428400 | 430238.3712 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 430238.3712 | 517800.713 | -87562.3419 | -16.9104 | OK
9 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1292.66 | 1315.52 | 22.86 | 60000 |  | 1371600 | 1377485.8774 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1377485.8774 | 1511304.5202 | -133818.6427 | -8.8545 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) |  | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) |  | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 227.78 | 239.06 | 11.28 | 60000 |  | 676800 | 679704.3175 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 679704.3175 | 841952.3789 | -162248.0614 | -19.2705 | OK
16 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 105.2 | 110.15 | 4.95 | 60000 |  | 297000 | 298274.501 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 298274.501 | 420374.7949 | -122100.2939 | -29.0456 | OK
17 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1220.63 | 1249.92 | 29.29 | 60000 |  | 1757400 | 1764941.4414 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1764941.4414 | 2561940.8101 | -796999.3687 | -31.1092 | OK
18 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1490.06 | 1520.31 | 30.25 | 60000 |  | 1815000 | 1822788.6174 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 1822788.6174 | 2278082.5795 | -455293.9622 | -19.9858 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 8762039.4331 | 8724600 | 8762039.4331 | 0.42912
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 8762039.4331
[6 empty] | Total = |  |  | 8762039.4331 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 820.3 | 834.74 | 14.44 | 360000 | 0 | 5198400 | 5196762.7087
0 | 0 |  | 33 | Backup | 041808904220 | 1 | 819.89 | 834.33 | 14.44 | 360000 | 0 | 5198400 | 5196762.7087
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 600.23 | 617.62 | 17.39 | 360000 | 0 | 6260400 | 6258428.2205
0 | 0 |  | 33 | Backup | 041808904219 | 1 | 600.6 | 617.99 | 17.39 | 360000 | 0 | 6260400 | 6258428.2205
| DAPA 33 KV SIDE (RECEIVING) |  | 10: Total | 0 | 11458800 | 11455190.9291
5 | 33 kV New Fatullah Incoming Circuit-2 |  | 33 | Import |  | 1 | 215665744 | 221931632 | 6265888 | 1 | 6265888
6 | 33 kV Shyampur Incoming Circuit |  | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder |  | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  |  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 |  | 33 | Import |  | 1 | 294787360 | 299998880 | 5211520 | 1 | 5211520
|  |  | 7: 0; 8: 0; 10: Total | 11477408 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DAPA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) |  | 33 | Export | 00000135 | 1 | 307227584 | 313493280 | 6265696 | 1 |  | 6265696
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) |  | 33 | Export | 00000193 | 1 | 296447040 | 301654336 | 5207296 | 1 |  | 5207296
|  |  | 10: Total |  | 11472992 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 4: 11455190.9291; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11472992
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 11472992 | 33 KV TX HV SIDE |  | 11472992
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 11455190.9291
11 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000035 | 1 | 294762144 | 299945344 | 5183200 | 1 | 5183200 |  | 5205428.2331
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000143 | 1 | 305916544 | 312157344 | 6240800 | 1 | 6240800 |  | 6267563.7669
|  |  | 7: 0; 8: 0; 10: Total | 11424000 |  | 11472992
| DAPA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV Katherpol Feeder | B8919 | 11 |  | 00000031 | 1 | 71074344 | 72541944 | 1467600 | 1 |  | 1467600 | 1480200.745 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 1480200.745 | 1780543.7815 | -300343.0365 | -16.8681 | OK
12 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | B8918 | 11 |  | 00000032 | 1 | 71909144 | 73690624 | 1781480 | 1 |  | 1781480 | 1796775.704 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1796775.704 | 2128228.6671 | -331452.9631 | -15.5741 | OK
14 | 11 kV Shiachar Feeder | B891G | 11 |  | 00000030 | 1 | 73433864 | 74275736 | 841872 | 1 |  | 841872 | 849100.2736 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 849100.2736 | 1635781.9984 | -786681.7248 | -48.0921 | CHECK
15 | 11 kV Sastapur Feeder | B8913 | 11 |  | 00000106 | 1 | 72296704 | 72643024 | 346320 | 1 |  | 346320 | 349293.4873 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 349293.4873 | 488573.0611 | -139279.5738 | -28.5074 | OK
17 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | B891JA | 11 |  | 00000172 | 1 | 5879505 | 5879505 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 0 | 247329.6416 | -247329.6416 | -100 | CHECK
19 | 11 kV Hajibari Feeder |  | 11 |  | 00000105 | 1 | 164959 | 853557 | 688598 | 1 |  | 688598 | 694510.2702 | Fatullah |  |  |  | 11 kV Hajibari Feeder | 694510.2702 | 168427.36 | 526082.9102 | 312.35 | FAULT
21 | 11 kV Railine Feeder |  | 11 |  |  | 1 | 195799 | 1103037 | 907238 | 1 |  | 907238 | 915027.503 | Fatullah |  |  |  | 11 kV Railine Feeder | 915027.503 | 200012.7891 | 715014.7139 | 357.4845 | FAULT
22 | 11 kV Lalpur Feeder | B8911 | 11 |  | 00000044 | 1 | 86381512 | 87083784 | 702272 | 1 |  | 702272 | 708301.6746 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 708301.6746 | 2338751.8857 | -1630450.2112 | -69.7145 | CHECK
23 | 11 kV Kotaler Bag Feeder | B8912 | 11 |  | 00000050 | 1 | 91574936 | 92944416 | 1369480 | 1 |  | 1369480 | 1381238.2912 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 1381238.2912 | 2006422.5038 | -625184.2125 | -31.1592 | OK
24 | 11 kV Idrakpur Feeder | B8915 | 11 |  | 00000021 | 1 | 80022008 | 80799760 | 777752 | 1 |  | 777752 | 784429.7423 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 784429.7423 | 983847.2999 | -199417.5576 | -20.2692 | OK
25 | 11 kV Isdair Feeder | B8914 | 11 |  | 00000029 | 1 | 43086456 | 43612092 | 525636 | 1 |  | 525636 | 530149.0861 | Fatullah |  |  |  | 11 kV Isdair Feeder | 530149.0861 | 624149.3274 | -94000.2413 | -15.0605 | OK
26 | 11 kV Shah Fateullah Express |  | 11 |  | 0000051 | 1 | 4770108 | 6178065 | 1407957 | 1 |  | 1407957 | 1420045.653 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 1420045.653 | 1937861.0792 | -517815.4262 | -26.721 | OK
27 | 11 kV Boubazar Feeder |  | 11 |  | 00000151 | 1 | 23719 | 579438 | 555719 | 1 |  | 555719 | 560490.3774 | Fatullah |  |  |  | 11 kV Boubazar Feeder | 560490.3774 | 24229.4565 | 536260.9209 | 2213.2602 | FAULT
28 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKF 7522 | 1 | 3239 | 3273 | 34 | 100 |  | 3400 | 3429.1922 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 3429.1922 | 4801.1487 | -1371.9564 | -28.5756 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 11472992 | 11375324 | 11472992 | 0.8586
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 11472992
[6 empty] | Total = |  |  | 11472992 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 |  | 132 | IMPORT | 50501730 | 1 | 2986.08 | 3017.096 | 31.016 | 480000 | 0 | 14887680
2 | Tranformer 1 |  | 132 |  | 80505634 | 1 | 8576.821 | 8605.814 | 28.993 | 480000 | 0 | 13916640
3 | Tranformer 2 |  | 132 |  | 80505637 | 1 | 8529.331 | 8558.906 | 29.575 | 480000 | 0 | 14196000
4 | MI CEMENT |  | 132 |  | 38992489 (New) | 1 | 375.942 | 400.476 | 24.534 | 480000 | 0 | 11776320
|  |  | 9=8-7: Total Import/Export | 0 | 54776640
|  |  | 10: Net Total | 54776640
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 375.928 | 400.459 | 24.531 | 480000 |  | 11774880
|  |  | 132 | DPDC | 16402670 | 1 | 1900.898 | 1925.387 | 24.489 | 480000 |  | 11754720
|  |  | 10: Total |  | 11754720
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 43021920
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 54776640; 6: EXPORT TO OTHER S/S; 9=8-7: 11754720 | 132 KV NET IMPORT |  | 43021920
| IMPORT-2 |  | 6: 132 KV NET IMPORT for Sitalakhya 33/11 KV; 9=8-7: 43021920 | GT (33 KV Side) |  | 42911963
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 109957
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2556%
| 132 KV TOTAL IMPORT |  | 4: 54776640
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A030701130-03 | 1 | 47153.34 | 61135.175 | 13981.835 | 1000 | 13981835
|  |  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  |  | 33 | DPDC | BD001913 | 1 | 1883.7495 | 1913.1242 | 29.3747 | 480000 | 14099856
18 | 132/33 KV Transformer, GT-3 Incoming |  | 33 | DPDC | BD001915 | 1 | 2978.555 | 3009.4514 | 30.8964 | 480000 | 14830272
|  |  | 7: 0; 8: 0; 10: Total | 42911963 |  | 0
| SITALAKHYA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 |  | 33 | DPDC | H/A030701089-03 | 1 | 7336.072 | 14264.44 | 6928.368 | 1000 |  | 6928368 | 6933713.3883 |  | 10413376.9557 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 6933713.3883 | 8707799.8827 | -1774086.4943 | -20.3735 | OK
|  |  | 33 | P. Cell | 08993597 | 1 | 6020.945 | 6049.816 | 28.871 | 240000 |  | 6929040 | 6934385.9068 |  |  |  |  | 0 | 6934385.9068 | 8692199.4065 | -1757813.4998 | -20.2229 | OK
13 | 33/11 KV Transformer T-4 |  | 33 | DPDC | H/A030701087-03 | 1 | 89862.416 | 93339.397 | 3476.981 | 1000 |  | 3476981 | 3479663.5673 |  |  |  |  | 33/11 KV Transformer T-4 | 3479663.5673 | 3935376.8061 | -455713.2388 | -11.5799 | OK
|  |  | 33 | P. Cell | 08993925 | 1 | 5760.334 | 5779.676 | 19.342 | 180000 |  | 3481560 | 3484246.1001 |  |  |  |  | 0 | 3484246.1001 | 3930420.2434 | -446174.1433 | -11.3518 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 10405349 | 10413376.9557 |  |  |  |  | 33 KV Feeders | 10413376.9557 | 12643176.6888 | -2229799.7331 | -17.6364 | OK
10 | 33 KV Char Syedpur Feeder (F1) |  | 33 | DPDC | H/A030701083-03 | 1 | 42622.667 | 42622.667 | 0 | 1000 |  | 0 | 0 |  | 360.2777 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Char Syedpur Feeder (F1) |  | 33 | P. Cell | 08993596 | 1 | 2186.832 | 2186.834 | 0.002 | 180000 |  | 360 | 360.2777 |  |  |  |  | 33 KV Char Syedpur Feeder (F1) | 360.2777 | 179.9478 | 180.3299 | 100.2123 | FAULT
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 63140.766 | 73168.276 | 10027.51 | 1000 |  | 10027510 | 10035246.4446 |  | 10035246.4446 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 10035246.4446 | 11021616.9142 | -986370.4696 | -8.9494 | OK
| 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9975.444 | 10031.213 | 55.769 | 180000 |  | 10038420 | 10046164.8619 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 10046164.8619 | 11003269.2347 | -957104.3728 | -8.6984 | OK
14 | 33 KV Shah Cement Feeder (F2) |  | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993926 | 1 | 2303.686 | 2303.686 | 0 | 180000 |  | 0 | 0 |  | 11301870.9198 | Khanpur 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 46039.096 | 51950.566 | 5911.47 | 1000 |  | 5911470 | 5916030.8292 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 5916030.8292 | 7653416.6363 | -1737385.8071 | -22.7008 | OK
|  |  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1729.3965 | 1761.5361 | 32.1396 | 180000 |  | 5785128 | 5789591.3535 |  | 11157009.242 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 5789591.3535 | 6713529.188 | -923937.8345 | -13.7623 | OK
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 537.5595 | 559.9832 | 22.4237 | 240000 |  | 5381688 | 5385840.0907 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 5385840.0907 | 6905293.5796 | -1519453.4889 | -22.0042 | OK
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1419.6294 | 1441.9764 | 22.347 | 240000 |  | 5363280 | 5367417.8885 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 5367417.8885 | 6662579.9625 | -1295162.074 | -19.4393 | OK
21 | 33/0.415 KV Transformer AT-1 |  | 0.415 | DPDC | 2001123043108 | 1 | 6583.1 | 6601.2 | 18.1 | 160 |  | 2896 | 2898.2343 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 2898.2343 | 3710.9239 | -812.6896 | -21.8999 | OK
22 | 33/0.415 KV Transformer AT-2 |  | 0.415 | DPDC | 2001123043171 | 1 | 4786.1 | 4793.6 | 7.5 | 160 |  | 1200 | 1200.9258 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 1200.9258 | 0 | 1200.9258 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 32473532 | 32498586.0443 |  |  |  |  | 0 | 32498586.0443 | 38960327.1522 | -6461741.1079 | -16.5854 | OK
|  |  | 9=8-7: Grand Total | 42911963 | 42878881 | 42911963 | 0.077152
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 4099.1602
[6 empty] | Total = |  |  | 4099.1602
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | DHK 9372 | 1 | 74991.6605 | 113270.3368 | 38278.6763 | 180 | 6890161.734 |  | 6926254.8594 |  |  |  |  | 33/11 kV Transformer, T-3 Incoming | 6926254.8594 | 8701056.5654 | -1774801.706 | -20.3975 | OK
10 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | DHK 9368 | 1 | 90959.8491 | 110231.7963 | 19271.9472 | 180 | 3468950.496 |  | 3487122.0963 |  |  |  |  | 33/11 kV Transformer, T-4 Incoming | 3487122.0963 | 3942120.1234 | -454998.0271 | -11.542 | OK
|  |  | 7: 0; 8: 0; 10: Total | 10359112.23 |  | 10413376.9557
| SITALAKHYA 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Bholail Feeder (F-3) | E330V | 11 |  | DHK 9335 | 1 | 15853.9958 | 44011.8562 | 28157.8604 | 60 |  | 1689471.624 | 1692519.7695 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 1692519.7695 | 2733762.095 | -1041242.3255 | -38.0883 | OK
4 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 |  | DHK 9336 | 1 | 34520.8952 | 52704.3896 | 18183.4944 | 60 |  | 1091009.664 | 1092978.0641 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1092978.0641 | 1031371.3237 | 61606.7404 | 5.9733 | OK
5 | 11 kV Baburail Feeder (F-5) | A730R | 11 |  | DHK 9322 | 1 | 11014.0086 | 31398.6709 | 20384.6623 | 60 |  | 1223079.738 | 1225286.419 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 1225286.419 | 1578860.4613 | -353574.0422 | -22.3943 | OK
6 | 11 kV Goghchar Feeder (F-1) | E330G | 11 |  | DHK 9323 | 1 | 93927.0295 | 108385.2865 | 14458.257 | 60 |  | 867495.42 | 869060.5556 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 869060.5556 | 1024995.3245 | -155934.7689 | -15.2132 | OK
7 | 11 kV Norshinghopur (F-2) | E330N | 11 |  | DHK 9365 | 1 | 92611.445 | 116984.1799 | 24372.7349 | 60 |  | 1462364.094 | 1465002.492 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1465002.492 | 1580945.372 | -115942.88 | -7.3338 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 |  | DHK 9367 | 1 | 27485.0632 | 37817.1704 | 10332.1072 | 60 |  | 619926.432 | 621044.9036 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 621044.9036 | 738106.28 | -117061.3765 | -15.8597 | OK
11 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 |  | H/A030701125-03 | 1 | 73961.68 | 74111.207 | 149.527 | 1000 |  | 149527 | 149796.7767 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 149796.7767 | 178278.8721 | -28482.0954 | -15.9761 | OK
12 | 11 kV Kashipur Feeder (F-7) | E317K | 11 |  | H/A030800169-03 | 1 | 41289.934 | 42354.858 | 1064.924 | 1000 |  | 1064924 | 1066845.3364 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1066845.3364 | 1250959.2711 | -184113.9347 | -14.7178 | OK
13 | 11 kV Spare Feeder (F-6) |  | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | A730D | 11 |  | H/A030701098-03 | 1 | 82381 | 83078.66 | 697.66 | 1000 |  | 697660 | 698918.7185 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 698918.7185 | 844950.6763 | -146031.9578 | -17.2829 | OK
15 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 |  | H/A030800205-03 | 1 | 98073.528 | 98948.784 | 875.256 | 1000 |  | 875256 | 876835.1373 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 876835.1373 | 909298.0281 | -32462.8908 | -3.5701 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 |  | H/A030701091-03 | 1 | 57053.47 | 57707.379 | 653.909 | 1000 |  | 653909 | 655088.7829 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 655088.7829 | 771648.9846 | -116560.2017 | -15.1053 | OK
|  |  | 10: Total | 10413376.9557 | 10394622.972 | 10413376.9557 | 0.18042
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 1026631.914
[6 empty] | Sytalakhya | at 33 KV level |  | 7462539.9042
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1924205.1375
[6 empty] | Total = |  |  | 10413376.9557 | 0
MI CEMENT 132/33 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 375.928 | 400.459 | 24.531 | 480000 | 11774880 |  | 11776320
|  |  | 132 | DPDC | 16402670 | 1 | 1900.898 | 1925.387 | 24.489 | 480000 | 11754720
2 | 132/33 kV Transformer (132 kV Side) |  | 132 |  | 06502030 | 1 | 3782.742 | 3832.024 | 49.282 | 240000 |  | 11827680
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 11754720 | 11827680
[7 empty] | 0 | 0 |  | Net Total
[7 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) |  | 33 |  | 14718815 | 1 | 7465.912 | 7563.377 | 97.465 | 120000 | 11695800
4 | 33 kV Outgoing Feeder-1 |  | 33 |  | 11745824 | 1 | 3816.137 | 3855.682 | 39.545 | 120000 |  | 4745400
5 | 33 kV Outgoing Feeder-2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 6950400
|  |  | 9=8-7: Total Import/Export | 11695800 | 11695800
|  |  | 9=8-7: Net Total | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 11776320
[6 empty] | Total = |  |  | 11776320
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1729.3965 | 1761.5361 | 32.1396 | 180000 | 0 | 5785128 | 5789591.3535
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1419.6294 | 1441.9764 | 22.347 | 240000 | 0 | 5363280 | 5367417.8885
|  |  | 10: Total | 0 | 11148408 | 11157009.242
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder |  | 33 |  | 00000188 | 1 | 342601120 | 348389376 | 5788256 | 1 | 5788256
7 | 33 kV Shitalakhya-1 Feeder |  | 33 |  | 00000153 | 1 | 341183872 | 346567680 | 5383808 | 1 | 5383808
|  |  | 7: 0; 8: 0; 10: Total | 11172064 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000116 | 1 | 347282176 | 353069056 | 5786880 | 1 |  | 5786880
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000194 | 1 | 336301184 | 341682944 | 5381760 | 1 |  | 5381760
|  |  | 10: Total |  | 11168640
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 11157009.242; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11157009.242
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 11157009.242 | 33 KV TX HV SIDE |  | 11168640
[11 empty] | LOSS UNITS=> |  | -11630.758
[11 empty] | LOSS % IN => |  | -0.1042%
| TOTAL IMPORT |  | 4: 11157009.242
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming |  | 11 |  | 00000055 | 1 | 334699168 | 340054176 | 5355008 | 1 | 5355008 |  | 5397386.5402
19 | 11 kV T-2 Incoming |  | 11 |  | 00000017 | 1 | 344656768 | 350371168 | 5714400 | 1 | 5714400 |  | 5759622.7018
|  |  | 7: 0; 8: 0; 10: Total | 11069408 |  | 11157009.242
| MONDOLPARA 11 KV SIDE |  | 7: 0; 8: 0
9 | 11 kV River View | B793U | 11 |  | 00000061 | 1 | 9679440 | 10379476 | 700036 | 1 |  | 700036 | 704573.4596 | N.Gonj (East) |  |  |  | 11 kV River View | 704573.4596 | 834579.227 | -130005.7675 | -15.5774 | OK
10 | 11 kV Railgate B.B. Road | B793F | 11 |  | 00000191 | 1 | 25321458 | 25747338 | 425880 | 1 |  | 425880 | 428640.4484 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 428640.4484 | 541179.2554 | -112538.807 | -20.7951 | OK
11 | 11 kV DIT | A722D | 11 |  | 00000174 | 1 | 148263920 | 150230640 | 1966720 | 1 |  | 1966720 | 1979467.7908 | N.Gonj (West) |  |  |  | 11 kV DIT | 1979467.7908 | 2494646.9299 | -515179.1392 | -20.6514 | OK
12 | 11 kV Dalpatti | B7227 | 11 |  | 00000182 | 1 | 6596464 | 7271502 | 675038 | 1 |  | 675038 | 679413.4287 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 679413.4287 | 717766.0913 | -38352.6626 | -5.3433 | OK
13 | 11 kV South Chasara | A793S | 11 |  | 00000043 | 1 | 104270584 | 105849784 | 1579200 | 1 |  | 1579200 | 1589435.9823 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 1589435.9823 | 2086962.942 | -497526.9597 | -23.8398 | OK
14 | 11 kV Spare |  | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | B7225 | 11 |  | 00000019 | 1 | 237799 | 253199 | 15400 | 1 |  | 15400 | 15499.819 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 15499.819 | 24295.6359 | -8795.8169 | -36.2033 | OK
17 | 11 kV Spare |  | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | B7229 | 11 |  | 00000173 | 1 | 9690976 | 10873413 | 1182437 | 1 |  | 1182437 | 1190101.2631 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1190101.2631 | 1131312.8093 | 58788.4538 | 5.1965 | OK
20 | 11 kV Nitaigonj | B722G | 11 |  | 00000189 | 1 | 61101972 | 61732128 | 630156 | 1 |  | 630156 | 634240.5147 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 634240.5147 | 721749.3286 | -87508.8139 | -12.1245 | OK
21 | 11 kV Shahid Nagar | E323T | 11 |  | 00000020 | 1 | 62024488 | 62912208 | 887720 | 1 |  | 887720 | 893473.9806 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 893473.9806 | 1062004.8821 | -168530.9015 | -15.8691 | OK
22 | 11 kV Bangla Bazar | A793Z | 11 |  | 00000139 | 1 | 75510416 | 76543656 | 1033240 | 1 |  | 1033240 | 1039937.2052 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1039937.2052 | 1307258.0634 | -267320.8582 | -20.449 | OK
23 | 11 kV Vogoban Gonj | B7228 | 11 |  | 00000181 | 1 | 4220269 | 4607869 | 387600 | 1 |  | 387600 | 390112.327 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 390112.327 | 454174.5319 | -64062.2049 | -14.1052 | OK
24 | 11 kV Tanbazar | B722I | 11 |  | 00000138 | 1 | 52421992 | 53049952 | 627960 | 1 |  | 627960 | 632030.2808 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 632030.2808 | 804089.0085 | -172058.7277 | -21.398 | OK
25 | 11 kV SS Road | A793O | 11 |  | 00000175 | 1 | 70578344 | 71549224 | 970880 | 1 |  | 970880 | 977173.0031 | N.Gonj (West) |  |  |  | 11 kV SS Road | 977173.0031 | 1192851.3622 | -215678.359 | -18.0809 | OK
26 | 11 kV Spare |  | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 |  | 0.415 |  |  | 1 | 2673.12 | 2701.84 | 28.72 | 100 |  | 2872 | 2890.6156 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 2890.6156 | 3239.0829 | -348.4673 | -10.7582 | OK
28 | 33/0.415 kV Auxiliary-2 |  | 0.415 |  |  | 1 | 3.98 | 4.17 | 0.19 | 100 |  | 19 | 19.1232 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 19.1232 | 0 | 19.1232 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 11157009.242 | 11085158 | 11157009.242 | 0.64818
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 893473.9806
[6 empty] | N.Gonj (East) | at 33 KV level |  | 4674611.5413
[6 empty] | N.Gonj (West) | at 33 KV level |  | 5588923.7201
[6 empty] | Total = |  |  | 11157009.242 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 63140.766 | 73168.276 | 10027.51 | 1000 | 0 | 10027510 | 10035246.4446
0 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9975.444 | 10031.213 | 55.769 | 180000 | 0 | 10038420 | 10046164.8619
| MATUAIL 33 KV SIDE |  | 10: Total |  | 10027510 | 10035246.4446
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 88663.917 | 94441.355 | 5777.438 | 1000 | 0 | 5777438 | 5745535.6778
0 | 0 |  | 33 | P. Cell | 08993580 | 1.5 | 1436.51 | 1457.985 | 21.475 | 180000 | 0 | 5798250 | 5766232.7564
|  |  | 10: Total | 0 | 5777438 | 5745535.6778
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) |  | 10: Total |  | 15804948 | 15780782.1223
3 | 33 kV Matuail Feeder |  | 33 | Digital | ABB03910 | 1 | 86520.8375 | 87540.6743 | 1019.8368 | 4000 | 4079347
6 | 33 kV Shitalakhya Feeder |  | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  |  | 33 | New | DHKA2199 | 1 | 4377.8099 | 4429.2833 | 51.4734 | 180000 | 9265212
|  |  | 7: 0; 8: 0; 10: Total | 13344559 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 20/28 MVA Transformer-3 |  | 33 | Old | HA021100524-02 | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 33 | New | DHKA2200 | 1 | 4411.5177 | 4442.8358 | 31.3181 | 180000 |  | 5637258
7 | 33/11 kV, 10/14 MVA Transformer-2 |  | 33 | Old | HA030800199-03 | 1 | 61346.715 | 66246.379 | 4899.664 | 1000 |  | 4899664
|  |  | 33 | New | DHKA2195 | 1 | 4704.6652 | 4755.8011 | 51.1359 | 90000 |  | 4602231
8 | 33/11 kV, 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03909 | 1 | 447034.8626 | 451872.3232 | 4837.4606 | 1000 |  | 4837460.62
|  |  | 10: Total |  | 15374382.62
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 10035246.4446; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 15780782.1223
| MATUAIL 33 KV SIDE |  | 4: 5745535.6778; 6: 33 KV NET IMPORT; 9=8-7: 15780782.1223 | 33 KV TX HV SIDE |  | 15374382.62
[11 empty] | LOSS UNITS=> |  | 406399.5023
[11 empty] | LOSS % IN => |  | 2.575%
| TOTAL IMPORT |  | 4: 15780782.1223
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | 51426632 | 1 | 3970994 | 4025346 | 54352 | 90 | 4891680 |  | 5548708.0437
16 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | DHKA2192 | 1 | 4090.3268 | 4145.1014 | 54.7746 | 90000 | 4929714 |  | 5591850.5963
22 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426630 | 1 | 4288196 | 4333649 | 45453 | 90 | 4090770 |  | 4640223.4823
|  |  | 7: 0; 8: 0; 10: Total | 13912164 |  | 15780782.1223
| NARAYANGONJ BSCIC 11 KV SIDE |  | 7: 0; 8: 0
10 | 11 kV Masdair Feeder (F-8) | A727M | 11 |  | XA575914 | 1 | 225307.3 | 227537.4 | 2230.1 | 1000 |  | 2230100 | 2222097.8958 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 2222097.8958 | 2875854.6768 | -653756.781 | -22.7326 | OK
11 | 11 kV Narayangonj (F-7) | A727N | 11 |  | XA575915 | 1 | 171294.6 | 172653 | 1358.4 | 1000 |  | 1358400 | 1353525.753 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1353525.753 | 1448790.766 | -95265.0131 | -6.5755 | OK
12 | 11 kV Nearest Feeder (F-6) | A727B | 11 |  | XA575927 | 1 | 109777.2 | 110754.8 | 977.6 | 1000 |  | 977600 | 974092.1497 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 974092.1497 | 1208994.3676 | -234902.218 | -19.4296 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 |  | XA575916 | 1 | 121288 | 122392.1 | 1104.1 | 1000 |  | 1104100 | 1100138.239 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1100138.239 | 1251647.0882 | -151508.8492 | -12.1048 | OK
14 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 |  | XA575912 | 1 | 58701.7 | 59670.9 | 969.2 | 1000 |  | 969200 | 965722.2908 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 965722.2908 | 1164739.667 | -199017.3762 | -17.0869 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 |  | DHK66615 | 1 | 262.4459 | 277.9005 | 15.4546 | 60000 |  | 927273.06 | 923945.7941 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 923945.7941 | 979158.7412 | -55212.9471 | -5.6388 | OK
17 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 |  | XA575920 | 1 | 235307.8 | 236532 | 1224.2 | 1000 |  | 1224200 | 1219807.293 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 1219807.293 | 774957.8804 | 444849.4126 | 57.403 | FAULT
18 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 |  | XA575929 | 1 | 24939.8 | 25997.9 | 1058.1 | 1000 |  | 1058100 | 1054303.2974 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1054303.2974 | 1209394.8627 | -155091.5653 | -12.8239 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 |  | HA021100913-02 | 1 | 46643.437 | 48995.357 | 2351.92 | 1000 |  | 2351920 | 2343480.778 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 2343480.778 | 2210541.3216 | 132939.4564 | 6.0139 | OK
20 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 |  | HA021100682-02 | 1 | 69020.842 | 71092.782 | 2071.94 | 1000 |  | 2071940 | 2064505.4097 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2064505.4097 | 2336119.5415 | -271614.1318 | -11.6267 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 |  | HA021100455-02 | 1 | 61478.231 | 63033.857 | 1555.626 | 1000 |  | 1555626 | 1550044.0614 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1550044.0614 | 1810143.413 | -260099.3517 | -14.369 | OK
23 | 11/0.415 KV Transformer,AT-1 |  | 0.415 | Analog | 2001123043161 | 1 | 4048.1 | 4100.5 | 52.4 | 160 |  | 8384 | 8353.9163 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 8353.9163 | 8426.4154 | -72.4991 | -0.86038 | OK
24 | 11/0.415 KV Transformer,AT-2 |  | 0.415 | Analog | 2001123043118 | 1 | 4122.3 | 4127.1 | 4.8 | 160 |  | 768 | 765.2442 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 765.2442 | 2274.8118 | -1509.5675 | -66.3601 | CHECK
|  |  | 10: Grand Total | 15780782.1223 | 15837611.06 | 15780782.1223 | -0.35882
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 1219807.293
[6 empty] | N.Gonj (West) | at 33 KV level |  | 14560974.8294
[6 empty] | Total = |  |  | 15780782.1223 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) |  | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  |  | IMPORT | 42627811 | 1 | 306.632 | 317.589 | 10.957 | 960000 | 0 | 10518720
| Madonganj to Charsyedpur-2 |  |  |  | 42627824 | 1 | 237.944 | 256.733 | 18.789 | 960000 | 0 | 18037440
|  |  | 9=8-7: Total Import/Export | 0 | 28556160 | 0
|  |  | 10: Net Total | 28556160
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 |  | 132 |  | 041808902821 | 1 | 252.73 | 261.51 | 8.78 | 1200000 | 10536000
|  |  | 132 |  | 041808904222 | 3 | 83.66 | 86.56 | 2.9 | 1200000 | 10440000
| 132 kV Madanganj Circuit-2 |  | 132 |  | 041808902865 | 1 | 190.32 | 205.33 | 15.01 | 1200000 | 18012000
|  |  | 132 |  | 041808904240 | 1 | 190.39 | 205.4 | 15.01 | 1200000 | 18012000
|  |  | 8: 0; 9=8-7: Total Import/Export | 28548000 | 0 | 0
|  |  | 8: 0; 9=8-7: Net Total | 28548000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| 132 kV Shah Cement |  | 132 | EXPORT | 042003953369 | 1 | 33.07 | 45.6 | 12.53 | 1200000 |  | 15036000 |  | Sytalakhya | Main Meter
| 133 kV Shah Cement |  | 132 |  | 042003953379 | 1 | 33.1 | 45.64 | 12.54 | 1200000 |  | 15048000 |  |  | Check Meter
|  |  | 8: 0; 10: Total |  | 15036000
| CHAR SYEDPUR 132 KV SIDE |  | 8: 0
4 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | EXPORT | 041808902864 | 1 | 203.03 | 212.59 | 9.56 | 1200000 |  | 11472000
|  |  | 132 |  | 041808904224 | 1 | 202.89 | 212.59 | 9.7 | 1200000 |  | 11640000
7 | 132/33 kV, 80/120 MVA GT-2 |  | 132 |  | 041808902848 | 1 | 206.93 | 208.58 | 1.65 | 1200000 |  | 1980000
|  |  | 132 |  | 041808904244 | 1 | 207.03 | 208.68 | 1.65 | 1200000 |  | 1980000
|  |  | 10: Total | 28488000 | 13452000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 28556160; 6: Sytalakhya NOCS; 9=8-7: 15036000 | 132 KV NET IMPORT |  | 13452000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 13452000 | 132/33 KV LV SIDE |  | 13363200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 88800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.6601%
| 132 KV TOTAL IMPORT |  | 4: 28556160
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902859 | 1 | 336.17 | 352.03 | 15.86 | 720000 | 11419200 |  | 11495081.8966
|  |  | 33 | Backup | 041808904285 | 1 | 336.17 | 352.03 | 15.86 | 720000 | 11419200 |  | 11495081.8966
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902812 | 1 | 343.17 | 345.87 | 2.7 | 720000 | 1944000 |  | 1956918.1034
|  |  | 33 | Backup | 041808904276 | 1 | 343.19 | 345.89 | 2.7 | 720000 | 1944000 |  | 1956918.1034
|  |  | 7: 0; 8: 0; 10: Total | 13363200 |  | 13452000
| CHAR SYEDPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902875 | 1 | 250.91 | 260.4 | 9.49 | 240000 |  | 2277600 | 2274731.3995 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2274731.3995 | 2301420.1682 | -26688.7687 | -1.1597 | OK
|  |  | 33 | Backup | 041808904241 | 1 | 250.83 | 260.31 | 9.48 | 240000 |  | 2275200 | 2272334.4222 |  |  |  |  | 0 | 2272334.4222 | 2301420.1682 | -29085.746 | -1.2638 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902844 | 3 | 72.62 | 74.85 | 2.23 | 240000 |  | 1605600 | 1603577.7727 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 1603577.7727 | 2241362.2306 | -637784.458 | -28.4552 | OK
|  |  | 33 | Backup | 041808904259 | 3 | 72.62 | 74.85 | 2.23 | 240000 |  | 1605600 | 1603577.7727 |  |  |  |  | 0 | 1603577.7727 | 2241362.2306 | -637784.458 | -28.4552 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 3883200 | 3878309.1721 |  |  |  |  | 33 KV Feeders | 3878309.1721 | 4542782.3988 | -664473.2267 | -14.627 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) |  | 33 | Main | 041808902866 | 1 | 375.17 | 395.51 | 20.34 | 360000 |  | 7322400 | 7313177.5551 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 7313177.5551 | 5005228.5182 | 2307949.0369 | 46.1108 | FAULT
|  |  | 33 | Backup | 041808904221 | 1 | 375.35 | 395.7 | 20.35 | 360000 |  | 7326000 | 7316773.021 |  |  |  |  | 0 | 7316773.021 | 5005228.5182 | 2311544.5028 | 46.1826 | FAULT
10 | 33 kV Delta Agro Premier Cement (=H2) |  | 33 | Main | 041808902876 | 1 | 130.36 | 135.43 | 5.07 | 360000 |  | 1825200 | 1822901.19 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 1822901.19 | 2659365.4762 | -836464.2862 | -31.4535 | OK
|  |  | 33 | Backup | 041808904237 | 1 | 130.36 | 135.43 | 5.07 | 360000 |  | 1825200 | 1822901.19 |  |  |  |  | 0 | 1822901.19 | 2659365.4762 | -836464.2862 | -31.4535 | OK
11 | 33 kV Crown Cement-1 (=H3) |  | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Crown Cement-1 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) |  | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904232 | 1 | 43.8 | 43.8 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Outgoing Feeder-6 (=H12) |  | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Crown Cement-2 (=H13) |  | 33 | Main | 041808902857 | 1 | 0.06 | 1.03 | 0.97 | 360000 |  | 349200 | 348760.1882 | Sytalakhya |  |  |  | 33 kV Crown Cement-2 (=H13) | 348760.1882 | 0 | 348760.1882 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904234 | 1 | 0.06 | 1.03 | 0.97 | 360000 |  | 349200 | 348760.1882 |  |  |  |  | 0 | 348760.1882 | 0 | 348760.1882 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) |  | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904242 | 1 | 499.7 | 499.7 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/0.415 kV Transformer AT-1 |  |  |  |  | 1 | 1995.97 | 2047.93 | 51.96 | 1 |  | 51.96 | 51.8946 | [5 empty] | 51.8946 | 79.6068
|  |  | 10: Total |  | 9496851.96 | 9484890.8279 |  |  |  |  | 0 | 9484890.8279 | 7664673.6012 | 1820217.2267 | 23.7481 | OK
|  |  | 9=8-7: Grand Total | 13363200 | 13380051.96 | 13363200 | -0.12595
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902756 | 1 | 239.75 | 248.41 | 8.66 | 250000 | 2165000 |  | 1713649.4056
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902778 | 1.72 | 155.57 | 161.93 | 6.36 | 250000 | 2734800 |  | 2164659.7665
|  |  | 7: 0; 8: 0; 10: Total | 4899800 |  | 3878309.1721
| CHAR SYEDPUR 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 |  | 041808902749 | 1 | 484.37 | 496.62 | 12.25 | 60000 |  | 735000 | 738639.4179 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 738639.4179 | 945964.8168 | -207325.3989 | -21.9168 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) |  | 11 |  | 041808902759 | 1 | 515.1 | 534.17 | 19.07 | 60000 |  | 1144200 | 1149865.6081 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1149865.6081 | 1335585.1962 | -185719.5881 | -13.9055 | OK
7 | 11 kV RMU Hygene Express -1 (=F4) |  | 11 |  | 041808902748 | 1 | 0.02 | 6.51 | 6.49 | 60000 |  | 389400 | 391328.1487 | Sytalakhya |  |  |  | 11 kV RMU Hygene Express -1 (=F4) | 391328.1487 | 0 | 391328.1487 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) |  | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) |  | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 |  | 041808902786 | 1 | 379.9 | 398.35 | 18.45 | 60000 |  | 1107000 | 1112481.409 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1112481.409 | 1382793.8004 | -270312.3914 | -19.5483 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 |  | 041808902789 | 1 | 230.47 | 238.53 | 8.06 | 60000 |  | 483600 | 485994.5884 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 485994.5884 | 878438.5854 | -392443.997 | -44.6752 | CHECK
15 | 11 kV Outgoing Feeder-12 (=F10) |  | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) |  | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) |  | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) |  | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907976 | 1 | 1995.97 | 2047.93 | 51.96 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 3878309.1721 | 3859200 | 3878309.1721 | 0.49516
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 13363148.1054
[6 empty] | Total = |  |  | 13363148.1054 | 9484838.9333
33 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 39708 | 40621 | 913 | 6000 | 0 | 5478000 | 5486137.0838
FROM Kazla 33 KV SIDE
| 33 kV Amulia Feeder | 0 | 33 | Main | 41812909523 | 1 | 23.56 | 23.61 | 0.05 | 360000 | 0 | 18000 | 17880.5799
|  |  | 10: Total |  | 5496000 | 5504017.6637
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving |  | 33 |  | 30799095 | 1 | 1403.57 | 1434.44 | 30.87 | 180000 | 5556600
| 33 kV Kazla |  |  |  | 952612101236 | 1 | 48.11 | 48.21 | 0.1 | 240000 | 24000
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 5580600 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AMULIA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transformer, T-1 |  | 33 |  | DHKA2194 | 1 | 412.1093 | 423.675 | 11.5657 | 240000 |  | 2775768
4 | 33/11 kV Transformer, T-2 |  | 33 |  | DHKA2198 | 1 | 589.4324 | 601.1122 | 11.6798 | 240000 |  | 2803152
|  |  | 10: Total |  | 5578920 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 4: 5504017.6637; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5504017.6637
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 5504017.6637 | 33 KV TX HV SIDE |  | 5578920
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -74902.3363
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.361%
| TOTAL IMPORT |  | 4: 5504017.6637
11 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | HA021100461-02 | 1 | 31065070 | 33869999 | 2804929 | 1 | 2804929 |  | 2765631.7618
11 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | HA021100478-02 | 1 | 99450702 | 102227998 | 2777296 | 1 | 2777296 |  | 2738385.9019
|  |  | 7: 0; 8: 0; 10: Total | 5582225 |  | 5504017.6637
| AMULIA 11 KV SIDE |  | 7: 0; 8: 0
5 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 73017725 | 73439809 | 422084 | 1 |  | 422084 | 422316.016 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 422316.016 | 938316.3983 | -516000.3823 | -54.9922 | CHECK
6 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 19053674 | 19988191 | 934517 | 1 |  | 934517 | 935030.696 | Demra |  |  |  | 11 kV Kayetpara Feeder | 935030.696 | 1013109.0793 | -78078.3832 | -7.7068 | OK
8 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 2915432 | 3438978 | 523546 | 1 |  | 523546 | 523833.7888 | Demra |  |  |  | 11 kV Paity Feeder | 523833.7888 | 523224.3018 | 609.4869 | 0.11649 | OK
9 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 73339160 | 75271966 | 1932806 | 1 |  | 1932806 | 1933868.447 | Demra |  |  |  | 11 kV Bamuil Feeder | 1933868.447 | 2094431.1329 | -160562.6859 | -7.6662 | OK
12 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 16625684 | 17115669 | 489985 | 1 |  | 489985 | 490254.3406 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 490254.3406 | 575953.3679 | -85699.0274 | -14.8795 | OK
13 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra |  | 1 | 52278896 | 52490923 | 212027 | 1 |  | 212027 | 212143.5494 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 212143.5494 | 120786.3374 | 91357.212 | 75.6354 | FAULT
14 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 16211336 | 17272226 | 1060890 | 1 |  | 1060890 | 1061473.1622 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1061473.1622 | 1171776.4455 | -110303.2833 | -9.4133 | OK
15 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5578920 | 5575855 | 5578920 | 0.054939
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Mugdapara | at 33 KV level |  | 912570.3566
[6 empty] | Demra | at 33 KV level |  | 4666349.6434
[6 empty] | Total = |  |  | 5578920 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MOGBAZAR T&T 11 KV SIDE | [9 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder |  | 33 |  | 8993 841 | 1 | 17.275 | 41.562 | 24.287 | 36000 | 1484 | 874332 | 875816 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 875816 | 3079152 | -2203336 | -71.5566 | CHECK
13 | 33 kV Mondol Para (Premire cement) Feeder |  | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 874332 | 875816 | 0.16973
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 875816
[6 empty] | Total = |  |  | 875816 | 0
Note on H481: User: Meter was faulty and New meter is installed properly in 12.07.23
Note on I481: User: Meter was faulty and New meter is installed properly in 12.07.23

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 |  | 132 | IMPORT | 50147584 | 1 | 3356.292 | 3386.62 | 30.328 | 1920000 | 0 | 58229760
| Maniknagar-2 |  | 132 |  | 50147585 | 1 | 3347.682 | 3377.577 | 29.895 | 1920000 | 0 | 57398400
|  |  | 9=8-7: Total Import/Export | 0 | 115628160
|  |  | 10: Net Total | 115628160
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 115628160
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 |  | 132 | EXPORT | 06604331 | 1 | 8942.66 | 8967.94 | 25.28 | 480000 |  | 12134400 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 |  | 132 |  | 06604334 | 1 | 9042.13 | 9067.6 | 25.47 | 480000 |  | 12225600
| 132kV Motijheel Circuit-1 |  | 132 |  | 06604332 | 1 | 1864.13 | 1870.84 | 6.71 | 1440000 |  | 9662400
| 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1.07 | 1659.62 | 1665.94 | 6.32 | 1440000 |  | 9737856
| 132 kV Kazla Circuit-1 |  | 132 |  | ABB03905 | 1 | 870310 | 893515 | 23205 | 1000 |  | 23205000
| 132 kV Kazla Circuit-2 |  | 132 |  | ABB03904 | 1 | 660390 | 685705 | 25315 | 1000 | From Downstream | 20577600 |  |  | R Phase PT Missing
| 132 KV Metro Rail -1 |  | 132 |  | 42627805 | 1 | 0.239 | 0.239 | 0 | 480000 |  | 0 |  | Motijheel | KVARH Reading Shown Seperately
| 132 KV Metro Rail -2 |  | 132 |  | 42627793 | 1 | 2.303 | 2.335 | 0.032 | 480000 |  | 15360 |  | Motijheel
0
|  |  | 7: 0; 8: 0; 10: Total |  | 87558216
| MANIKNAGAR 132 KV SIDE |  | 7: 0; 8: 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 13528000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) |  | 132 | Export | ABB03903 | 1 | 401094 | 416096 | 15002 | 1000 |  | 15002000 |  |  | 28530000
|  |  | 10: Total | 116088216 | 28530000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 4: 115628160; 6: EXPORT TO OTHER S/S; 9=8-7: 87542856 | 132 KV NET IMPORT |  | 28069944
| IMPORT-2 |  | 6: Motijheel NOCS; 9=8-7: 15360 | 33 KV NET IMPORT |  | 28564000
| IMPORT-3 |  | 6: 132 KV NET IMPORT; 9=8-7: 28069944 | LOSS UNITS=>(132 HV-33 LV) |  | -494056
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.76%
| 132 KV TOTAL IMPORT |  | 4: 115628160
KVARH For Metro Rail
|  | Previous | 3: Present; 4: Total KVARH; 5: Remark
| 132 KV Metro Rail -1 | 3.517 | 3: 6.724; 4: 1539360; 5: Leading PF
| 132 KV Metro Rail -2 | 6.57 | 3: 9.778; 4: 1539840; 5: Leading PF
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) |  | 33 | Digital | ABB03907 | 1 | 139276 | 152804 | 13528 | 1000 | 13528000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) |  | 33 | Digital | ABB03906 | 1 | 308336 | 323372 | 15036 | 1000 | 15036000
|  |  | 7: 0; 8: 0; 10: Total | 28564000
| Maniknagar 33 kV SIDE |  | 7: 0; 8: 0 |  |  |  |  | 4126429.8988
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 7595724.5533 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK00121 | 1 | 11269.2 | 11852.2 | 583 | 4444 | From Downstream | 2590852 | 2597991.1093 |  |  |  |  | 0 | 2597991.1093 | 3428826.2363 | -830835.127 | -24.2309 | OK | 4161360.0577
7 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Digital | ABB03913 | 1 | 395820 | 398312 | 2492 | 2000 |  | 4984000 | 4997733.444 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 4997733.444 | 5784978.6812 | -787245.2372 | -13.6084 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 7574852 | 7595724.5533 |  |  |  |  | 33 KV Feeders | 7595724.5533 | 9213804.9175 | -1618080.3642 | -17.5615 | OK
2 |  |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 6698406.7828 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder |  | 33 |  | DHK86054 | 1 | 2529.5 | 2543.3 | 13.8 | 270000 |  | 3726000 | 3736267.0169 |  |  |  |  | 33kV Motijheel-1 Feeder | 3736267.0169 | 3624980.8693 | 111286.1475 | 3.07 | OK
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 5678656 | 5694303.573 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 5694303.573 | 7095485.6643 | -1401182.0912 | -19.7475 | OK
|  |  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 10988852.6469 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 | Digital | ABB03918 | 1 | 314865 | 317505 | 2640 | 2000 |  | 5280000 | 5294549.0739 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 5294549.0739 | 6532520.7231 | -1237971.6492 | -18.9509 | OK
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 280390 | 281573 | 1183 | 2000 |  | 2366000 | 2372519.5282 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 2372519.5282 | 3695847.8549 | -1323328.3267 | -35.8058 | OK
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 292050 | 293527 | 1477 | 2000 |  | 2954000 | 2962139.7659 |  | 2372519.5282 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 2962139.7659 | 3679900.2914 | -717760.5254 | -19.5049 | OK
12 | 33kV Water Treatment Plant |  | 33 | Digital | 80379618 | 1 | 22050 | 22503 | 453 | 2000 |  | 906000 | 908496.4888 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 908496.4888 | 468459.6796 | 440036.8093 | 93.9327 | FAULT
|  |  | 10: Total |  | 20910656 | 20968275.4467 |  |  |  |  | 0 | 20968275.4467 | 25097195.0825 | -4128919.6358 | -16.4517 | OK
|  |  | 9=8-7: Grand Total | 28564000 | 28485508 | 28564000 | 0.27555
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 908496.4888
[6 empty] | Total = |  |  | 908496.4888 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 |  | 11 | Import | 6604357 | 1 | 5597.97 | 5628.96 | 30.99 | 160000 | 4958400 |  | 4988923.4887
9 | 11kV 10/14 MVA Transformer T-1 |  | 11 | Import | DHK00121 | 1 | 11269.2 | 11852.2 | 583 | 4444 | 2590852 |  | 2606801.0646
|  |  | 7: 0; 8: 0; 10: Total | 7549252 |  | 7595724.5533
| MANIKNAGAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nearest Feeder | B2110N | 11 |  | HA021101060-02 | 1 | 81633988 | 82699513 | 1065525 | 1 |  | 1065525 | 1080819.1243 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1080819.1243 | 1313766.3455 | -232947.2212 | -17.7313 | OK
2 | 11kV Spare |  | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | B2110C | 11 |  | HA021100937-02 | 1 | 80522134 | 81055406 | 533272 | 1 |  | 533272 | 540926.3753 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 540926.3753 | 688739.9281 | -147813.5528 | -21.4614 | OK
4 | 11 kV R K Mission Road Feeder | B2110R | 11 |  | HA021101035-02 | 1 | 20022438 | 21016003 | 993565 | 1 |  | 993565 | 1007826.239 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1007826.239 | 1205722.8029 | -197896.564 | -16.4131 | OK
5 | 11 kV Janapath Feeder | B2110J | 11 |  | HA021100864-02 | 1 | 35472819 | 36804184 | 1331365 | 1 |  | 1331365 | 1350474.8865 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 1350474.8865 | 1592664.201 | -242189.3145 | -15.2066 | OK
6 | 11 kV Dhalpur Feeder | B2110D | 11 |  | HA021100851-02 | 1 | 89539002 | 90114728 | 575726 | 1 |  | 575726 | 583989.7432 | Maniknagar |  | 11 |  | 11 kV Dhalpur Feeder | 583989.7432 | 804304.6434 | -220314.9002 | -27.392 | OK
7 | 11kV WTP | B2110O | 11 |  | X0599387 | 1 | 2506.6 | 2925.9 | 419.3 | 1000 |  | 419300 | 425318.4663 | Maniknagar |  | 9 |  | 11kV WTP | 425318.4663 | 252567.7657 | 172750.7006 | 68.3978 | FAULT
10 | 11kV Kamalapur Water pumping | B2110F | 11 |  | HA021100474-02 | 1 | 7681209 | 7702929 | 21720 | 1 |  | 21720 | 22031.7603 | Maniknagar |  | 9.6667 |  | 11kV Kamalapur Water pumping | 22031.7603 | 24054.7854 | -2023.0251 | -8.4101 | OK
11 | 11 kV Wasa Road Feeder | B2110A | 11 |  | HA021001011-02 | 1 | 28031254 | 29194203 | 1162949 | 1 |  | 1162949 | 1179641.5099 | Maniknagar |  |  |  | 11 kV Wasa Road Feeder | 1179641.5099 | 1724950.0596 | -545308.5497 | -31.613 | OK
12 | 11kV Sutikhalpar Feeder | B2110K | 11 |  | HA021101047-02 | 1 | 82588606 | 83966144 | 1377538 | 1 |  | 1377538 | 1397310.6355 | Maniknagar |  |  |  | 11kV Sutikhalpar Feeder | 1397310.6355 | 1698787.5503 | -301476.9148 | -17.7466 | OK
13 | 11kV Spare |  | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare |  | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare |  | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 |  | 0.415 |  | AH14044078 | 1 | 424443.4 | 427058.1 | 2614.7 | 1 |  | 2614.7 | 2652.2304 | Maniknagar |  |  |  | Axuxilary -1 | 2652.2304 | 3860.1372 | -1207.9068 | -31.2918 | OK
| Axuxilary -2 |  | 0.415 |  | AH14044072 | 1 | 392725.7 | 397392.3 | 4666.6 | 1 |  | 4666.6 | 4733.5825 | Maniknagar |  |  |  | Axuxilary -2 | 4733.5825 | 4282.1807 | 451.4018 | 10.5414 | OK
13 | AT-1 |  | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 7595724.5533 | 7488241.3 | 7595724.5533 | 1.4354
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 7595724.5533
[6 empty] | Total = |  |  | 7595724.5533 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder |  | 33 | 0 | DHK86054 | 1 | 2529.5 | 2543.3 | 13.8 | 270000 | 0 | 3726000 | 3736267.0169
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 292050 | 293527 | 1477 | 2000 | 0 | 2954000 | 2962139.7659
|  |  | 10: Total | 0 | 6680000 | 6698406.7828
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 |  | 33 | Import | DHK86054 | 1 | 2529.5 | 2543.3 | 13.8 | 270000 | 3726000
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) |  | 33 | Import | DHK68120 | 1 | 2207.29 | 2218.14 | 10.85 | 270000 | 2929500 |  |  |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 6655500 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33kV Biddyut Bhaban Circuit |  | 33 | Export |  | 1 | 503691 | 507718 | 4027 | 600 | Estimated | 1258980.3 |  |  | From remote end
|  |  | 7: 0; 8: 0; 10: Total |  | 1258980.3
[7 empty] | 0 | 0
| Motijheel 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK86053 | 1 | 3060.96 | 3078 | 17.04 | 180000 |  | 3067200
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) |  | 33 | Export | DHK86055 | 1 | 2388.21 | 2400.87 | 12.66 | 180000 |  | 2278800
|  |  | 10: Total | 6604980.3 | 5346000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 4: 6655500; 6: EXPORT TO OTHER S/S; 9=8-7: 1258980.3 | 33 KV NET IMPORT |  | 5396519.7
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5396519.7 | 33 KV TX HV SIDE |  | 5346000
[11 empty] | LOSS UNITS=> |  | 50519.7
[11 empty] | LOSS % IN => |  | 0.9362%
| TOTAL IMPORT |  | 4: 6655500
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 |  | 11 | Import | DHK86059 | 1 | 3461.47 | 3480.73 | 19.26 | 160000 | 3081600 |  | 3098895.9279 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 |  | 11 | Import | DHK86057 | 1 | 2678.64 | 2692.92 | 14.28 | 160000 | 2284800 |  | 2297623.7721
|  |  | 7: 0; 8: 0; 10: Total | 5366400 |  | 5396519.7
| MOTIJHEEL 11 KV SIDE |  | 7: 0; 8: 0
6 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 |  | DHK86058 | 1 | 1763.67 | 1775.85 | 12.18 | 60000 |  | 730800 | 734202.8494 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 734202.8494 | 859250.5994 | -125047.75 | -14.5531 | OK
7 | 11kV Station Road Feeder | A175H | 11 |  | DHK86075 | 1 | 2382.7 | 2383.68 | 0.98 | 60000 |  | 58800 | 59073.7925 | Motijheel |  |  |  | 11kV Station Road Feeder | 59073.7925 | 80099.6322 | -21025.8397 | -26.2496 | OK
8 | 11kV Box Culvert Road Feeder | A175F | 11 |  | DHK86071 | 1 | 3279.86 | 3303.43 | 23.57 | 60000 |  | 1414200 | 1420784.9886 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1420784.9886 | 1714253.4911 | -293468.5025 | -17.1193 | OK
9 | 11kV Mohamedan Club Feeder | A174V | 11 |  | DHK86062 | 1 | 1734.42 | 1743.1 | 8.68 | 60000 |  | 520800 | 523225.0191 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 523225.0191 | 731212.5511 | -207987.5319 | -28.4442 | OK
10 | 11kV Amina Ahmed Co. |  | 11 |  | DHK95754 | 1 | 122809 | 125374 | 2565 | 60 |  | 153900 | 154616.6099 | Motijheel |  | 267 |  | 11kV Amina Ahmed Co. | 154616.6099 | 203465.202 | -48848.5921 | -24.0083 | OK
11 | 11kV Bangabhaban -1 |  | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  | 16 |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | A175SB | 11 |  | DHK95753 | 1 | 89291 | 93455 | 4164 | 60 |  | 249840 | 251003.3387 | Motijheel |  | 251 |  | 11kV Sonali Bank | 251003.3387 | 265299.6907 | -14296.3521 | -5.3888 | OK
15 | 11kV NCC Bank Feeder | A133S | 11 |  | DHK68123 | 1 | 335.29 | 338.12 | 2.83 | 60000 |  | 169800 | 170590.6456 | Motijheel |  | 83.6667 |  | 11kV NCC Bank Feeder | 170590.6456 | 211778.5729 | -41187.9272 | -19.4486 | OK
16 | 11kV IFIC BANK Feeder |  | 11 |  | DHK68116 | 1 | 426.1 | 431.45 | 5.35 | 60000 |  | 321000 | 322494.6834 | Ramna |  | 99.6667 |  | 11kV IFIC BANK Feeder | 322494.6834 | 395036.8222 | -72542.1387 | -18.3634 | OK
17 | 11kV Arambagh Feeder | A174X | 11 |  | DHK68117 | 1 | 3445.31 | 3459.88 | 14.57 | 60000 |  | 874200 | 878270.5678 | Motijheel |  |  |  | 11kV Arambagh Feeder | 878270.5678 | 488486.393 | 389784.1748 | 79.7943 | FAULT
18 | 11kV Nikotborti Feeder | A175K | 11 |  | DHK68114 | 1 | 1443.26 | 1445.78 | 2.52 | 60000 |  | 151200 | 151904.0378 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 151904.0378 | 214812.6499 | -62908.612 | -29.2853 | OK
19 | 11kV Agrani Bank Feeder | A174O | 11 |  | DHK95756 | 1 | 381960 | 384470 | 2510 | 60 |  | 150600 | 151301.244 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 151301.244 | 192421.1618 | -41119.9178 | -21.3697 | OK
20 | 11kV Bangladesh Bank-2 | A133D | 11 |  | DHK95755 | 1 | 552 | 552 | 0 | 60000 | Estimated | 565004.16 | 567635.0085 | Motijheel | 48 |  |  | 11kV Bangladesh Bank-2 | 567635.0085 | 892846.9338 | -325211.9253 | -36.4242 | OK
21 | 11kV PDB Design Feeder 14 |  | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 |  | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT |  | 0.415 |  | ELIC5429 | 1 | 422280 | 433644 | 11364 | 1 |  | 11364 | 11416.9146 | Motijheel |  |  |  | 11/0.4 kV AT | 11416.9146 | 0 | 11416.9146 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5396519.7 | 5371508.16 | 5396519.7 | 0.46563
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 5074025.0166
[6 empty] | Ramna | at 33 KV level |  | 322494.6834
[6 empty] | Total = |  |  | 5396519.7 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 |  | 132 | 0 | 06604332 | 1 | 1864.13 | 1870.84 | 6.71 | 1440000 | 0 | 9662400
2 | 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1.07 | 1659.62 | 1665.94 | 6.32 | 1440000 | 0 | 9737856
|  |  | 9=8-7: Total Import/Export | 0 | 19400256
|  |  | 10: Net Total | 19400256
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 |  | 132 | Imp/Main | 41812909527 | 1 | 365.39 | 373.43 | 8.04 | 1200000 | 9648000
|  |  | 132 | Imp/Backup | 41812909575 | 1 | 365.48 | 373.53 | 8.05 | 1200000 | 9660000
5 | 132 kV Mniknagar Circuit-2 |  | 132 | Imp/Main | 41812909512 | 1 | 167.5 | 175.1 | 7.6 | 1200000 | 9120000
|  |  | 132 | Imp/Backup | 41812909591 | 1 | 167.54 | 175.14 | 7.6 | 1200000 | 9120000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 18768000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 18768000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1.45 | 41.84 | 43.1 | 1.26 | 1200000 |  | 2192400
|  |  | 132 | Exp/Backup | 41812909570 | 1.45 | 41.84 | 43.1 | 1.26 | 1200000 |  | 2192400
7 | 132 kV Bangabhaban Circuit-2 |  | 132 | Exp/Main | 41812909559 | 1 | 97.87 | 99.74 | 1.87 | 1200000 |  | 2244000
|  |  | 132 | Exp/Backup | 41812909569 | 1 | 97.87 | 99.74 | 1.87 | 1200000 |  | 2244000
|  |  | 7: 0; 8: 0; 10: Total |  | 4436400
| MOTIJHEEL 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41812909509 | 1 | 251.99 | 258.58 | 6.59 | 1200000 |  | 7908000
|  |  | 132 | Exp/Backup | 41812909594 | 1 | 251.99 | 258.58 | 6.59 | 1200000 |  | 7908000
6 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41812909508 | 1 | 141.26 | 146.92 | 5.66 | 1200000 |  | 6792000
|  |  | 132 | Exp/Backup | 41812909592 | 1 | 141.22 | 146.88 | 5.66 | 1200000 |  | 6792000
|  |  | 10: Total | 19136400 | 14700000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 4: 19400256; 6: EXPORT TO OTHER S/S; 9=8-7: 4436400 | 132 KV NET IMPORT |  | 14963856
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 14963856 | 33 KV NET IMPORT |  | 14896800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 67056
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4481%
| 132 KV TOTAL IMPORT |  | 4: 19400256
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41812909543 | 1 | 417.18 | 428.51 | 11.33 | 720000 | 8157600
|  |  | 33 | Backup | 41812909617 | 1 | 417.46 | 428.8 | 11.34 | 720000 | 8164800
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41812909468 | 1 | 232.9 | 242.26 | 9.36 | 720000 | 6739200
|  |  | 33 | Backup | 41812909600 | 1 | 232.86 | 242.21 | 9.35 | 720000 | 6732000
|  |  | 7: 0; 8: 0; 10: Total | 14896800 |  | 0
| MOTIJHEEL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) |  | 33 | Main | 41812909546 | 1 | 144.64 | 149.71 | 5.07 | 240000 |  | 1216800 | 1227878.0036 |  | 3039421.8826 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1227878.0036 | 1547607.8531 | -319729.8495 | -20.6596 | OK
|  |  | 33 | Backup | 41812909616 | 1 | 144.59 | 149.66 | 5.07 | 240000 |  | 1216800 | 1227878.0036 |  |  |  |  | 0 | 1227878.0036 | 1523613.9329 | -295735.9293 | -19.4102 | OK
17 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41812909482 | 1 | 242.77 | 250.25 | 7.48 | 240000 |  | 1795200 | 1811543.879 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 1811543.879 | 2423385.9405 | -611842.0614 | -25.2474 | OK
|  |  | 33 | Backup | 42003953371 | 1 | 242.83 | 250.31 | 7.48 | 240000 |  | 1795200 | 1811543.879 |  |  |  |  | 0 | 1811543.879 | 2425785.3325 | -614241.4534 | -25.3213 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 3012000 | 3039421.8826 |  |  |  |  | 33 KV Feeders | 3039421.8826 | 3970993.7935 | -931571.9109 | -23.4594 | OK
10 | 33 kV Spare Feeder 1 |  | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 |  | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 475.22 | 487.45 | 12.23 | 360000 |  | 4402800 | 4442884.0189 |  | 7327307.4947 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 4442884.0189 | 5675761.8239 | -1232877.8051 | -21.7218 | OK
|  |  | 33 | Backup | 41812909610 | 1 | 475.4 | 488.03 | 12.63 | 360000 |  | 4546800 | 4588195.0252 |  |  |  |  | 0 | 4588195.0252 | 5675761.8239 | -1087566.7987 | -19.1616 | OK
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 287.38 | 294.05 | 6.67 | 360000 |  | 2401200 | 2423061.0307 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 2423061.0307 | 3142003.8505 | -718942.8198 | -22.8817 | OK
|  |  | 33 | Backup | 41812909595 | 1 | 287.5 | 294.17 | 6.67 | 360000 |  | 2401200 | 2423061.0307 |  | 4530070.6227 | Kamlapur Railway 33/11 kv ss |  | 0 | 2423061.0307 | 3181593.8189 | -758532.7881 | -23.8413 | OK
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 121 | 126.8 | 5.8 | 360000 |  | 2088000 | 2107009.5919 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 2107009.5919 | 2677721.4946 | -570711.9027 | -21.3133 | OK
|  |  | 33 | Backup | 41621865733 | 1 | 121.02 | 126.82 | 5.8 | 360000 |  | 2088000 | 2107009.5919 |  |  |  |  | 0 | 2107009.5919 | 2677721.4946 | -570711.9027 | -21.3133 | OK
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 158.77 | 166.71 | 7.94 | 360000 |  | 2858400 | 2884423.4759 |  |  |  |  | 33 kV P & T - 2 Feeder | 2884423.4759 | 3476719.0374 | -592295.5615 | -17.036 | OK
|  |  | 33 | Backup | 41812909598 | 1 | 158.73 | 166.66 | 7.93 | 360000 |  | 2854800 | 2880790.7007 |  |  |  |  | 0 | 2880790.7007 | 3476719.0374 | -595928.3367 | -17.1405 | OK
20 | 33 kV Spare Feeder 9 |  | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 |  | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) |  | 0.415 |  |  | 1 | 1459.01 | 1459.01 | 0 | 300 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 11750400 | 11857378.1174 |  |  |  |  | 0 | 11857378.1174 | 14972206.2065 | -3114828.0891 | -20.8041 | OK
|  |  | 9=8-7: Grand Total | 14896800 | 14762400 | 14896800 | 0.91042
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) |  | 11 |  | 41812909493 | 1 | 137.81 | 142.63 | 4.82 | 250000 | 1205000 |  | 1225942.5501
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) |  | 11 |  | 41812909496 | 1 | 231.96 | 239.09 | 7.13 | 250000 | 1782500 |  | 1813479.3325
|  |  | 7: 0; 8: 0; 10: Total | 2987500 |  | 3039421.8826
| MOTIJHEEL 11 kV SIDE |  | 7: 0; 8: 0
2 | 11 kV Central Weman | A1111CW | 11 |  | 41812909492 | 1 | 188.77 | 194.54 | 5.77 | 60000 |  | 346200 | 352370.1881 | Motijheel |  |  |  | 11 kV Central Weman | 352370.1881 | 559606.8157 | -207236.6276 | -37.0325 | OK
3 | 11 kV Spare Feeder 2 |  | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len |  | 11 |  | 41812909499 | 1 | 308.53 | 317.41 | 8.88 | 60000 |  | 532800 | 542295.8874 | Swamibag |  |  |  | 11 kV K. M. Das Len | 542295.8874 | 679005.6837 | -136709.7962 | -20.1338 | OK
5 | 11 kV Gopibag | A1111GP | 11 |  | 41812909517 | 1 | 46.6 | 48.11 | 1.51 | 60000 |  | 90600 | 92214.7286 | Motijheel |  |  |  | 11 kV Gopibag | 92214.7286 | 109147.45 | -16932.7214 | -15.5136 | OK
6 | 11kV SPICE TV | B1111E | 11 |  | 41812909518 | 1 | 29.4 | 33.3 | 3.9 | 60000 |  | 234000 | 238170.4911 | Narinda |  |  |  | 11kV SPICE TV | 238170.4911 | 196586.015 | 41584.4761 | 21.1533 | OK
7 | 11 kV Spare Feeder 6 |  | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 |  | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 |  | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 |  | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 |  | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 |  | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | A1111SK | 11 |  | 41812909473 | 1 | 413.52 | 419.41 | 5.89 | 60000 |  | 353400 | 359698.5109 | Motijheel |  |  |  | 11 kV South Kamlapur | 359698.5109 | 441413.9968 | -81715.4859 | -18.5122 | OK
14 | 11 kV Spare Feeder 11 |  | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | A1111AC | 11 |  | 41812909514 | 1 | 225.49 | 232.83 | 7.34 | 60000 |  | 440400 | 448249.0781 | Motijheel |  |  |  | 11 kV Answer Camp | 448249.0781 | 582521.7499 | -134272.6718 | -23.0502 | OK
16 | 11 kV Shapla Chattar | A1111SC | 11 |  | 41812909516 | 1 | 210.07 | 221.82 | 11.75 | 60000 |  | 705000 | 717564.9411 | Motijheel |  |  |  | 11 kV Shapla Chattar | 717564.9411 | 919009.4688 | -201444.5277 | -21.9197 | OK
17 | 11 kV Sayedabad |  | 11 |  | 41812909497 | 1 | 118.23 | 122.96 | 4.73 | 60000 |  | 283800 | 288858.0572 | Swamibag |  |  |  | 11 kV Sayedabad | 288858.0572 | 483625.7179 | -194767.6607 | -40.2724 | CHECK
22 | 33/0.4 kV Aux Transformer |  | 0.415 |  | 41901920686 | 1 | 1459.01 | 1459.01 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 76.8957 | -76.8957 | -100 | CHECK
|  |  | 10: Total | 3039421.8826 | 2986200 | 3039421.8826 | 1.7823
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Motijheel | at 33 KV level |  | 1970097.4469
[7 empty] | Swamibag | at 33 KV level |  | 831153.9446
[7 empty] | Narinda | at 33 KV level |  | 238170.4911
|  |  | 7: Total =; 10: 3039421.8826 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 475.22 | 487.45 | 12.23 | 360000 | 0 | 4402800 | 4442884.0189
0 | 0 |  | 33 | Backup | 41812909610 | 1 | 475.4 | 488.03 | 12.63 | 360000 | 0 | 4546800 | 4588195.0252
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 158.77 | 166.71 | 7.94 | 360000 | 0 | 2858400 | 2884423.4759
0 | 0 |  | 33 | Backup | 41812909598 | 1 | 158.73 | 166.66 | 7.93 | 360000 | 0 | 2854800 | 2880790.7007
|  |  | 10: Total | 0 | 7405200 | 7472618.5011
P&T 33 KV SIDE (Sending) | bar: 4
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 7472618.5011
P&T 33 KV SIDE (Receiving)
5 | 33 kV Bidyut Bhaban Circuit |  | 33 | Import | BD017079 | 1 | 15811 | 15811 | 0 | 1000 | 0
|  |  | 33 | Export | BD017079 | 1 | 1533 | 3210 | 1677 | 1000 |  | 1677000
7 | 33 kV Motijheel Circuit-1 |  | 33 | Import | BD017081 | 1 | 70579 | 75107 | 4528 | 1000 | 4528000
8 | 33 kV Motijheel Circuit-2 |  | 33 | Import | BD017082 | 1 | 21372.33 | 21372.33 | 0 | 1000 | 2858400
11 | 33 kV Kamlapur Circuit |  | 33 | Import | BD017085 | 1 | 12870 | 12870 | 0 | 1000 | 0
|  |  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 7386400 | 1677000 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | BD017080 | 1 | 64013 | 67232 | 3219 | 888.88 |  | 2861304.72
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | BD017084 | 1 | 23588 | 26806 | 3218 | 888.88 |  | 2860415.84
|  |  | 10: Total |  | 5721720.56
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Sending Side |  | 4: 7472618.5011; 6: EXPORT TO OTHER S/S; 9=8-7: 1677000 | 33 KV NET IMPORT |  | 5795618.5011
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 5795618.5011 | 33 KV TX HV SIDE |  | 5721720.56
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 73897.9411
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.275%
| TOTAL IMPORT |  | 4: 7472618.5011
11 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
P&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 |  | 11 | Import | BD014056 | 1 | 77660 | 80498 | 2838 | 1000 | 2861304.72 |  | 5795618.5011 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | BD014057 | 1 | 101349 | 101349 | 0 | 1000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 2861304.72 |  | 5795618.5011
| P&T 11 KV SIDE |  | 7: 0; 8: 0
12 | Inner Circular Road Feeder | A161Z | 11 |  | BD014042 | 1 | 43389 | 43842 | 453 | 1000 |  | 453000 | 462807.6401 | Motijheel |  |  |  | Inner Circular Road Feeder | 462807.6401 | 1167930.2881 | -705122.648 | -60.3737 | CHECK
13 | NSI New Building Expres Feeder | D361NS | 11 |  | BD013982 | 1 | 11095 | 11324 | 229 | 1000 |  | 229000 | 233957.9461 | Ramna |  |  |  | NSI New Building Expres Feeder | 233957.9461 | 303173.5417 | -69215.5956 | -22.8304 | OK
14 | Police Hospital RMU Feeder | D661H | 11 |  | BD014044 | 1 | 4037 | 4109 | 72 | 1000 |  | 72000 | 73558.8302 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 73558.8302 | 119031.2227 | -45472.3925 | -38.2021 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder |  | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | D661J | 11 |  | BD014013 | 1 | 38143 | 39094 | 951 | 1000 |  | 951000 | 971589.5492 | Rajarbag |  |  |  | Jonaki O/H Feeder | 971589.5492 | 1202520.558 | -230931.0088 | -19.2039 | OK
17 | Nayapalton Overhead Feeder | D361N | 11 |  | BD014014 | 1 | 27311 | 27867 | 556 | 1000 |  | 556000 | 568037.6334 | Ramna |  |  |  | Nayapalton Overhead Feeder | 568037.6334 | 768107.463 | -200069.8296 | -26.0471 | OK
18 | Masjid Gali Over Head Feeder | D361MG | 11 |  | BD014016 | 1 | 16992 | 17566 | 574 | 1000 |  | 574000 | 586427.3409 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 586427.3409 | 687735.9536 | -101308.6127 | -14.7307 | OK
19 | Spare Feeder (Feeder-8) |  | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) |  | 11 |  | BD013988 | 1 | 13.18 | 13.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | D361MW | 11 |  | BD014015 | 1 | 25465 | 26030 | 565 | 1000 |  | 565000 | 577232.4871 | Ramna |  |  |  | Mid Way Over Head Feeder | 577232.4871 | 723343.5844 | -146111.0972 | -20.1994 | OK
24 | Palton Thana Over Head Feeder | D661F | 11 |  | BD014033 | 1 | 27288 | 28044 | 756 | 1000 |  | 756000 | 772367.7173 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 772367.7173 | 1016343.5173 | -243975.8 | -24.0052 | OK
25 | Police Hospital (South) U/G Feeder 7 |  | 11 |  | BD014034 | 1 | 12871 | 12972 | 101 | 1000 |  | 101000 | 103186.6924 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 103186.6924 | 130222.1924 | -27035.5 | -20.7611 | OK
26 | China Town Express Feeder | D361CT | 11 |  | BD013943 | 1 | 7132 | 7303 | 171 | 1000 |  | 171000 | 174702.2218 | Ramna |  |  |  | China Town Express Feeder | 174702.2218 | 210593.7018 | -35891.48 | -17.043 | OK
27 | Fakirapul Bazar O/H Feeder | A161FB | 11 |  | BD014032 | 1 | 33315 | 34326 | 1011 | 1000 |  | 1011000 | 1032888.5743 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1032888.5743 | 1155721.9576 | -122833.3833 | -10.6283 | OK
28 | PWD Ouarter (RMU) | A161PW | 11 |  | BD013937 | 1 | 2737 | 2844 | 107 | 1000 |  | 107000 | 109316.5949 | Motijheel |  |  |  | PWD Ouarter (RMU) | 109316.5949 | 124118.0271 | -14801.4322 | -11.9253 | OK
29 | Postal Quarter RMU | A161PO | 11 |  | BD013945 | 1 | 3356 | 3479 | 123 | 1000 |  | 123000 | 125663.0016 | Motijheel |  |  |  | Postal Quarter RMU | 125663.0016 | 149552.0491 | -23889.0475 | -15.9737 | OK
30 | 11/0.4 kV AT-1 |  | 0.415 |  | DHKH4409 | 1 | 1497 | 1497 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 0 | 2136.4578 | -2136.4578 | -100 | CHECK
31 | 11/0.4 kV AT-2 |  | 0.415 |  | DHKH4411 | 1 | 607 | 645 | 38 | 100 |  | 3800 | 3882.2716 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 3882.2716 | 2950.3465 | 931.925 | 31.587 | OK
|  |  | 10: Grand Total | 5795618.5011 | 5672800 | 5795618.5011 | 2.165
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 1730675.811
[6 empty] | Ramna | at 33 KV level |  | 2140357.6293
[6 empty] | Rajarbag | at 33 KV level |  | 1924585.0607
[6 empty] | Total = |  |  | 5795618.5011 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 287.38 | 294.05 | 6.67 | 360000 | 0 | 2401200 | 2423061.0307
0 | 0 |  | 33 | Backup | 41812909595 | 1 | 287.5 | 294.17 | 6.67 | 360000 | 0 | 2401200 | 2423061.0307
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 121 | 126.8 | 5.8 | 360000 | 0 | 2088000 | 2107009.5919
0 | 0 |  | 33 | Backup | 41621865733 | 1 | 121.02 | 126.82 | 5.8 | 360000 | 0 | 2088000 | 2107009.5919
|  |  | 10: Total | 0 | 4489200 | 4530070.6227
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 |  | 33 | Import | 101 | 1 | 382.5 | 391.2 | 8.7 | 270000 | 2349000
6 | 33 kV Motijheel Circuit-2 |  | 33 | Import | 113 | 1 | 161 | 168.8 | 7.8 | 270000 | 2106000
|  |  | 7: 0; 8: 0; 10: Total | 4455000 | 0 | 0
[7 empty] | 0 | 0
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0
[7 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  | 7: 0; 8: 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | 103 | 1 | 369.4 | 379.1 | 9.7 | 240000 |  | 2328000
4 | 33 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | 104 | 1 | 188.2 | 197 | 8.8 | 240000 |  | 2112000
|  |  | 10: Total |  | 4440000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Kamalapur Railway 33 KV SIDE (Sending) |  | 4: 4530070.6227; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4530070.6227
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 4530070.6227 | 33 KV TX HV SIDE |  | 4440000
[11 empty] | LOSS UNITS=> |  | 90070.6227
[11 empty] | LOSS % IN => |  | 1.988%
| TOTAL IMPORT |  | 4: 4530070.6227
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | 42 | 1 | 439.9 | 451.9 | 12 | 200000 | 2400000 |  | 2426823.5479
10 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | 64 | 1 | 223.2 | 233.6 | 10.4 | 200000 | 2080000 |  | 2103247.0748
|  |  | 7: 0; 8: 0; 10: Total | 4480000 |  | 4530070.6227
| KAMALAPUR RAILWAY 11 KV SIDE |  | 7: 0; 8: 0
1 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 469.4 | 482.7 | 13.3 | 40000 |  | 532000 | 542948.0376 | Rajarbag |  |  |  | Amtola O/H Feeder | 542948.0376 | 698504.7602 | -155556.7226 | -22.27 | OK
2 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 81.8 | 83.9 | 2.1 | 40000 |  | 84000 | 85728.6375 | Rajarbag |  |  |  | Police Telecom | 85728.6375 | 128460.6456 | -42732.008 | -33.2647 | OK
3 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 339.9 | 352 | 12.1 | 40000 |  | 484000 | 493960.2448 | Rajarbag |  |  |  | Railway Colony O/H | 493960.2448 | 634274.4374 | -140314.1927 | -22.122 | OK
4 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 792.7 | 811.7 | 19 | 40000 |  | 760000 | 775640.0538 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 775640.0538 | 967469.2368 | -191829.1831 | -19.8279 | OK
5 | 11 KV Majar Feeder |  | 11 |  | 96 | 1 | 78.2 | 83.8 | 5.6 | 40000 |  | 224000 | 228609.7001 | Motijheel |  |  |  | 11 KV Majar Feeder | 228609.7001 | 285022.0573 | -56412.3573 | -19.7923 | OK
7 | 11 kV Feeder-6 |  | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 364.4 | 371.1 | 6.7 | 40000 |  | 268000 | 273515.1768 | Rajarbag |  |  |  | Momenbagh O/H | 273515.1768 | 353266.7753 | -79751.5984 | -22.5755 | OK
9 | 11 kV Feeder-8 |  | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 239.1 | 243.8 | 4.7 | 40000 |  | 188000 | 191868.8554 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 191868.8554 | 256921.2911 | -65052.4357 | -25.32 | OK
12 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 379.3 | 391.2 | 11.9 | 40000 |  | 476000 | 485795.6126 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 485795.6126 | 622231.2519 | -136435.6393 | -21.9268 | OK
13 | 11 kV Feeder-11 |  | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway |  | 11 | Motijheel | 150 | 1 | 74.6 | 78.4 | 3.8 | 40000 |  | 152000 | 155128.0108 | Motijheel |  |  |  | Dhaka Railway | 155128.0108 | 112403.0649 | 42724.9459 | 38.0105 | OK
15 | Jasimuddin Feeder-13 |  | 11 |  | 91 | 1 | 299.6 | 321.5 | 21.9 | 40000 |  | 876000 | 894027.2198 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 894027.2198 | 1184246.5762 | -290219.3563 | -24.5067 | OK
16 | Police Box Feeder-14 |  | 11 |  | 18 | 1 | 127.9 | 137.7 | 9.8 | 40000 |  | 392000 | 400066.9751 | Motijheel |  |  |  | Police Box Feeder-14 | 400066.9751 | 493770.6063 | -93703.6312 | -18.9772 | OK
17 | 11 kV Feeder-15 |  | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 |  | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) |  | 0.415 |  | DHKF 7632 | 1 | 1052.87 | 1080.13 | 27.26 | 100 |  | 2726 | 2782.0984 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 2782.0984 | 3429.2971 | -647.1987 | -18.8726 | OK
20 | Auxiliary -1 (AT-2 ) |  | 0.415 |  | DHKF 7733 | 1 | 156.6 | 156.6 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4530070.6227 | 4438726 | 4530070.6227 | 2.0579
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Rajarbag | at 33 KV level |  | 2852238.7169
[6 empty] | Motijheel | at 33 KV level |  | 1677831.9057
[6 empty] | Total = |  |  | 4530070.6227 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1.45 | 41.84 | 43.1 | 1.26 | 1200000 | 0 | 2192400 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 |  | 132 |  | 41812909559 | 1 | 97.87 | 99.74 | 1.87 | 1200000 | 0 | 2244000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
|  |  | 10: Total | 0 | 4436400 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
|  |  | 10: Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
BANGABHABAN 33 KV SIDE
|  |  | 3: 132; 4: NET IMPORT |  | 0
|  |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 4: 4436400; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 4436400
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4436400 | 33 KV TX HV SIDE |  | 4436400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 4436400
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) |  | 11 | Import | 4150744 | 1 | 1530266.6 | 1532460.8 | 2194.2 | 1000 | 2194200 |  | 2597419.4519
12 | 11 kV 28/35 MVA Transformer (GT-1) |  | 11 | Import | 4150742 | 1 | 1446179 | 1447732.5 | 1553.5 | 1000 | 1553500 |  | 1838980.5481
|  |  | 7: 0; 8: 0; 10: Total | 3747700 |  | 4436400
| BANGABHABAN 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV DIT S/S-1 Feeder |  | 11 | Motijheel | 4150750 | 1 | 219429.19 | 220085.55 | 656.36 | 1000 | Estimated | 729797.04 | 732850.4474 | Motijheel | 60 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 732850.4474 | 734566.8339 | -1716.3865 | -0.23366 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 |  | 11 | Motijheel | 4150743 | 1 | 24348.79 | 24377.48 | 28.69 | 1000 |  | 28690 | 28810.0365 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 28810.0365 | 38328.8826 | -9518.8461 | -24.8347 | OK
3 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder |  | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation |  | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder |  | 11 | Ramna | 4150754 | 1 | 33904.2 | 33908.56 | 4.36 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 668980.62 | 671779.5768 | Motijheel | 55 | Meter Bad |  | 11 kV Modhumita via Ovisar | 671779.5768 | 675327.5731 | -3547.9963 | -0.52537 | OK
8 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16090.3 | 16127.43 | 37.13 | 1000 |  | 37130 | 37285.3487 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 37285.3487 | 63965.3489 | -26680.0002 | -41.7101 | CHECK
9 | 11 kV Motijheel-1 Feeder |  | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 251097.91 | 251918.65 | 820.74 | 1000 |  | 820740 | 824173.9049 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 824173.9049 | 1024190.419 | -200016.5142 | -19.5292 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 |  | 11 | Motijheel | 4150737 | 1 | 15124.38 | 15252.82 | 128.44 | 1000 |  | 128440 | 128977.3818 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 128977.3818 | 140844.5519 | -11867.1701 | -8.4257 | OK
14 | 11 kV Motijheel-2 Feeder |  | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | 19 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 232069.3083 | 236957.0432 | -4887.7349 | -2.0627 | OK
16 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 165136.78 | 165380.63 | 243.85 | 1000 |  | 243850 | 244870.2472 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 244870.2472 | 307144.3937 | -62274.1465 | -20.2752 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20803.97 | 20826.96 | 22.99 | 1000 | Estimated | 170285.976 | 170998.4377 | Motijheel | 14 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 170998.4377 | 177717.7824 | -6719.3447 | -3.7809 | OK
18 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82552.02 | 82655.11 | 103.09 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | 19 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 232069.3083 | 236957.0432 | -4887.7349 | -2.0627 | OK
19 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 124061.84 | 124241.41 | 179.57 | 1000 |  | 179570 | 180321.3053 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 180321.3053 | 243199.1755 | -62877.8702 | -25.8545 | OK
20 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273251.62 | 273786.78 | 535.16 | 1000 |  | 535160 | 537399.0629 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 537399.0629 | 60090.1862 | 477308.8768 | 794.3208 | FAULT
21 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 82213.59 | 82388.93 | 175.34 | 1000 |  | 175340 | 176073.6073 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 176073.6073 | 235529.3729 | -59455.7655 | -25.2435 | OK
22 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192985.49 | 193032.75 | 47.26 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | 19 | Meter Bad |  | 11 kV BCIC Feeder | 232069.3083 | 236957.0432 | -4887.7349 | -2.0627 | OK
23 | 11/0.4 kV AT-1 |  | 0.415 |  | 63412931 | 1 | 90029 | 91654 | 1625 | 1 |  | 1625 | 1631.7989 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 1631.7989 | 11191.6714 | -9559.8725 | -85.4195 | CHECK
24 | 11/0.4 kV AT-2 |  | 0.415 |  | 63403117 | 1 | 22902 | 22902 | 0 | 1 | Estimated | 5000 | 5020.9196 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5020.9196 | 5032.6789 | -11.7593 | -0.23366 | OK
|  |  | 10: Grand Total | 4436400 | 4417915.824 | 4436400 | 0.41839
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 0
[6 empty] | Ramna | at 33 KV level |  | 0
[6 empty] | Swamibag | at 33 KV level |  | 0
[6 empty] | Motijheel | at 33 KV level |  | 4436400
[6 empty] | Total = |  |  | 4436400 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
0 | 132 kV Narinda Circuit-1 | 0 | 132 | EXPORT | 06604331 | 1 | 8942.66 | 8967.94 | 25.28 | 480000 | 0 | 12134400 | 0 | 0 | Wrong Reading by Grid
0 | 132 kV Narinda Circuit-2 | 0 | 132 |  |  | 1 | 9042.13 | 9067.6 | 25.47 | 480000 | 0 | 12225600 | 0 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 24360000
|  |  | 10: Net Total | 24360000
NARINDA 132 KV SIDE (RECEIVING)
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 24360000
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 24360000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 4: 24360000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 24360000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 24360000 | 33 KV NET IMPORT |  | 24403200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -43200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.1773%
| 132 KV TOTAL IMPORT |  | 4: 24360000
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming |  | 33 | Import | 06604301 | 1 | 9408.5 | 9433.93 | 25.43 | 480000 | 12206400
7 | 132/33 kV 50/75 MVA GT-2 Incoming |  | 33 | Import | 06604304 | 1 | 9232.17 | 9257.58 | 25.41 | 480000 | 12196800
|  |  | 7: 0; 8: 0; 10: Total | 24403200 |  | 0
| NARINDA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 |  | 33 | Export | 06604300 | 1 | 9897.59 | 9925.82 | 28.23 | 180000 |  | 5081400 | 5114091.7359 |  | 10532528.9948 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 5114091.7359 | 6415094.3661 | -1301002.6302 | -20.2803 | OK
8 | 33 kV 20/28 MVA Transformer T-4 |  | 33 | Export | 06604303 | 1 | 10037.59 | 10067.5 | 29.91 | 180000 |  | 5383800 | 5418437.2589 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 5418437.2589 | 6862491.2735 | -1444054.0146 | -21.0427 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 10465200 | 10532528.9948 |  |  |  |  | 33 KV Feeders | 10532528.9948 | 13277585.6396 | -2745056.6448 | -20.6744 | OK
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 982800 | 989122.95 |  | 989122.95 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 989122.95 | 1125708.3477 | -136585.3977 | -12.1333 | OK
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 5381604.8082 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5773.32 | 5790.19 | 16.87 | 180000 |  | 3036600 | 3056136.2942 |  |  |  |  | 33 kV Kumertully-1 Feeder | 3056136.2942 | 4149245.5124 | -1093109.2182 | -26.3448 | OK
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5680.43 | 5704.96 | 24.53 | 180000 |  | 4415400 | 4443806.9529 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 4443806.9529 | 5579833.2042 | -1136026.2513 | -20.3595 | OK
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder |  | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 5347203 | 5381604.8082 |  | 7499943.2471 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 5381604.8082 | 7078492.5761 | -1696887.7679 | -23.9724 | OK
|  |  | 10: Total |  | 13782003 | 13870671.0052 |  |  |  |  | 0 | 13870671.0052 | 17933279.6404 | -4062608.6352 | -22.654 | OK
|  |  | 9=8-7: Grand Total | 24403200 | 24247203 | 24403200 | 0.64336
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 | Import | 06604351 | 1 | 11130.34 | 11162.2 | 31.86 | 160000 | 5097600 |  | 5112223.854
9 | 33/11 kV 20/28 MVA T-4 Incoming |  | 11 | Import | 06604295 | 1 | 11472.92 | 11506.7 | 33.78 | 160000 | 5404800 |  | 5420305.1408
|  |  | 7: 0; 8: 0; 10: Total | 10502400 |  | 10532528.9948
| NARINDA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bonogram Feeder | B124B | 11 |  | 06604467 | 1 | 25262.79 | 25343.65 | 80.86 | 8000 |  | 646880 | 656738.9275 | Narinda |  |  |  | 11 kV Bonogram Feeder | 656738.9275 | 833343.2066 | -176604.2792 | -21.1923 | OK
2 | 11 kV Sha Saheb Len Feeder | B524H | 11 |  | 06604469 | 1 | 17038.74 | 17094.2 | 55.46 | 8000 |  | 443680 | 450442.0099 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 450442.0099 | 558526.7169 | -108084.7071 | -19.3518 | OK
3 | 11 kV Sadiabad Water Treatment | B224W | 11 |  | 06604354 | 1 | 538.25 | 543.81 | 5.56 | 40000 |  | 222400 | 225789.5397 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 225789.5397 | 333110.8966 | -107321.3569 | -32.2179 | OK
4 | 11 kV Manashi Feeder | B124M | 11 |  | 06604353 | 1 | 5635.85 | 5652.37 | 16.52 | 40000 |  | 660800 | 670871.0785 | Narinda |  |  |  | 11 kV Manashi Feeder | 670871.0785 | 875224.6252 | -204353.5467 | -23.3487 | OK
5 | 11 kV Jatrabari Feeder | B524E | 11 |  | 06604324 | 1 | 3617.32 | 3647.47 | 30.15 | 40000 |  | 1206000 | 1224380.3279 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 1224380.3279 | 1448062.1743 | -223681.8464 | -15.447 | OK
6 | 11 kV Wari Feeder | B124W | 11 |  | 06604291 | 1 | 8709.16 | 8733.06 | 23.9 | 40000 |  | 956000 | 970570.1438 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 970570.1438 | 1184484.1348 | -213913.9909 | -18.0597 | OK
7 | 11 kV Narinda Feeder | B124N | 11 |  | 06604348 | 1 | 7442.6 | 7464.14 | 21.54 | 40000 |  | 861600 | 874731.4183 | Narinda |  |  |  | 11 kV Narinda Feeder | 874731.4183 | 1135164.3175 | -260432.8992 | -22.9423 | OK
10 | 11 kV Distillary Feeder | B524D | 11 |  | 06604347 | 1 | 6121.16 | 6140.77 | 19.61 | 40000 |  | 784400 | 796354.8335 | Swamibag |  |  |  | 11 kV Distillary Feeder | 796354.8335 | 1028035.2064 | -231680.3729 | -22.5362 | OK
11 | 11 kV Thatari Bazar Feeder | B124T | 11 |  | 06604296 | 1 | 5129.92 | 5145.48 | 15.56 | 40000 |  | 622400 | 631885.8342 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 631885.8342 | 785478.7283 | -153592.894 | -19.554 | OK
12 | 11 kV Swamibagh Feeder | B524C | 11 |  | 06604352 | 1 | 7918.91 | 7939.47 | 20.56 | 40000 |  | 822400 | 834933.9815 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 834933.9815 | 995694.3426 | -160760.3611 | -16.1456 | OK
13 | 11 kV Tipu Sultan Feeder | B124S | 11 |  | 06604322 | 1 | 6482.22 | 6500.16 | 17.94 | 40000 |  | 717600 | 728536.7523 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 728536.7523 | 911203.8361 | -182667.0838 | -20.0468 | OK
14 | 11 kV Spare |  | 11 |  | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | B124F | 11 |  | DHK00089 | 1 | 43986.5 | 46136 | 2149.5 | 444.44 |  | 955323.78 | 969883.6178 | Narinda |  |  |  | 11 kV Folder Street Feeder | 969883.6178 | 1264515.1272 | -294631.5095 | -23.3 | OK
16 | 11 kV Bhajohari Feeder | B124V | 11 |  | DHK27842 | 1 | 431839 | 437786 | 5947 | 80 |  | 475760 | 483010.9327 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 483010.9327 | 619650.9494 | -136640.0167 | -22.0511 | OK
17 | 11 kV Lal mohon shaha Feeder | B124L | 11 |  | DHK00086 | 1 | 43431.7 | 44846.9 | 1415.2 | 444.44 |  | 628971.488 | 638557.4766 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 638557.4766 | 845750.0473 | -207192.5707 | -24.4981 | OK
18 | 11 kV Dupkhola Feeder | B524A | 11 |  | 8838024/8838029 | 1 | 39022.1 | 39392.3 | 370.2 | 1000 |  | 370200 | 375842.1206 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 375842.1206 | 459341.3304 | -83499.2099 | -18.178 | OK
1 | 11/0.4 kV Aux Transformer-1 |  | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 |  | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 10532528.9948 | 10374415.268 | 10532528.9948 | 1.5241
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Narinda | at 33 KV level |  | 6624786.1817
[6 empty] | Maniknagar | at 33 KV level |  | 225789.5397
[6 empty] | Swamibag | at 33 KV level |  | 3681953.2733
[6 empty] | Total = |  |  | 10532528.9948 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5773.32 | 5790.19 | 16.87 | 180000 | 0 | 3036600 | 3056136.2942
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5680.43 | 5704.96 | 24.53 | 180000 | 0 | 4415400 | 4443806.9529
| MITFORD 33 KV SIDE | [10 empty] | 7452000 | 7499943.2471 | bar: 4
1 | Kumartuly Circuit-1 |  | 33 | 0 | DHK-66493 | 1 | 1304145 | 1305659 | 1514 | 180 | 0 | 132570 | 132570
6 | Kumartuly Circuit-2 |  | 33 | 0 | DHK-60914 | 1.1 | 786422.9 | 792788.8 | 6365.9 | 180 | 0 | 1271160 | 1271160
|  |  | 10: Total |  | 1403730 | 1403730
| KUMERTULY 33 KV SIDE (RECEIVING) | [11 empty] | 8903673.2471
5 | 33 kV Mitford Circuit-1 |  | 33 | Import | DHK60965 | 1 | 299268.6 | 300005.1 | 736.5 | 180 | 132570
6 | 33 kV Narinda Circuit-1 |  | 33 | Import | DHK60959 | 1 | 1000840.4 | 1000840.4 | 0 | 540 | 0
9 | 33 kV Mitford Circuit-2 |  | 33 | Import | DHK86072 | 1 | 1787.47 | 1793.89 | 6.42 | 180000 | 1155600
10 | 33 kV Narinda Circuit-2 |  | 33 | Import | DHK60957 | 1 | 940032.1 | 948225.2 | 8193.1 | 540 | 4424274
|  |  | 7: 0; 8: 0; 10: Total | 5712444 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
|  |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 1288170
[7 empty] | 0 | 0
| KUMERTULY 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK60960 | 1 | 222580.2 | 239898.5 | 17318.3 | 180 |  | 3117294
8 | 33/11 kV 20/28 MVA Transformer (T-2) |  | 33 | Export | DHK60958 | 1 | 418875.6 | 439356.4 | 20480.8 | 180 |  | 3686544
|  |  | 10: Total |  | 6803838
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 7499943.2471; 6: EXPORT TO OTHER S/S; 9=8-7: 1403730 | 33 KV NET IMPORT |  | 6803838
| MITFORD 33 KV SIDE |  | 6: 33 KV NET IMPORT; 9=8-7: 6803838 | 33 KV TX HV SIDE |  | 5712444
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 1091394
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 16.04%
| TOTAL IMPORT |  | 4: 7499943.2471
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 | Import | 06604403 | 1 | 7342.08 | 7361.42 | 19.34 | 160000 | 3117294 |  | 3121029.7836 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 | Import | 06604410 | 1 | 6805.33 | 6828.32 | 22.99 | 160000 | 3678400 |  | 3682808.2164
|  |  | 7: 0; 8: 0; 10: Total | 6795694 |  | 6803838
| KUMERTULY 11 KV SIDE |  | 7: 0; 8: 0
11 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63748 | 63943.2 | 195.2 | 2222.22 |  | 433777.344 | 436813.0585 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 436813.0585 | 559882.2686 | -123069.2101 | -21.9813 | OK
12 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4714.17 | 4734.1 | 19.93 | 40000 |  | 797200 | 802779.0641 | Banglabazar |  |  |  | 11kV Islampur Feeder | 802779.0641 | 1039961.1294 | -237182.0653 | -22.8068 | OK
13 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5192.58 | 5203.81 | 11.23 | 40000 |  | 449200 | 452343.6473 | Banglabazar |  | 95 |  | 11kV Majar O/H Feeder | 452343.6473 | 454027.8867 | -1684.2395 | -0.37096 | OK
15 | 11kV Spare |  | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  | 30 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5552.12 | 5569.8 | 17.68 | 40000 |  | 707200 | 712149.2149 | Banglabazar |  | 65 |  | 11kV Sadarghat Feeder | 712149.2149 | 978432.1066 | -266282.8917 | -27.2153 | OK
17 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal |  | 21.6667 |  | 11kV Mitford Hospital Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4194.33 | 4211.66 | 17.33 | 40000 |  | 693200 | 698051.2384 | Banglabazar |  | 51.6667 |  | 11kV Zindabahar Feeder | 698051.2384 | 980442.859 | -282391.6206 | -28.8025 | OK
21 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 681143.904 | 685910.7699 | Banglabazar | 56 |  |  | 11kV Police fari Feeder | 685910.7699 | 887565.2014 | -201654.4314 | -22.72 | OK
22 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 6005.67 | 6022.5 | 16.83 | 40000 |  | 673200 | 677911.2719 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 677911.2719 | 893980.5068 | -216069.2349 | -24.1693 | OK
23 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8373.78 | 8401.75 | 27.97 | 40000 |  | 1118800 | 1126629.7252 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1126629.7252 | 1559941.6941 | -433311.9689 | -27.7774 | OK
24 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3799.62 | 3805.19 | 5.57 | 40000 |  | 222800 | 224359.2266 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 224359.2266 | 333784.8946 | -109425.6679 | -32.7833 | OK
25 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7326.5 | 7346.17 | 19.67 | 40000 |  | 786800 | 792306.2815 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 792306.2815 | 995322.4266 | -203016.1451 | -20.397 | OK
26 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3612.86 | 3617.65 | 4.79 | 40000 |  | 191600 | 192940.8789 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 192940.8789 | 238073.0814 | -45132.2025 | -18.9573 | OK
27 | 11/0.4 kV AT-1 |  | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 |  | 0.415 |  | 05378636 | 1 | 178179.3 | 178995.4 | 816.1 | 2 |  | 1632.2 | 1643.6227 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 1643.6227 | 3093.9447 | -1450.322 | -46.8761 | CHECK
|  |  | 10: Grand Total | 6803838 | 6756553.448 | 6803838 | 0.69983
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 0
[6 empty] | Banglabazar | at 33 KV level |  | 6803838
[6 empty] | Total = |  |  | 6803838 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder |  | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 5347203 | 5381604.8082
|  |  | 10: Total | 0 | 5347203 | 5381604.8082
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 |  | 33 | Import | Mat-152447/1191738/007 | 1 | 128577100 | 130249100 | 1672000 | 1 | 1672000
5 | 33 kV Narinda Circuit-2 |  | 33 | Import | Mat-152447/1191738/002 | 1 | 259330000 | 262974400 | 3644400 | 1 | 3644400
|  |  | 7: 0; 8: 0; 10: Total | 5316400 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) |  | 33 | Export | Mat-152447/1191738/009 | 1 | 135799800 | 137483100 | 1683300 | 1 |  | 1683300 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) |  | 33 | Export | Mat-152447/1191738/004 | 1 | 256863000 | 260503600 | 3640600 | 1 |  | 3640600 |  |  | #VALUE!
|  |  | 10: Total |  | 5323900
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 5381604.8082; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5381604.8082
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5381604.8082 | 33 KV TX HV SIDE |  | 5323900
[11 empty] | LOSS UNITS=> |  | 57704.8082
[11 empty] | LOSS % IN => |  | 1.072%
| TOTAL IMPORT |  | 4: 5381604.8082
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 |  | 11 | Import | 340180016886 | 1 | 135833728 | 137522533 | 1688805 | 1 | 1688805 |  | 1699670.1094 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 |  | 11 | Import | 340180012685 | 1 | 260271611 | 263930009 | 3658398 | 1 | 3658398 |  | 3681934.6988
|  |  | 7: 0; 8: 0; 10: Total | 5347203 |  | 5381604.8082
| BANGSHAL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 41256087 | 41743836 | 487749 | 1 |  | 487749 | 490118.7926 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 490118.7926 | 617669.4796 | -127550.687 | -20.6503 | OK
2 | 11 kV Spare Feeder |  | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder |  | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 54945882 | 55731189 | 785307 | 1 |  | 785307 | 789122.5172 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 789122.5172 | 1083356.0922 | -294233.575 | -27.1595 | OK
5 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 23435352 | 23858970 | 423618 | 1 |  | 423618 | 425676.2037 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 425676.2037 | 568959.3967 | -143283.193 | -25.1834 | OK
8 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 52356480 | 53313937 | 957457 | 1 |  | 957457 | 962108.9306 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 962108.9306 | 1228122.7989 | -266013.8683 | -21.6602 | OK
9 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 66698574 | 67362715 | 664141 | 1 |  | 664141 | 667367.8163 | Bangshal |  |  |  | 11 kV French Road Feeder | 667367.8163 | 917105.0905 | -249737.2742 | -27.231 | OK
10 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 33052156 | 33422319 | 370163 | 1 |  | 370163 | 371961.4855 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 371961.4855 | 442857.7972 | -70896.3116 | -16.0088 | OK
11 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 68646258 | 69597215 | 950957 | 1 |  | 950957 | 955577.3495 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 955577.3495 | 1230776.8001 | -275199.4506 | -22.3598 | OK
12 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 55024234 | 55733426 | 709192 | 1 |  | 709192 | 712637.7025 | Narinda |  |  |  | 11 kV Suritolla Feeder | 712637.7025 | 982637.1962 | -269999.4938 | -27.477 | OK
13 | AT-1 |  | 0.415 |  | DHK-4415 | 1 | 777.4 | 799.54 | 22.14 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 |  | 0.415 |  | DHK-4410 | 1 | 786.95 | 786.95 | 0 | 100 |  | 7000 | 7034.0104 | Bangshal |  |  |  | AT-2 | 7034.0104 | 7007.9248 | 26.0856 | 0.37223 | OK
|  |  | 10: Grand Total | 5381604.8082 | 5355584 | 5381604.8082 | 0.48586
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 3879844.5885
[6 empty] | Banglabazar | at 33 KV level |  | 789122.5172
[6 empty] | Narinda | at 33 KV level |  | 712637.7025
[6 empty] | Total = |  |  | 5381604.8082 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING) Maniknagar 132
0 | 132 kV Kazla Circuit-1 | 0 | 132 | 0 | ABB03905 | 1 | 870310 | 893515 | 23205 | 1000 | 0 | 23205000
0 | 132 kV Kazla Circuit-2 | 0 | 132 |  |  | 1 | 660390 | 685705 | 25315 | 1000 | From Downstream | 20577600
|  |  | 9=8-7: Total Import/Export | 0 | 43782600
|  |  | 10: Net Total | 43782600
KAZLA 132 KV SIDE (RECEIVING)
3 | 132kV Maniknagar Circuit-1 |  | 132 | Main | 41812909505 | 1 | 727.64 | 747.08 | 19.44 | 1200000 | 23328000
|  |  | 132 | Backup | 41812909603 | 1 | 727.6 | 747.04 | 19.44 | 1200000 | 23328000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 |  | 132 | Main | 41812909540 | 1 | 553.18 | 570.29 | 17.11 | 1200000 | 20532000
|  |  | 132 | Backup | 41812909587 | 1 | 553.19 | 570.31 | 17.12 | 1200000 | 20544000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 43860000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 43860000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| KAZLA 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Main | 41812909542 | 1 | 728.45 | 747.85 | 19.4 | 1200000 |  | 23280000 |  |  | #DIV/0!
|  |  | 132 | Backup | 41812909589 | 1 | 728.87 | 748.29 | 19.42 | 1200000 |  | 23304000
7 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Main | 41812909501 | 1 | 552.58 | 569.77 | 17.19 | 1200000 |  | 20628000 |  |  | 100
|  |  | 132 | Backup | 41812909606 | 1 | 552.51 | 569.7 | 17.19 | 1200000 |  | 20628000
|  |  | 10: Total |  | 43908000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) Maniknagar 132 |  | 4: 43782600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 43782600
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 43782600 | 33 KV NET IMPORT |  | 43660800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 121800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2782%
| 132 KV TOTAL IMPORT |  | 4: 43782600
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) |  | 33 | Main | 41812909533 | 1 | 1209.38 | 1241.44 | 32.06 | 720000 | 23083200
|  |  | 33 | Backup | 41812909582 | 1 | 1209.48 | 1241.54 | 32.06 | 720000 | 23083200
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) |  | 33 | Main | 41812909479 | 1 | 917.98 | 946.56 | 28.58 | 720000 | 20577600
|  |  | 33 | Backup | 41812909622 | 1 | 917.85 | 946.43 | 28.58 | 720000 | 20577600
|  |  | 7: 0; 8: 0; 10: Total | 43660800 |  | 0
| KAZLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 |  | 33 | Main | 41812909465 | 1 | 1231.81 | 1263.25 | 31.44 | 240000 |  | 7545600 | 7495539.0941 |  | 25422608.5019 | Kazla 33/11 kv ss | 0.32549 | 33/11 kV 20/28 MVA T-1 | 7495539.0941 | 9885950.0203 | -2390410.9262 | -24.1799 | OK
|  |  | 33 | Backup | 41812909596 | 1 | 1231.47 | 1262.91 | 31.44 | 240000 |  | 7545600 | 7495539.0941 |  |  |  |  | 0 | 7495539.0941 | 9879700.6962 | -2384161.6021 | -24.1319 | OK
13 | 33/11 kV 28/35 MVA T-5 |  | 33 | Main | 41812909536 | 1 | 157.16 | 163.49 | 6.33 | 360000 |  | 2278800 | 2263681.4153 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 2263681.4153 | 3248446.7426 | -984765.3273 | -30.315 | OK
|  |  | 33 | Backup | 41812909578 | 1 | 144.59 | 149.66 | 5.07 | 360000 |  | 1825200 | 1813090.8019 |  |  |  |  | 0 | 1813090.8019 | 2289415.8508 | -476325.0489 | -20.8055 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 | Main | 41812909554 | 1 | 1187.47 | 1213.12 | 25.65 | 240000 |  | 6156000 | 6115158.3258 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 6115158.3258 | 6405557.2099 | -290398.884 | -4.5335 | OK
|  |  | 33 | Backup | 41812909613 | 1 | 1186.29 | 1211.92 | 25.63 | 240000 |  | 6151200 | 6110390.1712 |  |  |  |  | 0 | 6110390.1712 | 6395942.8651 | -285552.6939 | -4.4646 | OK
17 | 33/11 kV 20/28 MVA T-3 |  | 33 | Main | 41812909544 | 1 | 1039.39 | 1064.74 | 25.35 | 240000 |  | 6084000 | 6043636.0062 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 6043636.0062 | 7359780.9293 | -1316144.9231 | -17.8829 | OK
|  |  | 33 | Backup | 41812909614 | 1 | 1039.43 | 1064.78 | 25.35 | 240000 |  | 6084000 | 6043636.0062 |  |  |  |  | 0 | 6043636.0062 | 7362184.5155 | -1318548.5093 | -17.9097 | OK
22 | 33/11 kV 10/14 MVA T-4 |  | 33 | Main | 41812909506 | 1 | 550.48 | 565.18 | 14.7 | 240000 |  | 3528000 | 3504593.6604 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 3504593.6604 | 4110132.3936 | -605538.7332 | -14.7328 | OK
|  |  | 33 | Backup | 41812909602 | 1 | 550.62 | 565.34 | 14.72 | 240000 |  | 3532800 | 3509361.8151 |  |  |  |  | 0 | 3509361.8151 | 4105325.2212 | -595963.4061 | -14.5168 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 25592400 | 25422608.5019 |  |  |  |  | 33 KV Feeders | 25422608.5019 | 31009867.2957 | -5587258.7938 | -18.0177 | OK
10 | 33 kV Shahriar Steel Feeder |  | 33 | Main | 41812909534 | 1 | 652.26 | 672.83 | 20.57 | 360000 |  | 7405200 | 7356070.5709 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 7356070.5709 | 6734848.5186 | 621222.0523 | 9.224 | OK
|  |  | 33 | Backup | 41812909580 | 1 | 652.2 | 672.78 | 20.58 | 360000 |  | 7408800 | 7359646.6869 |  |  |  |  | 0 | 7359646.6869 | 6734848.5186 | 624798.1683 | 9.2771 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | A418S | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 |  | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 |  | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 |  | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Amulia Feeder |  | 33 | Main | 41812909523 | 1 | 23.56 | 23.61 | 0.05 | 360000 |  | 18000 | 17880.5799 |  |  |  |  | 33 kV Amulia Feeder | 17880.5799 | 2105541.5069 | -2087660.927 | -99.1508 | CHECK
|  |  | 33 | Backup | 41812909565 | 1 | 23.54 | 23.59 | 0.05 | 360000 |  | 18000 | 17880.5799 |  |  |  |  | 0 | 17880.5799 | 2101936.1276 | -2084055.5477 | -99.1493 | CHECK
21 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 751.24 | 781.62 | 30.38 | 360000 |  | 10936800 | 10864240.3473 | Kazla |  |  |  | 33 kV Zahir Steel | 10864240.3473 | 10607025.8788 | 257214.4684 | 2.4249 | OK
|  |  | 33 | Backup | 41812909563 | 1 | 751.52 | 781.91 | 30.39 | 360000 |  | 10940400 | 10867816.4633 |  |  |  |  | 0 | 10867816.4633 | 10610631.2581 | 257185.2051 | 2.4238 | OK
| Auxiliary Transformer-3 (AT-3) |  | 0.415 |  |  | 1 | 2874.18 | 2947.06 | 72.88 | 160 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 18360000 | 18238191.4981 |  |  |  |  | 0 | 18238191.4981 | 19447415.9043 | -1209224.4062 | -6.2179 | OK
|  |  | 9=8-7: Grand Total | 43660800 | 43952400 | 43660800 | -0.66344
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | KAZLA at 33 KV level |  |  | 18220310.9182
[7 empty] | Kazla 33/11 KV Substation |  |  | 25440489.0818
|  |  | 9=8-7: Total =; 10: 43660800 | 0
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK-61009 | 1 | 8083027 | 8123956 | 40929 | 180 | 7367220 |  | 7495539.0941
30 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK-61124 | 1 | 998043.7 | 1310345 | 312301.3 | 180 | 56214234 |  | 6115158.3258
24 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 |  | DHK-61015 | 1 | 619717.8 | 653307.6 | 33589.8 | 180 | 6046164 |  | 6043636.0062
39 | 33/11 kV 10/14 MVA T-4 Incoming |  | 11 |  | 8L55984 | 1 | 32702.3 | 33552 | 849.7 | 4000 | 3398800 |  | 3504593.6604
42 | 33/11 kv 28/35 MVA T-5 Incomer |  | 11 |  | DHK00112 | 1 | 22038.3 | 24603.6 | 2565.3 | 888.8 | 2280038.64 |  | 2263681.4153
|  |  | 7: 0; 8: 0; 10: Total | 75306456.64 |  | 25422608.5019
| KAZLA 11 kV SIDE |  | 7: 0; 8: 0 | [5 empty] | 120
17 | 11 kV Nayanagor Feeder | A418N | 11 |  | DHK-61125 | 1 | 957166.8 | 974598.2 | 17431.4 | 60 |  | 1045884 | 1049288.1996 | Kazla |  | 60 |  | 11 kV Nayanagor Feeder | 1049288.1996 | 1425042.8921 | -375754.6925 | -26.368 | OK
18 | 11 kV Madrasa Bazar Feeder | A418B | 11 |  | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1033879.14 | 1037244.2656 | Kazla | 85 | 60 |  | 11 kV Madrasa Bazar Feeder | 1037244.2656 | 1548060.2038 | -510815.9383 | -32.9972 | OK
19 | 11 kV Kazla Feeder | A418K | 11 |  | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 1946125.44 | 1952459.794 | Kazla | 160 | 20 |  | 11 kV Kazla Feeder | 1952459.794 | 2381631.0828 | -429171.2888 | -18.0201 | OK
20 | 11 kV Sayedabad Feeder | B218S | 11 |  | HA021101239-02 | 1 | 36964660 | 36964682 | 22 | 1000 | Estimated | 912246.3 | 915215.5285 | Maniknagar | 75 | 80 |  | 11 kV Sayedabad Feeder | 915215.5285 | 952652.4331 | -37436.9047 | -3.9298 | OK
21 | 11 kV Zenith Feeder | old | 11 |  | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | B318P | 11 |  | HA-021200060 | 1 | 122840.5 | 124064 | 1223.5 | 1000 |  | 1223500 | 1227482.3138 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 1227482.3138 | 1890790.3944 | -663308.0806 | -35.081 | OK
23 | 11 kV Matuail Feeder | A418M | 11 |  | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1216328.4 | 1220287.3713 | Kazla | 100 |  |  | 11 kV Matuail Feeder | 1220287.3713 | 1488519.4268 | -268232.0555 | -18.0201 | OK
25 | 11 kV Kutubkhali Feeder | B326C | 11 |  | DHK-61117 | 1 | 873380.8 | 899823.4 | 26442.6 | 60 |  | 1586556 | 1591720.008 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 1591720.008 | 2111396.7703 | -519676.7623 | -24.6129 | OK
26 | 11 kV Mridhabari Feeder | A418R | 11 |  | DHK-61118 | 1 | 722924.6 | 743943.1 | 21018.5 | 60 |  | 1261110 | 1265214.7288 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1265214.7288 | 1394116.481 | -128901.7522 | -9.2461 | OK
27 | 11 kV Muslim Nagar Feeder | A418U | 11 |  | DHK-61011 | 1 | 192344.8 | 225676.9 | 33332.1 | 60 |  | 1999926 | 2006435.467 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2006435.467 | 2307735.4737 | -301300.0067 | -13.0561 | OK
28 | 11 kV Jatrabari Thana Feeder | A418H | 11 |  | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | B518D | 11 |  | DHK-61008 | 1 | 375123.8 | 394906.3 | 19782.5 | 60 |  | 1186950 | 1190813.3489 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 1190813.3489 | 1593271.6426 | -402458.2937 | -25.2599 | OK
31 | 11 kV Mukti Sharani Feeder | B318T | 11 |  | DHK-61014 | 1 | 213219.9 | 235359.9 | 22140 | 60 |  | 1328400 | 1332723.748 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 1332723.748 | 182.0986 | 1332541.6494 | 731769.326 | FAULT
32 | 11 kV Kadamtali Feeder | B418K | 11 |  | DHK-61006 | 1 | 485277.4 | 512713.6 | 27436.2 | 60 |  | 1646172 | 1651530.0494 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 1651530.0494 | 2019121.3431 | -367591.2937 | -18.2055 | OK
33 | 11kV Rayerbagh Feeder | E218R | 11 |  | DHK-61012 | 1 | 473065.1 | 487739.3 | 14674.2 | 60 |  | 880452 | 883317.7427 | Matuail | Export to Jurain |  |  | 11kV Rayerbagh Feeder | 883317.7427 | 1505014.5244 | -621696.7817 | -41.3084 | CHECK
34 | 11 kV Donia Feeder | B318D | 11 |  | DHK-61013 | 1 | 2100163 | 2100163 | 0 | 60 |  | 0 | 0 | Jurain |  |  |  | 11 kV Donia Feeder | 0 | 932769.6947 | -932769.6947 | -100 | CHECK
35 | 11 kV Nimtoli Feeder | A418T | 11 |  | HA-021100855-02 | 1 | 35425036 | 36615614 | 1190578 | 1 |  | 1190578 | 1194453.1575 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1194453.1575 | 1438258.1917 | -243805.0342 | -16.9514 | OK
36 | 11 kV Gobindapur Feeder | A441G | 11 |  | HA-021101057-02 | 1 | 29299106 | 30389588 | 1090482 | 1 |  | 1090482 | 1094031.3596 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 1094031.3596 | 557604.1027 | 536427.2569 | 96.2022 | FAULT
37 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 |  | 9A56136 | 1 | 3949.3 | 4086 | 136.7 | 10000 |  | 1367000 | 1371449.3853 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1371449.3853 | 1500290.0775 | -128840.6922 | -8.5877 | OK
38 | 11 kV Samad Nagar Gate (Old) | old | 11 |  | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | A418D | 11 |  | 8K55676 | 1 | 820.6 | 1019.5 | 198.9 | 4000 |  | 795600 | 798189.5618 | Kazla |  |  |  | 11 kV Dharmik Para | 798189.5618 | 25898.4666 | 772291.0952 | 2981.9954 | FAULT
41 | 11 kV Sheikhdi Feeder | A418I | 11 |  | 9A56133 | 1 | 17420.9 | 17759.8 | 338.9 | 4000 |  | 1355600 | 1360012.28 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 1360012.28 | 2650141.5287 | -1290129.2487 | -48.6815 | CHECK
43 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 |  | T-5 Sum | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | A418Z | 11 |  | 61903661 | 1 | 23175.9 | 23269.7 | 93.8 | 2000 | 2259400 | 187600 | 188210.6106 | Kazla | OMF Corrected |  |  | 11 kV Jenith Feeder | 188210.6106 | 1045852.9212 | -857642.3106 | -82.0041 | CHECK
45 | 11 KV Samad Nagor Gate | A418A | 11 |  | 61903675 | 1 | 20299.2 | 20906 | 606.8 | 2000 |  | 1213600 | 1217550.0907 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1217550.0907 | 1246768.3692 | -29218.2785 | -2.3435 | OK
46 | 11 KV Bibir Bagicha | B218I | 11 |  | 61903557 | 1 | 38947.4 | 39376.5 | 429.1 | 2000 |  | 858200 | 860993.3156 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 860993.3156 | 974025.1427 | -113031.8271 | -11.6046 | OK
47 | 33/0.4 kV AT-1 |  | 0.415 |  | 503043 | 1 | 96207 | 96242 | 35 | 10 |  | 350 | 351.1392 | Kazla |  |  |  | 33/0.4 kV AT-1 | 351.1392 | 30.3498 | 320.7894 | 1056.975 | FAULT
48 | 33/0.4 kV AT-2 |  | 0.415 |  | 503044 | 1 | 96336 | 96529 | 193 | 10 |  | 1930 | 1936.2819 | Kazla |  |  |  | 33/0.4 kV AT-2 | 1936.2819 | 3500.3396 | -1564.0578 | -44.683 | CHECK
23 | Auxiliary Transformer |  | 0.415 |  | 41901920685 | 1 | 2874.18 | 2947.06 | 72.88 | 160 |  | 11660.8 | 11698.7542 | Kazla |  |  |  | Auxiliary Transformer | 11698.7542 | 17193.3445 | -5494.5903 | -31.9577 | OK
|  |  | 10: Total | 25422608.5019 | 25340130.08 | 25422608.5019 | 0.32549
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 883317.7427
[6 empty] | Jurain | at 33 KV level |  | 4151926.0698
[6 empty] | Swamibag | at 33 KV level |  | 1190813.3489
[6 empty] | Maniknagar | at 33 KV level |  | 1776208.8441
[6 empty] | Shyampur | at 33 KV level |  | 1651530.0494
[6 empty] | Kazla | at 33 KV level |  | 15768812.4471
[6 empty] | Total = |  |  | 25422608.5019 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT |  | 132 |  | 8993532 | 1 | 2234.461 | 2234.461 | 0 | 960000 | 0 | 0
|  |  | 132 |  |  | 1 | 667.558 | 667.558 | 0 | 960000 | 0 | 0
1 | Tranformer - 1 at Shyampur 230/132 |  | 132 |  | 38992560 | 1 | 1593.217 | 1632.528 | 39.311 | 1920000 | 0 | 75477120
|  |  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 |  | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  |  | 132 |  | 38992559 | 1 | 1683.807 | 1722.931 | 39.124 | 1920000 | 0 | 75118080
| Aggrekko 100 MW (Brammhongao) |  | 132 |  | PN-1711A04601 | 1 | 6.982 | 11.904 | 4.922 | 960000 | 0 | 4725120
|  |  | 132 |  |  | 1 | 0.242 | 2.117 | 1.875 | 960000 | 1800000 | 0
| Madanganj-Fatullah Exp |  | 132 |  | 38992544 | 1 | 33.859 | 34.145 | 0.286 | 960000 | 0 | 274560
| Madanganj-Fatullah Imp |  | 132 |  | 38992544 | 1 | 105.155 | 144.713 | 39.558 | 960000 | 37975680 | 0
|  |  | 9=8-7: Total Import/Export | 39775680 | 155594880
|  |  | 10: Net Total | 115819200
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) |  | 132 | Import | 08993727 | 1 | 9332.709 | 9392.366 | 59.657 | 720000 | 42953040
|  |  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) |  | 132 | Import | 08993726 | 1 | 7051.441 | 7109.354 | 57.913 | 720000 | 41697360
|  |  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 84650400 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 84650400
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 132 |  |  |  | 0 | 0
|  |  | 132 |  |  |  | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 30624000
| SHYAMPUR 132 KV SIDE |  | 7: 0; 8: 0
5 | 132 kV 80/120 MVA ( GT-1) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) |  | 132 | Export | ABB3902 | 1 | 2486388.1 | 2486388.1 | 0 | 1300 |  | 0
|  |  | 10: Total |  | 54026400
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 4: 115819200; 6: EXPORT TO OTHER S/S; 9=8-7: 30624000 | 132 KV NET IMPORT |  | 85195200
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 85195200 | 33 KV NET IMPORT |  | 84970656
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 224544
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2636%
| 132 KV TOTAL IMPORT |  | 4: 115819200
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) |  | 33 | Import | BD001826 | 1 | 3552.479 | 3595.326 | 42.847 | 480000 | 20566560
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) |  | 33 | Import | BD001850 | 1 | 3607.799 | 3650.724 | 42.925 | 480000 | 20604000
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) |  | 33 | Import | BD001835 | 1 | 3121.4169 | 3167.017 | 45.6001 | 480000 | 21888048
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) |  | 33 | Import | BD001831 | 1 | 4004.8999 | 4050.55 | 45.6501 | 480000 | 21912048
|  |  | 7: 0; 8: 0; 10: Total | 84970656
| SHYAMPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) |  | 33 | Export | BD001808 | 1 | 2242.62 | 2275.399 | 32.779 | 240000 |  | 7866960 | 7869489.5291 |  | 24741656.8336 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7869489.5291 | 8299487.545 | -429998.0159 | -5.181 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) |  | 33 | Export | BD001834 | 1 | 2054.427 | 2087.402 | 32.975 | 240000 |  | 7914000 | 7916544.6543 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7916544.6543 | 8290822.2675 | -374277.6132 | -4.5144 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) |  | 33 | Export | BD001846 | 1 | 1525.1669 | 1546.454 | 21.2871 | 240000 |  | 5108904 | 5110546.7084 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 5110546.7084 | 5989050.9308 | -878504.2224 | -14.6685 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) |  | 33 | Export | BD001847 | 1 | 1357.817 | 1373.833 | 16.016 | 240000 |  | 3843840 | 3845075.9419 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 3845075.9419 | 4249130.4245 | -404054.4826 | -9.5091 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 24733704 | 24741656.8336 |  |  |  |  | 33 KV Feeders | 24741656.8336 | 26828491.1678 | -2086834.3341 | -7.7784 | OK
1 | 33 kV Rani RRM Feeder |  | 33 | Export | BD001809 | 1 | 772.98 | 786.83 | 13.85 | 240000 |  | 3324000 | 3325068.7934 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 3325068.7934 | 3021325.4164 | 303743.377 | 10.0533 | OK
2 | 33 kV Postogola Feeder-1. |  | 33 | Export | BD001804 | 1 | 1564.544 | 1564.544 | 0 | 240000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv s/s | Grid Has No Reading | 33 kV Postogola Feeder-1. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV Prime Textile Feeder. |  | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1392.002 | 1412.48 | 20.478 | 240000 | From Downstream | 4914720 | 4916300.2708 |  | 9794908.4261 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 4916300.2708 | 6168429.3755 | -1252129.1047 | -20.299 | OK
7 | 33 kV Nondolalpur -2 feeder |  | 33 | Export | BD001807 | 1 | 1202.282 | 1222.603 | 20.321 | 240000 |  | 4877040 | 4878608.1553 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 4878608.1553 | 5156320.1662 | -277712.0109 | -5.3859 | OK
8 | 33 kV Postogola Feeder-2. |  | 33 | Export | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Postogola Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Rahima Steel feeder |  | 33 | Export | BD001803 | 1 | 665.824 | 678.085 | 12.261 | 240000 |  | 2942640 | 2943586.1715 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2943586.1715 | 2258252.921 | 685333.2505 | 30.3479 | OK
12 | 33 kV Salam Steel Feeder |  | 33 | Export | BD001849 | 1 | 1293.7049 | 1332.06 | 38.3551 | 240000 |  | 9205224 | 9208183.8323 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 9208183.8323 | 10104745.6836 | -896561.8514 | -8.8727 | OK
13 | 33 kV Fatullah Feeder-2. |  | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 12844.1286 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2679.862 | 2714.548 | 34.686 | 240000 |  | 8491132.8 | 8493863.0246 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8493863.0246 | 8673318.6567 | -179455.6321 | -2.0691 | OK
17 | 33 kV Akhter Steel Feeder |  | 33 | Export | BD001828 | 1 | 691.8555 | 691.909 | 0.0535 | 240000 | Prime Textile | 12840 | 12844.1286 | Fatullah | 17203622.6459 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 12844.1286 | 210535.038 | -197690.9094 | -93.8993 | CHECK
18 | 33 kV Steel Famus feeder |  | 33 | Export | BD001806 | 1 | 161.8755 | 169.307 | 7.4315 | 240000 |  | 1783560 | 1784133.4829 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1784133.4829 | 1983916.4772 | -199782.9943 | -10.0701 | OK
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.899 | 1544.899 | 0 | 240000 |  | 0 | 0 |  | 0 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 0 | -48.0071 | 48.0071 | -100 | CHECK
20 | 33 kV Rani Kamal Steel Feeder |  | 33 | Export | BD001829 | 1 | 1618.8289 | 1644.588 | 25.7591 | 240000 |  | 6182184 | 6184171.8091 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 6184171.8091 | 6138184.9168 | 45986.8923 | 0.74919 | OK
23 | 33 kV Shyampur BSCIC-2. |  | 33 | Export | BD001827 | 1 | 2629.531 | 2665.81 | 36.279 | 240000 |  | 8706960 | 8709759.6213 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 8709759.6213 | 9414139.8717 | -704380.2504 | -7.4822 | OK
24 | 33 kV Chakda Steel Feeder |  | 33 | Export | BD001832 | 1 | 2517.3479 | 2557.981 | 40.6331 | 240000 |  | 9751944 | 9755079.6237 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 9755079.6237 | 9470500.1805 | 284579.4432 | 3.0049 | OK
23 | Aux Tr-1 |  | 0.44kv | Export | DHKG9742 | 1.025 | 351.425 | 353.505 | 2.08 | 2400 |  | 5116.8 | 5116.8 | Fatullah
24 | Aux Tr-2 |  | 0.44kv | Export | DHKG9743 | 1.025 | 124.447 | 129.438 | 4.991 | 2400 |  | 12277.86 | 12277.86 | Fatullah
|  |  | 10: Total |  | 60209639.46 | 60228993.5733 |  |  |  |  | 0 | 60228993.5733 | 62619937.8365 | -2390944.2632 | -3.8182 | OK
|  |  | 9=8-7: Grand Total | 84970656 | 84943343.46 | 84970650.407 | 0.032147
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 33200223.7128
[6 empty] | Fatullah | at 33 KV level |  | 30238.7886
[7 empty] | Export to Other SS |  | 51740187.9056
[6 empty] | Total = |  |  | 84970650.407 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | BD001926 | 1 | 3053.08 | 3102.13 | 49.05 | 160000 | 7848000 |  | 7878843.522 |  | 7848000
16 | 11 kV 20/28 MVA Transformer-2 |  | 11 |  | BD001952 | 1 | 3064.67 | 3113.94 | 49.27 | 160000 | 7883200 |  | 7914181.8619
27 | 11 kV20/28 MVA Transformer-3 |  | 11 |  | BD001927 | 1 | 2152.17 | 2183.97 | 31.8 | 160000 | 5088000 |  | 5107996.4118 |  | 1663056
36 | 11 kV 20/28 MVA Transformer-4 |  | 11 |  | BD001927 | 1 | 2031.86 | 2055.77 | 23.91 | 160000 | 3825600 |  | 3840635.0379 |  | 1663056
|  |  | 7: 0; 8: 0; 10: Total | 24644800 |  | 24741656.8336
| SHYAMPUR 11 kV SIDE |  | 7: 0; 8: 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur |  | 1 | 799.6936 | 841.27 | 41.5764 | 40000 |  | 1663056 | 1664915.738 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1664915.738 | 1892333.6894 | -227417.9515 | -12.0179 | OK
6 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | B426E | 11 |  | BD001943 | 1 | 1100.56 | 1116.9598 | 16.3998 | 40000 |  | 655992 | 656725.5732 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 656725.5732 | 622979.2968 | 33746.2764 | 5.4169 | OK
8 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1606.52 | 1625.62 | 19.1 | 40000 |  | 764000 | 764854.3548 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 764854.3548 | 906406.8147 | -141552.4599 | -15.6169 | OK
10 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1491.05 | 1505.39 | 14.34 | 40000 |  | 573600 | 574241.437 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 574241.437 | 703156.8125 | -128915.3754 | -18.3338 | OK
11 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1411.27 | 1427.59 | 16.32 | 40000 |  | 652800 | 653530.0037 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 653530.0037 | 820616.8729 | -167086.8693 | -20.3611 | OK
12 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3529.38 | 3595.32 | 65.94 | 40000 |  | 2637600 | 2640549.5368 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2640549.5368 | 2858328.4338 | -217778.897 | -7.6191 | OK
13 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2300.68 | 2344.78 | 44.1 | 40000 |  | 1764000 | 1765972.6202 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1765972.6202 | 1793971.9132 | -27999.293 | -1.5607 | OK
15 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 500.99 | 504.69 | 3.7 | 40000 |  | 148000 | 148165.5033 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 148165.5033 | 166368.345 | -18202.8417 | -10.9413 | OK
17 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3319.55 | 3370.17 | 50.62 | 40000 |  | 2024800 | 2027064.2638 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 2027064.2638 | 1986798.8384 | 40265.4254 | 2.0266 | OK
18 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2091.49 | 2125.51 | 34.02 | 40000 |  | 1360800 | 1362321.7356 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1362321.7356 | 1609964.5147 | -247642.7792 | -15.3819 | OK
19 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1561.08 | 1609.74 | 48.66 | 40000 |  | 1946400 | 1948576.5918 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1948576.5918 | 1516958.5966 | 431617.9952 | 28.4529 | OK
20 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 891.78 | 916.9 | 25.12 | 40000 |  | 1004800 | 1005923.6331 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 1005923.6331 | 1095224.8641 | -89301.231 | -8.1537 | OK
22 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1385.17 | 1397.79 | 12.62 | 40000 |  | 504800 | 505364.5004 | Shyampur |  |  |  | 11 kV Delpara Feeder | 505364.5004 | 596520.7166 | -91156.2162 | -15.2813 | OK
23 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3261.15 | 3311.5 | 50.35 | 40000 |  | 2014000 | 2016252.1865 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2016252.1865 | 2248177.5395 | -231925.353 | -10.3161 | OK
24 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1128.58 | 1134.93 | 6.35 | 40000 |  | 254000 | 254284.0394 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 254284.0394 | 285431.9558 | -31147.9164 | -10.9126 | OK
26 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2088.29 | 2117.6 | 29.31 | 40000 |  | 1172400 | 1173711.0544 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1173711.0544 | 1318519.2453 | -144808.1909 | -10.9826 | OK
28 | 11 kV Spare Feeder | spare | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1435.214 | 1450.588 | 15.374 | 40000 |  | 614960 | 615647.6885 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 615647.6885 | 947858.5903 | -332210.9018 | -35.0486 | OK
30 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1414.78 | 1442.65 | 27.87 | 40000 |  | 1114800 | 1116046.6423 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 1116046.6423 | 1219099.1258 | -103052.4836 | -8.4532 | OK
31 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2381.97 | 2404.17 | 22.2 | 40000 |  | 888000 | 888993.0197 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 888993.0197 | 1226715.9898 | -337722.9701 | -27.5307 | OK
35 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 178.05 | 179 | 0.95 | 40000 |  | 38000 | 38042.4941 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 38042.4941 | 89397.93 | -51355.4359 | -57.4459 | CHECK
37 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1277.88 | 1298.4 | 20.52 | 40000 |  | 820800 | 821717.8722 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 821717.8722 | 867119.832 | -45401.9598 | -5.2359 | OK
39 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3859.6597 | 3910.37 | 50.7103 | 40000 |  | 2028412 | 2030680.303 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 2030680.303 | 1872132.9644 | 158547.3386 | 8.4688 | OK
40 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1132.87 | 1134.57 | 1.7 | 40000 |  | 68000 | 68076.042 | Shyampur |  |  |  | 11 kV Igloo Feeder | 68076.042 | 184408.2861 | -116332.244 | -63.0841 | CHECK
41 | 11/0.4 kV Aux Transformer, T-1 |  | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) |  | 0.415 | DPDC | DHK26108 | 1 | 65650.1 | 65952.1 | 302 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) |  | 0.415 |  |  | 1 | 625854 | 633261 | 7407 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 |  | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 24741656.8336 | 24714020 | 24741656.8336 | 0.11183
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 801695.5069
[6 empty] | Shyampur | at 33 KV level |  | 23939961.3267
[6 empty] | Total = |  |  | 24741656.8336 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2679.862 | 2714.548 | 34.686 | 240000 | 0 | 8491132.8 | 8493863.0246
23 | 33 kV Shyampur BSCIC-2. |  | 33 |  | BD001827 | 1 | 2629.531 | 2665.81 | 36.279 | 240000 | 0 | 8706960 | 8709759.6213
|  |  | 10: Total | 0 | 17198092.8 | 17203622.6459
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 |  | 33 | Import | DHK61071 | 1 | 1006470.9 | 1006470.9 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-2 |  | 33 | Import | DHK61067 | 1 | 860148 | 892655.5 | 32507.5 | 270 | 8777025
|  |  | 7: 0; 8: 0; 10: Total | 8777025 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  | 7: 0; 8: 0
2 | 33 kV 20/28 MVA Transformer-1 |  | 33 | Export | DHK61068 | 1 | 1024311.6 | 1024311.6 | 0 | 180 |  | 0
3 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Export | DHK61066 | 1 | 730036.7 | 730036.7 | 0 | 180 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 17203622.6459; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 17203622.6459
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 17203622.6459 | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 17203622.6459
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 4: 17203622.6459
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK61019 | 1.05 | 123536.9 | 167350 | 43813.1 | 180 | 8280675.9 |  | 8399826.1442 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK61018 | 1 | 902252.3 | 950468.5 | 48216.2 | 180 | 8678916 |  | 8803796.5017
|  |  | 7: 0; 8: 0; 10: Total | 16959591.9 |  | 17203622.6459
| SHYAMPUR BISIC 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nama shyampur Feeder |  | 11 | Shympur | HA-021101066-02 | 1 | 46233188 | 47694122 | 1460934 | 1 |  | 1460934 | 1460934 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 1460934 | 1775047.104 | -314113.104 | -17.696 | OK
2 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 24282013 | 24843560 | 561547 | 1 |  | 561547 | 561547 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 561547 | 664547.744 | -103000.744 | -15.4994 | OK
3 | 11 kV H. R Steel |  | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) |  | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 559360.2 | 587566.2 | 28206 | 60 |  | 1692360 | 1692360 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1692360 | 1847173.44 | -154813.44 | -8.3811 | OK
6 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 693053.6 | 712115.6 | 19062 | 60 |  | 1143720 | 1143720 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1143720 | 1448800.128 | -305080.128 | -21.0574 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 708041.4 | 726690.5 | 18649.1 | 60 |  | 1118946 | 1118946 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1118946 | 1325819.904 | -206873.904 | -15.6035 | OK
8 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 421306.3 | 440150 | 18843.7 | 60 |  | 1130622 | 1130622 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1130622 | 1052218.368 | 78403.632 | 7.4513 | OK
9 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 540442.3 | 570270.4 | 29828.1 | 60 |  | 1789686 | 1789686 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 1789686 | 1124308.992 | 665377.008 | 59.181 | FAULT
12 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 51207.4 | 85440.5 | 34233.1 | 60 |  | 2053986 | 2053986 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2053986 | 2314357.824 | -260371.824 | -11.2503 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 350357.3 | 371325.8 | 20968.5 | 60 |  | 1258110 | 1258110 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1258110 | 1329111.36 | -71001.36 | -5.342 | OK
14 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 518177 | 536518.3 | 18341.3 | 60 |  | 1100478 | 1100478 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 1100478 | 1158657.984 | -58179.984 | -5.0213 | OK
15 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 694813.1 | 722666.1 | 27853 | 60 |  | 1671180 | 1671180 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 1671180 | 2088491.328 | -417311.328 | -19.9815 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 907279.3 | 919770 | 12490.7 | 60 |  | 749442 | 749442 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 749442 | 766200.96 | -16758.96 | -2.1873 | OK
17 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 70053.1 | 101750.8 | 31697.7 | 60 |  | 1901862 | 1901862 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1901862 | 1859476.224 | 42385.776 | 2.2794 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| SUB-Station not match |  | 10: Grand Total | 17632873 | 17632873 | 17632873 | 0 |  |  |  | SUB-Station not match
| bscic 33/11 kv ss | [16 empty] | bscic 33/11 kv ss
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 5751528
[6 empty] | Jurain | at 33 KV level |  | 11881345
[6 empty] | Total = |  |  | 17632873 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1392.002 | 1412.48 | 20.478 | 240000 | From Downstream | 4914720 | 4916300.2708
7 | 33 kV Nondolalpur -2 feeder |  | 33 |  | BD001807 | 1 | 1202.282 | 1222.603 | 20.321 | 240000 | 0 | 4877040 | 4878608.1553
|  |  | 10: Total | 0 | 9791760 | 9794908.4261
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) |  | 33 | Import | 00000084 | 1 | 334080704 | 338997600 | 4916896 | 1 | 4916896
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) |  | 33 | Import | 00000070 | 1 | 309115200 | 313996320 | 4881120 | 1 | 4881120
|  |  | 7: 0; 8: 0; 10: Total | 9798016 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NANDALALPUR 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 28/35 MVA T-1 |  | 33 | Export | 00000086 | 1 | 334262976 | 339176960 | 4913984 | 1 |  | 4913984
5 | 33 kV, 28/35 MVA T-2 |  | 33 | Export | 00000083 | 1 | 308549248 | 313427872 | 4878624 | 1 |  | 4878624
|  |  | 10: Total |  | 9792608 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 4: 9794908.4261; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9794908.4261
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 9794908.4261 | 33 KV TX HV SIDE |  | 9792608
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 2300.4261
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.02349%
| TOTAL IMPORT |  | 4: 9794908.4261
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. |  | 11 |  | 00000036 | 1 | 332294976 | 337186176 | 4891200 | 1 | 4891200 |  | 4914543.3842 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000033 | 1 | 307212160 | 312069344 | 4857184 | 1 | 4857184 |  | 4880365.0419
|  |  | 7: 0; 8: 0; 10: Total | 9748384 |  | 9794908.4261
| NANDALALPUR 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Spare | spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | B889Z | 11 |  | 00000026 | 1 | 8000660 | 8420179 | 419519 | 1 |  | 419519 | 422037.4564 | Fatullah |  |  |  | 11 kV Khaza Moinuddin | 422037.4564 | 579356.8008 | -157319.3445 | -27.1541 | OK
10 | 11 kV Chitashal | B489Q | 11 |  | 00000027 | 1 | 36082072 | 36567832 | 485760 | 1 |  | 485760 | 488676.1143 | Shyampur |  |  |  | 11 kV Chitashal | 488676.1143 | 626907.0404 | -138230.926 | -22.0497 | OK
11 | 11 kV Local Feeder | B489G | 11 |  | 00000157 | 1.5 | 19190114 | 19311752 | 121638 | 1 | Estimated | 364898.52 | 367089.0787 | Shyampur | 30 |  |  | 11 kV Local Feeder | 367089.0787 | 471911.02 | -104821.9413 | -22.2122 | OK
12 | 11 kV Rasel Germants |  | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 |  | 00000121 | 1 | 82827040 | 84659512 | 1832472 | 1 |  | 1832472 | 1843472.6956 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 1843472.6956 | 2197883.0829 | -354410.3873 | -16.1251 | OK
14 | 11 kV Nandalalpur | B890X | 11 |  | 00000010 | 1 | 86980384 | 87569944 | 589560 | 1 |  | 589560 | 593099.2465 | Fatullah |  |  |  | 11 kV Nandalalpur | 593099.2465 | 845396.3918 | -252297.1453 | -29.8437 | OK
15 | 11 kV Sharif Bagh | B489SB | 11 |  | 00000132 | 1 | 78453808 | 79634888 | 1181080 | 1 |  | 1181080 | 1188170.2592 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1188170.2592 | 1429052.9803 | -240882.7211 | -16.8561 | OK
18 | 11 kV Spare | spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | B890Y | 11 |  | 00000158 | 1 | 69477432 | 70338192 | 860760 | 1 |  | 860760 | 865927.3143 | Fatullah |  |  |  | 11 KV Nayamati | 865927.3143 | 1006892.0073 | -140964.6931 | -14 | OK
20 | 11 kV Pulpar | B889S | 11 |  | 00000160 | 1 | 11257213 | 12265050 | 1007837 | 1 |  | 1007837 | 1013887.2469 | Fatullah |  |  |  | 11 kV Pulpar | 1013887.2469 | 944347.6364 | 69539.6105 | 7.3638 | OK
21 | 11 kV Shahi Bazar | B489X | 11 |  | 00000170 | 1 | 43910492 | 44378812 | 468320 | 1 |  | 468320 | 471131.4185 | Shyampur |  |  |  | 11 kV Shahi Bazar | 471131.4185 | 593266.4637 | -122135.0451 | -20.5869 | OK
22 | 11 kV Pagla Bazar | B890G | 11 |  | 00000060 | 1 | 52781312 | 53261828 | 480516 | 1 |  | 480516 | 483400.6336 | Fatullah |  |  |  | 11 kV Pagla Bazar | 483400.6336 | 561438.012 | -78037.3784 | -13.8996 | OK
23 | 11 kV Delpara bazar | B489M | 11 |  | 00000063 | 1 | 85270552 | 86688752 | 1418200 | 1 |  | 1418200 | 1426713.738 | Shyampur |  |  |  | 11 kV Delpara bazar | 1426713.738 | 1432420.6462 | -5706.9082 | -0.39841 | OK
24 | 11 kV Bhuighor (Board mill) | E289C | 11 |  | 00000146 | 1 | 46505368 | 47129844 | 624476 | 1 |  | 624476 | 628224.8542 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 628224.8542 | 631758.0829 | -3533.2287 | -0.55927 | OK
25 | 11 kV Spare |  | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 |  | 11 |  | 7803 | 1 | 2634 | 2659 | 25 | 100 |  | 2500 | 2515.008 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 2515.008 | 3407.7571 | -892.7491 | -26.1976 | OK
27 | 33/0.415 kV, 200 kVA AT-2 |  | 11 |  | 7805 | 1 | 78.2 | 83.8 | 5.6 | 100 |  | 560 | 563.3618 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 563.3618 | 711.6199 | -148.2581 | -20.8339 | OK
|  |  | 10: Grand Total | 9794908.4261 | 9736458.52 | 9794908.4261 | 0.60032
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 3944858.9786
[6 empty] | Fatullah | at 33 KV level |  | 3378351.8976
[6 empty] | Matuail | at 33 KV level |  | 2471697.5498
[6 empty] | Total = |  |  | 9794908.4261 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 |  | 132 | Import | 4262 7826 | 1 | 402.926 | 421.365 | 18.439 | 960000 | 0 | 17701440
[6 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 |  | 132 |  | 4262 7815 | 1 | 165.737 | 170.689 | 4.952 | 960000 | 0 | 4753920
2 | [5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 22455360
|  |  | 10: Net Total | 22455360
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 |  | 132 | Main | 41808902823 | 1 | 322.1 | 336.84 | 14.74 | 1200000 | 17688000
|  |  | 132 | Backup | 41808904269 | 1 | 322.16 | 336.91 | 14.75 | 1200000 | 17700000
4 | 132kV Hasnabad Circuit-2 |  | 132 | Imp/Main | 41808902845 | 1 | 132.48 | 136.44 | 3.96 | 1200000 | 4752000
|  |  | 132 | Imp/Backup | 41808904256 | 1 | 132.51 | 136.47 | 3.96 | 1200000 | 4752000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 22440000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 22440000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| POSTOGOLA 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41808902871 | 1 | 333.18 | 347.92 | 14.74 | 1200000 |  | 17688000
|  |  | 132 | Exp/Backup | 41808904257 | 1 | 333.26 | 348 | 14.74 | 1200000 |  | 17688000
5 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41808902846 | 1 | 121.22 | 125.18 | 3.96 | 1200000 |  | 4752000
|  |  | 132 | Exp/Backup | 41808904243 | 1 | 121.22 | 125.18 | 3.96 | 1200000 |  | 4752000
|  |  | 10: Total |  | 22440000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 22455360; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 22455360
|  |  | 6: 132 KV NET IMPORT; 9=8-7: 22455360 | 33 KV NET IMPORT |  | 23277600
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -822240
[11 empty] | LOSS % IN => |  | -3.662%
| 132 KV TOTAL IMPORT |  | 4: 22455360
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE |  | 10: Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41808902807 | 1 | 552.38 | 577.88 | 25.5 | 720000 | 18360000
|  |  | 33 | Backup | 41808904286 | 1 | 553.55 | 578.05 | 24.5 | 720000 | 17640000
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41808902869 | 1 | 200.38 | 207.21 | 6.83 | 720000 | 4917600
|  |  | 33 | Backup | 41808904268 | 1 | 200.7 | 207.25 | 6.55 | 720000 | 4716000
|  |  | 7: 0; 8: 0; 10: Total | 23277600 |  | 22455360
| POSTOGOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 |  | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss | 2.1067 | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  | 10: Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 495.61 | 512.75 | 17.14 | 360000 |  | 6170400 | 6198822.2 |  | 11142690.3141 | IG Gate 33/11 kv ss | 2.5 | 33 kV IG Gate Ckt-2 | 6198822.2 | 7293793.7007 | -1094971.5006 | -15.0124 | OK
|  |  | 33 | Backup | 41808904225 | 1 | 496.29 | 512.77 | 16.48 | 360000 |  | 5932800 | 5960127.7629 |  |  |  |  | 0 | 5960127.7629 | 7293793.7007 | -1333665.9377 | -18.2849 | OK
8 | 33 kV Spare Feeder 2 |  | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 |  | 33 | Main | 41808902810 | 1 | 611.1 | 644.99 | 33.89 | 360000 |  | 12200400 | 12256597.6872 |  |  |  |  | 33kV Postogola circuit-1 | 12256597.6872 | 15011352.865 | -2754755.1778 | -18.3511 | OK
|  |  | 33 | Backup | 41808904252 | 1 | 612.5 | 645.01 | 32.51 | 360000 |  | 11703600 | 11757509.3187 |  |  |  |  | 0 | 11757509.3187 | 15011352.865 | -3253843.5463 | -21.6759 | OK
14 | 31 kV Spare Feeder 4 |  | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 |  | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 |  | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1 | 399.15 | 412.82 | 13.67 | 360000 |  | 4921200 | 4943868.114 |  |  |  |  | 33 kV IG Gate Ckt-1 | 4943868.114 | 7089093.4343 | -2145225.3203 | -30.2609 | OK
|  |  | 33 | Backup | 41812909573 | 1 | 399.65 | 412.75 | 13.1 | 360000 |  | 4716000 | 4737722.9183 |  |  |  |  | 0 | 4737722.9183 | 7089093.4343 | -2351370.516 | -33.1688 | OK
|  |  | 10: Total |  | 22352400 | 22455360 |  | All Backup Meters Added |  |  | 0 | 22455360 | 29394240 | -6938880 | -23.6063 | OK
|  |  | 9=8-7: Grand Total | 22455360 | 22352400 | 22455360 | 0.46062
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola |  | 33 | Import | BD001804 | 1 | 612.5 | 645.01 | 32.51 | 360000 | 11703600 |  | 11757509.3187
2 | 33 kV Postogola Circuit-2 at Shyampur |  | 33 | Import | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 11703600 |  | 11757509.3187
| POSTOGOLA 33 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) |  | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) |  | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0
| POSTOGOLA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK61027 | 1 | 412476.1 | 442129.7 | 29653.6 | 180 |  | 5337648 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60870 | 1 | 897896.4 | 933289.9 | 35393.5 | 180 |  | 6370830
|  |  | 7: 0; 8: 0; 10: Total |  | 11708478
| POSTOGOLA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV 20/28 MVA T-1 Incoming. |  | 11 |  | DHK61005 | 1.165 | 985125.6 | 1010657.7 | 25532.1 | 180 | 5354081.37 |  | 11757509.3187 |  | 23416956
9 | 11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK60861 | 1.165 | 1038479.9 | 1038479.9 | 0 | 180 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 5354081.37 |  | 11757509.3187
| POSTOGOLA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 67083281 | 67884811 | 801530 | 1 |  | 801530 | 818415.5629 | Postogola |  |  |  | 11 kV Station Road Feeder | 818415.5629 | 964969.6559 | -146554.093 | -15.1874 | OK
2 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 594 | 1598.3 | 1004.3 | 1000 |  | 1004300 | 1025457.2503 | Jurain |  |  |  | 11 kV Samon & Sons Feeder. | 1025457.2503 | 1204492.2718 | -179035.0216 | -14.8639 | OK
3 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 26047328 | 26505115 | 457787 | 1 |  | 457787 | 467431.0447 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 467431.0447 | 407994.3823 | 59436.6625 | 14.568 | OK
4 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 80275699 | 81261612 | 985913 | 1 |  | 985913 | 1006682.8975 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1006682.8975 | 1282024.8716 | -275341.9741 | -21.4771 | OK
5 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 471377.73 | 479747.6 | 8369.87 | 60 |  | 502192.2 | 512771.7141 | Postogola |  |  |  | 11 kV Cyca Feeder | 512771.7141 | 575584.882 | -62813.1678 | -10.9129 | OK
6 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 941864.1 | 954801 | 12936.9 | 60 |  | 776214 | 792566.2392 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 792566.2392 | 972773.5086 | -180207.2694 | -18.5251 | OK
7 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 831587.6 | 844942.4 | 13354.8 | 60 |  | 801288 | 818168.4647 | Postogola |  |  |  | 11 kV Munshi Bari | 818168.4647 | 1013780.9955 | -195612.5307 | -19.2953 | OK
8 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 528585.6 | 530111.3 | 1525.7 | 60 |  | 91542 | 93470.4845 | Postogola |  |  |  | 11 kV Cantonment Feeder | 93470.4845 | 133370.1443 | -39899.6598 | -29.9165 | OK
9 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 927947.6 | 951343.8 | 23396.2 | 60 |  | 1403772 | 1433344.7925 | Postogola |  |  |  | 11 kV DIT Feeder. | 1433344.7925 | 1390963.4921 | 42381.3004 | 3.0469 | OK
10 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 469020.9 | 482727.4 | 13706.5 | 60 |  | 822390 | 839715.0135 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 839715.0135 | 1423612.5326 | -583897.5191 | -41.0152 | CHECK
11 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 47773398 | 48828389 | 1054991 | 1 |  | 1054991 | 1077216.1405 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 1077216.1405 | 2497097.0061 | -1419880.8656 | -56.8613 | CHECK
12 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 17714.8 | 19406.2 | 1691.4 | 1000 |  | 1691400 | 1727032.1548 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 1727032.1548 | 2152168.1359 | -425135.9811 | -19.7538 | OK
13 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 62312639 | 63349228 | 1036589 | 1 |  | 1036589 | 1058426.4718 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1058426.4718 | 1360729.5194 | -302303.0477 | -22.2162 | OK
14 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 53.1 | 135 | 81.9 | 1000 |  | 81900 | 83625.3597 | Postogola |  |  |  | 11 kV Rajabari Feeder. | 83625.3597 | 107674.3091 | -24048.9494 | -22.3349 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 |  | 11 |  | ELIB67385 | 1 | 585.41 | 624.41 | 39 | 80 |  | 3120 | 3185.728 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3185.728 | 3713.2428 | -527.5149 | -14.2063 | OK
|  |  | 10: Total | 11757509.3187 | 11514928.2 | 11757509.3187 | 2.1067
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Postogola | at 33 KV level |  | 6620657.715
[6 empty] | Jurain | at 33 KV level |  | 5136851.6038
[6 empty] | Total = |  |  | 11757509.3187 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.899 | 1544.899 | 0 | 240000 | 0 | 0 | 0
| Postogola 33 KV SIDE |  | 10: Total | 0 | 0 | 0
7 | 33 kV IG Gate Ckt-2 |  | 33 | Backup | 41808904225 | 1 | 496.29 | 512.77 | 16.48 | 360000 | 0 | 5932800 | 5960127.7629
17 | 33 kV IG Gate Ckt-1 |  | 33 | Backup | 41812909573 | 1 | 399.65 | 412.75 | 13.1 | 360000 | 0 | 4716000 | 4737722.9183
|  |  | 10: Total | 0 | 10648800 | 10697850.6813
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 |  | 33 | Import | DHK60973 | 1 | 322169.6 | 329357.2 | 7187.6 | 540 | 3881304
6 | 33 kV Postogola Incoming Feeder-2 |  | 33 | Import | DHK60966 | 1 | 515717.3 | 524743.7 | 9026.4 | 540 | 4874256
|  |  | 7: 0; 8: 0; 10: Total | 8755560 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| IG GATE 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK60893 | 1 | 931053.7 | 952602.8 | 21549.1 | 180 |  | 3878838
5 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60975 | 1 | 580754.6 | 607822.8 | 27068.2 | 180 |  | 4872276
|  |  | 10: Total |  | 8751114
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 4: 10697850.6813; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10697850.6813
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 10697850.6813 | 33 KV TX HV SIDE |  | 8751114
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 1946736.6813
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 18.2%
| TOTAL IMPORT |  | 4: 10697850.6813
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month December-2023 |  |  | Name of Feeders. | Month December-2023 | Month November-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK68139 | 1 | 3866.96 | 3878.73 | 11.77 | 180000 | 2118600 |  | 6224107.8852 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK68137 | 1 | 4514.34 | 4522.8 | 8.46 | 180000 | 1522800 |  | 4473742.796
|  |  | 7: 0; 8: 0; 10: Total | 3641400 |  | 10697850.6813
| IG GATE 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Feeder-1 |  | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 |  | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | A619R | 11 |  | DHK60970 | 1 | 354107.8 | 368780.4 | 14672.6 | 60 |  | 880356 | 902364.9 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 902364.9 | 1688724 | -786359.1 | -46.5653 | CHECK
4 | 11 kV Alom Gonj | A581A | 11 |  | DHK60894 | 1 | 520758.3 | 525772.1 | 5013.8 | 60 | 30 | 364898.52 | 374020.983 | Postogola | As per Load |  |  | 11 kV Alom Gonj | 374020.983 | 577380 | -203359.017 | -35.221 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 |  | DHK60895 | 1 | 650759.1 | 665360.2 | 14601.1 | 60 | 90 | 1094695.56 | 1122062.949 | Postogola | As per Load |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1122062.949 | 1533942 | -411879.051 | -26.851 | OK
6 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 |  | DHK68133 | 1 | 3711.29 | 3727.47 | 16.18 | 60000 |  | 970800 | 995070 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 995070 | 1656000 | -660930 | -39.9112 | OK
7 | 11 kV Doyaganj | B587Y | 11 |  | DHK68134 | 1 | 2488.28 | 2501.83 | 13.55 | 60000 |  | 813000 | 833325 | Swamibag |  |  |  | 11 kV Doyaganj | 833325 | 1512000 | -678675 | -44.8859 | CHECK
10 | 11 kV Faridabad | A587F | 11 |  | DHK68140 | 1 | 857.46 | 868.15 | 10.69 | 60000 | 65 | 790613.46 | 810378.7965 | Postogola | As per Load |  |  | 11 kV Faridabad | 810378.7965 | 1123200 | -312821.2035 | -27.8509 | OK
11 | 11 kV Gandaria | A524D | 11 |  | DHK60969 | 1 | 503196.3 | 519989.5 | 16793.2 | 60 | 100 | 1216328.4 | 1246736.61 | Postogola | As per Load |  |  | 11 kV Gandaria | 1246736.61 | 1778304 | -531567.39 | -29.8918 | OK
12 | 11 kV Walter Road | A687W | 11 |  | DHK68136 | 1 | 1075.44 | 1087.27 | 11.83 | 60000 |  | 709800 | 727545 | Banglabazar |  |  |  | 11 kV Walter Road | 727545 | 1269000 | -541455 | -42.6678 | CHECK
13 | 11 kV Murgitola Feeder (F-11) | B587G | 11 |  | DHK68138 | 1 | 4043.16 | 4062.72 | 19.56 | 60000 |  | 1173600 | 1202940 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 1202940 | 2049000 | -846060 | -41.2914 | CHECK
14 | 11 kV Feeder-12 |  | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 |  | DHK60899 | 1 | 777965.1 | 791930.4 | 13965.3 | 60 |  | 837918 | 858865.95 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 858865.95 | 1530696 | -671830.05 | -43.8905 | CHECK
16 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 |  | DHK60967 | 1 | 228309.7 | 236326.9 | 8017.2 | 60 | 47 | 571674.348 | 585966.2067 | Postogola | As per Load |  |  | 11 kV Lohar Pool Feeder (F-14) | 585966.2067 | 822432 | -236465.7933 | -28.752 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB2774 | 1 | 285932 | 286965 | 1033 | 1 |  | 1033 | 1058.825 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1058.825 | 1552 | -493.175 | -31.7767 | OK
|  |  | 10: Grand Total | 9660335.2202 | 9424717.288 | 9660335.2202 | 2.5
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Swamibag | at 33 KV level |  | 2895130.95
[6 empty] | Banglabazar | at 33 KV level |  | 2624979.9
[6 empty] | Postogola | at 33 KV level |  | 4140224.3702
[6 empty] | Total = |  |  | 9660335.2202 | 0
|  |  |  | 1 | 5 | 10 | 15 | 20 | 25 | 30 | AVG
| 11 kV Dholaikal RMU |  |  | 122-90 | 136-88 | 112-68 | 100-57 | 112-65 | 113-57
| 11 kV Alom Gonj |  |  | 29-23 | 41-24 | 37-16 | 74-16 | 37-16 | 29-16
| 11 kV Dhalka Nagar Feeder (F-5) |  |  | 115-90 | 118-90 | 133-68 | 111-61 | 103-71 | 115-61
| 11 kV Farashgonj Feeder (F-6) |  |  | 125-85 | 150-105 | 125-65 | 100-60 | 146-65 | 130-70
| 11 kV Doyaganj |  |  | 107-63 | 132-69 | 200-65 | 92-50 | 101-56 | 108-48
| 11 kV Faridabad |  |  | 83-63 | 86-67 | 75-50 | 71-47 | 81-53 | 81-51
| 11 kV Gandaria |  |  | 137-100 | 134-103 | 123-80 | 121-71 | 117-77 | 126-77
| 11 kV Walter Road |  |  | 95-65 | 105-65 | 90-40 | 71-44 | 94-56 | 90-50
| 11 kV Murgitola Feeder (F-11) |  |  | 140-105 | 205-113 | 205-80 | 112-78 | 185-71 | 185-80
| 11 kV Feeder-12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 11 kV Begumgonj Feeder (F-13) |  |  | 111-82 | 120-85 | 111-71 | 101-56 | 103-63 | 13-60
| 11 kV Lohar Pool Feeder (F-14) |  |  | 65-50 | 71-47 | 56-41 | 50-33 | 56-29 | 50-29
Note on J393: No Reading Due to PT Out
Note on L393: Reading From Higher Side
Note on J650: No Reading due to PT Open
Note on M650: Energy From Bangshal SS End
Note on M655: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month December-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month December-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.09.2023 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 5168036.7336 | 12074336.4406 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 5448670.0794 |  | North | 185523147.2015 | Tejgaon | 37823855.7762 | Tejgaon | 21607276.9197 | 26821171.9379 | -5213895.0182 | -19.4395 | North | 185523147.2015 | 303699254.015 | -63.6988 | Tejgaon | 37823855.7762 | 59346933 | -56.9034 | Tejgaon | 21607276.9197 | 31468806 | -45.6399 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 0 | [5 empty] | Kakrail | 16216578.8565 | 20593626.1987 | -4377047.3423 | -21.2544 | [8 empty] | Kakrail | 16216578.8565 | 27878127 | -71.9113 | 2 | Tejgaon | 31468806 | 196426 | 31665232 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | 9797032.3043
|  |  |  | Maghbazar | 1457629.6275 |  |  |  | Moghbazar | 21706002.7396 | Moghbazar | 11728437.3914 | 15252399.5754 | -3523962.184 | -23.1043 |  |  |  |  | Moghbazar | 21706002.7396 | 36894933 | -69.9757 | Moghbazar | 11728437.3914 | 20573106 | -75.4122 | 3 | Kakrail | 27878127 | 134050 | 28012177 | A1 | Motijheel | 22865869 | 164088 | 23029957
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 8806474.08 |  |  |  |  | Khilgaon | 9977565.3482 | 12685842.0352 | -2708276.6869 | -21.3488 | [8 empty] | Khilgaon | 9977565.3482 | 16321827 | -63.5853 | 4 | Moghbazar | 20573106 | 63535 | 20636641 | A2 | Khilgaon | 16321827 | 59703 | 16381530
|  |  |  | Jigatola | 1792963.0261 |  |  |  | Satmasjid | 28204854.1617 | Satmosjid | 13442024.8686 | 17020995.2428 | -3578970.3742 | -21.0268 |  |  |  |  | Satmasjid | 28204854.1617 | 46167247 | -63.6855 | Satmosjid | 13442024.8686 | 22160943 | -64.8631 | 5 | Khilgaon | 16321827 | 59703 | 16381530 | A3 | Lalbag | 32204138 | 464799 | 32668937
|  |  |  | Paribagh | 7013511.0538 | [5 empty] | Sherebanglanagar | 14762829.2931 | 18349952.7941 | -3587123.501 | -19.5484 | [8 empty] | Sherebangla nagar | 14762829.2931 | 24006304 | -62.6132 | 6 | Satmosjid | 22160943 | 83495 | 22244438 | A4 | Kazla | 38390804 | 86446 | 38477250
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 8315280 |  |  | Dhanmondi | 31494769.6323 | Dhanmondi | 13813128.0726 | 17445142.2053 | -3632014.1327 | -20.8196 |  |  |  |  | Dhanmondi | 31494769.6323 | 53818759.15 | -70.8816 | Dhanmondi | 13813128.0726 | 24555384 | -77.7685 | 7 | Sherebanglanagar | 24006304 | 57477 | 24063781 | A5 | Postogola | 15925283 | 139839 | 16065122
[11 empty] | Jhigatala | 17681641.5597 | 21955056.5988 | -4273415.0391 | -19.4644 | [8 empty] | Jhigatala | 17681641.5597 | 29263375.15 | -65.5015 | 8 | Dhanmondi | 24555384 | 124825 | 24680209 | A6 | Banglabazar | 16227586 | 65470 | 16293056
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 34192185.2138 | Azimpur | 12922881.9021 | 15774856.9994 | -2851975.0973 | -18.0792 |  |  |  |  | Azimpur | 34192185.2138 | 54252662.865 | -58.6698 | Azimpur | 12922881.9021 | 19587741 | -51.5741 | 9 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274 | A7 | N.Gonj (West) | 28707452 | 196212 | 28903664
|  |  |  | Dhanmondi | 8315280 | [5 empty] | Paribagh | 21269303.3118 | 26658917.0753 | -5389613.7635 | -20.2169 | [8 empty] | Paribagh | 21269303.3118 | 34664921.865 | -62.981 | 10 | Azimpur | 19587741 | 236081 | 19823822 | A8 | Siddirgonj | 49639472 | 532212 | 50171684
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 13793023.4657 | 13793023.4657 |  |  | Shamoly | 32101479.6779 | Shyamoli | 12055887.3066 | 13993395.6523 | -1937508.3458 | -13.8459 |  |  |  |  | Shamoly | 32101479.6779 | 53218719 | -65.7828 | Shyamoli | 12055887.3066 | 19516523 | -61.8838 | 11 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448 | A9 | Bashabo | 14583022 | 53363 | 14636385
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 8680459.8613 |  |  |  |  | Adabor | 20045592.3713 | 24675894.9005 | -4630302.5291 | -18.7645 | [8 empty] | Adabor | 20045592.3713 | 33702196 | -68.1277 | 12 | Shyamoli | 19516523 | 64518 | 19581041 | B1 | Narinda | 13978240 | 38770 | 14017010
|  |  |  | RAMNA | 651038.4521 |  | Central | 184833450.1963 | Lalbagh | 65956053.2427 | Lalbagh | 31889316.2164 | 34548667.0633 | -2659350.8469 | -7.6974 | Central | 184833450.1963 | 262953550.91 | -42.2651 | Lalbagh | 65956053.2427 | 70781931 | -7.3168 | Lalbagh | 31889316.2164 | 32204138 | -0.98723 | 13 | Adabor | 33702196 | 255452 | 33957648 | B2 | Maniknagar | 20970662 | 109760 | 21080422
|  |  |  | Kakrail | 1085651.3814 | [5 empty] | Kamrangirchar | 34066737.0263 | 37490818.0675 | -3424081.0412 | -9.1331 | [8 empty] | Kamrangirchar | 34066737.0263 | 38577793 | -13.2418 | 14 | Lalbagh | 32204138 | 464799 | 32668937 | B3 | Jurain | 27684985 | 453096 | 28138081
|  |  |  | Paribagh | 6943770.0278 |  |  |  | Ramna | 27390590.0884 | Ramna | 16429257.6353 | 21620213.0472 | -5190955.4119 | -24.0097 |  |  |  |  | Ramna | 27390590.0884 | 47932700 | -74.997 | Ramna | 16429257.6353 | 28702610 | -74.7042 | 15 | Kamrangirchar | 38577793 | 101944 | 38679737 | B4 | Shyampur | 66519316 | 426920 | 66946236
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 2619829.8982 |  |  |  |  | Rajarbagh | 10961332.453 | 13993106.5411 | -3031774.0881 | -21.6662 | [8 empty] | Rajarbagh | 10961332.453 | 19230090 | -75.4357 | 16 | Ramna | 28702610 | 211333 | 28913943 | B5 | Swamibag | 13880852 | 46920 | 13927772
|  |  |  | Kakrail | 222214.3306 |  |  |  | Bashabo | 23630464.3024 | Bashabo | 8425607.7962 | 11054667.4475 | -2629059.6513 | -23.7823 |  |  |  |  | Bashabo | 23630464.3024 | 39590401.91 | -67.5397 | Bashabo | 8425607.7962 | 14583022 | -73.0798 | 17 | Rajarbagh | 19230090 | 88052 | 19318142 | B6 | Bangshal | 19038085 | 79495 | 19117580
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 15204856.5062 | 19047800.3557 | -3842943.8496 | -20.1753 | [8 empty] | Bonossri | 15204856.5062 | 25007379.91 | -64.4697 | 18 | Bashabo | 14583022 | 53363 | 14636385 | B7 | N.Gonj (East) | 30757520 | 509964 | 31267484
|  |  |  | Shere Bangla Nagar | 2397615.5677 |  |  |  | Motijheel | 26999983.9447 | Motijheel | 15076779.7286 | 19678019.4179 | -4601239.6893 | -23.3826 |  |  |  |  | Motijheel | 26999983.9447 | 41523755 | -53.7918 | Motijheel | 15076779.7286 | 22865869 | -51.6628 | 19 | Bnossri | 25007379.91 | 102145 | 25109524.91 | B8 | Fateullah | 32245904 | 463782 | 32709686
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1500773.1413 | 5620693.7884 |  |  |  |  | Mughdapara | 11923204.2161 | 14984837.3823 | -3061633.1662 | -20.4315 | [8 empty] | Mughdapara | 11923204.2161 | 18657886 | -56.4838 | 20 | Motijheel | 22865869 | 164088 | 23029957 | B9 | Mugdapara | 18657886 | 36172 | 18694058
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 23076672.749 | Banglabazar | 10217940.4172 | 14621588.0922 | -4403647.675 | -30.1174 |  |  |  |  | Banglabazar | 23076672.749 | 35265671 | -52.8196 | Banglabazar | 10217940.4172 | 16227586 | -58.8146 | 21 | Mughdapara | 18657886 | 36172 | 18694058 | C1 | Tejgaon | 31468806 | 196426 | 31665232
|  |  |  | Narinda | 270900.7155 | [5 empty] | Bongshal | 12858732.3318 | 16109427.3226 | -3250694.9908 | -20.1788 | [8 empty] | Bongshal | 12858732.3318 | 19038085 | -48.0557 | 22 | Banglabazar | 16227586 | 65470 | 16293056 | C2 | Satmasjid | 22160943 | 83495 | 22244438
|  |  |  | Motijheel | 172389.5484 |  |  |  | Narinda | 17779685.8692 | Narinda | 9180634.3524 | 11735087.3128 | -2554452.9604 | -21.7677 |  |  |  |  | Narinda | 17779685.8692 | 27859092 | -56.6906 | Narinda | 9180634.3524 | 13978240 | -52.2579 | 23 | Bongshal | 19038085 | 79495 | 19117580 | C3 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448
|  |  |  | RAMNA | 3676630.3833 | [5 empty] | Swamibagh | 8599051.5168 | 11777258.8148 | -3178207.298 | -26.986 | [8 empty] | Swamibagh | 8599051.5168 | 13880852 | -61.4231 | 24 | Narinda | 13978240 | 38770 | 14017010 | C6 | Kakrail | 27878127 | 134050 | 28012177
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 359767888.1936 | Kazla | 48377992.7895 | Kazla | 33989123.3653 | 36372517.6492 | -2383394.2839 | -6.5527 | South | 359767888.1936 | 418742139 | -16.3923 | Kazla | 48377992.7895 | 59361466 | -22.7034 | Kazla | 33989123.3653 | 38390804 | -12.9503 | 25 | Swamibagh | 13880852 | 46920 | 13927772 | D1 | Moghbazar | 20573106 | 63535 | 20636641
|  | Khillgaon 33/11KV S/S |  | Kakrail | 63909.8612 | 4608360 |  |  |  |  | Maniknagar | 14388869.4242 | 16666821.9883 | -2277952.5641 | -13.6676 | [8 empty] | Maniknagar | 14388869.4242 | 20970662 | -45.7422 | 26 | Kazla | 38390804 | 86446 | 38477250 | D2 | Dhanmondi | 24555384 | 124825 | 24680209
|  |  |  | Khilgaon | 301.4616 |  |  |  | Shyampur | 86429930.0062 | Shyampur | 68845753.126 | 71763111.7333 | -2917358.6073 | -4.0653 |  |  |  |  | Shyampur | 86429930.0062 | 88513636 | -2.4109 | Shyampur | 68845753.126 | 66519316 | 3.3792 | 27 | Maniknagar | 20970662 | 109760 | 21080422 | D3 | Ramna | 28702610 | 211333 | 28913943
| 9 |  |  | Maghbazaar | 105125.6925 | [5 empty] | Matuail | 17584176.8802 | 20707811.4636 | -3123634.5833 | -15.0843 | [8 empty] | Matuail | 17584176.8802 | 21994320 | -25.0802 | 28 | Shyampur | 66519316 | 426920 | 66946236 | D4 | Shyamoli | 19516523 | 64518 | 19581041
|  |  |  | Rajarbagh | 4439022.9847 |  |  |  | Postogola | 31931004.7587 | Postogola | 10760882.0852 | 13642394.6213 | -2881512.5361 | -21.1218 |  |  |  |  | Postogola | 31931004.7587 | 43610268 | -36.5766 | Postogola | 10760882.0852 | 15925283 | -47.9924 | 29 | Matuail | 21994320 | 179400 | 22173720 | D5 | Shere b.nagar | 24006304 | 57477 | 24063781
| 10 | Goran 33/11KV S/S |  | Bashabo | 858727.1116 | 7421021 |  |  |  |  | Jurain | 21170122.6735 | 25953929.5907 | -4783806.9172 | -18.4319 | [8 empty] | Jurain | 21170122.6735 | 27684985 | -30.7739 | 30 | Postogola | 15925283 | 139839 | 16065122 | D6 | Rajarbag | 19230090 | 88052 | 19318142
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 50613399.7506 | Narayangonj-West | 25642231.6975 | 30568733.713 | -4926502.0154 | -16.1161 |  |  |  |  | Narayangonj | 50613399.7506 | 59464972 | -17.4886 | Narayangonj- West | 25642231.6975 | 28707452 | -11.9538 | 31 | Jurain | 27684985 | 453096 | 28138081 | D8 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274
|  |  |  | Banosree | 6562293.8884 | [5 empty] | Narayangonj-East | 24971168.053 | 30494026.2393 | -5522858.1863 | -18.1113 | [8 empty] | Narayangonj- East | 24971168.053 | 30757520 | -23.1721 | 32 | Narayangonj-West | 28707452 | 196212 | 28903664 | D9 | Azimpur | 19587741 | 236081 | 19823822
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 6748193.6713 | 8966904 |  |  | Demra | 55093676.0599 | Demra | 16651244.0051 | 19815215.6472 | -3163971.6421 | -15.9674 |  |  |  |  | Demra | 55093676.0599 | 71702210 | -30.146 | Demra | 16651244.0051 | 22062738 | -32.499 | 33 | Narayangonj-East | 30757520 | 509964 | 31267484 | E1 | Demra | 22062738 | 533151 | 22595889
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 38442432.0548 | 44777966.7198 | -6335534.6651 | -14.1488 | [8 empty] | Siddhirgonj | 38442432.0548 | 49639472 | -29.1268 | 34 | Damra | 22062738 | 533151 | 22595889 | E2 | Matuail | 21994320 | 179400 | 22173720
|  |  |  | Bashabo | 2218710.3287 |  |  |  | Fatullah | 87321884.8287 | Fatulla | 26765886.2265 | 31245273.6587 | -4479387.4322 | -14.3362 |  |  |  |  | Fatullah | 87321884.8287 | 96089587 | -10.0407 | Fatulla | 26765886.2265 | 32245904 | -20.4739 | 35 | Siddhirgonj | 49639472 | 532212 | 50171684 | E3 | Sytalakha | 63843683 | 329125 | 64172808
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 14857740 |  |  |  |  | Shitalakha | 60555998.6022 | 65129277.2683 | -4573278.6661 | -7.0218 | [8 empty] | Sytalakhya | 60555998.6022 | 63843683 | -5.4292 | 36 | Fatulla | 32245904 | 463782 | 32709686 | F1 | Kamrangirchar | 38577793 | 101944 | 38679737
|  |  |  | Shyamoli | 3456091.1195 |  | TOTAL=> | 730124485.5914 | TOTAL=> | 730124485.5914 | TOTAL=> | 730124485.5914 | 865025822.3734 | -134901336.782 | -15.5951 |  | 730124485.5914 | 985394943.925 |  | TOTAL=> | 730124485.5914 | 985394943.925 |  | Total=> | 730124485.5914 | 985394943.925 | -34.9626 | 37 | Shitalokko | 63843683 | 329125 | 64172808 | F2 | Banosree | 25007379.91 | 102145 | 25109524.91
|  |  |  | Shere Bangla Nagar | 0 | [23 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823 | G1 | Adabor | 33702196 | 255452 | 33957648
|  |  |  | Satmosjid | 7782407.7736 | [14 empty] | 132KV Import => |  |  |  |  | 734876860.1325 | [8 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823
|  |  |  | Dhanmondi NOCS | 3619241.1069 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 734876860.1325 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 730124485.5914
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 730124485.5914 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.64669
| 13 | Japan garden Building |  | Adabor | 974700 | 974700 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.64669 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 985394943.925
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 4752374.5411 | [8 empty] | System loss at 132kv level => |  |  |  |  | -34.0898
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 1303200 | 1303200
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 7825752 | 8343172
| 16 |  |  | Shere Bangla Nagar | 517420
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 21038400 | 21038400
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 532021.1483 | 10083942.1887
|  |  |  | Lalbagh | 9551921.0405
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 4669608
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 4669608
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 1494886.732 | 6330855.0018
|  |  |  | Rajarbaghl | 1745485.6908
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 3090482.5791 | 3090482.5791
|  | Banshal 33/11 KV S/S |  | Bangshal | 3879844.5885 | 5381604.8082
|  |  |  | Banglabazar | 789122.5172
|  |  |  | Narinda | 712637.7025
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 5307595.6542 | 8426700
|  |  |  | Shamoly | 2472937.1122
|  |  |  | Satmosjit | 646167.2337
|  | Azimpur 33/11 KV |  | jigatola | 230670.4639 | 12560183.914
|  |  |  | Azimpur | 10961556.9626
|  |  |  | RAMNA | 725182.4885
|  |  |  | Paribagh | 642773.9991
|  | T&T 33/11 KV |  | Kakrail | 2057208.2077 | 6715063.5869
|  |  |  | Mogbazar | 3685574.11
|  |  |  | Khilgaon | 972281.2692
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 2140241.5407 | 4208901.6297
|  |  |  | Shamoly | 1620831.5411
|  |  |  | Tejgaon | 444816.5085
|  |  |  | Satmosjit | 3012.0394
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 20001743.805 | 22144700
|  |  |  | Kamrangirchar | 2142956.195
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 2235348.2879 | 2971786.5315
|  |  |  | Kakrail | 736438.2437
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 304879.4917
|  |  |  | Shere Bangla Nagar | 681840.3498
|  |  |  | Shamoly | 4506027.5339
|  |  |  | Satmosjit | 2485822.5391
|  | Banasree 33/11SS |  | Khilgaon | 1749581.874
|  |  |  | Bansree | 5995906.298 | 5995906.298
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 507207.0721 | 10942848
|  |  |  | Bashabo | 4235456.2545
|  |  |  | Mugdapara | 2475344.3493
|  |  |  | Maniknagor | 3724840.3241
|  | DMC |  | Bangshal | 1996223.5882
|  |  |  | RAMNA | 1138484.8495 | 3166609.8342
|  |  |  | Lalbagh | 2028124.9847
|  | Green Road Dormatory |  | Paribagh | 4900840.9508
|  |  |  | Shere Bangla Nagar | 3962298.0898
|  | BSMMU 33/11KV S/S |  | Kakrail | 1132633.7173
|  |  |  | Paribagh | 1768407.2801
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 5937544.7172
|  |  |  | Satmasjid | 2524615.2828
|  | Dhaka University 33/11 KV SS |  | RAMNA | 1050000
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 3021006.1071
|  |  |  | Kakrail | 755863.7168
|  |  |  | Tejgaon | 1920766.8661
|  | BGB 33/11 KV SS |  | Kamrangirchar | 5680151.8839
|  |  |  | Jigatola | 2136424.3249
|  |  |  | Azimpur | 1429303.7913
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2042407.6381
|  | BB Avenue 33/11 KV SS |  | Narinda | 1334139.2616
|  |  |  | Ramna | 2994834.1293
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 12218383.7448
|  |  |  | Dhanmondi | 1573727.474
|  | Ispahani 33/11 KV SS |  | Moghbazar | 1810499.9613
|  |  |  | Kakrail | 1904140.0851
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 5205228.9474
|  |  |  | Total=> | 308049897.6736 | 211035636.2427
NORTH ZONE TOTAL=>
|  | NOCS |  | 308049897.6736 |  | 200857461
|  | diff |  |  | -308049897.6736
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 4436400
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 4436400
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 225789.5397 | 10532528.9948
|  |  |  | Swamibagh | 3681953.2733
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 6624786.1817
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 6803838
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 6803838
| 4 | Maderteck 33/11KV S/S |  | Banosree | 2646656.3198 | 12452469.6056
|  |  |  | Bashabo | 1112714.1015
|  |  |  | Maniknagar | 157809.6742
|  |  |  | Mugdapara | 8535289.5103
| 5 | Kazla 33/11KV S/S |  | Matual | 883317.7427 | 25422608.5019
|  |  |  | Jurain | 4151926.0698
|  |  |  | Swamibagh | 1190813.3489
|  |  |  | Maniknagar | 1776208.8441
|  |  |  | Shyampur | 1651530.0494
|  |  |  | Kazla | 15768812.4471
|  | Shyampur 132/11KV S/S |  | Shyampur | 33200223.7128 | 33230462.5014
|  |  |  | Fatullah. | 30238.7886
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 24741656.8336
|  |  |  | Fatullah | 801695.5069
|  |  |  | Shyampur | 23939961.3267
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 5751528 | 17632873
|  |  |  | Jurain | 11881345
| 8 | Postogola 33/11KV S/S |  | Jurain | 5136851.6038 | 11757509.3187
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 6620657.715
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 7912107.8774 | 9074862.6032
|  |  |  | Narayanganj (West) | 1178307.0346
|  |  |  | Shitalakhy | 1162754.7258
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 1026631.914 | 10417476.1158
|  |  |  | Shitalakhy | 7462539.9042
|  |  |  | Narayanganj (West) | 1924205.1375
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 4099.1602
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 1219807.293
| 11 |  |  | Narayanganj (West) | 14560974.8294 | 15780782.1223
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 13362125.8865 | 13362125.8865
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 8726898.0153 | 8726898.0153
|  |  |  | Matuail | 237057.3856
| 14 | Sarulia 33/11KV S/S |  | Demra | 10462485.8741 | 12169289.9577
|  |  |  | Matuail | 1706804.0836
|  | Demra 33/11KV S/S |  | Matuail | 5326046.2717 | 16512880
| 15 |  |  | Demra | 1522408.4876
|  |  |  | Siddhirganj | 9664425.2407
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 893473.9806
| 16 |  |  | Narayanganj (East) | 4674611.5413 | 10263535.2614
|  |  |  | Narayanganj (West) | 5588923.7201
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 2389820.9759 | 11301870.9198
|  |  |  | Narayanganj (East) | 8912049.9439
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 4136957.5661 | 14624362.6274
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 357651.0584
|  |  |  | Fatullah | 3170500.1559
|  |  |  | Matuail | 6959253.8469
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 875816 | 875816
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 908496.4888
|  |  |  | Maniknagar | 7595724.5533 | 7595724.5533
|  | IG Gate 33/11 kv |  | Swamibagh | 2895130.95 | 9660335.2202
|  |  |  | Banglabazr | 2624979.9
|  |  |  | Postogola | 4140224.3702
|  | Motijil 33/11kv |  | kamlapur | 5074025.0166 | 5396519.7
|  |  |  | RAMNA | 322494.6834
|  | Mitford 33/11kv |  | Banshal | 5481891.0138 | 5789417.4
|  |  |  | Lalbagh | 307526.3862
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 3944858.9786 | 9794908.4261
|  |  |  | Fatullah | 3378351.8976
|  |  |  | Matuail | 2471697.5498
|  | MI CEMENT |  | Shitalakhy | 11776320 | 11776320
|  | Dapa 33/11 kV |  | Fatullah | 11472992 | 11472992
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 6220917.0877 | 12909900
|  |  |  | Siddhirganj | 6688982.9123
|  | Amulia 33/11 KV SS |  | Mugdapara | 912570.3566 | 5578920
|  |  |  | Demra | 4666349.6434
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 8762039.4331
|  | P&T 33/11 KV SS |  | Motijeel | 1730675.811
|  |  |  | RAMNA | 2140357.6293
|  |  |  | Rajarbagh | 1924585.0607
|  | Kazla 132/33 KV SS |  | Kazla | 18220310.9182
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 2852238.7169
|  |  |  | Motijeel | 1677831.9057
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 13363148.1054
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 1970097.4469
|  |  |  | Swamibagh | 831153.9446
|  |  |  | Narinda | 238170.4911
|  | 132 KV Shah Cement |  | Sitalakhya | 15036000
|  | 132 KV Metro Rail |  | Motijeel | 15360
|  |  |  | Total=> | 422074587.9178 | 320133471.5651
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 422074587.9178
| Diff zone&Nocs |  |  |  | 90524654.4074
|  |  |  | Diff= | 0

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 21607276.9197 | 21607276.9197 | 0 | 0
Kakrail | 16216578.8565 | 16216578.8565 | 0 | 0
Moghbazar | 11728437.3914 | 11728437.3914 | 0 | 0
Khilgaon | 9977565.3482 | 9977565.3482 | 0 | 0
Satmosjid | 13442024.8686 | 13442024.8686 | 0 | 0
Sherebanglanagar | 14762829.2931 | 14762829.2931 | 0 | 0
Dhanmondi | 13813128.0726 | 13813128.0726 | 0 | 0
Jhigatala | 17681641.5597 | 17681641.5597 | 0 | 0
Azimpur | 12922881.9021 | 12922881.9021 | 0 | 0
Paribagh | 21269303.3118 | 21269303.3118 | 0 | 0
Shyamoli | 12301712.1942 | 12055887.3066 | -245824.8876 | -2.039
Adabor | 20045592.3713 | 20045592.3713 | 0 | 0
Lalbagh | 31889316.2164 | 31889316.2164 | 0 | 0
Kamrangirchar | 34066737.0263 | 34066737.0263 | 0 | 0
Ramna | 16429257.6353 | 16429257.6353 | 0 | 0
Rajarbagh | 10961332.453 | 10961332.453 | 0 | 0
Bashabo | 8425607.7962 | 8425607.7962 | 0 | 0
Bonoseeri | 15204856.5062 | 15204856.5062 | 0 | 0
Motijheel | 15076779.7286 | 15076779.7286 | 0 | 0
Mughdapara | 11923204.2161 | 11923204.2161 | 0 | 0
Banglabazar | 10217940.4172 | 10217940.4172 | 0 | 0
Bongshal | 12858732.3318 | 12858732.3318 | 0 | 0
Narinda | 9180634.3524 | 9180634.3524 | 0 | 0
Swamibagh | 8599051.5168 | 8599051.5168 | 0 | 0
Kazla | 33989123.3653 | 33989123.3653 | 0 | 0
Maniknagar | 14388869.4242 | 14388869.4242 | 0 | 0
Shyampur | 68845753.126 | 68845753.126 | 0 | 0
Matuail | 17584176.8802 | 17584176.8802 | 0 | 0
Postogola | 10760882.0852 | 10760882.0852 | 0 | 0
Jurain | 21170122.6735 | 21170122.6735 | 0 | 0
Narayangonj-West | 25642231.6975 | 25642231.6975 | 0 | 0
Narayangonj-East | 24971168.053 | 24971168.053 | 0 | 0
Damra | 16651244.0051 | 16651244.0051 | 0 | 0
Siddhirgonj | 38442432.0548 | 38442432.0548 | 0 | 0
Fatulla | 26765886.2265 | 26765886.2265 | 0 | 0
Shitalakha | 60555998.6022 | 60555998.6022 | 0 | 0
TOTAL=> | 730370310.479 | 730124485.5914 | -245824.8876 | -0.033669

## Linked_11KV
SL | Feeder_Name | FEEDER_NO | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | SUBSTN_CODE | November23_Consumption | October23_Consumption | September23_Consumption | August23_Consumption | July23_Consumption | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 11634850 | 12489127 | 854277 | 1 | 0 | 854277 | 852382.2989 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1117275.2423 | 1327224.0724 | 1457854.4301 | 1314371.1616 | 1273734.3863 | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | C301M | 11 | 0 | HA021100463-02 | 1 | 53414203 | 54398317 | 984114 | 1 | 0 | 984114 | 981931.3334 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1079510.4987 | 1506112.4428 | 1598079.2811 | 1562022.8871 | 1571851.4764 | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | C3011 | 11 | 0 | HA021101078-02 | 1 | 67706878 | 68510069 | 803191 | 1 | 0 | 803191 | 801409.6026 | Paribag | Dhanmondi 33/11KV S/S | 1 | 967771.1752 | 1200141.0854 | 2105982.2036 | 2198394.2713 | 2202528.7234 | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 | 0 | DHK60882 | 1 | 242194.26 | 247026.69 | 4832.43 | 60 | 0 | 289945.8 | 289302.7292 | Paribag | Dhanmondi 33/11KV S/S | 1 | 325387.5579 | 424694.4888 | 424650.6487 | 429515.8245 | 406161.3393 | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | C301P | 11 | 0 | DHK60889 | 1 | 296567.58 | 299102.92 | 2535.34 | 60 | 0 | 152120.4 | 151783.0121 | Paribag | Dhanmondi 33/11KV S/S | 1 | 122058.3971 | 224979.6606 | 224715.2737 | 240975.4757 | 236479.8549 | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 0 | 11 | 0 | DHK60890 | 1 | 726.52 | 731.24 | 4.72 | 60000 | 0 | 283200 | 282571.8907 | Paribag | Dhanmondi 33/11KV S/S | 1 | 343779.459 | 423304.2367 | 422384.6367 | 444161.7425 | 451511.4107 | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | D301H | 11 | 0 | DHK60880 | 1 | 581064.2 | 584988.43 | 3924.23 | 60 | 0 | 235453.8 | 234931.587 | Ramna | Dhanmondi 33/11KV S/S | 1 | 287616.8148 | 330665.314 | 381236.2759 | 740264.9629 | 797710.3468 | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 0 | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 kV TSC Feeder | D301U | 11 | 0 | DHK60873 | 1 | 963916.78 | 969708.1 | 5791.32 | 60 | 0 | 347479.2 | 346708.5258 | Ramna | Dhanmondi 33/11KV S/S | 1 | 436581.914 | 552858.9173 | 527789.8466 | 622520.63 | 596411.0072 | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | C301S | 11 | 0 | DHK60883 | 1 | 28971.13 | 29139.32 | 168.19 | 60 | 0 | 10091.4 | 10069.0183 | Paribag | Dhanmondi 33/11KV S/S | 1 | 10788.5554 | 14763.0376 | 14899.4821 | 7435.3517 | 6184.9227 | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 0 | 11 | 0 | DHK60871 | 1 | 563612.73 | 574627.71 | 11014.98 | 60 | 0 | 660898.8 | 659432.9925 | Paribag | Dhanmondi 33/11KV S/S | 1 | 837287.7716 | 1020090.0393 | 1178402.3777 | 1167367.0478 | 1168612.8044 | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | C301E | 11 | 0 | DHK60981 | 1 | 143677.95 | 154561.42 | 10883.47 | 60 | 0 | 653008.2 | 651559.893 | Paribag | Dhanmondi 33/11KV S/S | 1 | 749226.2334 | 894951.6314 | 961999.4403 | 1097238.176 | 1271574.285 | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | C301D | 11 | 0 | DHK61110 | 1 | 501237.66 | 518925.19 | 17687.53 | 60 | 0 | 1061251.8 | 1058898.0495 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1248319.0123 | 1468536.7336 | 1572278.7706 | 1519703.9096 | 1444426.5973 | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 0 | 11 | 0 | DHK61115 | 1 | 449664.26 | 467590.06 | 17925.8 | 60 | 0 | 1075548 | 1073162.5419 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1368467.8334 | 1667970.4775 | 1771267.2548 | 1745625.9685 | 1732224.4313 | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | D301M | 11 | 0 | DHK61107 | 1 | 556021.54 | 557180.75 | 1159.21 | 60 | 0 | 69552.6 | 69398.3393 | Ramna | Dhanmondi 33/11KV S/S | 1 | 102971.2474 | 132172.5149 | 123208.813 | 139745.6654 | 147111.9421 | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 0 | 11 | 0 | DHK61112 | 1 | 354429.92 | 356318.61 | 1888.69 | 60 | 0 | 113321.4 | 113070.0644 | Paribag | Dhanmondi 33/11KV S/S | 1 | 143833.6059 | 183722.5048 | 209615.174 | 205991.8784 | 207014.0635 | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | C601R | 11 | 0 | DHK61108 | 1 | 756877.47 | 764862.93 | 7985.46 | 60 | 0 | 479127.6 | 478064.9428 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 635092.6529 | 850234.9813 | 921150.1931 | 935875.2367 | 955769.4815 | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 0 | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 11 kV DPH Sw/S-1 | 0 | 11 | 0 | DHK60978 | 1 | 838049.17 | 848198.12 | 10148.95 | 60 | 0 | 608937 | 607586.4385 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 690742.9278 | 869594.4982 | 880434.4894 | 909712.3671 | 894673.7786 | 964542.5031 | 717844.627
20 | WASA Bhaban | C605M | 11 | 0 | 8536188 | 1.4 | 271216 | 271216 | 0 | 1000 | 897180 | 897180 | 897559.4039 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 933040.8402 | 1122893.6635 | 1128091.0061 | 1031848.2658 | 1051553.1772 | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 0 | 11 | 0 | 8536178 | 1.4 | 586004 | 587512 | 1508 | 44 | 0 | 92892.8 | 92932.083 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 218864.9052 | 224818.1088 | 56030.9835 | 205730.3432 | 203697.4272 | 26163.5003 | 291323.9838
22 | Air Port Road (West) | D505A | 11 | 0 | 8536182 | 1.4 | 4761.7 | 5005.7 | 244 | 1000 | 0 | 341600 | 341744.4575 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 711222.6426 | 1042454.0487 | 996313.4361 | 1009777.8086 | 1128128.4372 | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | C172C | 11 | 0 | 8536193 | 1.4 | 32421.4 | 32437.1 | 15.7 | 1000 | 0 | 21980 | 21989.295 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | (UTC) Tower | D505U | 11 | 0 | DHK00183 | 1.4 | 18092.4 | 18493.7 | 401.3 | 444.44 | 0 | 249695.2808 | 249800.8732 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 276538.0329 | 285253.3218 | 290292.9413 | 349161.1513 | 363430.7232 | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | C605O | 11 | 0 | 8536190 | 1.4 | 51744.1 | 51744.1 | 0 | 1000 | 20 | 54930.96 | 54954.1895 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 46976.984 | 0 | 0 | 110790.7123 | 63163.9823 | 0 | 0
26 | Panthopath | D505P | 11 | 0 | 8536184 | 1.4 | 39056.5 | 39621.9 | 565.4 | 1000 | 0 | 791560 | 791894.7388 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 929616.6174 | 1035454.7302 | 1172086.0871 | 1196734.0813 | 1204221.3334 | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | C605N | 11 | 0 | DHK00190 | 1.4 | 57494.3 | 57763 | 268.7 | 444.44 | 0 | 167189.4392 | 167260.1411 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 217096.7452 | 236270.9269 | 238706.8937 | 200780.8678 | 155748.3677 | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 0 | 11 | 0 | DHK00021 | 1.4 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Aux. Transformer, AT-1 | 0 | 11 | 0 | 85-12906 | 1.4 | 69426 | 69547 | 121 | 10 | 0 | 1694 | 1694.7164 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1765.989 | 2388.6563 | 2990.8959 | 2900.021 | 3641.847 | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 0 | 11 | 0 | 85-12909 | 1.4 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Police Bhaban | D315I | 11 | T-1 | DHK 00005 | 1 | 74352.7 | 74521.9 | 169.2 | 444.44 | 0 | 75199.248 | 76206.8169 | Ramna | New Ramna 33/11KV S/S | 15 | 98323.9544 | 113280.4639 | 112636.0604 | 117855.6107 | 121266.9463 | 121013.0538 | 111715.2077
32 | Baitul Mukarram (OLD Water Works) | 0 | 11 | T-1 | DHK 00010 | 1 | 17723.4 | 17725.1 | 1.7 | 444.44 | 0 | 755.548 | 765.6713 | Ramna | New Ramna 33/11KV S/S | 15 | 301881.114 | 0 | 0 | 0 | 0 | 0 | 0
33 | GPO | D3157 | 11 | T-1 | DHK 00060 | 1 | 681.6 | 1138.7 | 457.1 | 444.44 | 0 | 203153.524 | 205875.5083 | Ramna | New Ramna 33/11KV S/S | 15 | 264367.4251 | 254768.0345 | 252148.1113 | 248107.5506 | 224260.1714 | 278965.4908 | 233730.721
34 | Culvert Road | D315C | 11 | T-1 | 8536184 | 1 | 40342.5 | 40530.9 | 188.4 | 444.44 | 304292.984 | 304292.984 | 308370.1012 | Ramna | New Ramna 33/11KV S/S | 15 | 586507.5886 | 1175263.5465 | 1013459.3684 | 1052444.418 | 990314.9211 | 787025.6832 | 769934.2629
35 | Secretariat (East) | D315E | 11 | T-1 | DHK00059 | 1 | 81748.6 | 81751 | 2.4 | 444.44 | 0 | 1066.656 | 1080.9478 | Ramna | New Ramna 33/11KV S/S | 15 | 7972.2125 | 1672.5368 | 765.313 | 950.0836 | 1673.5834 | 2240.1359 | 29358.1395
36 | Siddik Bazar | B615S | 11 | T-1 | DHK00076 | 1 | 45245.7 | 47897.2 | 2651.5 | 444.44 | 0 | 1178432.66 | 1194222.0745 | Bangshal | New Ramna 33/11KV S/S | 15 | 1547982.2206 | 1854662.4712 | 1902703.0751 | 1396125.2558 | 499406.3237 | 894134.2296 | 765262.7858
37 | Bokshi Bazar | D315X | 11 | T-1 | DHK 00206 | 1 | 91450.6 | 92431.2 | 980.6 | 444.44 | 0 | 435817.864 | 441657.2379 | Ramna | New Ramna 33/11KV S/S | 15 | 530285.0026 | 560480.6352 | 561829.7499 | 563173.3752 | 477921.1318 | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 0 | 11 | T-1 | DHK00198 | 1 | 51162 | 51950.5 | 788.5 | 444.44 | 0 | 350440.94 | 355136.3778 | Ramna | New Ramna 33/11KV S/S | 15 | 406494.2583 | 588235.7049 | 500739.7682 | 521233.9697 | 36728.3702 | 1058898.5083 | 1085933.5304
39 | TNT RMU | D315Z | 11 | T-1 | DHK 00207 | 1 | 64922.1 | 65792.5 | 870.4 | 444.44 | 0 | 386840.576 | 392023.72 | Ramna | New Ramna 33/11KV S/S | 15 | 391967.1155 | 395125.5127 | 407146.495 | 424144.4724 | 438569.3066 | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 0 | 11 | T-1 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 35665.375
41 | Secretariat (West) | D315W | 11 | T-2 | DHK 00006 | 1.44 | 73143.7 | 73404.3 | 260.6 | 444.44 | 0 | 166782.3322 | 169016.9913 | Ramna | New Ramna 33/11KV S/S | 15 | 331909.7812 | 504156.8291 | 472288.1335 | 522274.5375 | 534325.4145 | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 0 | 11 | T-2 | DHK00197 | 1.44 | 89232.8 | 89265.4 | 32.6 | 444.44 | 0 | 20863.7914 | 21143.3381 | Ramna | New Ramna 33/11KV S/S | 15 | 3897.5261 | 12747.4425 | 1125.4602 | 1246464.4649 | 757545.2503 | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | D315A | 11 | T-2 | DHK00186 | 1.44 | 38231 | 39861.5 | 1630.5 | 444.44 | 0 | 1043509.5648 | 1057491.1911 | Ramna | New Ramna 33/11KV S/S | 15 | 977526.1249 | 1189218.8524 | 1357169.9895 | 1293561.4671 | 1334026.873 | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | D3153 | 11 | T-2 | DHK00030 | 1.44 | 56794.4 | 57092.1 | 297.7 | 444.44 | 0 | 190526.0947 | 193078.8884 | Ramna | New Ramna 33/11KV S/S | 15 | 172686.9812 | 222492.5951 | 223201.274 | 228427.247 | 210464.4166 | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | D3152 | 11 | T-2 | DHK 00008 | 1.44 | 564 | 615.7 | 51.7 | 444.44 | 0 | 33087.6691 | 33530.9994 | Ramna | New Ramna 33/11KV S/S | 15 | 53280.9537 | 61024.9905 | 71264.1421 | 71075.3031 | 68978.774 | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 0 | 11 | T-2 | DHK00196 | 1.44 | 29843.6 | 30109.4 | 265.8 | 444.44 | 0 | 170110.2989 | 172389.5484 | Motijheel | New Ramna 33/11KV S/S | 15 | 335231.5364 | 454930.0034 | 443071.1857 | 477711.0916 | 494476.0375 | 481492.0598 | 701782.0483
47 | Jail | B678Z | 11 | T-2 | DHK00009 | 1.44 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | Kosturi Bazar | D315K | 11 | T-3 | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 | 44349 | 44349 | 44943.217 | Ramna | New Ramna 33/11KV S/S | 15 | 0 | 254911.0541 | 109455.5914 | 110597.9648 | 782852.0054 | 108530.1819 | 101993.6695
49 | Kaptan Bazar | B124K | 11 | T-3 | HA021101251-02 | 1 | 8299757 | 8567076 | 267319 | 1 | 0 | 267319 | 270900.7155 | Narinda | New Ramna 33/11KV S/S | 15 | 367694.0766 | 419318.091 | 424171.1844 | 443349.7565 | 434935.9868 | 427872.7434 | 409490.3581
50 | G.T.V | D315G | 11 | T-3 | HA-021101054-02 | 1 | 73968193 | 74336827 | 368634 | 1 | 0 | 368634 | 373573.2004 | Ramna | New Ramna 33/11KV S/S | 15 | 423322.7388 | 579351.6265 | 620088.9847 | 609639.126 | 653967.7221 | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | B615K | 11 | T-3 | HA021100951-02 | 1 | 8159834 | 8462332 | 302498 | 1 | 0 | 302498 | 306551.0668 | Bangshal | New Ramna 33/11KV S/S | 15 | 320999.3644 | 441368.6747 | 366764.7103 | 373997.3699 | 641935.1027 | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.4 | T-3 | 2436 | 1 | 67991 | 68252 | 261 | 10 | 0 | 2610 | 2644.9705 | Ramna | New Ramna 33/11KV S/S | 15 | 2870.0252 | 2847.8614 | 0 | 0 | 0 | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.4 | T-3 | 2437 | 1 | 90000 | 90009 | 9 | 10 | 0 | 90 | 91.2059 | Ramna | New Ramna 33/11KV S/S | 15 | 0 | 4943.0737 | 3443.9428 | 3735.9019 | 3663.8273 | 3672.2594 | 3624.4279
54 | Pioneer | D304P | 11 | 0 | 06604395 | 1 | 24231.18 | 24289.89 | 58.71 | 8000 | 0 | 469680 | 477280.9094 | Ramna | Kakrail 33/11KV S/S | 4 | 570908.4836 | 784360.9682 | 828175.4667 | 850072.0555 | 872559.2 | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | D604L | 11 | 0 | DHK-00102 | 1 | 95296.1 | 97162 | 1865.9 | 444.444 | 0 | 829288.0596 | 842708.566 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1050082.5289 | 1392792.0181 | 1485476.6819 | 1494821.3647 | 1589289.5218 | 1570646.0565 | 1456807.534
56 | Montri Para | C604B | 11 | 0 | DHK-00110 | 1 | 12973.5 | 13024.5 | 51 | 2222.22 | 0 | 113333.22 | 115167.3103 | Kakrail | Kakrail 33/11KV S/S | 4 | 51314.9581 | 167051.5164 | 197223.0332 | 196663.3629 | 206488.6824 | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 0 | 11 | 0 | 9119865 | 1 | 73065.6 | 73065.6 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 4 | 684720.7122 | 2230006.6883 | 2380457.3749 | 2409184.7946 | 2711345 | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | High Court | D3046 | 11 | 0 | 1025651 | 1 | 30191.9 | 30298.4 | 106.5 | 1000 | 0 | 106500 | 108223.5072 | Ramna | Kakrail 33/11KV S/S | 4 | 181822.4648 | 251110.6689 | 202322.6667 | 325169.1484 | 265125 | 281963.0422 | 304725.5352
60 | Secretaiat | 0 | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Shanti Nagar Bazar | D604N | 11 | 0 | 06604402 | 1 | 5809.98 | 5832.19 | 22.21 | 40000 | 0 | 888400 | 902777.1248 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1155190.1048 | 1443886.346 | 1590213.609 | 1510645.8477 | 1601052 | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 0 | 11 | 0 | 9119867 | 1 | 33058.1 | 33187 | 128.9 | 1000 | 0 | 128900 | 130986.0101 | Kakrail | Kakrail 33/11KV S/S | 4 | 77638.4937 | 216622.9377 | 242037.4816 | 236872.8291 | 224220 | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 0 | 11 | 0 | DHK00199 | 1 | 79666.3 | 79852.8 | 186.5 | 2222.22 | 0 | 414444.03 | 421151.0466 | Kakrail | Kakrail 33/11KV S/S | 4 | 183819.1042 | 639993.908 | 715946.6275 | 682140.9217 | 703183.7413 | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 0 | 11 | 0 | DHK00027 | 1 | 58241 | 59278.4 | 1037.4 | 2222.22 | 0 | 2305331.028 | 2342638.5829 | Kakrail | Kakrail 33/11KV S/S | 4 | 1933413.755 | 1067396.9898 | 1227916.0084 | 1208524.4599 | 1467416.3104 | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | D304B | 11 | 0 | D1025656 | 1 | 70601.3 | 71184.1 | 582.8 | 1000 | 0 | 582800 | 592231.5492 | Ramna | Kakrail 33/11KV S/S | 4 | 791846.372 | 917673.5431 | 1028330.0287 | 1027534.5089 | 1059146.6 | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | D304F | 11 | 0 | D0086137 | 1 | 27773.3 | 28085.4 | 312.1 | 1000 | 0 | 312100 | 317150.7661 | Ramna | Kakrail 33/11KV S/S | 4 | 438773.4499 | 432945.982 | 472221.3068 | 517539.8234 | 576508 | 916863.5723 | 907912.3538
67 | Judges Complex | C604JC | 11 | 0 | 06604344 | 1 | 686.38 | 688.26 | 1.88 | 40000 | 0 | 75200 | 76416.9741 | Kakrail | Kakrail 33/11KV S/S | 4 | 88351.0596 | 118357.8949 | 136165.0797 | 135933.8524 | 151904 | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 0 | 11 | 0 | 39333 | 1 | 499183 | 499707 | 524 | 1 | 0 | 524 | 532.48 | Kakrail | Kakrail 33/11KV S/S | 4 | 2999.9201 | 3752.665 | 0 | 0 | 0 | 0 | 0
69 | Auxiliary Transformer, AT-2 | 0 | 11 | 0 | 39254 | 1 | 1228762 | 1232295 | 3533 | 1 | 0 | 3533 | 3590.1751 | Kakrail | Kakrail 33/11KV S/S | 4 | 0 | 1874.3332 | 6333.0946 | 25918.4591 | 0 | 0 | 0
70 | 11 kV Jamuna (F1) | C6101JG | 11 | 0 | BD017073 | 1 | 0.4177 | 0.4288 | 0.0111 | 2000 | 0 | 22.2 | 22.3208 | Kakrail | BSMMU 33/11KV S/S | 101 | 20.9345 | 34.3292 | 8.7511 | 22.0654 | 24.7258 | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | C6101PP | 11 | 0 | BD017074 | 1 | 3012.43 | 3027.97 | 15.54 | 2000 | 0 | 31080 | 31249.1675 | Kakrail | BSMMU 33/11KV S/S | 101 | 40077.555 | 42742.7844 | 43083.9288 | 43219.8277 | 44627.1399 | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 | 0 | BD017075 | 1 | 1878.4 | 1901.41 | 23.01 | 2000 | 0 | 46020 | 46270.4855 | Kakrail | BSMMU 33/11KV S/S | 101 | 47907.8759 | 87211.9487 | 84458.3395 | 31822.749 | 77353.7092 | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 | 0 | BD017076 | 1 | 3350.25 | 3398.96 | 48.71 | 2000 | 0 | 97420 | 97950.2541 | Kakrail | BSMMU 33/11KV S/S | 101 | 144186.603 | 174503.2711 | 172111.8499 | 179215.5198 | 177543.6485 | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 | 0 | BD017077 | 1 | 15660.41 | 15821.61 | 161.2 | 2000 | 0 | 322400 | 324154.8134 | Kakrail | BSMMU 33/11KV S/S | 101 | 500335.3629 | 627271.1967 | 702896.8986 | 697529.5567 | 750881.7825 | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | C6101NH | 11 | 0 | BD017078 | 1 | 27893.89 | 28087.2 | 193.31 | 2000 | 0 | 386620 | 388724.3609 | Kakrail | BSMMU 33/11KV S/S | 101 | 492746.5943 | 733453.4805 | 641089.6752 | 636961.0675 | 681006.1346 | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | C31016 | 11 | 0 | BD017079 | 1 | 34847.13 | 35288.67 | 441.54 | 2000 | 0 | 883080 | 887886.5777 | Paribag | BSMMU 33/11KV S/S | 101 | 1159088.7861 | 1451369.5422 | 1603019.2834 | 1597412.9298 | 1675286.7504 | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 | 0 | BD017080 | 1 | 7150.9 | 7242.66 | 91.76 | 2000 | 0 | 183520 | 184518.8938 | Paribag | BSMMU 33/11KV S/S | 101 | 291332.2219 | 378930.46 | 414273.243 | 428837.8596 | 457910.6397 | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 | 0 | BD017083 | 1 | 2558.44 | 2605.46 | 47.02 | 2000 | 0 | 94040 | 94551.8569 | Paribag | BSMMU 33/11KV S/S | 101 | 114173.7278 | 135094.1858 | 140648.5745 | 143344.075 | 137962.1897 | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | C6101RT | 11 | 0 | BD017084 | 1 | 1722.15 | 1801.76 | 79.61 | 2000 | 0 | 159220 | 160086.6296 | Kakrail | BSMMU 33/11KV S/S | 101 | 211841.3807 | 253083.3205 | 267336.0837 | 281930.9324 | 302057.3893 | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 | 0 | BD017085 | 1 | 2325.72 | 2367.58 | 41.86 | 2000 | 0 | 83720 | 84175.6854 | Kakrail | BSMMU 33/11KV S/S | 101 | 86093.2711 | 101598.4476 | 113805.0685 | 114841.2565 | 122402.9977 | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | C3101RM | 11 | 0 | BD017086 | 1 | 2390.79 | 2411.92 | 21.13 | 2000 | 0 | 42260 | 42490.0199 | Paribag | BSMMU 33/11KV S/S | 101 | 182774.5854 | 159898.4943 | 165660.4538 | 173668.8065 | 174287.0734 | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 | 0 | BD017087 | 1 | 4595.64 | 4656.67 | 61.03 | 2000 | 0 | 122060 | 122724.3689 | Paribag | BSMMU 33/11KV S/S | 101 | 185834.2481 | 231553.1807 | 239475.0074 | 241970.3048 | 234654.3262 | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 | 0 | BD017088 | 1 | 1140.23 | 1159.47 | 19.24 | 2000 | 0 | 38480 | 38689.4455 | Paribag | BSMMU 33/11KV S/S | 101 | 46559.2088 | 60542.3562 | 62295.6571 | 66843.9677 | 56065.3573 | 59004.3933 | 75292.0174
84 | Spare | 0 | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | C310113 | 11 | 0 | BD017090 | 1 | 2367.14 | 2560.35 | 193.21 | 2000 | 0 | 386420 | 388523.2723 | Paribag | BSMMU 33/11KV S/S | 101 | 426621.648 | 459157.5154 | 528668.5024 | 530318.42 | 510819.9335 | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKD4418 | 1 | 3035.81 | 3122.06 | 86.25 | 100 | 0 | 8625 | 8671.9456 | Paribag | BSMMU 33/11KV S/S | 101 | 7126.7998 | 0 | 6033.1746 | 14842.5188 | 15407.4195 | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 1915.93 | 1919.42 | 3.49 | 100 | 0 | 349 | 350.8996 | Paribag | BSMMU 33/11KV S/S | 101 | 3914.154 | 12158.0799 | 8446.8515 | 487.8678 | 0 | 0 | 0
88 | Chata Mosjid | 0 | 11 | 0 | 0 | 1 | 182187.1 | 184283.1 | 2096 | 1000 | 0 | 2096000 | 2142956.195 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 109 | 3224151.7427 | 2448059.1892 | 2307606.3907 | 2543835.8742 | 2199148.6226 | 2319503.7751 | 2426211.3577
89 | AC mosjid | A3109X | 11 | 0 | 0 | 1 | 11622.59 | 12645 | 1022.41 | 1000 | 0 | 1022410 | 1045314.8108 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1227807.0733 | 1300312.4106 | 1258989.8828 | 1405178.1975 | 1152835.6866 | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | A3109K | 11 | 0 | 0 | 1 | 29.8902 | 1763.086 | 1733.1958 | 1000 | 0 | 1733195.792 | 1772024.1697 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2150154.7266 | 2361420.5589 | 2255488.3746 | 2390177.1556 | 2000565.9387 | 2224217.61 | 2267338.6868
91 | Nazimuddin | A3109M | 11 | 0 | 0 | 1 | 7907.4712 | 8409.7048 | 502.2336 | 1000 | 0 | 502233.6 | 513485.0212 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 619180.2481 | 762703.8683 | 950975.5456 | 925339.67 | 477977.0793 | 0 | 0
92 | Kamal Bagh | A3109U | 11 | 0 | 0 | 1 | 21.7349 | 1189.24 | 1167.5051 | 1000 | 110 | 1337961.24 | 1367935.271 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1559969.3577 | 2099983.5161 | 1567737.0505 | 1686096.534 | 1618577.1268 | 1589844.4629 | 1583845.5588
93 | Rahamatganj | A3109B | 11 | 0 | 0 | 1 | 20350.666 | 22490 | 2139.334 | 1000 | 0 | 2139334 | 2187260.9964 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2312778.458 | 2488587.0183 | 2323808.6258 | 2495628.7814 | 2157043.5386 | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 0 | 11 | 0 | 0 | 1 | 6144.4552 | 7433.728 | 1289.2728 | 1000 | 0 | 1289272.8 | 1318156.0753 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1695142.4767 | 1852690.3414 | 1787173.2312 | 1980277.4376 | 1747210.9883 | 1862323.276 | 1854345.8684
95 | City Colony | A3109J | 11 | 0 | 0 | 1 | 3450.24 | 5297.59 | 1847.35 | 1000 | 0 | 1847350 | 1888735.7476 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1983609.3649 | 2200330.7905 | 2079469.3659 | 2219309.3581 | 1859682.1079 | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 0 | 11 | 0 | 0 | 1 | 10455.924 | 12227.5 | 1771.576 | 1000 | 0 | 1771576 | 1811264.2005 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2752272.8848 | 2717279.1674 | 2859477.1699 | 2599114.1368 | 2790703.3917 | 2997202.1128 | 3092062.2371
97 | Chun Goli | A3109H | 11 | 0 | 0 | 1 | 2584.3304 | 3396.59 | 812.2596 | 1000 | 0 | 812259.6 | 830456.4608 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 905187.2228 | 976536.6596 | 927964.1813 | 983357.245 | 754718.4448 | 841380.8401 | 894878.3402
98 | Alir Ghat | A3109L | 11 | 0 | 0 | 1 | 129316.3 | 131133.1 | 1816.8 | 1000 | 0 | 1816800 | 1857501.3431 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1968110.7302 | 2047969.8743 | 1928133.7897 | 2137361.0725 | 1734165.991 | 1904122.5273 | 2096766.6729
99 | Club Ghat | A3109C | 11 | 0 | 0 | 1 | 27337.512 | 30001.5 | 2663.988 | 1000 | 0 | 2663988 | 2723668.6966 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2705806.9627 | 2856757.5327 | 2651623.7603 | 2977501.1852 | 2317579.0304 | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | A3109V | 11 | 0 | 0 | 1 | 4371.9 | 6998.987 | 2627.087 | 1000 | 0 | 2627087 | 2685941.0122 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2625728.7516 | 2710169.0726 | 2405552.6316 | 2718263.3522 | 2261609.1864 | 2437761.5097 | 2619436.8857
101 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | Sowari Ghat | A319R | 11 | 0 | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2921891.112 | 2925967.2197 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2836655.3487 | 2802102.8851 | 2638720.3862 | 2802348.4469 | 2329233.6447 | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | A3202 | 11 | 0 | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 621678.96 | 622546.217 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 543189.3221 | 622689.53 | 658473.4491 | 560200.422 | 121854.324 | 118483.0867 | 132959.886
105 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | Eidgah | A320A | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1616365.296 | 1618620.1641 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1207087.3824 | 1369916.966 | 1376808.1209 | 1431623.3008 | 1096688.9157 | 1303313.9541 | 1329598.8604
108 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | Modumoti | A3201 | 11 | 0 | 0 | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 1367693.712 | 1369601.6773 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2052048.5501 | 2241682.3081 | 1975420.3474 | 2116312.7055 | 1584106.2116 | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | A320Y | 11 | 0 | 61389152 | 1 | 443210 | 443574 | 364 | 1000 | Estimated | 994686.336 | 996073.9471 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 965669.9059 | 1120841.154 | 1197224.4529 | 1244889.8267 | 1181986.9425 | 1066347.7806 | 1087853.6131
111 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | Water Works 11 kV Sw/S-2 | A320G | 11 | 0 | 61389109 | 1 | 405569 | 406689 | 1120 | 1000 | 0 | 1120000 | 1121562.4267 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 955036.4181 | 858393.0961 | 972107.7743 | 1045286.2834 | 874589.6653 | 951212.9635 | 980831.1601
114 | Islambagh | A320D | 11 | 0 | 61389186 | 1 | 503360 | 504200 | 840 | 1000 | 0 | 840000 | 841171.82 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 869765.3094 | 693124.8804 | 855693.6396 | 941158.1479 | 774407.5731 | 861627.8273 | 876487.4197
115 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | WASA Low Lift Pump | A320F | 11 | 0 | 61389202 | 1 | 15746 | 15795 | 49 | 1000 | 0 | 49000 | 49068.3562 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 57181.8023 | 43069.8986 | 55719.5858 | 56068.996 | 57103.7926 | 61401.0484 | 45712.4958
117 | Shahi Mosjid | D920M | 11 | 0 | 06604459 | 1 | 36593.61 | 36660.02 | 66.41 | 8000 | 0 | 531280 | 532021.1483 | Azimpur | Lalbagh Old 33/11KV S/S | 20 | 1405027.1069 | 1328075.3488 | 1734152.7099 | 1661564.6485 | 1773623.7611 | 1752245.002 | 1250534.8854
118 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | 5395822 | 1 | 67756.97 | 75056 | 7299.03 | 1 | 0 | 7299.03 | 7309.2123 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 7143.8831 | 13347.8624 | 8792.8491 | 9867.6427 | 0 | 0 | 0
120 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | Spare | 0 | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | Chawk Bazar | A319Z | 11 | 0 | DHK-60904 | 1 | 1004599.4 | 1005415 | 815.6 | 60 | 25 | 304082.1 | 307526.3862 | Lalbag | Mitford 33/11 kV | 88 | 440824.2804 | 524398.7147 | 501841.8638 | 526171.1474 | 480516.9276 | 522405.3875 | 508276.2976
123 | Spare | 0 | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | Chatrabas | B688D | 11 | 0 | DHK-66485 | 1 | 867960 | 871687 | 3727 | 60 | 0 | 223620 | 226152.9057 | Bangshal | Mitford 33/11 kV | 88 | 282876.7415 | 339280.009 | 1110389.3159 | 1353014.9285 | 1237900.3837 | 762976.1234 | 353557.5482
125 | Begum Bazar | B678G | 11 | 0 | DHK-66481 | 1 | 3818719 | 3843354 | 24635 | 60 | 0 | 1478100 | 1494842.1873 | Bangshal | Mitford 33/11 kV | 88 | 1874630.1846 | 2344342.8516 | 2422961.4211 | 2446646.3554 | 2397460.098 | 2421237.7604 | 2357293.0663
126 | SCC ROAD | B688R | 11 | 0 | DHK-60901 | 1 | 179474.4 | 198202.9 | 18728.5 | 60 | 0 | 1123710 | 1136438.0721 | Bangshal | Mitford 33/11 kV | 88 | 1342334.3996 | 1631812.3089 | 1626362.4279 | 1682445.687 | 1526989.2348 | 1650255.6547 | 1574186.7645
127 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | Armanitola | B619A | 11 | 0 | DHK-61104 | 1 | 745406.5 | 754499.2 | 9092.7 | 60 | 0 | 545562 | 551741.488 | Bangshal | Mitford 33/11 kV | 88 | 743803.3265 | 925763.6241 | 975265.6139 | 991422.0466 | 974917.2355 | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 0 | 11 | 0 | DHK-61101 | 1 | 425420.5 | 430089.5 | 4669 | 60 | 0 | 280140 | 283313.0981 | Bangshal | Mitford 33/11 kV | 88 | 415582.0452 | 494194.5928 | 534862.6587 | 551030.4718 | 539101.6117 | 513839.5885 | 528540.0121
130 | Emamganj | B688I | 11 | 0 | DHK-68130 | 1 | 1494.26 | 1506.36 | 12.1 | 60000 | 0 | 726000 | 734223.2785 | Bangshal | Mitford 33/11 kV | 88 | 961780.9211 | 1149360.3885 | 350737.4618 | 168709.5633 | 161982.5873 | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | A319T | 11 | 0 | DHK-68129 | 1 | 1226.83 | 1226.83 | 0 | 60000 | 0 | 0 | 0 | Lalbag | Mitford 33/11 kV | 88 | 601.8654 | 0 | 0 | 84652.8551 | 538371.2175 | 628439.5052 | 594724.3345
132 | Spare | 0 | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | Panghat | B688P | 11 | 0 | DHK-68127 | 1 | 1617.63 | 1634.95 | 17.32 | 60000 | 0 | 1039200 | 1050970.8417 | Bangshal | Mitford 33/11 kV | 88 | 1225999.835 | 1414831.0491 | 1293419.2063 | 1420021.8363 | 1363598.8715 | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | U0004460 | 1 | 5760.29 | 5801.91 | 41.62 | 100 | 0 | 4162 | 4209.1423 | Bangshal | Mitford 33/11 kV | 88 | 4259.2009 | 4363.7626 | 4064.0057 | 3905.7556 | 3927.8323 | 4152.4762 | 4434.1352
135 | Chadni chwok | 0 | 11 | 0 | DHK60916 | 1 | 454152 | 464674 | 10522 | 60 | 0 | 631320 | 642773.9991 | Paribag | Azimpur 33/11 KV | 66 | 585337.5096 | 659849.4891 | 735121.5421 | 735452.5478 | 623153.8648 | 792142.0147 | 648152.1238
136 | BGB | 0 | 11 | 0 | DHK61090 | 1 | 716307 | 720083 | 3776 | 60 | 0 | 226560 | 230670.4639 | Jigatola | Azimpur 33/11 KV | 66 | 138499.1268 | 715312.2841 | 771727.6444 | 791117.6745 | 677536.8748 | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | D920P | 11 | 0 | DHK61091 | 1 | 919902 | 951531 | 31629 | 60 | 0 | 1897740 | 1932170.5777 | Azimpur | Azimpur 33/11 KV | 66 | 1912839.727 | 2177491.1776 | 2180695.2965 | 2262756.8158 | 2133225.2763 | 2225341.7622 | 2144033.6462
138 | Azimpur | D901P | 11 | 0 | DHK61086 | 1 | 383398 | 407809 | 24411 | 60 | 0 | 1464660 | 1491233.2344 | Azimpur | Azimpur 33/11 KV | 66 | 1631381.6426 | 1038683.4379 | 1153765.578 | 1156672.3968 | 1153479.4596 | 1136633.6642 | 1104066.6214
139 | Aazd | D901Z | 11 | 0 | DHK61089 | 1 | 64260 | 77569 | 13309 | 60 | 0 | 798540 | 813027.8611 | Azimpur | Azimpur 33/11 KV | 66 | 1025333.4123 | 1260231.211 | 1354793.0694 | 1347891.2826 | 1333174.551 | 1318714.278 | 1257709.9294
140 | Dayra Sharif | D966D | 11 | 0 | DHK61088 | 1 | 579254 | 589162 | 9908 | 60 | 0 | 594480 | 605265.6133 | Azimpur | Azimpur 33/11 KV | 66 | 772833.6808 | 1018901.3032 | 1035744.5659 | 1040264.9944 | 1036318.7466 | 1007533.0284 | 980271.2172
141 | Naya palton | D966U | 11 | 0 | DHK86065 | 1 | 2006.64 | 2026.6 | 19.96 | 60000 | 0 | 1197600 | 1219327.9816 | Azimpur | Azimpur 33/11 KV | 66 | 1424702.0899 | 1594707.0602 | 1776436.6019 | 1764768.0283 | 1711787.3638 | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | D966V | 11 | 0 | DHK66477 | 1 | 1696824 | 1710480 | 13656 | 60 | 0 | 819360 | 834225.5971 | Azimpur | Azimpur 33/11 KV | 66 | 1008349.3994 | 1357200.0802 | 1489035.8491 | 1488032.8269 | 1499973.4477 | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | D966W | 11 | 0 | DHK66480 | 1 | 4107768 | 4138344 | 30576 | 60 | 0 | 1834560 | 1867844.3069 | Azimpur | Azimpur 33/11 KV | 66 | 1712147.3443 | 1414604.6799 | 1497238.5543 | 1598200.8415 | 1506117.3895 | 1034936.4652 | 1287496.6695
144 | Lalbagh | D920L | 11 | 0 | DHK61093 | 1 | 874634 | 898839 | 24205 | 60 | 0 | 1452300 | 1478648.9877 | Azimpur | Azimpur 33/11 KV | 66 | 1848324.9154 | 2271183.2515 | 2469993.6901 | 2465781.6021 | 2471750.3893 | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | D366J | 11 | 0 | DHK66497 | 1 | 1281591 | 1287059 | 5468 | 60 | 0 | 328080 | 334032.3348 | Ramna | Azimpur 33/11 KV | 66 | 483616.7128 | 594434.9453 | 771237.9306 | 746279.7208 | 668533.8709 | 616760.0188 | 675859.2968
146 | Eden College | D966E | 11 | 0 | DHK60917 | 1 | 962562 | 967289 | 4727 | 60 | 0 | 283620 | 288765.6999 | Azimpur | Azimpur 33/11 KV | 66 | 308522.5366 | 489031.3622 | 487693.6736 | 503127.1069 | 450271.8574 | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | D902N | 11 | 0 | DHK60918 | 1 | 519580 | 526604 | 7024 | 60 | 0 | 421440 | 429086.1595 | Azimpur | Azimpur 33/11 KV | 66 | 527298.6165 | 634848.7543 | 693863.1593 | 681133.1714 | 683984.9722 | 653358.8311 | 648152.1238
148 | BUET | D366BU | 11 | 0 | DHK66496 | 1 | 1015739 | 1022142 | 6403 | 60 | 0 | 384180 | 391150.1536 | Ramna | Azimpur 33/11 KV | 66 | 431931.5513 | 807548.0045 | 1180516.1912 | 815830.544 | 798043.2987 | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIG2780 | 1 | 404836 | 406762 | 1926 | 1 | 0 | 1926 | 1960.9433 | Azimpur | Azimpur 33/11 KV | 66 | 3021.0771 | 4277.027 | 4444.1522 | 3986.2756 | 4092.9197 | 4399.774 | 2203.9333
150 | Rasulpur | F120R | 11 | 0 | HA-021101042-02 | 1 | 97733809 | 98581922 | 848113 | 1 | 0 | 848113 | 861127.0146 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1135070.1317 | 1665082.8173 | 1532049.0872 | 1584215.5272 | 1403442.4135 | 1475786.882 | 1248201.2259
151 | Bheribadh | F120B | 11 | 0 | HA-021101105-02 | 1 | 74035356 | 75856137 | 1820781 | 1 | 0 | 1820781 | 1848720.2846 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2165499.7281 | 2508479.0993 | 2458320.6942 | 2620926.9562 | 2327005.5404 | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 | 0 | 30799521 | 1 | 2655.72 | 2661.25 | 5.53 | 60000 | 0 | 331800 | 336891.3617 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 271984.1018 | 253194.3598 | 408741.1592 | 362911.631 | 314576.4303 | 364934.8739 | 488122.7019
153 | Panna Battery Express | F140E | 11 | 0 | DHK15431 | 1 | 5345.3 | 5361.41 | 16.11 | 60000 | 0 | 966600 | 981432.1586 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 963251.5607 | 788120.5732 | 1093857.5249 | 1220535.5698 | 1068349.9537 | 1060687.1709 | 1118589.0702
154 | Eidgah | F140I | 11 | 0 | 30799460 | 1 | 5523.86 | 5556.72 | 32.86 | 60000 | 0 | 1971600 | 2001853.5525 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2214989.6293 | 2418400.8037 | 2321919.4185 | 2480917.8558 | 2121576.0406 | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | D840L | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | Huzur Para | F140H | 11 | 0 | HA-021101055-02 | 1 | 9989092 | 11777481 | 1788389 | 1 | 0 | 1788389 | 1815831.2401 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2641114.3542 | 2153483.8082 | 1914978.8856 | 2163917.8156 | 1832748.4977 | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | F103K | 11 | 0 | HA-021101015-02 | 1 | 29348087 | 30547592 | 1199505 | 1 | 0 | 1199505 | 1217911.0091 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2380775.6541 | 2064906.2609 | 1863929.1371 | 2041804.9994 | 1873617.2189 | 1726065.7983 | 1737567.1439
158 | Munshihati | F140T | 11 | 0 | HA-021100854-02 | 1 | 56404546 | 57165112 | 760566 | 1 | 0 | 760566 | 772236.6347 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 990193.2667 | 1294711.6864 | 1345431.4782 | 1376742.8712 | 1392932.3343 | 1212171.698 | 1205376.9608
159 | Jhawchar | F140J | 11 | 0 | HA-021101028-02 | 1 | 6004029 | 6932632 | 928603 | 1 | 0 | 928603 | 942852.1071 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1224855.4453 | 1505628.0528 | 1566579.6466 | 1562224.2267 | 1438582.214 | 1425641.3374 | 1328999.0751
160 | RMU Express | F140D | 11 | 0 | HA-021101248-02 | 1 | 8590513 | 9219291 | 628778 | 1 | 0 | 628778 | 638426.3913 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 630223.836 | 713470.7397 | 717231.4507 | 658611.0471 | 606779.6203 | 633839.2782 | 704501.3661
161 | Koyla Ghat | F140C | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2036133.7416 | 2067377.5431 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2106357.2232 | 1907872.1438 | 2053915.4269 | 2183072.3937 | 1900877.505 | 2223108.4368 | 1816011.9444
162 | Muslimbagh | F140M | 11 | 0 | HA-021100908-02 | 1 | 34050945 | 35892134 | 1841189 | 1 | 0 | 1841189 | 1869441.4387 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2918215.2206 | 1684632.0125 | 1681378.5129 | 1753494.5949 | 1596522.772 | 1696945.1326 | 1737474.4882
163 | Noyagaon | F140Y | 11 | 0 | HA-021101087-02 | 1 | 16193892 | 18030958 | 1837066 | 1 | 0 | 1837066 | 1865255.1726 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2290171.3321 | 2533643.7042 | 2800404.9743 | 2891878.4964 | 2674100.301 | 2742632.8101 | 2660587.4202
164 | Nurbagh | F140N | 11 | 0 | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2136683.556 | 2169470.2613 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2292212.2723 | 2098659.3582 | 2062025.6114 | 2315958.5809 | 1868573.9135 | 2159293.4513 | 2300317.433
165 | Ali Nagar | F140A | 11 | 0 | HA-021101022-02 | 1 | 30998173 | 32604402 | 1606229 | 1 | 0 | 1606229 | 1630876.0549 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2028577.6342 | 2162413.4126 | 2438442.3104 | 2505512.4752 | 2290198.0816 | 2360084.8023 | 2402380.2856
166 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | Nababgonj Park | D920K | 11 | 0 | 0 | 1 | 12523740 | 12523740 | 0 | 1 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 104 | 257344.0613 | 1028840.1279 | 1022665.2071 | 1042273.5833 | 1021134.2367 | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | F1104O | 11 | 0 | 0 | 1 | 88803750 | 91668720 | 2864970 | 1 | 0 | 2864970 | 2885529.8072 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2905973.3033 | 3092402.2195 | 2773618.4692 | 2851658.6512 | 2502740.2728 | 2762472.0542 | 2841690.4191
171 | Khalpar | F1104L | 11 | 0 | 0 | 1 | 91426620 | 92741032 | 1314412 | 1 | 0 | 1314412 | 1323844.5795 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2032339.2009 | 1943499.6703 | 1539343.6525 | 1698814.3914 | 1298185.7875 | 1375644.1828 | 1437529.7992
172 | Shahidnagar | D920S | 11 | 0 | 0 | 1 | 23321150 | 24739150 | 1418000 | 1 | 0 | 1418000 | 1428175.9553 | Azimpur | BGB 33/11 KV S/S | 104 | 1591215.1991 | 1859313.6405 | 1906528.5825 | 1984753.7699 | 1856790.3941 | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | D9104G | 11 | 0 | 0 | 1 | 37153410 | 37153410 | 0 | 1 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 104 | 345681.1733 | 1312194.6593 | 1412422.3679 | 1466652.5091 | 1458588.073 | 1375749.2129 | 1318685.5995
174 | Ganaktuli | D8104J | 11 | 0 | 0 | 1 | 26868220 | 27397800 | 529580 | 1 | 0 | 529580 | 533380.4107 | Jigatola | BGB 33/11 KV S/S | 104 | 706109.2655 | 871530.0895 | 914191.5251 | 939625.3117 | 882817.4598 | 725654.1445 | 693078.4919
175 | Thana | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Bot Tola Mazar | D8104L | 11 | 0 | 0 | 1 | 39081811 | 39081811 | 0 | 1 | 0 | 0 | 0 | Jigatola | BGB 33/11 KV S/S | 104 | 521511.0545 | 2086773.692 | 2120352.147 | 2064384.9311 | 2207948.9744 | 2074198.5352 | 1909183.4664
177 | Sikder Medical | D8104K | 11 | 0 | 0 | 1 | 40142320 | 40845832 | 703512 | 1 | 0 | 703512 | 708560.5942 | Jigatola | BGB 33/11 KV S/S | 104 | 897177.4288 | 1152362.6885 | 1220473.4868 | 1221157.6998 | 1181050.1989 | 1134381.9061 | 1138392.2283
178 | Gas Field | F1104G | 11 | 0 | 0 | 1 | 62157430 | 63617728 | 1460298 | 1 | 0 | 1460298 | 1470777.4973 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 1717515.6493 | 2221738.1672 | 2114640.3455 | 2213538.6558 | 2063276.8361 | 2061072.7993 | 1985612.1672
179 | Hazaribagh | D8104H | 11 | 0 | 0 | 1 | 45430730 | 46318840 | 888110 | 1 | 0 | 888110 | 894483.3199 | Jigatola | BGB 33/11 KV S/S | 104 | 1109528.647 | 1387872.6757 | 1512565.9182 | 1534113.0489 | 1525507.7666 | 1485016.8997 | 1465699.7946
180 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 0 | 1 | 2337.12 | 2389.78 | 52.66 | 10 | 0 | 526.6 | 530.379 | Azimpur | BGB 33/11 KV S/S | 104 | 413.4472 | 551.1966 | 644.3721 | 611.8898 | 0 | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 1909.01 | 1968.33 | 59.32 | 10 | 0 | 593.2 | 597.457 | Azimpur | BGB 33/11 KV S/S | 104 | 421.5697 | 541.173 | 593.9263 | 558.558 | 0 | 0 | 0
184 | Salek Garden | 0 | 11 | 0 | 2761 | 1 | 749.07 | 773.21 | 24.14 | 60000 | 0 | 1448400 | 1452181.1176 | Jigatola | Jigatola New 33/11 KV S/S |  | 1864953.454 | 2402250.1859 | 2551916.8348 | 2553649.2193 | 2650896.5462 | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 0 | 11 | 0 | 2850 | 1 | 578.8 | 596.45 | 17.65 | 60000 | 0 | 1059000 | 1061764.5702 | Jigatola | Jigatola New 33/11 KV S/S |  | 1304682.5555 | 1679891.0289 | 1793125.2848 | 1780723.9511 | 1886527.6034 | 1807426.7227 | 1737565.9216
186 | Modina Rayer Bazar | 0 | 11 | 0 | 2851 | 1 | 662.99 | 692.25 | 29.26 | 60000 | 0 | 1755600 | 1760183.0779 | Switching | Jigatola New 33/11 KV S/S |  | 2081696.183 | 0 | 0 | 0
187 | City College | 0 | 11 | 0 | 2784 | 1 | 617.99 | 635.88 | 17.89 | 60000 | 0 | 1073400 | 1076202.1621 | Jigatola | Jigatola New 33/11 KV S/S |  | 1313738.6584 | 1670267.593 | 1742699.2641 | 1753162.2749 | 1830510.0213 | 1777383.0604 | 2346194.6487
188 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | Post Office | 0 | 11 | 0 | 2836 | 1 | 488.7 | 506.21 | 17.51 | 60000 | 0 | 1050600 | 1053342.6416 | Jigatola | Jigatola New 33/11 KV S/S |  | 1284759.1292 | 1558395.1507 | 1658055.5864 | 1646510.5712 | 1676311.0857 | 1671629.3692 | 1589764.671
191 | Leather Institute | 0 | 11 | 0 | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 57222.2613 | 189875.9456 | 195265.8799
192 | Mina Bazar | 0 | 11 | 0 | 2853 | 1 | 237.44 | 244.3 | 6.86 | 60000 | 0 | 411600 | 412674.5015 | Jigatola | Jigatola New 33/11 KV S/S |  | 509556.7223 | 661611.218 | 704163.3609 | 701025.2432 | 763766.6032 | 746284.571 | 706562.076
193 | Mitali | 0 | 11 | 0 | 2852 | 1 | 536.6 | 549.65 | 13.05 | 60000 | 0 | 783000 | 785044.059 | Switching | Jigatola New 33/11 KV S/S |  | 1032999.469 | 2938155.2725 | 3066382.3082 | 3083312.7364
194 | Road-2 | 0 | 11 | 0 | 2839 | 1 | 774.77 | 801.77 | 27 | 60000 | 0 | 1620000 | 1624229.0876 | Jigatola | Jigatola New 33/11 KV S/S |  | 1929553.6546 | 2419692.6635 | 2344809.964 | 2360717.4857 | 2376832.0316 | 2301945.4038 | 2450136.1786
195 | SS-2 | 0 | 11 | 0 | 2838 | 1 | 387.95 | 424.49 | 36.54 | 60000 | 0 | 2192400 | 2198123.3652 | Jigatola | Jigatola New 33/11 KV S/S |  | 2140258.9817 | 1225183.6827 | 1208423.5682 | 1244469.5984 | 1139024.1692 | 1127238.2087 | 1112715.1061
196 | Spare | 0 | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | Bou Bazar | 0 | 11 | 0 | 2843 | 1 | 620.73 | 639.85 | 19.12 | 60000 | 0 | 1147200 | 1150194.8205 | Jigatola | Jigatola New 33/11 KV S/S |  | 1453202.6428 | 1833866.0032 | 1887974.2286 | 1919131.4991 | 1882311.2263 | 1850088.7231 | 1774816.6433
198 | BGB | 0 | 11 | 0 | 2764 | 1 | 214.64 | 222.92 | 8.28 | 60000 | 0 | 496800 | 498096.9202 | Jigatola | Jigatola New 33/11 KV S/S |  | 766146.304 | 453504.4167 | 461638.2136 | 445780.1547 | 580655.3671 | 1007063.5596 | 934872.9509
199 | Dhamondi-12 | 0 | 11 | 0 | 2763 | 1 | 499.01 | 510.98 | 11.97 | 60000 | 0 | 718200 | 720074.8955 | Dhanmondi | Jigatola New 33/11 KV S/S |  | 696112.4417 | 1536140.9551 | 2054260.035 | 1641717.2362 | 1520907.4708 | 1213163.0828 | 1602982.669
200 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 | 0 | DHK60907 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | Mitali Road | D803D | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | Bou Bazar | D803E | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | Mina Bazar | D803I | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | Simanto Square | D803R | 11 | 0 | DHK60946 | 1 | 1199.27 | 1209.99 | 10.72 | 60000 | 0 | 643200 | 650467.3454 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 732323.3006 | 891294.9856 | 910570.4517 | 922404.6994 | 967800 | 852145.3731 | 901151.3428
206 | Post Office | D803P | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | Hazaribagh Sw/S-2 | D803S | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | Green Road Via Park | D803G | 11 | 0 | DHK61070 | 1 | 3506.97 | 3516.73 | 9.76 | 60000 | 0 | 585600 | 592216.5384 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 824386.8012 | 963367.3565 | 1108520.5499 | 1276574.4307 | 1342800 | 1229862.9154 | 476757.7712
209 | PWD Quarters 11 kV Saleq Grand | D803A | 11 | 0 | DHK61028 | 1 | 3635.35 | 3636.29 | 0.94 | 60000 | 0 | 56400 | 57037.2486 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 62770.5686 | 73874.1801 | 78580.1905 | 73359.435 | 68400 | 74813.6195 | 63933.0345
210 | Road No.-2 | D803T | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | Hzaribagh O/H | D803H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | B.G.B | D803B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 11 kV City College | D803C | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | Jigatala Local | D803Z | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 33/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 243284 | 1 | 85569 | 85913 | 344 | 10 | 0 | 3440 | 3478.8676 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 2919.3296 | 1971.9801 | 3959.002 | 5251.4131 | 3680 | 2585.0234 | 3440.2061
216 | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 412277 | 1 | 39890 | 39890 | 0 | 10 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 1491.4977 | 769.8059 | 10.0218 | 1650 | 5393.0685 | 0
217 | Spare | 0 | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | D Block dhaka uddyan | G1103L | 11 | 0 | BD014031 | 1 | 50391.3 | 50616.29 | 224.99 | 1000 | 0 | 224990 | 224956.6107 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 285235.5277 | 367241.8104 | 387945.2586 | 382937.2777 | 364723.8055 | 376392.0985 | 356370.9019
219 | Dill Mohammad O/H | G1103DM | 11 | 0 | BD014027 | 1 | 25238.4 | 26373.57 | 1135.17 | 1000 | 0 | 1135170 | 1135001.5369 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1518244.1569 | 1927925.8849 | 1986501.3323 | 2019494.4174 | 1931376.746 | 1945233.0858 | 1925614.3584
220 | Turag O/H | G1103U | 11 | 0 | BD014028 | 1 | 28864.7 | 29356.45 | 491.75 | 1000 | 0 | 491750 | 491677.0226 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 590651.3937 | 705567.8194 | 641819.4994 | 770193.2072 | 703573.3851 | 725059.1327 | 419185.0275
221 | Nabadoy O/H | G1103N | 11 | 0 | BD014025 | 1 | 39575.1 | 41099.31 | 1524.21 | 1000 | 0 | 1524210 | 1523983.802 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1125982.5565 | 997660.9336 | 848979.0298 | 846778.6447 | 874784.3247 | 873886.7957 | 1264712.0241
222 | Chandrima O/H | G1103CH | 11 | 0 | BD014024 | 1 | 8643.05 | 9266.86 | 623.81 | 1000 | 0 | 623810 | 623717.4245 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 752545.8986 | 970880.6709 | 1055645.8739 | 1037828.5358 | 998647.327 | 974655.0029 | 879754.0777
223 | Shyamoli Housing Project-2 | G1103SH | 11 | 0 | BD014029 | 1 | 31988.5 | 32602.26 | 613.76 | 1000 | 0 | 613760 | 613668.9159 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 919460.3881 | 1164941.4253 | 2147810.8671 | 1346057.1733 | 1686564.4606 | 1305126.5223 | 2226602.9518
224 | Spare | 0 | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | Spare | 0 | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | Spare | 0 | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | U Lab | C2103U | 11 | 0 | BD013959 | 1 | 45500.4 | 46153.52 | 653.12 | 1000 | 0 | 653120 | 653023.0747 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 694263.8768 | 2706800.3719 | 2673135.1804 | 1523999.7543 | 2168216.2175 | 2766170.13 | 2585824.4138
228 | Akota | G1103AK | 11 | 0 | BD014020 | 1 | 8078.5 | 8424.99 | 346.49 | 1000 | 0 | 346490 | 346438.5797 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 380615.236 | 526131.9628 | 548510.7365 | 553675.3788 | 518552.2147 | 529306.7232 | 494561.9781
229 | Burigonga O/H | G1103BU | 11 | 0 | BD014019 | 1 | 6149.5 | 6461.38 | 311.88 | 1000 | 0 | 311880 | 311833.7159 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 278809.9473 | 387230.8575 | 410809.9274 | 413097.2082 | 391376.3535 | 420977.1349 | 372374.7602
230 | Garden City | C2103G | 11 | 0 | BD014021 | 1 | 94056.2 | 95724.67 | 1668.47 | 1000 | 0 | 1668470 | 1668222.3933 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 1892735.0117 | 2553547.6368 | 3028251.44 | 2810059.9564 | 2804225.2436 | 2395190.4943 | 2278829.2831
231 | Avenue O/H | G1103AV | 11 | 0 | BD014017 | 1 | 16683.5 | 17346.12 | 662.62 | 1000 | 0 | 662620 | 662521.6649 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 749985.7064 | 943169.2729 | 1027773.9029 | 1034448.2826 | 977183.594 | 966250.121 | 894892.5874
232 | Chand Uddyan | C2103D | 11 | 0 | BD014018 | 1 | 10938.7 | 11142.1 | 203.4 | 1000 | 0 | 203400 | 203369.8147 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 512239.2335 | 689384.282 | 764257.0863 | 760476.2406 | 759432.9748 | 732469.8888 | 645275.1572
233 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4416 | 1 | 1917.01 | 1954.47 | 37.46 | 100 | 0 | 3746 | 3745.4441 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 2862.3952 | 3787.2919 | 1595.7005 | 3776.8023 | 3734.949 | 3966.4616 | 1513.851
234 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4412 | 1 | 284.73 | 284.73 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 168.6715 | 0 | 3189.39 | 0 | 0 | 0 | 2409.7413
235 | Lalmatia O/H | C209M | 11 | 0 | DHK61042 | 1 | 3220.42 | 3232.99 | 12.57 | 60000 | 0 | 754200 | 768088.1431 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 970586.2531 | 911395.4616 | 1251951.9192 | 1243685.3152 | 1300189.4979 | 1240075.1783 | 1343819.1874
236 | Asad Avenue (South) | C209C | 11 | 0 | DHK 60999 | 1 | 2949.71 | 2960.26 | 10.55 | 60000 | 0 | 633000 | 644656.3174 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 816364.2657 | 854508.8922 | 1448736.6599 | 0 | 99461.5008 | 201384.8525 | 143036.2105
237 | Madrasha Road | 0 | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | Bashbari | C209H | 11 | 0 | DHK61002 | 1 | 2461.86 | 2477.67 | 15.81 | 60000 | 0 | 948600 | 966067.9031 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1190903.3781 | 1245452.7622 | 1339544.3993 | 1690928.3933 | 1784914.5226 | 1599091.6268 | 1533732.8114
239 | Road-27 | C209A | 11 | 0 | DHK61001 | 1 | 1479.65 | 1483.48 | 3.83 | 60000 | 0 | 229800 | 234031.6299 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 326307.5256 | 422413.036 | 1160540.6933 | 560250.965 | 379271.8673 | 89903.952 | 435118.5562
240 | Boishakhi O/H | D209O | 11 | 0 | DHK61024 | 1 | 4253.99 | 4274.92 | 20.93 | 60000 | 0 | 1255800 | 1278924.8078 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1623796.756 | 2461251.8872 | 2676105.4034 | 2946106.036 | 2918535.965 | 3026167.0253 | 2814447.7883
241 | Katasur O/H | C209K | 11 | 0 | DHK61003 | 1 | 3692.06 | 3705.25 | 13.19 | 60000 | 0 | 791400 | 805973.1589 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1044422.2626 | 1288420.2773 | 1430239.6103 | 1419182.7329 | 1436799.27 | 1431270.9163 | 1334804.3002
242 | Nurjahan Road | D409I | 11 | 0 | DHK61000 | 1 | 1912.62 | 1926.3 | 13.68 | 60000 | 0 | 820800 | 835914.5423 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1604146.8503 | 1215193.9487 | 1433819.6844 | 1423372.644 | 1464960.0563 | 1437863.8728 | 1376873.7739
243 | polpar over head | D209W | 11 | 0 | DHK61003 | 1 | 1928.75 | 1949.28 | 20.53 | 60000 | 0 | 1231800 | 1254482.8621 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1581519.6861 | 1999502.3937 | 2133127.4955 | 2142241.6706 | 2168380.5497 | 2135518.5405 | 2016930.7661
244 | Satmosjid Housing | C209S | 11 | 0 | DHK61043 | 1 | 2852.16 | 2870.9 | 18.74 | 60000 | 0 | 1124400 | 1145105.1552 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1396334.2108 | 0 | 189147.2492 | 1377283.6223 | 608153.1522 | 0 | 0
245 | Physical College | C209P | 11 | 0 | DHK61041 | 1 | 3423.91 | 3449.62 | 25.71 | 60000 | 0 | 1542600 | 1571006.0587 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1952486.0884 | 2469119.1787 | 2662381.786 | 2653410.8203 | 2677671.3668 | 2636583.2332 | 2184607.6683
246 | Asad Avenue (North) | D409V | 11 | 0 | DHK61022 | 1 | 2730.21 | 2741 | 10.79 | 60000 | 0 | 647400 | 659321.4848 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 288792.6455 | 0 | 3594.994 | 0 | 0
247 | Spare Feeder | 0 | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | Ghraphic artch college | D209Z | 11 | 0 | DHK61023 | 1 | 1170.56 | 1188.33 | 17.77 | 60000 | 0 | 1066200 | 1085833.4369 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1330834.525 | 1448791.9887 | 1578216.0071 | 1715469.3009 | 1620743.1298 | 1570921.7218 | 1701409.7136
249 | Mohammadpur O/H | D409W | 11 | 0 | DHK61025 | 1 | 2252.68 | 2284.77 | 32.09 | 60000 | 0 | 1925400 | 1960855.0924 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 652019.5995 | 1590403.2357 | 1624160.2917 | 1649627.8414 | 1683655.5249 | 1660825.6738 | 1343218.1949
250 | Bosila Feeder | C209V | 11 | 0 | DHK60997 | 1 | 4231.8 | 4258.71 | 26.91 | 60000 | 0 | 1614600 | 1644331.8958 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 2353225.0751 | 2736001.9135 | 2540659.2659 | 2707281.1054 | 2444595.9223 | 2900301.4925 | 3015179.277
251 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIB 7375 | 1 | 6168.9 | 6220.41 | 51.51 | 60 | 0 | 3090.6 | 3147.5116 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 4513.5238 | 7345.0244 | 8176.8893 | 8159.5525 | 8272.6804 | 8691.9141 | 0
252 | Dhaka Uddyan | G186D | 11 | 0 | DHK86067 | 1 | 3254.34 | 3254.98 | 0.64 | 60000 | 0 | 38400 | 38757.9222 | Adabor | Japan Garden 33/11 KV | 86 | 90112.6747 | 43181.0046 | 44366.4049 | 46170.0157 | 47362.5115 | 34177.6075 | 0
253 | Shia Mosjid | D409H | 11 | 0 | DHK60950 | 1 | 3569.61 | 3592.79 | 23.18 | 60000 | 0 | 1390800 | 1403763.4936 | Shyamoli | Japan Garden 33/11 KV | 86 | 1651270.0056 | 1965935.1818 | 2358614.0108 | 2312098.4465 | 2316566.3838 | 2321079.2736 | 1677029.4105
254 | Shekhar Tek | G186S | 11 | 0 | DHK60977 | 1 | 2464.44 | 2472.47 | 8.03 | 60000 | 0 | 481800 | 486290.8047 | Adabor | Japan Garden 33/11 KV | 86 | 1243674.2652 | 1739834.6438 | 2042053.7165 | 2050068.6174 | 2089945.7593 | 2160384.5576 | 1966584.1503
255 | Madrasha Road | D434D | 11 | 0 | DHK61083 | 1 | 2092.58 | 2108.17 | 15.59 | 60000 | 0 | 935400 | 944118.7603 | Shyamoli | Japan Garden 33/11 KV | 86 | 1646495.8242 | 1898764.7302 | 2311849.4219 | 1518214.0214 | 1459844.4991 | 1147648.0831 | 1148666.6379
256 | Baitul Aman Housing | G186B | 11 | 0 | DHK668115 | 1 | 4242.38 | 4269.31 | 26.93 | 60000 | 0 | 1615800 | 1630860.6938 | Adabor | Japan Garden 33/11 KV | 86 | 2021865.8399 | 2579465.2888 | 2865829.9369 | 2799581.8586 | 2963454.3569 | 2980047.5303 | 2714650.3131
257 | Shyamoli Square | D486G | 11 | 0 | DHK86063 | 1 | 480.53 | 484.66 | 4.13 | 30000 | 0 | 123900 | 125054.8582 | Shyamoli | Japan Garden 33/11 KV | 86 | 139346.4208 | 179920.8525 | 180163.5766 | 172388.0455 | 167267.6038 | 170888.0374 | 163284.9924
258 | Mohammadi Housing | G186E | 11 | 0 | DHK60948 | 1 | 3887.07 | 3887.07 | 0 | 60000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 796094.7552 | 1504138.327 | 1937732.7104 | 1867187.3865 | 2007211.2456 | 1954719.3056 | 1343295.1846
259 | Chand Housing | C286H | 11 | 0 | DHK60867 | 1 | 2223.07 | 2233.74 | 10.67 | 60000 | 0 | 640200 | 646167.2337 | Satmasjid | Japan Garden 33/11 KV | 86 | 578272.7269 | 1066930.6554 | 1224872.5023 | 796282.8675 | 850127.1046 | 960570.6526 | 891350.9825
260 | PC Culture Housing | 0 | 11 | 0 | DHK60979 | 1 | 4222.72 | 4245.93 | 23.21 | 60000 | 0 | 1392600 | 1405580.2712 | Adabor | Japan Garden 33/11 KV | 86 | 1788527.722 | 2352165.2785 | 2602029.6916 | 2565134.1168 | 2719447.494 | 2646665.9554 | 2456140.6176
261 | Mehedibagh | G186H | 11 | 0 | DHK68121 | 1 | 2445.54 | 2474.33 | 28.79 | 60000 | 0 | 1727400 | 1743500.9051 | Adabor | Japan Garden 33/11 KV | 86 | 2209252.4615 | 2861941.0273 | 3070874.6729 | 3016640.8933 | 3040793.1415 | 3013625.5306 | 2845397.7111
262 | 33/11 kV Incoming (Spare) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | 0 | 1 | 665030 | 667611 | 2581 | 1 | 0 | 2581 | 2605.0572 | Adabor | Japan Garden 33/11 KV | 86 | 3087.304 | 4523.0103 | 4813.3552 | 5033.7309 | 5179.9 | 5393.4663 | 0
264 | Mokarom Bhabon | D3108MB | 11 | 0 | 2761 | 1 | 63.51 | 65.52 | 2.01 | 60000 | 0 | 120600 | 121084.3373 | Ramna | Dhaka University 33/11 KV S/S | 108 | 174337.3 | 202329.0481 | 226720.401 | 207689.3161 | 186304.8566 | 168036.2342 | 191876.7922
265 | 11 kV Shaid Minar RMU | D3108SM | 11 | 0 | 2850 | 1 | 146.61 | 149 | 2.39 | 60000 | 0 | 143400 | 143975.9036 | Ramna | Dhaka University 33/11 KV S/S | 108 | 186918.3422 | 606987.1444 | 637120.699 | 361224.6845 | 367165.7402 | 336672.5979 | 339844.4752
266 | 11 kV Shaidulla Hall | D3108SH | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | Spare | 0 | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | MBA Bhabon | D3108MA | 11 | 0 | 2836 | 1 | 106.63 | 108.47 | 1.84 | 60000 | 0 | 110400 | 110843.3735 | Ramna | Dhaka University 33/11 KV S/S | 108 | 176733.689 | 232348.1947 | 278853.9691 | 280291.312 | 263125.3657 | 250253.9631 | 301348.8178
271 | Suprime Court | 0 | 11 | 0 | 2835 | 1 | 70.7 | 73.79 | 3.09 | 60000 | 0 | 185400 | 186144.5783 | Ramna | Dhaka University 33/11 KV S/S | 108 | 281575.7078 | 323006.0175 | 284309.8076 | 352893.3079 | 353253.3645 | 298264.3158 | 306762.2696
272 | Karjon Hall | D3108KH | 11 | 0 | 2853 | 1 | 76.92 | 79.81 | 2.89 | 60000 | 0 | 173400 | 174096.3855 | Ramna | Dhaka University 33/11 KV S/S | 108 | 243233.4838 | 317602.5711 | 349779.87 | 351108.0129 | 342970.3043 | 313267.551 | 333228.0341
273 | Spare | 0 | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | Swimming Pool | D3108SP | 11 | 0 | 2839 | 1 | 2.73 | 2.93 | 0.2 | 60000 | 0 | 12000 | 12048.1928 | Ramna | Dhaka University 33/11 KV S/S | 108 | 23963.89 | 46229.4858 | 46071.5253 | 0 | 0 | 0 | 0
275 | Spare | 0 | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | Police Head Quarter RMU | 0 | 11 | 0 | 2772 | 1 | 98.89 | 103 | 4.11 | 60000 | 0 | 246600 | 247590.3614 | Ramna | Dhaka University 33/11 KV S/S | 108 | 319318.8346 | 399254.6499 | 414643.728 | 474293.3666 | 554680.3686 | 488505.3381 | 444504.5437
277 | Spare | 0 | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | Spare | 0 | 11 | 0 | 2764 | 1 | 2.38 | 3.28 | 0.9 | 60000 | 0 | 54000 | 54216.8675 | Ramna | Dhaka University 33/11 KV S/S | 108 | 53918.7526 | 67242.8884 | 0 | 0 | 0 | 0 | 0
279 | Spare | 0 | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | Segunbagicha | D394S | 11 | 0 | DHK-C9360 | 1 | 20686.9 | 26166.36 | 5479.46 | 60 | 0 | 328767.6 | 331939.36 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 443816.6143 | 585591.0985 | 595887.9152 | 652730.1844 | 660791.8145 | 648570.0837 | 628132.1417
281 | Secretariat RMU | D394FB | 11 | 0 | DHK-C9379 | 1 | 81663.25 | 83159.69 | 1496.44 | 60 | 0 | 89786.4 | 90652.6074 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 124236.116 | 153919.5822 | 147122.5127 | 169088.4911 | 173479.2405 | 157347.3651 | 189151.3106
282 | NBR RMU | D394NR | 11 | 0 | DHK-C9319 | 1 | 78532.8 | 82593.8 | 4061 | 60 | 0 | 243660 | 246010.691 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 319447.2431 | 425924.9701 | 412789.7325 | 468220.1905 | 479026.3146 | 471677.0943 | 454185.7713
283 | Ramna 11 kV Sw/S-2 | 0 | 11 | 0 | DHK-C9364 | 1 | 64314.76 | 74109.1 | 9794.34 | 60 | 0 | 587660.4 | 593329.8083 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 847238.794 | 1202930.2093 | 1229384.6711 | 70113.1256 | 552257.97 | 1047973.9631 | 1309281.295
284 | Ramna 11 kV Sw/S-1 | 0 | 11 | 0 | DHK-C9375 | 1 | 57677.67 | 57712.71 | 35.04 | 60 | 0 | 2102.4 | 2122.6827 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 103793.1904 | 54867.1796 | 213365.2082 | 295845.9008 | 960645.5509 | 37569.2064 | 3932.094
285 | Family Planning | D394FP | 11 | 0 | DHK-C9378 | 1 | 77750.21 | 81981.71 | 4231.5 | 60 | 0 | 253890 | 256339.3842 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 360288.4749 | 436247.6925 | 440914.9728 | 477616.3037 | 472965.3149 | 459978.3897 | 450311.5022
286 | Muktijuddho Montranalaya | D394MJ | 11 | 0 | DHK-C9376 | 1 | 99696.86 | 107684.92 | 7988.06 | 60 | 0 | 479283.6 | 483907.4515 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 671537.2027 | 860939.7125 | 912278.2358 | 979522.345 | 1003580.0431 | 989924.3443 | 925250.3935
287 | Purana Palton | D394R | 11 | 0 | DHK-C9318 | 1 | 70819.4 | 74578.56 | 3759.16 | 60 | 0 | 225549.6 | 227725.5723 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 301353.4691 | 347167.2021 | 309416.4011 | 349193.9997 | 350733.9486 | 318744.0733 | 328976.7665
288 | Tip Top Feeder | 0 | 11 | 0 | DHK-C9318 | 1 | 92552.33 | 104709.02 | 12156.69 | 60 | 0 | 729401.4 | 736438.2437 | Kakrail | Biddyut Bhaban 33/11 KV | 94 | 1345378.9377 | 2213157.3667 | 1322789.6384 | 1326276.1291 | 1389761.4375 | 1427034.1549 | 1299449.2529
289 | 11/0.4 kV Auxiliary Transformer, AT | 0 | 0.415 | 0 | DHKD3784 | 1 | 359859 | 363148 | 3289 | 1 | 0 | 3289 | 3320.7304 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 4689.0579 | 5100.6865 | 4311.9923 | 4669.8501 | 4947.3654 | 4696.0253 | 4800.6724
290 | Nearest O/H | D398NE | 11 | 0 | 00000126 | 1 | 8118980 | 8233620 | 114640 | 1 | 0 | 114640 | 115623.9439 | Ramna | DMC 33/11 KV SS | 98 | 175545.4669 | 200195.8311 | 223877.2462 | 227289.0317 | 224820.1739 | 210729.7741 | 229906.9253
291 | Jagannath Hall | D398JA | 11 | 0 | 00000002 | 1 | 3050232 | 3117432.5 | 67200.5 | 1 | 0 | 67200.5 | 67777.2753 | Ramna | DMC 33/11 KV SS | 98 | 82037.8689 | 101039.4533 | 107985.9597 | 106229.8836 | 110593.2428 | 113276.1711 | 96242.8599
292 | Samsun Nahar Hall | D398SN | 11 | 0 | 00000024 | 1 | 10524494 | 10689174 | 164680 | 1 | 0 | 164680 | 166093.4323 | Ramna | DMC 33/11 KV SS | 98 | 229211.7629 | 277277.1279 | 321630.4227 | 329771.0476 | 322680.6125 | 293593.2672 | 312413.2678
293 | Spare, 4L | 0 | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | Board Office O/H, (5L) | A3983 | 11 | 0 | 00000023 | 1 | 23025144 | 23638862 | 613718 | 1 | 0 | 613718 | 618985.4813 | Lalbag | DMC 33/11 KV SS | 98 | 282360.0725 | 404116.548 | 474520.243 | 554924.1978 | 600144.1706 | 492983.2953 | 466712.6927
295 | OT- Complex | D398OT | 11 | 0 | 00000167 | 1 | 7175302 | 7368582 | 193280 | 1 | 0 | 193280 | 194938.9033 | Ramna | DMC 33/11 KV SS | 98 | 340061.3683 | 106528.8271 | 336918.4015 | 246189.5687 | 446170.5101 | 427837.7768 | 405707.0733
296 | Alia Mdrasha O/H, (7L) | A3984 | 11 | 0 | 00000148 | 1 | 9776616 | 9997056 | 220440 | 1 | 0 | 220440 | 222332.0149 | Lalbag | DMC 33/11 KV SS | 98 | 101819.0581 | 64901.5515 | 73635.9109 | 143184.6648 | 77701.5086 | 75154.3226 | 71193.4446
297 | Majed Sordar Road | B698J | 11 | 0 | 00000164 | 1 | 62242088 | 63519284 | 1277196 | 1 | 0 | 1277196 | 1288158.0478 | Bangshal | DMC 33/11 KV SS | 98 | 1959932.9522 | 1719312.7006 | 1747073.1814 | 1774470.2621 | 1602752.7729 | 1759301.3409 | 1689289.8138
298 | Chankharpool, 9L | B698Q | 11 | 0 | 00000001 | 1 | 50750956 | 51452996 | 702040 | 1 | 0 | 702040 | 708065.5404 | Bangshal | DMC 33/11 KV SS | 98 | 416746.8435 | 1136431.6854 | 1199639.3416 | 1210601.5564 | 1176945.2408 | 1201456.0712 | 1157798.1959
299 | Shahidullah College O/H, (10L) | A3986 | 11 | 0 | 00000003 | 1 | 13802806 | 14004206 | 201400 | 1 | 0 | 201400 | 203128.5964 | Lalbag | DMC 33/11 KV SS | 98 | 207912.8783 | 235452.0398 | 255337.0354 | 264888.6074 | 263222.0224 | 263967.4494 | 265403.8751
300 | Ananda Bazar | D398AB | 11 | 0 | 00000111 | 1 | 15359723 | 15427242 | 67519 | 1 | 0 | 67519 | 68098.5089 | Ramna | DMC 33/11 KV SS | 98 | 103817.0773 | 119468.7736 | 114687.4296 | 145238.9396 | 167074.5674 | 216784.0965 | 169141.9631
301 | Hosseni Dalan O/H, (12L) | A3985 | 11 | 0 | 0 | 1 | 65.91 | 67.97 | 2.06 | 60000 | Estimated | 688147.92 | 694054.226 | Lalbag | DMC 33/11 KV SS | 98 | 859332.9703 | 999393.6344 | 862949.5725 | 1039954.5727 | 1170127.1783 | 1629339.2554 | 1651805.4359
302 | Badrun Nessa College | A398W | 11 | 0 | 00000006 | 1 | 21354548 | 21641708 | 287160 | 1 | 0 | 287160 | 289624.6661 | Lalbag | DMC 33/11 KV SS | 98 | 354408.6447 | 469459.7974 | 504253.5009 | 510636.8949 | 522687.5196 | 511348.0734 | 487810.3149
303 | Dhaka Medical College, Unit-II | D398DM | 11 | 0 | 00000125 | 1 | 12836569 | 13008288 | 171719 | 1 | 0 | 171719 | 173192.8473 | Ramna | DMC 33/11 KV SS | 98 | 223818.1101 | 299392.072 | 310172.7151 | 327495.1248 | 332597.3491 | 314783.3957 | 318669.3545
304 | Spare, 15L | 0 | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | Sheikh Hasina National Burn Institute | D398SH | 11 | 0 | 00000127 | 1 | 22395106 | 22744864 | 349758 | 1 | 0 | 349758 | 352759.9386 | Ramna | DMC 33/11 KV SS | 98 | 420023.595 | 543136.2141 | 551404.561 | 585271.851 | 637362.5402 | 594088.462 | 527600.9918
306 | Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKF-7804 | 1 | 2923.68 | 2923.68 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 5076.9668 | 7678.1323 | 7994.6127 | 7937.0165 | 8829.1604 | 8254.0596 | 7320.9952
307 | Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | Secratariet East | D363BS | 11 | 0 | BD 013966 | 1 | 4544.19 | 4662.1 | 117.91 | 1000 | 0 | 117910 | 119229.0018 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 176076.397 | 242760.0671 | 221126.0937 | 241216.6768 | 260076.7434 | 245293.0009 | 245463.3743
309 | Taher Bag O/H | B163G | 11 | 0 | BD 014045 | 1 | 21284.07 | 21741.99 | 457.92 | 1000 | 0 | 457920 | 463042.5281 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 606900.3521 | 725752.2867 | 829864.029 | 794329.1648 | 678707.287 | 744464.9674 | 740283.3012
310 | Al Raji Complex | D363AR | 11 | 0 | BD 013983 | 1 | 16656.82 | 17122.03 | 465.21 | 1000 | 0 | 465210 | 470414.0777 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 584839.7594 | 756317.9861 | 777798.4115 | 793783.38 | 773675.1898 | 784809.8778 | 793405.3649
311 | Raduni | D363RI | 11 | 0 | BD 013999 | 1 | 31732.57 | 32490.8 | 758.23 | 1000 | 0 | 758230 | 766711.9498 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 970925.0317 | 1082729.9623 | 1265333.7606 | 1301100.4786 | 623159.8339 | 1293358.488 | 1280815.0384
312 | Sundor Bon Square O/H | B163D | 11 | 0 | BD 013954 | 1 | 14602.66 | 14944.13 | 341.47 | 1000 | 0 | 341470 | 345289.8586 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 413245.1984 | 496614.8713 | 482395.9106 | 519829.721 | 434096.0289 | 473931.0551 | 515871.5523
313 | Shromo Bhobon O/H | D363SB | 11 | 0 | BD 013985 | 1 | 14602.66 | 14888.74 | 286.08 | 1000 | 0 | 286080 | 289280.2377 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 470791.9727 | 489342.1006 | 495640.2335 | 516585.3335 | 525134.9167 | 505142.6077 | 521299.6391
314 | Nawabpur Road | B163P | 11 | 0 | BD 013953 | 1 | 22640.38 | 23160.37 | 519.99 | 1000 | 0 | 519990 | 525806.8749 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 713209.502 | 834593.0606 | 843248.6095 | 904941.5553 | 800366.4326 | 843066.7121 | 849749.7199
315 | Spair | 0 | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | Spare | 0 | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | Ahad Police Box | D363AP | 11 | 0 | BD 013984 | 1 | 12534.21 | 12968.49 | 434.28 | 1000 | 0 | 434280 | 439138.0789 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 488719.3167 | 481256.786 | 438024.4232 | 458924.1778 | 366641.2546 | 470281.7667 | 423970.1788
318 | Nearest O/H | D363NE | 11 | 0 | BD 013997 | 1 | 2970.68 | 3058.55 | 87.87 | 1000 | 0 | 87870 | 88852.9589 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 103430.8152 | 124640.2411 | 121402.9541 | 117384.1651 | 114763.3233 | 117912.5625 | 115595.8875
319 | Natab Bhaban | D363NB | 11 | 0 | BD 014000 | 1 | 5488.09 | 5613.02 | 124.93 | 1000 | 0 | 124930 | 126327.5311 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 141307.3092 | 179461.8844 | 187424.2009 | 177268.8886 | 180013.0381 | 185708.2311 | 177165.0302
320 | Spare | 0 | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | Awami League Party Office | D363AO | 11 | 0 | BD 013956 | 1 | 1452.23 | 1459.86 | 7.63 | 1000 | 0 | 7630 | 7715.3531 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 18136.4963 | 10332.35 | 10118.5826 | 5579.1337 | 3568.1872 | 9417.1914 | 9250.1106
322 | Khaddar Bazar | D363KB | 11 | 0 | BD 014012 | 1 | 11244.73 | 11528.62 | 283.89 | 1000 | 0 | 283890 | 287065.7392 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 332552.2312 | 396371.0138 | 401687.6915 | 409449.7945 | 392931.5775 | 394275.1992 | 392631.6173
323 | Bangobondu National Stidium | D363NS | 11 | 0 | BD 014008 | 1 | 11498.09 | 11887.08 | 388.99 | 1000 | 0 | 388990 | 393341.4417 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 1044626.3348 | 1319581.5303 | 1315375.6615 | 1298280.5904 | 390265.4601 | 288658.7112 | 290128.194
324 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4418 | 1 | 1481.27 | 1548.06 | 66.79 | 100 | 0 | 6679 | 6753.7147 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 7343.2393 | 8140.4874 | 6640.1946 | 13693.1347 | 0 | 0 | 1718.8942
325 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 48.11 | 48.15 | 0.04 | 100 | 0 | 4 | 4.0447 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 30.0552 | 597.3312 | 0 | 0 | 387.2849
326 | 11 KV Ring Road Feeder | G134R | 11 | 0 | 77816675 | 1 | 42456.21 | 42542.57 | 86.36 | 8000 | 0 | 690880 | 708152 | Adabor | Kallyanpur 33/11KV S/S | 34 | 871742 | 1122088 | 1191132 | 1186458 | 1209910 | 1172682 | 1124384
327 | 11 KV Gano Bhavan RMU | D534T | 11 | 0 | DHK14997 | 1 | 995.9 | 996.01 | 0.11 | 40000 | 0 | 4400 | 4510 | Shere b.nagar | Kallyanpur 33/11KV S/S | 34 | 1230 | 2050 | 2050 | 1230 | 1230 | 1230 | 1230
328 | 11 KV Adabor O/H | D434A | 11 | 0 | DHK14957 | 1 | 4620.87 | 4662.01 | 41.14 | 40000 | 0 | 1645600 | 1686740 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1540370 | 2118880 | 2481320 | 2098790 | 1976610 | 2150040 | 2995460
329 | 11 KV Goidertek (DPDC) | G134G | 11 | 0 | DHK14996 | 1 | 9431.09 | 9438.88 | 7.79 | 40000 | 0 | 311600 | 319390 | Adabor | Kallyanpur 33/11KV S/S | 34 | 663380 | 612540 | 617460 | 614590 | 586300 | 591220 | 558420
330 | 11 KV Beribandh Feeder. | G134K | 11 | 0 | DHK14960 | 1 | 9673.06 | 9678.27 | 5.21 | 40000 | 0 | 208400 | 213610 | Adabor | Kallyanpur 33/11KV S/S | 34 | 230010 | 285360 | 348090 | 239440 | 234930 | 301350 | 184500
331 | 11 KV Sewarage Pump | G134P | 11 | 0 | DHK14959 | 1 | 2350.06 | 2404.55 | 54.49 | 40000 | 0 | 2179600 | 2234090 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2206210 | 2792510 | 1776530 | 2952000 | 2380460 | 2601450 | 535870
332 | 11 KV Technical School (DPDC) | G134T | 11 | 0 | DHK15019 | 1 | 8401.63 | 8432.58 | 30.95 | 40000 | 0 | 1238000 | 1268950 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1626470 | 2204980 | 2398910 | 2363240 | 2400960 | 2347660 | 2184890
333 | 11 KV Mansurabad | G134M | 11 | 0 | 77816681 | 1 | 52970.34 | 53140.44 | 170.1 | 8000 | 0 | 1360800 | 1394820 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1650496 | 2258116 | 2458196 | 2422936 | 2313630 | 2379804 | 2220888
334 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 41105.9 | 41136.9 | 31 | 1000 | 0 | 31000 | 31110.7192 | Kakrail | Moghbazar 33/11KV S/S | 8 | 140940.5878 | 170232.3057 | 173300.7767 | 177316.5531 | 65016.8533 | 1691.4448 | 1119.369
335 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 81024 | 81311.7 | 287.7 | 1000 | 0 | 287700 | 288727.5453 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 67586.7284 | 136288.0862 | 107803.7381 | 78656.0729 | 96666.9717 | 802696.2793 | 1023306.7911
336 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1589911.0287
337 | 11 kV Tejgaon S/S-1 | 0 | 11 | T-1 | 30/11004-1101 | 1 | 121092.2 | 121388.3 | 296.1 | 1000 | 0 | 296100 | 297157.5466 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 354627.9687 | 467141.9849 | 391310.8557 | 416531.5604 | 434303.9973 | 326660.2796 | 342221.6327
338 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 125174.5 | 126081.4 | 906.9 | 1000 | Estimated | 1216328.4 | 1220672.6215 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1548241.5645 | 1803211.1873 | 1782922.7783 | 2012798.2977 | 1909092.2251 | 1919578.4326 | 1819483.4353
340 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 133873.6 | 135083.5 | 1209.9 | 1000 | 0 | 1209900 | 1214221.262 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 1754826.6729 | 2252689.725 | 2523568.5136 | 2372564.6062 | 2579216.4264 | 2455343.5773 | 1989016.959
341 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 150222.7 | 151349.6 | 1126.9 | 1000 | 0 | 1126900 | 1130924.8203 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1339188.5287 | 1537918.5242 | 1644738.2335 | 1666230.9769 | 1593234.7726 | 1205154.4296 | 1055666.7314
342 | 11 kV Vumi Bhaban | 0 | 11 | T-3 | 21101039 | 1 | 9098.9 | 9161.9 | 63 | 1000 | 0 | 63000 | 63225.0099 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 102897.7587 | 143547.2416 | 140604.4879 | 151132.7739 | 165331.6353 | 136267.0228 | 122011.2214
343 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10241.6 | 10338.2 | 96.6 | 1000 | 0 | 96600 | 96945.0152 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 117467.3528 | 150704.1553 | 173927.5426 | 164434.1337 | 177991.6827 | 170095.919 | 154167.6401
344 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 130036 | 131183.1 | 1147.1 | 1000 | 0 | 1147100 | 1151196.9663 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1495406.9549 | 1911100.4557 | 2221153.9574 | 2075012.1387 | 2269581.709 | 2138303.3901 | 1962152.1029
345 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 90371.6 | 91408.5 | 1036.9 | 1000 | 0 | 1036900 | 1040603.3776 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1298009.1897 | 1555095.1172 | 1652781.7295 | 1586003.8772 | 1603212.6065 | 1595983.8968 | 78254.0694
346 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 180854.9 | 181893.3 | 1038.4 | 1000 | 0 | 1038400 | 1042108.7349 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1981464.8041 | 2346752.0201 | 2390485.2167 | 1095738.7944 | 1085008.9734 | 952812.0065 | 1869447.9972
347 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124552.3 | 124790.9 | 238.6 | 1000 | 0 | 238600 | 239452.1804 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 307276.7877 | 363366.7355 | 399563.2736 | 370867.0494 | 398147.7603 | 399920.9831 | 690345.3929
348 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 116794.1 | 117328.9 | 534.8 | 1000 | 0 | 534800 | 536710.0842 | Kakrail | Moghbazar 33/11KV S/S | 8 | 748310.5439 | 931830.1708 | 991857.0675 | 900407.8011 | 994564.7368 | 950591.9851 | 944645.6784
349 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 45007.6 | 45319 | 311.4 | 1000 | 0 | 311400 | 312512.1919 | Kakrail | Moghbazar 33/11KV S/S | 8 | 397324.9737 | 478388.5637 | 514783.7418 | 344054.8595 | 0 | 0 | 323294.1205
350 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | 8665568.0754 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 1357.9928 | 0 | 0 | 0 | 0
351 | 11 kV TCB Feeder | C608P | 11 | T-4 | 0 | 1 | 37126.3 | 37210.6 | 84.3 | 1000 | 0 | 84300 | 91371.619 | Kakrail | Moghbazar 33/11KV S/S | 8 | 275835.9679 | 327449.4305 | 337617.6819 | 593608.4852 | 1091208.9552 | 1058026.2525 | 587067.814
352 | 11 kV Tejgaon SS-2 | 0 | 11 | T-4 | 0 | 1 | 35724.6 | 36834.7 | 1110.1 | 1000 | 0 | 1110100 | 1203222.2332 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1541959.4958 | 1519526.851 | 1537848.541 | 1385049.7687 | 1574127.4074 | 1532552.8114 | 1481122.0985
353 | Holy Day Inn | C108HY | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 263640 | 285755.7964 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 328334.8182 | 421689.4191 | 437235.9991 | 578900.3818 | 542740.3295 | 522630.1141 | 493817.3233
354 | Polly Bhabon-2 | C608PB | 11 | T-4 | 0 | 1 | 18385 | 18386 | 1 | 1000 | According to AMR meter reading | 9660 | 10470.3421 | Kakrail | Moghbazar 33/11KV S/S | 8 | 17302.438 | 23296.5077 | 25096.5994 | 28135.8532 | 27898.691 | 30058.9479 | 29444.1053
355 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 | 0 | 1 | 21533.5 | 22448.4 | 914.9 | 1000 | 0 | 914900 | 991647.6183 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1456551.0784 | 1783228.8258 | 1839066.8165 | 1861301.6803 | 1854771.9565 | 1842884.7823 | 1860061.7445
356 | 11 kV Tejturibazar | C608X | 11 | T-4 | 0 | 1 | 133302 | 133608 | 306 | 1000 | 0 | 306000 | 331669.222 | Kakrail | Moghbazar 33/11KV S/S | 8 | 405180.9614 | 781650.0519 | 797094.2458 | 844174.6782 | 788742.3253 | 776669.7972 | 731592.6735
357 | Songsad | 0 | 11 | T-4 | 0 | 1 | 3864.8 | 3864.8 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Moghbazar 33/11KV S/S | 8 | 0 | 154587.5799 | 443228.713 | 416692.9 | 475259.7411 | 544550.7215 | 126381.9385
358 | Chennel 24 | 0 | 11 | T-4 | 0 | 1 | 7329.92 | 7333.57 | 3.65 | 1000 | 0 | 3650 | 3956.1852 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 2657.627 | 3644.2295 | 5053.7147 | 7574.2329 | 3766.4072 | 1700.7368 | 1164.858
359 | Sonargaon | C608K | 11 | T-4 | 0 | 1 | 42568 | 43020.7 | 452.7 | 1000 | 0 | 452700 | 490675.349 | Kakrail | Moghbazar 33/11KV S/S | 8 | 653797.6846 | 888533.2859 | 916526.5008 | 698965.1841 | 733347.8124 | 844174.3497 | 839625.5215
360 | AT -1 | 0 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7215.9345
361 | AT -2 | 0 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 3408768.3652 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 225815 | 240206 | 14391 | 60 | 0 | 863460 | 872488.6042 | Kakrail | T&T 33/11 KV | 105 | 1045950.5553 | 350929.0306 | 1384212.3787 | 1354639.697 | 1410640.1386 | 1413099.3422 | 1314936.3633
363 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 508205 | 521860 | 13655 | 60 | 0 | 819300 | 827866.8536 | Kakrail | T&T 33/11 KV | 105 | 1005950.1284 | 1232617.5702 | 1434115.4167 | 1367760.1292 | 1475917.0544 | 1466512.1688 | 1363050.3594
364 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 968143 | 971446 | 3303 | 60 | 0 | 198180 | 200252.2312 | Moghbazar | T&T 33/11 KV | 105 | 266002.8385 | 363967.9203 | 383823.6058 | 382050.2122 | 390823.0756 | 376350.3769 | 416269.8468
365 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1999157 | 2007924 | 8767 | 60 | 0 | 526020 | 531520.2274 | Moghbazar | T&T 33/11 KV | 105 | 691583.1374 | 808883.1556 | 925176.0601 | 915135.1719 | 946635.0529 | 901476.4809 | 862940.0791
366 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 690.8 | 706.34 | 15.54 | 60000 | 0 | 932400 | 942149.4621 | Moghbazar | T&T 33/11 KV | 105 | 1206073.4761 | 1469087.5693 | 1653485.829 | 1672106.229 | 1759482.372 | 1708010.1623 | 1630130.9123
367 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 923585 | 929471 | 5886 | 60 | 0 | 353160 | 356852.7499 | Kakrail | T&T 33/11 KV | 105 | 456065.4727 | 614479.8006 | 616445.7818 | 601742.5641 | 617435.7813 | 612807.1598 | 591251.5937
368 | 11 kV cinema hall | 0 | 11 | Mogbazar | DHK60979 | 1 | 535968 | 546370 | 10402 | 60 | 0 | 624120 | 630645.9913 | Moghbazar | T&T 33/11 KV | 105 | 805584.354 | 981161.6979 | 1071064.8459 | 1069584.8264 | 1086052.1721 | 1077858.8375 | 1046359.7284
369 | 11 kV malibagh bazar | 0 | 11 | Khailgaon | DHK61106 | 1 | 803461 | 819498 | 16037 | 60 | 0 | 962220 | 972281.2692 | Khilgaon | T&T 33/11 KV | 105 | 1271165.0797 | 1621719.2778 | 1701657.7808 | 1728362.3289 | 1686240.4748 | 1646555.4045 | 1662984.8723
370 | 11 kv Sherebangla | D1105G | 11 | 0 | DHK60915 | 1 | 782199 | 795455 | 13256 | 60 | 0 | 795360 | 803676.5296 | Moghbazar | T&T 33/11 KV | 105 | 1035344.3815 | 1275392.2083 | 1525385.4467 | 1396637.0623 | 1544547.6466 | 1416880.2502 | 1438632.4204
371 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 364525 | 374009 | 9484 | 60 | 0 | 569040 | 574990.0578 | Moghbazar | T&T 33/11 KV | 105 | 572490.9575 | 647224.5235 | 706402.574 | 705627.6304 | 690498.0173 | 692746.3564 | 708065.6738
372 | Auxiliary | 0 | 0 | Export | U0004461 | 1 | 8333.5 | 8372.09 | 38.59 | 60 | 0 | 2315.4 | 2339.6105 | Moghbazar | T&T 33/11 KV | 105 | 2704.2713 | 3869.1873 | 7599.4686 | 0 | 4061.5417 | 3583.4605 | 3045.4245
373 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 588546 | 594097.7099 | Moghbazar | Ullon local 33/11KV S/S | 92 | 711283.282 | 977173.2999 | 1007307.2369 | 980334.5269 | 1038100.3806 | 1138226.0536 | 978294.9507
374 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1059382.8 | 1069375.8779 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1304019.3504 | 1832199.9373 | 1836854.3731 | 1838127.2379 | 1648747.6632 | 1617479.1288 | 1406298.9916
375 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 918131.76 | 926792.4275 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1244745.7435 | 1526833.2811 | 1659094.2725 | 1654314.5141 | 1770877.1198 | 1677385.7633 | 1345155.5572
376 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 588546 | 594097.7099 | Moghbazar | Ullon local 33/11KV S/S | 92 | 924668.2666 | 1038246.6311 | 1125813.9706 | 1102876.3427 | 1282359.2936 | 1317945.9568 | 1100581.8195
377 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 941673.6 | 950556.3359 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1185472.1367 | 1710053.2748 | 1718347.6394 | 1715585.422 | 1648747.6632 | 1557572.4944 | 1345155.5572
378 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 529691.4 | 534687.9389 | Moghbazar | Ullon local 33/11KV S/S | 92 | 889104.1025 | 1099319.9624 | 1149515.3174 | 1225418.1586 | 1282359.2936 | 1377852.5912 | 1222868.6883
379 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | AT-1 | 0 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | AT-2 | 0 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 17.0895 | 18.1608 | 1.0713 | 1000000 | 0 | 1071292 | 1077503.1322 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1312980.8765 | 1733090.4653 | 1860379.5125 | 1839023.3133 | 1914129.2674 | 1830321.6533 | 1753548.1446
383 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 106484.9 | 107601.2 | 1116.3 | 1000 | 0 | 1116300 | 1122772.0794 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1278337.9483 | 1814364.7668 | 1995837.5311 | 1955619.6426 | 2015001.2811 | 1947058.9925 | 1858521.5132
384 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 7446.5 | 8767.9 | 1321.4 | 1000 | 0 | 1321400 | 1329061.2073 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1227377.6551 | 2135456.6106 | 2140470.7173 | 2127980.2733 | 2037129.655 | 2033626.6462 | 1264456.5681
385 | Goran | A921G | 11 | 0 | X1390296 | 1 | 35532.5 | 36638.8 | 1106.3 | 1000 | 0 | 1106300 | 1112714.1015 | Bashabo | Madarteck 33/11KV S/S | 21 | 1214687.9378 | 1825010.9149 | 1949936.5823 | 1924894.1079 | 2047460.5279 | 1968306.9598 | 1851494.7743
386 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 15256.78 | 16123.789 | 867.009 | 1000 | 0 | 867009 | 872035.7411 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1038687.6018 | 1446701.0468 | 1502775.9682 | 1533961.2033 | 1583000.8619 | 1493157.2972 | 2039169.8043
387 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 21 | 0 | 0 | 0 | 0 | 0 | 373198.8946 | 881499.2996
388 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1661.0999 | 1837.281 | 176.1811 | 1000 | 0 | 176181.1 | 177202.562 | Mugdapara | Madarteck 33/11KV S/S | 21 | 183059.6459 | 244346.2732 | 252299.2953 | 242642.782 | 236939.3158 | 229733.5056 | 209712.5124
389 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 5343.364 | 5741.1932 | 397.8292 | 1000 | 0 | 397829.2 | 400135.7324 | Mugdapara | Madarteck 33/11KV S/S | 21 | 375481.886 | 578366.2569 | 687579.7395 | 671883.3535 | 576962.6065 | 679941.1966 | 331641.7074
390 | Mugdapara | B921P | 11 | 0 | X0854272 | 1 | 4957.2 | 5114.1 | 156.9 | 1000 | 0 | 156900 | 157809.6742 | Maniknagar | Madarteck 33/11KV S/S | 21 | 277461.6755 | 259324.0979 | 280126.3587 | 262278.8244 | 99804.6 | 280453.0279 | 256934.2344
391 | Singapur | F221S | 11 | 0 | X1390302 (N) | 1 | 41999.2 | 43327 | 1327.8 | 1000 | 0 | 1327800 | 1335498.3132 | Banosree | Madarteck 33/11KV S/S | 21 | 1578862.6815 | 2168600.2792 | 2400509.1335 | 2332917.0805 | 2449510.2642 | 2359732.7837 | 2200082.1244
392 | Trimohony | F221T | 11 | 0 | X1390308 | 1 | 34398.2 | 35701.8 | 1303.6 | 1000 | 0 | 1303600 | 1311158.0066 | Banosree | Madarteck 33/11KV S/S | 21 | 1565165.8438 | 2029899.048 | 2144287.4264 | 2101565.9326 | 2104795.0854 | 2021980.735 | 1604947.893
393 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 19281.996 | 20389.554 | 1107.558 | 1000 | 0 | 1107558 | 1113979.3951 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1516431.2867 | 1620835.8728 | 1884688.9362 | 1948965.1387 | 1816135.3069 | 1942171.9601 | 1839386.3794
394 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 7716.29 | 7952.16 | 235.87 | 1000 | 0 | 235870 | 237237.5261 | Mugdapara | Madarteck 33/11KV S/S | 21 | 554113.2234 | 808655.6976 | 863662.2068 | 854936.3865 | 710891.4812 | 850151.1099 | 596386.824
395 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 755370 | 761504 | 6134 | 200 | 0 | 1226800 | 1233912.7358 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1333024.5871 | 1795382.4839 | 1921009.9451 | 1954912.1468 | 1661387.6173 | 1892982.4123 | 480873.3471
396 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 783208 | 787992 | 4784 | 200 | 0 | 956800 | 962347.331 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1198876.1472 | 1488652.8964 | 1652835.9122 | 1533042.4693 | 1508090.9874 | 1450702.4488 | 298789.1572
397 | Nakhal Para Feeder | C110U | 11 | 0 | DHK60950 | 1 | 324180.3 | 338621.4 | 14441.1 | 60 | 0 | 866466 | 879252.6995 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1127439.9287 | 1500089.328 | 1599409.3479 | 1587033.6595 | 1590100.5899 | 1545202.0376 | 1536369.5556
398 | Badda-Meghna Feeder | C110N | 11 | 0 | DHK60979 | 1 | 952442.1 | 960822.6 | 8380.5 | 60 | 0 | 502830 | 510250.4136 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 710173.5747 | 794267.6303 | 812324.781 | 768867.2754 | 797427.1133 | 711868.0468 | 842649.7133
399 | Rasulbagh Feeder | C110K | 11 | 0 | DHK60948 | 1 | 107045.9 | 127321.3 | 20275.4 | 60 | 0 | 1216524 | 1234476.6108 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1507771.5116 | 1806034.3017 | 1726738.2372 | 1932163.7903 | 1821935.9992 | 1845073.9247 | 1902151.6741
400 | Lukas | C171V | 11 | 0 | 8A021100948-02 | 1 | 75134351 | 76487313 | 1352962 | 1 | 0 | 1352962 | 1372928.0674 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1596720.7407 | 2026298.4778 | 2352263.3192 | 2382018.4101 | 2450636.3287 | 2356930.5125 | 2345545.782
401 | PWD RMU | 0 | 11 | 0 | 0 | 1 | 661501.9 | 662699.7 | 1197.8 | 1 | 0 | 1197.8 | 1215.4763 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1463.309 | 1806.986 | 1917.0903 | 1854.955 | 1876.4622 | 1825.2484 | 1757.0539
402 | Civil Aviation Feeder | 0 | 11 | 0 | DHK60977 | 1 | 19068.7 | 47798.9 | 28730.2 | 60 | 0 | 1723812 | 1749250.8125 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2103712.8393 | 2870937.6357 | 3006456.2987 | 2816826.0828 | 2972868.5519 | 2843930.4649 | 2795399.6317
403 | Ahasanullah Eng. | C171L | 11 | 0 | DHK60867 | 1 | 908328.2 | 914459.3 | 6131.1 | 60 | 0 | 367866 | 373294.7093 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 467019.6637 | 571155.4762 | 575802.5636 | 668050.5071 | 681476.0179 | 638085.1899 | 673101.4258
404 | New GMG Feeder | C110M | 11 | 0 | DHK61106 | 1 | 180726.9 | 204440.4 | 23713.5 | 60 | 0 | 1422810 | 1443806.8354 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1745180.0137 | 1868942.3881 | 2083647.5312 | 2435471.7452 | 2366892.1845 | 2233355.6797 | 2281871.6214
405 | Shikajo | C171Z | 11 | 0 | HA021101036-02 | 1 | 66732385 | 67251272 | 518887 | 1 | 0 | 518887 | 526544.3716 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 677285.3335 | 862880.7653 | 832111.8625 | 813808.0835 | 877169.4199 | 833321.8823 | 756034.1648
406 | Kahinur | 0 | 11 | 0 | 0 | 1 | 602529.6 | 616855.2 | 14325.6 | 60 | 0 | 859536 | 872220.4314 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1070076.3665 | 1309013.1381 | 1330662.8857 | 1351230.8033 | 1347009.4431 | 1251045.3402 | 1294083.2246
407 | Link road | C171X | 11 | 0 | 8A021100380-02 | 1 | 66526725 | 66817451 | 290726 | 1 | 0 | 290726 | 295016.3311 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 416288.669 | 724119.8808 | 647867.3456 | 425896.0895 | 415317.8944 | 416737.628 | 435428.3198
408 | Shanta | C110E | 11 | 0 | 0 | 1 | 350241.3 | 357200.4 | 6959.1 | 60 | 0 | 417546 | 423707.852 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 526308.4207 | 628311.0309 | 599004.2611 | 643052.4099 | 671568.0547 | 608607.1616 | 630895.3248
409 | Karnafuly Feeder | C110Y | 11 | 0 | DHK61084 | 1 | 37300.6 | 37764.9 | 464.3 | 1000 | 0 | 464300 | 471151.8148 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 622218.1242 | 807314.3803 | 766856.2088 | 716684.8588 | 722759.1976 | 686952.8872 | 738300.0364
410 | Butex | C110BT | 11 | 0 | 0 | 1 | 1403 | 1478.6 | 75.6 | 1000 | 0 | 75600 | 76715.652 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 104608.2847 | 106281.4076 | 100920.6493 | 102946.4154 | 100374.7899 | 90006.1656 | 91610.1416
411 | OriON LAB | C171A | 11 | 0 | 0 | 1 | 8454240 | 8514212 | 59972 | 1 | 0 | 59972 | 60857.0249 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 76732.1885 | 90864.5418 | 93311.3932 | 93876.22 | 95833.6401 | 88588.4676 | 248723.2522
412 | Nina kabbo | C171Y | 11 | 0 | 201101025-2 | 1 | 17854558 | 18027840 | 173282 | 1 | 0 | 173282 | 175839.1746 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 208000.4981 | 261868.4978 | 264819.2014 | 285983.9298 | 281438.971 | 283127.915 | 99489.3009
413 | Satrong | C171S | 11 | 0 | HA021100515-2 | 1 | 98397161 | 99276332 | 879171 | 1 | 0 | 879171 | 892145.191 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1231591.5581 | 1888984.3136 | 2007795.2093 | 1899691.7228 | 1806807.9399 | 1563100.3489 | 1367977.887
414 | South East RMU | 0 | 11 | 0 | 0 | 1 | 1176.1 | 1238.1 | 62 | 1000 | 0 | 62000 | 62914.9527 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 67794.2153 | 115171.8675 | 137308.3735 | 130223.6796 | 128807.568 | 139045.3993 | 149070.967
415 | Rangs Bhaban | 0 | 11 | 0 | HA021100939-2 | 1 | 1006950 | 1105998 | 99048 | 1 | 0 | 99048 | 100509.6811 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 126221.9657 | 151848.0457 | 148545.345 | 152471.8244 | 163396.3968 | 151255.7649 | 161670.1139
416 | Babli | C171R | 11 | 0 | 0 | 1 | 61327 | 62640.4 | 1313.4 | 1000 | 0 | 1313400 | 1332782.2391 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 926990.3383 | 1047558.8549 | 1066401.5624 | 2240675.7095 | 2109084.7983 | 2111815.0669 | 1541422.4274
417 | SPL | 0 | 11 | 0 | 0 | 1 | 5708.6 | 6113.4 | 404.8 | 1000 | 0 | 404800 | 410773.7554 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 403948.9148 | 470689.2376 | 471130.5611 | 465633.0017 | 455733.9249 | 408962.9923 | 372268.4438
418 | DNCC Hospital | 0 | 11 | 0 | 0 | 1 | 18258.1 | 18777.8 | 519.7 | 1000 | 0 | 519700 | 527369.3693 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 724311.7867 | 958856.3113 | 1039161.0285 | 1028453.8853 | 1058083.8484 | 992388.6083 | 965076.0343
419 | 11/.415 kv Local transformer | 0 | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 0 | 0 | 0 | 0 | 0 | 6054.2264 | 6134.6077
420 | Gonobhaban | D570T | 11 | T-1 | DHKC9332 | 1 | 84785.44 | 86324.71 | 1539.27 | 60 | Previous Meter | 92356.2 | 94730.2684 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 138463.2177 | 186647.9358 | 199883.04 | 203554.794 | 226219.392 | 216875.2359 | 216836.1836
421 | Town hall | D270R | 11 | T-1 | DHKC9339 | 1 | 48476.04 | 48476.4 | 0.36 | 60 | 292041.6 | 292063.2 | 299570.85 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 907389.807 | 1054413.3744 | 1089910.392 | 1159561.608 | 1233509.5584 | 1199461.0668 | 1170856.0696
422 | Post Office | D570S | 11 | T-1 | DHKC9324 | 1 | 85995.04 | 95416.99 | 9421.95 | 60 | 0 | 565317 | 579848.7937 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 881149.6455 | 1103197.1415 | 1099590.636 | 1169672.112 | 1195401.7152 | 1120705.5276 | 1130327.1946
423 | Wasa O/H | C270W | 11 | T-1 | DHKC9333 | 1 | 70721.35 | 76278.95 | 5557.6 | 60 | 0 | 333456 | 342027.6753 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 723429.7254 | 739783.158 | 1806723.552 | 986766.768 | 1324483.5744 | 2118683.8855 | 1049087.4751
424 | Bangabandhu Memorial Museum | 0 | 11 | T-1 | DHKC9334 | 1 | 16545.05 | 16631.31 | 86.26 | 60 | 0 | 5175.6 | 5308.6417 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 12869.2668 | 18497.907 | 17876.394 | 21495.426 | 21201.264 | 20854.3329 | 20897.995
425 | Iqbal Road O/H | D470Q | 11 | T-1 | DHKC9330 | 1 | 66650.02 | 70225.65 | 3575.63 | 60 | 0 | 214537.8 | 220052.6157 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1111797.4278 | 1464338.9745 | 1539511.488 | 1602882.12 | 1776423.3984 | 1626760.4818 | 1601413.1174
426 | Rapa Plaza Feeder | D470W | 11 | T-1 | DHKC9351 | 1 | 34396.36 | 46751.85 | 12355.49 | 60 | 146162.4 | 887491.8 | 910305.2794 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 1599081.4323 | 1961962.9278 | 2111520.342 | 2123219.172 | 2353752.1728 | 1991480.522 | 2338946.2013
427 | Sukrabad/South Plaza | D470P | 11 | T-1 | DHKC9331 | 1 | 50889.76 | 55736.63 | 4846.87 | 60 | 0 | 290812.2 | 298287.6923 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1080300.7626 | 1412012.952 | 1209158.466 | 1512426.318 | 1672604.0352 | 1378440.8932 | 1492441.2314
428 | Shangshad Bhaban | 0 | 11 | T-2 | DHKC9370 | 1.05 | 24023.68 | 24136.05 | 112.37 | 60 | 0 | 7079.31 | 7261.2877 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 0.6051 | 94824.6159 | 417958.806 | 245083.974 | 292942.1376 | 474363.1372 | 422562.5169
429 | Jakir Hossain Road | C270J | 11 | T-2 | DHKC9373 | 1.05 | 83237.19 | 94960.21 | 11723.02 | 60 | 0 | 738550.26 | 757535.1127 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 934510.389 | 1496705.7735 | 741916.104 | 1368356.484 | 1603359.2736 | 1792634.4006 | 1277863.2905
430 | New Colony O/H Feeder | C270N | 11 | T-2 | DHKC9369 | 1.05 | 48198.28 | 61209.99 | 13011.71 | 60 | 0 | 819737.73 | 840809.5526 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1003963.767 | 1053637.6362 | 236025.486 | 1443709.554 | 1041715.3824 | 0 | 1328527.8719
431 | Aurangzeb Feeder | D470M | 11 | T-2 | DHKC9321 | 1 | 54002.53 | 69155.15 | 15152.62 | 60 | 0 | 909157.2 | 932527.6007 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1156516.7382 | 1667662.8612 | 711485.208 | 1577029.554 | 1636123.104 | 1847282.7847 | 2012075.4293
432 | Asadgate Local Feeder | C270E | 11 | T-2 | DHKC9338 | 1.05 | 52468.4 | 60842.91 | 8374.51 | 60 | 0 | 527594.13 | 541156.2359 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 617884.5528 | 1521583.8549 | 1037091.432 | 1943325.648 | 2129079.8592 | 2381609.9379 | 1832840.2298
433 | Sonarbangla Road | D470R | 11 | T-2 | DHKC9320 | 1.05 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0
434 | Humayun Road | D470H | 11 | T-2 | DHKC9366 | 1 | 83086.82 | 115702.31 | 32615.49 | 60 | 0 | 1956929.4 | 2007233.3786 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1566720.6843 | 1813580.3058 | 1032128.898 | 1903127.244 | 1920389.3856 | 263604.1533 | 1670349.266
435 | NHA | D470B | 11 | T-2 | DHKC9374 | 1 | 68657.31 | 70893.51 | 2236.2 | 60 | 0 | 134172 | 137620.9673 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 169863.0669 | 219431.6487 | 72214.596 | 237352.02 | 264138.5376 | 26450.7883 | 221861.5773
436 | Auxiliary transformer | 0 | 0.415 | T-2 | 0 | 1.05 | 672271 | 676258 | 3987 | 1 | 0 | 4186.35 | 4293.9625 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 5219.996 | 7644.43 | 8345.63 | 17430.58 | 0 | 7372.3763 | 6148.5505
437 | Angur Jora | F292A | 11 | 0 | 141 | 1 | 3821920 | 5002480 | 1180560 | 1 | 0 | 1180560 | 1194834.4269 | Banosree | Banasree 33/11 SS | 99 | 1423037.4494 | 2051370.0659 | 2226512.8044 | 2196051.2126 | 2182461.1184 | 2168323.5267 | 1879685.8324
438 | Block F-G Avenue | F299G | 11 | 0 | 68 | 1 | 6117160 | 6894840 | 777680 | 1 | 0 | 777680 | 787083.1107 | Banosree | Banasree 33/11 SS | 99 | 599512.8999 | 2148314.9942 | 2658158.1289 | 2630613.5558 | 2686465.1418 | 2772883.9436 | 2653782.5782
439 | Banasree Main Road(Monpura) | F292P | 11 | 0 | 168 | 1 | 766400 | 1156280 | 389880 | 1 | 0 | 389880 | 394594.1302 | Banosree | Banasree 33/11 SS | 99 | 496465.9196 | 1014510.7585 | 1233831.441 | 1794844.8609 | 1857089.8973 | 1771391.1453 | 1640446.1666
440 | Baitul Kuddus | F292Q | 11 | 0 | 62 | 1 | 7869640 | 9216840 | 1347200 | 1 | 0 | 1347200 | 1363489.3101 | Banosree | Banasree 33/11 SS | 99 | 1686613.9505 | 2119711.2807 | 2318179.6901 | 2240905.0671 | 2321761.5567 | 2248090.2296 | 2090165.4312
441 | Ideal | F214I | 11 | 0 | 0 | 1 | 1080480 | 1502200 | 421720 | 1 | 0 | 421720 | 426819.1151 | Banosree | Banasree 33/11 SS | 99 | 548800.1649 | 698230.2076 | 798010.2701 | 777466.8098 | 813387.6289 | 785714.1589 | 730886.4987
442 | Central Mosque | F292C | 11 | 0 | 46 | 1 | 7883600 | 9070960 | 1187360 | 1 | #REF! | 1187360 | 1201716.6473 | Banosree | Banasree 33/11 SS | 99 | 1552150.2079 | 2014405.8899 | 2216426.2192 | 2155463.3498 | 2252151.7613 | 2213991.1776 | 2027033.5767
443 | Larive | F299L | 11 | 0 | 47 | 1 | 3914200 | 4534040 | 619840 | 1 | 0 | 619840 | 627334.6303 | Banosree | Banasree 33/11 SS | 99 | 804309.6523 | 1248158.3596 | 1177386.9105 | 1133778.6787 | 1209136.6977 | 1154817.1834 | 1075325.8802
444 | Bank Colony | A299K | 11 | 0 | 0 | 1 | 8610600 | 9186160 | 575560 | 1 | 0 | 575560 | 582519.2305 | Khilgaon | Banasree 33/11 SS | 99 | 564812.5793 | 1882703.3 | 767992.5927 | 745817.2151 | 791659.8328 | 743707.201 | 684269.1356
445 | Salambagh | A299G | 11 | 0 | 0 | 1 | 6829880 | 7514640 | 684760 | 1 | 0 | 684760 | 693039.5932 | Khilgaon | Banasree 33/11 SS | 99 | 454833.6424 | 1308766.6526 | 927562.3697 | 1031151.1096 | 794065.0493 | 937481.2326 | 1234217.735
446 | Titas Road | A299T | 11 | 0 | 0 | 1 | 4913000 | 5381360 | 468360 | 1 | 0 | 468360 | 474023.0502 | Khilgaon | Banasree 33/11 SS | 99 | 281534.7278 | 1393019.0625 | 401204.0106 | 522157.3704 | 387724.9431 | 442215.7606 | 461564.0031
447 | AT-1 | 0 | 0.415 | 0 | 7734 | 1 | 3571.06 | 3605.57 | 34.51 | 1 | 0 | 34.51 | 34.9273 | Banosree | Banasree 33/11 SS | 99 | 36.6867 | 64.6367 | 66.5715 | 73.8423 | 76.0089 | 145.5702 | 0
448 | AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0
449 | Meradia | F214M | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estiimated by Grid | 1010556 | 1011378.211 | Banosree | Goran 33/11KV S/S | 14 | 2033879.5103 | 378160.5224 | 0 | 0 | 0 | 0 | 0
450 | Shipahibagh | A914S | 11 | 0 | HA-021001030-02 | 1 | 43252680 | 44110709 | 858029 | 1 | 0 | 858029 | 858727.1116 | Bashabo | Goran 33/11KV S/S | 14 | 1201195.1008 | 1194417.5741 | 1488941.4076 | 1499139.6523 | 1654071.9922 | 1292900.8718 | 1411235.5236
451 | Farazi Hospital | F214F | 11 | 0 | HA-030701081-03 | 1 | 52545470 | 53225584 | 680114 | 1 | 0 | 680114 | 680667.356 | Banosree | Goran 33/11KV S/S | 14 | 834659.8902 | 663014.2572 | 614880.5841 | 0 | 0 | 0 | 0
452 | West Bansree | F214W | 11 | 0 | New Meter | 1 | 99726960 | 100754861 | 1027901 | 1 | 0 | 1027901 | 1028737.3232 | Banosree | Goran 33/11KV S/S | 14 | 1344518.0725 | 1500984.3633 | 1948580.2361 | 1917412.8456 | 1975561.8751 | 1966878.4605 | 1837316.4777
453 | Model School(Nearest) | F214D | 11 | 0 | HA-030701099-03 | 1 | 26588810 | 27983298 | 1394488 | 1 | 0 | 1394488 | 1395622.5866 | Banosree | Goran 33/11KV S/S | 14 | 1890153.6365 | 2273552.5905 | 2474165.667 | 2481856.1691 | 2525253.4223 | 2475694.1412 | 2316464.2537
454 | Bhuiyan Para | F214V | 11 | 0 | HA-021100508-02 | 1 | 64706638 | 64706638 | 0 | 1 | Estiimated by Grid | 1596000 | 1597298.5413 | Banosree | Goran 33/11KV S/S | 14 | 1593748.1926 | 2480699.3677 | 2656699.6806 | 2382096.4852 | 2607870.9453 | 2554505.4549 | 2408712.741
455 | Bonobithi (Ideal) School | F214B | 11 | 0 | HA-021100879-02 | 1 | 21242510 | 22088634 | 846124 | 1 | 0 | 846124 | 846812.4254 | Banosree | Goran 33/11KV S/S | 14 | 1095885.5972 | 1387260.9532 | 1569496.2633 | 1543598.2091 | 1587554.1504 | 1568260.1835 | 1428642.8767
456 | AT-01 | 0 | 0.415 | 0 | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 14 | 0 | 562.2168 | 0 | 0 | 0 | 0 | 0
457 | AT-02 | 0 | 0.415 | 0 | 3043146 | 1 | 5084.2 | 5106.4 | 22.2 | 80 | 0 | 1776 | 1777.445 | Banosree | Goran 33/11KV S/S | 14 | 0 | 11959.1548 | 5508.1614 | 6933.6386 | 6257.2038 | 5424.4075 | 4669.3803
458 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 85 | 1033879.14 | 1043191.4697 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1437106.4117 | 1468016.3082 | 1541495.5501 | 1473463.6679 | 1695740.7049 | 1418643.1678 | 1399733.2864
459 | Bangabobondhu museum | D207B | 11 | Export | 0 | 1 | 629342 | 630081 | 739 | 1 | 0 | 739 | 745.6563 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 0 | 1906.9492 | 0 | 0 | 0 | 0
460 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 87980510 | 89026265 | 1045755 | 1 | 0 | 1045755 | 1055174.2976 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1526974.093 | 1886658.0381 | 1858256.0346 | 2288167.324 | 2330507.8061 | 2062161.6863 | 2160918.3029
461 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 8383244 | 8967300 | 584056 | 1 | 0 | 584056 | 589316.6942 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 788052.4828 | 2056165.5278 | 2227970.4742 | 2396456.6421 | 1846222.5257 | 2324395.3174 | 2181617.4346
462 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
463 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26317.7 | 26433.6 | 115.9 | 3333.33 | 0 | 386332.947 | 389812.7152 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 453765.7341 | 575970.5227 | 619531.2198 | 632620.8461 | 655652.5794 | 676925.663 | 643438.6457
464 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71326.8 | 71601.8 | 275 | 3333.33 | 0 | 916665.75 | 924922.3182 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1066926.0087 | 1423833.9987 | 1532206.4801 | 1409263.8848 | 1205565.6057 | 1637075.4163 | 1478674.7103
465 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79310 | 79491.8 | 181.8 | 3333.33 | 0 | 605999.394 | 611457.7362 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1026568.6676 | 1364158.3566 | 1534221.2158 | 1535115.0531 | 1547367.0274 | 1547019.5294 | 1459995.3095
466 | Road 25 | D207C | 11 | Export | 0 | 1 | 71667.3 | 71863.3 | 196 | 3333.3 | 0 | 653326.8 | 659211.4284 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 941775.8615 | 1290390.3315 | 1318296.8446 | 1268595.2792 | 1429491.6026 | 1320696.1949 | 1108412.3257
467 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38312.4 | 38377.8 | 65.4 | 3333.33 | 0 | 217999.782 | 219963.344 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 311328.0598 | 402642.9556 | 432160.8021 | 453939.1071 | 448887.9755 | 428853.4986 | 403274.921
468 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 64469326 | 65735404 | 1266078 | 1 | 0 | 1266078 | 1277481.7853 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1297830.3074 | 1076949.6203 | 939422.8232 | 963337.8167 | 1202715.5447 | 1761856.4725 | 924073.8841
469 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | Estimated | 1530219.6 | 1544002.5547 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1652672.3734 | 2233224.3406 | 2307141.6064 | 2239410.379 | 2263478.6281 | 2215613.0537 | 2070071.1797
470 | Lab aid/local RMU | C302L | 11 | 0 | 3C65883 | 1 | 76794 | 80402 | 3608 | 300 | 0 | 1082400 | 1091796.2723 | Paribag | Green Road 33/11KV S/S | 2 | 1099246.4449 | 1368745.9116 | 1391721.2231 | 1482077.1317 | 1556841.7376 | 1536617.643 | 1422394.5672
471 | Green View | C302V | 11 | 0 | DHK000151 | 1 | 68593.9 | 68803.9 | 210 | 3333.33 | 0 | 699999.3 | 706075.9667 | Paribag | Green Road 33/11KV S/S | 2 | 952604.6387 | 1155247.0433 | 1226741.8962 | 1226475.691 | 1233531.7182 | 1202336.4681 | 1154869.3417
472 | Central Road | C302C | 11 | 0 | 65943 | 1 | 41167 | 44228 | 3061 | 300 | 0 | 918300 | 926271.7266 | Paribag | Green Road 33/11KV S/S | 2 | 1084585.7532 | 1542540.4225 | 1699791.5522 | 1668170.2521 | 1747192.6716 | 1761466.4931 | 1692090.5953
473 | New Market | D802N | 11 | 0 | DHK000194 | 1 | 48019.6 | 48318.5 | 298.9 | 3333.33 | 0 | 996332.337 | 1004981.4593 | Jigatola | Green Road 33/11KV S/S | 2 | 1091745.3233 | 1265157.8423 | 1241755.0551 | 1233547.6266 | 1104020.9274 | 1190965.2748 | 1011316.673
474 | DPH Feeder | 0 | 11 | 0 | HA-021100459 | 1 | 42140.3 | 42220.2 | 79.9 | 1 | 20 | 243265.68 | 245377.4599 | Paribag | Green Road 33/11KV S/S | 2 | 299600.3974 | 308510.2151 | 353437.7385 | 245765.8495 | 244229.1636 | 236205.0715 | 247670.0176
475 | Dhanmondi Rd 4(md Banglo | D802F | 11 | 0 | 6604464 | 1 | 4589.51 | 4602.53 | 13.02 | 60000 | 0 | 781200 | 787981.5668 | Jigatola | Green Road 33/11KV S/S | 2 | 976157.721 | 1290523.1633 | 1536748.4833 | 1456011.9715 | 1566178.5714 | 1573640.9477 | 1319464.1465
476 | Green Road East | C302X | 11 | 0 | HA-021101050 | 1 | 777480 | 1597306 | 819826 | 1 | 0 | 819826 | 826942.8777 | Paribag | Green Road 33/11KV S/S | 2 | 1043123.4845 | 1394173.8849 | 1544603.3759 | 1523648.0314 | 1576340.6608 | 1533242.4019 | 1471624.0188
477 | North Road | C302Z | 11 | 0 | HA-021100884 | 1 | 86548201 | 87580680 | 1032479 | 1 | 0 | 1032479 | 1041441.9101 | Paribag | Green Road 33/11KV S/S | 2 | 1315225.9221 | 1610609.432 | 1705708.7444 | 1708178.2525 | 1755468.3191 | 1721328.8161 | 1634915.8518
478 | Green road SS | C302W | 11 | 0 | DHK00135 | 1 | 23172245 | 23910038 | 737793 | 1 | 0 | 737793 | 744197.7524 | Paribag | Green Road 33/11KV S/S | 2 | 927434.3375 | 1235249.8127 | 1304162.391 | 1263700.5929 | 1250797.3933 | 1224610.5159 | 1315498.6273
479 | Plane Moszid | C302A | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 729797.04 | 736132.3797 | Paribag | Green Road 33/11KV S/S | 2 | 719040.9537 | 740424.5162 | 1001406.9258 | 1044504.8605 | 976916.6543 | 944820.2858 | 990680.0705
480 | Malancha | C302H | 11 | 0 | HA-021100953 | 1 | 39024399 | 39708690 | 684291 | 1 | 0 | 684291 | 690231.3036 | Paribag | Green Road 33/11KV S/S | 2 | 1262646.9803 | 1505893.42 | 1581374.6424 | 1473084.6514 | 1290839.3587 | 1378192.0129 | 1148505.9825
481 | AT -1 | 0 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5043.4048 | Paribag | Green Road 33/11KV S/S | 2 | 5090.5179 | 5072.8112 | 5004.3913 | 5051.3876 | 5019.8031 | 5016.7079 | 5090.5253
482 | North Dhanmondi | C31002 | 11 | 0 | BD 014039 | 1 | 23783.66 | 24137.31 | 353.65 | 2000 | 0 | 707300 | 711975.1234 | Paribag | Green Road Dormatory 33/11 SS | 100 | 970901.1912 | 1220415.3715 | 539516.6063 | 454897.5939 | 484039.8994 | 504079.3978 | 452285.2955
483 | Lake circus | C31004 | 11 | 0 | BD 014047 | 1 | 39176.51 | 39691.93 | 515.42 | 2000 | 0 | 1030840 | 1037653.6636 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1359915.9406 | 1817014.2474 | 1989795.0818 | 1922931.395 | 2034236.8602 | 2046787.3073 | 1887308.9386
484 | Bashir Uddin | C31003 | 11 | 0 | BD 014037 | 1 | 15830.71 | 16042.42 | 211.71 | 2000 | 0 | 423420 | 426218.7286 | Paribag | Green Road Dormatory 33/11 SS | 100 | 519195.2113 | 699693.4639 | 775365.5929 | 750942.0597 | 792213.6477 | 798302.5936 | 740604.9957
485 | Raza Bazar | D5100R | 11 | 0 | BD 013939 | 1 | 23815.99 | 24260.81 | 444.82 | 2000 | 0 | 889640 | 895520.3575 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1203544.7399 | 1251949.7098 | 1335486.8536 | 1305339.0743 | 1333290.6732 | 1329360.3858 | 1277085.001
486 | Rasel Squar | D5100RS | 11 | 0 | BD 013970 | 1 | 35887.97 | 36460.54 | 572.57 | 2000 | 0 | 1145140 | 1152709.1657 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1357853.9899 | 1818453.1535 | 1979472.6721 | 1896362.0126 | 1946515.3317 | 1986224.7792 | 1860400.7233
487 | Bow Bazar | D5100O | 11 | 0 | BD 013967 | 1 | 26716.98 | 27345.66 | 628.68 | 2000 | 0 | 1257360 | 1265670.9193 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1309854.1577 | 1211822.467 | 1271865.4648 | 1228245.6279 | 1315379.6859 | 1361417.0663 | 1195690.6937
488 | BRB Hospital | D5100S | 11 | 0 | BD 014003 | 1 | 14382.67 | 14617.11 | 234.44 | 2000 | 0 | 468880 | 471979.2109 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 608037.5277 | 807753.2915 | 817558.9445 | 861081.3012 | 841735.8151 | 735319.9448 | 733624.2823
489 | Green Road North | C31008 | 11 | 0 | BD 013969 | 1 | 17616.03 | 17935.33 | 319.3 | 2000 | 0 | 638600 | 642821.029 | Paribag | Green Road Dormatory 33/11 SS | 100 | 876606.6014 | 1205661.5166 | 1207219.8681 | 1206463.1592 | 1244662.5143 | 1225136.5003 | 1163648.4072
490 | Water Bhaban | D5100PB | 11 | 0 | BD 014004 | 1 | 5723.95 | 5811.58 | 87.63 | 2000 | 0 | 175260 | 176418.4365 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 266368.3378 | 341567.9548 | 321038.9901 | 360889.0448 | 369844.7631 | 332111.9703 | 301428.8307
491 | Alamin Road | C31007 | 11 | 0 | BD 014006 | 1 | 19724.04 | 19878.23 | 154.19 | 2000 | 0 | 308380 | 310418.3353 | Paribag | Green Road Dormatory 33/11 SS | 100 | 564141.7704 | 583425.7911 | 637499.1681 | 607978.2671 | 645158.196 | 644406.723 | 578607.7993
492 | Katal Bagan | C3100K | 11 | 0 | 0 | 1 | 11681.91 | 12283.55 | 601.64 | 2000 | 0 | 1203280 | 1211233.4604 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1478597.0623 | 2049711.7232 | 2213293.3253 | 2170885.4799 | 2232426.2667 | 2461917.3517 | 1880307.9323
493 | Eastern Pantho chaya | C310010 | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0
494 | Kalabagan | 0 | 11 | 0 | BD 014005 | 1 | 6367.44 | 6453.74 | 86.3 | 2000 | 0 | 172600 | 173740.8544 | Paribag | Green Road Dormatory 33/11 SS | 100 | 284172.4888 | 308027.2544 | 333048.3305 | 321346.724 | 343995.7229 | 360201.2398 | 320179.3518
495 | Univer Hospital | C310012 | 11 | 0 | BD 013963 | 1 | 1392.56 | 1482.8 | 90.24 | 2000 | 0 | 180480 | 181672.9397 | Paribag | Green Road Dormatory 33/11 SS | 100 | 220053.7538 | 258516.7219 | 265852.2552 | 274362.5626 | 281740.4351 | 275219.2974 | 258266.1053
496 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 | 0 | BD 013971 | 1 | 10701.31 | 10803.19 | 101.88 | 2000 | 0 | 203760 | 205106.8163 | Paribag | Green Road Dormatory 33/11 SS | 100 | 341233.008 | 477291.2605 | 521121.028 | 519641.6074 | 508095.8262 | 507213.6524 | 520651.6433
497 | Matir Masjid | A229S | 11 | 0 | DHK00170 | 1 | 31256.8 | 32697.5 | 1440.7 | 888.8889 | 0 | 1280622.2222 | 1284398.1103 | Khilgaon | Taltola 33/11KV S/S | 29 | 1604310.6045 | 1914137.6974 | 2132185.0742 | 2085431.7227 | 2167154.5553 | 2177028.2382 | 2023352.6919
498 | Hajipara | A229P | 11 | 0 | DHK-00108 | 1 | 7020.3 | 7595.3 | 575 | 2222.2222 | 0 | 1277777.7778 | 1281545.2791 | Khilgaon | Taltola 33/11KV S/S | 29 | 1799894.6638 | 1077292.6606 | 2330316.32 | 2323985.9847 | 2257545.6108 | 2323390.6234 | 1505682.5673
499 | Nearest Feeder | A929N | 11 | 0 | DHK-00106 | 1 | 92041.4 | 92278.7 | 237.3 | 2222.222 | 0 | 527333.2806 | 528888.1119 | Bashabo | Taltola 33/11KV S/S | 29 | 952079.0172 | 736977.684 | 448845.991 | 661064.6612 | 0 | 0 | 102528.7436
500 | Reazbagh | A229C | 11 | 0 | DHK-00109 | 1 | 98929.8 | 99412.2 | 482.4 | 2222.222 | 0 | 1071999.8928 | 1075160.6623 | Khilgaon | Taltola 33/11KV S/S | 29 | 1369807.3375 | 1677297.9566 | 1831327.1429 | 1773544.5971 | 1831021.0001 | 1850181.9906 | 1693614.7124
501 | Chowdhury Para | A229F | 11 | 0 | DHK-00107 | 1 | 53518 | 53735.7 | 217.7 | 2222.222 | 0 | 483777.7294 | 485204.138 | Khilgaon | Taltola 33/11KV S/S | 29 | 558618.9372 | 561029.5515 | 662951.963 | 585903.1258 | 625509.6106 | 653692.0598 | 575139.5465
502 | Model Colleg | A229D | 11 | 0 | 9122392 | 1 | 2601.93 | 2615.34 | 13.41 | 40000 | 0 | 536400 | 537981.5643 | Khilgaon | Taltola 33/11KV S/S | 29 | 695285.1522 | 561252.3268 | 1334690.1699 | 1248930.587 | 1283320.9871 | 723685.6707 | 1038453.9207
503 | East Rampura | A229B | 11 | 0 | DHK-00181 | 1 | 70 | 290.4 | 220.4 | 2222.222 | 0 | 489777.7288 | 491221.8283 | Khilgaon | Taltola 33/11KV S/S | 29 | 1083981.397 | 632299.6811 | 1183684.3115 | 1041555.9945 | 1373711.9053 | 1177184.4648 | 1381135.5698
504 | Adarshabagh | A929A | 11 | 0 | DHK-00090 | 1 | 53089.4 | 53626.6 | 537.2 | 2222.222 | 0 | 1193777.6584 | 1197297.4871 | Bashabo | Taltola 33/11KV S/S | 29 | 1572716.7906 | 2035653.077 | 2182105.9426 | 2139761.9297 | 2323799.4344 | 2249760.2414 | 2012766.0076
505 | Khailgaon Govt Colony | A229K | 11 | 0 | DHK00167 | 1 | 77744.9 | 78176 | 431.1 | 2222.222 | 0 | 957999.9042 | 960824.5471 | Khilgaon | Taltola 33/11KV S/S | 29 | 1228467.3088 | 1508476.8371 | 1632974.0455 | 1590881.9934 | 1651220.4486 | 1644511.4325 | 1548206.2687
506 | TV Road | A214T | 11 | 0 | 6604434 | 1 | 5174.98 | 5190.73 | 15.75 | 40000 | 0 | 630000 | 631857.5419 | Khilgaon | Taltola 33/11KV S/S | 29 | 1115125.7501 | 339156.7632 | 1446513.4037 | 1300316.995 | 1457589.2313 | 1435653.3713 | 1278251.1059
507 | Post Office | 0 | 11 | 0 | 06604476 | 1 | 6654.54 | 6666.69 | 12.15 | 40000 | 0 | 486000 | 487432.9609 | Bashabo | Taltola 33/11KV S/S | 29 | 755551.2881 | 1009051.5047 | 850255.946 | 1067472.334 | 544086.3384 | 925315.57 | 631719.4629
508 | Navana | A929V | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509 | Shantipur | A929P | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 232625.2878
510 | AT-01 | 0 | 0.415 | 0 | 9187958 | 1 | 790.37 | 853.83 | 63.46 | 80 | 0 | 5076.8 | 5091.7688 | Bashabo | Taltola 33/11KV S/S | 29 | 215.1784 | 17609.6926 | 22368.6405 | 0 | 0 | 388.7134 | 5004.1149
511 | AT-02 | 0 | 0.415 | 0 | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 164.5672 | 981.0492 | 0 | 0 | 1243.317 | 0
512 | Sher-e-Banglanagar Local | 0 | 11 | 0 | DHK 66503 | 1.45 | 85742 | 86523 | 781 | 60 | 11 kv bus-1 R Phase PT missing | 67947 | 69188.3162 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 109846.5171 | 124871.9678 | 133378.1778 | 145611.0642 | 127632.9783 | 130259.0089 | 137740.1655
513 | Mirpur Road East | D550F | 11 | 0 | DHK 60961 | 1.45 | 854603 | 858191 | 3588 | 60 | 0 | 312156 | 317858.7434 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 395819.5598 | 504909.4833 | 511825.2027 | 595499.8531 | 565408.7832 | 579726.769 | 591320.8565
514 | Gonobhaban school | D550E | 11 | 0 | DHK 66492 | 1.45 | 536080 | 537174 | 1094 | 60 | 0 | 95178 | 96916.7963 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 122017.2321 | 162123.6893 | 177174.8965 | 204772.9102 | 187053.4171 | 201293.1928 | 178100.36
515 | Babor Road | D450B | 11 | 0 | DHK 66489 | 1.3 | 798679 | 804063 | 5384 | 60 | 0 | 419952 | 427624.0566 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 570860.7987 | 723610.3177 | 1641262.4555 | 827030.8546 | 821146.7988 | 2355047.2749 | 1531864.2685
516 | College Gate | D450K | 11 | 0 | DHK 66487 | 1.4 | 2718507 | 2732457 | 13950 | 60 | 0 | 1171800 | 1193207.4845 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 1044976.0411 | 1347445.4847 | 1954707.1976 | 2003387.1217 | 2118896.2632 | 2029429.4244 | 1693179.314
517 | Parade ground | 0 | 11 | 0 | DHK 66490 | 1.45 | 938469 | 938503 | 34 | 60 | 0 | 2958 | 3012.0394 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 3333.3805 | 6820.7377 | 4879.6894 | 117.618 | 1062.133 | 1780.3054
518 | Hospital RMU | D550H | 11 | 0 | DHK 66491 | 1.45 | 927197 | 930854 | 3657 | 60 | 0 | 318159 | 323971.4115 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 434269.7168 | 581861.3963 | 629901.6383 | 661895.205 | 606359.9098 | 560499.4711 | 544171.0965
519 | Shamoly Square | 0 | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520 | Gonobhaban RMU | D550D | 11 | 0 | DHK 60964 | 1 | 198714.3 | 200013.1 | 1298.8 | 60 | 0 | 77928 | 79351.658 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 75406.8335 | 93681.1141 | 88021.1633 | 97246.5492 | 98796.0682 | 102753.2911 | 81921.1363
521 | Krishi University | D550V | 11 | 0 | DHK 60963 | 1 | 386593 | 392263 | 5670 | 60 | 0 | 340200 | 346415.0761 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 461555.7137 | 534152.4164 | 582966.2552 | 608461.3549 | 589560.5067 | 563852.3796 | 574020.0379
522 | NEC | D550X | 11 | 0 | DHK 86073 | 1 | 51.31 | 53.71 | 2.4 | 60000 | 0 | 144000 | 146630.7201 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 204096.883 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 274760.4607 | 284784.5503
523 | Novo Theater/Army Musium (41%) | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 432.4 | 444.74 | 12.34 | 60000 | 0 | 303564 | 309109.7771 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 360791.2051 | 457676.9299 | 439900.9902 | 454264.1779 | 491118.4828 | 467152.1267 | 453385.8053
524 | Novo Theater/Army Musium (59%) | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 432.4 | 444.74 | 12.34 | 60000 | 0 | 436836 | 444816.5085 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 519187.344 | 658608.2649 | 633028.2541 | 653697.2316 | 706731.4752 | 672243.3043 | 652433.232
525 | Netor | 0 | 11 | 0 | DHK 60962 | 1 | 150829.4 | 155777.3 | 4947.9 | 60 | 0 | 296874 | 302297.5582 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 451889.8792 | 546388.7354 | 587213.3923 | 617847.27 | 628517.1836 | 620062.5542 | 596532.4766
526 | BICC | D550VV | 11 | 0 | 0 | 1 | 51.31 | 53.71 | 2.4 | 60000 | 0 | 144000 | 146630.7201 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 204096.883 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 193459.8492 | 69152.9813
527 | Auxiliary | 0 | 0.415 | 0 | 0 | 1 | 5439.49 | 5470.11 | 30.62 | 60 | 0 | 1837.2 | 1870.7636 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 2593.3022 | 3246.9365 | 3802.5432 | 2988.0849 | 4296.3279 | 3895.3081 | 5642.8833
528 | City Corporation | A997Y | 11 | 0 | 93 | 1 | 44783932 | 45377608 | 593676 | 1 | 0 | 593676 | 599738.4197 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 776082.8806 | 996604.0058 | 1085361.1698 | 1583920.0344 | 672002.1574 | 951549.8845 | 660250.7383
529 | Bot tola | B297L | 11 | 0 | 0 | 1 | 62504888 | 63949164 | 1444276 | 1 | 0 | 1444276 | 1459024.4609 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 1806337.3901 | 2300581.3394 | 2406944.4276 | 2386526.2912 | 2395209.9678 | 2298336.7826 | 2240795.0697
530 | Jhilpar | B997J | 11 | 0 | 145 | 1 | 38598064 | 39421184 | 823120 | 1 | 0 | 823120 | 831525.4247 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 819817.0349 | 964321.9183 | 1048862.0833 | 1018967.1456 | 1203846.2525 | 1011093.8025 | 1160185.3486
531 | Central Bashaboo | A997C | 11 | 0 | 128 | 1 | 43766652 | 44810732 | 1044080 | 1 | 0 | 1044080 | 1054741.7939 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1340049.7308 | 1729561.5012 | 1906586.5613 | 1065915.018 | 2018436.7723 | 1763582.1465 | 1733572.9987
532 | Kadamtala | B997L | 11 | 0 | 8 | 1.5 | 20429350 | 20678950 | 249600 | 1 | 0 | 374400 | 378223.2469 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 607566.4408 | 808410.7915 | 737461.0018 | 659233.1205 | 895857.2066 | 680353.9053 | 1958904.8441
533 | Ansar VDP | A297A | 11 | 0 | 119 | 1 | 21940426 | 22442506 | 502080 | 1 | 0 | 502080 | 507207.0721 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 97 | 657824.4358 | 1198004.0816 | 522827.1096 | 571466.9061 | 611327.4182 | 1128730.4864 | 727503.1317
534 | Mugda Hospital Express-01 | B997H | 11 | 0 | 0 | 1 | 7018583 | 7189702 | 171119 | 1 | 0 | 171119 | 172866.4097 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 206011.8286 | 296418.3041 | 309430.1308 | 314267.439 | 307500.5637 | 293639.1125 | 272764.3875
535 | Boro Masjid | B997Z | 11 | 0 | 7 | 1.22 | 52337832 | 52934072 | 596240 | 1 | 0 | 727412.8 | 734840.8949 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 1191583.9793 | 1366718.9494 | 1456683.3289 | 1401094.4155 | 1717015.7129 | 1405726.812 | 1342757.2732
536 | Anandodhara | B297B | 11 | 0 | 120 | 1 | 50564636 | 51256316 | 691680 | 1 | 0 | 691680 | 698743.2036 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 685213.6028 | 1028241.2626 | 986769.0262 | 991611.9155 | 1008287.8477 | 964251.0175 | 915566.0508
537 | Culvert | A997L | 11 | 0 | 117 | 1 | 45451008 | 46405368 | 954360 | 1 | 0 | 954360 | 964105.6034 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1368637.0118 | 1587860.9817 | 1735000.3001 | 1917088.0393 | 2175998.5274 | 1824104.3237 | 1912589.1389
538 | Mugda Hospital Express-02 | 0 | 11 | 0 | 97 | 1 | 4870948 | 4870948 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 25317.8849 | 0 | 0 | 0 | 0 | 0 | 0
539 | Jhor Pukur | A997J | 11 | 0 | 98 | 1 | 29587808 | 29972006 | 384198 | 1 | 0 | 384198 | 388121.3008 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 230851.2653 | 807820.7106 | 1233989.5056 | 952311.2849 | 1695311.8425 | 1643349.6255 | 1429146.8866
540 | T&T | B997T | 11 | 0 | 99 | 1 | 25731818 | 26086056 | 354238 | 1 | 0 | 354238 | 357855.3593 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 590205.7479 | 628322.5712 | 593432.5647 | 596600.2068 | 721459.9725 | 567104.166 | 852556.8368
541 | Haider Ali | B297H | 11 | 0 | 9 | 1 | 76603816 | 78155048 | 1551232 | 1 | 0 | 1551232 | 1567072.6596 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 1855860.7678 | 2415267.9161 | 2486025.7818 | 2500945.5412 | 2687168.9248 | 2028073.3969 | 1439434.5953
542 | 11kv Tilpapara | A929T | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 1216328.4 | 1228749.1366 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1642601.2461 | 2219790.0622 | 2267480.2014 | 2153708.0482 | 2169910.6664 | 2181802.1625 | 2151612.2434
543 | AT-01 | 0 | 11 | 0 | 0 | 1 | 3262 | 3294.68 | 32.68 | 1 | 0 | 32.68 | 33.0137 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 54.7524 | 80.2692 | 86.077 | 79.9328 | 89.8242 | 94.3756 | 0
544 | AT-02 | 0 | 11 | 0 | 0 | 1 | 17.34 | 17.34 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0 | 0 | 0.34315 | 0 | 8.4563
545 | Shantinagar s/s-1 | 0 | 11 | 0 | DHK60932 | 1 | 430321 | 457519 | 27198 | 60 | 0 | 1631880 | 1639830.5714 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1995495.3946 | 1888358.4836 | 1327460.0638 | 1164408 | 2916346.3506 | 2755360.6206 | 2616486.0095
546 | Gulbagh | D606G | 11 | 0 | DHK60934 | 1 | 189715 | 200689 | 10974 | 60 | 0 | 658440 | 661647.9407 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 827221.5772 | 1048994.4227 | 1110222.7304 | 1081462.2 | 329175.3109 | 325114.8574 | 314880.9114
547 | Rampura BTV | A206H | 11 | 0 | DHK60933 | 1 | 14076 | 14081 | 5 | 60 | 0 | 300 | 301.4616 | Khilgaon | Khillgaon 33/11KV S/S | 6 | 180.4191 | 0 | 0 | 0 | 0 | 1220.4011 | 241.3343
548 | West Shantibag | D606W | 11 | 0 | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 547347.78 | 550014.4758 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 707899.6007 | 1098102.3361 | 1003916.3939 | 885668.7 | 934072.7507 | 932020.3326 | 912726.2746
549 | East Malibagh | D606E | 11 | 0 | DHK60929 | 1 | 665295 | 678393 | 13098 | 60 | 0 | 785880 | 789708.8324 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 996093.8555 | 1225702.646 | 1396586.5654 | 1214224.2 | 1558104.7013 | 1377100.6198 | 1289630.0978
550 | Police Line | D606S | 11 | 0 | DHK60930 | 1 | 601907 | 606946 | 5039 | 60 | 0 | 302340 | 303813.0101 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 464398.7655 | 567380.2526 | 593599.4922 | 600534.9 | 624772.6414 | 596226.9654 | 576125.2774
551 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 | 0 | DHK61017 | 1 | 201786 | 203304 | 1518 | 60 | 0 | 91080 | 91523.7447 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 111138.1661 | 133734.902 | 145615.9492 | 150301.2 | 152458.8445 | 149621.1769 | 146188.2445
552 | Benjir Bagan | D662R | 11 | 0 | DHK60985 | 1 | 175954 | 177912 | 1958 | 60 | 0 | 117480 | 118052.3663 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 135073.7668 | 193500.3195 | 197704.2286 | 195610.8 | 195480.6318 | 194653.9781 | 180699.0476
553 | AT-1 & AT-2 | 0 | 0.415 | 0 | ELIB 7374 | 1 | 2427 | 2504.15 | 77.15 | 60 | 0 | 4629 | 4651.5526 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 5701.2436 | 7360.8364 | 7097.6366 | 6669.159 | 7349.5039 | 14431.2432 | 0
554 | Spare | 0 | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0
555 | Monipuripara west | D572W | 11 | 0 | BD013947 | 1 | 33710.12 | 34318.15 | 608.03 | 1000 | 0 | 608030 | 612114.5091 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 935544.6228 | 814448.4485 | 843758.793 | 830035.6978 | 847623.509 | 861249.4503 | 873090.4062
556 | Biggan College | C672BC | 11 | 0 | BD013949 | 1 | 21787.07 | 22412.2 | 625.13 | 1000 | 0 | 625130 | 629329.3802 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 983877.3078 | 910214.7983 | 898340.4903 | 876599.5577 | 835521.2072 | 819870.1443 | 853994.1863
557 | Green Road South | D572G | 11 | 0 | BD013948 | 1 | 32252.24 | 32736.24 | 484 | 1000 | 0 | 484000 | 487251.3238 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 613343.481 | 1046963.2451 | 997691.2194 | 972408.44 | 975210.3173 | 1037302.1428 | 986346.7996
558 | BARC Building O/H | D572B | 11 | 0 | BD014010 | 1 | 14613.61 | 14617.09 | 3.48 | 1000 | 0 | 3480 | 3503.3773 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 39283.5032 | 553036.0194 | 605164.5353 | 601022.2433 | 634425.9824 | 629218.3029 | 632910.7169
559 | Indira Road (Green Road North) | D572NN | 11 | 0 | BD014036 | 1 | 63504.96 | 63986.61 | 481.65 | 1000 | 0 | 481650 | 484885.5374 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 964099.8184 | 1738404.7784 | 1930586.7401 | 1889476.4806 | 1966221.9789 | 1919532.2257 | 1871294.3358
560 | Chundrima Uddan | D572C | 11 | 0 | BD014035 | 1 | 32488.76 | 32997.64 | 508.88 | 1000 | 0 | 508880 | 512298.4579 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 477595.7009 | 964413.0153 | 995724.673 | 1002061.8966 | 1070591.3324 | 1032887.2799 | 1015615.1889
561 | khamar bari RMU-1 Feeder | 0 | 11 | 0 | BD013940 | 1 | 1367.45 | 1648.58 | 281.13 | 1000 | 0 | 281130 | 283018.522 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 321406.8247 | 250904.1991 | 255319.9358 | 263025.0554 | 137015.3458 | 147255.7457 | 0
562 | Farmgate foot over bridge RMU | 0 | 11 | 0 | BD013946 | 1 | 239.33 | 457.31 | 217.98 | 1000 | 0 | 217980 | 219444.3049 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 176700.3547 | 0 | 0 | 0 | 0 | 0 | 0
563 | kawran Bazar North | C672K | 11 | 0 | BD013964 | 1 | 40517.44 | 40643.13 | 125.69 | 1000 | 0 | 125690 | 126534.3365 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 61252.9055 | 77104.1375 | 81762.1785 | 77492.626 | 79448.9981 | 30221.7434 | 0
564 | NAM Bhanan RMU | D572NM | 11 | 0 | BD013950 | 1 | 18967.08 | 19600.71 | 633.63 | 1000 | 0 | 633630 | 637886.4799 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 770397.0568 | 959936.9135 | 1011015.5749 | 965308.8823 | 1005888.2452 | 1030950.7605 | 1013545.3917
565 | Novo Theater | 0 | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0
566 | Monipuripara Nearest | C172I | 11 | 0 | BD013962 | 1 | 40098.87 | 40333.1 | 234.23 | 1000 | 0 | 234230 | 235803.4661 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 446918.9749 | 732201.3407 | 808641.8922 | 823257.478 | 844317.6909 | 794156.578 | 733061.8614
567 | Holy Cross | C172HC | 11 | 0 | BD013965 | 1 | 40933.65 | 41628.74 | 695.09 | 1000 | 0 | 695090 | 699759.3443 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 1032893.7086 | 1312589.0703 | 1258529.5254 | 1242673.6384 | 1267377.9768 | 1286005.418 | 1126874.592
568 | Honda Goli | C172HG | 11 | 0 | BD014011 | 1 | 17161.03 | 17805.97 | 644.94 | 1000 | 0 | 644940 | 649272.4561 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 812717.0632 | 996766.2388 | 1069470.1647 | 1059189.7376 | 1074102.0051 | 1068926.6085 | 953126.0337
569 | Navy Quarter | C172NQ | 11 | 0 | BD013941 | 1 | 5981.54 | 6097.25 | 115.71 | 1000 | 0 | 115710 | 116487.2948 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 259359.6022 | 175972.436 | 196544.2773 | 221522.2664 | 200143.5254 | 202962.2853 | 175339.91
570 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 2170.58 | 2170.58 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0
571 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 641.32 | 688.9 | 47.58 | 1 | 0 | 47.58 | 47.8996 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 56.1451 | 0 | 0 | 0 | 0 | 0 | 0
572 | Doctor Goli | D1113D | 11 | 0 | BD013944 | 1 | 11220.97 | 11738.94 | 517.97 | 1000 | 0 | 517970 | 521759.6267 | Moghbazar | Ispahani 33/11 KV SS | 113 | 680371.3877 | 917384.4784 | 958125.7556 | 963950.8063 | 948233.0953 | 958270.3835 | 898591.0283
573 | Ispahani | D1113S | 11 | 0 | BD013947 | 1 | 12560.14 | 13161.92 | 601.78 | 1000 | 0 | 601780 | 606182.8062 | Moghbazar | Ispahani 33/11 KV SS | 113 | 787241.7632 | 1000362.3505 | 1092016.0616 | 1087721.0462 | 1055882.4039 | 1058199.8531 | 999582.0108
574 | BTCL | C6113BT | 11 | 0 | BD013949 | 1 | 6628.46 | 7159.42 | 530.96 | 1000 | 0 | 530960 | 534844.6655 | Kakrail | Ispahani 33/11 KV SS | 113 | 534614.2847 | 552136.017 | 523407.6855 | 549951.6967 | 529591.2713 | 523726.617 | 532492.3633
575 | Vikarunnesa | C6113VQ | 11 | 0 | BD013948 | 1 | 9308.85 | 9895.52 | 586.67 | 1000 | 0 | 586670 | 590962.2568 | Kakrail | Ispahani 33/11 KV SS | 113 | 754158.2718 | 1059198.2594 | 1138092.7736 | 1152044.6426 | 1148347.0254 | 1136233.5895 | 1092064.7445
576 | OASIS | 0 | 11 | 0 | 0 | 1 | 424 | 546.82 | 122.82 | 1000 | 0 | 122820 | 123718.5886 | Kakrail | Ispahani 33/11 KV SS | 113 | 114056.2956 | 109560.3611 | 90109.3741 | 109400.2883 | 4342.8205 | 0 | 0
577 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
579 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
580 | Wireless | D1113W | 11 | 0 | 0 | 1 | 10751.41 | 11429.01 | 677.6 | 1000 | 0 | 677600 | 682557.5285 | Moghbazar | Ispahani 33/11 KV SS | 113 | 776089.4575 | 1063107.1511 | 1088068.9306 | 1084178.7327 | 1047125.901 | 1048087.1638 | 896344.5253
581 | Kazir Goli | C6113KG | 11 | 0 | 0 | 1 | 10477.16 | 11127.02 | 649.86 | 1000 | 0 | 649860 | 654614.5742 | Kakrail | Ispahani 33/11 KV SS | 113 | 954304.3117 | 1072332.5406 | 1195416.795 | 1197081.1949 | 1203659.779 | 1263311.3532 | 1182067.1763
582 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
583 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
584 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
585 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
586 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
587 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
589 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0
590 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1 | 221836.7 | 223150.6 | 1313.9 | 1000 | 0 | 1313900 | 1328840.997 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1907566.3908 | 2264304.2356 | 2396448.119 | 2486440.3485 | 2725888.0748 | 2549641.8301 | 2438789.3271
591 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1 | 17327.3 | 17397.1 | 69.8 | 1000 | 0 | 69800 | 70593.7298 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 97801.2231 | 114438.0991 | 122268.7906 | 127832.1205 | 148265.7961 | 145583.9006 | 138711.8093
592 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1 | 113678.5 | 114558.2 | 879.7 | 1000 | 0 | 879700 | 889703.4972 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1253935.5917 | 1366513.6955 | 1396305.5531 | 1491140.0618 | 1611243.3589 | 1535819.0344 | 1523513.0022
593 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1 | 179110.6 | 180686.4 | 1575.8 | 1000 | 0 | 1575800 | 1593719.1894 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2152733.2578 | 2379446.8789 | 2449713.7307 | 2507460.7365 | 2663481.8388 | 2529191.2405 | 2405949.7847
594 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1 | 7300.2 | 7399.4 | 99.2 | 1000 | 0 | 99200 | 100328.0515 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 99239.4764 | 85853.7366 | 56292.0669 | 68291.1171 | 54248.5581 | 41407.382 | 36566.7297
595 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 79934 | 80921.6 | 987.6 | 1000 | 0 | 987600 | 998830.4807 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1251179.7778 | 1359166.3065 | 1319938 | 1387647.3379 | 1431264.5899 | 1311672.4727 | 1337959.5143
596 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
597 | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 11 | T2 | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
598 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 155175.3 | 156626.1 | 1450.8 | 1000 | 0 | 1450800 | 1467297.7535 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1794799.2873 | 2274671.0995 | 2350345.1179 | 2375002.1192 | 2446793.5192 | 2328937.4468 | 2238024.8856
599 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 111.26 | 117.1198 | 5.8598 | 40000 | 0 | 234392 | 237057.3856 | Matuail | Siddhirganj 33/11KV S/S | 28 | 379449.435 | 283444.1488 | 297629.6761 | 330706.0205 | 314747.6869 | 291293.3394 | 424399.7103
600 | 11 kV Madrasha Road Feeder (F-11) | 0 | 11 | T2 | XA575919 | 1 | 2.5378 | 6.4972 | 3.9594 | 40000 | 0 | 158376 | 160176.9706 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 16870.9 | 17353.1 | 482.2 | 1000 | 0 | 482200 | 487683.3311 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 567556.8719 | 709475.9549 | 663499.8644 | 692465.8927 | 722974.2051 | 681450.0937 | 758130.0486
602 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129895.9 | 129896 | 0.1 | 1000 | 0 | 100 | 101.1371 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 156958.2 | 158569.5 | 1611.3 | 1000 | 0 | 1611300 | 1629622.8772 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2174578.6154 | 2726585.8445 | 2843859.0812 | 2866014.2453 | 2915044.2314 | 2806489.0873 | 2820775.6603
604 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 | 0 | HA021101013-02 | 1 | 57648360 | 59997998 | 2349638 | 1 | 0 | 2349638 | 2366952.3646 | Matuail | Demra 33/11KV S/S | 16 | 2709931.5892 | 3182659.205 | 3242375.7883 | 2482601.3667 | 2346002.1943 | 2312393.5546 | 2206583.7096
605 | 11 kV DND (WASA) Feeder. | A816B | 11 | 0 | HA021100992-02 | 1 | 6452560 | 6457730 | 5170 | 1 | 0 | 5170 | 5208.0975 | Siddirgonj | Demra 33/11KV S/S | 16 | 4780.8214 | 190285.6191 | 296942.4232 | 349346.3885 | 251256.153 | 80170.7162 | 6927.7253
606 | 11 kV Local Feeder | A816D | 11 | 0 | HA021100794-02 | 1 | 14233810 | 14945420 | 711610 | 1 | 0 | 711610 | 716853.8184 | Siddirgonj | Demra 33/11KV S/S | 16 | 898962.87 | 1098339.8454 | 1209825.1625 | 1190157.3614 | 1182388.6301 | 2088621.9879 | 1417684.9395
607 | 11 kV Mouchak Feeder | A816A | 11 | 0 | DHK60888 | 1 | 1047240.6 | 1077570.4 | 30329.8 | 60 | 0 | 1819788 | 1833197.9265 | Siddirgonj | Demra 33/11KV S/S | 16 | 2048559.8995 | 2345108.3326 | 2403503.8665 | 2439051.751 | 2339275.7144 | 2308639.9015 | 2074135.4747
608 | 11 kV Overhead-1 Feeder | A816C | 11 | 0 | HA021100829-02 | 1 | 79937310 | 80343450 | 406140 | 1 | 0 | 406140 | 409132.8253 | Siddirgonj | Demra 33/11KV S/S | 16 | 374998.6846 | 432331.1497 | 507759.6491 | 490206.9454 | 1190489.8427 | 1095153.438 | 1095304.9401
609 | 11 kV Provati Steel Feeder | A816Z | 11 | 0 | DHK60874 | 1 | 609350.3 | 615326.2 | 5975.9 | 60 | 0 | 358554 | 361196.1665 | Siddirgonj | Demra 33/11KV S/S | 16 | 473734.4777 | 572313.5546 | 603535.6264 | 2095360.2501 | 124835.9443 | 0 | 0
610 | 11 kV Islambagh Feeder. | E116I | 11 | 0 | DHKA2190 | 1 | 1212.637 | 1240.0398 | 27.4028 | 60000 | 0 | 1644168 | 1656283.7916 | Matuail | Demra 33/11KV S/S | 16 | 1979061.5163 | 2382248.0982 | 2479849.2574 | 3031414.6894 | 2979112.0563 | 3002442.9965 | 2983539.0327
611 | 11 kV Taj Jute Feeder. | A816E | 11 | 0 | DHK61062 | 1 | 702990.4 | 722690.8 | 19700.4 | 60 | 0 | 1182024 | 1190734.2756 | Siddirgonj | Demra 33/11KV S/S | 16 | 1388752.4047 | 1608771.849 | 1850699.8521 | 525126.6242 | 1404410.5059 | 1676660.8446 | 1675376.4941
612 | 11 kV Al-Aksa Steel Feeder | A816S | 11 | 0 | DHK61061 | 1 | 877240.8 | 906680.6 | 29439.8 | 60 | 0 | 1766388 | 1779404.4246 | Siddirgonj | Demra 33/11KV S/S | 16 | 1746616.1362 | 1742517.141 | 1948104.7891 | 1679729.0047 | 1595509.5853 | 1474597.4818 | 1597579.1906
613 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 | 0 | DHKA2189 | 1 | 1151.187 | 1180.884 | 29.697 | 60000 | 0 | 1781820 | 1794950.1423 | Siddirgonj | Demra 33/11KV S/S | 16 | 2085198.1573 | 2525197.0695 | 2620588.9584 | 2664152.1809 | 2514049.716 | 2467512.3805 | 2370283.5934
614 | 11 kV Over Head Feeder-2. | E116V | 11 | 0 | HA021100488-02 | 1 | 35111950 | 36458480 | 1346530 | 1 | 0 | 1346530 | 1356452.5121 | Demra | Demra 33/11KV S/S | 16 | 1697694.9376 | 2095936.8227 | 2186616.3464 | 2197276.8827 | 2204224.8423 | 2131027.6013 | 2071443.4949
615 | 11 kV Shimrail Express Feeder. | A8164 | 11 | 0 | HA021100511-02 | 1 | 8254917 | 8256130 | 1213 | 1 | 0 | 1213 | 1221.9385 | Siddirgonj | Demra 33/11KV S/S | 16 | 542.4548 | 30546.5041 | 1269.0967 | 53083.1379 | 75076.7556 | 29225.6688 | 0
616 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 | 0 | HA021100413-02 | 1 | 82521598 | 82686340 | 164742 | 1 | 0 | 164742 | 165955.9755 | Demra | Demra 33/11KV S/S | 16 | 367927.7214 | 330954.2369 | 688064.1207 | 409117.6527 | 331227.7744 | 650733.1002 | 409613.9007
617 | 11 kV Siddhirgonj Mazar Feeder | 0 | 11 | 0 | HA021100393-02 | 1 | 26893.78 | 27633.46 | 739.68 | 1000 | 0 | 739680 | 745130.6648 | Siddirgonj | Demra 33/11KV S/S | 16 | 826630.8876 | 1127913.2115 | 1241829.7858 | 1214207.0897 | 1262090.4156 | 281800.301 | 832832.3648
618 | 11 kV AST Beverage Feeder | A816J | 11 | 0 | 0 | 1 | 23358696 | 23586810 | 228114 | 1 | 0 | 228114 | 229794.9606 | Siddirgonj | Demra 33/11KV S/S | 16 | 294965.0476 | 533291.7199 | 269111.0012 | 890478.2395 | 1164572.2996 | 1051751.2525 | 1163750.6238
619 | 11 kV Karim Market Feeder | E216K | 11 | 0 | 0 | 1 | 64428.93 | 65722.21 | 1293.28 | 1000 | 0 | 1293280 | 1302810.1155 | Matuail | Demra 33/11KV S/S | 16 | 1746397.55 | 2153249.6409 | 2251573.1315 | 2292212.1727 | 2119617.9699 | 2072299.946 | 2089377.8867
620 | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 | 0 | 2007755114 | 1 | 5962.59 | 5999 | 36.41 | 60000 | 0 | 2184600 | 2226080.12 | Demra | Sarulia 33/11KV S/S | 83 | 2656170.9356 | 3219680.3589 | 3402160.7226 | 2567812.3685 | 2674737.7934 | 2648546.8605 | 3036942.6611
622 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 | 0 | 30799484 | 1 | 22.3065 | 22.573 | 0.2665 | 60000 | 0 | 15990 | 16293.6103 | Demra | Sarulia 33/11KV S/S | 83 | 14090.6259 | 14581.402 | 14754.6723 | 14656.6857 | 14157.8637 | 13577.9934 | 12817.0467
623 | 11 kV Konapara (=L13) **** | E183KL | 11 | 0 | DHKA2191 | 1 | 2242.8601 | 2270.8758 | 28.0157 | 60000 | 0 | 1680942 | 1712858.9074 | Demra | Sarulia 33/11KV S/S | 83 | 2092594.4251 | 2580974.9024 | 2723567.5839 | 3439291.4731 | 3588042.0557 | 3482255.5223 | 2467003.1131
624 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 | 0 | 575926 | 1 | 60597 | 62272 | 1675 | 1000 | 0 | 1675000 | 1706804.0836 | Matuail | Sarulia 33/11KV S/S | 83 | 2044950.3572 | 2502341.7238 | 2566996.3354 | 2566696.0166 | 2627544.9143 | 2556143.6589 | 2386518.0767
625 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 | 0 | 30799450 | 1 | 1829.83 | 1834.24 | 4.41 | 60000 | 0 | 264600 | 269624.0958 | Demra | Sarulia 33/11KV S/S | 83 | 277809.1547 | 324637.9555 | 325784.1394 | 326380.7042 | 261798.4288 | 295524.6849 | 302404.9427
626 | 11 kV Tengra Feeder (=L16) | E183T | 11 | 0 | 30799145 | 1 | 5648.31 | 5679.55 | 31.24 | 60000 | 0 | 1874400 | 1909990.1936 | Demra | Sarulia 33/11KV S/S | 83 | 2317704.7602 | 2700866.43 | 2803570.4254 | 2888103.8805 | 2785803.7935 | 2203397.2826 | 3315319.3041
627 | 11 kV Police Line Feeder (=L17) | E183PL | 11 | 0 | 30799480 | 1 | 3396.71 | 3410.21 | 13.5 | 60000 | 0 | 810000 | 825379.8852 | Demra | Sarulia 33/11KV S/S | 83 | 1025710.2197 | 1276100.2252 | 1292175.5957 | 1231843.5906 | 1213792.7153 | 1297576.8726 | 1183247.2468
628 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 | 0 | 30799119 | 1 | 1670.44 | 1675.8 | 5.36 | 60000 | 0 | 321600 | 327706.384 | Demra | Sarulia 33/11KV S/S | 83 | 385778.6515 | 493328.3324 | 441483.1795 | 534022.1596 | 561432.5279 | 558765.1604 | 495803.4526
629 | 11 kV Spare Feeder (=F9) | 0 | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 | 0 | HA021100493-02 | 1 | 91722476 | 93505305 | 1782829 | 1 | 0 | 1782829 | 1816680.4881 | Demra | Sarulia 33/11KV S/S | 83 | 2264027.3407 | 2874690.3342 | 3063617.2119 | 3062145.1731 | 3047117.0714 | 3001937.8862 | 2753359.8865
631 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 | 0 | HA021100518-02 | 1 | 50895377 | 50895377 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 26104.5324 | 0 | 0 | 1592.7597 | 158210.2162 | 30254.1689
632 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 | 0 | HA021100697-02 | 1 | 31095860 | 32428430 | 1332570 | 1 | 0 | 1332570 | 1357872.1896 | Demra | Sarulia 33/11KV S/S | 83 | 1792379.5779 | 2145386.6161 | 2228761.3555 | 2265661.5752 | 2324189.2905 | 2304863.862 | 2171918.011
633 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
634 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0
635 | 11 kV Khanpur Feeder | B723B | 11 | 0 | DHKC 9348 | 1 | 55005.6 | 71759.65 | 16754.05 | 60 | 0 | 1005243 | 1015879.0626 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1344397.4603 | 1671397.6523 | 1767813.7522 | 1753296.6737 | 1849730.4598 | 1858439.2031 | 1689432.0922
636 | 11 kV Mission Para Feeder. | B723T | 11 | 0 | DHKC 9347 | 1 | 33948.22 | 50154.35 | 16206.13 | 60 | 0 | 972367.8 | 982656.0237 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1274888.2401 | 1557478.0335 | 1662446.9196 | 1652830.7535 | 1736094.2229 | 1666330.9001 | 1591097.4109
637 | 11 kV Esha Kha Feeder | B723M | 11 | 0 | DHKC 9311 | 1 | 42944.3 | 55179.5 | 12235.2 | 60 | 0 | 734112 | 741879.3371 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 807699.1496 | 1039293.9368 | 1004043.7507 | 968513.5517 | 939733.5453 | 917602.1317 | 1040108.3114
638 | 11 kV New Hazigonj Feeder | B723F | 11 | 0 | DHKC 9314 | 1 | 302.18 | 324.58 | 22.4 | 60000 | 0 | 1344000 | 1358220.3111 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1630966.9503 | 2057845.6627 | 2170066.5597 | 2135314.0661 | 2193735.673 | 2054393.8757 | 2135156.6373
639 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640 | 11 kV Hospital RMU Feeder. | B723H | 11 | 0 | 6604412 | 1 | 8.79 | 9.36 | 0.57 | 60000 | 0 | 34200 | 34561.8561 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 46010.9459 | 61862.7343 | 64307.2562 | 63695.448 | 65004.0756 | 61352.3895 | 59949.0945
641 | 11 kV Old Hajiganj Feeder. | B723E | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 | 0 | 06604389 | 1 | 85919.8 | 98494.55 | 12574.75 | 60 | 0 | 754485 | 762467.8954 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 948106.9996 | 1250130.6264 | 1328944.0291 | 1304005.3624 | 1304824.3795 | 1324560.4284 | 1260578.6756
643 | 11 kV Spare Feeder. | 0 | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644 | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645 | 11 kV B. B. Road West Feeder. | A723A | 11 | 0 | 6604415 | 1 | 413.32 | 442.48 | 29.16 | 40000 | 0 | 1166400 | 1178741.1985 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1517554.0047 | 1864372.9936 | 1918297.585 | 1915716.4264 | 1976042.8964 | 1840166.7201 | 1800087.6245
646 | 11 kV Mondalpara Feeder. | 0 | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647 | 11 kV B. B. Road East Feeder. | B723C | 11 | 0 | 06604392 | 1 | 323.08 | 347.28 | 24.2 | 40000 | 0 | 968000 | 978242.0098 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1208392.7367 | 1428099.2005 | 1517085.0182 | 1504830.2349 | 1509066.5776 | 1463548.0912 | 1396793.7162
648 | 11 kV Bishaw Road Feeder. | B723A | 11 | 0 | 06604393 | 1 | 332.61 | 350.11 | 17.5 | 40000 | 0 | 700000 | 707406.412 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 953718.1152 | 1117572.534 | 1216580.0413 | 1210820.1352 | 1222724.6371 | 1779421.78 | 1969640.6189
649 | 11 kV Chasara Feeder. | A723B | 11 | 0 | 06604391 | 1 | 449.6 | 479.56 | 29.96 | 40000 | 0 | 1198400 | 1211079.7774 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1572444.256 | 1942004.6602 | 2118903.8684 | 2081122.3834 | 2195963.227 | 2115948.7484 | 2048765.3497
650 | 11 kV Pathan Tully Feeder. | B723G | 11 | 0 | 06604388 | 1 | 78.12 | 87.97 | 9.85 | 40000 | 0 | 394000 | 398168.7519 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 528318.6681 | 576981.1889 | 529827.0791 | 160552.9705 | 39690.9621 | 0 | 0
651 | 11 kV Spare Feeder. | 0 | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
652 | 11 kV Nayamati Feeder. | B722J | 11 | 0 | 6604289 | 1 | 294.9 | 317.91 | 23.01 | 40000 | 0 | 920400 | 930138.3737 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1139779.9227 | 1329442.2908 | 1269562.7492 | 1343468.4333 | 1193968.9401 | 1316545.3361 | 1343505.6323
653 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656 | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0.415 | 0 | 412109 | 1 | 9234.3 | 9273.7 | 39.4 | 10 | 0 | 394 | 398.1688 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 305.7306 | 270.9022 | 317.4918 | 324.5435 | 42.526 | 0 | 0
657 | 33/0.415 kV Auxiliary Transformer-2 | 0 | 0.415 | 0 | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 | 0 | 3000 | 3031.7418 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 3027.0359 | 3032.487 | 3033.3611 | 3033.1166 | 3037.5736 | 3037.247 | 3027.732
658 | 11 kV Link Road Feeder | B741N | 11 | 0 | HA021100475-02 | 1 | 99970.287 | 101790.348 | 1820.061 | 1000 | 0 | 1820061 | 1840204.9638 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 2900288.7042 | 3109326.5102 | 2934230.0248 | 2975929.581 | 2607402.2302 | 1951841.3049 | 1877540.2045
659 | 11 kV Lamapara Express Feeder | B723L | 11 | 0 | HA021100928-03 | 1 | 81154.775 | 82245.906 | 1091.131 | 1000 | 0 | 1091131 | 1103207.3553 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 980020.9332 | 1044271.2809 | 777935.2019 | 1101665.3091 | 726895.7131 | 1017580.9915 | 1063497.0225
660 | 11 kV Kutubpur Feeder*** | B741Q | 11 | 0 | DHK66616 | 1 | 18505.85 | 18653.41 | 147.56 | 8000 | 0 | 1180480 | 1193545.2469 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1740376.2153 | 1768072.7988 | 1341995.221 | 1569417.834 | 1641482.3695 | 1554956.8642 | 1703285.4205
661 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 | 0 | DHK66625 | 1 | 3598.24 | 3616.61 | 18.37 | 60000 | 0 | 1102200 | 1114398.8642 | Fatullah | Matuail 33/11KV S/S | 41 | 1066770.6323 | 1419365.2857 | 1418275.2675 | 1534196.2033 | 1364062.3916 | 1338941.0426 | 835792.1765
662 | 11 kV Tushardhara Feeder (F2) | E241T | 11 | 0 | DHK66623 | 1 | 3975.1 | 4010.76 | 35.66 | 60000 | 0 | 2139600 | 2163280.5387 | Matuail | Matuail 33/11KV S/S | 41 | 2634875.0823 | 2672602.3834 | 2999054.9265 | 2829014.2755 | 2689931.0362 | 2755784.1096 | 2760297.6743
663 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 | 0 | DHK66627 | 1 | 3345.82 | 3357.9 | 12.08 | 60000 | 0 | 724800 | 732821.8987 | Matuail | Matuail 33/11KV S/S | 41 | 826686.7655 | 937957.3247 | 903475.9079 | 1019170.5275 | 792368.687 | 795452.7012 | 696897.8308
664 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 | 0 | HA021101044-02 | 1 | 66770.571 | 66954.672 | 184.101 | 1000 | 0 | 184101 | 186138.5822 | Matuail | Matuail 33/11KV S/S | 41 | 243777.8524 | 299669.3822 | 351957.4279 | 332319.5113 | 349545.5347 | 361905.6203 | 323912.9361
665 | 11 kV Shibu Market Feeder (F7) | B841B | 11 | 0 | DHK66624 | 1 | 2396.07 | 2398.8 | 2.73 | 60000 | 0 | 163800 | 165612.896 | Fatullah | Matuail 33/11KV S/S | 41 | 311443.8071 | 425021.3863 | 388070.1886 | 515025.6758 | 398306.2183 | 387075.6832 | 615623.4101
666 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 | 0 | HA060300286-03 | 1 | 6365.598 | 7639.081 | 1273.483 | 1000 | 0 | 1273483 | 1287577.5801 | Fatullah | Matuail 33/11KV S/S | 41 | 1300740.5246 | 1507092.8931 | 1340202.4176 | 1497969.2549 | 1502329.9696 | 1201993.7471 | 1110650.3388
667 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 | 0 | DHK66626 | 1 | 4543.46 | 4574 | 30.54 | 60000 | 0 | 1832400 | 1852680.5287 | Matuail | Matuail 33/11KV S/S | 41 | 2054924.3814 | 2632586.1045 | 2681928.8192 | 2638599.8531 | 2625668.5413 | 2669361.5514 | 2690547.2387
668 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | 0 | DHK6622 | 1 | 4277.24 | 4295.85 | 18.61 | 60000 | 0 | 1116600 | 1128958.2396 | Matuail | Matuail 33/11KV S/S | 41 | 1266941.3122 | 1346002.1078 | 1350362.9845 | 1363125.4682 | 1274337.3987 | 1416234.4574 | 1374993.3702
669 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 | 0 | DHKA2187 | 1 | 131.7799 | 137.5179 | 5.738 | 60000 | 0 | 344280 | 348090.4019 | Shyampur | Matuail 33/11KV S/S | 41 | 342400.7167 | 335087.831 | 248953.0896 | 243349.6318 | 240620.6059 | 244740.1643 | 218634.2568
670 | 11 kV Bhuighor Bazar | 0 | 11 | 0 | HA021100861-02 | 1 | 3332.199 | 4204.39 | 872.191 | 1000 | 0 | 872191 | 881844.1841 | Matuail | Matuail 33/11KV S/S | 41 | 1074012.4568 | 1411612.637 | 1387743.4624 | 1286702.6096 | 1290448.3093 | 1462145.9342 | 1034107.8281
671 | 11 kV Tokkar Math Feeder | B8416 | 11 | 0 | HA021200298-02 | 1 | 83283.485 | 83870.096 | 586.611 | 1000 | 0 | 586611 | 593103.4586 | Fatullah | Matuail 33/11KV S/S | 41 | 658390.1923 | 791536.1434 | 789253.9157 | 797388.0996 | 771061.022 | 778486.6953 | 733095.2742
672 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 | 0 | XA575922 | 1 | 249.9 | 259.6 | 9.7 | 1000 | 0 | 9700 | 9807.3571 | Fatullah | Matuail 33/11KV S/S | 41 | 17235.2398 | 19603.9346 | 10611.2942 | 9873.3404 | 9194.7909 | 13287.9755 | 64493.8811
673 | 33/0.415 KV Transformer, AT-1 | 0 | 0.415 | 0 | 2001123043119 | 1 | 7626.4 | 7684.5 | 58.1 | 160 | 0 | 9296 | 9398.8857 | Shyampur | Matuail 33/11KV S/S | 41 | 7772.9924 | 11624.9311 | 12240.3805 | 12799.0731 | 12965.6656 | 12496.7831 | 11807.0303
674 | 33/0.415 KV Transformer, AT-2 | 0 | 0.415 | 0 | 2001123043157 | 1 | 4726.8 | 4727.8 | 1 | 160 | 0 | 160 | 161.7708 | Shyampur | Matuail 33/11KV S/S | 41 | 1854.5521 | 0 | 0 | 0 | 0 | 0 | 129.3921
675 | 11 kV Godnail (F16) | A8963 | 11 | 0 | 00000109 | 1 | 32205162 | 33556120 | 1350958 | 1 | 0 | 1350958 | 1350455.4719 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1608130.1776 | 1902311.4075 | 2038403.821 | 2022169.7421 | 1902174.2906 | 1848814.9706 | 1869406.9017
676 | 11 kV M. Circus (F15) | B796C | 11 | 0 | 00000123 | 1 | 114200200 | 115576320 | 1376120 | 1 | 0 | 1376120 | 1375608.1121 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1875844.4545 | 1681278.3417 | 1521029.259 | 1828274.6635 | 1936785.1498 | 1975646.3394 | 2135882.0516
677 | 11 kV Wapderpool (F14) | B723W | 11 | 0 | 00000190 | 1 | 59257536 | 60232292 | 974756 | 1 | 0 | 974756 | 974393.4111 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 927244.3035 | 798221.6352 | 482340.828 | 822312.035 | 474935.0147 | 619875.2088 | 595303.4365
678 | 11 kV Chowdhury Bari (F13) | A896C | 11 | 0 | 00000191 | 1 | 107236336 | 109195976 | 1959640 | 1 | 0 | 1959640 | 1958911.0549 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2117617.9441 | 2183088.6246 | 2226891.1005 | 2193767.4037 | 2204031.0267 | 2287431.9192 | 2194488.2982
679 | 11 kV Ailpara (F12) | B7966 | 1 | 0 | 00000192 | 1 | 61060412 | 62774568 | 1714156 | 1 | 0 | 1714156 | 1713518.3698 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2091231.2297 | 2449465.553 | 2507772.6658 | 2664936.682 | 2385423.2662 | 2312455.9158 | 2506620.5244
680 | 11 kV Spare (F11) | 0 | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | 11 kV Spare (F10) | 0 | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | 11 kV Spare (F9) | 0 | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
683 | 11 kV Spare (F8) | 0 | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
684 | 11 kV Zulfiqur Steel | A8962H | 11 | 0 | 00000197 | 1 | 19720952 | 20884910 | 1163958 | 1 | 0 | 1163958 | 1163525.0319 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1070830.7575 | 1205147.4911 | 881898.0967 | 1269192.9831 | 1109871.8066 | 1233882.0915 | 1248729.4855
685 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 | 0 | 00000198 | 1 | 4290309 | 4304189 | 13880 | 1 | 0 | 13880 | 13874.8369 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 49416.8148 | 38314.1839 | 81476.5739 | 45981.5802 | 80821.2927 | 12574.267 | 42071.0581
686 | 11 kV Lucky Bazar (F5) | B796Z | 11 | 0 | 00000199 | 1 | 93619848 | 94930648 | 1310800 | 1 | 0 | 1310800 | 1310312.4098 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1175901.2838 | 1409832.0895 | 1363293.8581 | 1360268.1394 | 1265880.4844 | 1332623.2308 | 1392661.9878
687 | 11 kV Enayetnagar (F4) | A896Y | 11 | 0 | 00000200 | 1 | 36816152 | 37943668 | 1127516 | 1 | 0 | 1127516 | 1127096.5876 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1294647.5791 | 1539178.9886 | 1637703.7047 | 1666199.7304 | 1606948.7378 | 1544300.7721 | 1576051.8888
688 | 11 kV Bhuiyapara (F3) | A896V | 11 | 0 | 00000201 | 1 | 70774584 | 71863984 | 1089400 | 1 | 0 | 1089400 | 1088994.766 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1494739.0596 | 1820491.9548 | 1638474.4387 | 1895985.9869 | 1703398.6781 | 2021560.4921 | 1949356.1666
689 | 11 kV Arambagh (F2) | B796D | 11 | 0 | 00000202 | 1 | 12144210 | 12975328 | 831118 | 1 | 0 | 831118 | 830808.8415 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 965266.6711 | 1110256.976 | 1096967.543 | 1072171.1368 | 1011302.9055 | 1033739.3311 | 1073358.7436
690 | 11 kV Spare (F1) | 0 | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | 11/0.415 kV Aux. Transformer-1 | 0 | 0.415 | 0 | 00000204 | 1 | 1782.91 | 1806.93 | 24.02 | 100 | 0 | 2402 | 2401.1065 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2999.8723 | 4062.7646 | 4590.7608 | 4148.0738 | 5028.3475 | 4509.4616 | 4713.1396
692 | 11/0.415 kV Aux. Transformer-2 | 0 | 0.415 | 0 | 00000205 | 1 | 61.17 | 61.17 | 0 | 100 | 0 | 0 | 0 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1.0135 | 44.6458 | 0 | 0 | 0.99927 | 0 | 0
693 | 11 kV Minan Steel Feeder | A717R | 11 | New | 0 | 1 | 78084808 | 78664998 | 580190 | 1 | 0 | 580190 | 588603.6575 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 632806.8774 | 639787.7036 | 668682.8226 | 690626.9008 | 493276.6302 | 608736.535 | 686221.5647
694 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 91204625 | 91785899 | 581274 | 1 | 0 | 581274 | 589703.3771 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 831073.3841 | 837776.7717 | 798148.0435 | 798255.2776 | 675313.5877 | 687996.4568 | 904286.638
695 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 228288.5 | 241520.1 | 13231.6 | 60 | 0 | 793896 | 805408.7269 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1363029.7869 | 1190995.536 | 1654746.3681 | 1713127.7082 | 1429973.3518 | 1348752.6633 | 1520277.0648
696 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 370704.6 | 381113.2 | 10408.6 | 60 | 0 | 624516 | 633572.4534 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 733183.1825 | 994384.377 | 1017275.0549 | 998917.0422 | 983661.4804 | 966418.4358 | 973413.7301
698 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 94344.4 | 115281.3 | 20936.9 | 60 | 0 | 1256214 | 1274431.057 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1605474.9303 | 1916663.5337 | 1932341.6728 | 1605143.4286 | 2269442.86 | 1903765.6601 | 1898489.4903
699 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 102086.1 | 110638.4 | 8552.3 | 60 | 0 | 513138 | 520579.2992 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 625630.6419 | 700600.4968 | 623925.9784 | 637276.1792 | 646164.6825 | 667510.2274 | 661387.5474
700 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 676359 | 688661.1 | 12302.1 | 60 | 0 | 738126 | 748829.9751 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 893996.3722 | 935867.4295 | 898188.9867 | 879720.3375 | 817413.76 | 827156.9088 | 863427.9271
701 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 576544.9 | 596465.2 | 19920.3 | 60 | 0 | 1195218 | 1212550.5201 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1055367.6461 | 1081150.4699 | 1065440.2479 | 1123770.5196 | 1043132.595 | 1256184.2479 | 1130265.9765
702 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 882166.7 | 902017.3 | 19850.6 | 60 | 0 | 1191036 | 1208307.8746 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 283482.5341 | 300394.2285 | 217235.7079 | 274279.1183 | 230613.5281 | 268951.939 | 461817.7457
703 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 3404.6005 | 458632.0662 | 1006566.474 | 739323.8488 | 888156.2557 | 505747.1466
704 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 3152340 | 3643474 | 491134 | 1 | 0 | 491134 | 498256.2069 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 624571.0906 | 739019.2541 | 764214.6584 | 798862.9891 | 731731.9387 | 686782.5544 | 645276.6941
705 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 26146252 | 26354730 | 208478 | 1 | 0 | 208478 | 211501.2553 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 266805.7231 | 329009.9458 | 336317.7733 | 326230.0217 | 318326.9039 | 335635.5116 | 326421.8579
706 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 16501720 | 16948242 | 446522 | 1 | 0 | 446522 | 452997.2635 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 377407.5066 | 371813.5071 | 231457.5089 | 350113.1813 | 373857.3757 | 329133.6781 | 311868.8913
707 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
708 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 123409.7429 | 535601.4665
709 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 18251948 | 18736168 | 484220 | 1 | 0 | 484220 | 491241.9432 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 609177.2667 | 739088.5512 | 985608.2317 | 2067941.9788 | 1957359.7515 | 2145386.8814 | 2599917.6327
710 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
711 | 0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 1166208 | 2168854.1 | 1002646.1 | 1 | 0 | 1002646.1 | 1017186.028 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 997122.6577 | 1798366.2205 | 1947566.1648 | 1839951.043 | 1845653.8856 | 1844325.072 | 1788794.6263
713 | 11 kV Spare Feeder | 0 | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
716 | 11 kV Outgoing Feeder-2 (=F2) | 0 | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
717 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 1032.15 | 1055.91 | 23.76 | 60000 | 0 | 1425600 | 1431717.6049 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1967161.5939 | 2374197.2935 | 2139879.5383 | 2225117.9731 | 1919103.2774 | 1925513.8961 | 2018573.5941
718 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 519.22 | 535.1 | 15.88 | 60000 | 0 | 952800 | 956888.7023 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1278564.8268 | 1599035.1072 | 1814088.8895 | 1616939.3533 | 1431521.3433 | 1476167.1668 | 1492878.3256
719 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 572.34 | 579.48 | 7.14 | 60000 | 0 | 428400 | 430238.3712 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 517800.713 | 643462.7923 | 673220.5289 | 698887.9434 | 713358.7902 | 702593.0118 | 691704.3007
720 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1292.66 | 1315.52 | 22.86 | 60000 | 0 | 1371600 | 1377485.8774 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1511304.5202 | 1737349.5392 | 1778023.504 | 1913418.8206 | 1823628.4898 | 1708359.7204 | 1811062.3039
721 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | 11 kV Outgoing Feeder-10 (=F8) | 0 | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
725 | 11 kV Outgoing Feeder-11 (=F9) | 0 | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
726 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 227.78 | 239.06 | 11.28 | 60000 | 0 | 676800 | 679704.3175 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 841952.3789 | 1083663.5063 | 1145075.9889 | 1196876.0424 | 1264590.5826 | 1201867.1554 | 1168078.0452
727 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 105.2 | 110.15 | 4.95 | 60000 | 0 | 297000 | 298274.501 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 420374.7949 | 572501.475 | 611308.2838 | 620963.1553 | 614881.6508 | 573262.9625 | 566596.0446
728 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1220.63 | 1249.92 | 29.29 | 60000 | 0 | 1757400 | 1764941.4414 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2561940.8101 | 2204010.4054 | 1471467.7275 | 1601110.8808 | 1579237.0524 | 1146525.925 | 1680540.7098
729 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1490.06 | 1520.31 | 30.25 | 60000 | 0 | 1815000 | 1822788.6174 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2278082.5795 | 2618352.3343 | 2670641.7946 | 2813206.6084 | 2526178.8135 | 2500581.4639 | 2536449.5967
730 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | 11 kV Katherpol Feeder | B8919 | 11 | 0 | 00000031 | 1 | 71074344 | 72541944 | 1467600 | 1 | 0 | 1467600 | 1480200.745 | Fatullah | Dapa 33/11 kV | 91 | 1780543.7815 | 2017920.9065 | 1907068.817 | 2019617.347 | 1872668.2415 | 1825325.1091 | 2095256.7912
732 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0
733 | 11 kV Union Parishad Feeder | B8918 | 11 | 0 | 00000032 | 1 | 71909144 | 73690624 | 1781480 | 1 | 0 | 1781480 | 1796775.704 | Fatullah | Dapa 33/11 kV | 91 | 2128228.6671 | 2252272.5782 | 1663620.755 | 1557194.9668 | 1351133.0591 | 1174339.0851 | 1364658.7564
734 | 11 kV Shiachar Feeder | B891G | 11 | 0 | 00000030 | 1 | 73433864 | 74275736 | 841872 | 1 | 0 | 841872 | 849100.2736 | Fatullah | Dapa 33/11 kV | 91 | 1635781.9984 | 2031118.288 | 2032383.0231 | 2001560.8541 | 1924678.9852 | 1907532.8668 | 1901950.2285
735 | 11 kV Sastapur Feeder | B8913 | 11 | 0 | 00000106 | 1 | 72296704 | 72643024 | 346320 | 1 | 0 | 346320 | 349293.4873 | Fatullah | Dapa 33/11 kV | 91 | 488573.0611 | 516338.7434 | 559825.9548 | 395679.6151 | 1143053.371 | 1344939.9892 | 1492863.3157
736 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0
737 | 11 kV Jalal Ahmed Express | B891JA | 11 | 0 | 00000172 | 1 | 5879505 | 5879505 | 0 | 1 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 91 | 247329.6416 | 398396.8352 | 281983.6134 | 872.8694 | 163.171 | 71453.7073 | 791901.0884
738 | 11 kV Hajibari Feeder | 0 | 11 | 0 | 00000105 | 1 | 164959 | 853557 | 688598 | 1 | 0 | 688598 | 694510.2702 | Fatullah | Dapa 33/11 kV | 91 | 168427.36 | 0 | 0 | 0 | 0 | 0 | 0
739 | 11 kV Railine Feeder | 0 | 11 | 0 | 0 | 1 | 195799 | 1103037 | 907238 | 1 | 0 | 907238 | 915027.503 | Fatullah | Dapa 33/11 kV | 91 | 200012.7891 | 0 | 0 | 0 | 0 | 0 | 0
740 | 11 kV Lalpur Feeder | B8911 | 11 | 0 | 00000044 | 1 | 86381512 | 87083784 | 702272 | 1 | 0 | 702272 | 708301.6746 | Fatullah | Dapa 33/11 kV | 91 | 2338751.8857 | 2709693.2174 | 2479807.3342 | 1402820.0857 | 1449235.5198 | 1159780.4978 | 373576.7292
741 | 11 kV Kotaler Bag Feeder | B8912 | 11 | 0 | 00000050 | 1 | 91574936 | 92944416 | 1369480 | 1 | 0 | 1369480 | 1381238.2912 | Fatullah | Dapa 33/11 kV | 91 | 2006422.5038 | 2309410.8982 | 2305548.0804 | 2521037.1496 | 1462297.3552 | 1401235.8745 | 1515181.1462
742 | 11 kV Idrakpur Feeder | B8915 | 11 | 0 | 00000021 | 1 | 80022008 | 80799760 | 777752 | 1 | 0 | 777752 | 784429.7423 | Fatullah | Dapa 33/11 kV | 91 | 983847.2999 | 1146390.3941 | 1054879.9219 | 1213883.5456 | 1042540.0593 | 1114166.2721 | 1068664.5804
743 | 11 kV Isdair Feeder | B8914 | 11 | 0 | 00000029 | 1 | 43086456 | 43612092 | 525636 | 1 | 0 | 525636 | 530149.0861 | Fatullah | Dapa 33/11 kV | 91 | 624149.3274 | 790469.7993 | 829018.6896 | 795100.6656 | 849835.155 | 794122.676 | 792940.801
744 | 11 kV Shah Fateullah Express | 0 | 11 | 0 | 0000051 | 1 | 4770108 | 6178065 | 1407957 | 1 | 0 | 1407957 | 1420045.653 | Fatullah | Dapa 33/11 kV | 91 | 1937861.0792 | 1875856.2789 | 1015342.7418 | 0 | 0 | 0 | 0
745 | 11 kV Boubazar Feeder | 0 | 11 | 0 | 00000151 | 1 | 23719 | 579438 | 555719 | 1 | 0 | 555719 | 560490.3774 | Fatullah | Dapa 33/11 kV | 91 | 24229.4565 | 0 | 0 | 0 | 0 | 0 | 0
746 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0 | 0.415 | 0 | DHKF 7522 | 1 | 3239 | 3273 | 34 | 100 | 0 | 3400 | 3429.1922 | Fatullah | Dapa 33/11 kV | 91 | 4801.1487 | 6039.9915 | 6235.0379 | 5653.8129 | 5914.9473 | 5529.8501 | 5198.5629
748 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0
749 | 11 kV Bholail Feeder (F-3) | E330V | 11 | 0 | DHK 9335 | 1 | 15853.9958 | 44011.8562 | 28157.8604 | 60 | 0 | 1689471.624 | 1692519.7695 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 2733762.095 | 2632122.2753 | 3204950.7718 | 3202295.2627 | 3113891.785 | 3046734.2178 | 2464743.5384
750 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 | 0 | DHK 9336 | 1 | 34520.8952 | 52704.3896 | 18183.4944 | 60 | 0 | 1091009.664 | 1092978.0641 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1031371.3237 | 1296469.7835 | 1414735.196 | 1450857.7553 | 1198137.3888 | 1083589.5043 | 1409860.9795
751 | 11 kV Baburail Feeder (F-5) | A730R | 11 | 0 | DHK 9322 | 1 | 11014.0086 | 31398.6709 | 20384.6623 | 60 | 0 | 1223079.738 | 1225286.419 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 1578860.4613 | 1983304.4857 | 2103409.2909 | 2067517.7824 | 2058052.5984 | 2038840.2789 | 1960329.6227
752 | 11 kV Goghchar Feeder (F-1) | E330G | 11 | 0 | DHK 9323 | 1 | 93927.0295 | 108385.2865 | 14458.257 | 60 | 0 | 867495.42 | 869060.5556 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1024995.3245 | 1237157.8572 | 1317359.8624 | 1330855.5581 | 1324242.6499 | 1303267.9767 | 1261095.5642
753 | 11 kV Norshinghopur (F-2) | E330N | 11 | 0 | DHK 9365 | 1 | 92611.445 | 116984.1799 | 24372.7349 | 60 | 0 | 1462364.094 | 1465002.492 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1580945.372 | 1560990.7311 | 1355613.7656 | 1460780.2783 | 1404336.8639 | 1352601.3966 | 1471201.0567
754 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 | 0 | DHK 9367 | 1 | 27485.0632 | 37817.1704 | 10332.1072 | 60 | 0 | 619926.432 | 621044.9036 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 738106.28 | 517148.8821 | 0 | 0 | 0 | 0 | 554462.5713
755 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 | 0 | H/A030701125-03 | 1 | 73961.68 | 74111.207 | 149.527 | 1000 | 0 | 149527 | 149796.7767 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 178278.8721 | 227804.4627 | 240354.077 | 235334.8005 | 246133.1449 | 234255.9876 | 224598.6372
756 | 11 kV Kashipur Feeder (F-7) | E317K | 11 | 0 | H/A030800169-03 | 1 | 41289.934 | 42354.858 | 1064.924 | 1000 | 0 | 1064924 | 1066845.3364 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1250959.2711 | 1588658.98 | 1710138.4368 | 1760370.7558 | 1741847.8978 | 1664580.229 | 1652181.4751
757 | 11 kV Spare Feeder (F-6) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0
758 | 11 kV Paikpara Feeder (F-8) | A730D | 11 | 0 | H/A030701098-03 | 1 | 82381 | 83078.66 | 697.66 | 1000 | 0 | 697660 | 698918.7185 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 844950.6763 | 1070234.6333 | 1102912.6399 | 1118443.5796 | 1135381.2606 | 1090515.7468 | 1082731.082
759 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 | 0 | H/A030800205-03 | 1 | 98073.528 | 98948.784 | 875.256 | 1000 | 0 | 875256 | 876835.1373 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 909298.0281 | 937852.0624 | 845475.6866 | 838157.9765 | 729788.4502 | 786055.2221 | 765048.1281
760 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 | 0 | H/A030701091-03 | 1 | 57053.47 | 57707.379 | 653.909 | 1000 | 0 | 653909 | 655088.7829 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 771648.9846 | 1009051.2889 | 1042925.7746 | 1035234.9191 | 1075488.4842 | 1015821.5301 | 958950.0681
761 | 11 kV River View | B793U | 11 | 0 | 00000061 | 1 | 9679440 | 10379476 | 700036 | 1 | 0 | 700036 | 704573.4596 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 834579.227 | 838291.0284 | 794103.9859 | 844731.2094 | 841728.9793 | 838140.6773 | 803073.4017
762 | 11 kV Railgate B.B. Road | B793F | 11 | 0 | 00000191 | 1 | 25321458 | 25747338 | 425880 | 1 | 0 | 425880 | 428640.4484 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 541179.2554 | 698256.3766 | 634632.2838 | 651403.112 | 672012.4136 | 662899.4007 | 611819.3181
763 | 11 kV DIT | A722D | 11 | 0 | 00000174 | 1 | 148263920 | 150230640 | 1966720 | 1 | 0 | 1966720 | 1979467.7908 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 2494646.9299 | 3067765.2362 | 3157724.5261 | 3006495.8053 | 3105959.8639 | 3165323.9759 | 2992837.0935
764 | 11 kV Dalpatti | B7227 | 11 | 0 | 00000182 | 1 | 6596464 | 7271502 | 675038 | 1 | 0 | 675038 | 679413.4287 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 717766.0913 | 789288.224 | 719006.8368 | 711194.3901 | 640949.3228 | 661646.5082 | 714092.6513
765 | 11 kV South Chasara | A793S | 11 | 0 | 00000043 | 1 | 104270584 | 105849784 | 1579200 | 1 | 0 | 1579200 | 1589435.9823 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 2086962.942 | 2534727.6524 | 2702179.486 | 2680027.0984 | 2791666.2107 | 2659640.365 | 2565218.7341
766 | 11 kV Spare | 0 | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
767 | 11 kV NCC Express | B7225 | 11 | 0 | 00000019 | 1 | 237799 | 253199 | 15400 | 1 | 0 | 15400 | 15499.819 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 24295.6359 | 23419.6471 | 28768.3897 | 31678.5827 | 33494.5516 | 30069.4219 | 22516.8296
768 | 11 kV Spare | 0 | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
769 | 11 kV Masuya Bazar | B7229 | 11 | 0 | 00000173 | 1 | 9690976 | 10873413 | 1182437 | 1 | 0 | 1182437 | 1190101.2631 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 1131312.8093 | 1152492.2619 | 1058401.5124 | 1053995.629 | 1019425.3124 | 1009868.8027 | 967617.4501
770 | 11 kV Nitaigonj | B722G | 11 | 0 | 00000189 | 1 | 61101972 | 61732128 | 630156 | 1 | 0 | 630156 | 634240.5147 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 721749.3286 | 797467.0545 | 710089.0378 | 797549.9114 | 692971.3447 | 773236.8002 | 671875.6098
771 | 11 kV Shahid Nagar | E323T | 11 | 0 | 00000020 | 1 | 62024488 | 62912208 | 887720 | 1 | 0 | 887720 | 893473.9806 | Sytalakhya | Mondalpara 33/11KV S/S | 22 | 1062004.8821 | 1271995.6228 | 1341667.6936 | 1338376.1519 | 1319788.4916 | 1324869.236 | 1256708.9709
772 | 11 kV Bangla Bazar | A793Z | 11 | 0 | 00000139 | 1 | 75510416 | 76543656 | 1033240 | 1 | 0 | 1033240 | 1039937.2052 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1307258.0634 | 1631386.9501 | 1686165.1422 | 1670015.7997 | 1659253.7348 | 1635218.8108 | 1605498.2865
773 | 11 kV Vogoban Gonj | B7228 | 11 | 0 | 00000181 | 1 | 4220269 | 4607869 | 387600 | 1 | 0 | 387600 | 390112.327 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 454174.5319 | 474606.7675 | 456596.7336 | 480180.888 | 455263.1874 | 451404.0608 | 442440.5963
774 | 11 kV Tanbazar | B722I | 11 | 0 | 00000138 | 1 | 52421992 | 53049952 | 627960 | 1 | 0 | 627960 | 632030.2808 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 804089.0085 | 976523.0891 | 1000661.8275 | 1022544.4626 | 983939.833 | 990185.2541 | 977004.8332
775 | 11 kV SS Road | A793O | 11 | 0 | 00000175 | 1 | 70578344 | 71549224 | 970880 | 1 | 0 | 970880 | 977173.0031 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1192851.3622 | 1337205.7052 | 1396187.0064 | 1386083.0342 | 1389631.5256 | 1367265.5042 | 1304240.0244
776 | 11 kV Spare | 0 | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
777 | 33/0.415 kV Auxiliary-1 | 0 | 0.415 | 0 | 0 | 1 | 2673.12 | 2701.84 | 28.72 | 100 | 0 | 2872 | 2890.6156 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 3239.0829 | 4162.6017 | 6314.1794 | 3653.8216 | 8763.4945 | 8081.1571 | 8402.5235
778 | 33/0.415 kV Auxiliary-2 | 0 | 0.415 | 0 | 0 | 1 | 3.98 | 4.17 | 0.19 | 100 | 0 | 19 | 19.1232 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0
779 | 11 kV Masdair Feeder (F-8) | A727M | 11 | 0 | XA575914 | 1 | 225307.3 | 227537.4 | 2230.1 | 1000 | 0 | 2230100 | 2222097.8958 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2875854.6768 | 3291294.4584 | 3221867.4125 | 3104675.7264 | 3190609.1379 | 3086175.0273 | 3077099.4263
780 | 11 kV Narayangonj (F-7) | A727N | 11 | 0 | XA575915 | 1 | 171294.6 | 172653 | 1358.4 | 1000 | 0 | 1358400 | 1353525.753 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1448790.766 | 1519105.835 | 1446695.3457 | 1509012.0982 | 1221622.7778 | 1186514.4598 | 1307443.1804
781 | 11 kV Nearest Feeder (F-6) | A727B | 11 | 0 | XA575927 | 1 | 109777.2 | 110754.8 | 977.6 | 1000 | 0 | 977600 | 974092.1497 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1208994.3676 | 1130497.3656 | 1036613.3317 | 1067352.4897 | 767732.4068 | 814473.5094 | 997748.2737
782 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 | 0 | XA575916 | 1 | 121288 | 122392.1 | 1104.1 | 1000 | 0 | 1104100 | 1100138.239 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1251647.0882 | 1407639.7693 | 1294481.9465 | 1274162.1574 | 1118663.9439 | 1197874.4889 | 1341268.5888
783 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 | 0 | XA575912 | 1 | 58701.7 | 59670.9 | 969.2 | 1000 | 0 | 969200 | 965722.2908 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1164739.667 | 905839.439 | 991802.3648 | 906095.6122 | 696086.8403 | 614760.142 | 701320.2188
784 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 | 0 | DHK66615 | 1 | 262.4459 | 277.9005 | 15.4546 | 60000 | 0 | 927273.06 | 923945.7941 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 979158.7412 | 1098396.235 | 953150.2952 | 1090118.5393 | 864699.4622 | 933339.9033 | 1045632.3523
785 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 | 0 | XA575920 | 1 | 235307.8 | 236532 | 1224.2 | 1000 | 0 | 1224200 | 1219807.293 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 27 | 774957.8804 | 1276885.4045 | 676995.0442 | 906804.2112 | 982770.4437 | 813154.9346 | 1189560.6195
786 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 | 0 | XA575929 | 1 | 24939.8 | 25997.9 | 1058.1 | 1000 | 0 | 1058100 | 1054303.2974 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1209394.8627 | 1314142.277 | 1121815.8354 | 1179007.44 | 1159908.2799 | 1225868.8461 | 1274022.8667
787 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 | 0 | HA021100913-02 | 1 | 46643.437 | 48995.357 | 2351.92 | 1000 | 0 | 2351920 | 2343480.778 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2210541.3216 | 2452393.5389 | 1730245.9891 | 1391497.0345 | 582908.1262 | 649651.6597 | 916096.371
788 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 | 0 | HA021100682-02 | 1 | 69020.842 | 71092.782 | 2071.94 | 1000 | 0 | 2071940 | 2064505.4097 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2336119.5415 | 2520803.045 | 2363695.2567 | 2414952.831 | 1958482.735 | 2197501.257 | 2366722.3025
789 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 | 0 | HA021100455-02 | 1 | 61478.231 | 63033.857 | 1555.626 | 1000 | 0 | 1555626 | 1550044.0614 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1810143.413 | 1837185.1157 | 1324011.9627 | 2155990.2798 | 1459919.7827 | 1675803.0813 | 1827353.8856
790 | 11/0.415 KV Transformer,AT-1 | 0 | 0.415 | Analog | 2001123043161 | 1 | 4048.1 | 4100.5 | 52.4 | 160 | 0 | 8384 | 8353.9163 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 8426.4154 | 10606.5342 | 9471.9695 | 9523.57 | 9809.4637 | 10077.9686 | 6902.8139
791 | 11/0.415 KV Transformer,AT-2 | 0 | 0.415 | Analog | 2001123043118 | 1 | 4122.3 | 4127.1 | 4.8 | 160 | 0 | 768 | 765.2442 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2274.8118 | 292.37 | 213.7771 | 583.0757 | 16.214 | 519.3156 | 421.2985
792 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
793 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 | 0 | 041808902749 | 1 | 484.37 | 496.62 | 12.25 | 60000 | 0 | 735000 | 738639.4179 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 945964.8168 | 1302048.296 | 1299547.0336 | 1326519.4669 | 1258154.7044 | 1256317.0074 | 1308593.1901
794 | 11 kV UltraTech Cement Feeder (=F3) | 0 | 11 | 0 | 041808902759 | 1 | 515.1 | 534.17 | 19.07 | 60000 | 0 | 1144200 | 1149865.6081 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1335585.1962 | 1070865.8478 | 1018127.8829 | 1172245.3124 | 1166152.8884 | 1226848.5855 | 1401162.4833
795 | 11 kV RMU Hygene Express -1 (=F4) | 0 | 11 | 0 | 041808902748 | 1 | 0.02 | 6.51 | 6.49 | 60000 | 0 | 389400 | 391328.1487 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
796 | 11 kV Outgoing Feeder-5 (=F5) | 0 | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | 11 kV Outgoing Feeder-6 (=F6) | 0 | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
798 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 | 0 | 041808902786 | 1 | 379.9 | 398.35 | 18.45 | 60000 | 0 | 1107000 | 1112481.409 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1382793.8004 | 1588331.224 | 1607255.8715 | 1649959.1034 | 1406910.8874 | 1384414.4332 | 1059738.0772
802 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 | 0 | 041808902789 | 1 | 230.47 | 238.53 | 8.06 | 60000 | 0 | 483600 | 485994.5884 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 878438.5854 | 830100.7076 | 664412.0926 | 761840.3225 | 831600.8302 | 763171.9877 | 845746.7241
803 | 11 kV Outgoing Feeder-12 (=F10) | 0 | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804 | 11 kV Outgoing Feeder-13 (=F11) | 0 | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805 | 11 kV Outgoing Feeder-14 (=F12) | 0 | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806 | 11 kV Outgoing Feeder-15 (=F13) | 0 | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
807 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | 33/0.415 kV Transformer AT-1 | 0 | 0.415 | 0 | 041811907976 | 1 | 1995.97 | 2047.93 | 51.96 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809 | 33/0.415 kV Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 73017725 | 73439809 | 422084 | 1 | 0 | 422084 | 422316.016 | Mugdapara | Amulia 33/11 kv | 102 | 938316.3983 | 618877.1744 | 747742.2401 | 669679.7315 | 704760.429 | 655997.4572 | 731782.37
811 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
812 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 19053674 | 19988191 | 934517 | 1 | 0 | 934517 | 935030.696 | Demra | Amulia 33/11 kv | 102 | 1013109.0793 | 1328671.185 | 1368274.6157 | 1317757.7287 | 1370677.2015 | 1292488.6152 | 1242034.7233
813 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 2915432 | 3438978 | 523546 | 1 | 0 | 523546 | 523833.7888 | Demra | Amulia 33/11 kv | 102 | 523224.3018 | 581908.8947 | 369688.6181 | 572405.5108 | 546070.575 | 498813.9667 | 550647.0061
814 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 73339160 | 75271966 | 1932806 | 1 | 0 | 1932806 | 1933868.447 | Demra | Amulia 33/11 kv | 102 | 2094431.1329 | 2508124.4895 | 2591251.8147 | 2450741.6785 | 2341533.0936 | 2143176.0462 | 2258006.7634
815 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 16625684 | 17115669 | 489985 | 1 | 0 | 489985 | 490254.3406 | Mugdapara | Amulia 33/11 kv | 102 | 575953.3679 | 671288.426 | 654683.7051 | 639938.2711 | 588274.3679 | 552448.5186 | 1045691.8176
816 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra | 0 | 1 | 52278896 | 52490923 | 212027 | 1 | 0 | 212027 | 212143.5494 | Demra | Amulia 33/11 kv | 102 | 120786.3374 | 168139.8027 | 155971.1495 | 189931.2691 | 165276.4 | 158821.9675 | 145542.9861
817 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 16211336 | 17272226 | 1060890 | 1 | 0 | 1060890 | 1061473.1622 | Demra | Amulia 33/11 kv | 102 | 1171776.4455 | 1342546.4505 | 1461872.9578 | 1326521.6668 | 1251754.1184 | 1263380.0786 | 1242709.7581
818 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
819 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
820 | 33/0.415 kV Transformer, AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0
821 | 11 kV Nearest Feeder | B2110N | 11 | 0 | HA021101060-02 | 1 | 81633988 | 82699513 | 1065525 | 1 | 0 | 1065525 | 1080819.1243 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1313766.3455 | 1615577.819 | 1668539.8072 | 1666551.6834 | 1691601.9901 | 1589546.8433 | 1558145.6337
822 | 11kV Spare | 0 | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
823 | 11 kV City Palli Feeder | B2110C | 11 | 0 | HA021100937-02 | 1 | 80522134 | 81055406 | 533272 | 1 | 0 | 533272 | 540926.3753 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 688739.9281 | 831311.9243 | 885994.3441 | 907412.698 | 936164.8797 | 876024.4652 | 849393.0553
824 | 11 kV R K Mission Road Feeder | B2110R | 11 | 0 | HA021101035-02 | 1 | 20022438 | 21016003 | 993565 | 1 | 0 | 993565 | 1007826.239 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1205722.8029 | 1505793.7255 | 1587170.4652 | 1556832.94 | 1647566.9154 | 1564049.4804 | 1502639.6704
825 | 11 kV Janapath Feeder | B2110J | 11 | 0 | HA021100864-02 | 1 | 35472819 | 36804184 | 1331365 | 1 | 0 | 1331365 | 1350474.8865 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1592664.201 | 2018970.5577 | 2145298.3795 | 2127410.4471 | 2194112.6593 | 2093083.5306 | 2005205.5254
826 | 11 kV Dhalpur Feeder | B2110D | 11 | 0 | HA021100851-02 | 1 | 89539002 | 90114728 | 575726 | 1 | 0 | 575726 | 583989.7432 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 804304.6434 | 844139.0145 | 879803.8192 | 873504.546 | 859344.4269 | 844664.2379 | 860069.6023
827 | 11kV WTP | B2110O | 11 | 0 | X0599387 | 1 | 2506.6 | 2925.9 | 419.3 | 1000 | 0 | 419300 | 425318.4663 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 252567.7657 | 0 | 285986.2262 | 561982.597 | 0 | 0 | 145877.5724
828 | 11kV Kamalapur Water pumping | B2110F | 11 | 0 | HA021100474-02 | 1 | 7681209 | 7702929 | 21720 | 1 | 0 | 21720 | 22031.7603 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 24054.7854 | 97542.6949 | 82536.7668 | 73055.4392 | 36822.7275 | 20221.1849 | 24456.8935
829 | 11 kV Wasa Road Feeder | B2110A | 11 | 0 | HA021001011-02 | 1 | 28031254 | 29194203 | 1162949 | 1 | 0 | 1162949 | 1179641.5099 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1724950.0596 | 2072782.2659 | 2063419.1707 | 2142959.5506 | 2098895.465 | 1863737.1947 | 2040994.3579
830 | 11kV Sutikhalpar Feeder | B2110K | 11 | 0 | HA021101047-02 | 1 | 82588606 | 83966144 | 1377538 | 1 | 0 | 1377538 | 1397310.6355 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1698787.5503 | 1889889.713 | 1886554.6703 | 2069904.1114 | 2025250.0101 | 1882771.0147 | 2076315.0532
831 | 11kV Spare | 0 | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
832 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | 11kV Spare | 0 | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
834 | 11kV Spare | 0 | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
835 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
836 | AT-1 | 0 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0
837 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 | 0 | DHK86058 | 1 | 1763.67 | 1775.85 | 12.18 | 60000 | 0 | 730800 | 734202.8494 | Motijheel | Motijheel old 33/11 kV | 75 | 859250.5994 | 1078290.2684 | 1069121.0153 | 1083441.1947 | 1084055.9235 | 997541.2473 | 913140.3988
838 | 11kV Station Road Feeder | A175H | 11 | 0 | DHK86075 | 1 | 2382.7 | 2383.68 | 0.98 | 60000 | 0 | 58800 | 59073.7925 | Motijheel | Motijheel old 33/11 kV | 75 | 80099.6322 | 97417.5285 | 97902.6548 | 101497.5399 | 109816.6442 | 95033.1244 | 121832.4707
839 | 11kV Box Culvert Road Feeder | A175F | 11 | 0 | DHK86071 | 1 | 3279.86 | 3303.43 | 23.57 | 60000 | 0 | 1414200 | 1420784.9886 | Motijheel | Motijheel old 33/11 kV | 75 | 1714253.4911 | 1945915.1314 | 1920213.4191 | 1954278.0752 | 1833753.908 | 1479451.1554 | 1996966.8828
840 | 11kV Mohamedan Club Feeder | A174V | 11 | 0 | DHK86062 | 1 | 1734.42 | 1743.1 | 8.68 | 60000 | 0 | 520800 | 523225.0191 | Motijheel | Motijheel old 33/11 kV | 75 | 731212.5511 | 895632.4025 | 840281.0677 | 917081.3217 | 976079.7817 | 1139171.2585 | 731597.9549
841 | 11kV Amina Ahmed Co. | 0 | 11 | 0 | DHK95754 | 1 | 122809 | 125374 | 2565 | 60 | 0 | 153900 | 154616.6099 | Motijheel | Motijheel old 33/11 kV | 75 | 203465.202 | 231731.9459 | 212983.3214 | 238309.0167 | 251289.93 | 373020.341 | 139323.2709
842 | 11kV Bangabhaban -1 | 0 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
843 | 11kV Sonali Bank | A175SB | 11 | 0 | DHK95753 | 1 | 89291 | 93455 | 4164 | 60 | 0 | 249840 | 251003.3387 | Motijheel | Motijheel old 33/11 kV | 75 | 265299.6907 | 525993.7678 | 476719.8595 | 524063.6289 | 553807.1772 | 446839.6196 | 345775.0268
844 | 11kV NCC Bank Feeder | A133S | 11 | 0 | DHK68123 | 1 | 335.29 | 338.12 | 2.83 | 60000 | 0 | 169800 | 170590.6456 | Motijheel | Motijheel old 33/11 kV | 75 | 211778.5729 | 238064.0852 | 224635.5392 | 249239.521 | 237424.8118 | 404044.0578 | 147163.9744
845 | 11kV IFIC BANK Feeder | 0 | 11 | 0 | DHK68116 | 1 | 426.1 | 431.45 | 5.35 | 60000 | 0 | 321000 | 322494.6834 | Ramna | Motijheel old 33/11 kV | 75 | 395036.8222 | 459080.103 | 425846.5168 | 457039.218 | 500616.6574 | 354381.5863 | 554880.5594
846 | 11kV Arambagh Feeder | A174X | 11 | 0 | DHK68117 | 1 | 3445.31 | 3459.88 | 14.57 | 60000 | 0 | 874200 | 878270.5678 | Motijheel | Motijheel old 33/11 kV | 75 | 488486.393 | 1367498.5561 | 1397665.5071 | 1278373.3459 | 1267688.622 | 59250.2714 | 488536.1447
847 | 11kV Nikotborti Feeder | A175K | 11 | 0 | DHK68114 | 1 | 1443.26 | 1445.78 | 2.52 | 60000 | 0 | 151200 | 151904.0378 | Motijheel | Motijheel old 33/11 kV | 75 | 214812.6499 | 275204.518 | 264277.1049 | 302690.8881 | 931907.7237 | 862042.4055 | 655000.3125
848 | 11kV Agrani Bank Feeder | A174O | 11 | 0 | DHK95756 | 1 | 381960 | 384470 | 2510 | 60 | 0 | 150600 | 151301.244 | Motijheel | Motijheel old 33/11 kV | 75 | 192421.1618 | 232340.8054 | 213403.7622 | 236867.6315 | 255891.186 | 369219.0161 | 144691.1372
849 | 11kV Bangladesh Bank-2 | A133D | 11 | 0 | DHK95755 | 1 | 552 | 552 | 0 | 60000 | Estimated | 565004.16 | 567635.0085 | Motijheel | Motijheel old 33/11 kV | 75 | 892846.9338 | 987430.8879 | 706996.5136 | 913123.8185 | 781881.091 | 669891.5592 | 180939.3128
850 | 11kV PDB Design Feeder 14 | 0 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
851 | 11kV Bangabhaban-2 | 0 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
852 | 11/0.4 kV AT | 0 | 0.415 | 0 | ELIC5429 | 1 | 422280 | 433644 | 11364 | 1 | 0 | 11364 | 11416.9146 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 5453.7184 | 4994.8 | 6386.5434 | 8270.9474 | 3518.2644
853 | 11 kV Central Weman | A1111CW | 11 | 0 | 41812909492 | 1 | 188.77 | 194.54 | 5.77 | 60000 | 0 | 346200 | 352370.1881 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 559606.8157 | 780631.0755 | 589767.3774 | 585552.4072 | 614594.3851 | 602582.0913 | 559727.7485
854 | 11 kV Spare Feeder 2 | 0 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
855 | 11 kV K. M. Das Len | 0 | 11 | 0 | 41812909499 | 1 | 308.53 | 317.41 | 8.88 | 60000 | 0 | 532800 | 542295.8874 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 679005.6837 | 845732.5401 | 957285.5746 | 992186.0233 | 1031748.0667 | 1006914.6746 | 933883.7569
856 | 11 kV Gopibag | A1111GP | 11 | 0 | 41812909517 | 1 | 46.6 | 48.11 | 1.51 | 60000 | 0 | 90600 | 92214.7286 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 109147.45 | 151903.4174 | 162651.6346 | 159641.3456 | 169750.8488 | 161492.0005 | 148216.3898
857 | 11kV SPICE TV | B1111E | 11 | 0 | 41812909518 | 1 | 29.4 | 33.3 | 3.9 | 60000 | 0 | 234000 | 238170.4911 | Narinda | Motijheel 33/11 KV SS (new) | 111 | 196586.015 | 229907.875 | 224111.6034 | 223497.8838 | 229344.2319 | 216326.9708 | 196416.8418
858 | 11 kV Spare Feeder 6 | 0 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
859 | 11 kV Spare Feeder 7 | 0 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
860 | 11 kV BPT-1 | 0 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
861 | 11 kV BPT-2 | 0 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
862 | 10 kV Spare Feeder 8 | 0 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
863 | 11 kV Spare Feeder 9 | 0 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
864 | 11 kV South Kamlapur | A1111SK | 11 | 0 | 41812909473 | 1 | 413.52 | 419.41 | 5.89 | 60000 | 0 | 353400 | 359698.5109 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 441413.9968 | 616997.6645 | 555002.1425 | 559648.3398 | 571253.7429 | 550760.0315 | 1048359.8303
865 | 11 kV Spare Feeder 11 | 0 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0
866 | 11 kV Answer Camp | A1111AC | 11 | 0 | 41812909514 | 1 | 225.49 | 232.83 | 7.34 | 60000 | 0 | 440400 | 448249.0781 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 582521.7499 | 703799.6173 | 759868.7052 | 750615.5343 | 784345.2339 | 758048.2709 | 729031.836
867 | 11 kV Shapla Chattar | A1111SC | 11 | 0 | 41812909516 | 1 | 210.07 | 221.82 | 11.75 | 60000 | 0 | 705000 | 717564.9411 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 919009.4688 | 1155990.8714 | 1143527.9043 | 1182550.7976 | 639274.4731 | 598966.5988 | 591058.0422
868 | 11 kV Sayedabad | 0 | 11 | 0 | 41812909497 | 1 | 118.23 | 122.96 | 4.73 | 60000 | 0 | 283800 | 288858.0572 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 483625.7179 | 303220.3351 | 309783.0751 | 311451.2289 | 306394.2625 | 315753.0159 | 300047.8135
869 | 33/0.4 kV Aux Transformer | 0 | 0.415 | 0 | 41901920686 | 1 | 1459.01 | 1459.01 | 0 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 76.8957 | 83.5078 | 86.4785 | 0 | 0 | 0 | 0
870 | Inner Circular Road Feeder | A161Z | 11 | 0 | BD014042 | 1 | 43389 | 43842 | 453 | 1000 | 0 | 453000 | 462807.6401 | Motijheel | P & T 33/11 KV SS | 61 | 1167930.2881 | 717359.185 | 740621.6003 | 751211.0308 | 786225.5313 | 2044037.2926 | 2028898.6132
871 | NSI New Building Expres Feeder | D361NS | 11 | 0 | BD013982 | 1 | 11095 | 11324 | 229 | 1000 | 0 | 229000 | 233957.9461 | Ramna | P & T 33/11 KV SS | 61 | 303173.5417 | 408763.2027 | 366793.6012 | 408464.6789 | 417588.6558 | 429529.4901 | 413128.6457
872 | Police Hospital RMU Feeder | D661H | 11 | 0 | BD014044 | 1 | 4037 | 4109 | 72 | 1000 | 0 | 72000 | 73558.8302 | Rajarbag | P & T 33/11 KV SS | 61 | 119031.2227 | 160874.6268 | 178874.6877 | 184011.3157 | 189813.0254 | 182072.2195 | 167833.5123
873 | Jonaki O/H Feeder | D661J | 11 | 0 | BD014013 | 1 | 38143 | 39094 | 951 | 1000 | 0 | 951000 | 971589.5492 | Rajarbag | P & T 33/11 KV SS | 61 | 1202520.558 | 1451918.8017 | 1556611.7488 | 1494333.6521 | 1501520.9321 | 1581312.3149 | 1420129.7195
874 | Nayapalton Overhead Feeder | D361N | 11 | 0 | BD014014 | 1 | 27311 | 27867 | 556 | 1000 | 0 | 556000 | 568037.6334 | Ramna | P & T 33/11 KV SS | 61 | 768107.463 | 920728.9962 | 1002904.148 | 1013073.2878 | 1003011.9866 | 1008941.636 | 976215.0449
875 | Masjid Gali Over Head Feeder | D361MG | 11 | 0 | BD014016 | 1 | 16992 | 17566 | 574 | 1000 | 0 | 574000 | 586427.3409 | Ramna | P & T 33/11 KV SS | 61 | 687735.9536 | 843832.9482 | 902412.7504 | 918034.4764 | 899114.3306 | 924444.0314 | 878891.4697
876 | Spare Feeder (Feeder-8) | 0 | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0
877 | Mid Way Over Head Feeder | D361MW | 11 | 0 | BD014015 | 1 | 25465 | 26030 | 565 | 1000 | 0 | 565000 | 577232.4871 | Ramna | P & T 33/11 KV SS | 61 | 723343.5844 | 925787.9468 | 990845.1803 | 982741.7522 | 1022992.3051 | 1000894.2451 | 972242.6541
878 | Palton Thana Over Head Feeder | D661F | 11 | 0 | BD014033 | 1 | 27288 | 28044 | 756 | 1000 | 0 | 756000 | 772367.7173 | Rajarbag | P & T 33/11 KV SS | 61 | 1016343.5173 | 1303185.6562 | 1382761.6309 | 1360874.8956 | 1387633.1169 | 1346932.0545 | 1294006.3108
879 | Police Hospital (South) U/G Feeder 7 | 0 | 11 | 0 | BD014034 | 1 | 12871 | 12972 | 101 | 1000 | 0 | 101000 | 103186.6924 | Rajarbag | P & T 33/11 KV SS | 61 | 130222.1924 | 174027.8982 | 183899.2576 | 186033.4181 | 181820.898 | 172012.9808 | 167833.5123
880 | China Town Express Feeder | D361CT | 11 | 0 | BD013943 | 1 | 7132 | 7303 | 171 | 1000 | 0 | 171000 | 174702.2218 | Ramna | P & T 33/11 KV SS | 61 | 210593.7018 | 268124.378 | 282380.8272 | 287138.5367 | 264739.2196 | 295741.6161 | 284025.9439
881 | Fakirapul Bazar O/H Feeder | A161FB | 11 | 0 | BD014032 | 1 | 33315 | 34326 | 1011 | 1000 | 0 | 1011000 | 1032888.5743 | Motijheel | P & T 33/11 KV SS | 61 | 1155721.9576 | 1453942.382 | 1464159.663 | 1476134.7307 | 1280738.4132 | 1354979.4454 | 1402253.9607
882 | PWD Ouarter (RMU) | A161PW | 11 | 0 | BD013937 | 1 | 2737 | 2844 | 107 | 1000 | 0 | 107000 | 109316.5949 | Motijheel | P & T 33/11 KV SS | 61 | 124118.0271 | 149744.9357 | 156766.5803 | 149635.5754 | 151850.4203 | 150888.5797 | 145985.3628
883 | Postal Quarter RMU | A161PO | 11 | 0 | BD013945 | 1 | 3356 | 3479 | 123 | 1000 | 0 | 123000 | 125663.0016 | Motijheel | P & T 33/11 KV SS | 61 | 149552.0491 | 176051.4784 | 181889.4296 | 177945.0086 | 177824.8343 | 174024.8285 | 164854.2192
884 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | DHKH4409 | 1 | 1497 | 1497 | 0 | 100 | 0 | 0 | 0 | Rajarbag | P & T 33/11 KV SS | 61 | 2136.4578 | 0 | 4220.6387 | 5762.9918 | 6093.9971 | 301.7772 | 0
885 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | DHKH4411 | 1 | 607 | 645 | 38 | 100 | 0 | 3800 | 3882.2716 | Rajarbag | P & T 33/11 KV SS | 61 | 2950.3465 | 5666.0246 | 1406.8796 | 0 | 5394.686 | 0 | 5362.7276
886 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 469.4 | 482.7 | 13.3 | 40000 | 0 | 532000 | 542948.0376 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 698504.7602 | 873041.3399 | 948762.3589 | 895110.6473 | 1426015.7648 | 1381038.2208 | 1302977.567
887 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 81.8 | 83.9 | 2.1 | 40000 | 0 | 84000 | 85728.6375 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 128460.6456 | 186790.2402 | 199525.1313 | 209665.557 | 202559.0575 | 214648.1692 | 201076.785
888 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 339.9 | 352 | 12.1 | 40000 | 0 | 484000 | 493960.2448 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 634274.4374 | 775585.5625 | 851035.764 | 818502.0784 | 866952.7661 | 866692.6078 | 735941.0332
889 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 792.7 | 811.7 | 19 | 40000 | 0 | 760000 | 775640.0538 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 967469.2368 | 1218197.2185 | 1388532.036 | 1274121.462 | 2264610.2629 | 2211281.1394 | 2079133.9572
890 | 11 KV Majar Feeder | 0 | 11 | 0 | 96 | 1 | 78.2 | 83.8 | 5.6 | 40000 | 0 | 224000 | 228609.7001 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 285022.0573 | 369519.8229 | 407194.1454 | 391106.9045 | 417271.6585 | 400946.5802 | 382045.8916
891 | 11 kV Feeder-6 | 0 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
892 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 364.4 | 371.1 | 6.7 | 40000 | 0 | 268000 | 273515.1768 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 353266.7753 | 495400.2022 | 517136.5647 | 483843.5932 | 563114.1799 | 1081340.777 | 1001362.3894
893 | 11 kV Feeder-8 | 0 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
894 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 239.1 | 243.8 | 4.7 | 40000 | 0 | 188000 | 191868.8554 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 256921.2911 | 345155.8786 | 354258.9065 | 330626.4553 | 352452.7601 | 340197.0984 | 337808.9988
895 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 379.3 | 391.2 | 11.9 | 40000 | 0 | 476000 | 485795.6126 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 622231.2519 | 1344077.5978 | 2296574.9803 | 2165200.0794 | 449681.1077 | 437396.2693 | 402153.5701
896 | 11 kV Feeder-11 | 0 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
897 | Dhaka Railway | 0 | 11 | Motijheel | 150 | 1 | 74.6 | 78.4 | 3.8 | 40000 | 0 | 152000 | 155128.0108 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 112403.0649 | 101516.4349 | 199525.1313 | 209665.557 | 230917.3256 | 222748.1001 | 217162.9278
898 | Jasimuddin Feeder-13 | 0 | 11 | 0 | 91 | 1 | 299.6 | 321.5 | 21.9 | 40000 | 0 | 876000 | 894027.2198 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 1184246.5762 | 1445594.0326 | 1653208.2305 | 1568459.6478 | 1713649.6265 | 1656435.8718 | 1097879.2463
899 | Police Box Feeder-14 | 0 | 11 | 0 | 18 | 1 | 127.9 | 137.7 | 9.8 | 40000 | 0 | 392000 | 400066.9751 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 493770.6063 | 605037.9519 | 655582.5742 | 628996.6711 | 656291.3463 | 664194.3349 | 643445.7121
900 | 11 kV Feeder-15 | 0 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
901 | 11 kV Feeder-16 | 0 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
902 | Auxiliary -1 (AT-1 ) | 0 | 0.415 | 0 | DHKF 7632 | 1 | 1052.87 | 1080.13 | 27.26 | 100 | 0 | 2726 | 2782.0984 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 3429.2971 | 7083.8168 | 0 | 4701.3469 | 8715.1034 | 2871.4255 | 5128.4634
903 | Auxiliary -1 (AT-2 ) | 0 | 0.415 | 0 | DHKF 7733 | 1 | 156.6 | 156.6 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 0 | 1938.9639 | 1823.2118 | 0 | 0 | 0 | 0
904 | 11 kV DIT S/S-1 Feeder | 0 | 11 | Motijheel | 4150750 | 1 | 219429.19 | 220085.55 | 656.36 | 1000 | Estimated | 729797.04 | 732850.4474 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 734566.8339 | 730932.291 | 825621.5358 | 884099.9496 | 816951.1322 | 793502.3098 | 860468.6016
905 | 11 kV Bangabhaban Switching Circuit-1 | 0 | 11 | Motijheel | 4150743 | 1 | 24348.79 | 24377.48 | 28.69 | 1000 | 0 | 28690 | 28810.0365 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 38328.8826 | 45380.4829 | 61964.371 | 72049.9558 | 82523.1488 | 83389.7606 | 79020.0597
906 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
907 | 11 kV Bangladesh Bank Feeder | 0 | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 240728.715
908 | 11 kV P & T Substation | 0 | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
909 | 11 kV Osmani Feeder | 0 | 11 | Ramna | 4150754 | 1 | 33904.2 | 33908.56 | 4.36 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 20212.3186
910 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 668980.62 | 671779.5768 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 675327.5731 | 670021.2667 | 766648.569 | 798145.7878 | 731598.0289 | 710599.0834 | 737544.5157
911 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16090.3 | 16127.43 | 37.13 | 1000 | 0 | 37130 | 37285.3487 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 63965.3489 | 73704.4745 | 67064.6079 | 76956.258 | 79365.3753 | 70158.8804 | 76837.1293
912 | 11 kV Motijheel-1 Feeder | 0 | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
913 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 251097.91 | 251918.65 | 820.74 | 1000 | 0 | 820740 | 824173.9049 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 1024190.419 | 1159901.5065 | 1104426.7361 | 1181560.7231 | 1155594.7497 | 1181422.0182 | 1217478.907
914 | 11 kV Bangabhaban Switching Circuit-2 | 0 | 11 | Motijheel | 4150737 | 1 | 15124.38 | 15252.82 | 128.44 | 1000 | 0 | 128440 | 128977.3818 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 140844.5519 | 163473.9003 | 173027.2895 | 175243.8256 | 162199.2891 | 174416.2041 | 171420.6744
915 | 11 kV Motijheel-2 Feeder | 0 | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0
916 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 236957.0432 | 243644.097 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
917 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 165136.78 | 165380.63 | 243.85 | 1000 | 0 | 243850 | 244870.2472 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 307144.3937 | 367060.1011 | 339501.426 | 365711.3213 | 363925.8833 | 326878.2024 | 270087.1078
918 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20803.97 | 20826.96 | 22.99 | 1000 | Estimated | 170285.976 | 170998.4377 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 177717.7824 | 182733.0727 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
919 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82552.02 | 82655.11 | 103.09 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 236957.0432 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
920 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 124061.84 | 124241.41 | 179.57 | 1000 | 0 | 179570 | 180321.3053 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 243199.1755 | 300166.2046 | 298839.8125 | 325451.3768 | 302665.0764 | 348419.8864 | 313139.3465
921 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273251.62 | 273786.78 | 535.16 | 1000 | 0 | 535160 | 537399.0629 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 60090.1862 | 0 | 0 | 98812.5217 | 790606.2505 | 819439.2218 | 796304.7174
922 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 82213.59 | 82388.93 | 175.34 | 1000 | 0 | 175340 | 176073.6073 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 235529.3729 | 274686.6308 | 474442.2708 | 529113.3929 | 587426.078 | 481785.1466 | 474463.9677
923 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192985.49 | 193032.75 | 47.26 | 1000 | Estimated | 231102.396 | 232069.3083 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 236957.0432 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
924 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 63412931 | 1 | 90029 | 91654 | 1625 | 1 | 0 | 1625 | 1631.7989 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 11191.6714 | 0 | 5939.9222 | 6215.6589 | 3575.8026 | 0 | 0
925 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 63403117 | 1 | 22902 | 22902 | 0 | 1 | Estimated | 5000 | 5020.9196 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 5032.6789 | 5007.7779 | 5010.0559 | 5047.636 | 5012.339 | 5030.7529 | 5053.0797
926 | 11 kV Bonogram Feeder | B124B | 11 | 0 | 06604467 | 1 | 25262.79 | 25343.65 | 80.86 | 8000 | 0 | 646880 | 656738.9275 | Narinda | Narinda 33/11KV S/S | 24 | 833343.2066 | 1081937.7982 | 1068648.5129 | 1111412.0708 | 1143423.9412 | 1139801.4532 | 1096395.2732
927 | 11 kV Sha Saheb Len Feeder | B524H | 11 | 0 | 06604469 | 1 | 17038.74 | 17094.2 | 55.46 | 8000 | 0 | 443680 | 450442.0099 | Swamibag | Narinda 33/11KV S/S | 24 | 558526.7169 | 661053.8831 | 660371.6402 | 659718.6519 | 672430.175 | 685656.1379 | 629657.0471
928 | 11 kV Sadiabad Water Treatment | B224W | 11 | 0 | 06604354 | 1 | 538.25 | 543.81 | 5.56 | 40000 | 0 | 222400 | 225789.5397 | Maniknagar | Narinda 33/11KV S/S | 24 | 333110.8966 | 795173.7239 | 352381.8247 | 28757.3823 | 552771.4205 | 653217.1868 | 492385.8425
929 | 11 kV Manashi Feeder | B124M | 11 | 0 | 06604353 | 1 | 5635.85 | 5652.37 | 16.52 | 40000 | 0 | 660800 | 670871.0785 | Narinda | Narinda 33/11KV S/S | 24 | 875224.6252 | 1137753.6547 | 1160429.802 | 1160826.1643 | 1102291.2443 | 1122855.7324 | 1066634.3599
930 | 11 kV Jatrabari Feeder | B524E | 11 | 0 | 06604324 | 1 | 3617.32 | 3647.47 | 30.15 | 40000 |  | 1206000 | 1224380.3279 | Swamibag | Narinda 33/11KV S/S | 24 | 1448062.1743 | 2046581.4052 | 2127657.1553 | 2119945.619 | 2124511.9226 | 2030258.73 | 1913892.8816
931 | 11 kV Wari Feeder | B124W | 11 | 0 | 06604291 | 1 | 8709.16 | 8733.06 | 23.9 | 40000 | 0 | 956000 | 970570.1438 | Narinda | Narinda 33/11KV S/S | 24 | 1184484.1348 | 1567697.5349 | 1678876.6245 | 1616488.912 | 1686359.282 | 1652611.2397 | 1532808.0158
932 | 11 kV Narinda Feeder | B124N | 11 | 0 | 06604348 | 1 | 7442.6 | 7464.14 | 21.54 | 40000 | 0 | 861600 | 874731.4183 | Narinda | Narinda 33/11KV S/S | 24 | 1135164.3175 | 1444336.4028 | 1555745.5042 | 1546013.0737 | 1594908.1278 | 1590073.4608 | 1585232.3889
933 | 11 kV Distillary Feeder | B524D | 11 | 0 | 06604347 | 1 | 6121.16 | 6140.77 | 19.61 | 40000 | 0 | 784400 | 796354.8335 | Swamibag | Narinda 33/11KV S/S | 24 | 1028035.2064 | 1274866.5196 | 1339455.9704 | 1343496.2969 | 1318115.968 | 1326607.8506 | 1271895.9437
934 | 11 kV Thatari Bazar Feeder | B124T | 11 | 0 | 06604296 | 1 | 5129.92 | 5145.48 | 15.56 | 40000 | 0 | 622400 | 631885.8342 | Narinda | Narinda 33/11KV S/S | 24 | 785478.7283 | 1002663.1035 | 1062005.913 | 1059567.7759 | 1097413.8494 | 1083315.7174 | 1015016.5156
935 | 11 kV Swamibagh Feeder | B524C | 11 | 0 | 06604352 | 1 | 7918.91 | 7939.47 | 20.56 | 40000 | 0 | 822400 | 834933.9815 | Swamibag | Narinda 33/11KV S/S | 24 | 995694.3426 | 1313290.4788 | 1313533.6293 | 1354837.2364 | 1370141.5135 | 1100261.4381 | 886375.1694
936 | 11 kV Tipu Sultan Feeder | B124S | 11 | 0 | 06604322 | 1 | 6482.22 | 6500.16 | 17.94 | 40000 | 0 | 717600 | 728536.7523 | Narinda | Narinda 33/11KV S/S | 24 | 911203.8361 | 1115103.7419 | 1147873.668 | 1151915.4261 | 1136839.4581 | 1115189.8112 | 1101315.099
937 | 11 kV Spare | 0 | 11 | 0 | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938 | 11 kV Folder Street Feeder | B124F | 11 | 0 | DHK00089 | 1 | 43986.5 | 46136 | 2149.5 | 444.44 | 0 | 955323.78 | 969883.6178 | Narinda | Narinda 33/11KV S/S | 24 | 1264515.1272 | 1585927.4386 | 1742899.9791 | 1675427.0415 | 1798340.7365 | 1748933.3106 | 1624153.5662
939 | 11 kV Bhajohari Feeder | B124V | 11 | 0 | DHK27842 | 1 | 431839 | 437786 | 5947 | 80 | 0 | 475760 | 483010.9327 | Narinda | Narinda 33/11KV S/S | 24 | 619650.9494 | 785385.7258 | 835023.4135 | 806745.8319 | 813305.5973 | 819688.7194 | 775800.0686
940 | 11 kV Lal mohon shaha Feeder | B124L | 11 | 0 | DHK00086 | 1 | 43431.7 | 44846.9 | 1415.2 | 444.44 | 0 | 628971.488 | 638557.4766 | Narinda | Narinda 33/11KV S/S | 24 | 845750.0473 | 1056805.6006 | 1090752.6026 | 1096369.8618 | 1097222.2328 | 1092539.7614 | 1048880.237
941 | 11 kV Dupkhola Feeder | B524A | 11 | 0 | 8838024/8838029 | 1 | 39022.1 | 39392.3 | 370.2 | 1000 | 0 | 370200 | 375842.1206 | Swamibag | Narinda 33/11KV S/S | 24 | 459341.3304 | 602548.3495 | 612719.0865 | 555706.0354 | 579800.3171 | 568589.4506 | 537047.3757
942 | 11/0.4 kV Aux Transformer-1 | 0 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
943 | 11/0.4 kV Aux Transformer-2 | 0 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0
944 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63748 | 63943.2 | 195.2 | 2222.22 | 0 | 433777.344 | 436813.0585 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 559882.2686 | 648124.404 | 633672.3537 | 653524.1946 | 604954.0102 | 476949.7245 | 555416.4351
945 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4714.17 | 4734.1 | 19.93 | 40000 | 0 | 797200 | 802779.0641 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1039961.1294 | 1308522.8246 | 1300047.3482 | 1372334.5518 | 1164609.944 | 1430849.1736 | 1481110.4937
946 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
947 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5192.58 | 5203.81 | 11.23 | 40000 | 0 | 449200 | 452343.6473 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 454027.8867 | 509541.8516 | 496023.0204 | 523045.3096 | 442936.2442 | 536568.4401 | 493703.4979
948 | 11kV Spare | 0 | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
949 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5552.12 | 5569.8 | 17.68 | 40000 | 0 | 707200 | 712149.2149 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 978432.1066 | 1158159.6042 | 1128130.2786 | 1172692.7423 | 878663.7611 | 1216221.7976 | 1419397.5564
950 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 40077.0255 | 0
951 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4194.33 | 4211.66 | 17.33 | 40000 | 0 | 693200 | 698051.2384 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 980442.859 | 1163400.1454 | 1221939.8271 | 1252630.6213 | 1111745.9438 | 834662.018 | 740555.2468
952 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 681143.904 | 685910.7699 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 887565.2014 | 1078713.9994 | 1184790.4407 | 1110503.0608 | 1217802.7423 | 1144679.3389 | 925694.0585
953 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 6005.67 | 6022.5 | 16.83 | 40000 | 0 | 673200 | 677911.2719 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 893980.5068 | 1075923.4193 | 1095518.3755 | 1129680.4826 | 931127.2764 | 1021492.1651 | 1019206.2302
954 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8373.78 | 8401.75 | 27.97 | 40000 | 0 | 1118800 | 1126629.7252 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1559941.6941 | 1898688.3869 | 2041666.1823 | 1567512.8248 | 2037666.9172 | 1989498.8221 | 1947085.7372
955 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3799.62 | 3805.19 | 5.57 | 40000 | 0 | 222800 | 224359.2266 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 333784.8946 | 430127.4966 | 443280.3129 | 472729.0813 | 450545.4563 | 410865.9482 | 427409.0643
956 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7326.5 | 7346.17 | 19.67 | 40000 | 0 | 786800 | 792306.2815 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 995322.4266 | 1252086.2271 | 586209.0241 | 1209618.3616 | 1050071.2769 | 1251993.0269 | 1073805.1079
957 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3612.86 | 3617.65 | 4.79 | 40000 | 0 | 191600 | 192940.8789 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 238073.0814 | 277345.5648 | 287870.5029 | 292158.7455 | 264720.4859 | 275126.2119 | 281286.3072
958 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0
959 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 05378636 | 1 | 178179.3 | 178995.4 | 816.1 | 2 | 0 | 1632.2 | 1643.6227 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 3093.9447 | 5594.0762 | 5930.3337 | 4006.0239 | 7168.6788 | 4775.6076 | 4915.4072
960 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 41256087 | 41743836 | 487749 | 1 | 0 | 487749 | 490118.7926 | Bangshal | Banshal 33/11KV S/S | 78 | 617669.4796 | 748100.1808 | 769760.338 | 773303.2759 | 760951.1172 | 778854.3109 | 716311.3918
961 | 11 kV Spare Feeder | 0 | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0
962 | 11 kV Siddikbazar Feeder | 0 | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0
963 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 54945882 | 55731189 | 785307 | 1 | 0 | 785307 | 789122.5172 | Banglabazar | Banshal 33/11KV S/S | 78 | 1083356.0922 | 1317991.7768 | 1424094.0148 | 1411190.2742 | 1426877.2604 | 1429747.5487 | 1353751.6158
964 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 23435352 | 23858970 | 423618 | 1 | 0 | 423618 | 425676.2037 | Bangshal | Banshal 33/11KV S/S | 78 | 568959.3967 | 737371.3191 | 742977.1081 | 744097.7084 | 751903.1259 | 737930.5287 | 715455.6721
965 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 52356480 | 53313937 | 957457 | 1 | 0 | 957457 | 962108.9306 | Bangshal | Banshal 33/11KV S/S | 78 | 1228122.7989 | 1543005.6588 | 1634853.1578 | 1636226.6255 | 1167271.1296 | 1660584.0104 | 1409457.3709
966 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 66698574 | 67362715 | 664141 | 1 | 0 | 664141 | 667367.8163 | Bangshal | Banshal 33/11KV S/S | 78 | 917105.0905 | 1128071.6101 | 1204002.0348 | 1205928.3277 | 1183358.8995 | 1169829.7548 | 1127796.6211
967 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 33052156 | 33422319 | 370163 | 1 | 0 | 370163 | 371961.4855 | Bangshal | Banshal 33/11KV S/S | 78 | 442857.7972 | 505257.2343 | 581501.911 | 1106821.025 | 1430551.6276 | 1633419.2244 | 1486833.0286
968 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 68646258 | 69597215 | 950957 | 1 | 0 | 950957 | 955577.3495 | Bangshal | Banshal 33/11KV S/S | 78 | 1230776.8001 | 1482806.5471 | 1592214.2158 | 1582391.9071 | 1508639.2033 | 1596892.4609 | 1498407.2378
969 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 55024234 | 55733426 | 709192 | 1 | 0 | 709192 | 712637.7025 | Narinda | Banshal 33/11KV S/S | 78 | 982637.1962 | 1224359.1662 | 1261180.3015 | 1301441.3762 | 1139549.3681 | 1267199.3373 | 1145519.8164
970 | AT-1 | 0 | 0.415 | 0 | DHK-4415 | 1 | 777.4 | 799.54 | 22.14 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0
971 | AT-2 | 0 | 0.415 | 0 | DHK-4410 | 1 | 786.95 | 786.95 | 0 | 100 | 0 | 7000 | 7034.0104 | Bangshal | Banshal 33/11KV S/S | 78 | 7007.9248 | 7005.1331 | 7007.3859 | 7008.295 | 7021.7228 | 7023.9917 | 6997.7081
972 | 11 kV Nayanagor Feeder | A418N | 11 | 0 | DHK-61125 | 1 | 957166.8 | 974598.2 | 17431.4 | 60 | 0 | 1045884 | 1049288.1996 | Kazla | Kazla 33/11KV S/S | 18 | 1425042.8921 | 1775388.4538 | 1866468.623 | 1836553.7788 | 1866699.9643 | 1792344.292 | 1710856.4639
973 | 11 kV Madrasa Bazar Feeder | A418B | 11 | 0 | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1033879.14 | 1037244.2656 | Kazla | Kazla 33/11KV S/S | 18 | 1548060.2038 | 1602675.9202 | 1563148.5482 | 1846586.4161 | 1853855.1196 | 1913492.0332 | 1855425.2355
974 | 11 kV Kazla Feeder | A418K | 11 | 0 | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 1946125.44 | 1952459.794 | Kazla | Kazla 33/11KV S/S | 18 | 2381631.0828 | 2712220.788 | 2825691.6063 | 2954538.2657 | 3027963.362 | 3049627.928 | 2968680.3768
975 | 11 kV Sayedabad Feeder | B218S | 11 | 0 | HA021101239-02 | 1 | 36964660 | 36964682 | 22 | 1000 | Estimated | 912246.3 | 915215.5285 | Maniknagar | Kazla 33/11KV S/S | 18 | 952652.4331 | 1232827.6309 | 1202421.9601 | 1231057.6107 | 988722.7304 | 1076339.2687 | 556627.5706
976 | 11 kV Zenith Feeder | A418Z | 11 | 0 | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
977 | 11 kV Paterbagh Feeder | B318P | 11 | 0 | HA-021200060 | 1 | 122840.5 | 124064 | 1223.5 | 1000 | 0 | 1223500 | 1227482.3138 | Jurain | Kazla 33/11KV S/S | 18 | 1890790.3944 | 2010101.6778 | 2308939.6211 | 2025231.2443 | 2541656.3466 | 2207984.2138 | 2092993.2394
978 | 11 kV Matuail Feeder | A418M | 11 | 0 | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1216328.4 | 1220287.3713 | Kazla | Kazla 33/11KV S/S | 18 | 1488519.4268 | 1849241.4463 | 1803632.9402 | 1969692.1771 | 1730264.7783 | 1734102.1551 | 1855425.2355
979 | 11 kV Kutubkhali Feeder | B326C | 11 | 0 | DHK-61117 | 1 | 873380.8 | 899823.4 | 26442.6 | 60 | 0 | 1586556 | 1591720.008 | Jurain | Kazla 33/11KV S/S | 18 | 2111396.7703 | 2432494.6655 | 2317847.2676 | 2260753.1891 | 2379719.4891 | 2279252.9698 | 2232712.5636
980 | 11 kV Mridhabari Feeder | A418R | 11 | 0 | DHK-61118 | 1 | 722924.6 | 743943.1 | 21018.5 | 60 | 0 | 1261110 | 1265214.7288 | Kazla | Kazla 33/11KV S/S | 18 | 1394116.481 | 1532023.4409 | 1493309.739 | 1567790.1074 | 1353302.4526 | 1381440.9902 | 1371332.0993
981 | 11 kV Muslim Nagar Feeder | A418U | 11 | 0 | DHK-61011 | 1 | 192344.8 | 225676.9 | 33332.1 | 60 | 0 | 1999926 | 2006435.467 | Kazla | Kazla 33/11KV S/S | 18 | 2307735.4737 | 2627245.0572 | 2655800.5175 | 2583205.2246 | 2385633.1534 | 2345596.1288 | 2459477.0573
982 | 11 kV Jatrabari Thana Feeder | A418H | 11 | 0 | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
983 | 11 kV Mirhazirbag Feeder | B518D | 11 | 0 | DHK-61008 | 1 | 375123.8 | 394906.3 | 19782.5 | 60 | 0 | 1186950 | 1190813.3489 | Swamibag | Kazla 33/11KV S/S | 18 | 1593271.6426 | 1997346.9786 | 2119778.8003 | 2106094.7503 | 2092254.4374 | 2069592.0061 | 1962979.7252
984 | 11 kV Mukti Sharani Feeder | B318T | 11 | 0 | DHK-61014 | 1 | 213219.9 | 235359.9 | 22140 | 60 | 0 | 1328400 | 1332723.748 | Jurain | Kazla 33/11KV S/S | 18 | 182.0986 | 1171257.2192 | 2474942.6039 | 2420269.7538 | 2465205.4697 | 2452063.3964 | 2370251.5382
985 | 11 kV Kadamtali Feeder | B418K | 11 | 0 | DHK-61006 | 1 | 485277.4 | 512713.6 | 27436.2 | 60 | 0 | 1646172 | 1651530.0494 | Shyampur | Kazla 33/11KV S/S | 18 | 2019121.3431 | 2235311.7183 | 2567504.4926 | 2822437.563 | 2221373.5062 | 2471771.8805 | 3092469.9692
986 | 11kV Rayerbagh Feeder | E218R | 11 | 0 | DHK-61012 | 1 | 473065.1 | 487739.3 | 14674.2 | 60 | 0 | 880452 | 883317.7427 | Matuail | Kazla 33/11KV S/S | 18 | 1505014.5244 | 1463413.2136 | 898785.6229 | 322767.8137 | 1280357.0984 | 1277473.0974 | 837095.6004
987 | 11 kV Donia Feeder | B318D | 11 | 0 | DHK-61013 | 1 | 2100163 | 2100163 | 0 | 60 | 0 | 0 | 0 | Jurain | Kazla 33/11KV S/S | 18 | 932769.6947 | 2275838.0926 | 2097995.927 | 2006588.1861 | 2090084.0617 | 2017361.1702 | 1952856.964
988 | 11 kV Nimtoli Feeder | A418T | 11 | 0 | HA-021100855-02 | 1 | 35425036 | 36615614 | 1190578 | 1 | 0 | 1190578 | 1194453.1575 | Kazla | Kazla 33/11KV S/S | 18 | 1438258.1917 | 1595582.0613 | 1529815.767 | 1526570.9331 | 1509829.6282 | 1633862.5979 | 1591423.3402
989 | 11 kV Gobindapur Feeder | A441G | 11 | 0 | HA-021101057-02 | 1 | 29299106 | 30389588 | 1090482 | 1 | 0 | 1090482 | 1094031.3596 | Kazla | Kazla 33/11KV S/S | 18 | 557604.1027 | 679496.8713 | 715534.2901 | 710807.5855 | 721136.817 | 697773.6086 | 686441.9856
990 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 | 0 | 9A56136 | 1 | 3949.3 | 4086 | 136.7 | 10000 | 0 | 1367000 | 1371449.3853 | Kazla | Kazla 33/11KV S/S | 18 | 1500290.0775 | 1773738.3704 | 1822390.0739 | 1778276.5099 | 1887901.7718 | 1946667.4736 | 1703398.1226
991 | 11 kV Samad Nagar Gate (Old) | A418A | 11 | 0 | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
992 | 11 kV Dharmik Para | A418D | 11 | 0 | 8K55676 | 1 | 820.6 | 1019.5 | 198.9 | 4000 | 0 | 795600 | 798189.5618 | Kazla | Kazla 33/11KV S/S | 18 | 25898.4666 | 0 | 0 | 0 | 0 | 23977.7413 | 1140208.9403
993 | 11 kV Sheikhdi Feeder | A418I | 11 | 0 | 9A56133 | 1 | 17420.9 | 17759.8 | 338.9 | 4000 | 0 | 1355600 | 1360012.28 | Kazla | Kazla 33/11KV S/S | 18 | 2650141.5287 | 3268543.7125 | 3436798.8591 | 3359798.9198 | 3415699.9979 | 3248780.7482 | 3103743.9224
994 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | T-5 Sum | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0
995 | 11 kV Jenith Feeder | A418Z | 11 | 0 | 61903661 | 1 | 23175.9 | 23269.7 | 93.8 | 2000 | 2259400 | 187600 | 188210.6106 | Kazla | Kazla 33/11KV S/S | 18 | 1045852.9212 | 1210196.351 | 1200080.6383 | 617589.258 | 551840.3941 | 574043.3834 | 0
996 | 11 KV Samad Nagor Gate | A418A | 11 | 0 | 61903675 | 1 | 20299.2 | 20906 | 606.8 | 2000 | 0 | 1213600 | 1217550.0907 | Kazla | Kazla 33/11KV S/S | 18 | 1246768.3692 | 1325742.7363 | 1296103.4337 | 1368574.557 | 1134163.594 | 1293375.6231 | 1288887.6302
997 | 11 KV Bibir Bagicha | B218I | 11 | 0 | 61903557 | 1 | 38947.4 | 39376.5 | 429.1 | 2000 | 0 | 858200 | 860993.3156 | Maniknagar | Kazla 33/11KV S/S | 18 | 974025.1427 | 1414936.4372 | 1478955.3526 | 1458247.4647 | 1460126.3972 | 1445370.1189 | 1356006.601
998 | 33/0.4 kV AT-1 | 0 | 0.415 | 0 | 503043 | 1 | 96207 | 96242 | 35 | 10 | 0 | 350 | 351.1392 | Kazla | Kazla 33/11KV S/S | 18 | 30.3498 | 0 | 0 | 0 | 0 | 0 | 244.069
999 | 33/0.4 kV AT-2 | 0 | 0.415 | 0 | 503044 | 1 | 96336 | 96529 | 193 | 10 | 0 | 1930 | 1936.2819 | Kazla | Kazla 33/11KV S/S | 18 | 3500.3396 | 6121.9313 | 14219.5459 | 6072.6574 | 6096.5612 | 6096.0359 | 6101.7246
1000 | Auxiliary Transformer | 0 | 0.415 | 0 | 41901920685 | 1 | 2874.18 | 2947.06 | 72.88 | 160 | 0 | 11660.8 | 11698.7542 | Kazla | Kazla 33/11KV S/S | 18 | 17193.3445 | 19919.386 | 20587.2873 | 0 | 0 | 0 | 0
1001 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur | 0 | 1 | 799.6936 | 841.27 | 41.5764 | 40000 | 0 | 1663056 | 1664915.738 | Shyampur | Shyampur 33/11KV S/S | 26 | 1892333.6894 | 1814264.1154 | 1610415.5328 | 1658511.8396 | 1848660.4463 | 1329002.2614 | 1796570.0888
1002 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1003 | 11 kV Road No.-21 Feeder | B426E | 11 | 0 | BD001943 | 1 | 1100.56 | 1116.9598 | 16.3998 | 40000 | 0 | 655992 | 656725.5732 | Shyampur | Shyampur 33/11KV S/S | 26 | 622979.2968 | 558390.1777 | 490213.532 | 606607.4764 | 536986.5578 | 689153.8135 | 726162.1684
1004 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1606.52 | 1625.62 | 19.1 | 40000 | 0 | 764000 | 764854.3548 | Shyampur | Shyampur 33/11KV S/S | 26 | 906406.8147 | 891408.4354 | 575920.7998 | 812129.1164 | 684264.5087 | 768373.9842 | 842780.9272
1005 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1491.05 | 1505.39 | 14.34 | 40000 | 0 | 573600 | 574241.437 | Shyampur | Shyampur 33/11KV S/S | 26 | 703156.8125 | 766828.9661 | 770964.9094 | 745215.0941 | 653846.0494 | 678120.977 | 664045.6474
1006 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1411.27 | 1427.59 | 16.32 | 40000 | 0 | 652800 | 653530.0037 | Fatullah | Shyampur 33/11KV S/S | 26 | 820616.8729 | 1034936.8854 | 1058124.3068 | 991363.1049 | 1100803.9423 | 1060453.8119 | 1011898.1651
1007 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3529.38 | 3595.32 | 65.94 | 40000 | 0 | 2637600 | 2640549.5368 | Shyampur | Shyampur 33/11KV S/S | 26 | 2858328.4338 | 2421034.6696 | 2293670.6681 | 2291008.6698 | 1731865.3068 | 2347543.3088 | 2415731.5404
1008 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1009 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2300.68 | 2344.78 | 44.1 | 40000 | 0 | 1764000 | 1765972.6202 | Shyampur | Shyampur 33/11KV S/S | 26 | 1793971.9132 | 1756207.6637 | 1462630.5709 | 1686790.98 | 1265223.6985 | 1510257.147 | 1400226.6095
1010 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 500.99 | 504.69 | 3.7 | 40000 | 0 | 148000 | 148165.5033 | Fatullah | Shyampur 33/11KV S/S | 26 | 166368.345 | 155220.3743 | 135769.9243 | 127455.2807 | 91577.1387 | 112254.6055 | 96981.9232
1011 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3319.55 | 3370.17 | 50.62 | 40000 | 0 | 2024800 | 2027064.2638 | Shyampur | Shyampur 33/11KV S/S | 26 | 1986798.8384 | 1913040.7173 | 1822681.1962 | 2162756.7937 | 1853587.4081 | 1927999.1795 | 1824622.7112
1012 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2091.49 | 2125.51 | 34.02 | 40000 | 0 | 1360800 | 1362321.7356 | Shyampur | Shyampur 33/11KV S/S | 26 | 1609964.5147 | 1509467.744 | 1396147.3632 | 1389660.8569 | 915888.0248 | 1677475.7016 | 1601003.2355
1013 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1561.08 | 1609.74 | 48.66 | 40000 | 0 | 1946400 | 1948576.5918 | Shyampur | Shyampur 33/11KV S/S | 26 | 1516958.5966 | 546698.2534 | 888712.2774 | 1726620.7552 | 1517234.7817 | 1359049.2203 | 1887540.7358
1014 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1015 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 891.78 | 916.9 | 25.12 | 40000 | 0 | 1004800 | 1005923.6331 | Shyampur | Shyampur 33/11KV S/S | 26 | 1095224.8641 | 747879.9854 | 273141.8536 | 751986.1559 | 501987.0295 | 565017.3838 | 552636.6613
1016 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1385.17 | 1397.79 | 12.62 | 40000 | 0 | 504800 | 505364.5004 | Shyampur | Shyampur 33/11KV S/S | 26 | 596520.7166 | 735784.8913 | 764156.3881 | 763138.4929 | 788989.597 | 774228.7961 | 1030332.7456
1017 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3261.15 | 3311.5 | 50.35 | 40000 | 0 | 2014000 | 2016252.1865 | Shyampur | Shyampur 33/11KV S/S | 26 | 2248177.5395 | 2749214.8896 | 3128315.2765 | 2945013.5787 | 2827927.2998 | 2567335.031 | 2104748.1835
1018 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1019 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1128.58 | 1134.93 | 6.35 | 40000 | 0 | 254000 | 254284.0394 | Shyampur | Shyampur 33/11KV S/S | 26 | 285431.9558 | 272542.7871 | 255119.2973 | 227029.7187 | 174848.8273 | 295251.5179 | 251271.3464
1020 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2088.29 | 2117.6 | 29.31 | 40000 | 0 | 1172400 | 1173711.0544 | Shyampur | Shyampur 33/11KV S/S | 26 | 1318519.2453 | 1539705.4793 | 1292017.0377 | 1541412.3005 | 1200352.7042 | 1365805.0805 | 1428279.2319
1021 | 11 kV Spare Feeder | spare | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1022 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1435.214 | 1450.588 | 15.374 | 40000 | 0 | 614960 | 615647.6885 | Shyampur | Shyampur 33/11KV S/S | 26 | 947858.5903 | 859154.8511 | 801803.5058 | 808146.1389 | 598969.7492 | 543740.6288 | 732574.1964
1023 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1414.78 | 1442.65 | 27.87 | 40000 | 0 | 1114800 | 1116046.6423 | Shyampur | Shyampur 33/11KV S/S | 26 | 1219099.1258 | 1035743.225 | 446558.8956 | 946355.4589 | 931203.8377 | 1080348.9594 | 971021.4868
1024 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1025 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1026 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1027 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2381.97 | 2404.17 | 22.2 | 40000 | 0 | 888000 | 888993.0197 | Shyampur | Shyampur 33/11KV S/S | 26 | 1226715.9898 | 1501001.1782 | 1526310.2699 | 1579250.5869 | 1494594.8892 | 1526560.1151 | 1250345.4555
1028 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 178.05 | 179 | 0.95 | 40000 | 0 | 38000 | 38042.4941 | Shyampur | Shyampur 33/11KV S/S | 26 | 89397.93 | 41123.3199 | 3604.5113 | 82447.6347 | 75834.9927 | 95891.5675 | 84558.6189
1029 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1030 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1277.88 | 1298.4 | 20.52 | 40000 | 0 | 820800 | 821717.8722 | Shyampur | Shyampur 33/11KV S/S | 26 | 867119.832 | 867218.2472 | 889112.7786 | 908118.8747 | 695610.598 | 869607.7672 | 875642.5706
1031 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3859.6597 | 3910.37 | 50.7103 | 40000 | 0 | 2028412 | 2030680.303 | Shyampur | Shyampur 33/11KV S/S | 26 | 1872132.9644 | 1624774.3078 | 1797850.1185 | 1620673.5531 | 2160897.1026 | 1905144.5888 | 2092324.8793
1032 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1132.87 | 1134.57 | 1.7 | 40000 | 0 | 68000 | 68076.042 | Shyampur | Shyampur 33/11KV S/S | 26 | 184408.2861 | 343903.8423 | 438548.8705 | 532125.7967 | 778413.3204 | 463585.7706 | 590307.3256
1033 | 11/0.4 kV Aux Transformer, T-1 | 0 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0.415 | DPDC | DHK26108 | 1 | 65650.1 | 65952.1 | 302 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1035 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0.415 | 0 | 0 | 1 | 625854 | 633261 | 7407 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1036 | 11/0.4 kV Aux Transformer, T-2 | 0 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1037 | 11 kV Nama shyampur Feeder | 0 | 11 | Shympur | HA-021101066-02 | 1 | 46233188 | 47694122 | 1460934 | 1 | 0 | 1460934 | 1460934 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1775047.104 | 2124178.3588 | 2141060 | 2242087.5527 | 2142439.5507 | 2098065.1104 | 2051822.5774
1038 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 24282013 | 24843560 | 561547 | 1 | 0 | 561547 | 561547 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 664547.744 | 735518.3371 | 786111 | 782826.8086 | 745206.3758 | 738065.3088 | 731764.9753
1039 | 11 kV H. R Steel | 0 | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1040 | 11 kV Shyampur Incoming (F1) | 0 | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1041 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 559360.2 | 587566.2 | 28206 | 60 | 0 | 1692360 | 1692360 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1847173.44 | 1772799.78 | 1740318 | 1920297.8361 | 1596859.747 | 1920766.0882 | 1940683.7189
1042 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 693053.6 | 712115.6 | 19062 | 60 | 0 | 1143720 | 1143720 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1448800.128 | 1537289.4923 | 1379322 | 1531676.01 | 1098969.809 | 1475476.6819 | 1381608.0185
1043 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 708041.4 | 726690.5 | 18649.1 | 60 | 0 | 1118946 | 1118946 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1325819.904 | 1436086.1084 | 1338426 | 1403188.8641 | 1231235.1282 | 1429313.0963 | 1378277.4296
1044 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 421306.3 | 440150 | 18843.7 | 60 | 0 | 1130622 | 1130622 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1052218.368 | 1093174.4833 | 818646 | 1160551.0823 | 887582.2839 | 954363.7317 | 1019394.7492
1045 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 540442.3 | 570270.4 | 29828.1 | 60 | 0 | 1789686 | 1789686 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1124308.992 | 208419.6185 | 288 | 3130.962 | 385792.207 | 8184.8678 | 8596.203
1046 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 51207.4 | 85440.5 | 34233.1 | 60 | 0 | 2053986 | 2053986 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2314357.824 | 2668033.8435 | 2872542 | 2819649.0049 | 2794077.3284 | 2700808.4363 | 2561826.8196
1047 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 350357.3 | 371325.8 | 20968.5 | 60 | 0 | 1258110 | 1258110 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1329111.36 | 1432539.3027 | 1270602 | 1528603.9007 | 1237892.1591 | 1229098.1908 | 1284557.7074
1048 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 518177 | 536518.3 | 18341.3 | 60 | 0 | 1100478 | 1100478 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1158657.984 | 1382304.8305 | 530982 | 646002.2013 | 711159.0569 | 480060.5409 | 1215195.8482
1049 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 694813.1 | 722666.1 | 27853 | 60 | 0 | 1671180 | 1671180 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2088491.328 | 2541202.6985 | 2715606 | 2647616.7695 | 2636452.1751 | 2526376.4464 | 2465450.8355
1050 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 907279.3 | 919770 | 12490.7 | 60 | 0 | 749442 | 749442 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 766200.96 | 752054.1743 | 714972 | 785812.6007 | 661368.2767 | 689554.7346 | 725640.3272
1051 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 70053.1 | 101750.8 | 31697.7 | 60 | 0 | 1901862 | 1901862 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1859476.224 | 1837006.5171 | 1401510 | 1411640.1073 | 1301431.6729 | 1235612.3209 | 1199610.0995
1052 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 43170.716 | 3507 | 3715.5651 | 3553.7906 | 3904.2091 | 3633.5474
1053 | 11 kV Spare | spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1054 | 11 kV Khaza Moinuddin | B889Z | 11 | 0 | 00000026 | 1 | 8000660 | 8420179 | 419519 | 1 | 0 | 419519 | 422037.4564 | Fatullah | Nandalalpur 33/11 kV | 89 | 579356.8008 | 656635.1076 | 680847.6789 | 682477.6462 | 727695.4191 | 676115.2751 | 672821.6526
1055 | 11 kV Chitashal | B489Q | 11 | 0 | 00000027 | 1 | 36082072 | 36567832 | 485760 | 1 | 0 | 485760 | 488676.1143 | Shyampur | Nandalalpur 33/11 kV | 89 | 626907.0404 | 735704.304 | 743621.9237 | 740092.1663 | 801503.5058 | 725908.576 | 676035.0889
1056 | 11 kV Local Feeder | B489G | 11 | 0 | 00000157 | 1.5 | 19190114 | 19311752 | 121638 | 1 | Estimated | 364898.52 | 367089.0787 | Shyampur | Nandalalpur 33/11 kV | 89 | 471911.02 | 670610.6986 | 650428.6635 | 670079.927 | 673810.7719 | 652026.96 | 610908.7086
1057 | 11 kV Rasel Germants | 0 | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1058 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 | 0 | 00000121 | 1 | 82827040 | 84659512 | 1832472 | 1 | 0 | 1832472 | 1843472.6956 | Matuail | Nandalalpur 33/11 kV | 89 | 2197883.0829 | 2409135.9772 | 2474142.3426 | 2710158.1798 | 2342109.1991 | 2438091.1118 | 2521439.5722
1059 | 11 kV Nandalalpur | B890X | 11 | 0 | 00000010 | 1 | 86980384 | 87569944 | 589560 | 1 | 0 | 589560 | 593099.2465 | Fatullah | Nandalalpur 33/11 kV | 89 | 845396.3918 | 817827.925 | 726019.9781 | 743459.691 | 869061.7913 | 928548.3765 | 892208.2473
1060 | 11 kV Sharif Bagh | B489SB | 11 | 0 | 00000132 | 1 | 78453808 | 79634888 | 1181080 | 1 | 0 | 1181080 | 1188170.2592 | Shyampur | Nandalalpur 33/11 kV | 89 | 1429052.9803 | 1697558.3187 | 1769871.618 | 1607397.0329 | 1797879.9406 | 1716982.5939 | 1682233.437
1061 | 11 kV Spare | spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1062 | 11 KV Nayamati | B890Y | 11 | 0 | 00000158 | 1 | 69477432 | 70338192 | 860760 | 1 | 0 | 860760 | 865927.3143 | Fatullah | Nandalalpur 33/11 kV | 89 | 1006892.0073 | 1138166.5842 | 1094447.1869 | 1160143.2858 | 1059913.8974 | 1145403.0364 | 1037983.1413
1063 | 11 kV Pulpar | B889S | 11 | 0 | 00000160 | 1 | 11257213 | 12265050 | 1007837 | 1 | 0 | 1007837 | 1013887.2469 | Fatullah | Nandalalpur 33/11 kV | 89 | 944347.6364 | 974125.8442 | 814027.697 | 905763.961 | 653442.1412 | 808373.695 | 916555.6279
1064 | 11 kV Shahi Bazar | B489X | 11 | 0 | 00000170 | 1 | 43910492 | 44378812 | 468320 | 1 | 0 | 468320 | 471131.4185 | Shyampur | Nandalalpur 33/11 kV | 89 | 593266.4637 | 769069.4058 | 789833.0592 | 884250.6672 | 830388.5657 | 784445.919 | 785444.6114
1065 | 11 kV Pagla Bazar | B890G | 11 | 0 | 00000060 | 1 | 52781312 | 53261828 | 480516 | 1 | 0 | 480516 | 483400.6336 | Fatullah | Nandalalpur 33/11 kV | 89 | 561438.012 | 651299.1372 | 675946.8632 | 703594.2894 | 679748.7175 | 834561.5067 | 783154.3223
1066 | 11 kV Delpara bazar | B489M | 11 | 0 | 00000063 | 1 | 85270552 | 86688752 | 1418200 | 1 | 0 | 1418200 | 1426713.738 | Shyampur | Nandalalpur 33/11 kV | 89 | 1432420.6462 | 1512147.634 | 1531851.518 | 1668168.7326 | 1521265.0516 | 1508132.7308 | 1527622.8486
1067 | 11 kV Bhuighor (Board mill) | E289C | 11 | 0 | 00000146 | 1 | 46505368 | 47129844 | 624476 | 1 | 0 | 624476 | 628224.8542 | Matuail | Nandalalpur 33/11 kV | 89 | 631758.0829 | 736149.3859 | 684221.3852 | 711807.7641 | 702632.7597 | 668462.9794 | 1074021.0416
1068 | 11 kV Spare | 0 | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1069 | 33/0.415 kV, 200 kVA AT-1 | 0 | 11 | 0 | 7803 | 1 | 2634 | 2659 | 25 | 100 | 0 | 2500 | 2515.008 | Shyampur | Nandalalpur 33/11 kV | 89 | 3407.7571 | 4811.696 | 5827.1281 | 5909.6952 | 6446.2091 | 6244.3055 | 5725.7228
1070 | 33/0.415 kV, 200 kVA AT-2 | 0 | 11 | 0 | 7805 | 1 | 78.2 | 83.8 | 5.6 | 100 | 0 | 560 | 563.3618 | Shyampur | Nandalalpur 33/11 kV | 89 | 711.6199 | 912.2174 | 1004.6773 | 100.1643 | 0 | 0 | 0
1071 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 67083281 | 67884811 | 801530 | 1 | 0 | 801530 | 818415.5629 | Postogola | Postogola 33/11KV S/S | 25 | 964969.6559 | 1255334.9139 | 1334586.3999 | 1219095.1394 | 1335055.4691 | 1307497.2614 | 1269812.3426
1072 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 594 | 1598.3 | 1004.3 | 1000 | 0 | 1004300 | 1025457.2503 | Jurain | Postogola 33/11KV S/S | 25 | 1204492.2718 | 1239052.6971 | 1255387.5265 | 1323367.1334 | 1374189.6942 | 1360936.1962 | 1367079.5822
1073 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 26047328 | 26505115 | 457787 | 1 | 0 | 457787 | 467431.0447 | Jurain | Postogola 33/11KV S/S | 25 | 407994.3823 | 537163.6113 | 519931.6597 | 537056.744 | 474949.556 | 542387.1952 | 435813.5436
1074 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 80275699 | 81261612 | 985913 | 1 | 0 | 985913 | 1006682.8975 | Postogola | Postogola 33/11KV S/S | 25 | 1282024.8716 | 1532425.7761 | 1609308.7492 | 1557430.4575 | 1587221.6201 | 1546887.4107 | 1509702.7057
1075 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 471377.73 | 479747.6 | 8369.87 | 60 | 0 | 502192.2 | 512771.7141 | Postogola | Postogola 33/11KV S/S | 25 | 575584.882 | 676389.0131 | 678803.9555 | 662617.3772 | 636891.4703 | 664686.4068 | 678488.3278
1076 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 941864.1 | 954801 | 12936.9 | 60 | 0 | 776214 | 792566.2392 | Postogola | Postogola 33/11KV S/S | 25 | 972773.5086 | 1191302.5568 | 1270287.67 | 1139734.1436 | 1267305.3443 | 1258808.5211 | 1186933.4512
1077 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 831587.6 | 844942.4 | 13354.8 | 60 | 0 | 801288 | 818168.4647 | Postogola | Postogola 33/11KV S/S | 25 | 1013780.9955 | 1266750.2722 | 1384014.8487 | 1419724.1658 | 1247409.4401 | 1227619.0196 | 1164704.2052
1078 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 528585.6 | 530111.3 | 1525.7 | 60 | 0 | 91542 | 93470.4845 | Postogola | Postogola 33/11KV S/S | 25 | 133370.1443 | 125848.0606 | 126732.5803 | 134717.5169 | 129509.8262 | 124992.5587 | 126222.4118
1079 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 927947.6 | 951343.8 | 23396.2 | 60 | 0 | 1403772 | 1433344.7925 | Postogola | Postogola 33/11KV S/S | 25 | 1390963.4921 | 1427602.3077 | 1330189.3065 | 1373424.2339 | 1052907.1287 | 1323292.4846 | 1331811.5849
1080 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 469020.9 | 482727.4 | 13706.5 | 60 | 0 | 822390 | 839715.0135 | Jurain | Postogola 33/11KV S/S | 25 | 1423612.5326 | 2449336.9799 | 2475377.6895 | 2446524.7479 | 2443876.2234 | 2429557.5202 | 2393972.4885
1081 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 47773398 | 48828389 | 1054991 | 1 | 0 | 1054991 | 1077216.1405 | Jurain | Postogola 33/11KV S/S | 25 | 2497097.0061 | 2454381.4966 | 2115704.7964 | 2221056.7969 | 2061497.5542 | 2071894.6482 | 1933992.5359
1082 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 17714.8 | 19406.2 | 1691.4 | 1000 | 0 | 1691400 | 1727032.1548 | Jurain | Postogola 33/11KV S/S | 25 | 2152168.1359 | 2435670.3328 | 2485795.0121 | 2477072.4328 | 2360182.711 | 2388027.6504 | 2351667.7366
1083 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 62312639 | 63349228 | 1036589 | 1 | 0 | 1036589 | 1058426.4718 | Postogola | Postogola 33/11KV S/S | 25 | 1360729.5194 | 1622380.5518 | 1682719.5891 | 1655098.2 | 1632466.5583 | 1639249.0712 | 1571920.5306
1084 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 53.1 | 135 | 81.9 | 1000 | 0 | 81900 | 83625.3597 | Postogola | Postogola 33/11KV S/S | 25 | 107674.3091 | 247810.5394 | 239121.4336 | 245164.3984 | 245637.4316 | 262708.1006 | 303872.8913
1085 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 11 | 0 | ELIB67385 | 1 | 585.41 | 624.41 | 39 | 80 | 0 | 3120 | 3185.728 | Postogola | Postogola 33/11KV S/S | 25 | 3713.2428 | 4606.8906 | 4570.7831 | 4670.5121 | 4307.9725 | 5751.9551 | 4375.6621
1086 | 11 kV Feeder-1 | 0 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1087 | 11 kV Feeder-2 | 0 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1088 | 11 kV Dholaikal RMU | A619R | 11 | 0 | DHK60970 | 1 | 354107.8 | 368780.4 | 14672.6 | 60 | 0 | 880356 | 902364.9 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1688724 | 1912589.3597 | 2044107.1526 | 2258178.5414 | 2013206.2605 | 1942348.072 | 1890634.7965
1089 | 11 kV Alom Gonj | A581A | 11 | 0 | DHK60894 | 1 | 520758.3 | 525772.1 | 5013.8 | 60 | 30 | 364898.52 | 374020.983 | Postogola | IG Gate GIS 33/11 kV | 87 | 577380 | 601965.5066 | 622652.7534 | 676806.1857 | 596654.2301 | 589855.3321 | 589628.102
1090 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 | 0 | DHK60895 | 1 | 650759.1 | 665360.2 | 14601.1 | 60 | 90 | 1094695.56 | 1122062.949 | Postogola | IG Gate GIS 33/11 kV | 87 | 1533942 | 1585262.0566 | 1935090.8799 | 1875565.0903 | 1850628.0181 | 1792355.2732 | 1711977.4089
1091 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 | 0 | DHK68133 | 1 | 3711.29 | 3727.47 | 16.18 | 60000 | 0 | 970800 | 995070 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1656000 | 1845366.1756 | 1846529.6992 | 2047321.2801 | 1803939.5949 | 1748762.5817 | 1815572.1775
1092 | 11 kV Doyaganj | B587Y | 11 | 0 | DHK68134 | 1 | 2488.28 | 2501.83 | 13.55 | 60000 | 0 | 813000 | 833325 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1512000 | 1596436.5035 | 1387958.4974 | 1645033.4081 | 1687142.9696 | 1819772.2117 | 1955417.8504
1093 | 11 kV Faridabad | A587F | 11 | 0 | DHK68140 | 1 | 857.46 | 868.15 | 10.69 | 60000 | 65 | 790613.46 | 810378.7965 | Postogola | IG Gate GIS 33/11 kV | 87 | 1123200 | 1253169.1806 | 1329183.0163 | 1411966.4378 | 1296128.1808 | 1292615.9757 | 1233789.9626
1094 | 11 kV Gandaria | A524D | 11 | 0 | DHK60969 | 1 | 503196.3 | 519989.5 | 16793.2 | 60 | 100 | 1216328.4 | 1246736.61 | Postogola | IG Gate GIS 33/11 kV | 87 | 1778304 | 1938857.8307 | 2106445.8973 | 2096887.3731 | 2186472.7241 | 2176408.4497 | 2008723.2675
1095 | 11 kV Walter Road | A687W | 11 | 0 | DHK68136 | 1 | 1075.44 | 1087.27 | 11.83 | 60000 | 0 | 709800 | 727545 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1269000 | 1348724.0914 | 2063264.286 | 1501529.2301 | 1391040.5522 | 1437042.3417 | 1402694.4766
1096 | 11 kV Murgitola Feeder (F-11) | B587G | 11 | 0 | DHK68138 | 1 | 4043.16 | 4062.72 | 19.56 | 60000 | 0 | 1173600 | 1202940 | Swamibag | IG Gate GIS 33/11 kV | 87 | 2049000 | 2352354.9699 | 2412855.9498 | 2416392.1157 | 2307519.2472 | 2337901.7997 | 2438521.0841
1097 | 11 kV Feeder-12 | 0 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1098 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 | 0 | DHK60899 | 1 | 777965.1 | 791930.4 | 13965.3 | 60 | 0 | 837918 | 858865.95 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1530696 | 1678266.8077 | 1754827.7038 | 1727816.5375 | 1778252.8009 | 1741101.9665 | 1809148.9629
1099 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 | 0 | DHK60967 | 1 | 228309.7 | 236326.9 | 8017.2 | 60 | 47 | 571674.348 | 585966.2067 | Postogola | IG Gate GIS 33/11 kV | 87 | 822432 | 935068.7084 | 1005323.9927 | 1010280.3195 | 1031522.1618 | 1006862.3928 | 984580.1304
1100 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB2774 | 1 | 285932 | 286965 | 1033 | 1 | 0 | 1033 | 1058.825 | Postogola | IG Gate GIS 33/11 kV | 87 | 1552 | 1538.8094 | 3608.1717 | 0 | 1665.5005 | 1667.9239 | 1718.3058
1101 | Nizambag | F1114Z | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 502225.92 | 504749.4737 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 234080.9166 | 1217190.9472 | 1180785.7325 | 1158100.6579 | 1095738.2283 | 1008260.1492 | 972380.6635
1102 | Merry Stopes | F1114P | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 60816.42 | 61122.0066 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 55077.8627 | 304297.7368 | 318812.1478 | 329144.3975 | 365246.0761 | 355856.5232 | 364642.7488
1103 | Mujibur Ghat | F1114V | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1344684.1447 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 275389.3137 | 1278050.4946 | 1298864.3057 | 1340958.6566 | 1217486.9203 | 1304807.2519 | 1337023.4124
1104 | Madrasa | F1114U | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 941673.6 | 946405.2632 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 330467.1764 | 1582348.2314 | 1653100.0255 | 1462863.989 | 1424459.6968 | 1542044.934 | 1701666.1612
1105 | Thana | F1114Q | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1520410.5 | 1528050.1645 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 247850.3823 | 1217190.9472 | 1298864.3057 | 1219053.3241 | 1217486.9203 | 1423426.093 | 1337023.4124
1106 | Al-Hera | 0 | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1107 | Waz Uddin School | F1114W | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 816117.12 | 820217.8947 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 192772.5196 | 852033.6631 | 1003667.8726 | 975242.6593 | 730492.1522 | 830331.8876 | 972380.6635
1108 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1109 | Bashundhara City | 0 | 33 | 0 | 660434 | 1 | 814.02 | 824.68 | 10.66 | 180000 | 0 | 1918800 | 1925027.8888 | Shere b.nagar | Moghbazar 132/33/11KV S/S |  | 1952470.6666 | 2191476.9852 | 2303155.9363 | 2253160.9458 | 2286948.2926 | 2480389.347 | 2161081.9864
1110 | 33 kV Apollo Ispat Feeder | 0 | 33 | DPDC | 7389486 | 1 | 4616.75 | 4641.55 | 24.8 | 240000 | 0 | 5952000 | 5981061.6729 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 5757883.9148 | 5345006.6439 | 5626849.4493 | 4868511.8333 | 6352475.5818 | 7317548.4229 | 5615154.9463
1111 | 33 kV Adamjee EPZ Feeder | 0 | 33 | DPDC | ABB03919 | 1 | 380367.7 | 384040.3 | 3672.6 | 2000 | 0 | 7345200 | 7381064.2136 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 9198984.9536 | 9835003.2885 | 9088565.8308 | 9139513.6232 | 7905743.5896 | 8068621.1441 | 8850787.3005
1112 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1022.36 | 1024.85 | 2.49 | 240000 | 0 | 597600 | 597600 | Siddirgonj | Demra 33/11KV S/S | 16 | 792000 | 799200 | 616800 | 492000 | 571200 | 446400 | 0
1113 | 33 kV ACI Pharmacuticles Feeder | 0 | 33 | 0 | DHKC4791 | 1 | 960.83 | 971.93 | 11.1 | 90000 | 0 | 999000 | 999000 | N.Gonj (East) | Khanpur 33/11KV S/S |  | 1583100 | 1440900 | 1206900 | 1225800 | 1291500 | 1045800 | 0
1114 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC | 0 | 1 | 9902.222 | 9905.803 | 3.581 | 1000 | From Customer End | 13605 | 13529.8748 | Matuail | Matuail 132/33 KV S/S | 41 | 7215.4751 | 8160.0632 | 8383.4623 | 9119.9454 | 10440.0638 | 10260.3419 | 10991.7418
1115 | 33 KV Shah Cement Feeder (F2) | 0 | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 0 | 108.9746 | 64646.4953 | 944204.0986 | 2494536.8881 | 923421.8011 | 1229303.7954
1116 | 33/0.415 KV Transformer AT-1 | 0 | 0.415 | DPDC | 2001123043108 | 1 | 6583.1 | 6601.2 | 18.1 | 160 | 0 | 2896 | 2898.2343 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 3710.9239 | 639.8509 | 0 | 0 | 0 | 0 | 0
1117 | 33/0.415 KV Transformer AT-2 | 0 | 0.415 | DPDC | 2001123043171 | 1 | 4786.1 | 4793.6 | 7.5 | 160 | 0 | 1200 | 1200.9258 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 0 | 3647.1499 | 6180.7322 | 7797.005 | 4755.5609 | 4035.644 | 2848.7249
1118 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 0 | 33 | Main | 041808902866 | 1 | 375.17 | 395.51 | 20.34 | 360000 | 0 | 7322400 | 7313177.5551 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 5005228.5182 | 6404881.1253 | 5779395.3475 | 7171154.3348 | 6850018.059 | 6815752.3123 | 6616060.3155
1119 | 33 kV Delta Agro Premier Cement (=H2) | 0 | 33 | Main | 041808902876 | 1 | 130.36 | 135.43 | 5.07 | 360000 | 0 | 1825200 | 1822901.19 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 2659365.4762 | 2937522.8571 | 2682130.383 | 2390384.7783 | 2530901.4092 | 2430058.343 | 2458012.5886
1120 | 33 kV Crown Cement-1 (=H3) | 0 | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
1121 | 33 kV Outgoing Feeder-4 (=H4) | 0 | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
1122 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 400185.2656 | 1006790.1928 | 1108090.8439
1123 | 33 kV Outgoing Feeder-6 (=H12) | 0 | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
1124 | 33 kV Crown Cement-2 (=H13) | 0 | 33 | Main | 041808902857 | 1 | 0.06 | 1.03 | 0.97 | 360000 | 0 | 349200 | 348760.1882 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
1125 | 33 kV Shah Cement VRM (=H14) | 0 | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 2277825.3993 | 11858183.3118 | 9272761.2883 | 10712537.375 | 10817421.0397
1126 | 11 KV Shahidbagh Feeder | 0 | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 278424 | 279780.4906 | Rajarbag | Santinagar Switching S/S |  | 407049.5473 | 492002.3987 | 599477.6789 | 597504.11 | 524779.3911 | 36416.7693 | -3994.0825
1127 | 11 Fortune(MogBazar)-new | 0 | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 104616 | 105125.6925 | Moghbazar | Santinagar Switching S/S |  | 104859.5814 | 122203.1256 | 123551.4515 | 107474.29 | 138756.0658 | 127666.1608 | 126229.899
1128 | Centerpoint-Kakrail | 0 | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 63600 | 63909.8612 | Kakrail | Santinagar Switching S/S |  | 63748.0823 | 61390.4591 | 62067.8095 | 43848 | 71600.1051 | 81766.8748 | 80846.9863
1129 | 11 KV Shyamoli O/H | 0 | 11 | 0 | DHK-15026 | 1 | 9229.09 | 9236.31 | 7.22 | 40000 | 0 | 288800 | 296020 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 378430 | 520290 | 602290 | 545300 | 584660 | 530950
1130 | 11 KV Nearest RMU | 0 | 11 | 0 | DHK-15027 | 1 | 3878 | 3880.96 | 2.96 | 40000 | 0 | 118400 | 121360 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 93070 | 157030 | 160310 | 164820 | 182450 | 165230
1131 | 11 KV Sher-e-bangla Nagar | 0 | 11 | 0 | DHK-15025 | 1 | 3984.04 | 3986.34 | 2.3 | 40000 | 0 | 92000 | 94300 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 144320 | 33620 | 51660 | 44280 | 49610 | 45920
1132 | Export to DESCO | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | -13837.5
1133 | 33/0.4 kV, 500 kVA AT-1 | 0 | 0.4 | 0 | 84.2659 | 1 | 325367 | 327184 | 1817 | 10 | 0 | 18170 | 18196.6014 | Paribag | Dhanmondi 33/11KV S/S |  | 19032.3858 | 23956.6474 | 23982.7488 | 25078.0786 | 24914.239 | 24707.6715
1134 | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0.4 | 0 | 84.2673 | 1 | 478776 | 478776 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S |  | 0 | 0 | 875.2094 | 10.0032 | 0 | 0
1135 | 33 KV Japan Genden City | 0 | 33 | 0 | DHK15681 | 1 | 750.68 | 804.83 | 54.15 | 18000 | 0 | 974700 | 974700 | Adabor | Japan Garden 33/11 KV |  | 1130040 | 1459800 | 1502640 | 1451700 | 1519200 | 1531620
1136 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKE6223 | 1 | 43796.79 | 43873.75 | 76.96 | 120 | 0 | 9235.2 | 9376.9111 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 21708.6097 | 23301.1673 | 23194.682 | 23415.1565 | 24412.3409 | 25361.4506
1137 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45670.4 | 76.5 | 120 | 0 | 9180 | 9320.8641 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
1138 | AT-1 | 0 | 0.415 | 0 | 0 | 1 | 1021.24 | 1075.8 | 54.56 | 80 | 0 | 4364.8 | 4390.1062 | Mugdapara | Madarteck 33/11KV S/S |  | 5672.1022 | 12954.5544 | 10606.4337 | 12573.2122 | 11708.7885 | 9611.7345
1139 | AT-2 | 0 | 0.415 | 0 | 63394003 | 1 | 549.25 | 607.81 | 58.56 | 80 | 0 | 4684.8 | 4711.9615 | Mugdapara | Madarteck 33/11KV S/S |  | 5966.9871 | 6056.6539 | 7745.9106 | 5649.4556 | 6156.9427 | 5477.3433
1140 | 33 kV Shahriar Steel Feeder | 0 | 33 | Main | 41812909534 | 1 | 652.26 | 672.83 | 20.57 | 360000 | 0 | 7405200 | 7356070.5709 | Kazla | Kazla 132/133 KV SS |  | 6734848.5186 | 7150980.086 | 7435235.4244 | 7833434.8553 | 7323524.0635 | 7145780.8426
1141 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 751.24 | 781.62 | 30.38 | 360000 | 0 | 10936800 | 10864240.3473 | Kazla | Kazla 132/133 KV SS |  | 10607025.8788 | 11059032.0485 | 10618692.0573 | 11070629.7471 | 10019388.2364 | 9121125.0936
1142 | 33kV Water Treatment Plant | 0 | 33 | Digital | 80379618 | 1 | 22050 | 22503 | 453 | 2000 | 0 | 906000 | 908496.4888 | Maniknagar | Maniknagar 132/33 KV SS |  | 468459.6796 | 526937.9846 | 686173.136 | 531621.6224 | 605078.9898 | 1062218.4705
1143 | Axuxilary -1 | 0 | 0.415 | 0 | AH14044078 | 1 | 424443.4 | 427058.1 | 2614.7 | 1 | 0 | 2614.7 | 2652.2304 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 3860.1372 | 5837.95 | 5955.9261 | 5213.2044 | 5831.4157 | 6475.0369
1144 | Axuxilary -2 | 0 | 0.415 | 0 | AH14044072 | 1 | 392725.7 | 397392.3 | 4666.6 | 1 | 0 | 4666.6 | 4733.5825 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 4282.1807 | 4943.482 | 4558.0495 | 4382.3431 | 5377.7142 | 4841.9103
1145 | 33 kV Rani RRM Feeder | 0 | 33 | Export | BD001809 | 1 | 772.98 | 786.83 | 13.85 | 240000 | 0 | 3324000 | 3325068.7934 | Shyampur | Shyampur 132/33KV S/S |  | 3021325.4164 | 2543674.3806 | 3093749.2487 | 2731257.9254 | 2448780.2928 | 2460914.9302
1146 | 33 kV Rahima Steel feeder | 0 | 33 | Export | BD001803 | 1 | 665.824 | 678.085 | 12.261 | 240000 | 0 | 2942640 | 2943586.1715 | Shyampur | Shyampur 132/33KV S/S |  | 2258252.921 | 387957.1282 | 1848762.9304 | 2408497.5549 | 1851141.9981 | 2281164.2763
1147 | 33 kV Salam Steel Feeder | 0 | 33 | Export | BD001849 | 1 | 1293.7049 | 1332.06 | 38.3551 | 240000 | 0 | 9205224 | 9208183.8323 | Shyampur | Shyampur 132/33KV S/S |  | 10104745.6836 | 9425654.7552 | 6942639.1851 | 9555598.3573 | 9761265.4061 | 10754060.1599
1148 | 33 kV Steel Famus feeder | 0 | 33 | Export | BD001806 | 1 | 161.8755 | 169.307 | 7.4315 | 240000 | 0 | 1783560 | 1784133.4829 | Shyampur | Shyampur 132/33KV S/S |  | 1983916.4772 | 1855188.4343 | 668060.7526 | 1802076.7353 | 1343089.4196 | 1442423.9509
1149 | 33 kV Rani Kamal Steel Feeder | 0 | 33 | Export | BD001829 | 1 | 1618.8289 | 1644.588 | 25.7591 | 240000 | 0 | 6182184 | 6184171.8091 | Shyampur | Shyampur 132/33KV S/S |  | 6138184.9168 | 5684015.7878 | 6636959.5785 | 7405918.76 | 5422228.9014 | 6501978.5941
1150 | 33 kV Chakda Steel Feeder | 0 | 33 | Export | BD001832 | 1 | 2517.3479 | 2557.981 | 40.6331 | 240000 | 0 | 9751944 | 9755079.6237 | Shyampur | Shyampur 132/33KV S/S |  | 9470500.1805 | 8724428.8439 | 9042995.7002 | 9230581.7605 | 8256580.7385 | 8640663.1605
1151 | 33 kV Akhter Steel Feeder | 0 | 33 | Export | BD001828 | 1 | 691.8555 | 691.909 | 0.0535 | 240000 | Prime Textile | 12840 | 12844.1286 | Fatullah | Shyampur 132/33KV S/S |  | 210535.038 | 1073036.1535 | 1039008.3182 | 1167285.0702 | 1147950.5517 | 674551.2513
1152 | Aux Tr-1 | 0 | 0.44kv | Export | DHKG9742 | 1.025 | 351.425 | 353.505 | 2.08 | 2400 | 0 | 5116.8 | 5116.8 | Fatullah | Shyampur 132/33KV S/S |  | 4324.68 | 5222.58 | 5052.84 | 5102.04 | 5527.62 | 10071.24
1153 | Aux Tr-2 | 0 | 0.44kv | Export | DHKG9743 | 1.025 | 124.447 | 129.438 | 4.991 | 2400 | 0 | 12277.86 | 12277.86 | Fatullah | Shyampur 132/33KV S/S |  | 15992.46 | 19576.68 | 17894.04 | 18044.1 | 19434 | 11042.94
1154 | 132 kV MI Cement Feeder [MICFL] | 0 | 132 | P. Cell | 08993599 | 1 | 375.928 | 400.459 | 24.531 | 480000 |  | 11776320 | 11776320 | Sytalakhya | MI CEMENT 132/33 kV |  | 12340320 | 12087360 | 11905920 | 10329120 | 10749120 | 9239520
1155 | 33 kV Shah Cement Feeder | 0 | 33 | 0 | 8993 841 | 1 | 17.275 | 41.562 | 24.287 | 36000 | 1484 | 874332 | 875816 | Sytalakhya | Madonganj 132/33 KV SS |  | 3079152 | 1948464 | 817416 | 2360592 | 3210156 | 3227092
1156 | 33 kV Mondol Para (Premire cement) Feeder | 0 | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS |  | 0 | 0 | 0 | 0 | 0 | 0
1157 | 11 kV Rayer Bazar Feeder | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 851429.88 | 853652.5785 | Dhanmondi | Jigatola Switching |  | 789619.7227 | 0 | 0 | 0 | 679467.069
1158 | 11 kV Madina Masjid Feeder | 0 | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1155511.98 | 1158528.4994 | Jigatola | Jigatola Switching |  | 1223910.5702 | 1463157.2985 | 1648779.5998 | 1579031.3193 | 1587392.6308
1159 | 11 kV Mitali | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 531658.14 | 533046.059 | Jigatola | Jigatola Switching |  | 1101165.3592 | 1474997.974 | 1417602.7084 | 1504281.4171 | 1520651.6572
1160 | 132 kV Shah Cement | 0 | 132 | EXPORT | 042003953369 | 1 | 33.07 | 45.6 | 12.53 | 1200000 |  | 15036000 | 15036000 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 13884000 | 15096000 | 10668000
1161 | 132 KV Metro Rail -1 | 0 | 132 | 0 | 42627805 | 1 | 0.239 | 0.239 | 0 | 480000 | 0 | 0 | 0 | Motijheel | Maniknagar 132/33 S/S |  | 111840
1162 | 132 KV Metro Rail -2 | 0 | 132 | 0 | 42627793 | 1 | 2.303 | 2.335 | 0.032 | 480000 | 0 | 15360 | 15360 | Motijheel | Maniknagar 132/33 S/S |  | 1104480

## SS List (hidden)
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.01.2024 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2324.72 | 2338.66 | 13.94 | 720000 | 10036800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2292.58 | 2306.73 | 14.15 | 720000 | 10188000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2046.44 | 2067.67 | 21.23 | 720000 | 15285600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1909.93 | 1933.02 | 23.09 | 480000 | 11083200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2191.32 | 2208.94 | 17.62 | 240000 | 0 | 4228800 | 4234991.0832 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2497.75 | 2516.17 | 18.42 | 240000 | 0 | 4420800 | 4427272.1767 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1527.47 | 1539.9 | 12.43 | 240000 | 0 | 2983200 | 2987567.4895 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 900.82 | 907.43 | 6.61 | 240000 | 0 | 1586400 | 1588722.5346 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1904.37 | 1914.8 | 10.43 | 240000 | 0 | 2503200 | 2506864.7558 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1246.56 | 1253.4 | 6.84 | 240000 | 0 | 1641600 | 1644003.349 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.44 | 462.91 | 0.47 | 240000 | 0 | 112800 | 112965.1424 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 464.63 | 475.63 | 11 | 240000 | 0 | 2640000 | 2643865.0349 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2193.69 | 2210.47 | 16.78 | 240000 | 0 | 4027200 | 4033095.9351 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1696.22 | 1715.95 | 19.73 | 240000 | 0 | 4735200 | 4742132.4672 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 766.57 | 774.65 | 8.08 | 240000 | 0 | 1939200 | 1942039.0438 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2072.37 | 2091.42 | 19.05 | 240000 | 0 | 4572000 | 4578693.5378 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1885.43 | 1904.68 | 19.25 | 240000 | From Downstream R Phase CT Problem | 5434560 | 5442516.3501 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 175.9 | 179.89 | 3.99 | 240000 | 0 | 957600 | 959001.9536 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1526.05 | 1545.91 | 19.86 | 240000 | 0 | 4766400 | 4773378.1449 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.01.2024 | Reading at 00.00hr 01.01.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2324.72 | 2338.66 | 13.94 | 720000 | 10036800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2292.58 | 2306.73 | 14.15 | 720000 | 10188000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2046.44 | 2067.67 | 21.23 | 720000 | 15285600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1909.93 | 1933.02 | 23.09 | 480000 | 11083200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2191.32 | 2208.94 | 17.62 | 240000 | 0 | 4228800 | 4234991.0832 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2497.75 | 2516.17 | 18.42 | 240000 | 0 | 4420800 | 4427272.1767 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1527.47 | 1539.9 | 12.43 | 240000 | 0 | 2983200 | 2987567.4895 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 900.82 | 907.43 | 6.61 | 240000 | 0 | 1586400 | 1588722.5346 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1904.37 | 1914.8 | 10.43 | 240000 | 0 | 2503200 | 2506864.7558 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1246.56 | 1253.4 | 6.84 | 240000 | 0 | 1641600 | 1644003.349 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.44 | 462.91 | 0.47 | 240000 | 0 | 112800 | 112965.1424 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 464.63 | 475.63 | 11 | 240000 | 0 | 2640000 | 2643865.0349 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2193.69 | 2210.47 | 16.78 | 240000 | 0 | 4027200 | 4033095.9351 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1696.22 | 1715.95 | 19.73 | 240000 | 0 | 4735200 | 4742132.4672 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 766.57 | 774.65 | 8.08 | 240000 | 0 | 1939200 | 1942039.0438 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2072.37 | 2091.42 | 19.05 | 240000 | 0 | 4572000 | 4578693.5378 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1885.43 | 1904.68 | 19.25 | 240000 | From Downstream R Phase CT Problem | 5434560 | 5442516.3501 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 175.9 | 179.89 | 3.99 | 240000 | 0 | 957600 | 959001.9536 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1526.05 | 1545.91 | 19.86 | 240000 | 0 | 4766400 | 4773378.1449 | 0 | Dhanmondi 132/33/11KV S/S