## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month February-2024 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 766 | 1 | 960000 | 2234.461 | 2234.461 | 0 |  | 0 | 1951.095 | 1951.095 | 0 |  | 0 | 0 | 0 | 0.95 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 667.558 | 667.558 | 0 | 0 |  | 379.591 | 379.591 | 0 | 0 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 438.262 | 455.625 | 17.363 |  | 16668480 | 197.029 | 205.234 | 8.205 |  | 7876800 | 16668480 | 7876800 | 0.9 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 175.272 | 180.139 | 4.867 |  | 4672320 | 57.8 | 59.042 | 1.242 |  | 1192320 | 4672320 | 1192320 | 0.97 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | HASNABAD –FATULLAH (New) |  | 132 | Exp | 5972 3848 | 1 | 960000 | 23.277 | 37.391 | 14.114 |  | 13549440 | 28.422 | 40.797 | 12.375 |  | 11880000 | 12494400 | 8914560 | 0.95 |  | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 3.862 | 4.961 | 1.099 | 1055040 |  | 2.615 | 5.704 | 3.089 | 2965440 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 1055040 | 34890240 |  |  | Total=> | 2965440 | 20949120 | 33835200 | 17983680 | 0.88 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 5972 3497 | 1 | 960000 | 0 | 3.12 | 3.12 |  | 5547840 | 0 | 0.593 | 0.593 |  | 2020800 | 5485440 | 1690560 | 0.96 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 0 | 0.065 | 0.065 | 62400 |  | 0 | 0.344 | 0.344 | 330240 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 62400 | 5547840 |  |  | Total=> | 330240 | 2020800 | 5485440 | 1690560 | 0.96 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 59723487(New) | 1 | 960000 | 0 | 11.816 | 11.816 |  | 15494400 | 0.05 | 3.454 | 3.404 |  | 4483200 | 13418880 | 3855360 | 0.96 | 0 | 0 |  | Old Meter 4151040 Units Added
|  |  | 132 | Imp |  | AMR | 960000 | 0.428 | 2.59 | 2.162 | 2075520 |  | 0.112 | 0.766 | 0.654 | 627840 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 393.184 | 408.474 | 15.29 |  | 14678400 | 149.502 | 154.16 | 4.658 |  | 4471680 | 14678400 | 4449600 | 0.96 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.408 | 4.408 | 0 | 0 |  | 30.631 | 30.654 | 0.023 | 22080
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 2075520 | 30172800 |  |  | Total=> | 649920 | 8954880 | 28097280 | 8304960 | 0.96
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 3046.435 | 3074.252 | 27.817 |  | 13352160 | 1229.048 | 1238.033 | 8.985 |  | 4312800 | 13352160 | 4312800 | 0.95 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8633.535 | 8660.035 | 26.5 |  | 12720000 | 5041.824 | 5055.1 | 13.276 |  | 6372480 | 12720000 | 6372480 | 0.89 | 0.005 | 63600
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8586.77 | 8613.4 | 26.63 |  | 12782400 | 5001.812 | 5015.16 | 13.348 |  | 6407040 | 12782400 | 6407040 | 0.89 | 0.005 | 63912
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 420.52 | 435.983 | 15.463 |  | 7422240 | 79.297 | 81.584 | 2.287 |  | 1097760 | 7422240 | 1097760 | 0.99 | 0 | 0
[10 empty] | Total=> | 0 | 46276800 |  |  | Total=> | 0 | 18190080 | 46276800 | 18190080 | 0.93
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 59723530-new | 1 | 960000 | 17.711 | 45.0887 | 27.3777 |  | 26282582.4 | 7.187 | 19.97 | 12.783 |  | 12271699.2 | 26282582.4 | 12271699.2 | 0.91 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 59723531-new | 1 | 960000 | 11.007 | 38.1403 | 27.1333 |  | 26047996.8 | 4.551 | 17.2599 | 12.7089 |  | 12200534.4 | 26047996.8 | 12200534.4 | 0.91 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 59723527 | 1 | 1440000 | 11.66 | 19.6365 | 7.9765 |  | 11486203.2 | 0.03 | 0.20628 | 0.17628 |  | 253843.2 | 11485425.6 | -1270785.6 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0.00054 | 0.00054 | 777.6 |  | 1.621 | 2.6798 | 1.0588 | 1524628.8 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 59723528 | 1 | 1440000 | 0 | 0.40918 | 0.40918 |  | 589219.2 | 0 | 0.01368 | 0.01368 |  | 19699.2 | 589219.2 | -106041.6 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0 | 0.08732 | 0.08732 | 125740.8 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 59723529-new | 1 | 1440000 | 19.763 | 41.6618 | 21.8988 |  | 31534286.4 | 7.14 | 15.8862 | 8.7462 |  | 12594484.8 | 31534286.4 | 12594484.8 | 0.93 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 777.6 | 95940288 |  |  | Total=> | 1650369.6 | 37340260.8 | 95939510.4 | 35689891.2 | 0.94 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993631 | 1 | 960000 | 5990.061 | 6012.753 | 22.692 |  | 21784320 | 3043.893 | 3053.071 | 9.178 |  | 8810880 | 21784320 | 8810880 | 0.93 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993659 | 1 | 960000 | 5095.586 | 5112.965 | 17.379 |  | 16683840 | 2578.675 | 2585.581 | 6.906 |  | 6629760 | 16683840 | 6629760 | 0.93 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993659 | 1 | 960000 | 4467.512 | 4478.623 | 11.111 |  | 10666560 | 1776.313 | 1777.281 | 0.968 |  | 929280 | 10666560 | 929280 | 1 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.561 | 1.561 | 0 | 0 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993660-old 59723872-new | 1 | 960000 | 7.475 | 17.691 | 10.216 |  | 9807360 | 0.92 | 1.198 | 0.278 |  | 266880 | 9807360 | 256320 | 1 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.236 | 0.247 | 0.011 | 10560 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 50146667 | 1 | 960000 | 1919.913 | 1935.541 | 15.628 |  | 15002880 | 704.876 | 710.451 | 5.575 |  | 5352000 | 15002880 | 5352000 | 0.94 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 50146668 | AMR | 960000 | 1713.054 | 1728.469 | 15.415 |  | 14798400 | 729.996 | 735.538 | 5.542 |  | 5320320 | 14798400 | 5320320 | 0.94 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 42627810 | 1 | 960000 | 250.518 | 268.606 | 18.088 |  | 17364480 | 4.508 | 5.034 | 0.526 |  | 504960 | 17364480 | 504960 | 1 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 73.871 | 74.678 | 0.807 | 774720 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 42627812 | 1 | 960000 | 253.056 | 271.08 | 18.024 |  | 17303040 | 3.133 | 3.395 | 0.262 |  | 251520 | 17303040 | 251520 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0.001 | 0.001 | 0 | 0 |  | 78.969 | 80.023 | 1.054 | 1011840
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 0 | 123410880 |  |  | Total=> | 1797120 | 28065600 | 123410880 | 26268480 | 0.98 |  | 0 |  |  |  |  | 10434240
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3415.423 | 3451.422 | 35.999 |  | 69118080 | 1697.516 | 1709.112 | 11.596 |  | 22264320 | 69118080 | 22264320 | 0.95 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3406.368 | 3427.255 | 20.887 |  | 40103040 | 1694.214 | 1700.911 | 6.697 |  | 12858240 | 40103040 | 12858240 | 0.95 | 0 | 0
[10 empty] | Total=> |  | 109221120 |  |  | Total=> | 0 | 35122560 | 109221120 | 35122560 | 0.95
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1669.918 | 1703.709 | 33.791 |  | 64878720 | 799.693 | 812.996 | 13.303 |  | 25541760 | 64878720 | 25541760 | 0.95 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
|  |  | Calculated Unit for 230/132kV T-1 due to R-phase PT Missing | [8 empty] | 0 |  |  |  |  | 0
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1760.133 | 1793.761 | 33.628 |  | 64565760 | 840.177 | 853.525 | 13.348 |  | 25628160 | 64565760 | 25628160 | 0.95 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 129444480 |  |  | Total=> | 0 | 51169920 | 129444480 | 51169920 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 1071.17 | 1089.136 | 17.966 |  | 25871040 | 220.633 | 221.058 | 0.425 |  | 612000 | 25859520 | -295200 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.029 | 0.008 | 11520 |  | 2.994 | 3.624 | 0.63 | 907200
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 805.688 | 833.164 | 27.476 |  | 39565440 | 343.1 | 355.577 | 12.477 |  | 17966880 | 39565440 | 17966880 | 0.91 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.838 | 0.838 | 0 | 0 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 11520 | 65436480 |  |  | Total=> | 907200 | 18578880 | 65424960 | 17671680 | 0.97
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 331.961 | 347.483 | 15.522 |  | 14901120 | 83.281 | 87.178 | 3.897 |  | 3741120 | 14901120 | 3741120 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 277.138 | 299.056 | 21.918 |  | 21041280 | 62.844 | 67.653 | 4.809 |  | 4616640 | 21041280 | 4616640 | 0.98 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 36.313 | 37.711 | 1.398 |  | 1342080 | 16.341 | 16.975 | 0.634 |  | 608640 | -29112000 | -20410560 | 0.95 | 0 | 0 | Loop PFC is Considered
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 182.56 | 214.283 | 31.723 | 30454080 |  | 132.38 | 154.275 | 21.895 | 21019200
[10 empty] | Total=> | 30454080 | 37284480 |  |  | Total=> | 21019200 | 8966400 | 6830400 | -12052800 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 33659337.6 | 677625408 |  |  |  | 29319489.6 | 229358500.8
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 643966070.4 |  |  |  |  | 200039011.2 | 643966070.4 | 200039011.2 | 0.95 |  | 127512 |  | 0.95499
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC Unit
[8 empty] | 643966070.4 |  | 200039011.2 |  | 0.95 | 127512
[8 empty] | PDB (Unit+PFC) |  | 644093582.4 |  | KWH
[8 empty] | PGCB Unit |  | 643966070.4 |  | KWH
33 KV LEVEL | [10 empty] | Month February-2024
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
4 | Shah Cement | Madanganj 132/33 kV | 33 | Exp | 8993 841 | 1 | 36000 | 39602.522 | 39602.522 | 0 |  | 0 | 10453.354 | 10453.354 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 3585
| Shah Cement (new) |  | 33 | Exp | 5050 1238 | 1 | 36000 | 96.731 | 198.152 | 101.421 |  | 3651156 | 28.552 | 55.149 | 26.597 |  | 957492 | 3651156 | 957492 | 0.96729 | 0 | 0 | 3585
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 3651156 |  |  | Total=> | 0 | 957492 | 3651156 | 957492 | 0.96729 |  | 0 | 3585
6 | Jigatala (JP garden) | Kallyanpur
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.581 | 4.837 | 3.256 |  | 586080 | 0.104 | 0.319 | 0.215 |  | 38700 | 586080 | 38700 | 0.99783 | 0 | 0 | 198
| Shere Bangla |  | 33 | Exp | 59723 485 | 1 | 180000 | 1.39 | 1.39 | 0 |  | 0 | 0.003 | 0.003 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Satmosjid-1 |  | 33 | Exp | 59723 483 | 1 | 180000 | 13.502 | 18.567 | 5.065 |  | 911700 | 1.754 | 2.566 | 0.812 |  | 146160 | 911700 | 146160 | 0.98739 | 0 | 0 | 308
| Satmosjid-2 |  | 33 | Exp | 59723 851 | 1 | 180000 | 59.739 | 87.514 | 27.775 |  | 4999500 | 23.501 | 35.219 | 11.718 |  | 2109240 | 4999500 | 2109240 | 0.92136 | 0 | 0 | 1691.4999
| Kallayanpur T3 |  | 33 | Exp | 59723 486 | 1 | 180000 | 50.675 | 60.668 | 9.993 |  | 1798740 | 22.529 | 26.695 | 4.166 |  | 749880 | 1798740 | 749880 | 0.923 | 0 | 0 | 608
| Kallayanpur T4 |  | 33 | Exp | 59723 875 | 1 | 180000 | 93.245 | 132.941 | 39.696 |  | 7145280 | 36.202 | 51.47 | 15.268 |  | 2748240 | 7145280 | 2748240 | 0.93334 | 0 | 0 | 2417.4999
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 187.412 | 188.853 | 1.441 |  | 259380 | 52.986 | 53.246 | 0.26 |  | 46800 | 259380 | 46800 | 0.98411 | 0 |  | 88.4999 | T-5 has been used by DESCO
| Exp to Desco at 11 KV |  | 33 | Exp |  | 1 |  |  |  |  | 2681400 |  |  |  |  | 297250 |  | -2681400 | -297250 | 0 | 0 | 0
| Lalmatia |  | 33 | Exp | 59723 850 | 1 | 180000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
[10 empty] | Total=> | 2681400 | 15700680 |  |  | Total=> | 297250 | 5839020 | 13019280 | 5541770 | 0.92011 |  | 0 | 5311.4997
SATMOSJID 132/33KV SS | [17 empty] | 15700680 | 5839020
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3362.081 | 3390.442 | 28.361 |  | 21270750 | 1673.736 | 1687.313 | 13.577 |  | 10182750 | 21270750 | 10182750 | 0.90197 | 0 | 0 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 3005.354 | 3034.23 | 28.876 |  | 21657000 | 1471.344 | 1485.144 | 13.8 |  | 10350000 | 21657000 | 10350000 | 0.90226 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 42927750 |  |  | Total=> | 0 | 20532750 | 42927750 | 20532750 | 0.90212 | 0 | 0 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1 | 180000 | 2024.763 | 2034.166 | 9.403 |  | 1692540 | 664.787 | 665.639 | 0.852 |  | 153360 | 1692540 | 153360 | 0.99592 | 0 | 0 | 10808.12
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1 | 180000 | 739.454 | 747.197 | 7.743 |  | 1393740 | 50.782 | 50.869 | 0.087 |  | 15660 | 1393740 | 15660 | 0.99994 | 0 | 0 | 8900.06
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1 | 180000 | 111.818 | 113.188 | 1.37 |  | 246600 | 4.16 | 4.16 | 0 |  | 0 | 246600 | 0 | 0 | 0 | 0 | 1574.72
19 | Monipuripara-1 |  |  |  |  | 1 | 180000 | 1186.857 | 1186.857 | 0 |  | 0 | 488.766 | 488.766 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Monipuripara-2 |  |  |  |  | 1 | 180000 | 930.081 | 964.575 | 34.494 |  | 6208920 | 329.504 | 342.406 | 12.902 |  | 2322360 | 6208920 | 2322360 | 0.93663 | 0 | 0 | 39648.53
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 9541800 |  |  | Total=> | 0 | 2491380 | 9541800 | 2491380 | 0.96756 |  | 0 | 60931.43
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 428437 | 434808.3 | 6371.3 |  | 6530.5825 | 276169.5 | 278990.9 | 2821.4 |  | 2891.935 | 6530.5825 | 2891.935 | 0.91436 | 0 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 402099 | 405236.1 | 3137.1 |  | 3215.5275 | 140020.7 | 140905 | 884.3 |  | 906.4075 | 3215.5275 | 906.4075 | 0.96249 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 9746.11 |  |  | Total=> | 0 | 3798.3425 | 9746.11 | 3798.3425 | 0.93174 |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 355.623 | 357.514 | 1.891 |  | 4651.86 | 228.991 | 230.522 | 1.531 |  | 3766.26 | 4651.86 | 3766.26 | 0.77721 | 0.12 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 133.786 | 137.425 | 3.639 |  | 8951.94 | 75.884 | 78.442 | 2.558 |  | 6292.68 | 8951.94 | 6292.68 | 0.8181 | 0.07 | 0 | 0
[10 empty] | Total=> | 0 | 13603.8 |  |  | Total=> | 0 | 10058.94 | 13603.8 | 10058.94 | 0.80406 |  | 0 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 2681400 | 71844735.91 |  |  |  | 297250 | 29834499.2825 | [5 empty] | 69827.9297 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 69163335.91 |  |  |  |  | 29537249.2825 | 69163335.91 | 29537249.2825 | 0.91965 |  | 0 |  | Total PFC Unit
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 422710 |  |  | 69586045.91
[8 empty] | 33 KV TOTAL | [18 empty] | 2681400
[8 empty] | KWH |  | KVARH |  | PF | PFC | [13 empty] | 422710
[8 empty] | 69163335.91 |  | 29537249.2825 |  | 0.91965 | 0 | [13 empty] | 69586045.91
69655873.8397
[8 empty] | PDB (Unit+PFC) |  | 69163335.91 |  | KWH
[8 empty] | PGCB Unit |  | 69163335.91 |  | KWH
11 KV LEVEL | [10 empty] | Month February-2024
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865)
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 15026 | 1 | 40000 | 9242.88 | 9249.79 | 6.91 |  | 276400 | 3483.49 | 3486.15 | 2.66 |  | 106400 | 283310 | 109060 | 0.93324 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 15027 | 1 | 40000 | 3882.98 | 3885.65 | 2.67 |  | 106800 | 1263.82 | 1263.89 | 0.07 |  | 2800 | 109470 | 2870 | 0.99966 | 1
3a | PD Betar |  | 11 | Imp | 2612100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 645015020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 645015020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 15025 | 1 | 40000 | 3987.09 | 3987.82 | 0.73 |  | 29200 | 1897.37 | 1897.91 | 0.54 |  | 21600 | 29930 | 22140 | 0.80395 | 1.1195
5 | BICC - U/G |  | 11 | Exp | 15024 | 1 | 40000 | 1038.93 | 1038.93 | 0 |  | 0 | 297.34 | 297.34 | 0 |  | 0 | 0 | 0 | 0 | 1
6 | NEC |  | 11 | Exp | 15023 | 1 | 40000 | 431.72 | 431.72 | 0 |  | 0 | 56.32 | 56.32 | 0 |  | 0 | 0 | 0 | 0 | 1
7 | Manikmia Avenue |  | 11 | Exp | 76026327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 412400 |  |  |  | 0 | 130800 | 422710 | 134070 | 0.9532
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 412400 |  |  |  | 0 | 130800
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 412400 |  |  |  |  | 130800
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 422710 |  |  |  |  | 134070 | 422710 | 134070 | 0.9532 |  | 0 |  | 0.9532
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 422710 |  | 134070 |  | 0.9532 | 0
[8 empty] | PDB (Unit + PFC) |  | 422710 |  | KWH
[8 empty] | PGCB Unit |  | 422710 |  | KWH

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE Month February-2024
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2024) | Amount (Taka) | Remarks |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 643966070.4 | 8.4735 | 5456646498 |  |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 643966070.4 | 643966070.4 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 5456646498 | 5456646498 | 0
2a | 33kv | 69163335.91 | 8.56 | 592038155 |  |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 69163335.91 | 69163335.91 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 592038155 | 592038155 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 422710 | 8.56 | 3618398 |  |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 422710 | 422710 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 3618398 | 3618398 | 0
2c | Bus Loss Units (33kv) | 69827.9297 | 8.56 | 597724.49 |  |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 69827.9297 | 69827.9297 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 597724.49 | 597724.49 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 69655873.8397 |  | 596254277 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 69655873.8397 | 69655873.8397 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 596254277 | 596254277 | 0
4 | TOTAL 132kv & 33kv (1+3) | 713621944.2397 |  | 6052900775 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 713621944.2397 | 713621944.2397 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 6052900775 | 6052900775 | 0
5 | 132KV P.F.C | 127512 | 8.4735 | 1080473 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 127512 | 127512 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 1080473 | 1080473 | 0
6 | 33KV P.F.C | 0 | 8.56 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 127512 |  | 1080473 |  |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 127512 | 127512 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 1080473 | 1080473 | 0
8 | TOTAL Billed Amount => (4+7) | 713749456.2397 |  | 6053981248 |  |  |  | 10 | সর্বমোট (৬+৯) | 713749456.2397 | 713749456.2397 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 6053981248 | 6053981248 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 363238875 | Source Tax | [10 empty] | 11 | উৎস কর (মোট বিলের উপর ৬%) | 363238875 | 363238875 | -
10 | NET BILL TOTAL => (8-9) |  |  | 5690742373 |  | 5728268116 | , কমা চেইঞ্জার | [8 empty] | 12 | কর পরবর্তী মোট পরিশোধ যোগ্য বিল (১০-১১) | 5690742373 | 5690742373 | -
11*** | 24th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  |  | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 5690742373
"In word: Taka Five Hundred Sixty Nine Crore Seven Lac Forty Two Thousand Three Hundred Seventy Three" | [5 empty] | NET BILL TOTAL => (8-9)
5690742373
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | 31683869.1762 | 2021-10-01
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid | 30306309.6468 | 2021-11-01
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid | 28928750.1174 | 2021-12-01
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid | 27551190.588 | 2022-01-01
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid | 26173631.0586 | 2022-02-01
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid | 24796071.5292 | 2022-03-01
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid | 23418511.9998 | 2022-04-01
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid | 22040952.4704 | 2022-05-01
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid | 20663392.941 | 2022-06-01
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid | 19285833.4116 | 2022-07-01
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid | 17908273.8822 | 2022-08-01
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid | 16530714.3528 | 2022-09-01
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid | 15153154.8234 | 2022-10-01
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid | 13775595.294 | 2022-11-01
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid | 12398035.7646 | 2022-12-01
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid | 11020476.2352 | 2023-01-01
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid | 9642916.7058 | 2023-02-01
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid | 8265357.1764 | 2023-03-01
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid | 6887797.647 | 2023-04-01 |  | 366430834.8204
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid | 5510238.1176 | 2023-05-01 |  | 20971130269.73
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid | 4132678.5882 | 2023-06-01
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Paid | 2755119.0588 | 2023-07-01
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94 | Paid | 1377559.5294 | 2023-08-01 |  | 20604699434.9096
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0 | Certified For Payment | 380206430.1144
| Total | 3306142870.56
20984905865.024
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | 0 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [9 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[12 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE Month February-2024
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February 2024) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 643966070.4 | 0.3086 | 198727929.3254 |  | 203441554 | , কমা চেইঞ্জার | 1 | 132 †Kwf (GbvwR©) | 643966070.4 | 643966070.4 | 643966070.4 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 5456646498 | 198727929.3254 | 198727929.3254 | 0
2a | 33kv Level | 69163335.91 | 0.3144 | 21744952.8101 |  |  |  | 2 | 33 †Kwf (GbvwR©) | 69163335.91 | 69163335.91 | 69163335.91 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 592038155 | 21744952.8101 | 21744952.8101 | 0 |  | 33KV Amount (2+3+4) => | 21899806.8425
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 422710 | 0.3144 | 132900.024 |  |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 422710 | 422710 | 422710 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 3618398 | 132900.024 | 132900.024 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 69827.1897 | 0.3144 | 21953.2784 |  |  |  | 4 | 33 ‡Kwf evm jm | 69827.9297 | 69827.1897 | 69827.1897 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 597724.49 | 21954.0084 | 21953.2784 | 0.73 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 69655873.0997 | 0.3144 | 21899806.1125 |  |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 69655873.8397 | 69655873.0997 | 69655873.0997 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 596254277 | 21899806.8425 | 21899806.1125 | 0.73
4 | TOTAL=> (1+3) | 713621943.4997 |  | 220627735.438 |  |  |  | 6 | me©‡gvU (1+5) | 713621944.2397 | 713621943.4997 | 713621943.4997 | 0 |  |  | 6 | me©‡gvU (1+5) | 6052900775 | 220627736.168 | 220627735.438 | 0.73
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000 | [12 empty] | 298330160 | , কমা চেইঞ্জার
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 17th Installment ) |  |  | 25993419.79 |  |  |  | ‡gvU (GbvwR©) |  | 713552116.31 | 713552116.31 | 713552116.31 | 0 |  |  | ‡gvU (GbvwR©) |  | 6052303051 | 220605782.1595 | 21899806.1125 | 198705976.047
7 | Grand TOTAL=> (4-5+6) |  |  | 245121155.228
| CERTIFIED UNITS |  |  | 713621943.4997 |  | 227934973.6307 | , কমা চেইঞ্জার
| CERTIFIED TAKA |  |  | 220627735.438
| CERTIFIED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 17th Installment of Wheeling Charge Due) |  |  | 245121155.228
evsjv
In word: Taka Twenty Four Crore Fifty One Lac Twenty One Thousand One Hundred Fifty Five Only | [5 empty] | 245121155.228
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Certified by T&EA
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Certified by T&EA
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Certified by T&EA
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Certified by T&EA
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Certified by T&EA
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Certified by T&EA
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Certified by T&EA
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Certified by T&EA
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Certified by T&EA
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06 | Certified by T&EA
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27 | Certified by T&EA
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48 | Certified by T&EA
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69 | Certified by T&EA
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9 | Certified by T&EA
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11 | Certified by T&EA
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32 | Certified by T&EA
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53 | Current Certified Installment For Payment
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check
[6 empty] | Month February-2024 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 112840483.8 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 112742140.32 | Fatullah Grid | 28087200 | 98343.48 | 0.08715%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 0 |  |  |  | Shyampur Grid | 84654940.32
|  |  | 132 | Import |  | 0 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 16668480 | 21340800 | Postogola 132/33 KV Grid | 21298118.4 | Postogola Grid | 21298118.4 | 42681.6 | 0.2%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 4672320
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 13549440 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 1055040 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 1055040 | 34890240
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 5547840 | 72701524.8 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 72119236.728 | Ullon Grid | 17752060.728 | 582288.072 | 0.8009%
|  |  | 132 | Import |  | 62400 | 0 |  |  |  | Dhanmondi Grid | 46925568
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 62400 | 5547840 |  |  |  | DU Grid | 7441608
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 15494400 | 93522240 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 91819696 | Lalbagh Grid | 39648544 | 1702544 | 1.82%
|  |  | 132 | Import |  | 2075520 | 0 |  |  |  | Kamrangirchar Grid | 24436752
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 14678400 |  |  |  | Jigatola Grid | 27734400
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 2075520 | 30172800
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 13352160 | 38854560 | Sitalakhya 132/33 KV Grid | 38751396 | Sitalakhya Grid | 38751396 | 103164 | 0.2655%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 12720000
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 12782400
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 7422240 | 7422240 | Sitalakhya NOCS | 7422240 | Sitalakhya NOCS | 7422240 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 46276800
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 26282582.4 | 52330579.2 | Siddirganj 132/33 KV Grid | 52278248.6208 | Siddirganj Grid | 52278248.6208 | 52330.5792 | 0.1%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 26047996.8
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 11486203.2 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 777.6 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 589219.2
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 31534286.4 | 31534286.4 | Matuail 132/33 KV Grid | 31423674.313 | Matuail Grid | 31423674.313 | 110612.087 | 0.3508%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 777.6 | 95940288
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 21784320 | 38468160 | Moghbazar 132/33 KV Grid | 38352755.52 | Moghbazar Gird | 38352755.52 | 115404.48 | 0.3%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 16683840
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 10666560 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 9807360
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 15002880 | 29801280 | Madartek 132/33 KV Grid | 29801280 | Madartek Grid | 29801280 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 14798400
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 17364480 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 17303040
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 123410880
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 69118080 | 109221120 | Maniknagar 132/33 KV Grid | 109171752 | Kazla Grid | 43358400 | 49368 | 0.0452%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 40103040 |  |  |  | Motijheel Grid | 14054400
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 109221120 |  |  |  | Narinda Grid | 21152352
[11 empty] | Bangabhaban Grid | 3818400
[11 empty] | Maniknagar Grid | 26097000
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 64878720 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid |  | Metro Rail | 691200
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 64565760
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 129444480
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 25871040 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 11520 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 39565440
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 11520 | 65436480
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 14901120 | 35942400 | Charsyedpur 132/33 KV Grid | 35940000 | Charsyedpur Grid | 35940000 | 2400 | 0.006677%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 21041280
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 1342080 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 30454080 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 30454080 | 37284480 | 643979674.2 |  | 641120537.9018 |  | 641120537.9018 | 2859136.2982 | 0.444%
[9 empty] | 33 KV Transmission Loss |  | 69149732.11 | 69020712.3742 | 129019.7358 | 0.1866%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 422710 | 428040 | -5330 | -1.261%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 713552116.31 | 710569290.276 | 2982826.034 | 0.418%
[9 empty] | From Summary Sheet |  |  |  | 3937654.3715 | 0.5518%
[9 empty] | Mismatch in KWH |  |  |  | -954828.3374
| 33 KV LEVEL |  |  |  |  | Month February-2024 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | #REF! | #REF!
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 3651156 | 3651156 | Sitalakhya NOCS | 3654741 | Sitalakhya NOCS | 3654741 | -3585 | -0.09819%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 3651156
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 586080 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 586080 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 586080
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 911700 | 48838950 | Shatmasjid 132/33 KV Grid | 49368980.1 | Asadgate SS | 9895940.1 | -530030.1 | -1.085%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 4999500 |  |  |  | Lalmatia SS | 6749190
[11 empty] | Japan Garden SS | 10638000
[11 empty] | Jigatola Old SS | 1243200
[11 empty] | Shatmasjid SS | 11907000
[11 empty] | BGB SS | 8935650
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 1798740 | 6522000 | Adabor NOCS | 6687624.8 | Adabor NOCS | 6687624.8 | -165624.8 | -2.539%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 7145280
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 259380
| Export to Desco at 11 KV |  |  |  |  | 2681400 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 0 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 2681400 | 15700680
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 21270750 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 21657000
AGARGAON 132/33KV SS | [5 empty] | 0 | 42927750
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 1692540 | 3332880 | Sherebanglanagar 33/11 KV SS | 3105988.18 | Sherebanglanagar SS | 3105988.18 | 226891.82 | 6.808%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 1393740
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 246600
19 | Monipuripara-1 |  |  |  |  | 0 | 0 | 6208920 | Monipuripara 33/11 KV SS | 6193900 | Monipuripara SS | 6193900 | 15020 | 0.2419%
20 | Monipuripara-2 |  |  |  |  | 0 | 6208920
| Maniknagar 230/132 kv |  |  |  |  | 0 | 9541800
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 6530.5825 | 9746.11 | Maniknagar 33/11 KV SS | 9478.2942 | Maniknagar 33/11 KV SS | 9478.2942 | 267.8158 | 2.748%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 3215.5275
Shyampur 230/132 kv | [5 empty] | 0 | 9746.11
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 4651.86 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 8951.94
[6 empty] | 0 | 13603.8
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 2681400 | 71844735.91 | 69149732.11 |  | 69020712.3742 |  | 69020712.3742 | 129019.7358 | 0.1866%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 276400 | 422710 | Sherebanglanagar NOCS | 428040 | Sherebanglanagar NOCS | 428040 | -5330 | -1.261%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 106800
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 29200
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 0
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 412400
TOTAL => | [5 empty] | 0 | 412400 | 422710 |  | 428040 |  | 428040 | -5330 | -1.261%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 188.853 | 187.412 |  | 1.441 | 180000 | 259380 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 132.941 | 93.245 |  | 39.696 | 180000 | 7145280 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 996.18 | #REF!
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 60.668 | 50.675 |  | 9.993 | 180000 | 1798740 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9688.09 | #REF!
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4698.53 | #REF!
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 4509.5 | 4482.3 |  | 27.88 | 8000 | 223040 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 53472.8 | #REF!
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 42702.034 | #REF!
03 |  | 11 KV Bashir Uddin |  | 74819925 | 935.309 | 935.309 |  | 0 | 16000 | 0 | 0 | #DIV/0! | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 2510.39 | #REF!
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8491.99 | #REF!
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1135.27 | 1135.27 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9452.95 | #REF!
05 |  | 11 KV Lalkuthy |  | DHK15018 | 1111.39 | 1084.32 |  | 27.7468 | 40000 | 1109870 | 0 | 1 |  |  |  |  | 0 |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9891.73 | 9858.84 |  | 33.7122 | 40000 | 1348490 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [5 empty] | #REF!
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 53472.8 | 53300.91 |  | 176.1872 | 8000 | 1409498 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  | #REF!
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8491.99 | 8461.48 |  | 31.2728 | 40000 | 1250910 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  | #REF!
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2510.39 | 2456.54 |  | 55.1962 | 40000 | 2207850 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  | #REF!
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  | #REF!
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.705 | 3273.705 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  | #REF!
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9688.09 | 9682.86 |  | 5.3607 | 40000 | 214430 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  | #REF!
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9452.95 | 9445.51 |  | 7.626 | 40000 | 305040 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  | #REF!
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4698.53 | 4683.11 |  | 15.8055 | 40000 | 632220 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  | #REF!
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 996.18 | 996.05 |  | 0.13325 | 40000 | 5330 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 42702.034 | 42620.61 |  | 83.4596 | 8000 | 667676.8 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 2681400 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 6522000 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [140 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [180 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[143 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | February-2024 % of Loss | January-2024 % of Loss | December-2023 % of Loss | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.16086 | -0.321 | 0.32457 | 0.15752 | 0.36993 | 0.1982 | 0.22066 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.5754 | 1.7227 | 2.5014 | 2.8235 | 3.3831 | 4.7675 | 6.4099 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.0943 | 1.652 | 0.8681 | 1.8104 | 1.4562 | 0.087826 | 1.0278 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.67882 | 1.3456 | 0.90072 | 1.7413 | 0.57703 | 0.73688 | 0.95024 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 2.6069 | 0.8019 | 1.4757 | 0.58489 | 1.028 | 0.51858 | 1.0269 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.3904 | 1.4812 | 1.0456 | 1.0112 | -1.6675 | -0.51228 | -0.14892 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.19969 | 0.55961 | 0.1464 | 0.11776 | 0.40506 | 0.59878 | 0.032224 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.2543 | 0.78461 | -0.22179 | -0.0059747 | 0.78672 | 0.71164 | 0.1718 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.60289 | 0.73449 | 0.042288 | -0.22661 | 0.090354 | 1.8004 | 0.72315 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.6271 | 2.1383 | 1.3399 | -0.34635 | 1.7093 | 1.2924 | 1.7957 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.022102 | 0.18093 | 0 | 0.078999 | 0.012837 | 0.076849 | 0.070408 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.33697 | 0.86166 | 0.94329 | 0.71194 | 0.42244 | 0.67755 | 0.74731 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | -0.975 | 1.3845 | 1.6183 | 0.39893 | -0.035562 | 1.3133 | 1.1413 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 1.5823 | 1.5248 | 0.4872 | 0.23283 | 0.31121 | 1.418 | 1.5 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 1.8571 | 2.6951 | 0.081362 | 1.6403 | 0.39586 | 0.22128 | 3.0565 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.46891 | 1.5227 | 0.29485 | 1.1177 | 0.22363 | -0.15783 | 0.36408 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.037889 | 1.7632 | 1.8414 | -0.75805 | 0.86271 | -0.5535 | -0.24021 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 0.17082 | 0.31348 | 1.1299 | -0.36418 | 0.10052 | -0.025203 | 0.21781 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.36227 | 0.71139 | -0.42032 | -0.086911 | -0.2611 | 0.97617 | -0.13914 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.3215 | 1.9485 | 1.5345 | 1.8667 | 1.1968 | 2.1342 | 2.1711 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 1.101 | 0.42175 | 0.1395 | 0.31895 | 0.16255 | -0.50074 | 0.12321 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | -0.66481 | 0.44571 | 0.48586 | 0.11321 | 0.07333 | 0.10551 | 0.1185 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.66628 | 0 | 0.93209 | -0.53789 | -0.043971 | -0.075665 | -0.064901 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 0.044131 | 2.0988 | 1.8143 | 1.8226 | 1.1357 | 2.0237 | 1.9508 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.43175 | 0.44157 | 1.8269 | 0.93812 | 0.5119 | 0.40513 | -1.985 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.064853 | 0.10366 | 0.11727 | 0.21759 | 0.14868 | 0.41233 | 0.10871 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 0.545 | 0.055917 | 2.2403 | -0.06039 | 1.5455 | 1.2197 | 1.7549 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 1.0914 | 0.32652 | 2.5706 | 0.85 | 0.85 | 1 | 1 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -2.4374 | -0.59266 | 1.6282 | -2.4815 | 2.0082 | -2.831 | -2.6717 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.1651 | 0.98996 | 1.2091 | 1.3444 | 1.2163 | 0.86585 | 1.5712 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | 0.21823 | 2.7201 | 1.0212 | -0.32329 | 1.3885 | 1.3864 | 1.1808 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | -0.045279 | 0.91695 | 0.85829 | -0.09904 | 0.15826 | 0.3214 | 0.74913 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.10994 | 2.044 | 0.66098 | -0.86776 | 1.3314 | 0.41255 | 0.56541 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.75438 | 1.5754 | 0.5443 | 0.6468 | -0.78277 | 1.757 | 1.2174 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.54186 | 0.47249 | -0.01484 | 0.39969 | 1.2104 | 0.54824 | 0.90308 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.38158 | 0.96804 | -0.53825 | 0.30898 | 0.026513 | 0.047491 | -0.25931 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 2.0831 | -0.035386 | 0.40161 | -0.15046 | 0.063822 | 1.034 | -0.81695 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 1.4858 | 1.0791 | 0.67176 | 0.54646 | 1.0407 | 0.334 | 0.41807 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.93986 | 1.0449 | 0.71763 | 0.27825 | 0.23578 | 1.0938 | 1.7781 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 0.053253 | 1.4868 | 1.1187 | -0.40364 | 0.31408 | 0.18399 | 1.0713 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.28045 | -0.27701 | -0.074543 | -0.26271 | -0.092639 | -0.05005 | 0.074283 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | -0.058602 | 0.41974 | 0.26105 | 0.62337 | 0.24412 | 0.051628 | -0.13885 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.6657 | 3.6279 | 0.73163 | 0.92584 | 1.2666 | 0.69212 | 0.34882 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.49269 | 0.24196 | 0.50247 | 0.26743 | 0.070914 | 0.3138 | 0.22403 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
N-1 | 46 | Bosila-1 (Shopnodanga) 33/11 KV |  | 0.61029
SOUTH
| Sl. No. | Name of S/S | Page No. | February-2024 % of Loss | January-2024 % of Loss | December-2023 % of Loss | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.79864 | 0.42412 | 0.41839 | 0.65358 | 0.15556 | 0.20112 | 0.95272 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.16741 | 1.2262 | 0.64336 | 0.22332 | 0.15665 | 0.20537 | 0.20884 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.1323 | 1.399 | 1.5241 | 1.0652 | 1.1157 | 1.2591 | 1.2584 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 1.2845 | 1.1227 | 0.69983 | 0.53762 | 0.77964 | 0.65402 | 1.444 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | -0.013836 | 0.63229 | 0.27555 | -0.32773 | 0.17832 | 0.31771 | 1.0687 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | -0.31662 | 0.69717 | 1.4354 | -0.2497 | 0.24297 | 0.17031 | 0.10378 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | -0.16322 | -0.025765 | 0.14854 | 0.0012825 | 0.10878 | -0.085961 | 0.041539 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.56115 | 0.60395 | 0.57978 | 0.71204 | 0.43536 | 0.43971 | 1.0708 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.13267 | 0.537 | -0.66344 | 0.14942 | -0.13156 | -0.4174 | 0.13595 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 0.76269 | 0.82385 | 0.32549 | 1.1659 | 1.3565 | 2.1519 | 1.211 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.041452 | 0.085545 | 0.032147 | 0.014741 | -0.031653 | -0.01844 | 0.010028 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.39561 | 0.41741 | 0.11183 | 0.22189 | 0.79245 | 0.12531 | -0.42556 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.22086 | 0.95764 | 0 | -0.8 | -0.48244 | 0 | -1.9122 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | 0.13785 | 0.72094 | 0.46062 | -0.24353 | -1.0495e-13 | -0.04852 | -0.048314 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.8472 | 2.5658 | 2.1067 | 1.3882 | 1.8683 | 1.573 | 0.29445 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 0.095797 | 0.50022 | 1.4502 | 1.1022 | 0.43069 | 0.068963 | -0.86273 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.017899 | 0.12302 | 0.077152 | -0.02899 | -0.023304 | 0.076622 | 0.064233 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | -0.032828 | 0.35188 | 0.18042 | 0.23889 | 0.18888 | 0.15171 | 0.25381 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.1512 | 0.92424 | -0.35882 | 0.12376 | 1.5174 | 2.7774 | 1.2284 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.085785 | 0.23308 | 0.48827 | -0.078372 | -0.48766 | 0.66641 | -0.41499 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.73895 | 0.79191 | 1.1371 | 0.57715 | 0.64916 | 0.88184 | 0.57602 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.10112 | 0.11851 | 0.73689 | 0.2689 | 0.32352 | 0.80196 | -0.26653 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.67215 | 0.87125 | 0.64818 | 0.56141 | 0.25534 | 0.44829 | 1.0739 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.1458 | 0.93218 | 1.0581 | 0.9012 | 1.0829 | 1.112 | 1.1039 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.19937 | 0.06694 | -0.55219 | 0.21493 | 0.33276 | 0.71435 | 0.23019 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 0.62521 | 0.43713 | 1.1068 | 0.79088 | 1.0512 | 1.0599 | 0.74837 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 2.1679 | 0.78375 | 1.8988 | 1.095 | 1.1333 | 1.4904 | 1.4865 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 1.4998 | 0.91562 | 2.5 | 0 | 1.4383 | 2.0408 | 0.18209 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.0422 | 0.22497 | 0.46563 | 1.1359 | 1.4766 | 0.10496 | 0.096193 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | 1.8768 | 1.4759 | 1.1327 | 0.3109 | 1.2474 | -0.24532 | -0.64219 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.48467 | 0.28002 | 0.96474 | 0.49417 | 0.28876 | -0.62244 | 1.8284 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.92581 | 0.54649 | 0.60032 | 0.22815 | 0.24367 | 0.46773 | 0.16433 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | 0.51858 | 0 | 0.8586 | 2.1521 | 0.66653 | 0.56513 | -0.8103 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.4726 | 0.33137 | -0.037198 | 1.347 | 1.4676 | 1.9489 | 1.3703 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | 0.16192 | 0.46405 | 0.054939 | 0.45149 | 1.3208 | 0.33477 | -0.12622 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.051243 | -0.074912 | -0.031496 | -0.073934 | -0.057847 | -0.086839 | 0.038802 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.33871 | 0.33596 | 0.42912 | 0.23243 | 0.22785 | 0.18163 | 1.4646 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | 0.063999 | 3.3525 | 2.165 | 1.7361 | 1.179 | 0.4914 | 1.1051 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.068259 | 1.3032 | 0.91042 | -0.025332 | -0.044529 | -0.040721 | -0.12694 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.72651 | 2.2478 | 1.7823 | 0.5041 | -2.2501 | 3.468 | 0.40336 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.99741 | 1.1256 | 2.0579 | 0.35988 | 1.5164 | 1.7985 | 0.80075 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.010474 | -0.11516 | -0.12595 | 0.096563 | 0.12007 | 0.27405 | 0.15019 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.43131 | 0.7317 | 0.49516 | -0.40379 | -0.18029 | -0.41785 | -0.72448 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0.098188 | 0.0061427 | 0.16973 | 0 | 0 | 0 | 0 | 0 | 0.033974

## ALL SS Loss History
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68
|  | DPDC TOTAL SS | 89 | 89
NORTH
[7 empty] | HV Side |  |  |  | LV Side |  |  | % LOSS
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export / Import | XFR-Sending | XFR-Receiving | Feeder Total | Corrected Feeder Total | S_FT | R_FT | XS_FT | XR_FT
[7 empty] | S | R | EI | XS | XR | FT | CFT | %S | %R | %XS | %XR
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.16086 | 132 | 33 | 38468160 | 38642400 | 0 | 38642400 | 38342400 | 38291159.6 | 2026454.5597 | 0.46225 | 0.91729 | 0.91729 | 0.13382 | 2026454.5597 | 13288343.7587
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.5754 | 33 | 11 |  |  |  | 11735247.2338 | 11639700 | 10979134.612 | 11261889.199 | -100 | -100 | 6.8868 | 6.0166 | 11261889.199
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.0943 | 33 | 11 | 9460453.5434 | 0 | 0 | 9441600 | 9903400 | 9358049.426 | 9460453.5434 | 1.0943 | -100 | 0.89282 | 5.8276 | 9460453.5434
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.67882 | 33 | 11 | 6584686.7117 | 0 | 0 | 0 | 6749190 | 6703684.199 | 6749190 | -1.7751 | -100 | -100 | 0.67882 | 6749190
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 2.6069 | 33 | 11 | 13240464.6677 | 0 | 0 | 14297121 | 10409310 | 12904063.97 | 13240464.6677 | 2.6069 | -100 | 10.7955 | -19.3331 | 13240464.6677
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.3904 | 33 | 11 | 6315244.0748 | 5150880 | 0 | 5175900 | 6225120 | 6228640.2 | 6315244.0748 | 1.3904 | -17.3033 | -16.9016 | -0.056516 | 6315244.0748
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.19969 | 132 | 33 | 0 | 47329000 | 27232000 | 47304000 | 47095200 | 46832051 | 17454.7853 | -100 | 1.0611 | 1.0077 | 0.5619 | 17454.7853 | 8287536.0603
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.2543 | 33 | 11 |  |  |  | 8270081.275 | 8192728.8 | 8249103.8 | 8270081.275 | -100 | -100 | 0.2543 | -0.68341 | 8270081.275
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.60289 | 33 | 11 | 2741463.4061 | 2748600 | 0 | 2743200 | 2696000 | 2725034.382 | 2741463.4061 | 0.60289 | 0.86478 | 0.66662 | -1.0655 | 2741463.4061
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.6271 | 33 | 11 | 5420060.6016 | 0 | 0 | 0 | 5360400 | 5333283.7 | 5420060.6016 | 1.6271 | -100 | -100 | 0.50844 | 5420060.6016
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.022102 | 132 | 33 | 38034004.8 | 0 | 20097000 | 17937004.8 | 17787636 | 17748138 | 17752060.728 | 114.2986 | -100 | 1.0641 | 0.22255
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.33697 | 33 | 11 |  |  |  | 4555342.6082 | 4554336 | 4540043.844 | 4555342.6082 | -100 | -100 | 0.33697 | 0.3148 | 4555342.6082
N-1 | 13 | Kakrail 33/11KV S/S | 13 | -0.975 | 33 | 11 | 5781121.0774 | 4584600 | 0 | 0 | 5788445.168 | 5838041.7024 | 5781121.0774 | -0.975 | -21.4702 | -100 | -0.84954 | 5781121.0774
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 1.5823 | 33 | 11 | 4585738.9289 | 4697352 | 0 | 4588920 | 4461120 | 4517438.352 | 4588920 | 1.5119 | 3.9826 | 1.5823 | -1.2467 | 4588920
N-2 | 15 | Goran 33/11KV S/S | 15 | 1.8571 | 33 | 11 | 7320032.997 | 7338698 | 0 | 7332000 | 7712583 | 7186571.88 | 7320032.997 | 1.8571 | 2.1168 | 2.0236 | 7.3194 | 7320032.997
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.46891 | 33 | 11 | 6945166.6951 | 0 | 0 | 0 | 6921600 | 6912751.8477 | 6945166.6951 | 0.46891 | -100 | -100 | 0.128 | 6945166.6951
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.037889 | 33 | 11 |  |  |  | 11616781.3732 | 11907000 | 11911513.2 | 11907000 | -100 | -100 | -2.4743 | -0.037889 | 11907000
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 0.17082 | 33 | 11 | CFT: 1243200; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 1243200
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 0 | 33 | 11 | CFT: 7115664.8; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 7115664.8
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.36227 | 132 | 33 | CFT: 24436752; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.3215 | 132 | 33 | CFT: 15426312.4721; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 15426312.4721
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 1.101 | 132 | 33 | CFT: 9061873.1322; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9061873.1322
S-2 | 23 | Banshal 33/11KV S/S | 23 | -0.66481 | 132 | 33 | CFT: 5102527.8727; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 5102527.8727
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.66628 | 132 | 33 | CFT: 10638000; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11566260
N-1 | 25 | Azimpur 33/11 KV, | 25 | 0.044131 | 132 | 33 | CFT: 11062276.784; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11062276.784
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.43175 | 132 | 33 | CFT: 3105988.18; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3354162.9
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.064853 | 132 | 33 | CFT: 39648544; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 0.545 | 132 | 33 | CFT: 23521244.4618; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 23521244.4618
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 1.0914 | 132 | 33 | CFT: 9895940.1; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9895940.1
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -2.4374 | 132 | 33 | CFT: 48838950; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 31 | Banasree 33/11 SS | 31 | 1.1651 | 132 | 33 | CFT: 8823574.9628; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 8823574.9628
N-2 | 32 | Mugdhapara Hospital | 32 | 0.21823 | 132 | 33 | CFT: 9912980.2809; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9912980.2809
N-1 | 33 | DMC | 33 | -0.045279 | 132 | 33 | CFT: 4626519.8258; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 4626519.8258
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.10994 | 132 | 33 | CFT: 7946046.441; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 7946046.441
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.75438 | 132 | 33 | CFT: 3061300.8035; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3061300.8035
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.54186 | 132 | 33 | CFT: 7679330; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 7679330
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.38158 | 132 | 33 | CFT: 7441608; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 2.0831 | 132 | 33 | CFT: 969585.7143; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 969585.7143
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 1.4858 | 132 | 33 | CFT: 6193900; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 6193900
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.93986 | 132 | 33 | CFT: 12042810; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 12042810
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 0.053253 | 132 | 33 | CFT: 4017030.0527; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 4017030.0527
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.28045 | 132 | 33 | CFT: 27734400; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | -0.058602 | 132 | 33 | CFT: 11767500; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11767500
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.6657 | 132 | 33 | CFT: 3517108.6043; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3517108.6043
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.49269 | 132 | 33 | CFT: 5918400; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 5918400
N-1 | 46 | Bosila-1 (Shopnodanga) 33/11 KV |  | 0.61029 |  |  | CFT: 3113479.9006 | 3113479.9006
|  | SOUTH |  |  |  |  | S: HV Side; XR: LV Side | 0
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export | XFR-Sending | XFR-Receiving | Feeder Total | 0 |  |  |  |  | 0
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.79864 | 132 | 33 | CFT: 3818400; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3818400
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.16741 | 132 | 33 | CFT: 21152352; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.1323 | 132 | 33 | CFT: 9726656.1946; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9726656.1946
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 1.2845 | 132 | 33 | CFT: 7260102; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 7260102
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | -0.013836 | 132 | 33 | CFT: 1039856.1088; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 1731056.1088 | 8907422.2715
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | -0.31662 | 132 | 33 | CFT: 7176366.1627; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 7176366.1627
N-2 | 7 | Madarteck 132/33KV S/S | 6 | -0.16322 | 132 | 33 | CFT: 29801280; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.56115 | 132 | 33 | CFT: 11998384.6915; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11998384.6915
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.13267 | 132 | 33 | CFT: 16717791.0448; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 16717791.0448 | 40435482.9851
S-2 | 10 | Kazla 33/11KV S/S | 8 | 0.76269 | 132 | 33 | CFT: 23717691.9403; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 23717691.9403
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.041452 | 132 | 33 | CFT: 33229448.8828; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 33229448.8828 | 56877304.8652
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.39561 | 132 | 33 | CFT: 23647855.9824; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 23647855.9824
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.22086 | 132 | 33 | CFT: 16950968.016; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 16950968.016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | 0.13785 | 132 | 33 | CFT: 21298118.4; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.8472 | 132 | 33 | CFT: 11114099.3614; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11114099.3614
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 0.095797 | 132 | 33 | CFT: 10319515.3191; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 10319515.3191
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.017899 | 132 | 33 | CFT: 3536.6329; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3536.6329 | 9688954.9479
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | -0.032828 | 132 | 33 | CFT: 9685418.315; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9685418.315
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.1512 | 132 | 33 | CFT: 13515856.8066; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 13515856.8066
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.085785 | 132 | 33 | CFT: 13557420.3071; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 13557420.3071 | 22055544.2009
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.73895 | 132 | 33 | CFT: 8498123.8938; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 8498123.8938
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.10112 | 132 | 33 | CFT: 16206841; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 16790041
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.67215 | 132 | 33 | CFT: 10606184.0964; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 10606184.0964
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.1458 | 132 | 33 | CFT: 9793103.3308; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 10557203.3308
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.19937 | 132 | 33 | CFT: 8847.3181; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 8847.3181 | 12851959.997
S-1 | 26 | Matuail 33/11KV S/S | 23 | 0.62521 | 132 | 33 | CFT: 12843112.6789; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 12843112.6789
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 2.1679 | 132 | 33 | CFT: 12908664.2467; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 12908664.2467
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 1.4998 | 132 | 33 | CFT: 10415754; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 10415754
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.0422 | 132 | 33 | CFT: 5183100; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 5183100
N-1 | 30 | Mitford 33/11 kV | 29 | 1.8768 | 132 | 33 | CFT: 5237128.8; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 5237128.8
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.48467 | 132 | 33 | CFT: 3071549.7; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3071549.7
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.92581 | 132 | 33 | CFT: 11318458.518; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 11318458.518
S-1 | 33 | Dapa 33/11 kV | 32 | 0.51858 | 132 | 33 | CFT: 9715680; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 9715680
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.4726 | 132 | 33 | CFT: 12919973.3033; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 12919973.3033
S-1 | 35 | Amulia 33/11 kv | 34 | 0.16192 | 132 | 33 | CFT: 4573944; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 4573944
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.051243 | 132 | 33 | CFT: 28087200; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.33871 | 132 | 33 | CFT: 8023886.2414; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 8023886.2414
S-2 | 38 | P & T 33/11 KV SS | 37 | 0.063999 | 132 | 33 | CFT: 5316000; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 5316000
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.068259 | 132 | 33 | CFT: 14054400; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.72651 | 132 | 33 | CFT: 2887627.5768; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 2887627.5768
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.99741 | 132 | 33 | CFT: 4220000; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 4220000
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.010474 | 132 | 33 | CFT: 22478400; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.43131 | 132 | 33 | CFT: 22446093.7993; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 35802093.7993
S-1 | 44 | Shah CEMENT 132/33 kV | 43 | 0.098188 | 132 | 33 | CFT: 3654741; %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0! | 3654741
|  | MI CEMENT 132/33 kV |  | 0 |  |  | CFT: 7422240 | 7422240
709684289.8682
709684289.8682
0

## Linked_11KV
SL | Feeder_Name | FEEDER_NO | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | SUBSTN_CODE | January24_Consumption | December23_Consumption | November23_Consumption | October23_Consumption | September23_Consumption | August23_Consumption | July23_Consumption | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 13260786 | 14063189 | 802403 | 1 | 0 | 802403 | 804443.5112 | Paribag | Dhanmondi 33/11KV S/S | 1 | 777713.5417 | 852382.2989 | 1117275.2423 | 1327224.0724 | 1457854.4301 | 1314371.1616 | 1273734.3863 | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | C301M | 11 | 0 | HA021100463-02 | 1 | 55207202 | 56128592 | 921390 | 1 | 0 | 921390 | 923733.0952 | Paribag | Dhanmondi 33/11KV S/S | 1 | 815231.6219 | 981931.3334 | 1079510.4987 | 1506112.4428 | 1598079.2811 | 1562022.8871 | 1571851.4764 | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | C3011 | 11 | 0 | HA021101078-02 | 1 | 69217222 | 69991075 | 773853 | 1 | 0 | 773853 | 775820.9086 | Paribag | Dhanmondi 33/11KV S/S | 1 | 712701.4188 | 801409.6026 | 967771.1752 | 1200141.0854 | 2105982.2036 | 2198394.2713 | 2202528.7234 | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 | 0 | DHK60882 | 1 | 251184 | 255718.75 | 4534.75 | 60 | 0 | 272085 | 272776.9123 | Paribag | Dhanmondi 33/11KV S/S | 1 | 251395.7292 | 289302.7292 | 325387.5579 | 424694.4888 | 424650.6487 | 429515.8245 | 406161.3393 | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | C301P | 11 | 0 | DHK60889 | 1 | 301747.2 | 304740.12 | 2992.92 | 60 | 0 | 179575.2 | 180031.8598 | Paribag | Dhanmondi 33/11KV S/S | 1 | 159901.6429 | 151783.0121 | 122058.3971 | 224979.6606 | 224715.2737 | 240975.4757 | 236479.8549 | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 0 | 11 | 0 | DHK60890 | 1 | 735.54 | 740.01 | 4.47 | 60000 | 0 | 268200 | 268882.0327 | Paribag | Dhanmondi 33/11KV S/S | 1 | 260024.3032 | 282571.8907 | 343779.459 | 423304.2367 | 422384.6367 | 444161.7425 | 451511.4107 | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | D301H | 11 | 0 | DHK60880 | 1 | 588760.2 | 593555.75 | 4795.55 | 60 | 0 | 287733 | 288464.7052 | Ramna | Dhanmondi 33/11KV S/S | 1 | 228081.8293 | 234931.587 | 287616.8148 | 330665.314 | 381236.2759 | 740264.9629 | 797710.3468 | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 0 | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 kV TSC Feeder | D301U | 11 | 0 | DHK60873 | 1 | 974895.6 | 980153 | 5257.4 | 60 | 0 | 315444 | 316246.1742 | Ramna | Dhanmondi 33/11KV S/S | 1 | 313692.1099 | 346708.5258 | 436581.914 | 552858.9173 | 527789.8466 | 622520.63 | 596411.0072 | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | C301S | 11 | 0 | DHK60883 | 1 | 29299.7 | 29463.27 | 163.57 | 60 | 0 | 9814.2 | 9839.1575 | Paribag | Dhanmondi 33/11KV S/S | 1 | 9698.3018 | 10069.0183 | 10788.5554 | 14763.0376 | 14899.4821 | 7435.3517 | 6184.9227 | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 0 | 11 | 0 | DHK60871 | 1 | 585029.6 | 595526.6 | 10497 | 60 | 0 | 629820 | 631421.6326 | Paribag | Dhanmondi 33/11KV S/S | 1 | 629010.2788 | 659432.9925 | 837287.7716 | 1020090.0393 | 1178402.3777 | 1167367.0478 | 1168612.8044 | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | C301E | 11 | 0 | DHK60981 | 1 | 163626.2 | 174019 | 10392.8 | 60 | 0 | 623568 | 625153.7337 | Paribag | Dhanmondi 33/11KV S/S | 1 | 548154.2099 | 651559.893 | 749226.2334 | 894951.6314 | 961999.4403 | 1097238.176 | 1271574.285 | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | C301D | 11 | 0 | DHK61110 | 1 | 533225.9 | 548723 | 15497.1 | 60 | 0 | 929826 | 932190.548 | Paribag | Dhanmondi 33/11KV S/S | 1 | 864774.9192 | 1058898.0495 | 1248319.0123 | 1468536.7336 | 1572278.7706 | 1519703.9096 | 1444426.5973 | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 0 | 11 | 0 | DHK61115 | 1 | 483056.9 | 500073.3 | 17016.4 | 60 | 0 | 1020984 | 1023580.3628 | Paribag | Dhanmondi 33/11KV S/S | 1 | 935291.696 | 1073162.5419 | 1368467.8334 | 1667970.4775 | 1771267.2548 | 1745625.9685 | 1732224.4313 | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | D301M | 11 | 0 | DHK61107 | 1 | 558125.1 | 559437.2 | 1312.1 | 60 | 0 | 78726 | 78926.2003 | Ramna | Dhanmondi 33/11KV S/S | 1 | 57105.5699 | 69398.3393 | 102971.2474 | 132172.5149 | 123208.813 | 139745.6654 | 147111.9421 | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 0 | 11 | 0 | DHK61112 | 1 | 358275 | 360035.74 | 1760.74 | 60 | 0 | 105644.4 | 105913.0538 | Paribag | Dhanmondi 33/11KV S/S | 1 | 118304.4062 | 113070.0644 | 143833.6059 | 183722.5048 | 209615.174 | 205991.8784 | 207014.0635 | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | C601R | 11 | 0 | DHK61108 | 1 | 771587.6 | 779424.2 | 7836.6 | 60 | 0 | 470196 | 471391.7087 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 406645.9606 | 478064.9428 | 635092.6529 | 850234.9813 | 921150.1931 | 935875.2367 | 955769.4815 | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 0 | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 11 kV DPH Sw/S-1 | 0 | 11 | 0 | DHK60978 | 1 | 856428.3 | 865759 | 9330.7 | 60 | 0 | 559842 | 561265.6785 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 497685.3068 | 607586.4385 | 690742.9278 | 869594.4982 | 880434.4894 | 909712.3671 | 894673.7786 | 964542.5031 | 717844.627
20 | WASA Bhaban | C605M | 11 | 0 | 8536188 | 1.5 | 271216 | 271216 | 0 | 1000 | 808320 | 808320 | 813193.2995 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 837708.0289 | 897559.4039 | 933040.8402 | 1122893.6635 | 1128091.0061 | 1031848.2658 | 1051553.1772 | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 0 | 11 | 0 | 8536178 | 1.5 | 588513 | 589987 | 1474 | 44 | 0 | 97284 | 97870.5178 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 66551.249 | 92932.083 | 218864.9052 | 224818.1088 | 56030.9835 | 205730.3432 | 203697.4272 | 26163.5003 | 291323.9838
22 | Air Port Road (West) | D505A | 11 | 0 | 8536182 | 1.5 | 5221.7 | 5498.5 | 276.8 | 1000 | 0 | 415200 | 417703.2091 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 326379.7515 | 341744.4575 | 711222.6426 | 1042454.0487 | 996313.4361 | 1009777.8086 | 1128128.4372 | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | C172C | 11 | 0 | 8536193 | 1.5 | 32437.1 | 32438.3 | 1.2 | 1000 | 0 | 1800 | 1810.8521 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 21989.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | (UTC) Tower | D505U | 11 | 0 | DHK00183 | 1.5 | 18819.3 | 19208.7 | 389.4 | 444.44 | 0 | 259597.404 | 261162.4969 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 218658.8156 | 249800.8732 | 276538.0329 | 285253.3218 | 290292.9413 | 349161.1513 | 363430.7232 | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | C605O | 11 | 0 | 8536190 | 1.5 | 51744.1 | 51744.1 | 0 | 1000 | 15 | 147136.5 | 148023.5747 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 29643.4409 | 54954.1895 | 46976.984 | 0 | 0 | 110790.7123 | 63163.9823 | 0 | 0
26 | Panthopath | D505P | 11 | 0 | 8536184 | 1.5 | 40118.8 | 40657.8 | 539 | 1000 | 0 | 808500 | 813374.3847 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 750824.5302 | 791894.7388 | 929616.6174 | 1035454.7302 | 1172086.0871 | 1196734.0813 | 1204221.3334 | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | C605N | 11 | 0 | DHK00190 | 1.5 | 58023.1 | 58301.4 | 278.3 | 444.44 | 0 | 185531.478 | 186650.0331 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 174671.861 | 167260.1411 | 217096.7452 | 236270.9269 | 238706.8937 | 200780.8678 | 155748.3677 | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 0 | 11 | 0 | DHK00021 | 1.5 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Aux. Transformer, AT-1 | 0 | 11 | 0 | 85-12906 | 1.5 | 69663 | 69774 | 111 | 10 | 0 | 1665 | 1675.0382 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1752.7801 | 1694.7164 | 1765.989 | 2388.6563 | 2990.8959 | 2900.021 | 3641.847 | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 0 | 11 | 0 | 85-12909 | 1.5 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Police Bhaban | D315I | 11 | T-1 | DHK 00005 | 1 | 74685.2 | 74867.5 | 182.3 | 444.44 | 0 | 81021.412 | 82339.6968 | Ramna | New Ramna 33/11KV S/S | 15 | 74128.9984 | 76206.8169 | 98323.9544 | 113280.4639 | 112636.0604 | 117855.6107 | 121266.9463 | 121013.0538 | 111715.2077
32 | Baitul Mukarram (OLD Water Works) | 0 | 11 | T-1 | DHK 00010 | 1 | 17727 | 17727.5 | 0.5 | 444.44 | 0 | 222.22 | 225.8357 | Ramna | New Ramna 33/11KV S/S | 15 | 862.4929 | 765.6713 | 301881.114 | 0 | 0 | 0 | 0 | 0 | 0
33 | GPO | D3157 | 11 | T-1 | DHK 00060 | 1 | 1497.4 | 1929.2 | 431.8 | 444.44 | 0 | 191909.192 | 195031.712 | Ramna | New Ramna 33/11KV S/S | 15 | 162829.588 | 205875.5083 | 264367.4251 | 254768.0345 | 252148.1113 | 248107.5506 | 224260.1714 | 278965.4908 | 233730.721
34 | Culvert Road | D315C | 11 | T-1 | 8536184 | 1 | 40701.5 | 40858.8 | 157.3 | 444.44 | 277980.176 | 277980.176 | 282503.1415 | Ramna | New Ramna 33/11KV S/S | 15 | 230311.946 | 308370.1012 | 586507.5886 | 1175263.5465 | 1013459.3684 | 1052444.418 | 990314.9211 | 787025.6832 | 769934.2629
35 | Secretariat (East) | D315E | 11 | T-1 | DHK00059 | 1 | 81752.7 | 81753.2 | 0.5 | 444.44 | 0 | 222.22 | 225.8357 | Ramna | New Ramna 33/11KV S/S | 15 | 771.7042 | 1080.9478 | 7972.2125 | 1672.5368 | 765.313 | 950.0836 | 1673.5834 | 2240.1359 | 29358.1395
36 | Siddik Bazar | B615S | 11 | T-1 | DHK00076 | 1 | 50249.5 | 52733.6 | 2484.1 | 444.44 | 0 | 1104033.404 | 1121996.9333 | Bangshal | New Ramna 33/11KV S/S | 15 | 1067811.6528 | 1194222.0745 | 1547982.2206 | 1854662.4712 | 1902703.0751 | 1396125.2558 | 499406.3237 | 894134.2296 | 765262.7858
37 | Bokshi Bazar | D315X | 11 | T-1 | DHK 00206 | 1 | 93252.6 | 94143.4 | 890.8 | 444.44 | 0 | 395907.152 | 402348.8862 | Ramna | New Ramna 33/11KV S/S | 15 | 372869.3158 | 441657.2379 | 530285.0026 | 560480.6352 | 561829.7499 | 563173.3752 | 477921.1318 | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 0 | 11 | T-1 | DHK00198 | 1 | 52687 | 53404 | 717 | 444.44 | 0 | 318663.48 | 323848.3963 | Ramna | New Ramna 33/11KV S/S | 15 | 334329.4998 | 355136.3778 | 406494.2583 | 588235.7049 | 500739.7682 | 521233.9697 | 36728.3702 | 1058898.5083 | 1085933.5304
39 | TNT RMU | D315Z | 11 | T-1 | DHK 00207 | 1 | 66649.9 | 67482.5 | 832.6 | 444.44 | 0 | 370040.744 | 376061.6105 | Ramna | New Ramna 33/11KV S/S | 15 | 389211.2873 | 392023.72 | 391967.1155 | 395125.5127 | 407146.495 | 424144.4724 | 438569.3066 | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 0 | 11 | T-1 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35665.375
41 | Secretariat (West) | D315W | 11 | T-2 | DHK 00006 | 1.5 | 73641.9 | 73876.7 | 234.8 | 444.44 | 0 | 156531.768 | 159078.6683 | Ramna | New Ramna 33/11KV S/S | 15 | 161785.5176 | 169016.9913 | 331909.7812 | 504156.8291 | 472288.1335 | 522274.5375 | 534325.4145 | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 0 | 11 | T-2 | DHK00197 | 1.5 | 89267.5 | 89269.4 | 1.9 | 444.44 | 0 | 1266.654 | 1287.2635 | Ramna | New Ramna 33/11KV S/S | 15 | 1429.9225 | 21143.3381 | 3897.5261 | 12747.4425 | 1125.4602 | 1246464.4649 | 757545.2503 | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | D315A | 11 | T-2 | DHK00186 | 1.5 | 41257.6 | 42745.5 | 1487.9 | 444.44 | 0 | 991923.414 | 1008062.8218 | Ramna | New Ramna 33/11KV S/S | 15 | 950626.099 | 1057491.1911 | 977526.1249 | 1189218.8524 | 1357169.9895 | 1293561.4671 | 1334026.873 | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | D3153 | 11 | T-2 | DHK00030 | 1.5 | 57286.7 | 57543.4 | 256.7 | 444.44 | 0 | 171131.622 | 173916.0739 | Ramna | New Ramna 33/11KV S/S | 15 | 132506.152 | 193078.8884 | 172686.9812 | 222492.5951 | 223201.274 | 228427.247 | 210464.4166 | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | D3152 | 11 | T-2 | DHK 00008 | 1.5 | 649.9 | 689.2 | 39.3 | 444.44 | 0 | 26199.738 | 26626.0292 | Ramna | New Ramna 33/11KV S/S | 15 | 23287.3094 | 33530.9994 | 53280.9537 | 61024.9905 | 71264.1421 | 71075.3031 | 68978.774 | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 0 | 11 | T-2 | DHK00196 | 1.5 | 30367 | 30641.4 | 274.4 | 444.44 | 0 | 182931.504 | 185907.9497 | Motijheel | New Ramna 33/11KV S/S | 15 | 175403.8272 | 172389.5484 | 335231.5364 | 454930.0034 | 443071.1857 | 477711.0916 | 494476.0375 | 481492.0598 | 701782.0483
47 | Jail | B678Z | 11 | T-2 | DHK00009 | 1.5 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | Kosturi Bazar | D315K | 11 | T-3 | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 15 | 29524.1095 | 44943.217 | 0 | 254911.0541 | 109455.5914 | 110597.9648 | 782852.0054 | 108530.1819 | 101993.6695
49 | Kaptan Bazar | B124K | 11 | T-3 | HA021101251-02 | 1 | 8893370 | 9141543 | 248173 | 1 | 0 | 248173 | 252210.9783 | Narinda | New Ramna 33/11KV S/S | 15 | 333271.2853 | 270900.7155 | 367694.0766 | 419318.091 | 424171.1844 | 443349.7565 | 434935.9868 | 427872.7434 | 409490.3581
50 | G.T.V | D315G | 11 | T-3 | HA-021101054-02 | 1 | 74683932 | 75024680 | 340748 | 1 | 0 | 340748 | 346292.2495 | Ramna | New Ramna 33/11KV S/S | 15 | 354527.2958 | 373573.2004 | 423322.7388 | 579351.6265 | 620088.9847 | 609639.126 | 653967.7221 | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | B615K | 11 | T-3 | HA021100951-02 | 1 | 8786027 | 9258275 | 472248 | 1 | 0 | 472248 | 479931.8624 | Bangshal | New Ramna 33/11KV S/S | 15 | 330616.7097 | 306551.0668 | 320999.3644 | 441368.6747 | 366764.7103 | 373997.3699 | 641935.1027 | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.4 | T-3 | 2436 | 1 | 68252 | 68252 | 0 | 10 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 15 | 0 | 2644.9705 | 2870.0252 | 2847.8614 | 0 | 0 | 0 | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.4 | T-3 | 2437 | 1 | 90090 | 90303 | 213 | 10 | 0 | 2130 | 2164.6568 | Ramna | New Ramna 33/11KV S/S | 15 | 827.3206 | 91.2059 | 0 | 4943.0737 | 3443.9428 | 3735.9019 | 3663.8273 | 3672.2594 | 3624.4279
54 | Pioneer | D304P | 11 | 0 | 06604395 | 1 | 24342.07 | 24396.51 | 54.44 | 8000 | 0 | 435520 | 431273.701 | Ramna | Kakrail 33/11KV S/S | 4 | 423219.6512 | 477280.9094 | 570908.4836 | 784360.9682 | 828175.4667 | 850072.0555 | 872559.2 | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | D604L | 11 | 0 | DHK-00102 | 1 | 98876.5 | 100672.6 | 1796.1 | 444.444 | 0 | 798265.8684 | 790482.8147 | Rajarbag | Kakrail 33/11KV S/S | 4 | 772549.4723 | 842708.566 | 1050082.5289 | 1392792.0181 | 1485476.6819 | 1494821.3647 | 1589289.5218 | 1570646.0565 | 1456807.534
56 | Montri Para | C604B | 11 | 0 | DHK-00110 | 1 | 13080.9 | 13130.4 | 49.5 | 2222.22 | 0 | 109999.89 | 108927.3964 | Kakrail | Kakrail 33/11KV S/S | 4 | 127068.5046 | 115167.3103 | 51314.9581 | 167051.5164 | 197223.0332 | 196663.3629 | 206488.6824 | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 0 | 11 | 0 | 9119865 | 1 | 73065.6 | 73976.2 | 910.6 | 1000 | 0 | 910600 | 901721.6939 | Kakrail | Kakrail 33/11KV S/S | 4 | 0 | 0 | 684720.7122 | 2230006.6883 | 2380457.3749 | 2409184.7946 | 2711345 | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | High Court | D3046 | 11 | 0 | 1025651 | 1 | 30487.8 | 30689.4 | 201.6 | 1000 | 0 | 201600 | 199634.4097 | Ramna | Kakrail 33/11KV S/S | 4 | 192022.3312 | 108223.5072 | 181822.4648 | 251110.6689 | 202322.6667 | 325169.1484 | 265125 | 281963.0422 | 304725.5352
60 | Secretaiat | 0 | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Shanti Nagar Bazar | D604N | 11 | 0 | 06604402 | 1 | 5852.63 | 5874.69 | 22.06 | 40000 | 0 | 882400 | 873796.6426 | Rajarbag | Kakrail 33/11KV S/S | 4 | 828920.0528 | 902777.1248 | 1155190.1048 | 1443886.346 | 1590213.609 | 1510645.8477 | 1601052 | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 0 | 11 | 0 | 9119867 | 1 | 33300.4 | 33421.3 | 120.9 | 1000 | 0 | 120900 | 119721.2308 | Kakrail | Kakrail 33/11KV S/S | 4 | 114970.0758 | 130986.0101 | 77638.4937 | 216622.9377 | 242037.4816 | 236872.8291 | 224220 | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 0 | 11 | 0 | DHK00199 | 1 | 80032.9 | 80210.4 | 177.5 | 2222.22 | 0 | 394444.05 | 390598.2395 | Kakrail | Kakrail 33/11KV S/S | 4 | 405763.0795 | 421151.0466 | 183819.1042 | 639993.908 | 715946.6275 | 682140.9217 | 703183.7413 | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 0 | 11 | 0 | DHK00027 | 1 | 60175.9 | 60723.6 | 547.7 | 2222.22 | 0 | 1217109.894 | 1205243.1312 | Kakrail | Kakrail 33/11KV S/S | 4 | 2022056.4346 | 2342638.5829 | 1933413.755 | 1067396.9898 | 1227916.0084 | 1208524.4599 | 1467416.3104 | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | D304B | 11 | 0 | D1025656 | 1 | 71704.2 | 72297.5 | 593.3 | 1000 | 0 | 593300 | 587515.3536 | Ramna | Kakrail 33/11KV S/S | 4 | 527301.0267 | 592231.5492 | 791846.372 | 917673.5431 | 1028330.0287 | 1027534.5089 | 1059146.6 | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | D304F | 11 | 0 | D0086137 | 1 | 28206.8 | 28310 | 103.2 | 1000 | 0 | 103200 | 102193.805 | Ramna | Kakrail 33/11KV S/S | 4 | 123080.8395 | 317150.7661 | 438773.4499 | 432945.982 | 472221.3068 | 517539.8234 | 576508 | 916863.5723 | 907912.3538
67 | Judges Complex | C604JC | 11 | 0 | 06604344 | 1 | 690.43 | 692.15 | 1.72 | 40000 | 0 | 68800 | 68129.2033 | Kakrail | Kakrail 33/11KV S/S | 4 | 88001.7864 | 76416.9741 | 88351.0596 | 118357.8949 | 136165.0797 | 135933.8524 | 151904 | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 0 | 11 | 0 | 39333 | 1 | 499707 | 499707 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 4 | 0 | 532.48 | 2999.9201 | 3752.665 | 0 | 0 | 0 | 0 | 0
69 | Auxiliary Transformer, AT-2 | 0 | 11 | 0 | 39254 | 1 | 1235419 | 1237321 | 1902 | 1 | 0 | 1902 | 1883.4556 | Kakrail | Kakrail 33/11KV S/S | 4 | 3167.2532 | 3590.1751 | 0 | 1874.3332 | 6333.0946 | 25918.4591 | 0 | 0 | 0
70 | 11 kV Jamuna (F1) | C6101JG | 11 | 0 | BD017073 | 1 | 0.4408 | 0.4517 | 0.0109 | 2000 | 0 | 21.8 | 21.9645 | Kakrail | BSMMU 33/11KV S/S | 101 | 24.3781 | 22.3208 | 20.9345 | 34.3292 | 8.7511 | 22.0654 | 24.7258 | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | C6101PP | 11 | 0 | BD017074 | 1 | 3047.06 | 3065.02 | 17.96 | 2000 | 0 | 35920 | 36190.9742 | Kakrail | BSMMU 33/11KV S/S | 101 | 38781.503 | 31249.1675 | 40077.555 | 42742.7844 | 43083.9288 | 43219.8277 | 44627.1399 | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 | 0 | BD017075 | 1 | 1915.81 | 1950.68 | 34.87 | 2000 | 0 | 69740 | 70266.1063 | Kakrail | BSMMU 33/11KV S/S | 101 | 29253.7267 | 46270.4855 | 47907.8759 | 87211.9487 | 84458.3395 | 31822.749 | 77353.7092 | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 | 0 | BD017076 | 1 | 3438.44 | 3484.18 | 45.74 | 2000 | 0 | 91480 | 92170.109 | Kakrail | BSMMU 33/11KV S/S | 101 | 80203.9675 | 97950.2541 | 144186.603 | 174503.2711 | 172111.8499 | 179215.5198 | 177543.6485 | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 | 0 | BD017077 | 1 | 16013.45 | 16195.5 | 182.05 | 2000 | 0 | 364100 | 366846.7064 | Kakrail | BSMMU 33/11KV S/S | 101 | 389724.6483 | 324154.8134 | 500335.3629 | 627271.1967 | 702896.8986 | 697529.5567 | 750881.7825 | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | C6101NH | 11 | 0 | BD017078 | 1 | 28368.92 | 28693.65 | 324.73 | 2000 | 0 | 649460 | 654359.4121 | Kakrail | BSMMU 33/11KV S/S | 101 | 572316.6594 | 388724.3609 | 492746.5943 | 733453.4805 | 641089.6752 | 636961.0675 | 681006.1346 | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | C31016 | 11 | 0 | BD017079 | 1 | 35705.62 | 36132.95 | 427.33 | 2000 | 0 | 854660 | 861107.4049 | Paribag | BSMMU 33/11KV S/S | 101 | 847037.5945 | 887886.5777 | 1159088.7861 | 1451369.5422 | 1603019.2834 | 1597412.9298 | 1675286.7504 | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 | 0 | BD017080 | 1 | 7316.36 | 7404.3 | 87.94 | 2000 | 0 | 175880 | 177206.8078 | Paribag | BSMMU 33/11KV S/S | 101 | 149722.1986 | 184518.8938 | 291332.2219 | 378930.46 | 414273.243 | 428837.8596 | 457910.6397 | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 | 0 | BD017083 | 1 | 2648.04 | 2692.86 | 44.82 | 2000 | 0 | 89640 | 90316.2284 | Paribag | BSMMU 33/11KV S/S | 101 | 86501.6447 | 94551.8569 | 114173.7278 | 135094.1858 | 140648.5745 | 143344.075 | 137962.1897 | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | C6101RT | 11 | 0 | BD017084 | 1 | 1866.59 | 1944.89 | 78.3 | 2000 | 0 | 156600 | 157781.3629 | Kakrail | BSMMU 33/11KV S/S | 101 | 131702.7156 | 160086.6296 | 211841.3807 | 253083.3205 | 267336.0837 | 281930.9324 | 302057.3893 | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 | 0 | BD017085 | 1 | 2416.46 | 2457.04 | 40.58 | 2000 | 0 | 81160 | 81772.2568 | Kakrail | BSMMU 33/11KV S/S | 101 | 99300.1502 | 84175.6854 | 86093.2711 | 101598.4476 | 113805.0685 | 114841.2565 | 122402.9977 | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | C3101RM | 11 | 0 | BD017086 | 1 | 2411.95 | 2414.12 | 2.17 | 2000 | 0 | 4340 | 4372.7402 | Paribag | BSMMU 33/11KV S/S | 101 | 60.9453 | 42490.0199 | 182774.5854 | 159898.4943 | 165660.4538 | 173668.8065 | 174287.0734 | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 | 0 | BD017087 | 1 | 4705.28 | 4762.51 | 57.23 | 2000 | 0 | 114460 | 115323.4661 | Paribag | BSMMU 33/11KV S/S | 101 | 98751.6428 | 122724.3689 | 185834.2481 | 231553.1807 | 239475.0074 | 241970.3048 | 234654.3262 | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 | 0 | BD017088 | 1 | 1173.86 | 1189.09 | 15.23 | 2000 | 0 | 30460 | 30689.7849 | Paribag | BSMMU 33/11KV S/S | 101 | 29233.4116 | 38689.4455 | 46559.2088 | 60542.3562 | 62295.6571 | 66843.9677 | 56065.3573 | 59004.3933 | 75292.0174
84 | Spare | 0 | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | C310113 | 11 | 0 | BD017090 | 1 | 2714.45 | 2870.38 | 155.93 | 2000 | 0 | 311860 | 314212.6171 | Paribag | BSMMU 33/11KV S/S | 101 | 313055.5062 | 388523.2723 | 426621.648 | 459157.5154 | 528668.5024 | 530318.42 | 510819.9335 | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKD4418 | 1 | 3207.96 | 3293.94 | 85.98 | 100 | 0 | 8598 | 8662.8618 | Paribag | BSMMU 33/11KV S/S | 101 | 8725.3303 | 8671.9456 | 7126.7998 | 0 | 6033.1746 | 14842.5188 | 15407.4195 | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 1919.42 | 1919.42 | 0 | 100 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 350.8996 | 3914.154 | 12158.0799 | 8446.8515 | 487.8678 | 0 | 0 | 0
88 | Chata Mosjid | 0 | 11 | 0 | 0 | 1 | 186386.5 | 188496.5 | 2110 | 1000 | 0 | 2110000 | 2121499.4576 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 109 | 2104576.1621 | 2142956.195 | 3224151.7427 | 2448059.1892 | 2307606.3907 | 2543835.8742 | 2199148.6226 | 2319503.7751 | 2426211.3577
89 | AC mosjid | A3109X | 11 | 0 | 0 | 1 | 14088.621 | 15403.218 | 1314.597 | 1000 | 0 | 1314597 | 1321761.5272 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1444428.2322 | 1045314.8108 | 1227807.0733 | 1300312.4106 | 1258989.8828 | 1405178.1975 | 1152835.6866 | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | A3109K | 11 | 0 | 0 | 1 | 3815.7512 | 5901.9428 | 2086.1916 | 1000 | 0 | 2086191.6 | 2097561.3023 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2053812.9926 | 1772024.1697 | 2150154.7266 | 2361420.5589 | 2255488.3746 | 2390177.1556 | 2000565.9387 | 2224217.61 | 2267338.6868
91 | Nazimuddin | A3109M | 11 | 0 | 0 | 1 | 8961.7128 | 9587.6336 | 625.9208 | 1000 | 0 | 625920.8 | 629332.0558 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 552316.6673 | 513485.0212 | 619180.2481 | 762703.8683 | 950975.5456 | 925339.67 | 477977.0793 | 0 | 0
92 | Kamal Bagh | A3109U | 11 | 0 | 0 | 1 | 2788.3572 | 4399.1324 | 1610.7752 | 1000 | 0 | 1610775.2 | 1619553.8925 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1600011.3813 | 1367935.271 | 1559969.3577 | 2099983.5161 | 1567737.0505 | 1686096.534 | 1618577.1268 | 1589844.4629 | 1583845.5588
93 | Rahamatganj | A3109B | 11 | 0 | 0 | 1 | 24671.398 | 26818.372 | 2146.974 | 1000 | 0 | 2146974 | 2158674.9651 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2182617.7764 | 2187260.9964 | 2312778.458 | 2488587.0183 | 2323808.6258 | 2495628.7814 | 2157043.5386 | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 0 | 11 | 0 | 0 | 1 | 8925.3704 | 10419.22 | 1493.8496 | 1000 | 0 | 1493849.6 | 1501991.0503 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1492476.4844 | 1318156.0753 | 1695142.4767 | 1852690.3414 | 1787173.2312 | 1980277.4376 | 1747210.9883 | 1862323.276 | 1854345.8684
95 | City Colony | A3109J | 11 | 0 | 0 | 1 | 7217.068 | 9111.3624 | 1894.2944 | 1000 | 0 | 1894294.4 | 1904618.2664 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1920551.3181 | 1888735.7476 | 1983609.3649 | 2200330.7905 | 2079469.3659 | 2219309.3581 | 1859682.1079 | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 0 | 11 | 0 | 0 | 1 | 14394.01 | 16538.576 | 2144.566 | 1000 | 0 | 2144566 | 2156253.8416 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2167721.4514 | 1811264.2005 | 2752272.8848 | 2717279.1674 | 2859477.1699 | 2599114.1368 | 2790703.3917 | 2997202.1128 | 3092062.2371
97 | Chun Goli | A3109H | 11 | 0 | 0 | 1 | 4256.7304 | 5262.686 | 1005.9556 | 1000 | 0 | 1005955.6 | 1011438.0378 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 860621.3663 | 830456.4608 | 905187.2228 | 976536.6596 | 927964.1813 | 983357.245 | 754718.4448 | 841380.8401 | 894878.3402
98 | Alir Ghat | A3109L | 11 | 0 | 0 | 1 | 133060.1 | 134991.2 | 1931.1 | 1000 | 0 | 1931100 | 1941624.4562 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1928077.5242 | 1857501.3431 | 1968110.7302 | 2047969.8743 | 1928133.7897 | 2137361.0725 | 1734165.991 | 1904122.5273 | 2096766.6729
99 | Club Ghat | A3109C | 11 | 0 | 0 | 1 | 32758.904 | 35205.384 | 2446.48 | 1000 | 0 | 2446480 | 2459813.2668 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2758945.8627 | 2723668.6966 | 2705806.9627 | 2856757.5327 | 2651623.7603 | 2977501.1852 | 2317579.0304 | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | A3109V | 11 | 0 | 0 | 1 | 9665.9152 | 12248.96 | 2583.0448 | 1000 | 0 | 2583044.8 | 2597122.3422 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2668419.4712 | 2685941.0122 | 2625728.7516 | 2710169.0726 | 2405552.6316 | 2718263.3522 | 2261609.1864 | 2437761.5097 | 2619436.8857
101 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | Sowari Ghat | A319R | 11 | 0 | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2209968.432 | 2234300.9651 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2372343.4886 | 2925967.2197 | 2836655.3487 | 2802102.8851 | 2638720.3862 | 2802348.4469 | 2329233.6447 | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | A3202 | 11 | 0 | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 523413.576 | 529176.5444 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 499440.7344 | 622546.217 | 543189.3221 | 622689.53 | 658473.4491 | 560200.422 | 121854.324 | 118483.0867 | 132959.886
105 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | Eidgah | A320A | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1046827.152 | 1058353.0887 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1123741.6525 | 1618620.1641 | 1207087.3824 | 1369916.966 | 1376808.1209 | 1431623.3008 | 1096688.9157 | 1303313.9541 | 1329598.8604
108 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | Modumoti | A3201 | 11 | 0 | 0 | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 1977340.176 | 1999111.3898 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2122623.1214 | 1369601.6773 | 2052048.5501 | 2241682.3081 | 1975420.3474 | 2116312.7055 | 1584106.2116 | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | A320Y | 11 | 0 | 61389152 | 1 | 443916 | 444305 | 389 | 1000 | Estimated | 872355.96 | 881960.9073 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 874021.2853 | 996073.9471 | 965669.9059 | 1120841.154 | 1197224.4529 | 1244889.8267 | 1181986.9425 | 1066347.7806 | 1087853.6131
111 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | Water Works 11 kV Sw/S-2 | A320G | 11 | 0 | 61389109 | 1 | 407526 | 408402 | 876 | 1000 | 0 | 876000 | 885645.0694 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 840530.0839 | 1121562.4267 | 955036.4181 | 858393.0961 | 972107.7743 | 1045286.2834 | 874589.6653 | 951212.9635 | 980831.1601
114 | Islambagh | A320D | 11 | 0 | 61389186 | 1 | 504954 | 505646 | 692 | 1000 | 0 | 692000 | 699619.1644 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 757180.0278 | 841171.82 | 869765.3094 | 693124.8804 | 855693.6396 | 941158.1479 | 774407.5731 | 861627.8273 | 876487.4197
115 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | WASA Low Lift Pump | A320F | 11 | 0 | 61389202 | 1 | 15832 | 15858 | 26 | 1000 | 0 | 26000 | 26286.2692 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 37156.0491 | 49068.3562 | 57181.8023 | 43069.8986 | 55719.5858 | 56068.996 | 57103.7926 | 61401.0484 | 45712.4958
117 | Shahi Mosjid | D920M | 11 | 0 | 06604459 | 1 | 36754.1 | 36846.51 | 92.41 | 8000 | 0 | 739280 | 747419.7339 | Azimpur | Lalbagh Old 33/11KV S/S | 20 | 755814.2919 | 532021.1483 | 1405027.1069 | 1328075.3488 | 1734152.7099 | 1661564.6485 | 1773623.7611 | 1752245.002 | 1250534.8854
118 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | 5395822 | 1 | 82720.6 | 82720.6 | 0 | 1 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 7696.9258 | 7309.2123 | 7143.8831 | 13347.8624 | 8792.8491 | 9867.6427 | 0 | 0 | 0
120 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | Spare | 0 | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | Chawk Bazar | A319Z | 11 | 0 | DHK-60904 | 1 | 5415 | 21857.4 | 16442.4 | 60 | 32 | 364113.792 | 370947.5017 | Lalbag | Mitford 33/11 kV | 88 | 246855.923 | 307526.3862 | 440824.2804 | 524398.7147 | 501841.8638 | 526171.1474 | 480516.9276 | 522405.3875 | 508276.2976
123 | Spare | 0 | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | Chatrabas | B688D | 11 | 0 | DHK-66485 | 1 | 876789 | 880190 | 3401 | 60 | 0 | 204060 | 207889.8104 | Bangshal | Mitford 33/11 kV | 88 | 310637.8801 | 226152.9057 | 282876.7415 | 339280.009 | 1110389.3159 | 1353014.9285 | 1237900.3837 | 762976.1234 | 353557.5482
125 | Begum Bazar | B678G | 11 | 0 | DHK-66481 | 1 | 3867004 | 3889474 | 22470 | 60 | 0 | 1348200 | 1373503.0993 | Bangshal | Mitford 33/11 kV | 88 | 1439942.349 | 1494842.1873 | 1874630.1846 | 2344342.8516 | 2422961.4211 | 2446646.3554 | 2397460.098 | 2421237.7604 | 2357293.0663
126 | SCC ROAD | B688R | 11 | 0 | DHK-60901 | 1 | 214082.8 | 232175.1 | 18092.3 | 60 | 0 | 1085538 | 1105911.443 | Bangshal | Mitford 33/11 kV | 88 | 966855.8354 | 1136438.0721 | 1342334.3996 | 1631812.3089 | 1626362.4279 | 1682445.687 | 1526989.2348 | 1650255.6547 | 1574186.7645
127 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | Armanitola | B619A | 11 | 0 | DHK-61104 | 1 | 762604.6 | 771102.4 | 8497.8 | 60 | 0 | 509868 | 519437.2335 | Bangshal | Mitford 33/11 kV | 88 | 493501.4256 | 551741.488 | 743803.3265 | 925763.6241 | 975265.6139 | 991422.0466 | 974917.2355 | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 0 | 11 | 0 | DHK-61101 | 1 | 433797 | 433797.1 | 0.1 | 60 | 0 | 6 | 6.1126 | Bangshal | Mitford 33/11 kV | 88 | 225733.0342 | 283313.0981 | 415582.0452 | 494194.5928 | 534862.6587 | 551030.4718 | 539101.6117 | 513839.5885 | 528540.0121
130 | Emamganj | B688I | 11 | 0 | DHK-68130 | 1 | 1516.11 | 1527.46 | 11.35 | 60000 | 0 | 681000 | 693781.0493 | Bangshal | Mitford 33/11 kV | 88 | 593633.738 | 734223.2785 | 961780.9211 | 1149360.3885 | 350737.4618 | 168709.5633 | 161982.5873 | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | A319T | 11 | 0 | DHK-68129 | 1 | 1226.82 | 1226.82 | 0 | 60000 | 0 | 0 | 0 | Lalbag | Mitford 33/11 kV | 88 | -608.8551 | 0 | 601.8654 | 0 | 0 | 84652.8551 | 538371.2175 | 628439.5052 | 594724.3345
132 | Spare | 0 | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | Panghat | B688P | 11 | 0 | DHK-68127 | 1 | 1648.83 | 1664.56 | 15.73 | 60000 | 0 | 943800 | 961513.2956 | Bangshal | Mitford 33/11 kV | 88 | 845090.9008 | 1050970.8417 | 1225999.835 | 1414831.0491 | 1293419.2063 | 1420021.8363 | 1363598.8715 | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | U0004460 | 1 | 5846.88 | 5887.51 | 40.63 | 100 | 0 | 4063 | 4139.2546 | Bangshal | Mitford 33/11 kV | 88 | 4563.3691 | 4209.1423 | 4259.2009 | 4363.7626 | 4064.0057 | 3905.7556 | 3927.8323 | 4152.4762 | 4434.1352
135 | Chadni chwok | 0 | 11 | 0 | DHK60916 | 1 | 473428 | 484246 | 10818 | 60 | 0 | 649080 | 649366.4481 | Paribag | Azimpur 33/11 KV | 66 | 536263.7735 | 642773.9991 | 585337.5096 | 659849.4891 | 735121.5421 | 735452.5478 | 623153.8648 | 792142.0147 | 648152.1238
136 | BGB | 0 | 11 | 0 | DHK61090 | 1 | 726294 | 729913 | 3619 | 60 | 0 | 217140 | 217235.8269 | Jigatola | Azimpur 33/11 KV | 66 | 380481.4139 | 230670.4639 | 138499.1268 | 715312.2841 | 771727.6444 | 791117.6745 | 677536.8748 | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | D920P | 11 | 0 | DHK61091 | 1 | 978510 | 1007094 | 28584 | 60 | 0 | 1715040 | 1715796.8712 | Azimpur | Azimpur 33/11 KV | 66 | 1652714.2274 | 1932170.5777 | 1912839.727 | 2177491.1776 | 2180695.2965 | 2262756.8158 | 2133225.2763 | 2225341.7622 | 2144033.6462
138 | Azimpur | D901P | 11 | 0 | DHK61086 | 1 | 429615 | 443570 | 13955 | 60 | 0 | 837300 | 837669.5122 | Azimpur | Azimpur 33/11 KV | 66 | 1335819.9504 | 1491233.2344 | 1631381.6426 | 1038683.4379 | 1153765.578 | 1156672.3968 | 1153479.4596 | 1136633.6642 | 1104066.6214
139 | Aazd | D901Z | 11 | 0 | DHK61089 | 1 | 90027 | 101664 | 11637 | 60 | 0 | 698220 | 698528.1343 | Azimpur | Azimpur 33/11 KV | 66 | 763168.1621 | 813027.8611 | 1025333.4123 | 1260231.211 | 1354793.0694 | 1347891.2826 | 1333174.551 | 1318714.278 | 1257709.9294
140 | Dayra Sharif | D966D | 11 | 0 | DHK61088 | 1 | 598264 | 609253 | 10989 | 60 | 0 | 659340 | 659630.976 | Azimpur | Azimpur 33/11 KV | 66 | 557582.0044 | 605265.6133 | 772833.6808 | 1018901.3032 | 1035744.5659 | 1040264.9944 | 1036318.7466 | 1007533.0284 | 980271.2172
141 | Naya palton | D966U | 11 | 0 | DHK86065 | 1 | 2045.23 | 2064.31 | 19.08 | 60000 | 0 | 1144800 | 1145305.2163 | Azimpur | Azimpur 33/11 KV | 66 | 1141260.4639 | 1219327.9816 | 1424702.0899 | 1594707.0602 | 1776436.6019 | 1764768.0283 | 1711787.3638 | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | D966V | 11 | 0 | DHK66477 | 1 | 1722998 | 1736553 | 13555 | 60 | 0 | 813300 | 813658.9207 | Azimpur | Azimpur 33/11 KV | 66 | 766843.7191 | 834225.5971 | 1008349.3994 | 1357200.0802 | 1489035.8491 | 1488032.8269 | 1499973.4477 | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | D966W | 11 | 0 | DHK66480 | 1 | 4164565 | 4185323 | 20758 | 60 | 0 | 1245480 | 1246029.6478 | Azimpur | Azimpur 33/11 KV | 66 | 1606279.69 | 1867844.3069 | 1712147.3443 | 1414604.6799 | 1497238.5543 | 1598200.8415 | 1506117.3895 | 1034936.4652 | 1287496.6695
144 | Lalbagh | D920L | 11 | 0 | DHK61093 | 1 | 920565 | 943675 | 23110 | 60 | 0 | 1386600 | 1387211.926 | Azimpur | Azimpur 33/11 KV | 66 | 1330919.2077 | 1478648.9877 | 1848324.9154 | 2271183.2515 | 2469993.6901 | 2465781.6021 | 2471750.3893 | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | D366J | 11 | 0 | DHK66497 | 1 | 1292347 | 1298527 | 6180 | 60 | 0 | 370800 | 370963.6392 | Ramna | Azimpur 33/11 KV | 66 | 323939.0946 | 334032.3348 | 483616.7128 | 594434.9453 | 771237.9306 | 746279.7208 | 668533.8709 | 616760.0188 | 675859.2968
146 | Eden College | D966E | 11 | 0 | DHK60917 | 1 | 971842 | 976460 | 4618 | 60 | 0 | 277080 | 277202.2793 | Azimpur | Azimpur 33/11 KV | 66 | 278913.5208 | 288765.6999 | 308522.5366 | 489031.3622 | 487693.6736 | 503127.1069 | 450271.8574 | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | D902N | 11 | 0 | DHK60918 | 1 | 533446 | 540356 | 6910 | 60 | 0 | 414600 | 414782.9688 | Azimpur | Azimpur 33/11 KV | 66 | 419136.0222 | 429086.1595 | 527298.6165 | 634848.7543 | 693863.1593 | 681133.1714 | 683984.9722 | 653358.8311 | 648152.1238
148 | BUET | D366BU | 11 | 0 | DHK66496 | 1 | 1033226 | 1043678 | 10452 | 60 | 0 | 627120 | 627396.7568 | Ramna | Azimpur 33/11 KV | 66 | 678997.9056 | 391150.1536 | 431931.5513 | 807548.0045 | 1180516.1912 | 815830.544 | 798043.2987 | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIG2780 | 1 | 408450 | 409947 | 1497 | 1 | 0 | 1497 | 1497.6606 | Azimpur | Azimpur 33/11 KV | 66 | 1723.4279 | 1960.9433 | 3021.0771 | 4277.027 | 4444.1522 | 3986.2756 | 4092.9197 | 4399.774 | 2203.9333
150 | Rasulpur | F120R | 11 | 0 | HA-021101042-02 | 1.5 | 99314921 | 99628473 | 313552 | 1 | 0 | 470328 | 476543.206 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 747281.5913 | 861127.0146 | 1135070.1317 | 1665082.8173 | 1532049.0872 | 1584215.5272 | 1403442.4135 | 1475786.882 | 1248201.2259
151 | Bheribadh | F120B | 11 | 0 | HA-021101105-02 | 1.5 | 77687448 | 78413126 | 725678 | 1 | 0 | 1088517 | 1102901.339 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1866994.3592 | 1848720.2846 | 2165499.7281 | 2508479.0993 | 2458320.6942 | 2620926.9562 | 2327005.5404 | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 | 0 | 30799521 | 1.5 | 2663.91 | 2665.11 | 1.2 | 60000 | 0 | 108000 | 109427.179 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 162709.829 | 336891.3617 | 271984.1018 | 253194.3598 | 408741.1592 | 362911.631 | 314576.4303 | 364934.8739 | 488122.7019
153 | Panna Battery Express | F140E | 11 | 0 | DHK15431 | 1 | 5375.75 | 5382.23 | 6.48 | 60000 | 0 | 388800 | 393937.8444 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 877165.0182 | 981432.1586 | 963251.5607 | 788120.5732 | 1093857.5249 | 1220535.5698 | 1068349.9537 | 1060687.1709 | 1118589.0702
154 | Eidgah | F140I | 11 | 0 | 30799460 | 1 | 5589.33 | 5621.88 | 32.55 | 60000 | 0 | 1953000 | 1978808.1538 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1994724.6335 | 2001853.5525 | 2214989.6293 | 2418400.8037 | 2321919.4185 | 2480917.8558 | 2121576.0406 | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | D840L | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | Huzur Para | F140H | 11 | 0 | HA-021101055-02 | 1 | 13533389 | 15522799 | 1989410 | 1 | 0 | 1989410 | 2015699.2981 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1790122.1209 | 1815831.2401 | 2641114.3542 | 2153483.8082 | 1914978.8856 | 2163917.8156 | 1832748.4977 | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | F103K | 11 | 0 | HA-021101015-02 | 1 | 31631669 | 32048318 | 416649 | 1 | 0 | 416649 | 422154.8584 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1105200.3969 | 1217911.0091 | 2380775.6541 | 2064906.2609 | 1863929.1371 | 2041804.9994 | 1873617.2189 | 1726065.7983 | 1737567.1439
158 | Munshihati | F140T | 11 | 0 | HA-021100854-02 | 1 | 57816310 | 58111286 | 294976 | 1 | 0 | 294976 | 298873.9959 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 663886.687 | 772236.6347 | 990193.2667 | 1294711.6864 | 1345431.4782 | 1376742.8712 | 1392932.3343 | 1212171.698 | 1205376.9608
159 | Jhawchar | F140J | 11 | 0 | HA-021101028-02 | 1 | 7831319 | 8178936 | 347617 | 1 | 0 | 347617 | 352210.6267 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 916198.0459 | 942852.1071 | 1224855.4453 | 1505628.0528 | 1566579.6466 | 1562224.2267 | 1438582.214 | 1425641.3374 | 1328999.0751
160 | RMU Express | F140D | 11 | 0 | HA-021101248-02 | 1 | 9846204 | 10451988 | 605784 | 1 | 0 | 605784 | 613789.2056 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 639128.4903 | 638426.3913 | 630223.836 | 713470.7397 | 717231.4507 | 658611.0471 | 606779.6203 | 633839.2782 | 704501.3661
161 | Koyla Ghat | F140C | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2010996.288 | 2037570.8407 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1922044.5384 | 2067377.5431 | 2106357.2232 | 1907872.1438 | 2053915.4269 | 2183072.3937 | 1900877.505 | 2223108.4368 | 1816011.9444
162 | Muslimbagh | F140M | 11 | 0 | HA-021100908-02 | 1 | 37215219 | 38199598 | 984379 | 1 | 0 | 984379 | 997387.1949 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1348865.5022 | 1869441.4387 | 2918215.2206 | 1684632.0125 | 1681378.5129 | 1753494.5949 | 1596522.772 | 1696945.1326 | 1737474.4882
163 | Noyagaon | F140Y | 11 | 0 | HA-021101087-02 | 1 | 19796598 | 20487577 | 690979 | 1 | 0 | 690979 | 700110.0252 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1800043.7503 | 1865255.1726 | 2290171.3321 | 2533643.7042 | 2800404.9743 | 2891878.4964 | 2674100.301 | 2742632.8101 | 2660587.4202
164 | Nurbagh | F140N | 11 | 0 | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2262370.824 | 2292267.1958 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2178317.1436 | 2169470.2613 | 2292212.2723 | 2098659.3582 | 2062025.6114 | 2315958.5809 | 1868573.9135 | 2159293.4513 | 2300317.433
165 | Ali Nagar | F140A | 11 | 0 | HA-021101022-02 | 1 | 34081371 | 35680798 | 1599427 | 1 | 0 | 1599427 | 1620562.8208 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1505747.9542 | 1630876.0549 | 2028577.6342 | 2162413.4126 | 2438442.3104 | 2505512.4752 | 2290198.0816 | 2360084.8023 | 2402380.2856
166 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | Nababgonj Park | D920K | 11 | 0 | 0 | 1 | 12523740 | 12956970 | 433230 | 1 | 0 | 433230 | 437301.7528 | Azimpur | BGB 33/11 KV S/S | 104 | 0 | 0 | 257344.0613 | 1028840.1279 | 1022665.2071 | 1042273.5833 | 1021134.2367 | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | F1104O | 11 | 0 | 0 | 1 | 94560736 | 97301320 | 2740584 | 1 | 0 | 2740584 | 2766341.6358 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2922234.8502 | 2885529.8072 | 2905973.3033 | 3092402.2195 | 2773618.4692 | 2851658.6512 | 2502740.2728 | 2762472.0542 | 2841690.4191
171 | Khalpar | F1104L | 11 | 0 | 0 | 1 | 94084000 | 96060500 | 1976500 | 1 | 0 | 1976500 | 1995076.3206 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 1357000.7539 | 1323844.5795 | 2032339.2009 | 1943499.6703 | 1539343.6525 | 1698814.3914 | 1298185.7875 | 1375644.1828 | 1437529.7992
172 | Shahidnagar | D920S | 11 | 0 | 0 | 1 | 26032520 | 27374940 | 1342420 | 1 | 0 | 1342420 | 1355036.8603 | Azimpur | BGB 33/11 KV S/S | 104 | 1306884.5014 | 1428175.9553 | 1591215.1991 | 1859313.6405 | 1906528.5825 | 1984753.7699 | 1856790.3941 | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | D9104G | 11 | 0 | 0 | 1 | 37153410 | 37725810 | 572400 | 1 | 0 | 572400 | 577779.7551 | Azimpur | BGB 33/11 KV S/S | 104 | 0 | 0 | 345681.1733 | 1312194.6593 | 1412422.3679 | 1466652.5091 | 1458588.073 | 1375749.2129 | 1318685.5995
174 | Ganaktuli | D8104J | 11 | 0 | 0 | 1 | 27939600 | 28480330 | 540730 | 1 | 0 | 540730 | 545812.1016 | Jigatola | BGB 33/11 KV S/S | 104 | 547461.301 | 533380.4107 | 706109.2655 | 871530.0895 | 914191.5251 | 939625.3117 | 882817.4598 | 725654.1445 | 693078.4919
175 | Thana | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Bot Tola Mazar | D8104L | 11 | 0 | 0 | 1 | 39473749 | 40794581 | 1320832 | 1 | 40794581 | 1320832 | 1333245.9634 | Jigatola | BGB 33/11 KV S/S | 104 | 396033.3839 | 0 | 521511.0545 | 2086773.692 | 2120352.147 | 2064384.9311 | 2207948.9744 | 2074198.5352 | 1909183.4664
177 | Sikder Medical | D8104K | 11 | 0 | 0 | 1 | 41542992 | 42216880 | 673888 | 1 | 0 | 673888 | 680221.5996 | Jigatola | BGB 33/11 KV S/S | 104 | 704444.667 | 708560.5942 | 897177.4288 | 1152362.6885 | 1220473.4868 | 1221157.6998 | 1181050.1989 | 1134381.9061 | 1138392.2283
178 | Gas Field | F1104G | 11 | 0 | 0 | 1 | 65021220 | 66468860 | 1447640 | 1 | 0 | 1447640 | 1461245.7803 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 1418157.1729 | 1470777.4973 | 1717515.6493 | 2221738.1672 | 2114640.3455 | 2213538.6558 | 2063276.8361 | 2061072.7993 | 1985612.1672
179 | Hazaribagh | D8104H | 11 | 0 | 0 | 1 | 47131648 | 48013400 | 881752 | 1 | 0 | 881752 | 890039.2289 | Jigatola | BGB 33/11 KV S/S | 104 | 821301.08 | 894483.3199 | 1109528.647 | 1387872.6757 | 1512565.9182 | 1534113.0489 | 1525507.7666 | 1485016.8997 | 1465699.7946
180 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 0 | 1 | 2426.91 | 2460.78 | 33.87 | 10 | 0 | 338.7 | 341.8833 | Azimpur | BGB 33/11 KV S/S | 104 | 375.1797 | 530.379 | 413.4472 | 551.1966 | 644.3721 | 611.8898 | 0 | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 2008.62 | 2044.99 | 36.37 | 10 | 0 | 363.7 | 367.1183 | Azimpur | BGB 33/11 KV S/S | 104 | 407.1099 | 597.457 | 421.5697 | 541.173 | 593.9263 | 558.558 | 0 | 0 | 0
184 | Salek Garden | 0 | 11 | 0 | 2761 | 1 | 794.02 | 818.11 | 24.09 | 60000 | 0 | 1445400 | 1444552.9709 | Jigatola | Jigatola New 33/11 KV S/S |  | 1253840.8307 | 1452181.1176 | 1864953.454 | 2402250.1859 | 2551916.8348 | 2553649.2193 | 2650896.5462 | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 0 | 11 | 0 | 2850 | 1 | 611.33 | 628.17 | 16.84 | 60000 | 0 | 1010400 | 1009807.8883 | Jigatola | Jigatola New 33/11 KV S/S |  | 896547.408 | 1061764.5702 | 1304682.5555 | 1679891.0289 | 1793125.2848 | 1780723.9511 | 1886527.6034 | 1807426.7227 | 1737565.9216
186 | City College | 0 | 11 | 0 | 2784 | 1 | 644.28 | 644.31 | 0.03 | 60000 | 0 | 1800 | 1798.9452 | Jigatola | Jigatola New 33/11 KV S/S |  | 506115.4723 | 1076202.1621 | 1313738.6584 | 1670267.593 | 1742699.2641 | 1753162.2749 | 1830510.0213 | 1777383.0604 | 2346194.6487
187 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | Post Office | 0 | 11 | 0 | 2836 | 1 | 521.18 | 537.81 | 16.63 | 60000 | 0 | 997800 | 997215.2721 | Jigatola | Jigatola New 33/11 KV S/S |  | 901970.0738 | 1053342.6416 | 1284759.1292 | 1558395.1507 | 1658055.5864 | 1646510.5712 | 1676311.0857 | 1671629.3692 | 1589764.671
190 | Leather Institute | 0 | 11 | 0 | 2835 | 1 | 58.33 | 59.04 | 0.71 | 60000 | 0 | 42600 | 42575.0357 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 57222.2613 | 189875.9456 | 195265.8799
191 | Mina Bazar | 0 | 11 | 0 | 2853 | 1 | 250.76 | 257.54 | 6.78 | 60000 | 0 | 406800 | 406561.6082 | Jigatola | Jigatola New 33/11 KV S/S |  | 389226.8989 | 412674.5015 | 509556.7223 | 661611.218 | 704163.3609 | 701025.2432 | 763766.6032 | 746284.571 | 706562.076
192 | Road-2 | 0 | 11 | 0 | 2839 | 1 | 823.37 | 849.2 | 25.83 | 60000 | 0 | 1549800 | 1548891.7907 | Jigatola | Jigatola New 33/11 KV S/S |  | 1301439.7858 | 1624229.0876 | 1929553.6546 | 2419692.6635 | 2344809.964 | 2360717.4857 | 2376832.0316 | 2301945.4038 | 2450136.1786
193 | SS-2 | 0 | 11 | 0 | 2838 | 1 | 450.61 | 465.05 | 14.44 | 60000 | 0 | 866400 | 865892.2748 | Jigatola | Jigatola New 33/11 KV S/S |  | 1573778.1113 | 2198123.3652 | 2140258.9817 | 1225183.6827 | 1208423.5682 | 1244469.5984 | 1139024.1692 | 1127238.2087 | 1112715.1061
194 | Spare | 0 | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | Bou Bazar | 0 | 11 | 0 | 2843 | 1 | 655.46 | 674.37 | 18.91 | 60000 | 0 | 1134600 | 1133935.105 | Jigatola | Jigatola New 33/11 KV S/S |  | 940531.2526 | 1150194.8205 | 1453202.6428 | 1833866.0032 | 1887974.2286 | 1919131.4991 | 1882311.2263 | 1850088.7231 | 1774816.6433
196 | BGB | 0 | 11 | 0 | 2764 | 1 | 228.5 | 236.94 | 8.44 | 60000 | 0 | 506400 | 506103.2409 | Jigatola | Jigatola New 33/11 KV S/S |  | 336205.278 | 498096.9202 | 766146.304 | 453504.4167 | 461638.2136 | 445780.1547 | 580655.3671 | 1007063.5596 | 934872.9509
197 | Dhamondi-12 | 0 | 11 | 0 | 2763 | 1 | 521.56 | 543.6 | 22.04 | 60000 | 0 | 1322400 | 1321625.051 | Dhanmondi | Jigatola New 33/11 KV S/S |  | 637464.4877 | 720074.8955 | 696112.4417 | 1536140.9551 | 2054260.035 | 1641717.2362 | 1520907.4708 | 1213163.0828 | 1602982.669
198 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 | 0 | DHK60907 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | Mitali Road | D803D | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | Bou Bazar | D803E | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | Mina Bazar | D803I | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | Simanto Square | D803R | 11 | 0 | DHK60946 | 1 | 1218.95 | 1228.76 | 9.81 | 60000 | 0 | 588600 | 589605.4404 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 539285.2665 | 650467.3454 | 732323.3006 | 891294.9856 | 910570.4517 | 922404.6994 | 967800 | 852145.3731 | 901151.3428
204 | Post Office | D803P | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | Hazaribagh Sw/S-2 | D803S | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | Green Road Via Park | D803G | 11 | 0 | DHK61070 | 1 | 3526.42 | 3536.26 | 9.84 | 60000 | 0 | 590400 | 591408.5152 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 583222.5705 | 592216.5384 | 824386.8012 | 963367.3565 | 1108520.5499 | 1276574.4307 | 1342800 | 1229862.9154 | 476757.7712
207 | PWD Quarters 11 kV Saleq Grand | D803A | 11 | 0 | DHK61028 | 1 | 3637.35 | 3638.36 | 1.01 | 60000 | 0 | 60600 | 60703.5163 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 63799.373 | 57037.2486 | 62770.5686 | 73874.1801 | 78580.1905 | 73359.435 | 68400 | 74813.6195 | 63933.0345
208 | Road No.-2 | D803T | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | Hzaribagh O/H | D803H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | B.G.B | D803B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 11 kV City College | D803C | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | Jigatala Local | D803Z | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 33/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 243284 | 1 | 86315 | 86442 | 127 | 10 | 0 | 1270 | 1272.1694 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 4032.6019 | 3478.8676 | 2919.3296 | 1971.9801 | 3959.002 | 5251.4131 | 3680 | 2585.0234 | 3440.2061
214 | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 412277 | 1 | 39896 | 39917 | 21 | 10 | 0 | 210 | 210.3587 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 60.1881 | 0 | 0 | 1491.4977 | 769.8059 | 10.0218 | 1650 | 5393.0685 | 0
215 | Spare | 0 | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | D Block dhaka uddyan | G1103L | 11 | 0 | BD014031 | 1 | 50828.11 | 51042.64 | 214.53 | 1000 | 0 | 214530 | 215692.4534 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 212820.8188 | 224956.6107 | 285235.5277 | 367241.8104 | 387945.2586 | 382937.2777 | 364723.8055 | 376392.0985 | 356370.9019
217 | Dill Mohammad O/H | G1103DM | 11 | 0 | BD014027 | 1 | 27275.39 | 28232.64 | 957.25 | 1000 | 0 | 957250 | 962436.9601 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 906080.9687 | 1135001.5369 | 1518244.1569 | 1927925.8849 | 1986501.3323 | 2019494.4174 | 1931376.746 | 1945233.0858 | 1925614.3584
218 | Turag O/H | G1103U | 11 | 0 | BD014028 | 1 | 29810.93 | 30322.94 | 512.01 | 1000 | 0 | 512010 | 514784.3802 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 456627.3521 | 491677.0226 | 590651.3937 | 705567.8194 | 641819.4994 | 770193.2072 | 703573.3851 | 725059.1327 | 419185.0275
219 | Nabadoy O/H | G1103N | 11 | 0 | BD014025 | 1 | 41533.54 | 41984.31 | 450.77 | 1000 | 0 | 450770 | 453212.5448 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 436281.6738 | 1523983.802 | 1125982.5565 | 997660.9336 | 848979.0298 | 846778.6447 | 874784.3247 | 873886.7957 | 1264712.0241
220 | Chandrima O/H | G1103CH | 11 | 0 | BD014024 | 1 | 9907.12 | 10527.40 | 620.28 | 1000 | 0 | 620280 | 623641.0526 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 643285.1357 | 623717.4245 | 752545.8986 | 970880.6709 | 1055645.8739 | 1037828.5358 | 998647.327 | 974655.0029 | 879754.0777
221 | Shyamoli Housing Project-2 | G1103SH | 11 | 0 | BD014029 | 1 | 33170.52 | 33773.81 | 603.29 | 1000 | 0 | 603290 | 606558.9905 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 570944.9461 | 613668.9159 | 919460.3881 | 1164941.4253 | 2147810.8671 | 1346057.1733 | 1686564.4606 | 1305126.5223 | 2226602.9518
222 | Spare | 0 | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | Spare | 0 | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | Spare | 0 | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | U Lab | C2103U | 11 | 0 | BD013959 | 1 | 46607.12 | 47408.36 | 801.24 | 1000 | 0 | 801240 | 805581.6035 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 455743.1942 | 653023.0747 | 694263.8768 | 2706800.3719 | 2673135.1804 | 1523999.7543 | 2168216.2175 | 2766170.13 | 2585824.4138
226 | Akota | G1103AK | 11 | 0 | BD014020 | 1 | 8749.58 | 9084.98 | 335.4 | 1000 | 0 | 335400 | 337217.4003 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 326123.6407 | 346438.5797 | 380615.236 | 526131.9628 | 548510.7365 | 553675.3788 | 518552.2147 | 529306.7232 | 494561.9781
227 | Burigonga O/H | G1103BU | 11 | 0 | BD014019 | 1 | 6950.61 | 7466.87 | 516.26 | 1000 | 0 | 516260 | 519057.4093 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 491541.5408 | 311833.7159 | 278809.9473 | 387230.8575 | 410809.9274 | 413097.2082 | 391376.3535 | 420977.1349 | 372374.7602
228 | Garden City | C2103G | 11 | 0 | BD014021 | 1 | 97620.97 | 99383.31 | 1762.34 | 1000 | 0 | 1762340 | 1771889.4252 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 1905259.7426 | 1668222.3933 | 1892735.0117 | 2553547.6368 | 3028251.44 | 2810059.9564 | 2804225.2436 | 2395190.4943 | 2278829.2831
229 | Avenue O/H | G1103AV | 11 | 0 | BD014017 | 1 | 18014.25 | 18677.34 | 663.09 | 1000 | 0 | 663090 | 666683.0231 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 671286.8174 | 662521.6649 | 749985.7064 | 943169.2729 | 1027773.9029 | 1034448.2826 | 977183.594 | 966250.121 | 894892.5874
230 | Chand Uddyan | C2103D | 11 | 0 | BD014018 | 1 | 11333.82 | 11532.03 | 198.21 | 1000 | 0 | 198210 | 199284.0218 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 192625.8492 | 203369.8147 | 512239.2335 | 689384.282 | 764257.0863 | 760476.2406 | 759432.9748 | 732469.8888 | 645275.1572
231 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4416 | 1 | 1995.36 | 2028.09 | 32.73 | 100 | 0 | 3273 | 3290.7351 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 4108.3199 | 3745.4441 | 2862.3952 | 3787.2919 | 1595.7005 | 3776.8023 | 3734.949 | 3966.4616 | 1513.851
232 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4412 | 1 | 284.73 | 284.73 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 168.6715 | 0 | 3189.39 | 0 | 0 | 0 | 2409.7413
233 | Lalmatia O/H | C209M | 11 | 0 | DHK61042 | 1 | 3244.77 | 3253.63 | 8.86 | 60000 | 0 | 531600 | 531398.58 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 719262.1967 | 768088.1431 | 970586.2531 | 911395.4616 | 1251951.9192 | 1243685.3152 | 1300189.4979 | 1240075.1783 | 1343819.1874
234 | Asad Avenue (South) | C209C | 11 | 0 | DHK 60999 | 1 | 2969.85 | 2978.17 | 8.32 | 60000 | 0 | 499200 | 499010.8562 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 585545.3707 | 644656.3174 | 816364.2657 | 854508.8922 | 1448736.6599 | 0 | 99461.5008 | 201384.8525 | 143036.2105
235 | Madrasha Road | 0 | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | Bashbari | C209H | 11 | 0 | DHK61002 | 1 | 2492.43 | 2503.14 | 10.71 | 60000 | 0 | 642600 | 642356.5228 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 901214.7728 | 966067.9031 | 1190903.3781 | 1245452.7622 | 1339544.3993 | 1690928.3933 | 1784914.5226 | 1599091.6268 | 1533732.8114
237 | Road-27 | C209A | 11 | 0 | DHK61001 | 1 | 1492.16 | 1496.32 | 4.16 | 60000 | 0 | 249600 | 249505.4281 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 529982.6713 | 234031.6299 | 326307.5256 | 422413.036 | 1160540.6933 | 560250.965 | 379271.8673 | 89903.952 | 435118.5562
238 | Boishakhi O/H | D209O | 11 | 0 | DHK61024 | 1 | 4293.22 | 4312.61 | 19.39 | 60000 | 0 | 1163400 | 1162959.1948 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1117359.7793 | 1278924.8078 | 1623796.756 | 2461251.8872 | 2676105.4034 | 2946106.036 | 2918535.965 | 3026167.0253 | 2814447.7883
239 | Katasur O/H | C209K | 11 | 0 | DHK61003 | 1 | 3717.15 | 3729.42 | 12.27 | 60000 | 0 | 736200 | 735921.0583 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 726589.1461 | 805973.1589 | 1044422.2626 | 1288420.2773 | 1430239.6103 | 1419182.7329 | 1436799.27 | 1431270.9163 | 1334804.3002
240 | Nurjahan Road | D409I | 11 | 0 | DHK61000 | 1 | 1938.98 | 1950.01 | 11.03 | 60000 | 0 | 661800 | 661549.248 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 774214.317 | 835914.5423 | 1604146.8503 | 1215193.9487 | 1433819.6844 | 1423372.644 | 1464960.0563 | 1437863.8728 | 1376873.7739
241 | polpar over head | D209W | 11 | 0 | DHK61003 | 1 | 1967.39 | 1983.57 | 16.18 | 60000 | 0 | 970800 | 970432.1698 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1105758.7761 | 1254482.8621 | 1581519.6861 | 1999502.3937 | 2133127.4955 | 2142241.6706 | 2168380.5497 | 2135518.5405 | 2016930.7661
242 | Satmosjid Housing | C209S | 11 | 0 | DHK61043 | 1 | 2887.27 | 2899.56 | 12.29 | 60000 | 0 | 737400 | 737120.6036 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 999518.0102 | 1145105.1552 | 1396334.2108 | 0 | 189147.2492 | 1377283.6223 | 608153.1522 | 0 | 0
243 | Physical College | C209P | 11 | 0 | DHK61041 | 1 | 3473.23 | 3495.45 | 22.22 | 60000 | 0 | 1333200 | 1332694.8586 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1441577.2891 | 1571006.0587 | 1952486.0884 | 2469119.1787 | 2662381.786 | 2653410.8203 | 2677671.3668 | 2636583.2332 | 2184607.6683
244 | Asad Avenue (North) | D409V | 11 | 0 | DHK61022 | 1 | 2754.07 | 2765.66 | 11.59 | 60000 | 0 | 695400 | 695136.5172 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 798026.9025 | 659321.4848 | 0 | 0 | 288792.6455 | 0 | 3594.994 | 0 | 0
245 | Spare Feeder | 0 | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | Ghraphic artch college | D209Z | 11 | 0 | DHK61023 | 1 | 1204.49 | 1222.87 | 18.38 | 60000 | 0 | 1102800 | 1102382.1558 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 986695.8488 | 1085833.4369 | 1330834.525 | 1448791.9887 | 1578216.0071 | 1715469.3009 | 1620743.1298 | 1570921.7218 | 1701409.7136
247 | Mohammadpur O/H | D409W | 11 | 0 | DHK61025 | 1 | 2305.67 | 2322.25 | 16.58 | 60000 | 0 | 994800 | 994423.0763 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1276110.3491 | 1960855.0924 | 652019.5995 | 1590403.2357 | 1624160.2917 | 1649627.8414 | 1683655.5249 | 1660825.6738 | 1343218.1949
248 | Bosila Feeder | C209V | 11 | 0 | DHK60997 | 1 | 4283.2 | 4309.7 | 26.5 | 60000 | 0 | 1590000 | 1589397.5587 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1495308.2511 | 1644331.8958 | 2353225.0751 | 2736001.9135 | 2540659.2659 | 2707281.1054 | 2444595.9223 | 2900301.4925 | 3015179.277
249 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIB 7375 | 1 | 6273.9 | 6319.12 | 45.22 | 60 | 0 | 2713.2 | 2712.172 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 3265.9877 | 3147.5116 | 4513.5238 | 7345.0244 | 8176.8893 | 8159.5525 | 8272.6804 | 8691.9141 | 0
250 | Dhaka Uddyan | G186D | 11 | 0 | DHK86067 | 1 | 3255.51 | 3255.51 | 0 | 60000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 31800 | 38757.9222 | 90112.6747 | 43181.0046 | 44366.4049 | 46170.0157 | 47362.5115 | 34177.6075 | 0
251 | Shia Mosjid | D409H | 11 | 0 | DHK60950 | 1 | 3612.35 | 3634.81 | 22.46 | 60000 | 0 | 1347600 | 1338621.2464 | Shyamoli | Japan Garden 33/11 KV | 86 | 1173600 | 1403763.4936 | 1651270.0056 | 1965935.1818 | 2358614.0108 | 2312098.4465 | 2316566.3838 | 2321079.2736 | 1677029.4105
252 | Shekhar Tek | G186S | 11 | 0 | DHK60977 | 1 | 2492.28 | 2516.63 | 24.35 | 60000 | 0 | 1461000 | 1451265.6879 | Adabor | Japan Garden 33/11 KV | 86 | 1188600 | 486290.8047 | 1243674.2652 | 1739834.6438 | 2042053.7165 | 2050068.6174 | 2089945.7593 | 2160384.5576 | 1966584.1503
253 | Madrasha Road | D434D | 11 | 0 | DHK61083 | 1 | 2126.47 | 2148.2 | 21.73 | 60000 | 0 | 1303800 | 1295113.0759 | Shyamoli | Japan Garden 33/11 KV | 86 | 1098000 | 944118.7603 | 1646495.8242 | 1898764.7302 | 2311849.4219 | 1518214.0214 | 1459844.4991 | 1147648.0831 | 1148666.6379
254 | Baitul Aman Housing | G186B | 11 | 0 | DHK668115 | 1 | 4293.9 | 4319.47 | 25.57 | 60000 | 0 | 1534200 | 1523977.9729 | Adabor | Japan Garden 33/11 KV | 86 | 1475400 | 1630860.6938 | 2021865.8399 | 2579465.2888 | 2865829.9369 | 2799581.8586 | 2963454.3569 | 2980047.5303 | 2714650.3131
255 | Shyamoli Square | D486G | 11 | 0 | DHK86063 | 1 | 487.51 | 491.2 | 3.69 | 30000 | 0 | 110700 | 109962.431 | Shyamoli | Japan Garden 33/11 KV | 86 | 85500 | 125054.8582 | 139346.4208 | 179920.8525 | 180163.5766 | 172388.0455 | 167267.6038 | 170888.0374 | 163284.9924
256 | Mohammadi Housing | G186E | 11 | 0 | DHK60948 | 1 | 3904.19 | 3920.87 | 16.68 | 60000 | 0 | 1000800 | 994131.8963 | Adabor | Japan Garden 33/11 KV | 86 | 1027200 | 0 | 796094.7552 | 1504138.327 | 1937732.7104 | 1867187.3865 | 2007211.2456 | 1954719.3056 | 1343295.1846
257 | Chand Housing | C286H | 11 | 0 | DHK60867 | 1 | 2244.2 | 2258.48 | 14.28 | 60000 | 0 | 856800 | 851091.3357 | Satmasjid | Japan Garden 33/11 KV | 86 | 627600 | 646167.2337 | 578272.7269 | 1066930.6554 | 1224872.5023 | 796282.8675 | 850127.1046 | 960570.6526 | 891350.9825
258 | PC Culture Housing | 0 | 11 | 0 | DHK60979 | 1 | 4268.17 | 4290.89 | 22.72 | 60000 | 0 | 1363200 | 1354117.3072 | Adabor | Japan Garden 33/11 KV | 86 | 1334400 | 1405580.2712 | 1788527.722 | 2352165.2785 | 2602029.6916 | 2565134.1168 | 2719447.494 | 2646665.9554 | 2456140.6176
259 | Mehedibagh | G186H | 11 | 0 | DHK68121 | 1 | 2501.63 | 2530.44 | 28.81 | 60000 | 0 | 1728600 | 1717082.7297 | Adabor | Japan Garden 33/11 KV | 86 | 1638000 | 1743500.9051 | 2209252.4615 | 2861941.0273 | 3070874.6729 | 3016640.8933 | 3040793.1415 | 3013625.5306 | 2845397.7111
260 | 33/11 kV Incoming (Spare) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | 0 | 1 | 670790 | 673444 | 2654 | 1 | 0 | 2654 | 2636.317 | Adabor | Japan Garden 33/11 KV | 86 | 3179 | 2605.0572 | 3087.304 | 4523.0103 | 4813.3552 | 5033.7309 | 5179.9 | 5393.4663 | 0
262 | Mokarom Bhabon | D3108MB | 11 | 0 | 2761 | 1 | 67.48 | 69.76 | 2.28 | 60000 | 0 | 136800 | 139649.7428 | Ramna | Dhaka University 33/11 KV S/S | 108 | 117558.3864 | 121084.3373 | 174337.3 | 202329.0481 | 226720.401 | 207689.3161 | 186304.8566 | 168036.2342 | 191876.7922
263 | 11 kV Shaid Minar RMU | D3108SM | 11 | 0 | 2850 | 1 | 150.87 | 153.05 | 2.18 | 60000 | 0 | 130800 | 133524.7541 | Ramna | Dhaka University 33/11 KV S/S | 108 | 112160.2972 | 143975.9036 | 186918.3422 | 606987.1444 | 637120.699 | 361224.6845 | 367165.7402 | 336672.5979 | 339844.4752
264 | 11 kV Shaidulla Hall | D3108SH | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | Spare | 0 | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | MBA Bhabon | D3108MA | 11 | 0 | 2836 | 1 | 110.14 | 112.26 | 2.12 | 60000 | 0 | 127200 | 129849.7608 | Ramna | Dhaka University 33/11 KV S/S | 108 | 100164.5435 | 110843.3735 | 176733.689 | 232348.1947 | 278853.9691 | 280291.312 | 263125.3657 | 250253.9631 | 301348.8178
269 | Suprime Court | 0 | 11 | 0 | 2835 | 1 | 75.41 | 77.13 | 1.72 | 60000 | 0 | 103200 | 105349.806 | Ramna | Dhaka University 33/11 KV S/S | 108 | 97165.6051 | 186144.5783 | 281575.7078 | 323006.0175 | 284309.8076 | 352893.3079 | 353253.3645 | 298264.3158 | 306762.2696
270 | Karjon Hall | D3108KH | 11 | 0 | 2853 | 1 | 82.55 | 85.39 | 2.84 | 60000 | 0 | 170400 | 173949.6796 | Ramna | Dhaka University 33/11 KV S/S | 108 | 164341.8259 | 174096.3855 | 243233.4838 | 317602.5711 | 349779.87 | 351108.0129 | 342970.3043 | 313267.551 | 333228.0341
271 | Spare | 0 | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | Swimming Pool | D3108SP | 11 | 0 | 2839 | 1 | 3.1 | 3.36 | 0.26 | 60000 | 0 | 15600 | 15924.9707 | Ramna | Dhaka University 33/11 KV S/S | 108 | 10196.3907 | 12048.1928 | 23963.89 | 46229.4858 | 46071.5253 | 0 | 0 | 0 | 0
273 | Spare | 0 | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | Police Head Quarter RMU | 0 | 11 | 0 | 2772 | 1 | 106.3 | 110 | 3.7 | 60000 | 0 | 222000 | 226624.5826 | Ramna | Dhaka University 33/11 KV S/S | 108 | 197929.9363 | 247590.3614 | 319318.8346 | 399254.6499 | 414643.728 | 474293.3666 | 554680.3686 | 488505.3381 | 444504.5437
275 | Spare | 0 | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | Spare | 0 | 11 | 0 | 2764 | 1 | 4.08 | 4.81 | 0.73 | 60000 | 0 | 43800 | 44712.4177 | Ramna | Dhaka University 33/11 KV S/S | 108 | 47983.0149 | 54216.8675 | 53918.7526 | 67242.8884 | 0 | 0 | 0 | 0 | 0
277 | Spare | 0 | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | Segunbagicha | D394S | 11 | 0 | DHK-C9360 | 1 | 31840.5 | 36770.24 | 4929.74 | 60 | 0 | 295784.4 | 297217.9806 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 341401.7306 | 331939.36 | 443816.6143 | 585591.0985 | 595887.9152 | 652730.1844 | 660791.8145 | 648570.0837 | 628132.1417
279 | Secretariat RMU | D394FB | 11 | 0 | DHK-C9379 | 1 | 84355.2 | 85730.16 | 1374.96 | 60 | 0 | 82497.6 | 82897.4418 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 71931.4615 | 90652.6074 | 124236.116 | 153919.5822 | 147122.5127 | 169088.4911 | 173479.2405 | 157347.3651 | 189151.3106
280 | NBR RMU | D394NR | 11 | 0 | DHK-C9319 | 1 | 86985.63 | 90868.82 | 3883.19 | 60 | 0 | 232991.4 | 234120.6413 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 264247.6855 | 246010.691 | 319447.2431 | 425924.9701 | 412789.7325 | 468220.1905 | 479026.3146 | 471677.0943 | 454185.7713
281 | Ramna 11 kV Sw/S-2 | 0 | 11 | 0 | DHK-C9364 | 1 | 84979.32 | 97750.53 | 12771.21 | 60 | 0 | 766272.6 | 769986.4995 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 654039.5407 | 593329.8083 | 847238.794 | 1202930.2093 | 1229384.6711 | 70113.1256 | 552257.97 | 1047973.9631 | 1309281.295
282 | Ramna 11 kV Sw/S-1 | 0 | 11 | 0 | DHK-C9375 | 1 | 57712.71 | 58182.9 | 470.19 | 60 | 0 | 28211.4 | 28348.1324 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 0 | 2122.6827 | 103793.1904 | 54867.1796 | 213365.2082 | 295845.9008 | 960645.5509 | 37569.2064 | 3932.094
283 | Family Planning | D394FP | 11 | 0 | DHK-C9378 | 1 | 85649.71 | 89440.33 | 3790.62 | 60 | 0 | 227437.2 | 228539.5217 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 220696.2725 | 256339.3842 | 360288.4749 | 436247.6925 | 440914.9728 | 477616.3037 | 472965.3149 | 459978.3897 | 450311.5022
284 | Muktijuddho Montranalaya | D394MJ | 11 | 0 | DHK-C9376 | 1 | 15380.32 | 23102.1 | 7721.78 | 60 | 0 | 463306.8 | 465552.3128 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 463016.929 | 483907.4515 | 671537.2027 | 860939.7125 | 912278.2358 | 979522.345 | 1003580.0431 | 989924.3443 | 925250.3935
285 | Purana Palton | D394R | 11 | 0 | DHK-C9318 | 1 | 77924.2 | 81427.53 | 3503.33 | 60 | 0 | 210199.8 | 211218.577 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 201300.5118 | 227725.5723 | 301353.4691 | 347167.2021 | 309416.4011 | 349193.9997 | 350733.9486 | 318744.0733 | 328976.7665
286 | Tip Top Feeder | 0 | 11 | 0 | DHK-C9318 | 1 | 15769.02 | 28227.41 | 12458.39 | 60 | 0 | 747503.4 | 751126.3307 | Kakrail | Biddyut Bhaban 33/11 KV | 94 | 665458.2263 | 736438.2437 | 1345378.9377 | 2213157.3667 | 1322789.6384 | 1326276.1291 | 1389761.4375 | 1427034.1549 | 1299449.2529
287 | 11/0.4 kV Auxiliary Transformer, AT | 0 | 0.415 | 0 | DHKD3784 | 1 | 366020 | 368550 | 2530 | 1 | 0 | 2530 | 2542.2622 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 2880.0422 | 3320.7304 | 4689.0579 | 5100.6865 | 4311.9923 | 4669.8501 | 4947.3654 | 4696.0253 | 4800.6724
288 | Nearest O/H | D398NE | 11 | 0 | 00000126 | 1 | 8336299 | 8445459 | 109160 | 1 | 0 | 109160 | 109110.5738 | Ramna | DMC 33/11 KV SS | 98 | 103620.5102 | 115623.9439 | 175545.4669 | 200195.8311 | 223877.2462 | 227289.0317 | 224820.1739 | 210729.7741 | 229906.9253
289 | Jagannath Hall | D398JA | 11 | 0 | 00000002 | 1 | 3181672 | 3244072 | 62400 | 1 | 0 | 62400 | 62371.7461 | Ramna | DMC 33/11 KV SS | 98 | 64828.5411 | 67777.2753 | 82037.8689 | 101039.4533 | 107985.9597 | 106229.8836 | 110593.2428 | 113276.1711 | 96242.8599
290 | Samsun Nahar Hall | D398SN | 11 | 0 | 00000024 | 1 | 10868893 | 11037013 | 168120 | 1 | 0 | 168120 | 168043.8775 | Ramna | DMC 33/11 KV SS | 98 | 181366.9249 | 166093.4323 | 229211.7629 | 277277.1279 | 321630.4227 | 329771.0476 | 322680.6125 | 293593.2672 | 312413.2678
291 | Spare, 4L | 0 | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | Board Office O/H, (5L) | A3983 | 11 | 0 | 00000023 | 1 | 23859342 | 24059182 | 199840 | 1 | 0 | 199840 | 199749.5152 | Lalbag | DMC 33/11 KV SS | 98 | 222501.681 | 618985.4813 | 282360.0725 | 404116.548 | 474520.243 | 554924.1978 | 600144.1706 | 492983.2953 | 466712.6927
293 | OT- Complex | D398OT | 11 | 0 | 00000167 | 1 | 7522541 | 7697461 | 174920 | 1 | 0 | 174920 | 174840.7986 | Ramna | DMC 33/11 KV SS | 98 | 155370.7198 | 194938.9033 | 340061.3683 | 106528.8271 | 336918.4015 | 246189.5687 | 446170.5101 | 427837.7768 | 405707.0733
294 | Alia Mdrasha O/H, (7L) | A3984 | 11 | 0 | 00000148 | 1 | 10039575 | 10103615 | 64040 | 1 | 0 | 64040 | 64011.0036 | Lalbag | DMC 33/11 KV SS | 98 | 42908.876 | 222332.0149 | 101819.0581 | 64901.5515 | 73635.9109 | 143184.6648 | 77701.5086 | 75154.3226 | 71193.4446
295 | Majed Sordar Road | B698J | 11 | 0 | 00000164 | 1 | 64831840 | 66168440 | 1336600 | 1 | 0 | 1336600 | 1335994.8057 | Bangshal | DMC 33/11 KV SS | 98 | 1324591.4203 | 1288158.0478 | 1959932.9522 | 1719312.7006 | 1747073.1814 | 1774470.2621 | 1602752.7729 | 1759301.3409 | 1689289.8138
296 | Chankharpool, 9L | B698Q | 11 | 0 | 00000001 | 1 | 52091712 | 52823192 | 731480 | 1 | 0 | 731480 | 731148.7958 | Bangshal | DMC 33/11 KV SS | 98 | 644572.6762 | 708065.5404 | 416746.8435 | 1136431.6854 | 1199639.3416 | 1210601.5564 | 1176945.2408 | 1201456.0712 | 1157798.1959
297 | Shahidullah College O/H, (10L) | A3986 | 11 | 0 | 00000003 | 1 | 14293560 | 14564044 | 270484 | 1 | 0 | 270484 | 270361.5285 | Lalbag | DMC 33/11 KV SS | 98 | 292007.2179 | 203128.5964 | 207912.8783 | 235452.0398 | 255337.0354 | 264888.6074 | 263222.0224 | 263967.4494 | 265403.8751
298 | Ananda Bazar | D398AB | 11 | 0 | 00000111 | 1 | 15493882 | 15623002 | 129120 | 1 | 0 | 129120 | 129061.5362 | Ramna | DMC 33/11 KV SS | 98 | 67251.0523 | 68098.5089 | 103817.0773 | 119468.7736 | 114687.4296 | 145238.9396 | 167074.5674 | 216784.0965 | 169141.9631
299 | Hosseni Dalan O/H, (12L) | A3985 | 11 | 0 | 0 | 1 | 69.55 | 71.4 | 1.85 | 60000 | Estimated | 573456.6 | 573196.9466 | Lalbag | DMC 33/11 KV SS | 98 | 347228.9299 | 694054.226 | 859332.9703 | 999393.6344 | 862949.5725 | 1039954.5727 | 1170127.1783 | 1629339.2554 | 1651805.4359
300 | Badrun Nessa College | A398W | 11 | 0 | 00000006 | 1 | 21900706 | 22150383 | 249677 | 1 | 0 | 249677 | 249563.9496 | Lalbag | DMC 33/11 KV SS | 98 | 261372.8699 | 289624.6661 | 354408.6447 | 469459.7974 | 504253.5009 | 510636.8949 | 522687.5196 | 511348.0734 | 487810.3149
301 | Dhaka Medical College, Unit-II | D398DM | 11 | 0 | 00000125 | 1 | 13442768 | 13442768 | 0 | 1 | Estimated | 217240 | 217141.6367 | Ramna | DMC 33/11 KV SS | 98 | 438463.9439 | 173192.8473 | 223818.1101 | 299392.072 | 310172.7151 | 327495.1248 | 332597.3491 | 314783.3957 | 318669.3545
302 | Spare, 15L | 0 | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | Sheikh Hasina National Burn Institute | D398SH | 11 | 0 | 00000127 | 1 | 23060064 | 23402142 | 342078 | 1 | 0 | 342078 | 341923.1117 | Ramna | DMC 33/11 KV SS | 98 | 318090.2115 | 352759.9386 | 420023.595 | 543136.2141 | 551404.561 | 585271.851 | 637362.5402 | 594088.462 | 527600.9918
304 | Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKF-7804 | 1 | 2923.68 | 2923.68 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 0 | 0 | 5076.9668 | 7678.1323 | 7994.6127 | 7937.0165 | 8829.1604 | 8254.0596 | 7320.9952
305 | Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | Secratariet East | D363BS | 11 | 0 | BD 013966 | 1 | 4767.71 | 4874.78 | 107.07 | 1000 | 0 | 107070 | 107127.018 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 107180.1737 | 119229.0018 | 176076.397 | 242760.0671 | 221126.0937 | 241216.6768 | 260076.7434 | 245293.0009 | 245463.3743
307 | Taher Bag O/H | B163G | 11 | 0 | BD 014045 | 1 | 22237.12 | 22685.2 | 448.08 | 1000 | 0 | 448080 | 448318.6163 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 502491.425 | 463042.5281 | 606900.3521 | 725752.2867 | 829864.029 | 794329.1648 | 678707.287 | 744464.9674 | 740283.3012
308 | Al Raji Complex | D363AR | 11 | 0 | BD 013983 | 1 | 17531.62 | 17966.27 | 434.65 | 1000 | 0 | 434650 | 434881.4644 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 415679.6453 | 470414.0777 | 584839.7594 | 756317.9861 | 777798.4115 | 793783.38 | 773675.1898 | 784809.8778 | 793405.3649
309 | Raduni | D363RI | 11 | 0 | BD 013999 | 1 | 33159.17 | 33855.6 | 696.43 | 1000 | 0 | 696430 | 696800.8703 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 678307.0986 | 766711.9498 | 970925.0317 | 1082729.9623 | 1265333.7606 | 1301100.4786 | 623159.8339 | 1293358.488 | 1280815.0384
310 | Sundor Bon Square O/H | B163D | 11 | 0 | BD 013954 | 1 | 15297.78 | 15663.4 | 365.62 | 1000 | 0 | 365620 | 365814.7038 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 358907.9483 | 345289.8586 | 413245.1984 | 496614.8713 | 482395.9106 | 519829.721 | 434096.0289 | 473931.0551 | 515871.5523
311 | Shromo Bhobon O/H | D363SB | 11 | 0 | BD 013985 | 1 | 15110.41 | 15350.3 | 239.89 | 1000 | 0 | 239890 | 240017.7488 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 224965.7144 | 289280.2377 | 470791.9727 | 489342.1006 | 495640.2335 | 516585.3335 | 525134.9167 | 505142.6077 | 521299.6391
312 | Nawabpur Road | B163P | 11 | 0 | BD 013953 | 1 | 23709.12 | 24208.6 | 499.48 | 1000 | 0 | 499480 | 499745.9884 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 556908.629 | 525806.8749 | 713209.502 | 834593.0606 | 843248.6095 | 904941.5553 | 800366.4326 | 843066.7121 | 849749.7199
313 | Spair | 0 | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | Spare | 0 | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | Ahad Police Box | D363AP | 11 | 0 | BD 013984 | 1 | 13292.97 | 13673.3 | 380.33 | 1000 | 0 | 380330 | 380532.5373 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 329304.2587 | 439138.0789 | 488719.3167 | 481256.786 | 438024.4232 | 458924.1778 | 366641.2546 | 470281.7667 | 423970.1788
316 | Nearest O/H | D363NE | 11 | 0 | BD 013997 | 1 | 3134.09 | 3210.8 | 76.71 | 1000 | 0 | 76710 | 76750.8504 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 76663.1031 | 88852.9589 | 103430.8152 | 124640.2411 | 121402.9541 | 117384.1651 | 114763.3233 | 117912.5625 | 115595.8875
317 | Natab Bhaban | D363NB | 11 | 0 | BD 014000 | 1 | 5718.35 | 5841.7 | 123.35 | 1000 | 0 | 123350 | 123415.6876 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 106896.0107 | 126327.5311 | 141307.3092 | 179461.8844 | 187424.2009 | 177268.8886 | 180013.0381 | 185708.2311 | 177165.0302
318 | Spare | 0 | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | Awami League Party Office | D363AO | 11 | 0 | BD 013956 | 1 | 1466.68 | 1473.7 | 7.02 | 1000 | 0 | 7020 | 7023.7384 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 6921.3974 | 7715.3531 | 18136.4963 | 10332.35 | 10118.5826 | 5579.1337 | 3568.1872 | 9417.1914 | 9250.1106
320 | Khaddar Bazar | D363KB | 11 | 0 | BD 014012 | 1 | 11770.14 | 12032.5 | 262.36 | 1000 | 0 | 262360 | 262499.7147 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 245110.8375 | 287065.7392 | 332552.2312 | 396371.0138 | 401687.6915 | 409449.7945 | 392931.5775 | 394275.1992 | 392631.6173
321 | Bangobondu National Stidium | D363NS | 11 | 0 | BD 014008 | 1 | 12229.98 | 12597.7 | 367.72 | 1000 | 0 | 367720 | 367915.8221 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 347998.121 | 393341.4417 | 1044626.3348 | 1319581.5303 | 1315375.6615 | 1298280.5904 | 390265.4601 | 288658.7112 | 290128.194
322 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4418 | 1 | 1611.8 | 1673.62 | 61.82 | 100 | 0 | 6182 | 6185.2921 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 6468.7665 | 6753.7147 | 7343.2393 | 8140.4874 | 6640.1946 | 13693.1347 | 0 | 0 | 1718.8942
323 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 48.15 | 48.15 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 0 | 4.0447 | 0 | 0 | 30.0552 | 597.3312 | 0 | 0 | 387.2849
324 | 11 KV Ring Road Feeder | G134R | 11 | 0 | 77816675 | 1 | 42620.61 | 42702.034 | 81.424 | 8000 | 0 | 651392 | 667676.8 | Adabor | Kallyanpur 33/11KV S/S | 34 | 639928 | 708152 | 871742 | 1122088 | 1191132 | 1186458 | 1209910 | 1172682 | 1124384
325 | 11 KV Gano Bhavan RMU | D534T | 11 | 0 | DHK14997 | 1 | 996.05 | 996.18 | 0.13 | 40000 | 0 | 5200 | 5330 | Shere b.nagar | Kallyanpur 33/11KV S/S | 34 | 1640 | 4510 | 1230 | 2050 | 2050 | 1230 | 1230 | 1230 | 1230
326 | 11 KV Adabor O/H | D434A | 11 | 0 | DHK14957 | 1 | 4683.11 | 4698.53 | 15.42 | 40000 | 0 | 616800 | 632220 | Adabor | Kallyanpur 33/11KV S/S | 34 | 865100 | 1686740 | 1540370 | 2118880 | 2481320 | 2098790 | 1976610 | 2150040 | 2995460
327 | 11 KV Goidertek (DPDC) | G134G | 11 | 0 | DHK14996 | 1 | 9445.51 | 9452.95 | 7.44 | 40000 | 0 | 297600 | 305040 | Adabor | Kallyanpur 33/11KV S/S | 34 | 271830 | 319390 | 663380 | 612540 | 617460 | 614590 | 586300 | 591220 | 558420
328 | 11 KV Beribandh Feeder. | G134K | 11 | 0 | DHK14960 | 1 | 9682.86 | 9688.09 | 5.23 | 40000 | 0 | 209200 | 214430 | Adabor | Kallyanpur 33/11KV S/S | 34 | 188190 | 213610 | 230010 | 285360 | 348090 | 239440 | 234930 | 301350 | 184500
329 | 11 KV Sewarage Pump | G134P | 11 | 0 | DHK14959 | 1 | 2456.54 | 2510.39 | 53.85 | 40000 | 0 | 2154000 | 2207850 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2131590 | 2234090 | 2206210 | 2792510 | 1776530 | 2952000 | 2380460 | 2601450 | 535870
330 | 11 KV Technical School (DPDC) | G134T | 11 | 0 | DHK15019 | 1 | 8461.48 | 8491.99 | 30.51 | 40000 | 0 | 1220400 | 1250910 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1184900 | 1268950 | 1626470 | 2204980 | 2398910 | 2363240 | 2400960 | 2347660 | 2184890
331 | 11 KV Mansurabad | G134M | 11 | 0 | 77816681 | 1 | 53300.91 | 53472.8 | 171.89 | 8000 | 0 | 1375120 | 1409498 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1315854 | 1394820 | 1650496 | 2258116 | 2458196 | 2422936 | 2313630 | 2379804 | 2220888
332 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 41136.9 | 41136.9 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Moghbazar 33/11KV S/S | 8 | 0 | 31110.7192 | 140940.5878 | 170232.3057 | 173300.7767 | 177316.5531 | 65016.8533 | 1691.4448 | 1119.369
333 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 81608.6 | 81937.7 | 329.1 | 1000 | 0 | 329100 | 320804.0202 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 291760.8196 | 288727.5453 | 67586.7284 | 136288.0862 | 107803.7381 | 78656.0729 | 96666.9717 | 802696.2793 | 1023306.7911
334 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1589911.0287
335 | 11 kV Tejgaon S/S-1 | 0 | 11 | T-1 | 30/11004-1101 | 1 | 121644.9 | 121886.8 | 241.9 | 1000 | 0 | 241900 | 235802.1649 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 252158.3911 | 297157.5466 | 354627.9687 | 467141.9849 | 391310.8557 | 416531.5604 | 434303.9973 | 326660.2796 | 342221.6327
336 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 126698.4 | 127274.6 | 576.2 | 1000 | Estimated | 1137855.6 | 1109172.4426 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1135510.6851 | 1220672.6215 | 1548241.5645 | 1803211.1873 | 1782922.7783 | 2012798.2977 | 1909092.2251 | 1919578.4326 | 1819483.4353
338 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 136176.7 | 137436.2 | 1259.5 | 1000 | 0 | 1259500 | 1227750.4206 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 1074277.2921 | 1214221.262 | 1754826.6729 | 2252689.725 | 2523568.5136 | 2372564.6062 | 2579216.4264 | 2455343.5773 | 1989016.959
339 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 152262.9 | 153366.6 | 1103.7 | 1000 | 0 | 1103700 | 1075877.8398 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 897491.265 | 1130924.8203 | 1339188.5287 | 1537918.5242 | 1644738.2335 | 1666230.9769 | 1593234.7726 | 1205154.4296 | 1055666.7314
340 | 11 kV Vumi Bhaban | 0 | 11 | T-3 | 21101039 | 1 | 9217.9 | 9274.5 | 56.6 | 1000 | 0 | 56600 | 55173.2226 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 55030.6699 | 63225.0099 | 102897.7587 | 143547.2416 | 140604.4879 | 151132.7739 | 165331.6353 | 136267.0228 | 122011.2214
341 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10433.8 | 10527.2 | 93.4 | 1000 | 0 | 93400 | 91045.5651 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 93945.2151 | 96945.0152 | 117467.3528 | 150704.1553 | 173927.5426 | 164434.1337 | 177991.6827 | 170095.919 | 154167.6401
342 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 132251.8 | 133366 | 1114.2 | 1000 | 0 | 1114200 | 1086113.1549 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1050201.374 | 1151196.9663 | 1495406.9549 | 1911100.4557 | 2221153.9574 | 2075012.1387 | 2269581.709 | 2138303.3901 | 1962152.1029
343 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 92305.8 | 93305.9 | 1000.1 | 1000 | 0 | 1000100 | 974889.3971 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 881768.2165 | 1040603.3776 | 1298009.1897 | 1555095.1172 | 1652781.7295 | 1586003.8772 | 1603212.6065 | 1595983.8968 | 78254.0694
344 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 182592.9 | 183797 | 1204.1 | 1000 | 0 | 1204100 | 1173746.9483 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 687490.2978 | 1042108.7349 | 1981464.8041 | 2346752.0201 | 2390485.2167 | 1095738.7944 | 1085008.9734 | 952812.0065 | 1869447.9972
345 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124987.8 | 125221.7 | 233.9 | 1000 | 0 | 233900 | 228003.8296 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 193491.7662 | 239452.1804 | 307276.7877 | 363366.7355 | 399563.2736 | 370867.0494 | 398147.7603 | 399920.9831 | 690345.3929
346 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 117806.9 | 118298.6 | 491.7 | 1000 | 0 | 491700 | 479305.186 | Kakrail | Moghbazar 33/11KV S/S | 8 | 469726.0754 | 536710.0842 | 748310.5439 | 931830.1708 | 991857.0675 | 900407.8011 | 994564.7368 | 950591.9851 | 944645.6784
347 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 45592.3 | 45896.4 | 304.1 | 1000 | 0 | 304100 | 296434.2222 | Kakrail | Moghbazar 33/11KV S/S | 8 | 268569.323 | 312512.1919 | 397324.9737 | 478388.5637 | 514783.7418 | 344054.8595 | 0 | 0 | 323294.1205
348 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19580.9 | 19580.9 | 0 | 1000 | 8354118.414 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 3341.1478 | 0 | 0 | 0 | 1357.9928 | 0 | 0 | 0 | 0
349 | 11 kV TCB Feeder | C608P | 11 | T-4 | 0 | 1 | 37226.1 | 37317.2 | 91.1 | 1000 | 0 | 91100 | 109962.7341 | Kakrail | Moghbazar 33/11KV S/S | 8 | 17261.2059 | 91371.619 | 275835.9679 | 327449.4305 | 337617.6819 | 593608.4852 | 1091208.9552 | 1058026.2525 | 587067.814
350 | 11 kV Tejgaon SS-2 | 0 | 11 | T-4 | 0 | 1 | 37710.4 | 38269.9 | 559.5 | 1000 | 0 | 559500 | 675347.4173 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 975202.4512 | 1203222.2332 | 1541959.4958 | 1519526.851 | 1537848.541 | 1385049.7687 | 1574127.4074 | 1532552.8114 | 1481122.0985
351 | Holy Day Inn | C108HY | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 270030 | 325941.1316 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 253338.8211 | 285755.7964 | 328334.8182 | 421689.4191 | 437235.9991 | 578900.3818 | 542740.3295 | 522630.1141 | 493817.3233
352 | Polly Bhabon-2 | C608PB | 11 | T-4 | 0 | 1 | 18386 | 18386 | 0 | 1000 | According to AMR meter reading | 8748 | 10559.3194 | Kakrail | Moghbazar 33/11KV S/S | 8 | 10550.4945 | 10470.3421 | 17302.438 | 23296.5077 | 25096.5994 | 28135.8532 | 27898.691 | 30058.9479 | 29444.1053
353 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 | 0 | 1 | 23357.9 | 24355.8 | 997.9 | 1000 | 0 | 997900 | 1204520.4428 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1012843.0163 | 991647.6183 | 1456551.0784 | 1783228.8258 | 1839066.8165 | 1861301.6803 | 1854771.9565 | 1842884.7823 | 1860061.7445
354 | 11 kV Tejturibazar | C608X | 11 | T-4 | 0 | 1 | 3354.85 | 3370.19 | 15.34 | 1000 | Estimated | 307221.012 | 370832.7382 | Kakrail | Moghbazar 33/11KV S/S | 8 | 365724.4924 | 331669.222 | 405180.9614 | 781650.0519 | 797094.2458 | 844174.6782 | 788742.3253 | 776669.7972 | 731592.6735
355 | Songsad | 0 | 11 | T-4 | 0 | 1 | 3864.8 | 3864.8 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 154587.5799 | 443228.713 | 416692.9 | 475259.7411 | 544550.7215 | 126381.9385
356 | Chennel 24 | 0 | 11 | T-4 | 0 | 1 | 7337.59 | 7353.27 | 15.68 | 1000 | 0 | 15680 | 18926.6265 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 4476.7773 | 3956.1852 | 2657.627 | 3644.2295 | 5053.7147 | 7574.2329 | 3766.4072 | 1700.7368 | 1164.858
357 | Sonargaon | C608K | 11 | T-4 | 0 | 1 | 43332 | 43490.8 | 158.8 | 1000 | 0 | 158800 | 191680.3751 | Kakrail | Moghbazar 33/11KV S/S | 8 | 346671.8318 | 490675.349 | 653797.6846 | 888533.2859 | 916526.5008 | 698965.1841 | 733347.8124 | 844174.3497 | 839625.5215
358 | AT -1 | 0 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7215.9345
359 | AT -2 | 0 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 2907770.785 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 252304 | 265229 | 12925 | 60 | 0 | 775500 | 786282.6593 | Kakrail | T&T 33/11 KV | 105 | 736632.0122 | 872488.6042 | 1045950.5553 | 350929.0306 | 1384212.3787 | 1354639.697 | 1410640.1386 | 1413099.3422 | 1314936.3633
361 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 534944 | 547858 | 12914 | 60 | 0 | 774840 | 785613.4825 | Kakrail | T&T 33/11 KV | 105 | 796668.3127 | 827866.8536 | 1005950.1284 | 1232617.5702 | 1434115.4167 | 1367760.1292 | 1475917.0544 | 1466512.1688 | 1363050.3594
362 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 974455 | 977621 | 3166 | 60 | 0 | 189960 | 192601.2301 | Moghbazar | T&T 33/11 KV | 105 | 183214.2275 | 200252.2312 | 266002.8385 | 363967.9203 | 383823.6058 | 382050.2122 | 390823.0756 | 376350.3769 | 416269.8468
363 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 2016391 | 2024815 | 8424 | 60 | 0 | 505440 | 512467.7077 | Moghbazar | T&T 33/11 KV | 105 | 515544.9865 | 531520.2274 | 691583.1374 | 808883.1556 | 925176.0601 | 915135.1719 | 946635.0529 | 901476.4809 | 862940.0791
364 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 720.76 | 735.76 | 15 | 60000 | 0 | 900000 | 912513.7245 | Moghbazar | T&T 33/11 KV | 105 | 878015.6733 | 942149.4621 | 1206073.4761 | 1469087.5693 | 1653485.829 | 1672106.229 | 1759482.372 | 1708010.1623 | 1630130.9123
365 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 934914 | 940400 | 5486 | 60 | 0 | 329160 | 333736.6862 | Kakrail | T&T 33/11 KV | 105 | 331417.4279 | 356852.7499 | 456065.4727 | 614479.8006 | 616445.7818 | 601742.5641 | 617435.7813 | 612807.1598 | 591251.5937
366 | 11 kV cinema hall | 0 | 11 | Mogbazar | DHK60979 | 1 | 555813 | 566022 | 10209 | 60 | 0 | 612540 | 621056.8409 | Moghbazar | T&T 33/11 KV | 105 | 574972.3996 | 630645.9913 | 805584.354 | 981161.6979 | 1071064.8459 | 1069584.8264 | 1086052.1721 | 1077858.8375 | 1046359.7284
367 | 11 kV malibagh bazar | 0 | 11 | Khailgaon | DHK61106 | 1 | 833874 | 849490 | 15616 | 60 | 0 | 936960 | 949987.6214 | Khilgaon | T&T 33/11 KV | 105 | 875336.5686 | 972281.2692 | 1271165.0797 | 1621719.2778 | 1701657.7808 | 1728362.3289 | 1686240.4748 | 1646555.4045 | 1662984.8723
368 | 11 kv Sherebangla | D1105G | 11 | 0 | DHK60915 | 1 | 807901 | 820487 | 12586 | 60 | 0 | 755160 | 765659.8491 | Moghbazar | T&T 33/11 KV | 105 | 757821.2947 | 803676.5296 | 1035344.3815 | 1275392.2083 | 1525385.4467 | 1396637.0623 | 1544547.6466 | 1416880.2502 | 1438632.4204
369 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 380856 | 388308 | 7452 | 60 | 0 | 447120 | 453336.8183 | Moghbazar | T&T 33/11 KV | 105 | 416905.223 | 574990.0578 | 572490.9575 | 647224.5235 | 706402.574 | 705627.6304 | 690498.0173 | 692746.3564 | 708065.6738
370 | Auxiliary | 0 | 0 | Export | U0004461 | 1 | 8409.19 | 8441.86 | 32.67 | 60 | 0 | 1960.2 | 1987.4549 | Moghbazar | T&T 33/11 KV | 105 | 2258.9724 | 2339.6105 | 2704.2713 | 3869.1873 | 7599.4686 | 0 | 4061.5417 | 3583.4605 | 3045.4245
371 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 568927.8 | 570844.9384 | Moghbazar | Ullon local 33/11KV S/S | 92 | 552064.0532 | 594097.7099 | 711283.282 | 977173.2999 | 1007307.2369 | 980334.5269 | 1038100.3806 | 1138226.0536 | 978294.9507
372 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1046827.152 | 1050354.6866 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1042787.6561 | 1069375.8779 | 1304019.3504 | 1832199.9373 | 1836854.3731 | 1838127.2379 | 1648747.6632 | 1617479.1288 | 1406298.9916
373 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 933041.592 | 936185.6989 | Moghbazar | Ullon local 33/11KV S/S | 92 | 920106.7554 | 926792.4275 | 1244745.7435 | 1526833.2811 | 1659094.2725 | 1654314.5141 | 1770877.1198 | 1677385.7633 | 1345155.5572
374 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 512035.02 | 513760.4445 | Moghbazar | Ullon local 33/11KV S/S | 92 | 490723.6029 | 594097.7099 | 924668.2666 | 1038246.6311 | 1125813.9706 | 1102876.3427 | 1282359.2936 | 1317945.9568 | 1100581.8195
375 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 933041.592 | 936185.6989 | Moghbazar | Ullon local 33/11KV S/S | 92 | 920106.7554 | 950556.3359 | 1185472.1367 | 1710053.2748 | 1718347.6394 | 1715585.422 | 1648747.6632 | 1557572.4944 | 1345155.5572
376 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 546170.688 | 548011.1408 | Moghbazar | Ullon local 33/11KV S/S | 92 | 490723.6029 | 534687.9389 | 889104.1025 | 1099319.9624 | 1149515.3174 | 1225418.1586 | 1282359.2936 | 1377852.5912 | 1222868.6883
377 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | AT-1 | 0 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | AT-2 | 0 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 19.1733 | 20.183 | 1.0096 | 1000000 | 0 | 1009624 | 1015289.519 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1018645.2215 | 1077503.1322 | 1312980.8765 | 1733090.4653 | 1860379.5125 | 1839023.3133 | 1914129.2674 | 1830321.6533 | 1753548.1446
381 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 108640.5 | 109694.8 | 1054.3 | 1000 | 0 | 1054300 | 1060216.219 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1045576.9001 | 1122772.0794 | 1278337.9483 | 1814364.7668 | 1995837.5311 | 1955619.6426 | 2015001.2811 | 1947058.9925 | 1858521.5132
382 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 10038.7 | 11333.5 | 1294.8 | 1000 | 0 | 1294800 | 1302065.7881 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1278475.055 | 1329061.2073 | 1227377.6551 | 2135456.6106 | 2140470.7173 | 2127980.2733 | 2037129.655 | 2033626.6462 | 1264456.5681
383 | Goran | A921G | 11 | 0 | X1390296 | 1 | 37628.5 | 38632.1 | 1003.6 | 1000 | 0 | 1003600 | 1009231.7153 | Bashabo | Madarteck 33/11KV S/S | 21 | 995677.3386 | 1112714.1015 | 1214687.9378 | 1825010.9149 | 1949936.5823 | 1924894.1079 | 2047460.5279 | 1968306.9598 | 1851494.7743
384 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 16940.342 | 17797.798 | 857.456 | 1000 | 0 | 857456 | 862267.6262 | Mugdapara | Madarteck 33/11KV S/S | 21 | 821484.6094 | 872035.7411 | 1038687.6018 | 1446701.0468 | 1502775.9682 | 1533961.2033 | 1583000.8619 | 1493157.2972 | 2039169.8043
385 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373198.8946 | 881499.2996
386 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 2023.5624 | 2195.3558 | 171.7934 | 1000 | 0 | 171793.4 | 172757.421 | Mugdapara | Madarteck 33/11KV S/S | 21 | 187406.4551 | 177202.562 | 183059.6459 | 244346.2732 | 252299.2953 | 242642.782 | 236939.3158 | 229733.5056 | 209712.5124
387 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 6111.0168 | 6481.5268 | 370.51 | 1000 | 0 | 370510 | 372589.122 | Mugdapara | Madarteck 33/11KV S/S | 21 | 372057.1666 | 400135.7324 | 375481.886 | 578366.2569 | 687579.7395 | 671883.3535 | 576962.6065 | 679941.1966 | 331641.7074
388 | Mugdapara | B921P | 11 | 0 | X0854272 | 1 | 5258.7 | 5404.2 | 145.5 | 1000 | 0 | 145500 | 146316.4753 | Maniknagar | Madarteck 33/11KV S/S | 21 | 145473.3183 | 157809.6742 | 277461.6755 | 259324.0979 | 280126.3587 | 262278.8244 | 99804.6 | 280453.0279 | 256934.2344
389 | Singapur | F221S | 11 | 0 | X1390302 (N) | 1 | 44586.9 | 45819.9 | 1233 | 1000 | 0 | 1233000 | 1239918.9965 | Banosree | Madarteck 33/11KV S/S | 21 | 1267509.224 | 1335498.3132 | 1578862.6815 | 2168600.2792 | 2400509.1335 | 2332917.0805 | 2449510.2642 | 2359732.7837 | 2200082.1244
390 | Trimohony | F221T | 11 | 0 | X1390308 | 1 | 37205.2 | 38505 | 1299.8 | 1000 | 0 | 1299800 | 1307093.8456 | Banosree | Madarteck 33/11KV S/S | 21 | 1512479.8534 | 1311158.0066 | 1565165.8438 | 2029899.048 | 2144287.4264 | 2101565.9326 | 2104795.0854 | 2021980.735 | 1604947.893
391 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 170.2634 | 1198.3345 | 1028.0711 | 1000 | 0 | 1028071.1 | 1033840.1352 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1000706.9327 | 1113979.3951 | 1516431.2867 | 1620835.8728 | 1884688.9362 | 1948965.1387 | 1816135.3069 | 1942171.9601 | 1839386.3794
392 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 8394.9392 | 8860.1024 | 465.1632 | 1000 | 0 | 465163.2 | 467773.4697 | Mugdapara | Madarteck 33/11KV S/S | 21 | 445453.3853 | 237237.5261 | 554113.2234 | 808655.6976 | 863662.2068 | 854936.3865 | 710891.4812 | 850151.1099 | 596386.824
393 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 766942 | 772268 | 5326 | 200 | 0 | 1065200 | 1071177.3845 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1094168.6102 | 1233912.7358 | 1333024.5871 | 1795382.4839 | 1921009.9451 | 1954912.1468 | 1661387.6173 | 1892982.4123 | 480873.3471
394 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 792410 | 797029 | 4619 | 200 | 0 | 923800 | 928983.9165 | Mugdapara | Madarteck 33/11KV S/S | 21 | 888936.5428 | 962347.331 | 1198876.1472 | 1488652.8964 | 1652835.9122 | 1533042.4693 | 1508090.9874 | 1450702.4488 | 298789.1572
395 | Nakhal Para Feeder | C110U | 11 | 0 | DHK60950 | 1 | 351484.6 | 365588.1 | 14103.5 | 60 | 0 | 846210 | 868270.1537 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 777981.0035 | 879252.6995 | 1127439.9287 | 1500089.328 | 1599409.3479 | 1587033.6595 | 1590100.5899 | 1545202.0376 | 1536369.5556
396 | Badda-Meghna Feeder | C110N | 11 | 0 | DHK60979 | 1 | 968577.3 | 976789.1 | 8211.8 | 60 | 0 | 492708 | 505552.5826 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 469013.0985 | 510250.4136 | 710173.5747 | 794267.6303 | 812324.781 | 768867.2754 | 797427.1133 | 711868.0468 | 842649.7133
397 | Rasulbagh Feeder | C110K | 11 | 0 | DHK60948 | 1 | 146096.4 | 165694.3 | 19597.9 | 60 | 0 | 1175874 | 1206528.2834 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1135539.4567 | 1234476.6108 | 1507771.5116 | 1806034.3017 | 1726738.2372 | 1932163.7903 | 1821935.9992 | 1845073.9247 | 1902151.6741
398 | Lukas | C171V | 11 | 0 | 8A021100948-02 | 1 | 77490225 | 78636044 | 1145819 | 1 | 0 | 1145819 | 1175689.7688 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1010954.3559 | 1372928.0674 | 1596720.7407 | 2026298.4778 | 2352263.3192 | 2382018.4101 | 2450636.3287 | 2356930.5125 | 2345545.782
399 | PWD RMU | 0 | 11 | 0 | 0 | 1 | 663812.1 | 664891.07 | 1078.97 | 1 | 0 | 1078.97 | 1107.0981 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1121.3203 | 1215.4763 | 1463.309 | 1806.986 | 1917.0903 | 1854.955 | 1876.4622 | 1825.2484 | 1757.0539
400 | Civil Aviation Feeder | 0 | 11 | 0 | DHK60977 | 1 | 75045.2 | 104221.4 | 29176.2 | 60 | 0 | 1750572 | 1796208.2928 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1647887.2922 | 1749250.8125 | 2103712.8393 | 2870937.6357 | 3006456.2987 | 2816826.0828 | 2972868.5519 | 2843930.4649 | 2795399.6317
401 | Ahasanullah Eng. | C171L | 11 | 0 | DHK60867 | 1 | 920168.5 | 925616.4 | 5447.9 | 60 | 0 | 326874 | 335395.3962 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 345298.926 | 373294.7093 | 467019.6637 | 571155.4762 | 575802.5636 | 668050.5071 | 681476.0179 | 638085.1899 | 673101.4258
402 | New GMG Feeder | C110M | 11 | 0 | DHK61106 | 1 | 226666.6 | 250038.5 | 23371.9 | 60 | 0 | 1402314 | 1438871.4294 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1344265.9199 | 1443806.8354 | 1745180.0137 | 1868942.3881 | 2083647.5312 | 2435471.7452 | 2366892.1845 | 2233355.6797 | 2281871.6214
403 | Shikajo | C171Z | 11 | 0 | HA021101036-02 | 1 | 67747307 | 68364188 | 616881 | 1 | 0 | 616881 | 632962.6933 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 500012.7069 | 526544.3716 | 677285.3335 | 862880.7653 | 832111.8625 | 813808.0835 | 877169.4199 | 833321.8823 | 756034.1648
404 | Kahinur | 0 | 11 | 0 | 0 | 1 | 629590.2 | 643107.3 | 13517.1 | 60 | 0 | 811026 | 832168.9293 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 770227.3214 | 872220.4314 | 1070076.3665 | 1309013.1381 | 1330662.8857 | 1351230.8033 | 1347009.4431 | 1251045.3402 | 1294083.2246
405 | Link road | C171X | 11 | 0 | 8A021100380-02 | 1 | 67053201 | 67314478 | 261277 | 1 | 0 | 261277 | 268088.3243 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 237640.4803 | 295016.3311 | 416288.669 | 724119.8808 | 647867.3456 | 425896.0895 | 415317.8944 | 416737.628 | 435428.3198
406 | Shanta | C110E | 11 | 0 | 0 | 1 | 363300.9 | 370028.3 | 6727.4 | 60 | 0 | 403644 | 414166.741 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 368965.1962 | 423707.852 | 526308.4207 | 628311.0309 | 599004.2611 | 643052.4099 | 671568.0547 | 608607.1616 | 630895.3248
407 | Karnafuly Feeder | C110Y | 11 | 0 | DHK61084 | 1 | 38208.8 | 38707.8 | 499 | 1000 | 0 | 499000 | 512008.611 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 447459.6361 | 471151.8148 | 622218.1242 | 807314.3803 | 766856.2088 | 716684.8588 | 722759.1976 | 686952.8872 | 738300.0364
408 | Butex | C110BT | 11 | 0 | 0 | 1 | 1556 | 1632.1 | 76.1 | 1000 | 0 | 76100 | 78083.8783 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 78020.671 | 76715.652 | 104608.2847 | 106281.4076 | 100920.6493 | 102946.4154 | 100374.7899 | 90006.1656 | 91610.1416
409 | OriON LAB | C171A | 11 | 0 | 0 | 1 | 8567709 | 8638421 | 70712 | 1 | 0 | 70712 | 72555.4166 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 53925.9927 | 60857.0249 | 76732.1885 | 90864.5418 | 93311.3932 | 93876.22 | 95833.6401 | 88588.4676 | 248723.2522
410 | Nina kabbo | C171Y | 11 | 0 | 201101025-2 | 1 | 18183943 | 18353070 | 169127 | 1 | 0 | 169127 | 173536.0328 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 157354.7907 | 175839.1746 | 208000.4981 | 261868.4978 | 264819.2014 | 285983.9298 | 281438.971 | 283127.915 | 99489.3009
411 | Satrong | C171S | 11 | 0 | HA021100515-2 | 1 | 43959 | 885436 | 841477 | 1 | 0 | 841477 | 863413.7674 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 773782.6044 | 892145.191 | 1231591.5581 | 1888984.3136 | 2007795.2093 | 1899691.7228 | 1806807.9399 | 1563100.3489 | 1367977.887
412 | South East RMU | 0 | 11 | 0 | 0 | 1 | 1291.7 | 1351.4 | 59.7 | 1000 | 0 | 59700 | 61256.3408 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 54029.8186 | 62914.9527 | 67794.2153 | 115171.8675 | 137308.3735 | 130223.6796 | 128807.568 | 139045.3993 | 149070.967
413 | Rangs Bhaban | 0 | 11 | 0 | HA021100939-2 | 1 | 1190991 | 1287761 | 96770 | 1 | 0 | 96770 | 99292.732 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 85674.5593 | 100509.6811 | 126221.9657 | 151848.0457 | 148545.345 | 152471.8244 | 163396.3968 | 151255.7649 | 161670.1139
414 | Babli | C171R | 11 | 0 | 0 | 1 | 64050.3 | 65182.6 | 1132.3 | 1000 | 0 | 1132300 | 1161818.3371 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1421205.9945 | 1332782.2391 | 926990.3383 | 1047558.8549 | 1066401.5624 | 2240675.7095 | 2109084.7983 | 2111815.0669 | 1541422.4274
415 | SPL | 0 | 11 | 0 | 0 | 1 | 6491.7 | 6879.1 | 387.4 | 1000 | 0 | 387400 | 397499.2703 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 381333.5894 | 410773.7554 | 403948.9148 | 470689.2376 | 471130.5611 | 465633.0017 | 455733.9249 | 408962.9923 | 372268.4438
416 | DNCC Hospital | 0 | 11 | 0 | 0 | 1 | 19236.1 | 19573.3 | 337.2 | 1000 | 0 | 337200 | 345990.5884 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 461975.1098 | 527369.3693 | 724311.7867 | 958856.3113 | 1039161.0285 | 1028453.8853 | 1058083.8484 | 992388.6083 | 965076.0343
417 | 11/.415 kv Local transformer | 0 | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6054.2264 | 6134.6077
418 | Gonobhaban | D570T | 11 | T-3 | DHKC9332 | 1 | 88196.59 | 89964.8 | 1768.21 | 60 | 0 | 106092.6 | 107250.5214 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 122369.9622 | 94730.2684 | 138463.2177 | 186647.9358 | 199883.04 | 203554.794 | 226219.392 | 216875.2359 | 216836.1836
419 | Town hall | D270R | 11 | T-1 | DHKC9339 | 1 | 62557.11 | 82632.87 | 20075.76 | 60 | 0 | 1204545.6 | 1217692.3145 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 920494.8774 | 299570.85 | 907389.807 | 1054413.3744 | 1089910.392 | 1159561.608 | 1233509.5584 | 1199461.0668 | 1170856.0696
420 | Sukrabad/South Plaza | D570S | 11 | T-1 | DHKC9324 | 1 | 4830.73 | 15312.4 | 10481.67 | 60 | 0 | 628900.2 | 635764.1754 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 615402.167 | 579848.7937 | 881149.6455 | 1103197.1415 | 1099590.636 | 1169672.112 | 1195401.7152 | 1120705.5276 | 1130327.1946
421 | Wasa O/H | C270W | 11 | T-1 | DHKC9333 | 1 | 85676.5 | 96035.51 | 10359.01 | 60 | 0 | 621540.6 | 628324.2509 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 614343.782 | 342027.6753 | 723429.7254 | 739783.158 | 1806723.552 | 986766.768 | 1324483.5744 | 2118683.8855 | 1049087.4751
422 | Bangabandhu Memorial Museum | 0 | 11 | T-1 | DHKC9334 | 1 | 16724.78 | 16819.36 | 94.58 | 60 | 0 | 5674.8 | 5736.7362 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 6110.3919 | 5308.6417 | 12869.2668 | 18497.907 | 17876.394 | 21495.426 | 21201.264 | 20854.3329 | 20897.995
423 | Post Office | D470Q | 11 | T-3 | DHKC9330 | 1 | 70225.65 | 71903.05 | 1677.4 | 60 | 0 | 100644 | 101742.454 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 0 | 220052.6157 | 1111797.4278 | 1464338.9745 | 1539511.488 | 1602882.12 | 1776423.3984 | 1626760.4818 | 1601413.1174
424 | Rapa Plaza Feeder | D470W | 11 | T-3 | DHKC9351 | 1 | 69378.79 | 93104.74 | 23725.95 | 60 | 0 | 1423557 | 1439094.0602 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 1479185.5212 | 910305.2794 | 1599081.4323 | 1961962.9278 | 2111520.342 | 2123219.172 | 2353752.1728 | 1991480.522 | 2338946.2013
425 | Iqbal Road O/H | D470P | 11 | T-1 | DHKC9331 | 1 | 71246.62 | 85155.03 | 13908.41 | 60 | 0 | 834504.6 | 843612.5937 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1013930.856 | 298287.6923 | 1080300.7626 | 1412012.952 | 1209158.466 | 1512426.318 | 1672604.0352 | 1378440.8932 | 1492441.2314
426 | Shangshad Bhaban | 0 | 11 | T-2 | DHKC9370 | 1 | 24139.05 | 24273.39 | 134.34 | 60 | 0 | 8060.4 | 8148.3732 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 196.1183 | 7261.2877 | 0.6051 | 94824.6159 | 417958.806 | 245083.974 | 292942.1376 | 474363.1372 | 422562.5169
427 | Jakir Hossain Road | C270J | 11 | T-2 | DHKC9373 | 1 | 5219.5 | 20350.99 | 15131.49 | 60 | 0 | 907889.4 | 917798.3339 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 670678.1043 | 757535.1127 | 934510.389 | 1496705.7735 | 741916.104 | 1368356.484 | 1603359.2736 | 1792634.4006 | 1277863.2905
428 | New Colony O/H Feeder | C270N | 11 | T-2 | DHKC9369 | 1 | 72759.3 | 86310.66 | 13551.36 | 60 | 0 | 813081.6 | 821955.7777 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 755010.2724 | 840809.5526 | 1003963.767 | 1053637.6362 | 236025.486 | 1443709.554 | 1041715.3824 | 0 | 1328527.8719
429 | Aurangzeb Feeder | D470M | 11 | T-2 | DHKC9321 | 1 | 82718.83 | 98346.78 | 15627.95 | 60 | 0 | 937677 | 947911.0433 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 886695.1992 | 932527.6007 | 1156516.7382 | 1667662.8612 | 711485.208 | 1577029.554 | 1636123.104 | 1847282.7847 | 2012075.4293
430 | Asadgate Local Feeder | C270E | 11 | T-2 | DHKC9338 | 1 | 68343.91 | 79518.09 | 11174.18 | 60 | 0 | 670450.8 | 677768.2691 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 490361.0738 | 541156.2359 | 617884.5528 | 1521583.8549 | 1037091.432 | 1943325.648 | 2129079.8592 | 2381609.9379 | 1832840.2298
431 | Sonarbangla Road | D470R | 11 | T-2 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
432 | Humayun Road | D470H | 11 | T-2 | DHKC9366 | 1 | 37436.64 | 60570.87 | 23134.23 | 60 | 0 | 1388053.8 | 1403203.3693 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1420833.1418 | 2007233.3786 | 1566720.6843 | 1813580.3058 | 1032128.898 | 1903127.244 | 1920389.3856 | 263604.1533 | 1670349.266
433 | NHA | D470B | 11 | T-2 | DHKC9374 | 1 | 72931.85 | 75168.7 | 2236.85 | 60 | 0 | 134211 | 135675.8127 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 133251.9119 | 137620.9673 | 169863.0669 | 219431.6487 | 72214.596 | 237352.02 | 264138.5376 | 26450.7883 | 221861.5773
434 | Auxiliary transformer | 0 | 0.415 | T-2 | 0 | 1 | 680111 | 684327 | 4216 | 1 | 0 | 4216 | 4262.0145 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 4198.0207 | 4293.9625 | 5219.996 | 7644.43 | 8345.63 | 17430.58 | 0 | 7372.3763 | 6148.5505
435 | Angur Jora | F292A | 11 | 0 | 141 | 1 | 5889040 | 7062540 | 1173500 | 1 | 0 | 1173500 | 1187172.5914 | Banosree | Banasree 33/11 SS | 99 | 895336.6304 | 1194834.4269 | 1423037.4494 | 2051370.0659 | 2226512.8044 | 2196051.2126 | 2182461.1184 | 2168323.5267 | 1879685.8324
436 | Block F-G Avenue | F299G | 11 | 0 | 68 | 1 | 7370560 | 7830960 | 460400 | 1 | 0 | 460400 | 465764.1765 | Banosree | Banasree 33/11 SS | 99 | 480429.4597 | 787083.1107 | 599512.8999 | 2148314.9942 | 2658158.1289 | 2630613.5558 | 2686465.1418 | 2772883.9436 | 2653782.5782
437 | Banasree Main Road(Monpura) | F292P | 11 | 0 | 168 | 1 | 1529960 | 1901200 | 371240 | 1 | 0 | 371240 | 375565.3624 | Banosree | Banasree 33/11 SS | 99 | 377379.2998 | 394594.1302 | 496465.9196 | 1014510.7585 | 1233831.441 | 1794844.8609 | 1857089.8973 | 1771391.1453 | 1640446.1666
438 | Baitul Kuddus | F292Q | 11 | 0 | 62 | 1 | 544440 | 1829560 | 1285120 | 1 | 0 | 1285120 | 1300093.0896 | Banosree | Banasree 33/11 SS | 99 | 1340742.7704 | 1363489.3101 | 1686613.9505 | 2119711.2807 | 2318179.6901 | 2240905.0671 | 2321761.5567 | 2248090.2296 | 2090165.4312
439 | Ideal | F214I | 11 | 0 | 0 | 1 | 1916520 | 2321480 | 404960 | 1 | 0 | 404960 | 409678.2383 | Banosree | Banasree 33/11 SS | 99 | 418421.6214 | 426819.1151 | 548800.1649 | 698230.2076 | 798010.2701 | 777466.8098 | 813387.6289 | 785714.1589 | 730886.4987
440 | Central Mosque | F292C | 11 | 0 | 46 | 1 | 209120 | 1371180 | 1162060 | 1 | #REF! | 1162060 | 1175599.3026 | Banosree | Banasree 33/11 SS | 99 | 1149427.3814 | 1201716.6473 | 1552150.2079 | 2014405.8899 | 2216426.2192 | 2155463.3498 | 2252151.7613 | 2213991.1776 | 2027033.5767
441 | Larive | F299L | 11 | 0 | 47 | 1 | 5116560 | 5702000 | 585440 | 1 | 0 | 585440 | 592261.0327 | Banosree | Banasree 33/11 SS | 99 | 588286.7419 | 627334.6303 | 804309.6523 | 1248158.3596 | 1177386.9105 | 1133778.6787 | 1209136.6977 | 1154817.1834 | 1075325.8802
442 | Bank Colony | A299K | 11 | 0 | 0 | 1 | 246920 | 1337360 | 1090440 | 1 | 0 | 1090440 | 1103144.8492 | Khilgaon | Banasree 33/11 SS | 99 | 1071261.1488 | 582519.2305 | 564812.5793 | 1882703.3 | 767992.5927 | 745817.2151 | 791659.8328 | 743707.201 | 684269.1356
443 | Salambagh | A299G | 11 | 0 | 0 | 1 | 8586160 | 9701240 | 1115080 | 1 | 0 | 1115080 | 1128071.9329 | Khilgaon | Banasree 33/11 SS | 99 | 1082127.669 | 693039.5932 | 454833.6424 | 1308766.6526 | 927562.3697 | 1031151.1096 | 794065.0493 | 937481.2326 | 1234217.735
444 | Titas Road | A299T | 11 | 0 | 0 | 1 | 6413520 | 7487200 | 1073680 | 1 | 0 | 1073680 | 1086189.5764 | Khilgaon | Banasree 33/11 SS | 99 | 1042378.0189 | 474023.0502 | 281534.7278 | 1393019.0625 | 401204.0106 | 522157.3704 | 387724.9431 | 442215.7606 | 461564.0031
445 | AT-1 | 0 | 0.415 | 0 | 7734 | 1 | 3637.89 | 3672.3 | 34.41 | 1 | 0 | 34.41 | 34.8109 | Banosree | Banasree 33/11 SS | 99 | 32.64 | 34.9273 | 36.6867 | 64.6367 | 66.5715 | 73.8423 | 76.0089 | 145.5702 | 0
446 | AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
447 | Meradia | F214M | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estiimated | 1137855.6 | 1158986.604 | Banosree | Goran 33/11KV S/S | 14 | 1017252.8765 | 1011378.211 | 2033879.5103 | 378160.5224 | 0 | 0 | 0 | 0 | 0
448 | Shipahibagh | A914S | 11 | 0 | HA-021001030-02 | 1 | 44871090 | 45650758 | 779668 | 1 | 0 | 779668 | 794147.1375 | Bashabo | Goran 33/11KV S/S | 14 | 780874.3368 | 858727.1116 | 1201195.1008 | 1194417.5741 | 1488941.4076 | 1499139.6523 | 1654071.9922 | 1292900.8718 | 1411235.5236
449 | Farazi Hospital | F214F | 11 | 0 | HA-030701081-03 | 1 | 53897450 | 54546599 | 649149 | 1 | 0 | 649149 | 661204.282 | Banosree | Goran 33/11KV S/S | 14 | 689973.7331 | 680667.356 | 834659.8902 | 663014.2572 | 614880.5841 | 0 | 0 | 0 | 0
450 | West Bansree | F214W | 11 | 0 | New Meter | 1 | 1715160 | 2703058 | 987898 | 1 | 0 | 987898 | 1006244.1562 | Banosree | Goran 33/11KV S/S | 14 | 986180.4079 | 1028737.3232 | 1344518.0725 | 1500984.3633 | 1948580.2361 | 1917412.8456 | 1975561.8751 | 1966878.4605 | 1837316.4777
451 | Model School(Nearest) | F214D | 11 | 0 | HA-030701099-03 | 1 | 29276106 | 30608951 | 1332845 | 1 | 0 | 1332845 | 1357597.1329 | Banosree | Goran 33/11KV S/S | 14 | 1327650.9928 | 1395622.5866 | 1890153.6365 | 2273552.5905 | 2474165.667 | 2481856.1691 | 2525253.4223 | 2475694.1412 | 2316464.2537
452 | Bhuiyan Para | F214V | 11 | 0 | HA-021100508-02 | 1 | 64706638 | 64706638 | 0 | 1 | Estiimated | 1479212.28 | 1506682.5852 | Banosree | Goran 33/11KV S/S | 14 | 1536319.3028 | 1597298.5413 | 1593748.1926 | 2480699.3677 | 2656699.6806 | 2382096.4852 | 2607870.9453 | 2554505.4549 | 2408712.741
453 | Bonobithi (Ideal) School | F214B | 11 | 0 | HA-021100879-02 | 1 | 22891440 | 23707824 | 816384 | 1 | 0 | 816384 | 831544.9867 | Banosree | Goran 33/11KV S/S | 14 | 824442.7501 | 846812.4254 | 1095885.5972 | 1387260.9532 | 1569496.2633 | 1543598.2091 | 1587554.1504 | 1568260.1835 | 1428642.8767
454 | AT-01 | 0 | 0.415 | 0 | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 14 | 0 | 0 | 0 | 562.2168 | 0 | 0 | 0 | 0 | 0
455 | AT-02 | 0 | 0.415 | 0 | 3043146 | 1 | 5148.5 | 5193 | 44.5 | 80 | 0 | 3560 | 3626.1124 | Banosree | Goran 33/11KV S/S | 14 | 3458.7723 | 1777.445 | 0 | 11959.1548 | 5508.1614 | 6933.6386 | 6257.2038 | 5424.4075 | 4669.3803
456 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 90 | 1024070.04 | 1031021.6096 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 986156.5854 | 1043191.4697 | 1437106.4117 | 1468016.3082 | 1541495.5501 | 1473463.6679 | 1695740.7049 | 1418643.1678 | 1399733.2864
457 | Bangabobondhu museum | D207B | 11 | Export | 0 | 1 | 630081 | 630081 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 745.6563 | 0 | 0 | 1906.9492 | 0 | 0 | 0 | 0
458 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 89989535 | 90650326 | 660791 | 1 | 0 | 660791 | 665276.5669 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 976232.0912 | 1055174.2976 | 1526974.093 | 1886658.0381 | 1858256.0346 | 2288167.324 | 2330507.8061 | 2062161.6863 | 2160918.3029
459 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 9575787 | 10165740 | 589953 | 1 | 0 | 589953 | 593957.7059 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 616675.0096 | 589316.6942 | 788052.4828 | 2056165.5278 | 2227970.4742 | 2396456.6421 | 1846222.5257 | 2324395.3174 | 2181617.4346
460 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
461 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26546.3 | 26657.2 | 110.9 | 3333.33 | 0 | 369666.297 | 372175.6576 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 380721.3853 | 389812.7152 | 453765.7341 | 575970.5227 | 619531.2198 | 632620.8461 | 655652.5794 | 676925.663 | 643438.6457
462 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71863.1 | 72125 | 261.9 | 3333.33 | 0 | 872999.127 | 878925.2004 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 882719.5917 | 924922.3182 | 1066926.0087 | 1423833.9987 | 1532206.4801 | 1409263.8848 | 1205565.6057 | 1637075.4163 | 1478674.7103
463 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79491.8 | 79491.8 | 0 | 3333.33 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 611457.7362 | 1026568.6676 | 1364158.3566 | 1534221.2158 | 1535115.0531 | 1547367.0274 | 1547019.5294 | 1459995.3095
464 | Road 25 | D207C | 11 | Export | 0 | 1 | 72062.7 | 72248.8 | 186.1 | 3333.3 | 0 | 620327.13 | 624538.0209 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 673603.913 | 659211.4284 | 941775.8615 | 1290390.3315 | 1318296.8446 | 1268595.2792 | 1429491.6026 | 1320696.1949 | 1108412.3257
465 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38432.5 | 38501 | 68.5 | 3333.33 | 0 | 228333.105 | 229883.0707 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 184786.6884 | 219963.344 | 311328.0598 | 402642.9556 | 432160.8021 | 453939.1071 | 448887.9755 | 428853.4986 | 403274.921
466 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 66976858 | 67892083 | 915225 | 1 | 0 | 915225 | 921437.7101 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1258159.4304 | 1277481.7853 | 1297830.3074 | 1076949.6203 | 939422.8232 | 963337.8167 | 1202715.5447 | 1761856.4725 | 924073.8841
467 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | Estimated | 1422319.5 | 1431974.4578 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1355965.3049 | 1544002.5547 | 1652672.3734 | 2233224.3406 | 2307141.6064 | 2239410.379 | 2263478.6281 | 2215613.0537 | 2070071.1797
468 | Lab aid/local RMU | C302L | 11 | 0 | 3C65883 | 1 | 83870 | 87751 | 3881 | 300 | 0 | 1164300 | 1177040.8083 | Paribag | Green Road 33/11KV S/S | 2 | 1057587.2788 | 1091796.2723 | 1099246.4449 | 1368745.9116 | 1391721.2231 | 1482077.1317 | 1556841.7376 | 1536617.643 | 1422394.5672
469 | Green View | C302V | 11 | 0 | DHK000151 | 1 | 68990.1 | 69185.4 | 195.3 | 3333.33 | 0 | 650999.349 | 658123.1641 | Paribag | Green Road 33/11KV S/S | 2 | 630919.372 | 706075.9667 | 952604.6387 | 1155247.0433 | 1226741.8962 | 1226475.691 | 1233531.7182 | 1202336.4681 | 1154869.3417
470 | Central Road | C302C | 11 | 0 | 65943 | 1 | 47189 | 50082 | 2893 | 300 | 0 | 867900 | 877397.3353 | Paribag | Green Road 33/11KV S/S | 2 | 902974.6057 | 926271.7266 | 1084585.7532 | 1542540.4225 | 1699791.5522 | 1668170.2521 | 1747192.6716 | 1761466.4931 | 1692090.5953
471 | New Market | D802N | 11 | 0 | DHK000194 | 1 | 48560.4 | 48818.9 | 258.5 | 3333.33 | 0 | 861665.805 | 871094.9202 | Jigatola | Green Road 33/11KV S/S | 2 | 819653.0402 | 1004981.4593 | 1091745.3233 | 1265157.8423 | 1241755.0551 | 1233547.6266 | 1104020.9274 | 1190965.2748 | 1011316.673
472 | DPH Feeder | 0 | 11 | 0 | HA-021100459 | 1 | 42295.5 | 42371.7 | 76.2 | 1 | 22 | 250328.232 | 253067.5466 | Paribag | Green Road 33/11KV S/S | 2 | 247284.3988 | 245377.4599 | 299600.3974 | 308510.2151 | 353437.7385 | 245765.8495 | 244229.1636 | 236205.0715 | 247670.0176
473 | Dhanmondi Rd 4(md Banglo | D802F | 11 | 0 | 6604464 | 1 | 4622.84 | 4651.5 | 28.66 | 60000 | 0 | 1719600 | 1738417.3958 | Jigatola | Green Road 33/11KV S/S | 2 | 1238731.1207 | 787981.5668 | 976157.721 | 1290523.1633 | 1536748.4833 | 1456011.9715 | 1566178.5714 | 1573640.9477 | 1319464.1465
474 | Green Road East | C302X | 11 | 0 | HA-021101050 | 1 | 2346095 | 3117617 | 771522 | 1 | 0 | 771522 | 779964.6814 | Paribag | Green Road 33/11KV S/S | 2 | 761158.9013 | 826942.8777 | 1043123.4845 | 1394173.8849 | 1544603.3759 | 1523648.0314 | 1576340.6608 | 1533242.4019 | 1471624.0188
475 | North Road | C302Z | 11 | 0 | HA-021100884 | 1 | 88545456 | 89511698 | 966242 | 1 | 0 | 966242 | 976815.4812 | Paribag | Green Road 33/11KV S/S | 2 | 980713.9797 | 1041441.9101 | 1315225.9221 | 1610609.432 | 1705708.7444 | 1708178.2525 | 1755468.3191 | 1721328.8161 | 1634915.8518
476 | Green road SS | C302W | 11 | 0 | DHK00135 | 1 | 24585820 | 25236846 | 651026 | 1 | 0 | 651026 | 658150.1067 | Paribag | Green Road 33/11KV S/S | 2 | 686945.8347 | 744197.7524 | 927434.3375 | 1235249.8127 | 1304162.391 | 1263700.5929 | 1250797.3933 | 1224610.5159 | 1315498.6273
477 | Plane Moszid | C302A | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 90 | 1024070.04 | 1035276.3271 | Paribag | Green Road 33/11KV S/S | 2 | 803674.2962 | 736132.3797 | 719040.9537 | 740424.5162 | 1001406.9258 | 1044504.8605 | 976916.6543 | 944820.2858 | 990680.0705
478 | Malancha | C302H | 11 | 0 | HA-021100953 | 1 | 40127485 | 40552881 | 425396 | 1 | 0 | 425396 | 430051.0622 | Paribag | Green Road 33/11KV S/S | 2 | 425713.4414 | 690231.3036 | 1262646.9803 | 1505893.42 | 1581374.6424 | 1473084.6514 | 1290839.3587 | 1378192.0129 | 1148505.9825
479 | AT -1 | 0 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5054.7145 | Paribag | Green Road 33/11KV S/S | 2 | 5082.5994 | 5043.4048 | 5090.5179 | 5072.8112 | 5004.3913 | 5051.3876 | 5019.8031 | 5016.7079 | 5090.5253
480 | North Dhanmondi | C31002 | 11 | 0 | BD 014039 | 1 | 24454.33 | 24800.46 | 346.13 | 2000 | 0 | 692260 | 693021.0838 | Paribag | Green Road Dormatory 33/11 SS | 100 | 646999.5384 | 711975.1234 | 970901.1912 | 1220415.3715 | 539516.6063 | 454897.5939 | 484039.8994 | 504079.3978 | 452285.2955
481 | Lake circus | C31004 | 11 | 0 | BD 014047 | 1 | 40180.55 | 40691.07 | 510.52 | 2000 | 0 | 1021040 | 1022162.5508 | Paribag | Green Road Dormatory 33/11 SS | 100 | 997214.4169 | 1037653.6636 | 1359915.9406 | 1817014.2474 | 1989795.0818 | 1922931.395 | 2034236.8602 | 2046787.3073 | 1887308.9386
482 | Bashir Uddin | C31003 | 11 | 0 | BD 014037 | 1 | 16256.19 | 16477.88 | 221.69 | 2000 | 0 | 443380 | 443867.4604 | Paribag | Green Road Dormatory 33/11 SS | 100 | 436278.7563 | 426218.7286 | 519195.2113 | 699693.4639 | 775365.5929 | 750942.0597 | 792213.6477 | 798302.5936 | 740604.9957
483 | Raza Bazar | D5100R | 11 | 0 | BD 013939 | 1 | 24591.09 | 24953.77 | 362.68 | 2000 | 0 | 725360 | 726157.4746 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 674061.5972 | 895520.3575 | 1203544.7399 | 1251949.7098 | 1335486.8536 | 1305339.0743 | 1333290.6732 | 1329360.3858 | 1277085.001
484 | Rasel Squar | D5100RS | 11 | 0 | BD 013970 | 1 | 36953.14 | 37481.95 | 528.81 | 2000 | 0 | 1057620 | 1058782.7676 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1005337.1163 | 1152709.1657 | 1357853.9899 | 1818453.1535 | 1979472.6721 | 1896362.0126 | 1946515.3317 | 1986224.7792 | 1860400.7233
485 | Bow Bazar | D5100O | 11 | 0 | BD 013967 | 1 | 27679.89 | 28026.56 | 346.67 | 2000 | 0 | 693340 | 694102.2712 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 682123.0702 | 1265670.9193 | 1309854.1577 | 1211822.467 | 1271865.4648 | 1228245.6279 | 1315379.6859 | 1361417.0663 | 1195690.6937
486 | BRB Hospital | D5100S | 11 | 0 | BD 014003 | 1 | 14821.96 | 15069.96 | 248 | 2000 | 0 | 496000 | 496545.3119 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 418074.1134 | 471979.2109 | 608037.5277 | 807753.2915 | 817558.9445 | 861081.3012 | 841735.8151 | 735319.9448 | 733624.2823
487 | Green Road North | C31008 | 11 | 0 | BD 013969 | 1 | 18290.35 | 18578.83 | 288.48 | 2000 | 0 | 576960 | 577594.3208 | Paribag | Green Road Dormatory 33/11 SS | 100 | 724552.9497 | 642821.029 | 876606.6014 | 1205661.5166 | 1207219.8681 | 1206463.1592 | 1244662.5143 | 1225136.5003 | 1163648.4072
488 | Water Bhaban | D5100PB | 11 | 0 | BD 014004 | 1 | 5892.83 | 5979.43 | 86.6 | 2000 | 0 | 173200 | 173390.4194 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 165821.4387 | 176418.4365 | 266368.3378 | 341567.9548 | 321038.9901 | 360889.0448 | 369844.7631 | 332111.9703 | 301428.8307
489 | Alamin Road | C31007 | 11 | 0 | BD 014006 | 1 | 20044 | 20202.42 | 158.42 | 2000 | 0 | 316840 | 317188.3399 | Paribag | Green Road Dormatory 33/11 SS | 100 | 338316.5525 | 310418.3353 | 564141.7704 | 583425.7911 | 637499.1681 | 607978.2671 | 645158.196 | 644406.723 | 578607.7993
490 | Katal Bagan | C3100K | 11 | 0 | 0 | 1 | 12838.84 | 13439.45 | 600.61 | 2000 | 0 | 1201220 | 1202540.6442 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1133279.8362 | 1211233.4604 | 1478597.0623 | 2049711.7232 | 2213293.3253 | 2170885.4799 | 2232426.2667 | 2461917.3517 | 1880307.9323
491 | Eastern Pantho chaya | C310010 | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
492 | Kalabagan | 0 | 11 | 0 | BD 014005 | 1 | 6548.85 | 6635.97 | 87.12 | 2000 | 0 | 174240 | 174431.5628 | Paribag | Green Road Dormatory 33/11 SS | 100 | 194108.025 | 173740.8544 | 284172.4888 | 308027.2544 | 333048.3305 | 321346.724 | 343995.7229 | 360201.2398 | 320179.3518
493 | Univer Hospital | C310012 | 11 | 0 | BD 013963 | 1 | 1566.06 | 1656.03 | 89.97 | 2000 | 0 | 179940 | 180137.8295 | Paribag | Green Road Dormatory 33/11 SS | 100 | 169923.606 | 181672.9397 | 220053.7538 | 258516.7219 | 265852.2552 | 274362.5626 | 281740.4351 | 275219.2974 | 258266.1053
494 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 | 0 | BD 013971 | 1 | 10877.61 | 10970.57 | 92.96 | 2000 | 0 | 185920 | 186124.404 | Paribag | Green Road Dormatory 33/11 SS | 100 | 151882.2334 | 205106.8163 | 341233.008 | 477291.2605 | 521121.028 | 519641.6074 | 508095.8262 | 507213.6524 | 520651.6433
495 | Matir Masjid | A229S | 11 | 0 | DHK00170 | 1 | 33985.2 | 35295.8 | 1310.6 | 888.8889 | 0 | 1164977.7778 | 1170440.5193 | Khilgaon | Taltola 33/11KV S/S | 29 | 1162051.2612 | 1284398.1103 | 1604310.6045 | 1914137.6974 | 2132185.0742 | 2085431.7227 | 2167154.5553 | 2177028.2382 | 2023352.6919
496 | Hajipara | A229P | 11 | 0 | DHK-00108 | 1 | 7902.6 | 8226.2 | 323.6 | 2222.2222 | 0 | 719111.1111 | 722483.1223 | Khilgaon | Taltola 33/11KV S/S | 29 | 693287.1642 | 1281545.2791 | 1799894.6638 | 1077292.6606 | 2330316.32 | 2323985.9847 | 2257545.6108 | 2323390.6234 | 1505682.5673
497 | Nearest Feeder | A929N | 11 | 0 | DHK-00106 | 1 | 92381.2 | 92686.4 | 305.2 | 2222.222 | 0 | 678222.1544 | 681402.4317 | Bashabo | Taltola 33/11KV S/S | 29 | 231246.1023 | 528888.1119 | 952079.0172 | 736977.684 | 448845.991 | 661064.6612 | 0 | 0 | 102528.7436
498 | Reazbagh | A229C | 11 | 0 | DHK-00109 | 1 | 99870.3 | 100329.8 | 459.5 | 2222.222 | 0 | 1021111.009 | 1025899.1394 | Khilgaon | Taltola 33/11KV S/S | 29 | 1033500.8727 | 1075160.6623 | 1369807.3375 | 1677297.9566 | 1831327.1429 | 1773544.5971 | 1831021.0001 | 1850181.9906 | 1693614.7124
499 | Chowdhury Para | A229F | 11 | 0 | DHK-00107 | 1 | 53937 | 54150.3 | 213.3 | 2222.222 | 0 | 473999.9526 | 476222.6038 | Khilgaon | Taltola 33/11KV S/S | 29 | 454144.7843 | 485204.138 | 558618.9372 | 561029.5515 | 662951.963 | 585903.1258 | 625509.6106 | 653692.0598 | 575139.5465
500 | Model Colleg | A229D | 11 | 0 | 9122392 | 1 | 2615.34 | 2624.97 | 9.63 | 40000 | 0 | 385200 | 387006.256 | Khilgaon | Taltola 33/11KV S/S | 29 | 0 | 537981.5643 | 695285.1522 | 561252.3268 | 1334690.1699 | 1248930.587 | 1283320.9871 | 723685.6707 | 1038453.9207
501 | East Rampura | A229B | 11 | 0 | DHK-00181 | 1 | 290.7 | 290.7 | 0 | 2222.222 | 0 | 0 | 0 | Khilgaon | Taltola 33/11KV S/S | 29 | 676.8179 | 491221.8283 | 1083981.397 | 632299.6811 | 1183684.3115 | 1041555.9945 | 1373711.9053 | 1177184.4648 | 1381135.5698
502 | Adarshabagh | A929A | 11 | 0 | DHK-00090 | 1 | 54102.3 | 54599.9 | 497.6 | 2222.222 | 0 | 1105777.6672 | 1110962.8113 | Bashabo | Taltola 33/11KV S/S | 29 | 1073207.5205 | 1197297.4871 | 1572716.7906 | 2035653.077 | 2182105.9426 | 2139761.9297 | 2323799.4344 | 2249760.2414 | 2012766.0076
503 | Khailgaon Govt Colony | A229K | 11 | 0 | DHK00167 | 1 | 78570.4 | 78980.2 | 409.8 | 2222.222 | 0 | 910666.5756 | 914936.8168 | Khilgaon | Taltola 33/11KV S/S | 29 | 889789.8804 | 960824.5471 | 1228467.3088 | 1508476.8371 | 1632974.0455 | 1590881.9934 | 1651220.4486 | 1644511.4325 | 1548206.2687
504 | TV Road | A214T | 11 | 0 | 6604434 | 1 | 5190.73 | 5190.73 | 0 | 40000 | 0 | 0 | 0 | Khilgaon | Taltola 33/11KV S/S | 29 | 0 | 631857.5419 | 1115125.7501 | 339156.7632 | 1446513.4037 | 1300316.995 | 1457589.2313 | 1435653.3713 | 1278251.1059
505 | Post Office | 0 | 11 | 0 | 06604476 | 1 | 6677.6 | 6688.82 | 11.22 | 40000 | 0 | 448800 | 450904.4851 | Bashabo | Taltola 33/11KV S/S | 29 | 443045.0157 | 487432.9609 | 755551.2881 | 1009051.5047 | 850255.946 | 1067472.334 | 544086.3384 | 925315.57 | 631719.4629
506 | Navana | A929V | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507 | Shantipur | A929P | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232625.2878
508 | AT-01 | 0 | 0.415 | 0 | 9187958 | 1 | 919.21 | 980.28 | 61.07 | 80 | 0 | 4885.6 | 4908.5093 | Bashabo | Taltola 33/11KV S/S | 29 | 5310.0427 | 5091.7688 | 215.1784 | 17609.6926 | 22368.6405 | 0 | 0 | 388.7134 | 5004.1149
509 | AT-02 | 0 | 0.415 | 0 | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 164.5672 | 981.0492 | 0 | 0 | 1243.317 | 0
510 | Sher-e-Banglanagar Local | 0 | 11 | 0 | DHK 66503 | 1 | 87224 | 88011 | 787 | 60 | 11 kv bus-1 R Phase PT missing | 47220 | 47423.8712 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 58299.0972 | 69188.3162 | 109846.5171 | 124871.9678 | 133378.1778 | 145611.0642 | 127632.9783 | 130259.0089 | 137740.1655
511 | Mirpur Road East | D550F | 11 | 0 | DHK 60961 | 1 | 861495 | 865247 | 3752 | 60 | 0 | 225120 | 226091.9501 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 274779.1972 | 317858.7434 | 395819.5598 | 504909.4833 | 511825.2027 | 595499.8531 | 565408.7832 | 579726.769 | 591320.8565
512 | Gonobhaban school | D550E | 11 | 0 | DHK 66492 | 1 | 538182 | 539146 | 964 | 60 | 0 | 57840 | 58089.7228 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 83830.9415 | 96916.7963 | 122017.2321 | 162123.6893 | 177174.8965 | 204772.9102 | 187053.4171 | 201293.1928 | 178100.36
513 | Babor Road | D450B | 11 | 0 | DHK 66489 | 1 | 809511 | 815041 | 5530 | 60 | 0 | 331800 | 333232.5384 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 453086.2792 | 427624.0566 | 570860.7987 | 723610.3177 | 1641262.4555 | 827030.8546 | 821146.7988 | 2355047.2749 | 1531864.2685
514 | College Gate | D450K | 11 | 0 | DHK 66487 | 1 | 2743173 | 2752409 | 9236 | 60 | 0 | 554160 | 556552.5723 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 891202.7474 | 1193207.4845 | 1044976.0411 | 1347445.4847 | 1954707.1976 | 2003387.1217 | 2118896.2632 | 2029429.4244 | 1693179.314
515 | Parade ground | 0 | 11 | 0 | DHK 66490 | 1 | 938548 | 938644 | 96 | 60 | 0 | 5760 | 5784.8687 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 3742.4527 | 3012.0394 | 3333.3805 | 6820.7377 | 4879.6894 | 117.618 | 1062.133 | 1780.3054
516 | Hospital RMU | D550H | 11 | 0 | DHK 66491 | 1 | 934179 | 937696 | 3517 | 60 | 0 | 211020 | 211931.0737 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 276525.6752 | 323971.4115 | 434269.7168 | 581861.3963 | 629901.6383 | 661895.205 | 606359.9098 | 560499.4711 | 544171.0965
517 | Shamoly Square | 0 | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
518 | Gonobhaban RMU | D550D | 11 | 0 | DHK 60964 | 1 | 201092.5 | 202037.6 | 945.1 | 60 | 0 | 56706 | 56950.8268 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 65049.9758 | 79351.658 | 75406.8335 | 93681.1141 | 88021.1633 | 97246.5492 | 98796.0682 | 102753.2911 | 81921.1363
519 | Krishi University | D550V | 11 | 0 | DHK 60963 | 1 | 398255.2 | 404088.9 | 5833.7 | 60 | 0 | 350022 | 351533.2115 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 361119.5708 | 346415.0761 | 461555.7137 | 534152.4164 | 582966.2552 | 608461.3549 | 589560.5067 | 563852.3796 | 574020.0379
520 | NEC | D550X | 11 | 0 | DHK 86073 | 1 | 56.16 | 58.43 | 2.27 | 60000 | 0 | 136200 | 136788.0402 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 147649.1019 | 146630.7201 | 204096.883 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 274760.4607 | 284784.5503
521 | Novo Theater/Army Musium (41%) | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 456.07 | 467.79 | 11.72 | 60000 | 0 | 288312 | 289556.7801 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 279948.7237 | 309109.7771 | 360791.2051 | 457676.9299 | 439900.9902 | 454264.1779 | 491118.4828 | 467152.1267 | 453385.8053
522 | Novo Theater/Army Musium (59%) | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 456.07 | 467.79 | 11.72 | 60000 | 0 | 414888 | 416679.2689 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 402853.0415 | 444816.5085 | 519187.344 | 658608.2649 | 633028.2541 | 653697.2316 | 706731.4752 | 672243.3043 | 652433.232
523 | Netor | 0 | 11 | 0 | DHK 60962 | 1 | 160020.5 | 164620.5 | 4600 | 60 | 0 | 276000 | 277191.6233 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 255716.1915 | 302297.5582 | 451889.8792 | 546388.7354 | 587213.3923 | 617847.27 | 628517.1836 | 620062.5542 | 596532.4766
524 | BICC | D550VV | 11 | 0 | 0 | 1 | 56.16 | 58.43 | 2.27 | 60000 | 0 | 136200 | 136788.0402 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 147649.1019 | 146630.7201 | 204096.883 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 193459.8492 | 69152.9813
525 | Auxiliary | 0 | 0.415 | 0 | 0 | 1 | 5506.58 | 5529.71 | 23.13 | 60 | 0 | 1387.8 | 1393.7918 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 2197.8623 | 1870.7636 | 2593.3022 | 3246.9365 | 3802.5432 | 2988.0849 | 4296.3279 | 3895.3081 | 5642.8833
526 | City Corporation | A997Y | 11 | 0 | 93 | 1 | 45498128 | 46441248 | 943120 | 1 | 0 | 943120 | 945178.1823 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 123798.2877 | 599738.4197 | 776082.8806 | 996604.0058 | 1085361.1698 | 1583920.0344 | 672002.1574 | 951549.8845 | 660250.7383
527 | Bot tola | B297L | 11 | 0 | 0 | 1 | 65267360 | 66613436 | 1346076 | 1 | 0 | 1346076 | 1349013.5582 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 1354052.5032 | 1459024.4609 | 1806337.3901 | 2300581.3394 | 2406944.4276 | 2386526.2912 | 2395209.9678 | 2298336.7826 | 2240795.0697
528 | Jhilpar | B997J | 11 | 0 | 145 | 1 | 39956424 | 40492100 | 535676 | 1 | 0 | 535676 | 536845.0123 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 549799.1663 | 831525.4247 | 819817.0349 | 964321.9183 | 1048862.0833 | 1018967.1456 | 1203846.2525 | 1011093.8025 | 1160185.3486
529 | Central Bashaboo | A997C | 11 | 0 | 128 | 1 | 45762528 | 46705244 | 942716 | 1 | 0 | 942716 | 944773.3007 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 977685.9863 | 1054741.7939 | 1340049.7308 | 1729561.5012 | 1906586.5613 | 1065915.018 | 2018436.7723 | 1763582.1465 | 1733572.9987
530 | Kadamtala | B997L | 11 | 0 | 8 | 1 | 20912708 | 21153428 | 240720 | 1 | 0 | 240720 | 241245.3262 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 360174.7446 | 378223.2469 | 607566.4408 | 808410.7915 | 737461.0018 | 659233.1205 | 895857.2066 | 680353.9053 | 1958904.8441
531 | Ansar VDP | A297A | 11 | 0 | 119 | 1 | 23402382 | 24000982 | 598600 | 1 | 0 | 598600 | 599906.3321 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 97 | 985985.7719 | 507207.0721 | 657824.4358 | 1198004.0816 | 522827.1096 | 571466.9061 | 611327.4182 | 1128730.4864 | 727503.1317
532 | Mugda Hospital Express-01 | B997H | 11 | 0 | 0 | 1 | 7334222 | 7471102 | 136880 | 1 | 0 | 136880 | 137178.7149 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 148451.1163 | 172866.4097 | 206011.8286 | 296418.3041 | 309430.1308 | 314267.439 | 307500.5637 | 293639.1125 | 272764.3875
533 | Boro Masjid | B997Z | 11 | 0 | 7 | 1 | 53562788 | 54202588 | 639800 | 1 | 0 | 639800 | 641196.2434 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 787897.7465 | 734840.8949 | 1191583.9793 | 1366718.9494 | 1456683.3289 | 1401094.4155 | 1717015.7129 | 1405726.812 | 1342757.2732
534 | Anandodhara | B297B | 11 | 0 | 120 | 1 | 51855752 | 52464832 | 609080 | 1 | 0 | 609080 | 610409.2028 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 615741.3741 | 698743.2036 | 685213.6028 | 1028241.2626 | 986769.0262 | 991611.9155 | 1008287.8477 | 964251.0175 | 915566.0508
535 | Culvert | A997L | 11 | 0 | 117 | 1 | 47238964 | 48102164 | 863200 | 1 | 0 | 863200 | 865083.772 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 856270.8053 | 964105.6034 | 1368637.0118 | 1587860.9817 | 1735000.3001 | 1917088.0393 | 2175998.5274 | 1824104.3237 | 1912589.1389
536 | Mugda Hospital Express-02 | 0 | 11 | 0 | 97 | 1 | 4870948 | 4885388 | 14440 | 1 | 0 | 14440 | 14471.5126 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 25317.8849 | 0 | 0 | 0 | 0 | 0 | 0
537 | Jhor Pukur | A997J | 11 | 0 | 98 | 1 | 30580126 | 30755084 | 174958 | 1 | 0 | 174958 | 175339.813 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 624661.5892 | 388121.3008 | 230851.2653 | 807820.7106 | 1233989.5056 | 952311.2849 | 1695311.8425 | 1643349.6255 | 1429146.8866
538 | T&T | B997T | 11 | 0 | 99 | 1 | 26413816 | 26756894 | 343078 | 1 | 0 | 343078 | 343826.7033 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 336675.4629 | 357855.3593 | 590205.7479 | 628322.5712 | 593432.5647 | 596600.2068 | 721459.9725 | 567104.166 | 852556.8368
539 | Haider Ali | B297H | 11 | 0 | 9 | 1 | 79614568 | 81093520 | 1478952 | 1 | 0 | 1478952 | 1482179.5351 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 1499220.6846 | 1567072.6596 | 1855860.7678 | 2415267.9161 | 2486025.7818 | 2500945.5412 | 2687168.9248 | 2028073.3969 | 1439434.5953
540 | 11kv Tilpapara | A929T | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 1024070.04 | 1026304.8806 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1436826.0805 | 1228749.1366 | 1642601.2461 | 2219790.0622 | 2267480.2014 | 2153708.0482 | 2169910.6664 | 2181802.1625 | 2151612.2434
541 | AT-01 | 0 | 11 | 0 | 0 | 1 | 3318.67 | 3345.06 | 26.39 | 1 | 0 | 26.39 | 26.4476 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 24.6426 | 33.0137 | 54.7524 | 80.2692 | 86.077 | 79.9328 | 89.8242 | 94.3756 | 0
542 | AT-02 | 0 | 11 | 0 | 0 | 1 | 17.34 | 19.08 | 1.74 | 1 | 0 | 1.74 | 1.7438 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34315 | 0 | 8.4563
543 | Shantinagar s/s-1 | 0 | 11 | 0 | DHK60932 | 1 | 481372 | 507338 | 25966 | 60 | 0 | 1557960 | 1582612.367 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1453002.4337 | 1639830.5714 | 1995495.3946 | 1888358.4836 | 1327460.0638 | 1164408 | 2916346.3506 | 2755360.6206 | 2616486.0095
544 | Gulbagh | D606G | 11 | 0 | DHK60934 | 1 | 210552 | 220922 | 10370 | 60 | 0 | 622200 | 632045.3765 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 600803.3792 | 661647.9407 | 827221.5772 | 1048994.4227 | 1110222.7304 | 1081462.2 | 329175.3109 | 325114.8574 | 314880.9114
545 | Rampura BTV | A206H | 11 | 0 | DHK60933 | 1 | 15382 | 19607 | 4225 | 60 | 0 | 253500 | 257511.2551 | Khilgaon | Khillgaon 33/11KV S/S | 6 | 79250.248 | 301.4616 | 180.4191 | 0 | 0 | 0 | 0 | 1220.4011 | 241.3343
546 | West Shantibag | D606W | 11 | 0 | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 477899.352 | 485461.3884 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 493949.9225 | 550014.4758 | 707899.6007 | 1098102.3361 | 1003916.3939 | 885668.7 | 934072.7507 | 932020.3326 | 912726.2746
547 | East Malibagh | D606E | 11 | 0 | DHK60929 | 1 | 690468 | 702800 | 12332 | 60 | 0 | 739920 | 751628.1179 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 735547.0753 | 789708.8324 | 996093.8555 | 1225702.646 | 1396586.5654 | 1214224.2 | 1558104.7013 | 1377100.6198 | 1289630.0978
548 | Police Line | D606S | 11 | 0 | DHK60930 | 1 | 611483 | 615719 | 4236 | 60 | 0 | 254160 | 258181.6986 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 276370.7727 | 303813.0101 | 464398.7655 | 567380.2526 | 593599.4922 | 600534.9 | 624772.6414 | 596226.9654 | 576125.2774
549 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 | 0 | DHK61017 | 1 | 204786 | 206322 | 1536 | 60 | 0 | 92160 | 93618.293 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 90275.8398 | 91523.7447 | 111138.1661 | 133734.902 | 145615.9492 | 150301.2 | 152458.8445 | 149621.1769 | 146188.2445
550 | Benjir Bagan | D662R | 11 | 0 | DHK60985 | 1 | 179547 | 180938 | 1391 | 60 | 0 | 83460 | 84780.6286 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 99595.8152 | 118052.3663 | 135073.7668 | 193500.3195 | 197704.2286 | 195610.8 | 195480.6318 | 194653.9781 | 180699.0476
551 | AT-1 & AT-2 | 0 | 0.415 | 0 | ELIB 7374 | 1 | 2579.7 | 2648.35 | 68.65 | 60 | 0 | 4119 | 4184.177 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 4602.1186 | 4651.5526 | 5701.2436 | 7360.8364 | 7097.6366 | 6669.159 | 7349.5039 | 14431.2432 | 0
552 | Spare | 0 | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553 | Monipuripara west | D572W | 11 | 0 | BD013947 | 1 | 34737.3 | 35145.8 | 408.5 | 1000 | 0 | 408500 | 414569.2893 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 423673.0441 | 612114.5091 | 935544.6228 | 814448.4485 | 843758.793 | 830035.6978 | 847623.509 | 861249.4503 | 873090.4062
554 | Biggan College | C672BC | 11 | 0 | BD013949 | 1 | 22925.68 | 23411.7 | 486.02 | 1000 | 0 | 486020 | 493241.0428 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 519020.9584 | 629329.3802 | 983877.3078 | 910214.7983 | 898340.4903 | 876599.5577 | 835521.2072 | 819870.1443 | 853994.1863
555 | Green Road South | D572G | 11 | 0 | BD013948 | 1 | 33271.48 | 33825.73 | 554.25 | 1000 | 0 | 554250 | 562484.7701 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 541015.7704 | 487251.3238 | 613343.481 | 1046963.2451 | 997691.2194 | 972408.44 | 975210.3173 | 1037302.1428 | 986346.7996
556 | BARC Building O/H | D572B | 11 | 0 | BD014010 | 1 | 14618.87 | 14620.53 | 1.66 | 1000 | 0 | 1660 | 1684.6635 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 1799.208 | 3503.3773 | 39283.5032 | 553036.0194 | 605164.5353 | 601022.2433 | 634425.9824 | 629218.3029 | 632910.7169
557 | Indira Road (Green Road North) | D572NN | 11 | 0 | BD014036 | 1 | 64945.32 | 65934.2 | 988.88 | 1000 | 0 | 988880 | 1003572.286 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 969055.4316 | 484885.5374 | 964099.8184 | 1738404.7784 | 1930586.7401 | 1889476.4806 | 1966221.9789 | 1919532.2257 | 1871294.3358
558 | Chundrima Uddan | D572C | 11 | 0 | BD014035 | 1 | 33773.82 | 34549.23 | 775.41 | 1000 | 0 | 775410 | 786930.6551 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 784555.7519 | 512298.4579 | 477595.7009 | 964413.0153 | 995724.673 | 1002061.8966 | 1070591.3324 | 1032887.2799 | 1015615.1889
559 | khamar bari RMU-1 Feeder | 0 | 11 | 0 | BD013940 | 1 | 1863.62 | 2084.35 | 220.73 | 1000 | 0 | 220730 | 224009.4963 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 217360.4948 | 283018.522 | 321406.8247 | 250904.1991 | 255319.9358 | 263025.0554 | 137015.3458 | 147255.7457 | 0
560 | Farmgate foot over bridge RMU | 0 | 11 | 0 | BD013946 | 1 | 635.81 | 825.3 | 189.49 | 1000 | 0 | 189490 | 192305.3479 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 180426.192 | 219444.3049 | 176700.3547 | 0 | 0 | 0 | 0 | 0 | 0
561 | kawran Bazar North | C672K | 11 | 0 | BD013964 | 1 | 40777.26 | 40940.51 | 163.25 | 1000 | 0 | 163250 | 165675.4871 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 135577.3957 | 126534.3365 | 61252.9055 | 77104.1375 | 81762.1785 | 77492.626 | 79448.9981 | 30221.7434 | 0
562 | NAM Bhanan RMU | D572NM | 11 | 0 | BD013950 | 1 | 20232.07 | 20852.88 | 620.81 | 1000 | 0 | 620810 | 630033.6854 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 638173.0005 | 637886.4799 | 770397.0568 | 959936.9135 | 1011015.5749 | 965308.8823 | 1005888.2452 | 1030950.7605 | 1013545.3917
563 | Novo Theater | 0 | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
564 | Monipuripara Nearest | C172I | 11 | 0 | BD013962 | 1 | 40572.34 | 40789.94 | 217.6 | 1000 | 0 | 217600 | 220832.9923 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 241821.6368 | 235803.4661 | 446918.9749 | 732201.3407 | 808641.8922 | 823257.478 | 844317.6909 | 794156.578 | 733061.8614
565 | Holy Cross | C172HC | 11 | 0 | BD013965 | 1 | 42526.73 | 43370.96 | 844.23 | 1000 | 0 | 844230 | 856773.1484 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 907680.2026 | 699759.3443 | 1032893.7086 | 1312589.0703 | 1258529.5254 | 1242673.6384 | 1267377.9768 | 1286005.418 | 1126874.592
566 | Honda Goli | C172HG | 11 | 0 | BD014011 | 1 | 18394.93 | 19009.47 | 614.54 | 1000 | 0 | 614540 | 623670.5289 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 595315.4624 | 649272.4561 | 812717.0632 | 996766.2388 | 1069470.1647 | 1059189.7376 | 1074102.0051 | 1068926.6085 | 953126.0337
567 | Navy Quarter | C172NQ | 11 | 0 | BD013941 | 1 | 6161.05 | 6178.85 | 17.8 | 1000 | 0 | 17800 | 18064.4635 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 64488.4653 | 116487.2948 | 259359.6022 | 175972.436 | 196544.2773 | 221522.2664 | 200143.5254 | 202962.2853 | 175339.91
568 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 2170.58 | 2170.58 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
569 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 739.45 | 790.83 | 51.38 | 1 | 0 | 51.38 | 52.1434 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 51.0955 | 47.8996 | 56.1451 | 0 | 0 | 0 | 0 | 0 | 0
570 | Doctor Goli | D1113D | 11 | 0 | BD013944 | 1 | 12159.11 | 12681.1 | 521.99 | 1000 | 0 | 521990 | 525464.8941 | Moghbazar | Ispahani 33/11 KV SS | 113 | 435413.5519 | 521759.6267 | 680371.3877 | 917384.4784 | 958125.7556 | 963950.8063 | 948233.0953 | 958270.3835 | 898591.0283
571 | Ispahani | D1113S | 11 | 0 | BD013947 | 1 | 13686.54 | 14257.9 | 571.36 | 1000 | 0 | 571360 | 575163.5509 | Moghbazar | Ispahani 33/11 KV SS | 113 | 543652.9443 | 606182.8062 | 787241.7632 | 1000362.3505 | 1092016.0616 | 1087721.0462 | 1055882.4039 | 1058199.8531 | 999582.0108
572 | BTCL | C6113BT | 11 | 0 | BD013949 | 1 | 7657.92 | 8169.35 | 511.43 | 1000 | 0 | 511430 | 514834.5961 | Kakrail | Ispahani 33/11 KV SS | 113 | 516585.3241 | 534844.6655 | 534614.2847 | 552136.017 | 523407.6855 | 549951.6967 | 529591.2713 | 523726.617 | 532492.3633
573 | Vikarunnesa | C6113VQ | 11 | 0 | BD013948 | 1 | 10452.53 | 11019.56 | 567.03 | 1000 | 0 | 567030 | 570804.726 | Kakrail | Ispahani 33/11 KV SS | 113 | 577218.0369 | 590962.2568 | 754158.2718 | 1059198.2594 | 1138092.7736 | 1152044.6426 | 1148347.0254 | 1136233.5895 | 1092064.7445
574 | OASIS | 0 | 11 | 0 | 0 | 1 | 681.71 | 813.16 | 131.45 | 1000 | 0 | 131450 | 132325.0643 | Kakrail | Ispahani 33/11 KV SS | 113 | 139783.74 | 123718.5886 | 114056.2956 | 109560.3611 | 90109.3741 | 109400.2883 | 4342.8205 | 0 | 0
575 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
576 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
577 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578 | Wireless | D1113W | 11 | 0 | 0 | 1 | 12016.06 | 12585.13 | 569.07 | 1000 | 0 | 569070 | 572858.3063 | Moghbazar | Ispahani 33/11 KV SS | 113 | 608347.8726 | 682557.5285 | 776089.4575 | 1063107.1511 | 1088068.9306 | 1084178.7327 | 1047125.901 | 1048087.1638 | 896344.5253
579 | Kazir Goli | C6113KG | 11 | 0 | 0 | 1 | 11748.83 | 12370.35 | 621.52 | 1000 | 0 | 621520 | 625657.4666 | Kakrail | Ispahani 33/11 KV SS | 113 | 644368.9476 | 654614.5742 | 954304.3117 | 1072332.5406 | 1195416.795 | 1197081.1949 | 1203659.779 | 1263311.3532 | 1182067.1763
580 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
581 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
582 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
583 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
584 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
585 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
586 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
587 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1.25 | 224037.5 | 225005.7 | 968.2 | 1000 | 0 | 1210250 | 1219193.0905 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1215735.951 | 1328840.997 | 1907566.3908 | 2264304.2356 | 2396448.119 | 2486440.3485 | 2725888.0748 | 2549641.8301 | 2438789.3271
589 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1.25 | 17446.2 | 17495.1 | 48.9 | 1000 | 0 | 61125 | 61576.6806 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 67304.8091 | 70593.7298 | 97801.2231 | 114438.0991 | 122268.7906 | 127832.1205 | 148265.7961 | 145583.9006 | 138711.8093
590 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1.25 | 115144.6 | 115785.2 | 640.6 | 1000 | 0 | 800750 | 806667.1078 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 803819.5531 | 889703.4972 | 1253935.5917 | 1366513.6955 | 1396305.5531 | 1491140.0618 | 1611243.3589 | 1535819.0344 | 1523513.0022
591 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1.25 | 181090.3 | 181522.8 | 432.5 | 1000 | 0 | 540625 | 544619.9253 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 553654.0203 | 1593719.1894 | 2152733.2578 | 2379446.8789 | 2449713.7307 | 2507460.7365 | 2663481.8388 | 2529191.2405 | 2405949.7847
592 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1.25 | 7471.9 | 7568.5 | 96.6 | 1000 | 0 | 120750 | 121642.2769 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 99380.8281 | 100328.0515 | 99239.4764 | 85853.7366 | 56292.0669 | 68291.1171 | 54248.5581 | 41407.382 | 36566.7297
593 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 81835.9 | 82723.7 | 887.8 | 1000 | 0 | 887800 | 894360.36 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 921540.4781 | 998830.4807 | 1251179.7778 | 1359166.3065 | 1319938 | 1387647.3379 | 1431264.5899 | 1311672.4727 | 1337959.5143
594 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
595 | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 11 | T2 | 0 | 1 | 38.3337 | 58.7932 | 20.4595 | 40000 | 0 | 818380 | 824427.3839 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 514361.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
596 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 157475.6 | 158147.5 | 671.9 | 1000 | 0 | 671900 | 676864.9762 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 856227.3172 | 1467297.7535 | 1794799.2873 | 2274671.0995 | 2350345.1179 | 2375002.1192 | 2446793.5192 | 2328937.4468 | 2238024.8856
597 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 121.6911 | 126.4018 | 4.7107 | 40000 | 0 | 188428 | 189820.3806 | Matuail | Siddhirganj 33/11KV S/S | 28 | 184300.0323 | 237057.3856 | 379449.435 | 283444.1488 | 297629.6761 | 330706.0205 | 314747.6869 | 291293.3394 | 424399.7103
598 | 11 kV Madrasha Road Feeder (F-11) | 0 | 11 | T2 | XA575919 | 1 | 53.16 | 186.67 | 133.51 | 8000 | 0 | 1068080 | 1075972.5314 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1043305.1747 | 160176.9706 | 0 | 0 | 0 | 0 | 0 | 0 | 0
599 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 17778.3 | 18205.9 | 427.6 | 1000 | 0 | 427600 | 430759.7319 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 428567.2222 | 487683.3311 | 567556.8719 | 709475.9549 | 663499.8644 | 692465.8927 | 722974.2051 | 681450.0937 | 758130.0486
600 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129896 | 129896 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 101.1371 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 160068.2 | 161708.3 | 1640.1 | 1000 | 0 | 1640100 | 1652219.4486 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1510568.4289 | 1629622.8772 | 2174578.6154 | 2726585.8445 | 2843859.0812 | 2866014.2453 | 2915044.2314 | 2806489.0873 | 2820775.6603
602 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 | 0 | HA021101013-02 | 1 | 62386752 | 64648696 | 2261944 | 1 | 0 | 2261944 | 2264231.3054 | Matuail | Demra 33/11KV S/S | 16 | 2391584.9101 | 2366952.3646 | 2709931.5892 | 3182659.205 | 3242375.7883 | 2482601.3667 | 2346002.1943 | 2312393.5546 | 2206583.7096
603 | 11 kV DND (WASA) Feeder. | A816B | 11 | 0 | HA021100992-02 | 1 | 6463180 | 6468980 | 5800 | 1 | 0 | 5800 | 5805.865 | Siddirgonj | Demra 33/11KV S/S | 16 | 5456.4588 | 5208.0975 | 4780.8214 | 190285.6191 | 296942.4232 | 349346.3885 | 251256.153 | 80170.7162 | 6927.7253
604 | 11 kV Local Feeder | A816D | 11 | 0 | HA021100794-02 | 1 | 15617269 | 16325156 | 707887 | 1 | 0 | 707887 | 708602.824 | Siddirgonj | Demra 33/11KV S/S | 16 | 672645.2076 | 716853.8184 | 898962.87 | 1098339.8454 | 1209825.1625 | 1190157.3614 | 1182388.6301 | 2088621.9879 | 1417684.9395
605 | 11 kV Mouchak Feeder | A816A | 11 | 0 | DHK60888 | 1 | 1107709.6 | 1137462.4 | 29752.8 | 60 | 0 | 1785168 | 1786973.1837 | Siddirgonj | Demra 33/11KV S/S | 16 | 1810495.0763 | 1833197.9265 | 2048559.8995 | 2345108.3326 | 2403503.8665 | 2439051.751 | 2339275.7144 | 2308639.9015 | 2074135.4747
606 | 11 kV Overhead-1 Feeder | A816C | 11 | 0 | HA021100829-02 | 1 | 80732532 | 81294895 | 562363 | 1 | 0 | 562363 | 562931.6683 | Siddirgonj | Demra 33/11KV S/S | 16 | 389543.1007 | 409132.8253 | 374998.6846 | 432331.1497 | 507759.6491 | 490206.9454 | 1190489.8427 | 1095153.438 | 1095304.9401
607 | 11 kV Provati Steel Feeder | A816Z | 11 | 0 | DHK60874 | 1 | 620995.2 | 624065.6 | 3070.4 | 60 | 0 | 184224 | 184410.2896 | Siddirgonj | Demra 33/11KV S/S | 16 | 340543.0996 | 361196.1665 | 473734.4777 | 572313.5546 | 603535.6264 | 2095360.2501 | 124835.9443 | 0 | 0
608 | 11 kV Islambagh Feeder. | E116I | 11 | 0 | DHKA2190 | 1 | 1267.4897 | 1293.659 | 26.1693 | 60000 | 0 | 1570158 | 1571745.7629 | Matuail | Demra 33/11KV S/S | 16 | 1648945.851 | 1656283.7916 | 1979061.5163 | 2382248.0982 | 2479849.2574 | 3031414.6894 | 2979112.0563 | 3002442.9965 | 2983539.0327
609 | 11 kV Taj Jute Feeder. | A816E | 11 | 0 | DHK61062 | 1 | 743003.7 | 763156.5 | 20152.8 | 60 | 0 | 1209168 | 1210390.7255 | Siddirgonj | Demra 33/11KV S/S | 16 | 1220218.3679 | 1190734.2756 | 1388752.4047 | 1608771.849 | 1850699.8521 | 525126.6242 | 1404410.5059 | 1676660.8446 | 1675376.4941
610 | 11 kV Al-Aksa Steel Feeder | A816S | 11 | 0 | DHK61061 | 1 | 938855.7 | 967430.2 | 28574.5 | 60 | 0 | 1714470 | 1716203.693 | Siddirgonj | Demra 33/11KV S/S | 16 | 1932793.8409 | 1779404.4246 | 1746616.1362 | 1742517.141 | 1948104.7891 | 1679729.0047 | 1595509.5853 | 1474597.4818 | 1597579.1906
611 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 | 0 | DHKA2189 | 1 | 1208.0447 | 1238.7475 | 30.7028 | 60000 | 0 | 1842168 | 1844030.8228 | Siddirgonj | Demra 33/11KV S/S | 16 | 1631573.2872 | 1794950.1423 | 2085198.1573 | 2525197.0695 | 2620588.9584 | 2664152.1809 | 2514049.716 | 2467512.3805 | 2370283.5934
612 | 11 kV Over Head Feeder-2. | E116V | 11 | 0 | HA021100488-02 | 1 | 37716071 | 38981989 | 1265918 | 1 | 0 | 1265918 | 1267198.1117 | Demra | Demra 33/11KV S/S | 16 | 1259081.3699 | 1356452.5121 | 1697694.9376 | 2095936.8227 | 2186616.3464 | 2197276.8827 | 2204224.8423 | 2131027.6013 | 2071443.4949
613 | 11 kV Shimrail Express Feeder. | A8164 | 11 | 0 | HA021100511-02 | 1 | 8257879 | 8260815 | 2936 | 1 | 0 | 2936 | 2938.9689 | Siddirgonj | Demra 33/11KV S/S | 16 | 1751.0727 | 1221.9385 | 542.4548 | 30546.5041 | 1269.0967 | 53083.1379 | 75076.7556 | 29225.6688 | 0
614 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 | 0 | HA021100413-02 | 1 | 82841955 | 83053097 | 211142 | 1 | 0 | 211142 | 211355.5094 | Demra | Demra 33/11KV S/S | 16 | 155799.4192 | 165955.9755 | 367927.7214 | 330954.2369 | 688064.1207 | 409117.6527 | 331227.7744 | 650733.1002 | 409613.9007
615 | 11 kV Siddhirgonj Mazar Feeder | 0 | 11 | 0 | HA021100393-02 | 1 | 28334.251 | 29040.997 | 706.746 | 1000 | 0 | 706746 | 707460.6702 | Siddirgonj | Demra 33/11KV S/S | 16 | 701621.5068 | 745130.6648 | 826630.8876 | 1127913.2115 | 1241829.7858 | 1214207.0897 | 1262090.4156 | 281800.301 | 832832.3648
616 | 11 kV AST Beverage Feeder | A816J | 11 | 0 | 0 | 1 | 23850034 | 24496315 | 646281 | 1 | 0 | 646281 | 646934.5272 | Siddirgonj | Demra 33/11KV S/S | 16 | 263535.9465 | 229794.9606 | 294965.0476 | 533291.7199 | 269111.0012 | 890478.2395 | 1164572.2996 | 1051751.2525 | 1163750.6238
617 | 11 kV Karim Market Feeder | E216K | 11 | 0 | 0 | 1 | 67122.502 | 68636.598 | 1514.096 | 1000 | 0 | 1514096 | 1515627.0724 | Matuail | Demra 33/11KV S/S | 16 | 1401951.4847 | 1302810.1155 | 1746397.55 | 2153249.6409 | 2251573.1315 | 2292212.1727 | 2119617.9699 | 2072299.946 | 2089377.8867
618 | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 | 0 | 2007755114 | 1 | 6034.84 | 6071.31 | 36.47 | 60000 | 0 | 2188200 | 2235638.4098 | Demra | Sarulia 33/11KV S/S | 83 | 2167253.8322 | 2226080.12 | 2656170.9356 | 3219680.3589 | 3402160.7226 | 2567812.3685 | 2674737.7934 | 2648546.8605 | 3036942.6611
620 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 | 0 | 30799484 | 1 | 22.8458 | 23.0952 | 0.2494 | 60000 | 0 | 14964 | 15288.4074 | Demra | Sarulia 33/11KV S/S | 83 | 16496.2847 | 16293.6103 | 14090.6259 | 14581.402 | 14754.6723 | 14656.6857 | 14157.8637 | 13577.9934 | 12817.0467
621 | 11 kV Konapara (=L13) **** | E183KL | 11 | 0 | DHKA2191 | 1 | 2297.792 | 2325.0065 | 27.2145 | 60000 | 0 | 1632870 | 1668269.3036 | Demra | Sarulia 33/11KV S/S | 83 | 1627629.3973 | 1712858.9074 | 2092594.4251 | 2580974.9024 | 2723567.5839 | 3439291.4731 | 3588042.0557 | 3482255.5223 | 2467003.1131
622 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 | 0 | 575926 | 1 | 63859.6 | 65468 | 1608.4 | 1000 | 0 | 1608400 | 1643268.8138 | Matuail | Sarulia 33/11KV S/S | 83 | 1600042.8683 | 1706804.0836 | 2044950.3572 | 2502341.7238 | 2566996.3354 | 2566696.0166 | 2627544.9143 | 2556143.6589 | 2386518.0767
623 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 | 0 | 30799450 | 1 | 1838.66 | 1843.4 | 4.74 | 60000 | 0 | 284400 | 290565.5624 | Demra | Sarulia 33/11KV S/S | 83 | 267278.5139 | 269624.0958 | 277809.1547 | 324637.9555 | 325784.1394 | 326380.7042 | 261798.4288 | 295524.6849 | 302404.9427
624 | 11 kV Tengra Feeder (=L16) | E183T | 11 | 0 | 30799145 | 1 | 5710.51 | 5742.63 | 32.12 | 60000 | 0 | 1927200 | 1968980.1404 | Demra | Sarulia 33/11KV S/S | 83 | 1872159.0024 | 1909990.1936 | 2317704.7602 | 2700866.43 | 2803570.4254 | 2888103.8805 | 2785803.7935 | 2203397.2826 | 3315319.3041
625 | 11 kV Police Line Feeder (=L17) | E183PL | 11 | 0 | 30799480 | 1 | 3424.38 | 3439.36 | 14.98 | 60000 | 0 | 898800 | 918285.2585 | Demra | Sarulia 33/11KV S/S | 83 | 856863.471 | 825379.8852 | 1025710.2197 | 1276100.2252 | 1292175.5957 | 1231843.5906 | 1213792.7153 | 1297576.8726 | 1183247.2468
626 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 | 0 | 30799119 | 1 | 1681.12 | 1686.61 | 5.49 | 60000 | 0 | 329400 | 336541.1261 | Demra | Sarulia 33/11KV S/S | 83 | 321701.7407 | 327706.384 | 385778.6515 | 493328.3324 | 441483.1795 | 534022.1596 | 561432.5279 | 558765.1604 | 495803.4526
627 | 11 kV Spare Feeder (=F9) | 0 | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
628 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 | 0 | HA021100493-02 | 1 | 95230968 | 97024827 | 1793859 | 1 | 0 | 1793859 | 1832748.4152 | Demra | Sarulia 33/11KV S/S | 83 | 1739187.9417 | 1816680.4881 | 2264027.3407 | 2874690.3342 | 3063617.2119 | 3062145.1731 | 3047117.0714 | 3001937.8862 | 2753359.8865
629 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 | 0 | HA021100518-02 | 1 | 50895377 | 51370624 | 475247 | 1 | 0 | 475247 | 485549.9714 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 26104.5324 | 0 | 0 | 1592.7597 | 158210.2162 | 30254.1689
630 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 | 0 | HA021100697-02 | 1 | 33817648 | 35299061 | 1481413 | 1 | 0 | 1481413 | 1513528.8381 | Demra | Sarulia 33/11KV S/S | 83 | 1400106.0427 | 1357872.1896 | 1792379.5779 | 2145386.6161 | 2228761.3555 | 2265661.5752 | 2324189.2905 | 2304863.862 | 2171918.011
631 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
632 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
633 | 11 kV Khanpur Feeder | B723B | 11 | 0 | DHKC 9348 | 1 | 86923.13 | 103601.58 | 16678.45 | 60 | 0 | 1000707 | 1012173.2768 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 918289.8994 | 1015879.0626 | 1344397.4603 | 1671397.6523 | 1767813.7522 | 1753296.6737 | 1849730.4598 | 1858439.2031 | 1689432.0922
634 | 11 kV Mission Para Feeder. | B723T | 11 | 0 | DHKC 9347 | 1 | 65601.86 | 79593.68 | 13991.82 | 60 | 0 | 839509.2 | 849128.444 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 935490.5604 | 982656.0237 | 1274888.2401 | 1557478.0335 | 1662446.9196 | 1652830.7535 | 1736094.2229 | 1666330.9001 | 1591097.4109
635 | 11 kV Esha Kha Feeder | B723M | 11 | 0 | DHKC 9311 | 1 | 66957.6 | 77627.6 | 10670 | 60 | 0 | 640200 | 647535.5242 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 713273.6195 | 741879.3371 | 807699.1496 | 1039293.9368 | 1004043.7507 | 968513.5517 | 939733.5453 | 917602.1317 | 1040108.3114
636 | 11 kV New Hazigonj Feeder | B723F | 11 | 0 | DHKC 9314 | 1 | 345.95 | 367.79 | 21.84 | 60000 | 0 | 1310400 | 1325414.7936 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1294152.4735 | 1358220.3111 | 1630966.9503 | 2057845.6627 | 2170066.5597 | 2135314.0661 | 2193735.673 | 2054393.8757 | 2135156.6373
637 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
638 | 11 kV Hospital RMU Feeder. | B723H | 11 | 0 | 6604412 | 1 | 9.86 | 10.41 | 0.55 | 60000 | 0 | 33000 | 33378.1198 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 30279.6554 | 34561.8561 | 46010.9459 | 61862.7343 | 64307.2562 | 63695.448 | 65004.0756 | 61352.3895 | 59949.0945
639 | 11 kV Old Hajiganj Feeder. | B723E | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 | 0 | 06604389 | 1 | 10821.98 | 23295.95 | 12473.97 | 60 | 0 | 748438.2 | 757013.9365 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 746540.6657 | 762467.8954 | 948106.9996 | 1250130.6264 | 1328944.0291 | 1304005.3624 | 1304824.3795 | 1324560.4284 | 1260578.6756
641 | 11 kV Spare Feeder. | 0 | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642 | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643 | 11 kV B. B. Road West Feeder. | A723A | 11 | 0 | 6604415 | 1 | 467.5 | 495.02 | 27.52 | 40000 | 0 | 1100800 | 1113413.16 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1010129.3055 | 1178741.1985 | 1517554.0047 | 1864372.9936 | 1918297.585 | 1915716.4264 | 1976042.8964 | 1840166.7201 | 1800087.6245
644 | 11 kV Mondalpara Feeder. | 0 | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645 | 11 kV B. B. Road East Feeder. | B723C | 11 | 0 | 06604392 | 1 | 367.96 | 389.72 | 21.76 | 40000 | 0 | 870400 | 880373.1963 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 834911.0327 | 978242.0098 | 1208392.7367 | 1428099.2005 | 1517085.0182 | 1504830.2349 | 1509066.5776 | 1463548.0912 | 1396793.7162
646 | 11 kV Bishaw Road Feeder. | B723A | 11 | 0 | 06604393 | 1 | 366.72 | 383.73 | 17.01 | 40000 | 0 | 680400 | 688196.1428 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 670593.4358 | 707406.412 | 953718.1152 | 1117572.534 | 1216580.0413 | 1210820.1352 | 1222724.6371 | 1779421.78 | 1969640.6189
647 | 11 kV Chasara Feeder. | A723B | 11 | 0 | 06604391 | 1 | 507.05 | 535.07 | 28.02 | 40000 | 0 | 1120800 | 1133642.3235 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1109850.3041 | 1211079.7774 | 1572444.256 | 1942004.6602 | 2118903.8684 | 2081122.3834 | 2195963.227 | 2115948.7484 | 2048765.3497
648 | 11 kV Pathan Tully Feeder. | B723G | 11 | 0 | 06604388 | 1 | 96.85 | 105.87 | 9.02 | 40000 | 0 | 360800 | 364934.1098 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 358511.1204 | 398168.7519 | 528318.6681 | 576981.1889 | 529827.0791 | 160552.9705 | 39690.9621 | 0 | 0
649 | 11 kV Spare Feeder. | 0 | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650 | 11 kV Nayamati Feeder. | B722J | 11 | 0 | 6604289 | 1 | 340.54 | 364.95 | 24.41 | 40000 | 0 | 976400 | 987587.7629 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 913638.1368 | 930138.3737 | 1139779.9227 | 1329442.2908 | 1269562.7492 | 1343468.4333 | 1193968.9401 | 1316545.3361 | 1343505.6323
651 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
652 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654 | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0.415 | 0 | 412109 | 1 | 9309.8 | 9315.4 | 5.6 | 10 | 0 | 56 | 56.6417 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 364.3652 | 398.1688 | 305.7306 | 270.9022 | 317.4918 | 324.5435 | 42.526 | 0 | 0
655 | 33/0.415 kV Auxiliary Transformer-2 | 0 | 0.415 | 0 | 243285 | 1 | 6441.8 | 6467.1 | 25.3 | 10 | 0 | 253 | 255.8989 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 86.8017 | 3031.7418 | 3027.0359 | 3032.487 | 3033.3611 | 3033.1166 | 3037.5736 | 3037.247 | 3027.732
656 | 11 kV Link Road Feeder | B741N | 11 | 0 | HA021100475-02 | 1 | 3617.14 | 5393.63 | 1776.49 | 1000 | 0 | 1776490 | 1787596.815 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1834777.3994 | 1840204.9638 | 2900288.7042 | 3109326.5102 | 2934230.0248 | 2975929.581 | 2607402.2302 | 1951841.3049 | 1877540.2045
657 | 11 kV Lamapara Express Feeder | B723L | 11 | 0 | HA021100928-03 | 1 | 83442.772 | 84501.883 | 1059.111 | 1000 | 0 | 1059111 | 1065732.6809 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1202097.8234 | 1103207.3553 | 980020.9332 | 1044271.2809 | 777935.2019 | 1101665.3091 | 726895.7131 | 1017580.9915 | 1063497.0225
658 | 11 kV Kutubpur Feeder*** | B741Q | 11 | 0 | DHK66616 | 1 | 18785.32 | 18919.7 | 134.38 | 8000 | 0 | 1075040 | 1081761.2708 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1059892.9128 | 1193545.2469 | 1740376.2153 | 1768072.7988 | 1341995.221 | 1569417.834 | 1641482.3695 | 1554956.8642 | 1703285.4205
659 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 | 0 | DHK66625 | 1 | 3631.91 | 3646.26 | 14.35 | 60000 | From Check Meter | 1093749 | 1100587.2416 | Fatullah | Matuail 33/11KV S/S | 41 | 922012.825 | 1114398.8642 | 1066770.6323 | 1419365.2857 | 1418275.2675 | 1534196.2033 | 1364062.3916 | 1338941.0426 | 835792.1765
660 | 11 kV Tushardhara Feeder (F2) | E241T | 11 | 0 | DHK66623 | 1 | 4045.32 | 4080.1 | 34.78 | 60000 | 0 | 2086800 | 2099846.908 | Matuail | Matuail 33/11KV S/S | 41 | 2082664.2636 | 2163280.5387 | 2634875.0823 | 2672602.3834 | 2999054.9265 | 2829014.2755 | 2689931.0362 | 2755784.1096 | 2760297.6743
661 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 | 0 | DHK66627 | 1 | 3369.81 | 3381.23 | 11.42 | 60000 | 0 | 685200 | 689483.9474 | Matuail | Matuail 33/11KV S/S | 41 | 717723.7089 | 732821.8987 | 826686.7655 | 937957.3247 | 903475.9079 | 1019170.5275 | 792368.687 | 795452.7012 | 696897.8308
662 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 | 0 | HA021101044-02 | 1 | 67133.062 | 67308.119 | 175.057 | 1000 | 0 | 175057 | 176151.476 | Matuail | Matuail 33/11KV S/S | 41 | 179169.7907 | 186138.5822 | 243777.8524 | 299669.3822 | 351957.4279 | 332319.5113 | 349545.5347 | 361905.6203 | 323912.9361
663 | 11 kV Shibu Market Feeder (F7) | B841B | 11 | 0 | DHK66624 | 1 | 2401.85 | 2405.22 | 3.37 | 60000 | 0 | 202200 | 203464.1771 | Fatullah | Matuail 33/11KV S/S | 41 | 183799.9422 | 165612.896 | 311443.8071 | 425021.3863 | 388070.1886 | 515025.6758 | 398306.2183 | 387075.6832 | 615623.4101
664 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 | 0 | HA060300286-03 | 1 | 8238.449 | 8238.449 | 0 | 1000 | 0 | 0 | 0 | Fatullah | Matuail 33/11KV S/S | 41 | 601987.9988 | 1287577.5801 | 1300740.5246 | 1507092.8931 | 1340202.4176 | 1497969.2549 | 1502329.9696 | 1201993.7471 | 1110650.3388
665 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 | 0 | DHK66626 | 1 | 4603.97 | 4634.5 | 30.53 | 60000 | 0 | 1831800 | 1843252.6193 | Matuail | Matuail 33/11KV S/S | 41 | 1806060.4161 | 1852680.5287 | 2054924.3814 | 2632586.1045 | 2681928.8192 | 2638599.8531 | 2625668.5413 | 2669361.5514 | 2690547.2387
666 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | 0 | DHK6622 | 1 | 4311.94 | 4327.96 | 16.02 | 60000 | 0 | 961200 | 967209.5304 | Matuail | Matuail 33/11KV S/S | 41 | 969620.0232 | 1128958.2396 | 1266941.3122 | 1346002.1078 | 1350362.9845 | 1363125.4682 | 1274337.3987 | 1416234.4574 | 1374993.3702
667 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 | 0 | DHKA2187 | 1 | 143.2655 | 148.8233 | 5.5578 | 60000 | 0 | 333468 | 335552.8794 | Shyampur | Matuail 33/11KV S/S | 41 | 346363.4584 | 348090.4019 | 342400.7167 | 335087.831 | 248953.0896 | 243349.6318 | 240620.6059 | 244740.1643 | 218634.2568
668 | 11 kV Bhuighor Bazar | 0 | 11 | 0 | HA021100861-02 | 1 | 5007.34 | 5868.005 | 860.665 | 1000 | 0 | 860665 | 866045.9742 | Matuail | Matuail 33/11KV S/S | 41 | 806459.9105 | 881844.1841 | 1074012.4568 | 1411612.637 | 1387743.4624 | 1286702.6096 | 1290448.3093 | 1462145.9342 | 1034107.8281
669 | 11 kV Tokkar Math Feeder | B8416 | 11 | 0 | HA021200298-02 | 1 | 84494.857 | 85107.792 | 612.935 | 1000 | 0 | 612935 | 616767.1385 | Fatullah | Matuail 33/11KV S/S | 41 | 627491.9984 | 593103.4586 | 658390.1923 | 791536.1434 | 789253.9157 | 797388.0996 | 771061.022 | 778486.6953 | 733095.2742
670 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 | 0 | XA575922 | 1 | 268.7 | 278.3 | 9.6 | 1000 | 0 | 9600 | 9660.0203 | Fatullah | Matuail 33/11KV S/S | 41 | 9139.7785 | 9807.3571 | 17235.2398 | 19603.9346 | 10611.2942 | 9873.3404 | 9194.7909 | 13287.9755 | 64493.8811
671 | 33/0.415 KV Transformer, AT-1 | 0 | 0.415 | 0 | 2001123043119 | 1 | 7750 | 7808 | 58 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 41 | 0 | 9398.8857 | 7772.9924 | 11624.9311 | 12240.3805 | 12799.0731 | 12965.6656 | 12496.7831 | 11807.0303
672 | 33/0.415 KV Transformer, AT-2 | 0 | 0.415 | 0 | 2001123043157 | 1 | 4727.8 | 4727.8 | 0 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 41 | 0 | 161.7708 | 1854.5521 | 0 | 0 | 0 | 0 | 0 | 129.3921
673 | 11 kV Godnail (F16) | A8963 | 11 | 0 | 00000109 | 1 | 34819036 | 36125672 | 1306636 | 1 | 0 | 1306636 | 1325877.9256 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1267100.9327 | 1350455.4719 | 1608130.1776 | 1902311.4075 | 2038403.821 | 2022169.7421 | 1902174.2906 | 1848814.9706 | 1869406.9017
674 | 11 kV M. Circus (F15) | B796C | 11 | 0 | 00000123 | 1 | 117011272 | 118224352 | 1213080 | 1 | 0 | 1213080 | 1230944.191 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1439707.0094 | 1375608.1121 | 1875844.4545 | 1681278.3417 | 1521029.259 | 1828274.6635 | 1936785.1498 | 1975646.3394 | 2135882.0516
675 | 11 kV Wapderpool (F14) | B723W | 11 | 0 | 00000190 | 1 | 61037372 | 61829048 | 791676 | 1 | 0 | 791676 | 803334.4655 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 807747.7986 | 974393.4111 | 927244.3035 | 798221.6352 | 482340.828 | 822312.035 | 474935.0147 | 619875.2088 | 595303.4365
676 | 11 kV Chowdhury Bari (F13) | A896C | 11 | 0 | 00000191 | 1 | 111311768 | 113386280 | 2074512 | 1 | 0 | 2074512 | 2105061.9049 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2122803.1132 | 1958911.0549 | 2117617.9441 | 2183088.6246 | 2226891.1005 | 2193767.4037 | 2204031.0267 | 2287431.9192 | 2194488.2982
677 | 11 kV Ailpara (F12) | B7966 | 1 | 0 | 00000192 | 1 | 64386884 | 66223200 | 1836316 | 1 | 0 | 1836316 | 1863358.157 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1617658.7416 | 1713518.3698 | 2091231.2297 | 2449465.553 | 2507772.6658 | 2664936.682 | 2385423.2662 | 2312455.9158 | 2506620.5244
678 | 11 kV Spare (F11) | 0 | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679 | 11 kV Spare (F10) | 0 | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680 | 11 kV Spare (F9) | 0 | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | 11 kV Spare (F8) | 0 | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | 11 kV Zulfiqur Steel | A8962H | 11 | 0 | 00000197 | 1 | 22047826 | 23453782 | 1405956 | 1 | 0 | 1405956 | 1426660.5426 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1166769.562 | 1163525.0319 | 1070830.7575 | 1205147.4911 | 881898.0967 | 1269192.9831 | 1109871.8066 | 1233882.0915 | 1248729.4855
683 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 | 0 | 00000198 | 1 | 4368189 | 4418549 | 50360 | 1 | 0 | 50360 | 51101.6169 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 64212.0772 | 13874.8369 | 49416.8148 | 38314.1839 | 81476.5739 | 45981.5802 | 80821.2927 | 12574.267 | 42071.0581
684 | 11 kV Lucky Bazar (F5) | B796Z | 11 | 0 | 00000199 | 1 | 96274088 | 97578320 | 1304232 | 1 | 0 | 1304232 | 1323438.5235 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1347891.7655 | 1310312.4098 | 1175901.2838 | 1409832.0895 | 1363293.8581 | 1360268.1394 | 1265880.4844 | 1332623.2308 | 1392661.9878
685 | 11 kV Enayetnagar (F4) | A896Y | 11 | 0 | 00000200 | 1 | 39019104 | 40056704 | 1037600 | 1 | 0 | 1037600 | 1052880.0183 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1078999.679 | 1127096.5876 | 1294647.5791 | 1539178.9886 | 1637703.7047 | 1666199.7304 | 1606948.7378 | 1544300.7721 | 1576051.8888
686 | 11 kV Bhuiyapara (F3) | A896V | 11 | 0 | 00000201 | 1 | 72932584 | 73827656 | 895072 | 1 | 0 | 895072 | 908253.1069 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1072141.0265 | 1088994.766 | 1494739.0596 | 1820491.9548 | 1638474.4387 | 1895985.9869 | 1703398.6781 | 2021560.4921 | 1949356.1666
687 | 11 kV Arambagh (F2) | B796D | 11 | 0 | 00000202 | 1 | 13814126 | 14628804 | 814678 | 1 | 0 | 814678 | 826675.2 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 841577.5302 | 830808.8415 | 965266.6711 | 1110256.976 | 1096967.543 | 1072171.1368 | 1011302.9055 | 1033739.3311 | 1073358.7436
688 | 11 kV Spare (F1) | 0 | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
689 | 11/0.415 kV Aux. Transformer-1 | 0 | 0.415 | 0 | 00000204 | 1 | 1830.36 | 1853.89 | 23.53 | 100 | 0 | 2353 | 2387.651 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2350.764 | 2401.1065 | 2999.8723 | 4062.7646 | 4590.7608 | 4148.0738 | 5028.3475 | 4509.4616 | 4713.1396
690 | 11/0.415 kV Aux. Transformer-2 | 0 | 0.415 | 0 | 00000205 | 1 | 61.17 | 61.17 | 0 | 100 | 0 | 0 | 0 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 1.0135 | 44.6458 | 0 | 0 | 0.99927 | 0 | 0
691 | 11 kV Minan Steel Feeder | A717R | 11 | New | 0 | 1 | 79206654 | 79864949 | 658295 | 1 | 0 | 658295 | 658925.6265 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 544365.4981 | 588603.6575 | 632806.8774 | 639787.7036 | 668682.8226 | 690626.9008 | 493276.6302 | 608736.535 | 686221.5647
692 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 92516438 | 93349508 | 833070 | 1 | 0 | 833070 | 833868.0556 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 734193.3379 | 589703.3771 | 831073.3841 | 837776.7717 | 798148.0435 | 798255.2776 | 675313.5877 | 687996.4568 | 904286.638
693 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 253988.1 | 267690.1 | 13702 | 60 | 0 | 822120 | 822907.5658 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 751822.0823 | 805408.7269 | 1363029.7869 | 1190995.536 | 1654746.3681 | 1713127.7082 | 1429973.3518 | 1348752.6633 | 1520277.0648
694 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
695 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 391310.2 | 401337.2 | 10027 | 60 | 0 | 601620 | 602196.3336 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 614880.4759 | 633572.4534 | 733183.1825 | 994384.377 | 1017275.0549 | 998917.0422 | 983661.4804 | 966418.4358 | 973413.7301
696 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 135662.3 | 156105.3 | 20443 | 60 | 0 | 1226580 | 1227755.0262 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1228977.05 | 1274431.057 | 1605474.9303 | 1916663.5337 | 1932341.6728 | 1605143.4286 | 2269442.86 | 1903765.6601 | 1898489.4903
697 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 120216.4 | 129577.4 | 9361 | 60 | 0 | 561660 | 562198.0531 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 577554.6924 | 520579.2992 | 625630.6419 | 700600.4968 | 623925.9784 | 637276.1792 | 646164.6825 | 667510.2274 | 661387.5474
698 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 699968.1 | 710675.1 | 10707 | 60 | 0 | 642420 | 643035.4187 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 681813.6257 | 748829.9751 | 893996.3722 | 935867.4295 | 898188.9867 | 879720.3375 | 817413.76 | 827156.9088 | 863427.9271
699 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 616583.2 | 635410.2 | 18827 | 60 | 0 | 1129620 | 1130702.1414 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1213118.1146 | 1212550.5201 | 1055367.6461 | 1081150.4699 | 1065440.2479 | 1123770.5196 | 1043132.595 | 1256184.2479 | 1130265.9765
700 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 927864.3 | 956770.4 | 28906.1 | 60 | 0 | 1734366 | 1736027.4696 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1558577.5876 | 1208307.8746 | 283482.5341 | 300394.2285 | 217235.7079 | 274279.1183 | 230613.5281 | 268951.939 | 461817.7457
701 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 3404.6005 | 458632.0662 | 1006566.474 | 739323.8488 | 888156.2557 | 505747.1466
702 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 4060626 | 4501007 | 440381 | 1 | 0 | 440381 | 440802.8715 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 419238.6981 | 498256.2069 | 624571.0906 | 739019.2541 | 764214.6584 | 798862.9891 | 731731.9387 | 686782.5544 | 645276.6941
703 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 26535184 | 26739064 | 203880 | 1 | 0 | 203880 | 204075.3108 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 181356.6758 | 211501.2553 | 266805.7231 | 329009.9458 | 336317.7733 | 326230.0217 | 318326.9039 | 335635.5116 | 326421.8579
704 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 17345074 | 17738197 | 393123 | 1 | 0 | 393123 | 393499.5998 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 398817.0524 | 452997.2635 | 377407.5066 | 371813.5071 | 231457.5089 | 350113.1813 | 373857.3757 | 329133.6781 | 311868.8913
705 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
706 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123409.7429 | 535601.4665
707 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 19199164 | 19678202 | 479038 | 1 | 0 | 479038 | 479496.9038 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 465312.0212 | 491241.9432 | 609177.2667 | 739088.5512 | 985608.2317 | 2067941.9788 | 1957359.7515 | 2145386.8814 | 2599917.6327
708 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709 | 0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 2782121.1 | 13885274 | 11103152.9 | 1 | Estimated | 583466 | 584024.9426 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 569321.714 | 1017186.028 | 997122.6577 | 1798366.2205 | 1947566.1648 | 1839951.043 | 1845653.8856 | 1844325.072 | 1788794.6263
711 | 11 kV Spare Feeder | 0 | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
713 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | 11 kV Outgoing Feeder-2 (=F2) | 0 | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 1078.73 | 1099.46 | 20.73 | 60000 | 0 | 1243800 | 1248012.9185 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1373799.9394 | 1431717.6049 | 1967161.5939 | 2374197.2935 | 2139879.5383 | 2225117.9731 | 1919103.2774 | 1925513.8961 | 2018573.5941
716 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 549.2 | 563.02 | 13.82 | 60000 | 0 | 829200 | 832008.6124 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 848842.2062 | 956888.7023 | 1278564.8268 | 1599035.1072 | 1814088.8895 | 1616939.3533 | 1431521.3433 | 1476167.1668 | 1492878.3256
717 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 586.35 | 593.29 | 6.94 | 60000 | 0 | 416400 | 417810.403 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 413584.8196 | 430238.3712 | 517800.713 | 643462.7923 | 673220.5289 | 698887.9434 | 713358.7902 | 702593.0118 | 691704.3007
718 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1337.33 | 1359.7 | 22.37 | 60000 | 0 | 1342200 | 1346746.2126 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1312996.3488 | 1377485.8774 | 1511304.5202 | 1737349.5392 | 1778023.504 | 1913418.8206 | 1823628.4898 | 1708359.7204 | 1811062.3039
719 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
720 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
721 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | 11 kV Outgoing Feeder-10 (=F8) | 0 | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | 11 kV Outgoing Feeder-11 (=F9) | 0 | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 250.63 | 264.89 | 14.26 | 60000 | 0 | 855600 | 858498.0327 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 696532.2217 | 679704.3175 | 841952.3789 | 1083663.5063 | 1145075.9889 | 1196876.0424 | 1264590.5826 | 1201867.1554 | 1168078.0452
725 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 114.82 | 119.87 | 5.05 | 60000 | 0 | 303000 | 304026.3019 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 281141.3548 | 298274.501 | 420374.7949 | 572501.475 | 611308.2838 | 620963.1553 | 614881.6508 | 573262.9625 | 566596.0446
726 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1283.61 | 1307.02 | 23.41 | 60000 | 0 | 1404600 | 1409357.5699 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2028191.0587 | 1764941.4414 | 2561940.8101 | 2204010.4054 | 1471467.7275 | 1601110.8808 | 1579237.0524 | 1146525.925 | 1680540.7098
727 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1548.27 | 1574.97 | 26.7 | 60000 | 0 | 1602000 | 1607426.1903 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1683236.0345 | 1822788.6174 | 2278082.5795 | 2618352.3343 | 2670641.7946 | 2813206.6084 | 2526178.8135 | 2500581.4639 | 2536449.5967
728 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | 11 kV Katherpol Feeder | B8919 | 11 | 0 | 00000031 | 1 | 74107936 | 75499056 | 1391120 | 1 | 0 | 1391120 | 1398334.1219 | Fatullah | Dapa 33/11 kV | 91 | 1565992 | 1480200.745 | 1780543.7815 | 2017920.9065 | 1907068.817 | 2019617.347 | 1872668.2415 | 1825325.1091 | 2095256.7912
730 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | 11 kV Union Parishad Feeder | B8918 | 11 | 0 | 00000032 | 1 | 75379016 | 76520056 | 1141040 | 1 | 0 | 1141040 | 1146957.2477 | Fatullah | Dapa 33/11 kV | 91 | 1688392 | 1796775.704 | 2128228.6671 | 2252272.5782 | 1663620.755 | 1557194.9668 | 1351133.0591 | 1174339.0851 | 1364658.7564
732 | 11 kV Shiachar Feeder | B891G | 11 | 0 | 00000030 | 1 | 75050736 | 75786576 | 735840 | 1 | 0 | 735840 | 739655.9465 | Fatullah | Dapa 33/11 kV | 91 | 775000 | 849100.2736 | 1635781.9984 | 2031118.288 | 2032383.0231 | 2001560.8541 | 1924678.9852 | 1907532.8668 | 1901950.2285
733 | 11 kV Sastapur Feeder | B8913 | 11 | 0 | 00000106 | 1 | 72981944 | 73300544 | 318600 | 1 | 0 | 318600 | 320252.2077 | Fatullah | Dapa 33/11 kV | 91 | 338920 | 349293.4873 | 488573.0611 | 516338.7434 | 559825.9548 | 395679.6151 | 1143053.371 | 1344939.9892 | 1492863.3157
734 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
735 | 11 kV Jalal Ahmed Express | B891JA | 11 | 0 | 00000172 | 1 | 7006920 | 7453942 | 447022 | 1 | 0 | 447022 | 449340.1833 | Fatullah | Dapa 33/11 kV | 91 | 1127415 | 0 | 247329.6416 | 398396.8352 | 281983.6134 | 872.8694 | 163.171 | 71453.7073 | 791901.0884
736 | 11 kV Hajibari Feeder | 0 | 11 | 0 | 00000105 | 1 | 1476956 | 2068515 | 591559 | 1 | 0 | 591559 | 594626.7287 | Fatullah | Dapa 33/11 kV | 91 | 623399 | 694510.2702 | 168427.36 | 0 | 0 | 0 | 0 | 0 | 0
737 | 11 kV Railine Feeder | 0 | 11 | 0 | 0 | 1 | 1930995 | 2811513 | 880518 | 1 | 0 | 880518 | 885084.223 | Fatullah | Dapa 33/11 kV | 91 | 827958 | 915027.503 | 200012.7891 | 0 | 0 | 0 | 0 | 0 | 0
738 | 11 kV Lalpur Feeder | B8911 | 11 | 0 | 00000044 | 1 | 87270824 | 87457064 | 186240 | 1 | 0 | 186240 | 187205.8103 | Fatullah | Dapa 33/11 kV | 91 | 187040 | 708301.6746 | 2338751.8857 | 2709693.2174 | 2479807.3342 | 1402820.0857 | 1449235.5198 | 1159780.4978 | 373576.7292
739 | 11 kV Kotaler Bag Feeder | B8912 | 11 | 0 | 00000050 | 1 | 94020488 | 95110648 | 1090160 | 1 | 0 | 1090160 | 1095813.3923 | Fatullah | Dapa 33/11 kV | 91 | 1076072 | 1381238.2912 | 2006422.5038 | 2309410.8982 | 2305548.0804 | 2521037.1496 | 1462297.3552 | 1401235.8745 | 1515181.1462
740 | 11 kV Idrakpur Feeder | B8915 | 11 | 0 | 00000021 | 1 | 81621160 | 82410480 | 789320 | 1 | 0 | 789320 | 793413.285 | Fatullah | Dapa 33/11 kV | 91 | 821400 | 784429.7423 | 983847.2999 | 1146390.3941 | 1054879.9219 | 1213883.5456 | 1042540.0593 | 1114166.2721 | 1068664.5804
741 | 11 kV Isdair Feeder | B8914 | 11 | 0 | 00000029 | 1 | 44106812 | 44588012 | 481200 | 1 | 0 | 481200 | 483695.4249 | Fatullah | Dapa 33/11 kV | 91 | 494720 | 530149.0861 | 624149.3274 | 790469.7993 | 829018.6896 | 795100.6656 | 849835.155 | 794122.676 | 792940.801
742 | 11 kV Shah Fateullah Express | 0 | 11 | 0 | 0000051 | 1 | 7578901 | 7862421 | 283520 | 1 | 0 | 283520 | 284990.2886 | Fatullah | Dapa 33/11 kV | 91 | 1400836 | 1420045.653 | 1937861.0792 | 1875856.2789 | 1015342.7418 | 0 | 0 | 0 | 0
743 | 11 kV Boubazar Feeder | 0 | 11 | 0 | 00000151 | 1 | 1726035 | 3051752 | 1325717 | 1 | 0 | 1325717 | 1332591.9526 | Fatullah | Dapa 33/11 kV | 91 | 1146597 | 560490.3774 | 24229.4565 | 0 | 0 | 0 | 0 | 0 | 0
744 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
745 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0 | 0.415 | 0 | DHKF 7522 | 1 | 3306 | 3343 | 37 | 100 | 0 | 3700 | 3719.1876 | Fatullah | Dapa 33/11 kV | 91 | 3300 | 3429.1922 | 4801.1487 | 6039.9915 | 6235.0379 | 5653.8129 | 5914.9473 | 5529.8501 | 5198.5629
746 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | 11 kV Bholail Feeder (F-3) | E330V | 11 | 0 | DHK 9335 | 1 | 77455.415 | 108437.6691 | 30982.2541 | 60 | 0 | 1858935.246 | 1858324.9967 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 2013674.4126 | 1692519.7695 | 2733762.095 | 2632122.2753 | 3204950.7718 | 3202295.2627 | 3113891.785 | 3046734.2178 | 2464743.5384
748 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 | 0 | DHK 9336 | 1 | 68565.3996 | 80596.998 | 12031.5984 | 60 | 0 | 721895.904 | 721658.9208 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 955009.3094 | 1092978.0641 | 1031371.3237 | 1296469.7835 | 1414735.196 | 1450857.7553 | 1198137.3888 | 1083589.5043 | 1409860.9795
749 | 11 kV Baburail Feeder (F-5) | A730R | 11 | 0 | DHK 9322 | 1 | 50469.7377 | 69584.4928 | 19114.7551 | 60 | 0 | 1146885.306 | 1146508.8077 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 1148290.4515 | 1225286.419 | 1578860.4613 | 1983304.4857 | 2103409.2909 | 2067517.7824 | 2058052.5984 | 2038840.2789 | 1960329.6227
750 | 11 kV Goghchar Feeder (F-1) | E330G | 11 | 0 | DHK 9323 | 1 | 22798.1622 | 36757.1711 | 13959.0089 | 60 | 0 | 837540.534 | 837265.5871 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 867815.5092 | 869060.5556 | 1024995.3245 | 1237157.8572 | 1317359.8624 | 1330855.5581 | 1324242.6499 | 1303267.9767 | 1261095.5642
751 | 11 kV Norshinghopur (F-2) | E330N | 11 | 0 | DHK 9365 | 1 | 42671.5983 | 63259.5479 | 20587.9496 | 60 | 0 | 1235276.976 | 1234871.4606 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1546668.4472 | 1465002.492 | 1580945.372 | 1560990.7311 | 1355613.7656 | 1460780.2783 | 1404336.8639 | 1352601.3966 | 1471201.0567
752 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 | 0 | DHK 9367 | 1 | 48332.3462 | 59007.8114 | 10675.4652 | 60 | 0 | 640527.912 | 640317.6402 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 633130.6001 | 621044.9036 | 738106.28 | 517148.8821 | 0 | 0 | 0 | 0 | 554462.5713
753 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 | 0 | H/A030701125-03 | 1 | 74234.025 | 74352.257 | 118.232 | 1000 | 0 | 118232 | 118193.1869 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 123250.1728 | 149796.7767 | 178278.8721 | 227804.4627 | 240354.077 | 235334.8005 | 246133.1449 | 234255.9876 | 224598.6372
754 | 11 kV Kashipur Feeder (F-7) | E317K | 11 | 0 | H/A030800169-03 | 1 | 43340.071 | 44353.535 | 1013.464 | 1000 | 0 | 1013464 | 1013131.3011 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 988679.7738 | 1066845.3364 | 1250959.2711 | 1588658.98 | 1710138.4368 | 1760370.7558 | 1741847.8978 | 1664580.229 | 1652181.4751
755 | 11 kV Spare Feeder (F-6) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
756 | 11 kV Paikpara Feeder (F-8) | A730D | 11 | 0 | H/A030701098-03 | 1 | 83745.993 | 84409.069 | 663.076 | 1000 | 0 | 663076 | 662858.3261 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 669681.2156 | 698918.7185 | 844950.6763 | 1070234.6333 | 1102912.6399 | 1118443.5796 | 1135381.2606 | 1090515.7468 | 1082731.082
757 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 | 0 | H/A030800205-03 | 1 | 99929.399 | 100789.088 | 859.689 | 1000 | 0 | 859689 | 859406.7822 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 984065.5944 | 876835.1373 | 909298.0281 | 937852.0624 | 845475.6866 | 838157.9765 | 729788.4502 | 786055.2221 | 765048.1281
758 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 | 0 | H/A030701091-03 | 1 | 58318.957 | 58912.033 | 593.076 | 1000 | 0 | 593076 | 592881.3056 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 613730.0246 | 655088.7829 | 771648.9846 | 1009051.2889 | 1042925.7746 | 1035234.9191 | 1075488.4842 | 1015821.5301 | 958950.0681
759 | 11 kV River View | B793U | 11 | 0 | 00000061 | 1 | 973316 | 1554356 | 581040 | 1 | 0 | 581040 | 584945.4383 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 599013.8573 | 704573.4596 | 834579.227 | 838291.0284 | 794103.9859 | 844731.2094 | 841728.9793 | 838140.6773 | 803073.4017
760 | 11 kV Railgate B.B. Road | B793F | 11 | 0 | 00000191 | 1 | 26175216 | 26608216 | 433000 | 1 | 0 | 433000 | 435910.3931 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 431605.906 | 428640.4484 | 541179.2554 | 698256.3766 | 634632.2838 | 651403.112 | 672012.4136 | 662899.4007 | 611819.3181
761 | 11 kV DIT | A722D | 11 | 0 | 00000174 | 1 | 152106944 | 154077504 | 1970560 | 1 | 0 | 1970560 | 1983805.0443 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1892651.3817 | 1979467.7908 | 2494646.9299 | 3067765.2362 | 3157724.5261 | 3006495.8053 | 3105959.8639 | 3165323.9759 | 2992837.0935
762 | 11 kV Dalpatti | B7227 | 11 | 0 | 00000182 | 1 | 7996260 | 8685539 | 689279 | 1 | 0 | 689279 | 693911.9626 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 731072.4862 | 679413.4287 | 717766.0913 | 789288.224 | 719006.8368 | 711194.3901 | 640949.3228 | 661646.5082 | 714092.6513
763 | 11 kV South Chasara | A793S | 11 | 0 | 00000043 | 1 | 107368256 | 108895656 | 1527400 | 1 | 0 | 1527400 | 1537666.3611 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1531701.7545 | 1589435.9823 | 2086962.942 | 2534727.6524 | 2702179.486 | 2680027.0984 | 2791666.2107 | 2659640.365 | 2565218.7341
764 | 11 kV Spare | 0 | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
765 | 11 kV NCC Express | B7225 | 11 | 0 | 00000019 | 1 | 270279 | 284999 | 14720 | 1 | 0 | 14720 | 14818.9399 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 17228.8103 | 15499.819 | 24295.6359 | 23419.6471 | 28768.3897 | 31678.5827 | 33494.5516 | 30069.4219 | 22516.8296
766 | 11 kV Spare | 0 | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
767 | 11 kV Masuya Bazar | B7229 | 11 | 0 | 00000173 | 1 | 12029731 | 13087848 | 1058117 | 1 | 0 | 1058117 | 1065229.0933 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 1166392.4718 | 1190101.2631 | 1131312.8093 | 1152492.2619 | 1058401.5124 | 1053995.629 | 1019425.3124 | 1009868.8027 | 967617.4501
768 | 11 kV Nitaigonj | B722G | 11 | 0 | 00000189 | 1 | 62416688 | 63026568 | 609880 | 1 | 0 | 609880 | 613979.2853 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 690524.2593 | 634240.5147 | 721749.3286 | 797467.0545 | 710089.0378 | 797549.9114 | 692971.3447 | 773236.8002 | 671875.6098
769 | 11 kV Shahid Nagar | E323T | 11 | 0 | 00000020 | 1 | 63774244 | 64601524 | 827280 | 1 | 0 | 827280 | 832840.5311 | Sytalakhya | Mondalpara 33/11KV S/S | 22 | 869546.5268 | 893473.9806 | 1062004.8821 | 1271995.6228 | 1341667.6936 | 1338376.1519 | 1319788.4916 | 1324869.236 | 1256708.9709
770 | 11 kV Bangla Bazar | A793Z | 11 | 0 | 00000139 | 1 | 77532128 | 78510408 | 978280 | 1 | 0 | 978280 | 984855.4719 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 997084.1061 | 1039937.2052 | 1307258.0634 | 1631386.9501 | 1686165.1422 | 1670015.7997 | 1659253.7348 | 1635218.8108 | 1605498.2865
771 | 11 kV Vogoban Gonj | B7228 | 11 | 0 | 00000181 | 1 | 4974668 | 5301627 | 326959 | 1 | 0 | 326959 | 329156.6425 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 369994.7525 | 390112.327 | 454174.5319 | 474606.7675 | 456596.7336 | 480180.888 | 455263.1874 | 451404.0608 | 442440.5963
772 | 11 kV Tanbazar | B722I | 11 | 0 | 00000138 | 1 | 53665148 | 54277388 | 612240 | 1 | 0 | 612240 | 616355.1479 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 620555.9224 | 632030.2808 | 804089.0085 | 976523.0891 | 1000661.8275 | 1022544.4626 | 983939.833 | 990185.2541 | 977004.8332
773 | 11 kV SS Road | A793O | 11 | 0 | 00000175 | 1 | 72509304 | 73412984 | 903680 | 1 | 0 | 903680 | 909754.0508 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 968444.7395 | 977173.0031 | 1192851.3622 | 1337205.7052 | 1396187.0064 | 1386083.0342 | 1389631.5256 | 1367265.5042 | 1304240.0244
774 | 11 kV Spare | 0 | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
775 | 33/0.415 kV Auxiliary-1 | 0 | 0.415 | 0 | 0 | 1 | 2729.32 | 2758.68 | 29.36 | 100 | 0 | 2936 | 2955.7342 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 2771.9421 | 2890.6156 | 3239.0829 | 4162.6017 | 6314.1794 | 3653.8216 | 8763.4945 | 8081.1571 | 8402.5235
776 | 33/0.415 kV Auxiliary-2 | 0 | 0.415 | 0 | 0 | 1 | 4.17 | 4.17 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 0 | 19.1232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
777 | 11 kV Masdair Feeder (F-8) | A727M | 11 | 0 | XA575914 | 1 | 229632.2 | 231707.3 | 2075.1 | 1000 | 0 | 2075100 | 2098989.5568 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2114160.9709 | 2222097.8958 | 2875854.6768 | 3291294.4584 | 3221867.4125 | 3104675.7264 | 3190609.1379 | 3086175.0273 | 3077099.4263
778 | 11 kV Narayangonj (F-7) | A727N | 11 | 0 | XA575915 | 1 | 174073.5 | 175376.8 | 1303.3 | 1000 | 0 | 1303300 | 1318304.2212 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1433628.8234 | 1353525.753 | 1448790.766 | 1519105.835 | 1446695.3457 | 1509012.0982 | 1221622.7778 | 1186514.4598 | 1307443.1804
779 | 11 kV Nearest Feeder (F-6) | A727B | 11 | 0 | XA575927 | 1 | 111780.3 | 112632.8 | 852.5 | 1000 | 0 | 852500 | 862314.3931 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1034978.077 | 974092.1497 | 1208994.3676 | 1130497.3656 | 1036613.3317 | 1067352.4897 | 767732.4068 | 814473.5094 | 997748.2737
780 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 | 0 | XA575916 | 1 | 123435.1 | 124470.2 | 1035.1 | 1000 | 0 | 1035100 | 1047016.5728 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1052639.8189 | 1100138.239 | 1251647.0882 | 1407639.7693 | 1294481.9465 | 1274162.1574 | 1118663.9439 | 1197874.4889 | 1341268.5888
781 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 | 0 | XA575912 | 1 | 60091.3 | 60190.9 | 99.6 | 1000 | 0 | 99600 | 100746.6435 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 424285.5032 | 965722.2908 | 1164739.667 | 905839.439 | 991802.3648 | 906095.6122 | 696086.8403 | 614760.142 | 701320.2188
782 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 | 0 | DHK66615 | 1 | 293.277 | 309.5082 | 16.2313 | 60000 | 0 | 973876.68 | 985088.4203 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 931115.7309 | 923945.7941 | 979158.7412 | 1098396.235 | 953150.2952 | 1090118.5393 | 864699.4622 | 933339.9033 | 1045632.3523
783 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 | 0 | XA575920 | 1 | 237301.7 | 237737.5 | 435.8 | 1000 | 0 | 435800 | 440817.1408 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 27 | 776813.8721 | 1219807.293 | 774957.8804 | 1276885.4045 | 676995.0442 | 906804.2112 | 982770.4437 | 813154.9346 | 1189560.6195
784 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 | 0 | XA575929 | 1 | 27035.8 | 28020.2 | 984.4 | 1000 | 0 | 984400 | 995732.8899 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1047492.6827 | 1054303.2974 | 1209394.8627 | 1314142.277 | 1121815.8354 | 1179007.44 | 1159908.2799 | 1225868.8461 | 1274022.8667
785 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 | 0 | HA021100913-02 | 1 | 50963.735 | 52907.64 | 1943.905 | 1000 | 0 | 1943905 | 1966284.1764 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1986570.5288 | 2343480.778 | 2210541.3216 | 2452393.5389 | 1730245.9891 | 1391497.0345 | 582908.1262 | 649651.6597 | 916096.371
786 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 | 0 | HA021100682-02 | 1 | 73152.506 | 75288.503 | 2135.997 | 1000 | 0 | 2135997 | 2160587.6326 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2078760.7847 | 2064505.4097 | 2336119.5415 | 2520803.045 | 2363695.2567 | 2414952.831 | 1958482.735 | 2197501.257 | 2366722.3025
787 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 | 0 | HA021100455-02 | 1 | 64616.288 | 66130.592 | 1514.304 | 1000 | 0 | 1514304 | 1531737.4015 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1597056.4538 | 1550044.0614 | 1810143.413 | 1837185.1157 | 1324011.9627 | 2155990.2798 | 1459919.7827 | 1675803.0813 | 1827353.8856
788 | 11/0.415 KV Transformer,AT-1 | 0 | 0.415 | Analog | 2001123043161 | 1 | 4158.3 | 4198.6 | 40.3 | 160 | 0 | 6448 | 6522.2325 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 9333.4737 | 8353.9163 | 8426.4154 | 10606.5342 | 9471.9695 | 9523.57 | 9809.4637 | 10077.9686 | 6902.8139
789 | 11/0.415 KV Transformer,AT-2 | 0 | 0.415 | Analog | 2001123043118 | 1 | 4131.2 | 4141.8 | 10.6 | 160 | 0 | 1696 | 1715.5252 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 662.063 | 765.2442 | 2274.8118 | 292.37 | 213.7771 | 583.0757 | 16.214 | 519.3156 | 421.2985
790 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
791 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 | 0 | 041808902749 | 1 | 508.18 | 519.12 | 10.94 | 60000 | 0 | 656400 | 653568.887 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 698675.0469 | 738639.4179 | 945964.8168 | 1302048.296 | 1299547.0336 | 1326519.4669 | 1258154.7044 | 1256317.0074 | 1308593.1901
792 | 11 kV UltraTech Cement Feeder (=F3) | 0 | 11 | 0 | 041808902759 | 1 | 556.24 | 579.04 | 22.8 | 60000 | 0 | 1368000 | 1362099.6914 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1333889.1251 | 1149865.6081 | 1335585.1962 | 1070865.8478 | 1018127.8829 | 1172245.3124 | 1166152.8884 | 1226848.5855 | 1401162.4833
793 | 11 kV RMU Hygene Express -1 (=F4) | 0 | 11 | 0 | 041808902748 | 1 | 16.81 | 27.37 | 10.56 | 60000 | 0 | 633600 | 630867.2255 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 622521.8844 | 391328.1487 | 0 | 0 | 0 | 0 | 0 | 0 | 0
794 | 11 kV Outgoing Feeder-5 (=F5) | 0 | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
795 | 11 kV Outgoing Feeder-6 (=F6) | 0 | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
796 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
798 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 | 0 | 041808902786 | 1 | 415.39 | 432.02 | 16.63 | 60000 | 0 | 997800 | 993496.3977 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1029880.865 | 1112481.409 | 1382793.8004 | 1588331.224 | 1607255.8715 | 1649959.1034 | 1406910.8874 | 1384414.4332 | 1059738.0772
800 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 | 0 | 041808902789 | 1 | 244.79 | 248.97 | 4.18 | 60000 | 0 | 250800 | 249718.2768 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 378348.2521 | 485994.5884 | 878438.5854 | 830100.7076 | 664412.0926 | 761840.3225 | 831600.8302 | 763171.9877 | 845746.7241
801 | 11 kV Outgoing Feeder-12 (=F10) | 0 | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802 | 11 kV Outgoing Feeder-13 (=F11) | 0 | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803 | 11 kV Outgoing Feeder-14 (=F12) | 0 | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804 | 11 kV Outgoing Feeder-15 (=F13) | 0 | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806 | 33/0.415 kV Transformer AT-1 | 0 | 0.415 | 0 | 041811907976 | 1 | 2097.69 | 2143.63 | 45.94 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
807 | 33/0.415 kV Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 73882730 | 74325242 | 442512 | 1 | 0 | 442512 | 443229.6649 | Mugdapara | Amulia 33/11 kv | 102 | 444985.9723 | 422316.016 | 938316.3983 | 618877.1744 | 747742.2401 | 669679.7315 | 704760.429 | 655997.4572 | 731782.37
809 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 20944489 | 21858886 | 914397 | 1 | 0 | 914397 | 915879.9668 | Demra | Amulia 33/11 kv | 102 | 960756.4223 | 935030.696 | 1013109.0793 | 1328671.185 | 1368274.6157 | 1317757.7287 | 1370677.2015 | 1292488.6152 | 1242034.7233
811 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 3860132 | 4231387 | 371255 | 1 | 0 | 371255 | 371857.1004 | Demra | Amulia 33/11 kv | 102 | 423117.4909 | 523833.7888 | 523224.3018 | 581908.8947 | 369688.6181 | 572405.5108 | 546070.575 | 498813.9667 | 550647.0061
812 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 76995070 | 78048613 | 1053543 | 1 | 0 | 1053543 | 1055251.6334 | Demra | Amulia 33/11 kv | 102 | 1731137.401 | 1933868.447 | 2094431.1329 | 2508124.4895 | 2591251.8147 | 2450741.6785 | 2341533.0936 | 2143176.0462 | 2258006.7634
813 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 17610226 | 18107260 | 497034 | 1 | 0 | 497034 | 497840.0885 | Mugdapara | Amulia 33/11 kv | 102 | 496862.708 | 490254.3406 | 575953.3679 | 671288.426 | 654683.7051 | 639938.2711 | 588274.3679 | 552448.5186 | 1045691.8176
814 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra | 0 | 1 | 52653434 | 52789052 | 135618 | 1 | 0 | 135618 | 135837.9449 | Demra | Amulia 33/11 kv | 102 | 163268.6536 | 212143.5494 | 120786.3374 | 168139.8027 | 155971.1495 | 189931.2691 | 165276.4 | 158821.9675 | 145542.9861
815 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 18396671 | 19548850 | 1152179 | 1 | 0 | 1152179 | 1154047.601 | Demra | Amulia 33/11 kv | 102 | 1129687.3519 | 1061473.1622 | 1171776.4455 | 1342546.4505 | 1461872.9578 | 1326521.6668 | 1251754.1184 | 1263380.0786 | 1242709.7581
816 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
818 | 33/0.415 kV Transformer, AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
819 | 11 kV Nearest Feeder | B2110N | 11 | 0 | HA021101060-02 | 1 | 83718205 | 84713406 | 995201 | 1 | 0 | 995201 | 992049.9593 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1025794.0549 | 1080819.1243 | 1313766.3455 | 1615577.819 | 1668539.8072 | 1666551.6834 | 1691601.9901 | 1589546.8433 | 1558145.6337
820 | 11kV Spare | 0 | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
821 | 11 kV City Palli Feeder | B2110C | 11 | 0 | HA021100937-02 | 1 | 81563466 | 82075352 | 511886 | 1 | 0 | 511886 | 510265.2484 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 511602.0618 | 540926.3753 | 688739.9281 | 831311.9243 | 885994.3441 | 907412.698 | 936164.8797 | 876024.4652 | 849393.0553
822 | 11 kV R K Mission Road Feeder | B2110R | 11 | 0 | HA021101035-02 | 1 | 21945140 | 22852524 | 907384 | 1 | 0 | 907384 | 904511.0086 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 935614.7008 | 1007826.239 | 1205722.8029 | 1505793.7255 | 1587170.4652 | 1556832.94 | 1647566.9154 | 1564049.4804 | 1502639.6704
823 | 11 kV Janapath Feeder | B2110J | 11 | 0 | HA021100864-02 | 1 | 38085422 | 39323924 | 1238502 | 1 | 0 | 1238502 | 1234580.611 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1290170.4571 | 1350474.8865 | 1592664.201 | 2018970.5577 | 2145298.3795 | 2127410.4471 | 2194112.6593 | 2093083.5306 | 2005205.5254
824 | 11 kV Dhalpur Feeder | B2110D | 11 | 0 | HA021100851-02 | 1 | 90597737 | 91088256 | 490519 | 1 | 0 | 490519 | 488965.9013 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 486376.4127 | 583989.7432 | 804304.6434 | 844139.0145 | 879803.8192 | 873504.546 | 859344.4269 | 844664.2379 | 860069.6023
825 | 11kV WTP | B2110O | 11 | 0 | X0599387 | 1 | 3614.4 | 4237.1 | 622.7 | 1000 | 0 | 622700 | 620728.3852 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 693300.0424 | 425318.4663 | 252567.7657 | 0 | 285986.2262 | 561982.597 | 0 | 0 | 145877.5724
826 | 11kV Kamalapur Water pumping | B2110F | 11 | 0 | HA021100474-02 | 1 | 7724215 | 7746131 | 21916 | 1 | 0 | 21916 | 21846.6088 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 21434.4004 | 22031.7603 | 24054.7854 | 97542.6949 | 82536.7668 | 73055.4392 | 36822.7275 | 20221.1849 | 24456.8935
827 | 11 kV Wasa Road Feeder | B2110A | 11 | 0 | HA021001011-02 | 1 | 30335894 | 31468609 | 1132715 | 1 | 0 | 1132715 | 1129128.5575 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1149650.5718 | 1179641.5099 | 1724950.0596 | 2072782.2659 | 2063419.1707 | 2142959.5506 | 2098895.465 | 1863737.1947 | 2040994.3579
828 | 11kV Sutikhalpar Feeder | B2110K | 11 | 0 | HA021101047-02 | 1 | 85232802 | 86501631 | 1268829 | 1 | 0 | 1268829 | 1264811.5886 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1275488.8091 | 1397310.6355 | 1698787.5503 | 1889889.713 | 1886554.6703 | 2069904.1114 | 2025250.0101 | 1882771.0147 | 2076315.0532
829 | 11kV Spare | 0 | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
830 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
831 | 11kV Spare | 0 | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
832 | 11kV Spare | 0 | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
834 | AT-1 | 0 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
835 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 | 0 | DHK86058 | 1 | 1785.77 | 1796 | 10.23 | 60000 | 0 | 613800 | 620196.8668 | Motijheel | Motijheel old 33/11 kV | 75 | 596539.0356 | 734202.8494 | 859250.5994 | 1078290.2684 | 1069121.0153 | 1083441.1947 | 1084055.9235 | 997541.2473 | 913140.3988
836 | 11kV Station Road Feeder | A175H | 11 | 0 | DHK86075 | 1 | 2384.56 | 2385.46 | 0.9 | 60000 | 0 | 54000 | 54562.7742 | Motijheel | Motijheel old 33/11 kV | 75 | 52918.7854 | 59073.7925 | 80099.6322 | 97417.5285 | 97902.6548 | 101497.5399 | 109816.6442 | 95033.1244 | 121832.4707
837 | 11kV Box Culvert Road Feeder | A175F | 11 | 0 | DHK86071 | 1 | 3323.76 | 3344.52 | 20.76 | 60000 | 0 | 1245600 | 1258581.3251 | Motijheel | Motijheel old 33/11 kV | 75 | 1222544.2131 | 1420784.9886 | 1714253.4911 | 1945915.1314 | 1920213.4191 | 1954278.0752 | 1833753.908 | 1479451.1554 | 1996966.8828
838 | 11kV Mohamedan Club Feeder | A174V | 11 | 0 | DHK86062 | 1 | 1750.28 | 1758.05 | 7.77 | 60000 | 0 | 466200 | 471058.6173 | Motijheel | Motijheel old 33/11 kV | 75 | 431769.181 | 523225.0191 | 731212.5511 | 895632.4025 | 840281.0677 | 917081.3217 | 976079.7817 | 1139171.2585 | 731597.9549
839 | 11kV Amina Ahmed Co. | 0 | 11 | 0 | DHK95754 | 1 | 127579 | 129815 | 2236 | 60 | 0 | 134160 | 135558.1813 | Motijheel | Motijheel old 33/11 kV | 75 | 132597.6385 | 154616.6099 | 203465.202 | 231731.9459 | 212983.3214 | 238309.0167 | 251289.93 | 373020.341 | 139323.2709
840 | 11kV Bangabhaban -1 | 0 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
841 | 11kV Sonali Bank | A175SB | 11 | 0 | DHK95753 | 1 | 98361 | 104817 | 6456 | 60 | 0 | 387360 | 391396.967 | Motijheel | Motijheel old 33/11 kV | 75 | 295022.2287 | 251003.3387 | 265299.6907 | 525993.7678 | 476719.8595 | 524063.6289 | 553807.1772 | 446839.6196 | 345775.0268
842 | 11kV NCC Bank Feeder | A133S | 11 | 0 | DHK68123 | 1 | 340.63 | 343.14 | 2.51 | 60000 | 0 | 150600 | 152169.5147 | Motijheel | Motijheel old 33/11 kV | 75 | 150938.8084 | 170590.6456 | 211778.5729 | 238064.0852 | 224635.5392 | 249239.521 | 237424.8118 | 404044.0578 | 147163.9744
843 | 11kV IFIC BANK Feeder | 0 | 11 | 0 | DHK68116 | 1 | 436.24 | 441.2 | 4.96 | 60000 | 0 | 297600 | 300701.5112 | Ramna | Motijheel old 33/11 kV | 75 | 288046.5706 | 322494.6834 | 395036.8222 | 459080.103 | 425846.5168 | 457039.218 | 500616.6574 | 354381.5863 | 554880.5594
844 | 11kV Arambagh Feeder | A174X | 11 | 0 | DHK68117 | 1 | 3472.29 | 3485.51 | 13.22 | 60000 | 0 | 793200 | 801466.5278 | Motijheel | Motijheel old 33/11 kV | 75 | 746275.1443 | 878270.5678 | 488486.393 | 1367498.5561 | 1397665.5071 | 1278373.3459 | 1267688.622 | 59250.2714 | 488536.1447
845 | 11kV Nikotborti Feeder | A175K | 11 | 0 | DHK68114 | 1 | 1447.93 | 1450.29 | 2.36 | 60000 | 0 | 141600 | 143075.719 | Motijheel | Motijheel old 33/11 kV | 75 | 129290.2144 | 151904.0378 | 214812.6499 | 275204.518 | 264277.1049 | 302690.8881 | 931907.7237 | 862042.4055 | 655000.3125
846 | 11kV Agrani Bank Feeder | A174O | 11 | 0 | DHK95756 | 1 | 386701 | 388991 | 2290 | 60 | 0 | 137400 | 138831.9477 | Motijheel | Motijheel old 33/11 kV | 75 | 134161.148 | 151301.244 | 192421.1618 | 232340.8054 | 213403.7622 | 236867.6315 | 255891.186 | 369219.0161 | 144691.1372
847 | 11kV Bangladesh Bank-2 | A133D | 11 | 0 | DHK95755 | 1 | 552 | 552 | 0 | 60000 | Estimated | 706255.2 | 713615.6113 | Motijheel | Motijheel old 33/11 kV | 75 | 495490.8554 | 567635.0085 | 892846.9338 | 987430.8879 | 706996.5136 | 913123.8185 | 781881.091 | 669891.5592 | 180939.3128
848 | 11kV PDB Design Feeder 14 | 0 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
849 | 11kV Bangabhaban-2 | 0 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
850 | 11/0.4 kV AT | 0 | 0.415 | 0 | ELIC5429 | 1 | 435945 | 437810 | 1865 | 1 | 0 | 1865 | 1884.4366 | Motijheel | Motijheel old 33/11 kV | 75 | 2306.1766 | 11416.9146 | 0 | 0 | 5453.7184 | 4994.8 | 6386.5434 | 8270.9474 | 3518.2644
851 | 11 kV Central Weman | A1111CW | 11 | 0 | 41812909492 | 1 | 200.24 | 205.61 | 5.37 | 60000 | 0 | 322200 | 324540.8139 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 349687.3512 | 352370.1881 | 559606.8157 | 780631.0755 | 589767.3774 | 585552.4072 | 614594.3851 | 602582.0913 | 559727.7485
852 | 11 kV Spare Feeder 2 | 0 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
853 | 11 kV K. M. Das Len | 0 | 11 | 0 | 41812909499 | 1 | 325.78 | 333.94 | 8.16 | 60000 | 0 | 489600 | 493156.9909 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 513488.2684 | 542295.8874 | 679005.6837 | 845732.5401 | 957285.5746 | 992186.0233 | 1031748.0667 | 1006914.6746 | 933883.7569
854 | 11 kV Gopibag | A1111GP | 11 | 0 | 41812909517 | 1 | 49.57 | 54.64 | 5.07 | 60000 | 0 | 304200 | 306410.0422 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 89569.0408 | 92214.7286 | 109147.45 | 151903.4174 | 162651.6346 | 159641.3456 | 169750.8488 | 161492.0005 | 148216.3898
855 | 11kV SPICE TV | B1111E | 11 | 0 | 41812909518 | 1 | 37.24 | 41.63 | 4.39 | 60000 | 0 | 263400 | 265313.6262 | Narinda | Motijheel 33/11 KV SS (new) | 111 | 241713.7129 | 238170.4911 | 196586.015 | 229907.875 | 224111.6034 | 223497.8838 | 229344.2319 | 216326.9708 | 196416.8418
856 | 11 kV Spare Feeder 6 | 0 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
857 | 11 kV Spare Feeder 7 | 0 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
858 | 11 kV BPT-1 | 0 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
859 | 11 kV BPT-2 | 0 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
860 | 10 kV Spare Feeder 8 | 0 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
861 | 11 kV Spare Feeder 9 | 0 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
862 | 11 kV South Kamlapur | A1111SK | 11 | 0 | 41812909473 | 1 | 424.77 | 430.33 | 5.56 | 60000 | 0 | 333600 | 336023.636 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 328828.8075 | 359698.5109 | 441413.9968 | 616997.6645 | 555002.1425 | 559648.3398 | 571253.7429 | 550760.0315 | 1048359.8303
863 | 11 kV Spare Feeder 11 | 0 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
864 | 11 kV Answer Camp | A1111AC | 11 | 0 | 41812909514 | 1 | 239.5 | 246.18 | 6.68 | 60000 | 0 | 400800 | 403711.8504 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 409195.5496 | 448249.0781 | 582521.7499 | 703799.6173 | 759868.7052 | 750615.5343 | 784345.2339 | 758048.2709 | 729031.836
865 | 11 kV Shapla Chattar | A1111SC | 11 | 0 | 41812909516 | 1 | 232.07 | 240.26 | 8.19 | 60000 | 0 | 491400 | 494970.0681 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 628823.7456 | 717564.9411 | 919009.4688 | 1155990.8714 | 1143527.9043 | 1182550.7976 | 639274.4731 | 598966.5988 | 591058.0422
866 | 11 kV Sayedabad | 0 | 11 | 0 | 41812909497 | 1 | 128.21 | 132.57 | 4.36 | 60000 | 0 | 261600 | 263500.5491 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 322080.4551 | 288858.0572 | 483625.7179 | 303220.3351 | 309783.0751 | 311451.2289 | 306394.2625 | 315753.0159 | 300047.8135
867 | 33/0.4 kV Aux Transformer | 0 | 0.415 | 0 | 41901920686 | 1 | 1564.41 | 1564.41 | 0 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 107.7691 | 0 | 76.8957 | 83.5078 | 86.4785 | 0 | 0 | 0 | 0
868 | Inner Circular Road Feeder | A161Z | 11 | 0 | BD014042 | 1 | 44268 | 44708 | 440 | 1000 | 0 | 440000 | 440281.5947 | Motijheel | P & T 33/11 KV SS | 61 | 440281.5307 | 462807.6401 | 1167930.2881 | 717359.185 | 740621.6003 | 751211.0308 | 786225.5313 | 2044037.2926 | 2028898.6132
869 | NSI New Building Expres Feeder | D361NS | 11 | 0 | BD013982 | 1 | 11504 | 11706 | 202 | 1000 | 0 | 202000 | 202129.2776 | Ramna | P & T 33/11 KV SS | 61 | 186034.4496 | 233957.9461 | 303173.5417 | 408763.2027 | 366793.6012 | 408464.6789 | 417588.6558 | 429529.4901 | 413128.6457
870 | Police Hospital RMU Feeder | D661H | 11 | 0 | BD014044 | 1 | 4203 | 4222 | 19 | 1000 | 0 | 19000 | 19012.1598 | Rajarbag | P & T 33/11 KV SS | 61 | 97151.3237 | 73558.8302 | 119031.2227 | 160874.6268 | 178874.6877 | 184011.3157 | 189813.0254 | 182072.2195 | 167833.5123
871 | Jonaki O/H Feeder | D661J | 11 | 0 | BD014013 | 1 | 39937 | 40796 | 859 | 1000 | 0 | 859000 | 859549.7497 | Rajarbag | P & T 33/11 KV SS | 61 | 871261.3389 | 971589.5492 | 1202520.558 | 1451918.8017 | 1556611.7488 | 1494333.6521 | 1501520.9321 | 1581312.3149 | 1420129.7195
872 | Nayapalton Overhead Feeder | D361N | 11 | 0 | BD014014 | 1 | 28341 | 28851 | 510 | 1000 | 0 | 510000 | 510326.3939 | Ramna | P & T 33/11 KV SS | 61 | 489890.7172 | 568037.6334 | 768107.463 | 920728.9962 | 1002904.148 | 1013073.2878 | 1003011.9866 | 1008941.636 | 976215.0449
873 | Masjid Gali Over Head Feeder | D361MG | 11 | 0 | BD014016 | 1 | 18062 | 18556 | 494 | 1000 | 0 | 494000 | 494316.154 | Ramna | P & T 33/11 KV SS | 61 | 512628.2611 | 586427.3409 | 687735.9536 | 843832.9482 | 902412.7504 | 918034.4764 | 899114.3306 | 924444.0314 | 878891.4697
874 | Spare Feeder (Feeder-8) | 0 | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
875 | Mid Way Over Head Feeder | D361MW | 11 | 0 | BD014015 | 1 | 26552 | 27093 | 541 | 1000 | 0 | 541000 | 541346.2335 | Ramna | P & T 33/11 KV SS | 61 | 539499.9038 | 577232.4871 | 723343.5844 | 925787.9468 | 990845.1803 | 982741.7522 | 1022992.3051 | 1000894.2451 | 972242.6541
876 | Palton Thana Over Head Feeder | D661F | 11 | 0 | BD014033 | 1 | 28700 | 29433 | 733 | 1000 | 0 | 733000 | 733469.1112 | Rajarbag | P & T 33/11 KV SS | 61 | 677992.2163 | 772367.7173 | 1016343.5173 | 1303185.6562 | 1382761.6309 | 1360874.8956 | 1387633.1169 | 1346932.0545 | 1294006.3108
877 | Police Hospital (South) U/G Feeder 7 | 0 | 11 | 0 | BD014034 | 1 | 13024 | 13181 | 157 | 1000 | 0 | 157000 | 157100.4781 | Rajarbag | P & T 33/11 KV SS | 61 | 53743.2854 | 103186.6924 | 130222.1924 | 174027.8982 | 183899.2576 | 186033.4181 | 181820.898 | 172012.9808 | 167833.5123
878 | China Town Express Feeder | D361CT | 11 | 0 | BD013943 | 1 | 7445 | 7603 | 158 | 1000 | 0 | 158000 | 158101.1181 | Ramna | P & T 33/11 KV SS | 61 | 146760.5102 | 174702.2218 | 210593.7018 | 268124.378 | 282380.8272 | 287138.5367 | 264739.2196 | 295741.6161 | 284025.9439
879 | Fakirapul Bazar O/H Feeder | A161FB | 11 | 0 | BD014032 | 1 | 35244 | 36215 | 971 | 1000 | 0 | 971000 | 971621.4283 | Motijheel | P & T 33/11 KV SS | 61 | 948775.6929 | 1032888.5743 | 1155721.9576 | 1453942.382 | 1464159.663 | 1476134.7307 | 1280738.4132 | 1354979.4454 | 1402253.9607
880 | PWD Ouarter (RMU) | A161PW | 11 | 0 | BD013937 | 1 | 2954 | 3061 | 107 | 1000 | 0 | 107000 | 107068.4787 | Motijheel | P & T 33/11 KV SS | 61 | 113687.7192 | 109316.5949 | 124118.0271 | 149744.9357 | 156766.5803 | 149635.5754 | 151850.4203 | 150888.5797 | 145985.3628
881 | Postal Quarter RMU | A161PO | 11 | 0 | BD013945 | 1 | 3593 | 3710 | 117 | 1000 | 0 | 117000 | 117074.8786 | Motijheel | P & T 33/11 KV SS | 61 | 117821.8181 | 125663.0016 | 149552.0491 | 176051.4784 | 181889.4296 | 177945.0086 | 177824.8343 | 174024.8285 | 164854.2192
882 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | DHKH4409 | 1 | 1497 | 1535 | 38 | 100 | 0 | 3800 | 3802.432 | Rajarbag | P & T 33/11 KV SS | 61 | 0 | 0 | 2136.4578 | 0 | 4220.6387 | 5762.9918 | 6093.9971 | 301.7772 | 0
883 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | DHKH4411 | 1 | 684 | 692 | 8 | 100 | 0 | 800 | 800.512 | Rajarbag | P & T 33/11 KV SS | 61 | 4030.7464 | 3882.2716 | 2950.3465 | 5666.0246 | 1406.8796 | 0 | 5394.686 | 0 | 5362.7276
884 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 494.8 | 507.4 | 12.6 | 40000 | 0 | 504000 | 509026.9426 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 489447.7453 | 542948.0376 | 698504.7602 | 873041.3399 | 948762.3589 | 895110.6473 | 1426015.7648 | 1381038.2208 | 1302977.567
885 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 86 | 87.8 | 1.8 | 40000 | 0 | 72000 | 72718.1347 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 84945.4765 | 85728.6375 | 128460.6456 | 186790.2402 | 199525.1313 | 209665.557 | 202559.0575 | 214648.1692 | 201076.785
886 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 362.6 | 373.7 | 11.1 | 40000 | 0 | 444000 | 448428.4971 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 428772.405 | 493960.2448 | 634274.4374 | 775585.5625 | 851035.764 | 818502.0784 | 866952.7661 | 866692.6078 | 735941.0332
887 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 828.8 | 846.8 | 18 | 40000 | 0 | 720000 | 727181.3466 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 691698.8798 | 775640.0538 | 967469.2368 | 1218197.2185 | 1388532.036 | 1274121.462 | 2264610.2629 | 2211281.1394 | 2079133.9572
888 | 11 KV Majar Feeder | 0 | 11 | 0 | 96 | 1 | 89 | 94.3 | 5.3 | 40000 | 0 | 212000 | 214114.5076 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 210341.1798 | 228609.7001 | 285022.0573 | 369519.8229 | 407194.1454 | 391106.9045 | 417271.6585 | 400946.5802 | 382045.8916
889 | 11 kV Feeder-6 | 0 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
890 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 377.6 | 384.2 | 6.6 | 40000 | 0 | 264000 | 266633.1604 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 262926.4748 | 273515.1768 | 353266.7753 | 495400.2022 | 517136.5647 | 483843.5932 | 563114.1799 | 1081340.777 | 1001362.3894
891 | 11 kV Feeder-8 | 0 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
892 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 248.2 | 252.9 | 4.7 | 40000 | 0 | 188000 | 189875.1294 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 177980.9983 | 191868.8554 | 256921.2911 | 345155.8786 | 354258.9065 | 330626.4553 | 352452.7601 | 340197.0984 | 337808.9988
893 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 402.3 | 413.2 | 10.9 | 40000 | 0 | 436000 | 440348.7043 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 448997.5185 | 485795.6126 | 622231.2519 | 1344077.5978 | 2296574.9803 | 2165200.0794 | 449681.1077 | 437396.2693 | 402153.5701
894 | 11 kV Feeder-11 | 0 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
895 | Dhaka Railway | 0 | 11 | Motijheel | 150 | 1 | 81.7 | 85 | 3.3 | 40000 | 0 | 132000 | 133316.5802 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 133485.7487 | 155128.0108 | 112403.0649 | 101516.4349 | 199525.1313 | 209665.557 | 230917.3256 | 222748.1001 | 217162.9278
896 | Jasimuddin Feeder-13 | 0 | 11 | 0 | 91 | 1 | 340.9 | 361.8 | 20.9 | 40000 | 0 | 836000 | 844338.3413 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 784734.4016 | 894027.2198 | 1184246.5762 | 1445594.0326 | 1653208.2305 | 1568459.6478 | 1713649.6265 | 1656435.8718 | 1097879.2463
897 | Police Box Feeder-14 | 0 | 11 | 0 | 18 | 1 | 146.7 | 155.9 | 9.2 | 40000 | 0 | 368000 | 371670.466 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 364052.042 | 400066.9751 | 493770.6063 | 605037.9519 | 655582.5742 | 628996.6711 | 656291.3463 | 664194.3349 | 643445.7121
898 | 11 kV Feeder-15 | 0 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
899 | 11 kV Feeder-16 | 0 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
900 | Auxiliary -1 (AT-1 ) | 0 | 0.415 | 0 | DHKF 7632 | 1 | 1106.01 | 1129.25 | 23.24 | 100 | 0 | 2324 | 2347.1798 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 2617.1297 | 2782.0984 | 3429.2971 | 7083.8168 | 0 | 4701.3469 | 8715.1034 | 2871.4255 | 5128.4634
901 | Auxiliary -1 (AT-2 ) | 0 | 0.415 | 0 | DHKF 7733 | 1 | 156.6 | 156.61 | 0.01 | 100 | 0 | 1 | 1.01 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 1938.9639 | 1823.2118 | 0 | 0 | 0 | 0
902 | 11 kV DIT S/S-1 Feeder | 0 | 11 | Motijheel | 4150750 | 1 | 220648.42 | 221265.34 | 616.92 | 1000 | Estimated | 568927.8 | 573471.5104 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 671817.8752 | 732850.4474 | 734566.8339 | 730932.291 | 825621.5358 | 884099.9496 | 816951.1322 | 793502.3098 | 860468.6016
903 | 11 kV Bangabhaban Switching Circuit-1 | 0 | 11 | Motijheel | 4150743 | 1 | 24395.39 | 24419.88 | 24.49 | 1000 | 0 | 24490 | 24685.588 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 17985.9592 | 28810.0365 | 38328.8826 | 45380.4829 | 61964.371 | 72049.9558 | 82523.1488 | 83389.7606 | 79020.0597
904 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
905 | 11 kV Bangladesh Bank Feeder | 0 | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240728.715
906 | 11 kV P & T Substation | 0 | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
907 | 11 kV Osmani Feeder | 0 | 11 | Ramna | 4150754 | 1 | 33909.49 | 33913.48 | 3.99 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20212.3186
908 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 512035.02 | 516124.3594 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 610743.5229 | 671779.5768 | 675327.5731 | 670021.2667 | 766648.569 | 798145.7878 | 731598.0289 | 710599.0834 | 737544.5157
909 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16152.87 | 16186.18 | 33.31 | 1000 | 0 | 33310 | 33576.0285 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 25547.8952 | 37285.3487 | 63965.3489 | 73704.4745 | 67064.6079 | 76956.258 | 79365.3753 | 70158.8804 | 76837.1293
910 | 11 kV Motijheel-1 Feeder | 0 | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
911 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 252560.28 | 253417.92 | 857.64 | 1000 | 0 | 857640 | 864489.4944 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 644351.2568 | 824173.9049 | 1024190.419 | 1159901.5065 | 1104426.7361 | 1181560.7231 | 1155594.7497 | 1181422.0182 | 1217478.907
912 | 11 kV Bangabhaban Switching Circuit-2 | 0 | 11 | Motijheel | 4150737 | 1 | 15369.61 | 15481.23 | 111.62 | 1000 | 0 | 111620 | 112511.447 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 117285.3253 | 128977.3818 | 140844.5519 | 163473.9003 | 173027.2895 | 175243.8256 | 162199.2891 | 174416.2041 | 171420.6744
913 | 11 kV Motijheel-2 Feeder | 0 | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
914 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 227571.12 | 229388.6042 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 305371.7615 | 232069.3083 | 236957.0432 | 243644.097 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
915 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 165578.1 | 165757.59 | 179.49 | 1000 | 0 | 179490 | 180923.487 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 198307.5023 | 244870.2472 | 307144.3937 | 367060.1011 | 339501.426 | 365711.3213 | 363925.8833 | 326878.2024 | 270087.1078
916 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20826.96 | 20863.36 | 36.4 | 1000 | Estimated | 113785.56 | 114694.3021 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 183223.0569 | 170998.4377 | 177717.7824 | 182733.0727 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
917 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82655.11 | 82655.11 | 0 | 1000 | Estimated | 170678.34 | 172041.4531 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 244297.4092 | 232069.3083 | 236957.0432 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
918 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 124388.29 | 124552.01 | 163.72 | 1000 | 0 | 163720 | 165027.5407 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 147502.9419 | 180321.3053 | 243199.1755 | 300166.2046 | 298839.8125 | 325451.3768 | 302665.0764 | 348419.8864 | 313139.3465
919 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 274234.07 | 274721.65 | 487.58 | 1000 | 0 | 487580 | 491474.0307 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 449187.0294 | 537399.0629 | 60090.1862 | 0 | 0 | 98812.5217 | 790606.2505 | 819439.2218 | 796304.7174
920 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 82533.39 | 82695.01 | 161.62 | 1000 | 0 | 161620 | 162910.7692 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 145072.6783 | 176073.6073 | 235529.3729 | 274686.6308 | 474442.2708 | 529113.3929 | 587426.078 | 481785.1466 | 474463.9677
921 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 193032.75 | 193032.75 | 0 | 1000 | Estimated | 170678.34 | 172041.4531 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 244297.4092 | 232069.3083 | 236957.0432 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
922 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 63412931 | 1 | 94429.4 | 94429.4 | 0 | 1 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 2787.1709 | 1631.7989 | 11191.6714 | 0 | 5939.9222 | 6215.6589 | 3575.8026 | 0 | 0
923 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 63403117 | 1 | 29520.2 | 34458 | 4937.8 | 1 | Estimated | 5000 | 5039.9322 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 5021.2058 | 5020.9196 | 5032.6789 | 5007.7779 | 5010.0559 | 5047.636 | 5012.339 | 5030.7529 | 5053.0797
924 | 11 kV Bonogram Feeder | B124B | 11 | 0 | 06604467 | 1 | 25406.9 | 25482.9 | 76 | 8000 | 0 | 608000 | 614884.5864 | Narinda | Narinda 33/11KV S/S | 24 | 513078.8188 | 656738.9275 | 833343.2066 | 1081937.7982 | 1068648.5129 | 1111412.0708 | 1143423.9412 | 1139801.4532 | 1096395.2732
925 | 11 kV Sha Saheb Len Feeder | B524H | 11 | 0 | 06604469 | 1 | 17141.59 | 17196.38 | 54.79 | 8000 | 0 | 438320 | 443283.2433 | Swamibag | Narinda 33/11KV S/S | 24 | 384423.798 | 450442.0099 | 558526.7169 | 661053.8831 | 660371.6402 | 659718.6519 | 672430.175 | 685656.1379 | 629657.0471
926 | 11 kV Sadiabad Water Treatment | B224W | 11 | 0 | 06604354 | 1 | 543.82 | 543.82 | 0 | 40000 | 0 | 0 | 0 | Maniknagar | Narinda 33/11KV S/S | 24 | 405.5959 | 225789.5397 | 333110.8966 | 795173.7239 | 352381.8247 | 28757.3823 | 552771.4205 | 653217.1868 | 492385.8425
927 | 11 kV Manashi Feeder | B124M | 11 | 0 | 06604353 | 1 | 5664.95 | 5680.64 | 15.69 | 40000 | 0 | 627600 | 634706.5237 | Narinda | Narinda 33/11KV S/S | 24 | 510239.6475 | 670871.0785 | 875224.6252 | 1137753.6547 | 1160429.802 | 1160826.1643 | 1102291.2443 | 1122855.7324 | 1066634.3599
928 | 11 kV Jatrabari Feeder | B524E | 11 | 0 | 06604324 | 1 | 3673.34 | 3702.77 | 29.43 | 40000 |  | 1177200 | 1190529.8275 | Swamibag | Narinda 33/11KV S/S | 24 | 1049276.6041 | 1224380.3279 | 1448062.1743 | 2046581.4052 | 2127657.1553 | 2119945.619 | 2124511.9226 | 2030258.73 | 1913892.8816
929 | 11 kV Wari Feeder | B124W | 11 | 0 | 06604291 | 1 | 8754.52 | 8775.32 | 20.8 | 40000 | 0 | 832000 | 841421.013 | Narinda | Narinda 33/11KV S/S | 24 | 870408.8104 | 970570.1438 | 1184484.1348 | 1567697.5349 | 1678876.6245 | 1616488.912 | 1686359.282 | 1652611.2397 | 1532808.0158
930 | 11 kV Narinda Feeder | B124N | 11 | 0 | 06604348 | 1 | 7483.85 | 7504.19 | 20.34 | 40000 | 0 | 813600 | 822812.6637 | Narinda | Narinda 33/11KV S/S | 24 | 799429.5271 | 874731.4183 | 1135164.3175 | 1444336.4028 | 1555745.5042 | 1546013.0737 | 1594908.1278 | 1590073.4608 | 1585232.3889
931 | 11 kV Distillary Feeder | B524D | 11 | 0 | 06604347 | 1 | 6158.21 | 6176.79 | 18.58 | 40000 | 0 | 743200 | 751615.501 | Swamibag | Narinda 33/11KV S/S | 24 | 707359.2569 | 796354.8335 | 1028035.2064 | 1274866.5196 | 1339455.9704 | 1343496.2969 | 1318115.968 | 1326607.8506 | 1271895.9437
932 | 11 kV Thatari Bazar Feeder | B124T | 11 | 0 | 06604296 | 1 | 5158.07 | 5173.07 | 15 | 40000 | 0 | 600000 | 606793.9997 | Narinda | Narinda 33/11KV S/S | 24 | 510645.2434 | 631885.8342 | 785478.7283 | 1002663.1035 | 1062005.913 | 1059567.7759 | 1097413.8494 | 1083315.7174 | 1015016.5156
933 | 11 kV Swamibagh Feeder | B524C | 11 | 0 | 06604352 | 1 | 7958.04 | 7977.17 | 19.13 | 40000 | 0 | 765200 | 773864.6143 | Swamibag | Narinda 33/11KV S/S | 24 | 753191.5941 | 834933.9815 | 995694.3426 | 1313290.4788 | 1313533.6293 | 1354837.2364 | 1370141.5135 | 1100261.4381 | 886375.1694
934 | 11 kV Tipu Sultan Feeder | B124S | 11 | 0 | 06604322 | 1 | 6516.74 | 6533.9 | 17.16 | 40000 | 0 | 686400 | 694172.3357 | Narinda | Narinda 33/11KV S/S | 24 | 672478.0091 | 728536.7523 | 911203.8361 | 1115103.7419 | 1147873.668 | 1151915.4261 | 1136839.4581 | 1115189.8112 | 1101315.099
935 | 11 kV Spare | 0 | 11 | 0 | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936 | 11 kV Folder Street Feeder | B124F | 11 | 0 | DHK00089 | 1 | 48074.3 | 50229.8 | 2155.5 | 444.44 | 0 | 957990.42 | 968838.0644 | Narinda | Narinda 33/11KV S/S | 24 | 873509.6438 | 969883.6178 | 1264515.1272 | 1585927.4386 | 1742899.9791 | 1675427.0415 | 1798340.7365 | 1748933.3106 | 1624153.5662
937 | 11 kV Bhajohari Feeder | B124V | 11 | 0 | DHK27842 | 1 | 443129 | 448780 | 5651 | 80 | 0 | 452080 | 457199.0523 | Narinda | Narinda 33/11KV S/S | 24 | 433419.7832 | 483010.9327 | 619650.9494 | 785385.7258 | 835023.4135 | 806745.8319 | 813305.5973 | 819688.7194 | 775800.0686
938 | 11 kV Lal mohon shaha Feeder | B124L | 11 | 0 | DHK00086 | 1 | 46086.3 | 47411.7 | 1325.4 | 444.44 | 0 | 589060.776 | 595730.9073 | Narinda | Narinda 33/11KV S/S | 24 | 558545.0408 | 638557.4766 | 845750.0473 | 1056805.6006 | 1090752.6026 | 1096369.8618 | 1097222.2328 | 1092539.7614 | 1048880.237
939 | 11 kV Dupkhola Feeder | B524A | 11 | 0 | 8838024/8838029 | 1 | 39744.7 | 40071.8 | 327.1 | 1000 | 0 | 327100 | 330803.8622 | Swamibag | Narinda 33/11KV S/S | 24 | 357329.9916 | 375842.1206 | 459341.3304 | 602548.3495 | 612719.0865 | 555706.0354 | 579800.3171 | 568589.4506 | 537047.3757
940 | 11/0.4 kV Aux Transformer-1 | 0 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
941 | 11/0.4 kV Aux Transformer-2 | 0 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
942 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 64111.2 | 64292.9 | 181.7 | 2222.22 | 0 | 403777.374 | 408963.7094 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 377524.4019 | 436813.0585 | 559882.2686 | 648124.404 | 633672.3537 | 653524.1946 | 604954.0102 | 476949.7245 | 555416.4351
943 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4753.64 | 4774.93 | 21.29 | 40000 | 0 | 851600 | 862538.4119 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 790375.0918 | 802779.0641 | 1039961.1294 | 1308522.8246 | 1300047.3482 | 1372334.5518 | 1164609.944 | 1430849.1736 | 1481110.4937
944 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
945 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5212.68 | 5222.65 | 9.97 | 40000 | 0 | 398800 | 403922.4033 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 358783.3707 | 452343.6473 | 454027.8867 | 509541.8516 | 496023.0204 | 523045.3096 | 442936.2442 | 536568.4401 | 493703.4979
946 | 11kV Spare | 0 | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
947 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5586.22 | 5605.76 | 19.54 | 40000 | 0 | 781600 | 791639.2939 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 664173.9512 | 712149.2149 | 978432.1066 | 1158159.6042 | 1128130.2786 | 1172692.7423 | 878663.7611 | 1216221.7976 | 1419397.5564
948 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.96 | 1020.13 | 6.17 | 40000 | 255057 | 246800 | 249970.0329 | Bangshal | Kumertuly 33/11KV S/S | 19 | 10516.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 40077.0255 | 0
949 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4230.07 | 4248.01 | 17.94 | 40000 | 0 | 717600 | 726817.2432 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 744667.6274 | 698051.2384 | 980442.859 | 1163400.1454 | 1221939.8271 | 1252630.6213 | 1111745.9438 | 834662.018 | 740555.2468
950 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 739606.14 | 749106.042 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 688791.1664 | 685910.7699 | 887565.2014 | 1078713.9994 | 1184790.4407 | 1110503.0608 | 1217802.7423 | 1144679.3389 | 925694.0585
951 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 6038.9 | 6057.45 | 18.55 | 40000 | 0 | 742000 | 751530.6501 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 663364.9696 | 677911.2719 | 893980.5068 | 1075923.4193 | 1095518.3755 | 1129680.4826 | 931127.2764 | 1021492.1651 | 1019206.2302
952 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8428.9 | 8456.57 | 27.67 | 40000 | 0 | 1106800 | 1121016.3389 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1098192.6173 | 1126629.7252 | 1559941.6941 | 1898688.3869 | 2041666.1823 | 1567512.8248 | 2037666.9172 | 1989498.8221 | 1947085.7372
953 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3809.84 | 3814.8 | 4.96 | 40000 | 0 | 198400 | 200948.3571 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 188088.2383 | 224359.2266 | 333784.8946 | 430127.4966 | 443280.3129 | 472729.0813 | 450545.4563 | 410865.9482 | 427409.0643
954 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7366.02 | 7385.57 | 19.55 | 40000 | 0 | 782000 | 792044.4317 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 802914.3077 | 792306.2815 | 995322.4266 | 1252086.2271 | 586209.0241 | 1209618.3616 | 1050071.2769 | 1251993.0269 | 1073805.1079
955 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3622.49 | 3627.41 | 4.92 | 40000 | 0 | 196800 | 199327.8058 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 195773.5642 | 192940.8789 | 238073.0814 | 277345.5648 | 287870.5029 | 292158.7455 | 264720.4859 | 275126.2119 | 281286.3072
956 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
957 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 05378636 | 1 | 180125 | 181249.2 | 1124.2 | 2 | 0 | 2248.4 | 2277.2797 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 2284.5642 | 1643.6227 | 3093.9447 | 5594.0762 | 5930.3337 | 4006.0239 | 7168.6788 | 4775.6076 | 4915.4072
958 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 42162552 | 42601022 | 438470 | 1 | 0 | 438470 | 435555.0089 | Bangshal | Banshal 33/11KV S/S | 78 | 420582.2469 | 490118.7926 | 617669.4796 | 748100.1808 | 769760.338 | 773303.2759 | 760951.1172 | 778854.3109 | 716311.3918
959 | 11 kV Spare Feeder | 0 | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
960 | 11 kV Siddikbazar Feeder | 0 | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
961 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 56411721 | 57130789 | 719068 | 1 | 0 | 719068 | 714287.5661 | Banglabazar | Banshal 33/11KV S/S | 78 | 683565.1793 | 789122.5172 | 1083356.0922 | 1317991.7768 | 1424094.0148 | 1411190.2742 | 1426877.2604 | 1429747.5487 | 1353751.6158
962 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 24405397 | 24842589 | 437192 | 1 | 0 | 437192 | 434285.5051 | Bangshal | Banshal 33/11KV S/S | 78 | 548862.4638 | 425676.2037 | 568959.3967 | 737371.3191 | 742977.1081 | 744097.7084 | 751903.1259 | 737930.5287 | 715455.6721
963 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 54134428 | 55139107 | 1004679 | 1 | 0 | 1004679 | 997999.7965 | Bangshal | Banshal 33/11KV S/S | 78 | 824147.9865 | 962108.9306 | 1228122.7989 | 1543005.6588 | 1634853.1578 | 1636226.6255 | 1167271.1296 | 1660584.0104 | 1409457.3709
964 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 67942920 | 68550161 | 607241 | 1 | 0 | 607241 | 603204.0029 | Bangshal | Banshal 33/11KV S/S | 78 | 582791.0148 | 667367.8163 | 917105.0905 | 1128071.6101 | 1204002.0348 | 1205928.3277 | 1183358.8995 | 1169829.7548 | 1127796.6211
965 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 33735643 | 34106584 | 370941 | 1 | 0 | 370941 | 368474.9482 | Bangshal | Banshal 33/11KV S/S | 78 | 314720.5073 | 371961.4855 | 442857.7972 | 505257.2343 | 581501.911 | 1106821.025 | 1430551.6276 | 1633419.2244 | 1486833.0286
966 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 70381721 | 71284889 | 903168 | 1 | 0 | 903168 | 897163.6515 | Bangshal | Banshal 33/11KV S/S | 78 | 788002.5988 | 955577.3495 | 1230776.8001 | 1482806.5471 | 1592214.2158 | 1582391.9071 | 1508639.2033 | 1596892.4609 | 1498407.2378
967 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 56327460 | 56981121 | 653661 | 1 | 0 | 653661 | 649315.3982 | Narinda | Banshal 33/11KV S/S | 78 | 596681.6516 | 712637.7025 | 982637.1962 | 1224359.1662 | 1261180.3015 | 1301441.3762 | 1139549.3681 | 1267199.3373 | 1145519.8164
968 | AT-1 | 0 | 0.415 | 0 | DHK-4415 | 1 | 823.77 | 823.77 | 0 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 2433.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969 | AT-2 | 0 | 0.415 | 0 | DHK-4410 | 1 | 791.91 | 814.48 | 22.57 | 100 | 0 | 2257 | 2241.9952 | Bangshal | Banshal 33/11KV S/S | 78 | 498.2107 | 7034.0104 | 7007.9248 | 7005.1331 | 7007.3859 | 7008.295 | 7021.7228 | 7023.9917 | 6997.7081
970 | 11 kV Nayanagor Feeder | A418N | 11 | 0 | DHK-61125 | 1 | 978699.2 | 994230.3 | 15531.1 | 60 | 0 | 931866 | 938973.2616 | Kazla | Kazla 33/11KV S/S | 18 | 919761.8478 | 1049288.1996 | 1425042.8921 | 1775388.4538 | 1866468.623 | 1836553.7788 | 1866699.9643 | 1792344.292 | 1710856.4639
971 | 11 kV Madrasa Bazar Feeder | A418B | 11 | 0 | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1024070.04 | 1031880.5339 | Kazla | Kazla 33/11KV S/S | 18 | 981079.3043 | 1037244.2656 | 1548060.2038 | 1602675.9202 | 1563148.5482 | 1846586.4161 | 1853855.1196 | 1913492.0332 | 1855425.2355
972 | 11 kV Kazla Feeder | A418K | 11 | 0 | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 910284.48 | 917227.1412 | Kazla | Kazla 33/11KV S/S | 18 | 858444.3912 | 1952459.794 | 2381631.0828 | 2712220.788 | 2825691.6063 | 2954538.2657 | 3027963.362 | 3049627.928 | 2968680.3768
973 | 11 kV Sayedabad Feeder | B218S | 11 | 0 | HA021101239-02 | 1 | 36964704 | 36964704 | 0 | 1000 | Estimated | 796498.92 | 802573.7486 | Maniknagar | Kazla 33/11KV S/S | 18 | 797126.9347 | 915215.5285 | 952652.4331 | 1232827.6309 | 1202421.9601 | 1231057.6107 | 988722.7304 | 1076339.2687 | 556627.5706
974 | 11 kV Zenith Feeder | A418Z | 11 | 0 | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
975 | 11 kV Paterbagh Feeder | B318P | 11 | 0 | HA-021200060 | 1 | 124359.6 | 125421.6 | 1062 | 1000 | 0 | 1062000 | 1070099.7824 | Jurain | Kazla 33/11KV S/S | 18 | 981079.3043 | 1227482.3138 | 1890790.3944 | 2010101.6778 | 2308939.6211 | 2025231.2443 | 2541656.3466 | 2207984.2138 | 2092993.2394
976 | 11 kV Matuail Feeder | A418M | 11 | 0 | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1365426.72 | 1375840.7118 | Kazla | Kazla 33/11KV S/S | 18 | 1471618.9564 | 1220287.3713 | 1488519.4268 | 1849241.4463 | 1803632.9402 | 1969692.1771 | 1730264.7783 | 1734102.1551 | 1855425.2355
977 | 11 kV Kutubkhali Feeder | B326C | 11 | 0 | DHK-61117 | 1 | 925127.6 | 950243.5 | 25115.9 | 60 | 0 | 1506954 | 1518447.4082 | Jurain | Kazla 33/11KV S/S | 18 | 1530760.1301 | 1591720.008 | 2111396.7703 | 2432494.6655 | 2317847.2676 | 2260753.1891 | 2379719.4891 | 2279252.9698 | 2232712.5636
978 | 11 kV Mridhabari Feeder | A418R | 11 | 0 | DHK-61118 | 1 | 765154.9 | 786583.2 | 21428.3 | 60 | 0 | 1285698 | 1295503.9078 | Kazla | Kazla 33/11KV S/S | 18 | 1283193.2141 | 1265214.7288 | 1394116.481 | 1532023.4409 | 1493309.739 | 1567790.1074 | 1353302.4526 | 1381440.9902 | 1371332.0993
979 | 11 kV Muslim Nagar Feeder | A418U | 11 | 0 | DHK-61011 | 1 | 257414.9 | 288975.2 | 31560.3 | 60 | 0 | 1893618 | 1908060.4612 | Kazla | Kazla 33/11KV S/S | 18 | 1919968.4246 | 2006435.467 | 2307735.4737 | 2627245.0572 | 2655800.5175 | 2583205.2246 | 2385633.1534 | 2345596.1288 | 2459477.0573
980 | 11 kV Jatrabari Thana Feeder | A418H | 11 | 0 | DHK-61010 | 1 | 121954 | 140076.8 | 18122.8 | 60 | 0 | 1087368 | 1095661.262 | Kazla | Kazla 33/11KV S/S | 18 | 1033841.7159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
981 | 11 kV Mirhazirbag Feeder | B518D | 11 | 0 | DHK-61008 | 1 | 413011.9 | 432336.8 | 19324.9 | 60 | 0 | 1159494 | 1168337.3608 | Swamibag | Kazla 33/11KV S/S | 18 | 1095285.787 | 1190813.3489 | 1593271.6426 | 1997346.9786 | 2119778.8003 | 2106094.7503 | 2092254.4374 | 2069592.0061 | 1962979.7252
982 | 11 kV Mukti Sharani Feeder | B318T | 11 | 0 | DHK-61014 | 1 | 255768.2 | 277319.8 | 21551.6 | 60 | 0 | 1293096 | 1302958.3317 | Jurain | Kazla 33/11KV S/S | 18 | 1234586.0356 | 1332723.748 | 182.0986 | 1171257.2192 | 2474942.6039 | 2420269.7538 | 2465205.4697 | 2452063.3964 | 2370251.5382
983 | 11 kV Kadamtali Feeder | B418K | 11 | 0 | DHK-61006 | 1 | 534192.9 | 557719.4 | 23526.5 | 60 | 0 | 1411590 | 1422356.0752 | Shyampur | Kazla 33/11KV S/S | 18 | 1299375.4421 | 1651530.0494 | 2019121.3431 | 2235311.7183 | 2567504.4926 | 2822437.563 | 2221373.5062 | 2471771.8805 | 3092469.9692
984 | 11kV Rayerbagh Feeder | E218R | 11 | 0 | DHK-61012 | 1 | 500356.9 | 504174.2 | 3817.3 | 60 | 0 | 229038 | 230784.8531 | Matuail | Kazla 33/11KV S/S | 18 | 763293.0113 | 883317.7427 | 1505014.5244 | 1463413.2136 | 898785.6229 | 322767.8137 | 1280357.0984 | 1277473.0974 | 837095.6004
985 | 11 kV Donia Feeder | B318D | 11 | 0 | DHK-61013 | 1 | 2100163 | 2100163 | 0 | 60 | 0 | 0 | 0 | Jurain | Kazla 33/11KV S/S | 18 | 0 | 0 | 932769.6947 | 2275838.0926 | 2097995.927 | 2006588.1861 | 2090084.0617 | 2017361.1702 | 1952856.964
986 | 11 kV Nimtoli Feeder | A418T | 11 | 0 | HA-021100855-02 | 1 | 37786069 | 38891345 | 1105276 | 1 | 0 | 1105276 | 1113705.8447 | Kazla | Kazla 33/11KV S/S | 18 | 1180097.802 | 1194453.1575 | 1438258.1917 | 1595582.0613 | 1529815.767 | 1526570.9331 | 1509829.6282 | 1633862.5979 | 1591423.3402
987 | 11 kV Gobindapur Feeder | A441G | 11 | 0 | HA-021101057-02 | 1 | 31752696 | 33259887 | 1507191 | 1 | 0 | 1507191 | 1518686.2158 | Kazla | Kazla 33/11KV S/S | 18 | 1374337.9751 | 1094031.3596 | 557604.1027 | 679496.8713 | 715534.2901 | 710807.5855 | 721136.817 | 697773.6086 | 686441.9856
988 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 | 0 | 9A56136 | 1 | 4203 | 4323.9 | 120.9 | 10000 | 0 | 1209000 | 1218220.9387 | Kazla | Kazla 33/11KV S/S | 18 | 1179639.0535 | 1371449.3853 | 1500290.0775 | 1773738.3704 | 1822390.0739 | 1778276.5099 | 1887901.7718 | 1946667.4736 | 1703398.1226
989 | 11 kV Samad Nagar Gate (Old) | A418A | 11 | 0 | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
990 | 11 kV Dharmik Para | A418D | 11 | 0 | 8K55676 | 1 | 1252.4 | 1475.1 | 222.7 | 4000 | 0 | 890800 | 897594.0548 | Kazla | Kazla 33/11KV S/S | 18 | 939274.9933 | 798189.5618 | 25898.4666 | 0 | 0 | 0 | 0 | 23977.7413 | 1140208.9403
991 | 11 kV Sheikhdi Feeder | A418I | 11 | 0 | 9A56133 | 2 | 17993.4 | 18085 | 91.6 | 4000 | 0 | 732800 | 738389.0024 | Kazla | Kazla 33/11KV S/S | 18 | 942098.0612 | 1360012.28 | 2650141.5287 | 3268543.7125 | 3436798.8591 | 3359798.9198 | 3415699.9979 | 3248780.7482 | 3103743.9224
992 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | T-5 Sum | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
993 | 11 kV Jenith Feeder | A418Z | 11 | 0 | 61903661 | 1 | 23269.7 | 23269.7 | 0 | 2000 | 2126000 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 188210.6106 | 1045852.9212 | 1210196.351 | 1200080.6383 | 617589.258 | 551840.3941 | 574043.3834 | 0
994 | 11 KV Samad Nagor Gate | A418A | 11 | 0 | 61903675 | 1 | 21504.2 | 22164 | 659.8 | 2000 | 0 | 1319600 | 1329664.4754 | Kazla | Kazla 33/11KV S/S | 18 | 1206256.5501 | 1217550.0907 | 1246768.3692 | 1325742.7363 | 1296103.4337 | 1368574.557 | 1134163.594 | 1293375.6231 | 1288887.6302
995 | 11 KV Bibir Bagicha | B218I | 11 | 0 | 61903557 | 1 | 39760.2 | 40163.4 | 403.2 | 2000 | 0 | 806400 | 812550.3433 | Maniknagar | Kazla 33/11KV S/S | 18 | 773722.2305 | 860993.3156 | 974025.1427 | 1414936.4372 | 1478955.3526 | 1458247.4647 | 1460126.3972 | 1445370.1189 | 1356006.601
996 | 33/0.4 kV AT-1 | 0 | 0.415 | 0 | 503043 | 1 | 96242 | 96242 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 351.1392 | 30.3498 | 0 | 0 | 0 | 0 | 0 | 244.069
997 | 33/0.4 kV AT-2 | 0 | 0.415 | 0 | 503044 | 1 | 96796 | 96796 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 2691.9968 | 1936.2819 | 3500.3396 | 6121.9313 | 14219.5459 | 6072.6574 | 6096.5612 | 6096.0359 | 6101.7246
998 | Auxiliary Transformer | 0 | 0.415 | 0 | 41901920685 | 1 | 2995.78 | 3058.9 | 63.12 | 160 | 0 | 10099.2 | 10176.2257 | Kazla | Kazla 33/11KV S/S | 18 | 7859.4208 | 11698.7542 | 17193.3445 | 19919.386 | 20587.2873 | 0 | 0 | 0 | 0
999 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur | 0 | 1 | 885.4112 | 928.523 | 43.1118 | 40000 | 0 | 1724472 | 1731294.1357 | Shyampur | Shyampur 33/11KV S/S | 26 | 1773018.0469 | 1664915.738 | 1892333.6894 | 1814264.1154 | 1610415.5328 | 1658511.8396 | 1848660.4463 | 1329002.2614 | 1796570.0888
1000 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1001 | 11 kV Road No.-21 Feeder | B426E | 11 | 0 | BD001943 | 1 | 1132.88 | 1147.74 | 14.86 | 40000 | 0 | 594400 | 596751.4893 | Shyampur | Shyampur 33/11KV S/S | 26 | 639466.1203 | 656725.5732 | 622979.2968 | 558390.1777 | 490213.532 | 606607.4764 | 536986.5578 | 689153.8135 | 726162.1684
1002 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1648.4 | 1671.48 | 23.08 | 40000 | 0 | 923200 | 926852.2458 | Shyampur | Shyampur 33/11KV S/S | 26 | 915003.4686 | 764854.3548 | 906406.8147 | 891408.4354 | 575920.7998 | 812129.1164 | 684264.5087 | 768373.9842 | 842780.9272
1003 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1521.28 | 1534.69 | 13.41 | 40000 | 0 | 536400 | 538522.0371 | Shyampur | Shyampur 33/11KV S/S | 26 | 638253.078 | 574241.437 | 703156.8125 | 766828.9661 | 770964.9094 | 745215.0941 | 653846.0494 | 678120.977 | 664045.6474
1004 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1442.71 | 1458.11 | 15.4 | 40000 | 0 | 616000 | 618436.9405 | Fatullah | Shyampur 33/11KV S/S | 26 | 607324.5147 | 653530.0037 | 820616.8729 | 1034936.8854 | 1058124.3068 | 991363.1049 | 1100803.9423 | 1060453.8119 | 1011898.1651
1005 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3653.66 | 3713.44 | 59.78 | 40000 | 0 | 2391200 | 2400659.7598 | Shyampur | Shyampur 33/11KV S/S | 26 | 2343340.7532 | 2640549.5368 | 2858328.4338 | 2421034.6696 | 2293670.6681 | 2291008.6698 | 1731865.3068 | 2347543.3088 | 2415731.5404
1006 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1007 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2391.92 | 2437.96 | 46.04 | 40000 | 0 | 1841600 | 1848885.5025 | Shyampur | Shyampur 33/11KV S/S | 26 | 1893470.7423 | 1765972.6202 | 1793971.9132 | 1756207.6637 | 1462630.5709 | 1686790.98 | 1265223.6985 | 1510257.147 | 1400226.6095
1008 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 508.47 | 511.61 | 3.14 | 40000 | 0 | 125600 | 126096.8827 | Fatullah | Shyampur 33/11KV S/S | 26 | 151831.1287 | 148165.5033 | 166368.345 | 155220.3743 | 135769.9243 | 127455.2807 | 91577.1387 | 112254.6055 | 96981.9232
1009 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3421.82 | 3471.12 | 49.3 | 40000 | 0 | 1972000 | 1979801.3743 | Shyampur | Shyampur 33/11KV S/S | 26 | 2074623.7556 | 2027064.2638 | 1986798.8384 | 1913040.7173 | 1822681.1962 | 2162756.7937 | 1853587.4081 | 1927999.1795 | 1824622.7112
1010 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2156.92 | 2186.86 | 29.94 | 40000 | 0 | 1197600 | 1202337.792 | Shyampur | Shyampur 33/11KV S/S | 26 | 1261644.3788 | 1362321.7356 | 1609964.5147 | 1509467.744 | 1396147.3632 | 1389660.8569 | 915888.0248 | 1677475.7016 | 1601003.2355
1011 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1664.56 | 1706.02 | 41.46 | 40000 | 0 | 1658400 | 1664960.7501 | Shyampur | Shyampur 33/11KV S/S | 26 | 2201953.0355 | 1948576.5918 | 1516958.5966 | 546698.2534 | 888712.2774 | 1726620.7552 | 1517234.7817 | 1359049.2203 | 1887540.7358
1012 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1013 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 942.91 | 967.25 | 24.34 | 40000 | 0 | 973600 | 977451.6319 | Shyampur | Shyampur 33/11KV S/S | 26 | 1044742.7664 | 1005923.6331 | 1095224.8641 | 747879.9854 | 273141.8536 | 751986.1559 | 501987.0295 | 565017.3838 | 552636.6613
1014 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1410.22 | 1420.84 | 10.62 | 40000 | 0 | 424800 | 426480.5395 | Shyampur | Shyampur 33/11KV S/S | 26 | 499275.3782 | 505364.5004 | 596520.7166 | 735784.8913 | 764156.3881 | 763138.4929 | 788989.597 | 774228.7961 | 1030332.7456
1015 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3356.67 | 3403.54 | 46.87 | 40000 | 0 | 1874800 | 1882216.8441 | Shyampur | Shyampur 33/11KV S/S | 26 | 1814341.8208 | 2016252.1865 | 2248177.5395 | 2749214.8896 | 3128315.2765 | 2945013.5787 | 2827927.2998 | 2567335.031 | 2104748.1835
1016 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1017 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1141.41 | 1149.59 | 8.18 | 40000 | 0 | 327200 | 328494.4268 | Shyampur | Shyampur 33/11KV S/S | 26 | 260281.9349 | 254284.0394 | 285431.9558 | 272542.7871 | 255119.2973 | 227029.7187 | 174848.8273 | 295251.5179 | 251271.3464
1018 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2145.18 | 2170.65 | 25.47 | 40000 | 0 | 1018800 | 1022830.4463 | Shyampur | Shyampur 33/11KV S/S | 26 | 1107804.9019 | 1173711.0544 | 1318519.2453 | 1539705.4793 | 1292017.0377 | 1541412.3005 | 1200352.7042 | 1365805.0805 | 1428279.2319
1019 | 11 kV Spare Feeder | spare | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1020 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1471.2 | 1486.17 | 14.97 | 40000 | 0 | 598800 | 601168.896 | Shyampur | Shyampur 33/11KV S/S | 26 | 827921.4879 | 615647.6885 | 947858.5903 | 859154.8511 | 801803.5058 | 808146.1389 | 598969.7492 | 543740.6288 | 732574.1964
1021 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1470.28 | 1494.86 | 24.58 | 40000 | 0 | 983200 | 987089.6102 | Shyampur | Shyampur 33/11KV S/S | 26 | 1109813.2501 | 1116046.6423 | 1219099.1258 | 1035743.225 | 446558.8956 | 946355.4589 | 931203.8377 | 1080348.9594 | 971021.4868
1022 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1023 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1024 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1025 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2424.49 | 2446.259 | 21.769 | 40000 | 0 | 870760 | 874204.7894 | Shyampur | Shyampur 33/11KV S/S | 26 | 816192.7341 | 888993.0197 | 1226715.9898 | 1501001.1782 | 1526310.2699 | 1579250.5869 | 1494594.8892 | 1526560.1151 | 1250345.4555
1026 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 179.09 | 179.796 | 0.706 | 40000 | 0 | 28240 | 28351.7195 | Shyampur | Shyampur 33/11KV S/S | 26 | 3615.0269 | 38042.4941 | 89397.93 | 41123.3199 | 3604.5113 | 82447.6347 | 75834.9927 | 95891.5675 | 84558.6189
1027 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1028 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1318.14 | 1335.45 | 17.31 | 40000 | 0 | 692400 | 695139.1844 | Shyampur | Shyampur 33/11KV S/S | 26 | 792895.8942 | 821717.8722 | 867119.832 | 867218.2472 | 889112.7786 | 908118.8747 | 695610.598 | 869607.7672 | 875642.5706
1029 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3961.57 | 4010.77 | 49.2 | 40000 | 0 | 1968000 | 1975785.55 | Shyampur | Shyampur 33/11KV S/S | 26 | 2056548.6213 | 2030680.303 | 1872132.9644 | 1624774.3078 | 1797850.1185 | 1620673.5531 | 2160897.1026 | 1905144.5888 | 2092324.8793
1030 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1138.63 | 1143.96 | 5.33 | 40000 | 0 | 213200 | 214043.4346 | Shyampur | Shyampur 33/11KV S/S | 26 | 163077.879 | 68076.042 | 184408.2861 | 343903.8423 | 438548.8705 | 532125.7967 | 778413.3204 | 463585.7706 | 590307.3256
1031 | 11/0.4 kV Aux Transformer, T-1 | 0 | 0.415 | DPDC | DHK20964 | 1 | 514432.1 | 530255 | 15822.9 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1032 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0.415 | DPDC | DHK26108 | 1 | 65952.1 | 65952.1 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1033 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0.415 | 0 | 0 | 1 | 640912 | 646898 | 5986 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | 11/0.4 kV Aux Transformer, T-2 | 0 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1035 | 11 kV Nama shyampur Feeder | 0 | 11 | Shympur | HA-021101066-02 | 1 | 49050602 | 50526250 | 1475648 | 1 | 0 | 1475648 | 1472388.9525 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1369470.1894 | 1460934 | 1775047.104 | 2124178.3588 | 2141060 | 2242087.5527 | 2142439.5507 | 2098065.1104 | 2051822.5774
1036 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 25352647 | 25888911 | 536264 | 1 | 0 | 536264 | 535079.6323 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 513962.2186 | 561547 | 664547.744 | 735518.3371 | 786111 | 782826.8086 | 745206.3758 | 738065.3088 | 731764.9753
1037 | 11 kV H. R Steel | 0 | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1038 | 11 kV Shyampur Incoming (F1) | 0 | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1039 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 611106.2 | 639043.5 | 27937.3 | 60 | 0 | 1676238 | 1672535.9388 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1425925.7015 | 1692360 | 1847173.44 | 1772799.78 | 1740318 | 1920297.8361 | 1596859.747 | 1920766.0882 | 1940683.7189
1040 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 728502.7 | 746070.8 | 17568.1 | 60 | 0 | 1054086 | 1051757.9947 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 992641.7614 | 1143720 | 1448800.128 | 1537289.4923 | 1379322 | 1531676.01 | 1098969.809 | 1475476.6819 | 1381608.0185
1041 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 742996.5 | 760500 | 17503.5 | 60 | 0 | 1050210 | 1047890.5551 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 987729.1626 | 1118946 | 1325819.904 | 1436086.1084 | 1338426 | 1403188.8641 | 1231235.1282 | 1429313.0963 | 1378277.4296
1042 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 463549.2 | 484253.6 | 20704.4 | 60 | 0 | 1242264 | 1239520.3935 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1417396.8001 | 1130622 | 1052218.368 | 1093174.4833 | 818646 | 1160551.0823 | 887582.2839 | 954363.7317 | 1019394.7492
1043 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 599333.5 | 622666.5 | 23333 | 60 | 0 | 1399980 | 1396888.0693 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1760485.185 | 1789686 | 1124308.992 | 208419.6185 | 288 | 3130.962 | 385792.207 | 8184.8678 | 8596.203
1044 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 119817.6 | 156765.8 | 36948.2 | 60 | 0 | 2216892 | 2211995.8755 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2082378.5231 | 2053986 | 2314357.824 | 2668033.8435 | 2872542 | 2819649.0049 | 2794077.3284 | 2700808.4363 | 2561826.8196
1045 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 391926.2 | 412196.4 | 20270.2 | 60 | 0 | 1216212 | 1213525.9308 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1247860.6551 | 1258110 | 1329111.36 | 1432539.3027 | 1270602 | 1528603.9007 | 1237892.1591 | 1229098.1908 | 1284557.7074
1046 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 556070.7 | 573450.5 | 17379.8 | 60 | 0 | 1042788 | 1040484.9469 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1184378.4913 | 1100478 | 1158657.984 | 1382304.8305 | 530982 | 646002.2013 | 711159.0569 | 480060.5409 | 1215195.8482
1047 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 748024.9 | 775050 | 27025.1 | 60 | 0 | 1621506 | 1617924.8173 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1536098.7544 | 1671180 | 2088491.328 | 2541202.6985 | 2715606 | 2647616.7695 | 2636452.1751 | 2526376.4464 | 2465450.8355
1048 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 932193.5 | 943773.6 | 11580.1 | 60 | 0 | 694806 | 693271.4838 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 752548.3412 | 749442 | 766200.96 | 752054.1743 | 714972 | 785812.6007 | 661368.2767 | 689554.7346 | 725640.3272
1049 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 132355.9 | 161715.8 | 29359.9 | 60 | 0 | 1761594 | 1757703.4255 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1853891.1932 | 1901862 | 1859476.224 | 1837006.5171 | 1401510 | 1411640.1073 | 1301431.6729 | 1235612.3209 | 1199610.0995
1050 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 43170.716 | 3507 | 3715.5651 | 3553.7906 | 3904.2091 | 3633.5474
1051 | 11 kV Spare | spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1052 | 11 kV Khaza Moinuddin | B889Z | 11 | 0 | 00000026 | 1 | 8820818 | 9206898 | 386080 | 1 | 0 | 386080 | 389654.3551 | Fatullah | Nandalalpur 33/11 kV | 89 | 402828.4716 | 422037.4564 | 579356.8008 | 656635.1076 | 680847.6789 | 682477.6462 | 727695.4191 | 676115.2751 | 672821.6526
1053 | 11 kV Chitashal | B489Q | 11 | 0 | 00000027 | 1 | 37064908 | 37511028 | 446120 | 1 | 0 | 446120 | 450250.2095 | Shyampur | Nandalalpur 33/11 kV | 89 | 499792.4948 | 488676.1143 | 626907.0404 | 735704.304 | 743621.9237 | 740092.1663 | 801503.5058 | 725908.576 | 676035.0889
1054 | 11 kV Local Feeder | B489G | 11 | 0 | 00000157 | 1.5 | 19432112 | 19560472 | 128360 | 1 | Estimated | 341356.68 | 344516.9835 | Shyampur | Nandalalpur 33/11 kV | 89 | 366892.6717 | 367089.0787 | 471911.02 | 670610.6986 | 650428.6635 | 670079.927 | 673810.7719 | 652026.96 | 610908.7086
1055 | 11 kV Rasel Germants | 0 | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1056 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 | 0 | 00000121 | 1 | 86458552 | 88835864 | 2377312 | 1 | 0 | 2377312 | 2399321.3174 | Matuail | Nandalalpur 33/11 kV | 89 | 1808871.6613 | 1843472.6956 | 2197883.0829 | 2409135.9772 | 2474142.3426 | 2710158.1798 | 2342109.1991 | 2438091.1118 | 2521439.5722
1057 | 11 kV Nandalalpur | B890X | 11 | 0 | 00000010 | 1 | 88538464 | 90142376 | 1603912 | 1 | 0 | 1603912 | 1618761.1272 | Fatullah | Nandalalpur 33/11 kV | 89 | 973812.9121 | 593099.2465 | 845396.3918 | 817827.925 | 726019.9781 | 743459.691 | 869061.7913 | 928548.3765 | 892208.2473
1058 | 11 kV Sharif Bagh | B489SB | 11 | 0 | 00000132 | 1 | 80714720 | 81823560 | 1108840 | 1 | 0 | 1108840 | 1119105.7167 | Shyampur | Nandalalpur 33/11 kV | 89 | 1085733.2265 | 1188170.2592 | 1429052.9803 | 1697558.3187 | 1769871.618 | 1607397.0329 | 1797879.9406 | 1716982.5939 | 1682233.437
1059 | 11 kV Spare | spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1060 | 11 KV Nayamati | B890Y | 11 | 0 | 00000158 | 1 | 71063584 | 71687344 | 623760 | 1 | 0 | 623760 | 629534.8128 | Fatullah | Nandalalpur 33/11 kV | 89 | 729356.23 | 865927.3143 | 1006892.0073 | 1138166.5842 | 1094447.1869 | 1160143.2858 | 1059913.8974 | 1145403.0364 | 1037983.1413
1061 | 11 kV Pulpar | B889S | 11 | 0 | 00000160 | 1 | 13525447 | 15039563 | 1514116 | 1 | 0 | 1514116 | 1528133.7897 | Fatullah | Nandalalpur 33/11 kV | 89 | 1267285.0049 | 1013887.2469 | 944347.6364 | 974125.8442 | 814027.697 | 905763.961 | 653442.1412 | 808373.695 | 916555.6279
1062 | 11 kV Shahi Bazar | B489X | 11 | 0 | 00000170 | 1 | 44797452 | 45356488 | 559036 | 1 | 0 | 559036 | 564211.5936 | Shyampur | Nandalalpur 33/11 kV | 89 | 420927.8461 | 471131.4185 | 593266.4637 | 769069.4058 | 789833.0592 | 884250.6672 | 830388.5657 | 784445.919 | 785444.6114
1063 | 11 kV Pagla Bazar | B890G | 11 | 0 | 00000060 | 1 | 53705668 | 54194108 | 488440 | 1 | 0 | 488440 | 492962.011 | Fatullah | Nandalalpur 33/11 kV | 89 | 446265.5628 | 483400.6336 | 561438.012 | 651299.1372 | 675946.8632 | 703594.2894 | 679748.7175 | 834561.5067 | 783154.3223
1064 | 11 kV Delpara bazar | B489M | 11 | 0 | 00000063 | 1 | 88033984 | 89240144 | 1206160 | 1 | 0 | 1206160 | 1217326.7119 | Shyampur | Nandalalpur 33/11 kV | 89 | 1352583.6238 | 1426713.738 | 1432420.6462 | 1512147.634 | 1531851.518 | 1668168.7326 | 1521265.0516 | 1508132.7308 | 1527622.8486
1065 | 11 kV Bhuighor (Board mill) | E289C | 11 | 0 | 00000146 | 1 | 47761524 | 48318124 | 556600 | 1 | 0 | 556600 | 561753.0409 | Matuail | Nandalalpur 33/11 kV | 89 | 635132.0988 | 628224.8542 | 631758.0829 | 736149.3859 | 684221.3852 | 711807.7641 | 702632.7597 | 668462.9794 | 1074021.0416
1066 | 11 kV Spare | 0 | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1067 | 33/0.415 kV, 200 kVA AT-1 | 0 | 11 | 0 | 7803 | 1 | 2684 | 2707.7 | 23.7 | 100 | 0 | 2370 | 2391.9416 | Shyampur | Nandalalpur 33/11 kV | 89 | 2513.6624 | 2515.008 | 3407.7571 | 4811.696 | 5827.1281 | 5909.6952 | 6446.2091 | 6244.3055 | 5725.7228
1068 | 33/0.415 kV, 200 kVA AT-2 | 0 | 11 | 0 | 7805 | 1 | 89 | 94.3 | 5.3 | 100 | 0 | 530 | 534.9068 | Shyampur | Nandalalpur 33/11 kV | 89 | 522.8418 | 563.3618 | 711.6199 | 912.2174 | 1004.6773 | 100.1643 | 0 | 0 | 0
1069 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 68603944 | 69356979 | 753035 | 1 | 0 | 753035 | 766944.6993 | Postogola | Postogola 33/11KV S/S | 25 | 737584.4324 | 818415.5629 | 964969.6559 | 1255334.9139 | 1334586.3999 | 1219095.1394 | 1335055.4691 | 1307497.2614 | 1269812.3426
1070 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 2469.7 | 3314.1 | 844.4 | 1000 | 0 | 844400 | 859997.3495 | Jurain | Postogola 33/11KV S/S | 25 | 893758.2817 | 1025457.2503 | 1204492.2718 | 1239052.6971 | 1255387.5265 | 1323367.1334 | 1374189.6942 | 1360936.1962 | 1367079.5822
1071 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 26932943 | 27319153 | 386210 | 1 | 0 | 386210 | 393343.8848 | Jurain | Postogola 33/11KV S/S | 25 | 438805.162 | 467431.0447 | 407994.3823 | 537163.6113 | 519931.6597 | 537056.744 | 474949.556 | 542387.1952 | 435813.5436
1072 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 82148708 | 83065054 | 916346 | 1 | 0 | 916346 | 933272.3014 | Postogola | Postogola 33/11KV S/S | 25 | 909857.0079 | 1006682.8975 | 1282024.8716 | 1532425.7761 | 1609308.7492 | 1557430.4575 | 1587221.6201 | 1546887.4107 | 1509702.7057
1073 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 487008.3 | 494591.1 | 7582.8 | 60 | 0 | 454968 | 463371.9495 | Postogola | Postogola 33/11KV S/S | 25 | 446819.6527 | 512771.7141 | 575584.882 | 676389.0131 | 678803.9555 | 662617.3772 | 636891.4703 | 664686.4068 | 678488.3278
1074 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 966474.7 | 978748.4 | 12273.7 | 60 | 0 | 736422 | 750024.832 | Postogola | Postogola 33/11KV S/S | 25 | 718393.3477 | 792566.2392 | 972773.5086 | 1191302.5568 | 1270287.67 | 1139734.1436 | 1267305.3443 | 1258808.5211 | 1186933.4512
1075 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 857587.6 | 870988.1 | 13400.5 | 60 | 0 | 804030 | 818881.6544 | Postogola | Postogola 33/11KV S/S | 25 | 778178.9459 | 818168.4647 | 1013780.9955 | 1266750.2722 | 1384014.8487 | 1419724.1658 | 1247409.4401 | 1227619.0196 | 1164704.2052
1076 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 531085.9 | 532049.3 | 963.4 | 60 | 0 | 57804 | 58871.7276 | Postogola | Postogola 33/11KV S/S | 25 | 59976.3705 | 93470.4845 | 133370.1443 | 125848.0606 | 126732.5803 | 134717.5169 | 129509.8262 | 124992.5587 | 126222.4118
1077 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 975578.9 | 998174.5 | 22595.6 | 60 | 0 | 1355736 | 1380778.5015 | Postogola | Postogola 33/11KV S/S | 25 | 1491415.2858 | 1433344.7925 | 1390963.4921 | 1427602.3077 | 1330189.3065 | 1373424.2339 | 1052907.1287 | 1323292.4846 | 1331811.5849
1078 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 495051.3 | 511122.6 | 16071.3 | 60 | 0 | 964278 | 982089.6781 | Jurain | Postogola 33/11KV S/S | 25 | 758406.3132 | 839715.0135 | 1423612.5326 | 2449336.9799 | 2475377.6895 | 2446524.7479 | 2443876.2234 | 2429557.5202 | 2393972.4885
1079 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 49734483 | 50750371 | 1015888 | 1 | 0 | 1015888 | 1034652.9932 | Jurain | Postogola 33/11KV S/S | 25 | 929342.4564 | 1077216.1405 | 2497097.0061 | 2454381.4966 | 2115704.7964 | 2221056.7969 | 2061497.5542 | 2071894.6482 | 1933992.5359
1080 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 20898.3 | 22454.9 | 1556.6 | 1000 | 0 | 1556600 | 1585352.7644 | Jurain | Postogola 33/11KV S/S | 25 | 1530384.1315 | 1727032.1548 | 2152168.1359 | 2435670.3328 | 2485795.0121 | 2477072.4328 | 2360182.711 | 2388027.6504 | 2351667.7366
1081 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 64278986 | 65251735 | 972749 | 1 | 0 | 972749 | 990717.1504 | Postogola | Postogola 33/11KV S/S | 25 | 953613.6246 | 1058426.4718 | 1360729.5194 | 1622380.5518 | 1682719.5891 | 1655098.2 | 1632466.5583 | 1639249.0712 | 1571920.5306
1082 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 217.2 | 308.4 | 91.2 | 1000 | 0 | 91200 | 92884.6024 | Postogola | Postogola 33/11KV S/S | 25 | 84309.0782 | 83625.3597 | 107674.3091 | 247810.5394 | 239121.4336 | 245164.3984 | 245637.4316 | 262708.1006 | 303872.8913
1083 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 11 | 0 | ELIB67385 | 1 | 666.1 | 701.88 | 35.78 | 80 | 0 | 2862.4 | 2915.2729 | Postogola | Postogola 33/11KV S/S | 25 | 3420.7742 | 3185.728 | 3713.2428 | 4606.8906 | 4570.7831 | 4670.5121 | 4307.9725 | 5751.9551 | 4375.6621
1084 | 11 kV Feeder-1 | 0 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1085 | 11 kV Feeder-2 | 0 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1086 | 11 kV Dholaikal RMU | A619R | 11 | 0 | DHK60970 | 1 | 385192.6 | 402446.4 | 17253.8 | 60 | 0 | 1035228 | 1050754.3313 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 993748.355 | 902364.9 | 1688724 | 1912589.3597 | 2044107.1526 | 2258178.5414 | 2013206.2605 | 1942348.072 | 1890634.7965
1087 | 11 kV Alom Gonj | A581A | 11 | 0 | DHK60894 | 1 | 531417.9 | 537217.3 | 5799.4 | 60 | 0 | 347964 | 353182.7579 | Postogola | IG Gate GIS 33/11 kV | 87 | 341849.6279 | 374020.983 | 577380 | 601965.5066 | 622652.7534 | 676806.1857 | 596654.2301 | 589855.3321 | 589628.102
1088 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 | 0 | DHK60895 | 1 | 681848.5 | 698964.4 | 17115.9 | 60 | 0 | 1026954 | 1042356.2379 | Postogola | IG Gate GIS 33/11 kV | 87 | 998356.1619 | 1122062.949 | 1533942 | 1585262.0566 | 1935090.8799 | 1875565.0903 | 1850628.0181 | 1792355.2732 | 1711977.4089
1089 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 | 0 | DHK68133 | 1 | 3746.38 | 3765.72 | 19.34 | 60000 | 0 | 1160400 | 1177803.6587 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1144988.569 | 995070 | 1656000 | 1845366.1756 | 1846529.6992 | 2047321.2801 | 1803939.5949 | 1748762.5817 | 1815572.1775
1090 | 11 kV Doyaganj | B587Y | 11 | 0 | DHK68134 | 1 | 2516.51 | 2535.08 | 18.57 | 60000 | 0 | 1114200 | 1130910.7519 | Swamibag | IG Gate GIS 33/11 kV | 87 | 888864.7379 | 833325 | 1512000 | 1596436.5035 | 1387958.4974 | 1645033.4081 | 1687142.9696 | 1819772.2117 | 1955417.8504
1091 | 11 kV Faridabad | A587F | 11 | 0 | DHK68140 | 1 | 880.02 | 891.93 | 11.91 | 60000 | 0 | 714600 | 725317.5582 | Postogola | IG Gate GIS 33/11 kV | 87 | 718721.0108 | 810378.7965 | 1123200 | 1253169.1806 | 1329183.0163 | 1411966.4378 | 1296128.1808 | 1292615.9757 | 1233789.9626
1092 | 11 kV Gandaria | A524D | 11 | 0 | DHK60969 | 1 | 539206 | 558384.7 | 19178.7 | 60 | 0 | 1150722 | 1167980.5082 | Postogola | IG Gate GIS 33/11 kV | 87 | 1163546.9506 | 1246736.61 | 1778304 | 1938857.8307 | 2106445.8973 | 2096887.3731 | 2186472.7241 | 2176408.4497 | 2008723.2675
1093 | 11 kV Walter Road | A687W | 11 | 0 | DHK68136 | 1 | 1099.91 | 1113.41 | 13.5 | 60000 | 0 | 810000 | 822148.3657 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 765344.025 | 727545 | 1269000 | 1348724.0914 | 2063264.286 | 1501529.2301 | 1391040.5522 | 1437042.3417 | 1402694.4766
1094 | 11 kV Murgitola Feeder (F-11) | B587G | 11 | 0 | DHK68138 | 1 | 4084.44 | 4107.26 | 22.82 | 60000 | 0 | 1369200 | 1389735.2374 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1315132.2961 | 1202940 | 2049000 | 2352354.9699 | 2412855.9498 | 2416392.1157 | 2307519.2472 | 2337901.7997 | 2438521.0841
1095 | 11 kV Feeder-12 | 0 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1096 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 | 0 | DHK60899 | 1 | 808791.9 | 825043.7 | 16251.8 | 60 | 0 | 975108 | 989732.6526 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1020953.1865 | 858865.95 | 1530696 | 1678266.8077 | 1754827.7038 | 1727816.5375 | 1778252.8009 | 1741101.9665 | 1809148.9629
1097 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 | 0 | DHK60967 | 1 | 245164.3 | 254436.4 | 9272.1 | 60 | 0 | 556326 | 564669.7675 | Postogola | IG Gate GIS 33/11 kV | 87 | 535098.9942 | 585966.2067 | 822432 | 935068.7084 | 1005323.9927 | 1010280.3195 | 1031522.1618 | 1006862.3928 | 984580.1304
1098 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB2774 | 1 | 288325 | 289470 | 1145 | 1 | 0 | 1145 | 1162.1727 | Postogola | IG Gate GIS 33/11 kV | 87 | 1372.4524 | 1058.825 | 1552 | 1538.8094 | 3608.1717 | 0 | 1665.5005 | 1667.9239 | 1718.3058
1099 | Nizambag | F1114Z | 11 | 0 | 6604414 | 1 | 3907.2 | 3929.07 | 21.87 | 8000 | Estimated | 1592997.84 | 1600846.3691 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 853490.0177 | 504749.4737 | 234080.9166 | 1217190.9472 | 1180785.7325 | 1158100.6579 | 1095738.2283 | 1008260.1492 | 972380.6635
1100 | Merry Stopes | F1114P | 11 | 0 | 6604287 | 1 | 21637.99 | 21649.31 | 11.32 | 8000 | Estimated | 284463.9 | 285865.4231 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 98328.343 | 61122.0066 | 55077.8627 | 304297.7368 | 318812.1478 | 329144.3975 | 365246.0761 | 355856.5232 | 364642.7488
1101 | Mujibur Ghat | F1114V | 11 | 0 | 6604387 | 1 | 4433.72 | 4433.72 | 0 | 8000 | Estimated | 313891.2 | 315437.7082 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 975417.1631 | 1344684.1447 | 275389.3137 | 1278050.4946 | 1298864.3057 | 1340958.6566 | 1217486.9203 | 1304807.2519 | 1337023.4124
1102 | Madrasa | F1114U | 11 | 0 | 6604481 | 1 | 14283.77 | 14471.07 | 187.3 | 8000 | Estimated | 1592997.84 | 1600846.3691 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1463125.7446 | 946405.2632 | 330467.1764 | 1582348.2314 | 1653100.0255 | 1462863.989 | 1424459.6968 | 1542044.934 | 1701666.1612
1103 | Thana | F1114Q | 11 | 0 | 6604443 | 1 | 10583.45 | 10693.55 | 110.1 | 8000 | Estimated | 1080962.82 | 1086288.6076 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1158307.8811 | 1528050.1645 | 247850.3823 | 1217190.9472 | 1298864.3057 | 1219053.3241 | 1217486.9203 | 1423426.093 | 1337023.4124
1104 | Al-Hera | 0 | 11 | 0 | 6604372 | 1 | 0 | 0 | 0 | 8000 | Estimated | 227571.12 | 228692.3384 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1105 | Waz Uddin School | F1114W | 11 | 0 | 6604448 | 1 | 8387.85 | 8561.84 | 173.99 | 8000 | Estimated | 796498.92 | 800423.1845 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 853490.0177 | 820217.8947 | 192772.5196 | 852033.6631 | 1003667.8726 | 975242.6593 | 730492.1522 | 830331.8876 | 972380.6635
1106 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1107 | Bashundhara City | 0 | 33 | 0 | 660434 | 1 | 834.35 | 845.2 | 10.85 | 180000 | 0 | 1953000 | 1956141.6346 | Shere b.nagar | Moghbazar 132/33/11KV S/S |  | 1735012.7134 | 1925027.8888 | 1952470.6666 | 2191476.9852 | 2303155.9363 | 2253160.9458 | 2286948.2926 | 2480389.347 | 2161081.9864
1108 | 33 kV Apollo Ispat Feeder | 0 | 33 | DPDC | 7389486 | 1 | 4671.22 | 4695.7 | 24.48 | 240000 | 0 | 5875200 | 5880240.0588 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 7137397.0479 | 5981061.6729 | 5757883.9148 | 5345006.6439 | 5626849.4493 | 4868511.8333 | 6352475.5818 | 7317548.4229 | 5615154.9463
1109 | 33 kV Adamjee EPZ Feeder | 0 | 33 | DPDC | ABB03919 | 1 | 387654.7 | 391490 | 3835.3 | 2000 | 0 | 7670600 | 7677180.2483 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 7245648.7726 | 7381064.2136 | 9198984.9536 | 9835003.2885 | 9088565.8308 | 9139513.6232 | 7905743.5896 | 8068621.1441 | 8850787.3005
1110 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1027.67 | 1030.1 | 2.43 | 240000 | 0 | 583200 | 583200 | Siddirgonj | Demra 33/11KV S/S | 16 | 676800 | 597600 | 792000 | 799200 | 616800 | 492000 | 571200 | 446400 | 0
1111 | 33 kV ACI Pharmacuticles Feeder | 0 | 33 | 0 | DHKC4791 | 1 | 981.97 | 990.46 | 8.49 | 90000 | 0 | 764100 | 764100 | N.Gonj (East) | Khanpur 33/11KV S/S |  | 903600 | 999000 | 1583100 | 1440900 | 1206900 | 1225800 | 1291500 | 1045800 | 0
1112 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC | 0 | 1 | 39.34 | 40.81 | 1.47 | 6000 | From Customer End | 8820 | 8847.3181 | Matuail | Matuail 132/33 KV S/S | 41 | 13860 | 13529.8748 | 7215.4751 | 8160.0632 | 8383.4623 | 9119.9454 | 10440.0638 | 10260.3419 | 10991.7418
1113 | 33 KV Shah Cement Feeder (F2) | 0 | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 0 | 0 | 0 | 108.9746 | 64646.4953 | 944204.0986 | 2494536.8881 | 923421.8011 | 1229303.7954
1114 | 33/0.415 KV Transformer AT-1 | 0 | 0.415 | DPDC | 2001123043108 | 1 | 6601.2 | 6601.2 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 0 | 2898.2343 | 3710.9239 | 639.8509 | 0 | 0 | 0 | 0 | 0
1115 | 33/0.415 KV Transformer AT-2 | 0 | 0.415 | DPDC | 2001123043171 | 1 | 4821.1 | 4843.2 | 22.1 | 160 | 0 | 3536 | 3536.6329 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 4405.413 | 1200.9258 | 0 | 3647.1499 | 6180.7322 | 7797.005 | 4755.5609 | 4035.644 | 2848.7249
1116 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 0 | 33 | Main | 041808902866 | 1 | 414.31 | 436.67 | 22.36 | 360000 | 0 | 8049600 | 8050443.0861 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 6760205.7754 | 7313177.5551 | 5005228.5182 | 6404881.1253 | 5779395.3475 | 7171154.3348 | 6850018.059 | 6815752.3123 | 6616060.3155
1117 | 33 kV Delta Agro Premier Cement (=H2) | 0 | 33 | Main | 041808902876 | 1 | 145.66 | 157.03 | 11.37 | 360000 | 0 | 4093200 | 4093628.707 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 3678558.781 | 1822901.19 | 2659365.4762 | 2937522.8571 | 2682130.383 | 2390384.7783 | 2530901.4092 | 2430058.343 | 2458012.5886
1118 | 33 kV Crown Cement-1 (=H3) | 0 | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1119 | 33 kV Outgoing Feeder-4 (=H4) | 0 | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1120 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 400185.2656 | 1006790.1928 | 1108090.8439
1121 | 33 kV Outgoing Feeder-6 (=H12) | 0 | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1122 | 33 kV Crown Cement-2 (=H13) | 0 | 33 | Main | 041808902857 | 1 | 12.92 | 30.73 | 17.81 | 360000 | 0 | 6411600 | 6412271.5279 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 4275470.5675 | 348760.1882 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1123 | 33 kV Shah Cement VRM (=H14) | 0 | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 2277825.3993 | 11858183.3118 | 9272761.2883 | 10712537.375 | 10817421.0397
1124 | 11 KV Shahidbagh Feeder | 0 | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 311340 | 316266.4859 | Rajarbag | Santinagar Switching S/S |  | 254453.6019 | 279780.4906 | 407049.5473 | 492002.3987 | 599477.6789 | 597504.11 | 524779.3911 | 36416.7693 | -3994.0825
1125 | 11 Fortune(MogBazar)-new | 0 | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 65520 | 66556.7552 | Moghbazar | Santinagar Switching S/S |  | 64569.764 | 105125.6925 | 104859.5814 | 122203.1256 | 123551.4515 | 107474.29 | 138756.0658 | 127666.1608 | 126229.899
1126 | Centerpoint-Kakrail | 0 | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 55200 | 56073.4567 | Kakrail | Santinagar Switching S/S |  | 60659.0292 | 63909.8612 | 63748.0823 | 61390.4591 | 62067.8095 | 43848 | 71600.1051 | 81766.8748 | 80846.9863
1127 | 11 KV Shyamoli O/H | 0 | 11 | 0 | DHK-15026 | 1 | 9242.88 | 9249.79 | 6.91 | 40000 | 0 | 276400 | 283310 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 269370 | 296020 | 378430 | 520290 | 602290 | 545300 | 584660 | 530950
1128 | 11 KV Nearest RMU | 0 | 11 | 0 | DHK-15027 | 1 | 3882.98 | 3885.65 | 2.67 | 40000 | 0 | 106800 | 109470 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 82820 | 121360 | 93070 | 157030 | 160310 | 164820 | 182450 | 165230
1129 | 11 KV Sher-e-bangla Nagar | 0 | 11 | 0 | DHK-15025 | 1 | 3987.09 | 3987.82 | 0.73 | 40000 | 0 | 29200 | 29930 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 30750 | 94300 | 144320 | 33620 | 51660 | 44280 | 49610 | 45920
1130 | Export to DESCO | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13837.5
1131 | 33/0.4 kV, 500 kVA AT-1 | 0 | 0.4 | 0 | 84.2659 | 1 | 328945 | 330687 | 1742 | 10 | 0 | 17420 | 17454.7853 | Paribag | Dhanmondi 33/11KV S/S |  | 17708.5481 | 18196.6014 | 19032.3858 | 23956.6474 | 23982.7488 | 25078.0786 | 24914.239 | 24707.6715
1132 | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0.4 | 0 | 84.2673 | 1 | 478776 | 478776 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S |  | 0 | 0 | 0 | 0 | 875.2094 | 10.0032 | 0 | 0
1133 | 33 KV Japan Genden City | 0 | 33 | 0 | DHK15681 | 1 | 855.55 | 907.12 | 51.57 | 18000 | 0 | 928260 | 928260 | Adabor | Japan Garden 33/11 KV |  | 912960 | 974700 | 1130040 | 1459800 | 1502640 | 1451700 | 1519200 | 1531620
1134 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKE6223 | 1 | 43873.75 | 43929.56 | 55.81 | 120 | 0 | 6697.2 | 6785.701 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 0 | 9376.9111 | 21708.6097 | 23301.1673 | 23194.682 | 23415.1565 | 24412.3409 | 25361.4506
1135 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHK37495 | 1 | 45794.4 | 45854.3 | 59.9 | 120 | 0 | 7188 | 7282.9867 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 15169.9389 | 9320.8641 | 0 | 0 | 0 | 0 | 0 | 0
1136 | AT-1 | 0 | 0.415 | 0 | 0 | 1 | 1121.79 | 1172.79 | 51 | 80 | 0 | 4080 | 4102.895 | Mugdapara | Madarteck 33/11KV S/S |  | 3701.4207 | 4390.1062 | 5672.1022 | 12954.5544 | 10606.4337 | 12573.2122 | 11708.7885 | 9611.7345
1137 | AT-2 | 0 | 0.415 | 0 | 63394003 | 1 | 671.6 | 730.77 | 59.17 | 80 | 0 | 4733.6 | 4760.1627 | Mugdapara | Madarteck 33/11KV S/S |  | 5134.021 | 4711.9615 | 5966.9871 | 6056.6539 | 7745.9106 | 5649.4556 | 6156.9427 | 5477.3433
1138 | 33 kV Shahriar Steel Feeder | 0 | 33 | Main | 41812909534 | 1 | 692.92 | 710.82 | 17.9 | 360000 | 0 | 6444000 | 6435450.7463 | Kazla | Kazla 132/133 KV SS |  | 7271238.1943 | 7356070.5709 | 6734848.5186 | 7150980.086 | 7435235.4244 | 7833434.8553 | 7323524.0635 | 7145780.8426
1139 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 806.02 | 834.62 | 28.6 | 360000 | 0 | 10296000 | 10282340.2985 | Kazla | Kazla 132/133 KV SS |  | 8831170.3306 | 10864240.3473 | 10607025.8788 | 11059032.0485 | 10618692.0573 | 11070629.7471 | 10019388.2364 | 9121125.0936
1140 | 33kV Water Treatment Plant | 0 | 33 | Digital | 80379618 | 1 | 22980 | 23500 | 520 | 2000 | 0 | 1040000 | 1039856.1088 | Maniknagar | Maniknagar 132/33 KV SS |  | 960032.0942 | 908496.4888 | 468459.6796 | 526937.9846 | 686173.136 | 531621.6224 | 605078.9898 | 1062218.4705
1141 | Axuxilary -1 | 0 | 0.415 | 0 | AH14044078 | 1 | 428437 | 434808.3 | 6371.3 | 1 | 0 | 6371.3 | 6351.127 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 1388.5133 | 2652.2304 | 3860.1372 | 5837.95 | 5955.9261 | 5213.2044 | 5831.4157 | 6475.0369
1142 | Axuxilary -2 | 0 | 0.415 | 0 | AH14044072 | 1 | 402099 | 405236.1 | 3137.1 | 1 | 0 | 3137.1 | 3127.1672 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 4739.5139 | 4733.5825 | 4282.1807 | 4943.482 | 4558.0495 | 4382.3431 | 5377.7142 | 4841.9103
1143 | 33 kV Rani RRM Feeder | 0 | 33 | Export | BD001809 | 1 | 795.3914 | 802.1699 | 6.7785 | 240000 | 0 | 1626840 | 1627514.4634 | Shyampur | Shyampur 132/33KV S/S |  | 2056494.036 | 3325068.7934 | 3021325.4164 | 2543674.3806 | 3093749.2487 | 2731257.9254 | 2448780.2928 | 2460914.9302
1144 | 33 kV Rahima Steel feeder | 0 | 33 | Export | BD001803 | 1 | 690.9685 | 702.6719 | 11.7034 | 240000 | 0 | 2808816 | 2809980.4929 | Shyampur | Shyampur 132/33KV S/S |  | 3094685.5552 | 2943586.1715 | 2258252.921 | 387957.1282 | 1848762.9304 | 2408497.5549 | 1851141.9981 | 2281164.2763
1145 | 33 kV Salam Steel Feeder | 0 | 33 | Export | BD001849 | 1 | 1373.5909 | 1415.526 | 41.9351 | 240000 | 0 | 10064424 | 10068596.5588 | Shyampur | Shyampur 132/33KV S/S |  | 9975944.1398 | 9208183.8323 | 10104745.6836 | 9425654.7552 | 6942639.1851 | 9555598.3573 | 9761265.4061 | 10754060.1599
1146 | 33 kV Steel Famus feeder | 0 | 33 | Export | BD001806 | 1 | 178.6475 | 187.0834 | 8.4359 | 240000 | 0 | 2024616 | 2025455.3753 | Shyampur | Shyampur 132/33KV S/S |  | 2243638.0198 | 1784133.4829 | 1983916.4772 | 1855188.4343 | 668060.7526 | 1802076.7353 | 1343089.4196 | 1442423.9509
1147 | 33 kV Rani Kamal Steel Feeder | 0 | 33 | Export | BD001829 | 1 | 1672.456 | 1700.5059 | 28.0499 | 240000 | 0 | 6731976 | 6734766.976 | Shyampur | Shyampur 132/33KV S/S |  | 6694042.5391 | 6184171.8091 | 6138184.9168 | 5684015.7878 | 6636959.5785 | 7405918.76 | 5422228.9014 | 6501978.5941
1148 | 33 kV Chakda Steel Feeder | 0 | 33 | Export | BD001832 | 1 | 2604.5029 | 2645.9221 | 41.4192 | 240000 | 0 | 9940608 | 9944729.2265 | Shyampur | Shyampur 132/33KV S/S |  | 11174809.0139 | 9755079.6237 | 9470500.1805 | 8724428.8439 | 9042995.7002 | 9230581.7605 | 8256580.7385 | 8640663.1605
1149 | 33 kV Akhter Steel Feeder | 0 | 33 | Export | BD001828 | 1 | 691.9165 | 691.9365 | 0.02 | 240000 | Prime Textile | 4800 | 4801.99 | Fatullah | Shyampur 132/33KV S/S |  | 1801.5401 | 12844.1286 | 210535.038 | 1073036.1535 | 1039008.3182 | 1167285.0702 | 1147950.5517 | 674551.2513
1150 | Aux Tr-1 | 0 | 0.44kv | Export | DHKG9742 | 1.025 | 355.623 | 357.514 | 1.891 | 2400 | 0 | 4651.86 | 4651.86 | Fatullah | Shyampur 132/33KV S/S |  | 5210.28 | 5116.8 | 4324.68 | 5222.58 | 5052.84 | 5102.04 | 5527.62 | 10071.24
1151 | Aux Tr-2 | 0 | 0.44kv | Export | DHKG9743 | 1.025 | 133.786 | 137.425 | 3.639 | 2400 | 0 | 8951.94 | 8951.94 | Fatullah | Shyampur 132/33KV S/S |  | 10696.08 | 12277.86 | 15992.46 | 19576.68 | 17894.04 | 18044.1 | 19434 | 11042.94
1152 | 132 kV MI Cement Feeder [MICFL] | 0 | 132 | P. Cell | 08993599 | 1 | 420.507 | 435.968 | 15.461 | 480000 |  | 7422240 | 7422240 | Sytalakhya | MI CEMENT 132/33 kV |  | 9621120 | 11776320 | 12340320 | 12087360 | 11905920 | 10329120 | 10749120 | 9239520
1153 | 33 kV Shah Cement Feeder | 0 | 33 | 0 | 8993 841 | 1 | 96.731 | 198.152 | 101.421 | 36000 | 3585 | 3651156 | 3654741 | Sytalakhya | Madonganj 132/33 KV SS |  | 1986206 | 875816 | 3079152 | 1948464 | 817416 | 2360592 | 3210156 | 3227092
1154 | 33 kV Mondol Para (Premire cement) Feeder | 0 | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1155 | 11 kV Rayer Bazar Feeder | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 668980.62 | 668588.5859 | Dhanmondi | Jigatola Switching |  | 610716.8875 | 853652.5785 | 789619.7227 | 0 | 0 | 0 | 679467.069
1156 | 11 kV Madina Masjid Feeder | 0 | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1094695.56 | 1094054.0497 | Jigatola | Jigatola Switching |  | 977147.02 | 1158528.4994 | 1223910.5702 | 1463157.2985 | 1648779.5998 | 1579031.3193 | 1587392.6308
1157 | 11 kV Mitali | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 726323.82 | 725898.1818 | Jigatola | Jigatola Switching |  | 540833.6681 | 533046.059 | 1101165.3592 | 1474997.974 | 1417602.7084 | 1504281.4171 | 1520651.6572
1158 | 132 kV Shah Cement | 0 | 132 | EXPORT | 042003953369 | 1 | 57.56 | 68.69 | 11.13 | 1200000 |  | 13356000 | 13356000 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 14352000 | 15036000 | 13884000 | 15096000 | 10668000
1159 | 132 KV Metro Rail -1 | 0 | 132 | 0 | 42627805 | 1 | 0.245 | 1.685 | 1.44 | 480000 | 0 | 691200 | 691200 | Motijheel | Maniknagar 132/33 S/S |  | 2880 | 0 | 111840
1160 | 132 KV Metro Rail -2 | 0 | 132 | 0 | 42627793 | 1 | 2.335 | 2.335 | 0 | 480000 | 0 | 0 | 0 | Motijheel | Maniknagar 132/33 S/S |  | 0 | 15360 | 1104480
1161 | 33 KV Khejurbagan | 0 | 33 | 0 | 0 | 1 | 6237.41 | 6237.8 | 0.39 | 180000 | 0 | 70200 | 70312.9251 | Shere b.nagar | Moghbazar 132/33/11KV S/S
1162 | Sangsad Bhaban (DPDC Ckt-03) | 0 | 33 | 0 | 3578 6580 | 1 | 111.818 | 113.188 | 1.37 | 180000 | 0 | 246600 | 248174.72 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
1163 | Mahadinagar | 0 | 11 | 0 | WP042358 | 1 | 148.6 | 841988 | 841839.4 | 1 | 0 | 841839.4 | 846977.0681 | Kamrangirchar | Bosila-1 S/S
1164 | Badsha Mia School | 0 | 11 | 0 | WP042375 | 1 | 59.32 | 1138613 | 1138553.68 | 1 | 0 | 1138553.68 | 1145502.1679 | Kamrangirchar | Bosila-1 S/S
1165 | Shahjahan Sir | 0 | 11 | 0 | WP042361 | 1 | 41.37 | 384521 | 384479.63 | 1 | 0 | 384479.63 | 386826.0737 | Kamrangirchar | Bosila-1 S/S
1166 | Gazirghat | 0 | 11 | 0 | WP042395 | 1 | 41.83 | 729763 | 729721.17 | 1 | 0 | 729721.17 | 734174.5909 | Kamrangirchar | Bosila-1 S/S

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Feeder Code | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) |  | 3: 132; 4: IMPORT; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000
| 132 KV DHANMONDI-3 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 10: Net Total | 47329000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 |  | 132 |  | SIEM0480 | 1 | 1632768 | 1635373 | 2605 | 1000 | 2605000
| 132 kV Dhaka University |  | 132 |  | SIEM0480 | 1 | 187780 | 215012 | 27232 | 1000 | 27232000
3 | 132 kV Dhaka University |  | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 |  | 132 |  | SIEM0481 | 1 | 2254582 | 2263314 | 8732 | 1000 | 8732000
8 | 132 kV Ullon Circuit-3 |  | 132 |  | SIEM0484 | 1 | 3010496 | 3019256 | 8760 | 1000 | 8760000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 47329000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 47329000
| DHANMONDI 132 KV SIDE (EXPORT To / IMPORT From OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhaka University (Export) |  | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) |  | 132 |  |  | 1 | 187780 | 215012 | 27232 | 1000 |  | 27232000
|  |  | 7: 0; 8: 0; 10: Total |  | 27232000
| DHANMONDI 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) |  | 132 | NET IMPORT | SIEM0487 | 1 | 943227 | 954739 | 11512 | 1000 |  | 11512000
5 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | SIEM0496 | 1 | 1506046 | 1511080 | 5034 | 2000 |  | 10068000
9 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | SIEM0493 | 1 | 1375861 | 1380869 | 5008 | 2000 |  | 10016000
10 | 132/33kV, 80/120 MVA GT-3 (HV) |  | 132 |  | SIEM0497 | 1 | 1355256 | 1363110 | 7854 | 2000 |  | 15708000
|  |  | 10: Total |  | 47304000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 4: 47304000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 47304000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 47304000 | 132/33 kv GT LV Side |  | 47095200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 208800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4414%
| 132 KV TOTAL IMPORT |  | 4: 47304000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming |  | 33 | IMPORT | BD001860 | 1 | 2350.93 | 2364.83 | 13.9 | 720000 | 10008000
12 | 132/33 kV GT-2 Incoming |  | 33 |  | BD001818 | 1 | 2318.9 | 2332.75 | 13.85 | 720000 | 9972000
17 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001863 | 1 | 2090.21 | 2111.95 | 21.74 | 720000 | 15652800
24 | 132/33 kV GT-4 Incoming |  | 33 |  | BD001916 | 1 | 1955.87 | 1979.75 | 23.88 | 480000 | 11462400
|  |  | 7: 0; 8: 0; 10: Total | 47095200 |  | 0
| DHANMONDI 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 |  |  |  |  | 8270081.275 | Dhanmondi 33/11 kv ss | 0.2543 |  | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 |  | 33 |  | BD001861 | 1 | 2224.38 | 2240.56 | 16.18 | 240000 |  | 3883200 | 3890954.2027 | [5 empty] | 33/11 kV 20/28 MVA T-1 | 3890954.2027 | 3726337.0774 | 164617.1252 | 4.4177 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 |  | BD001892 | 1 | 2532.16 | 2550.37 | 18.21 | 240000 |  | 4370400 | 4379127.0723 | [5 empty] | 33/11 kV 20/28 MVA T-2 | 4379127.0723 | 3859075.7686 | 520051.3037 | 13.4761 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8253600 | 8270081.275 | [5 empty] | 33 KV Feeders | 8270081.275 | 7585412.8461 | 684668.4289 | 9.0261 | OK
5 | New Ramna Circuit-1 |  | 33 |  | BD001919 | 1 | 1550.75 | 1562.31 | 11.56 | 240000 |  | 2774400 | 2779940.0855 |  | 4359888.7326 | New Ramna 33/11 kv ss | 1.6271 |  | New Ramna Circuit-1 | 2779940.0855 | 2618572.3633 | 161367.7221 | 6.1624 | OK
8 | Kakrail Circuit-1 |  | 33 |  | BD001825 | 1 | 913.91 | 924.13 | 10.22 | 240000 |  | 2452800 | 2457697.8956 | [5 empty] | Kakrail Circuit-1 | 2457697.8956 | 1563903.1258 | 893794.7699 | 57.1515 | FAULT
9 | Kawran Bazar Circuit-1 |  | 33 |  | BD001820 | 1 | 1924.77 | 1936.17 | 11.4 | 240000 |  | 2736000 | 2741463.4061 |  | 5781121.0774 | Kakrail 33/11 kv ss | -0.975 |  | Kawran Bazar Circuit-1 | 2741463.4061 | 2406190.4574 | 335272.9487 | 13.9338 | OK
10 | New Ramna Circuit-2 |  | 33 |  | BD001816 | 1 | 1259.49 | 1266.06 | 6.57 | 240000 |  | 1576800 | 1579948.6472 | [5 empty] | New Ramna Circuit-2 | 1579948.6472 | 1469779.3265 | 110169.3207 | 7.4956 | OK
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.91 | 462.91 | 0 | 240000 |  | 0 | 0 |  | 2741463.4061 | Kawran Bazar 33/11 kv ss | 0.60289 |  | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder |  | 33 |  | BD001840 | 1 | 484.37 | 493.4 | 9.03 | 240000 |  | 2167200 | 2171527.5927 | [5 empty] | DMC Hospital Feeder | 2171527.5927 | 2109338.4752 | 62189.1175 | 2.9483 | OK
15 | Green Road Circuit-2 (U/G) |  | 33 |  | BD001918 | 1 | 2225.57 | 2241.26 | 15.69 | 240000 |  | 3765600 | 3773119.372 |  | 2171527.5927 | DMC Hospital 33/11 kv ss | -0.045279 |  | Green Road Circuit-2 (U/G) | 3773119.372 | 3644280.4319 | 128838.9401 | 3.5354 | OK
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1732.79 | 1746.61 | 13.82 | 240000 |  | 3316800 | 3323423.1818 | [5 empty] | Kakrail Circuit-2 | 3323423.1818 | 4064217.3824 | -740794.2006 | -18.2272 | OK
18 | BSMMU Hospital Circuit-1 |  | 33 |  | BD001920 | 1 | 783.4 | 792.87 | 9.47 | 240000 |  | 2272800 | 2277338.461 |  | 9460453.5434 | Green Road 33/11 kv ss | 1.0943 |  | BSMMU Hospital Circuit-1 | 2277338.461 | 2111751.9059 | 165586.5551 | 7.8412 | OK
19 | Azimpur Circuit-1 |  | 33 |  | BD001822 | 1 | 2118.25 | 2144.4 | 26.15 | 240000 |  | 6276000 | 6288532.2867 | [5 empty] | Azimpur Circuit-1 | 6288532.2867 | 6475234.7012 | -186702.4145 | -2.8833 | OK
20 | Azimpur Circuit-2 |  | 33 |  | BD001857 | 0.95 | 1919.51 | 1933.54 | 14.03 | 240000 | From Downstream R Phase CT Problem | 4764231 | 4773744.4973 |  | 3061300.8035 | BSMMU 33/11 kv ss | 0.75438 |  | Azimpur Circuit-2 | 4773744.4973 | 5298807.8823 | -525063.385 | -9.9091 | OK
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 183.05 | 186.31 | 3.26 | 240000 |  | 782400 | 783962.3424 | [5 empty] | BSMMU Hospital Circuit-2 | 783962.3424 | 762644.1169 | 21318.2256 | 2.7953 | OK
23 | Green Road Circuit-1 |  | 33 |  | BD001865 | 1 | 1566.28 | 1589.93 | 23.65 | 240000 |  | 5676000 | 5687334.1714 |  | 11062276.784 | Azimpur 33/11 kv ss | 0.044131 |  | Green Road Circuit-1 | 5687334.1714 | 4916158.437 | 771175.7344 | 15.6866 | OK
26 | 33/0.4 kV, 500 kVA AT-1 |  | 0.4 |  | 84.2659 | 1 | 328945 | 330687 | 1742 | 10 |  | 17420 | 17454.7853 | Paribag |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 17454.7853 | 17708.5481 | -253.7628 | -1.433 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 |  | 0.4 |  | 84.2673 | 1 | 478776 | 478776 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total |  | 38578451 | 38655486.725 | [6 empty] | 38655486.725 | 37458587.1539 | 1196899.5711 | 3.1953 | OK
|  |  | 9=8-7: Grand Total | 46925568 | 46832051 | 46925568 | 0.19969
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming |  | 11 | IMPORT | DHK60884 | 1 | 87949.2 | 112188.24 | 24239.04 | 180 | 4363027.2 |  | 4404221.1612
16 | 33/11 kV Transformer-1 Incoming |  | 11 |  | DHK60976 | 1 | 683009.3 | 704285.42 | 21276.12 | 180 | 3829701.6 |  | 3865860.1138
|  |  | 7: 0; 8: 0; 10: Total | 8192728.8 |  | 8270081.275
| DHANMONDI 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 13260786 | 14063189 | 802403 | 1 |  | 802403 | 804443.5112 | Paribag |  |  |  |  | 11 kV Balaka Feeder | 804443.5112 | 777713.5417 | 26729.9696 | 3.437 | OK
5 | 11 kV Mogbazar O/H | C301M | 11 |  | HA021100463-02 | 1 | 55207202 | 56128592 | 921390 | 1 |  | 921390 | 923733.0952 | Paribag |  |  |  |  | 11 kV Mogbazar O/H | 923733.0952 | 815231.6219 | 108501.4733 | 13.3093 | OK
6 | 11 kV Panthopath Feeder | C3011 | 11 |  | HA021101078-02 | 1 | 69217222 | 69991075 | 773853 | 1 |  | 773853 | 775820.9086 | Paribag |  |  |  |  | 11 kV Panthopath Feeder | 775820.9086 | 712701.4188 | 63119.4898 | 8.8564 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 |  | DHK60882 | 1 | 251184 | 255718.75 | 4534.75 | 60 |  | 272085 | 272776.9123 | Paribag |  |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 272776.9123 | 251395.7292 | 21381.183 | 8.505 | OK
8 | 11 kV P G Hospital Feeder | C301P | 11 |  | DHK60889 | 1 | 301747.2 | 304740.12 | 2992.92 | 60 |  | 179575.2 | 180031.8598 | Paribag |  |  |  |  | 11 kV P G Hospital Feeder | 180031.8598 | 159901.6429 | 20130.217 | 12.5891 | OK
9 | 11 kV Abdul Monem Ltd |  | 11 |  | DHK60890 | 1 | 735.54 | 740.01 | 4.47 | 60000 |  | 268200 | 268882.0327 | Paribag |  |  |  |  | 11 kV Abdul Monem Ltd | 268882.0327 | 260024.3032 | 8857.7296 | 3.4065 | OK
10 | 11 kV Surjasen Hall Feeder | D301H | 11 |  | DHK60880 | 1 | 588760.2 | 593555.75 | 4795.55 | 60 |  | 287733 | 288464.7052 | Ramna |  |  |  |  | 11 kV Surjasen Hall Feeder | 288464.7052 | 228081.8293 | 60382.8759 | 26.4742 | OK
11 | 11 kV Azimpur-1 Feeder |  | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | D301U | 11 |  | DHK60873 | 1 | 974895.6 | 980153 | 5257.4 | 60 |  | 315444 | 316246.1742 | Ramna |  |  |  |  | 11 kV TSC Feeder | 316246.1742 | 313692.1099 | 2554.0643 | 0.81419 | OK
13 | 11 kV SCADA Bhaban | C301S | 11 |  | DHK60883 | 1 | 29299.7 | 29463.27 | 163.57 | 60 |  | 9814.2 | 9839.1575 | Paribag |  |  |  |  | 11 kV SCADA Bhaban | 9839.1575 | 9698.3018 | 140.8557 | 1.4524 | OK
14 | 11 kV DPH Sw/S-2 |  | 11 |  | DHK60871 | 1 | 585029.6 | 595526.6 | 10497 | 60 |  | 629820 | 631421.6326 | Paribag |  |  |  |  | 11 kV DPH Sw/S-2 | 631421.6326 | 629010.2788 | 2411.3538 | 0.38336 | OK
17 | 11 kV New Elephant Road Feeder | C301E | 11 |  | DHK60981 | 1 | 163626.2 | 174019 | 10392.8 | 60 |  | 623568 | 625153.7337 | Paribag |  |  |  |  | 11 kV New Elephant Road Feeder | 625153.7337 | 548154.2099 | 76999.5238 | 14.0471 | OK
18 | 11 kV Dhanmondi O/H Feeder | C301D | 11 |  | DHK61110 | 1 | 533225.9 | 548723 | 15497.1 | 60 |  | 929826 | 932190.548 | Paribag |  |  |  |  | 11 kV Dhanmondi O/H Feeder | 932190.548 | 864774.9192 | 67415.6288 | 7.7957 | OK
19 | 11 kV Sonargaon Feeder |  | 11 |  | DHK61115 | 1 | 483056.9 | 500073.3 | 17016.4 | 60 |  | 1020984 | 1023580.3628 | Paribag |  |  |  |  | 11 kV Sonargaon Feeder | 1023580.3628 | 935291.696 | 88288.6668 | 9.4397 | OK
20 | 11 kV Museum Feeder | D301M | 11 |  | DHK61107 | 1 | 558125.1 | 559437.2 | 1312.1 | 60 |  | 78726 | 78926.2003 | Ramna |  |  |  |  | 11 kV Museum Feeder | 78926.2003 | 57105.5699 | 21820.6303 | 38.211 | OK
21 | 11 kV Shanta property |  | 11 |  | DHK61112 | 1 | 358275 | 360035.74 | 1760.74 | 60 |  | 105644.4 | 105913.0538 | Paribag |  |  |  |  | 11 kV Shanta property | 105913.0538 | 118304.4062 | -12391.3524 | -10.4741 | OK
22 | 11 kV BIRDEM RMU Feeder | C601R | 11 |  | DHK61108 | 1 | 771587.6 | 779424.2 | 7836.6 | 60 |  | 470196 | 471391.7087 | Kakrail |  |  |  |  | 11 kV BIRDEM RMU Feeder | 471391.7087 | 406645.9606 | 64745.748 | 15.9219 | OK
23 | 11 kV Azimpur-2 Feeder |  | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 |  | 11 |  | DHK60978 | 1 | 856428.3 | 865759 | 9330.7 | 60 |  | 559842 | 561265.6785 | Kakrail |  |  |  |  | 11 kV DPH Sw/S-1 | 561265.6785 | 497685.3068 | 63580.3717 | 12.7752 | OK
|  |  | 10: Total | 8270081.275 | 8249103.8 | 8270081.275 | 0.2543
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Paribag at 33 KV level |  |  | 6571241.5935
[7 empty] | Azimpur at 33 KV level |  |  | 0
[7 empty] | Ramna at 33 KV level |  |  | 683637.0797
[7 empty] | Kakrail at 33 KV level |  |  | 1032657.3871
|  |  | 7: Total =; 10: 8287536.0603 | 2.874e-10
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 |  | 33 | 0 | BD001820 | 1 | 1924.77 | 1936.17 | 11.4 | 240000 | 0 | 2736000 | 2741463.4061
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.91 | 462.91 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 2736000 | 2741463.4061
MOGBAZAR 33 KV SIDE
17 | 33KV Karwan Bazar |  | 33 | 0 | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAWRANBAZAR 33 KV SIDE (RECEIVING) | [10 empty] | 2736000 | 2741463.4061
1 | 33 kV Dhanmondi Circuit-1 |  | 33 |  | DHK61036 | 1 | 3493.23 | 3503.41 | 10.18 | 270000 | 2748600
5 | 33 kV Dhanmondi Circuit-2 |  | 33 |  | DHK61037 | 1 | 1157.47 | 1157.47 | 0 | 270000 | 0
4 | 33 kV Moghbazar |  | 33 |  | DHK 61038 | 1 | 1061.95 | 1061.95 | 0 | 270000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 2748600 | 0 | 2741463.4061
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | DHK61039 | 1 | 5248 | 5263.24 | 15.24 | 180000 |  | 2743200
3 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 2743200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4: 2741463.4061; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 2741463.4061
| MOGBAZAR 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 2741463.4061 | 33 KV TX HV SIDE |  | 2743200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -1736.5939
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.06335%
| TOTAL IMPORT |  | 4: 2741463.4061
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK00182 | 1 | 16052 | 16321.6 | 269.6 | 10000 | 2696000 |  | 2741463.4061
15 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 2696000 | 2743200 | 2741463.4061
| KAWRANBAZAR 11 KV SIDE |  | 7: 0; 8: 0
6 | WASA Bhaban | C605M | 11 |  | 8536188 | 1.5 | 271216 | 271216 | 0 | 1000 | 808320 | 808320 | 813193.2995 | Shere b.nagar | From Customer End | 90 |  |  | WASA Bhaban | 813193.2995 | 837708.0289 | -24514.7294 | -2.9264 | OK
7 | Sangsad Bhaban |  | 11 |  | 8536178 | 1.5 | 588513 | 589987 | 1474 | 44 |  | 97284 | 97870.5178 | Shere b.nagar |  | 30 | 5 | 80 | Sangsad Bhaban | 97870.5178 | 66551.249 | 31319.2688 | 47.0604 | FAULT
8 | Air Port Road (West) | D505A | 11 |  | 8536182 | 1.5 | 5221.7 | 5498.5 | 276.8 | 1000 |  | 415200 | 417703.2091 | Shere b.nagar |  | 60 | 30 | 90 | Air Port Road (West) | 417703.2091 | 326379.7515 | 91323.4576 | 27.9807 | OK
9 | ICC (PM Office) | C172C | 11 |  | 8536193 | 1.5 | 32437.1 | 32438.3 | 1.2 | 1000 |  | 1800 | 1810.8521 | Shere b.nagar |  | 20 |  |  | ICC (PM Office) | 1810.8521 | 0 | 1810.8521 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | D505U | 11 |  | DHK00183 | 1.5 | 18819.3 | 19208.7 | 389.4 | 444.44 |  | 259597.404 | 261162.4969 | Shere b.nagar |  | 50 |  |  | (UTC) Tower | 261162.4969 | 218658.8156 | 42503.6813 | 19.4384 | OK
11 | Sonargaon Hotel | C605O | 11 |  | 8536190 | 1.5 | 51744.1 | 51744.1 | 0 | 1000 | 15 | 147136.5 | 148023.5747 | Kakrail | Estimated |  |  |  | Sonargaon Hotel | 148023.5747 | 29643.4409 | 118380.1338 | 399.3468 | FAULT
12 | Panthopath | D505P | 11 |  | 8536184 | 1.5 | 40118.8 | 40657.8 | 539 | 1000 |  | 808500 | 813374.3847 | Shere b.nagar |  |  |  |  | Panthopath | 813374.3847 | 750824.5302 | 62549.8545 | 8.3308 | OK
13 | Titas Bhaban | C605N | 11 |  | DHK00190 | 1.5 | 58023.1 | 58301.4 | 278.3 | 444.44 |  | 185531.478 | 186650.0331 | Kakrail |  |  |  |  | Titas Bhaban | 186650.0331 | 174671.861 | 11978.1721 | 6.8575 | OK
16 | Green Road Dormatory s/s |  | 11 |  | DHK00021 | 1.5 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | [5 empty] | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 |  | 11 |  | 85-12906 | 1.5 | 69663 | 69774 | 111 | 10 |  | 1665 | 1675.0382 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-1 | 1675.0382 | 1752.7801 | -77.742 | -4.4354 | OK
27 | Aux. Transformer, AT-2 |  | 11 |  | 85-12909 | 1.5 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 2741463.4061 | 2725034.382 | 2741463.4061 | 0.60289
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail at 33 KV level |  |  | 334673.6078
[6 empty] | Shere b.nagar at 33 KV level |  |  | 2406789.7983
[6 empty] | Total = |  |  | 2741463.4061 | 0
|  |  | 9=8-7: Customer Name; 10: Customer Number | Feeder name | Consumption | OMF
|  |  | 9=8-7: Square Hospital; 10: 27529489 | Wasa Bhaban | 808320 | 6000
|  |  | 9=8-7: NOCS Name; 10: Previous Total | Present Total
|  |  | 9=8-7: ShereBangla Nagar; 10: 4448.88 | 4583.6
|  |  | 10: prev | 3189.91 | 1258.97 | 4448.88 |  | 134.72
|  |  | 10: present | 3285.75 | 1297.85 | 4583.6 |  | 808320
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 |  | 33 | 0 | BD001919 | 1 | 1550.75 | 1562.31 | 11.56 | 240000 | 0 | 2774400 | 2779940.0855
10 | New Ramna Circuit-2 |  | 33 | 0 | BD001816 | 1 | 1259.49 | 1266.06 | 6.57 | 240000 | 0 | 1576800 | 1579948.6472
|  |  | 10: Total | 0 | 4351200 | 4359888.7326
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1058400 | 1060171.869
|  |  | 10: Total | 0 | 1058400 | 1060171.869
| NEW RAMNA 33 KV SIDE (RECEIVING) | [10 empty] | 5409600 | 5420060.6016
|  |  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 10: Total |  | 0 | 5420060.6016
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 9=8-7: 0 |  | 0
| Feeder No.2 |  | 3: 33; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.3. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 5420060.6016 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 4359888.7326; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5420060.6016
| NARINDA 33 KV SIDE |  | 4: 1060171.869; 6: 33 KV NET IMPORT; 9=8-7: 5420060.6016 | 33 KV TX HV SIDE |  | 5420060.6016
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 5420060.6016
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK 00002 | 1 | 27294.9 | 27568.9 | 274 | 10000 | 2740000 |  | 2770495.8675
15 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK 00007 | 1 | 15143.9 | 15300.1 | 156.2 | 10000 | 1562000 |  | 1579384.8705
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming |  | 11 |  | DHKA2182 | 3 | 633.03 | 634.99 | 1.96 | 180000 | 1058400 |  | 1070179.8636 |  | PT Missing
|  |  | 7: 0; 8: 0; 10: Total | 5360400 |  | 5420060.6016
| NEW RAMNA 11 KV SIDE |  | 7: 0; 8: 0
4 | Police Bhaban | D315I | 11 | T-1 | DHK 00005 | 1 | 74685.2 | 74867.5 | 182.3 | 444.44 |  | 81021.412 | 82339.6968 | Ramna |  |  |  |  | Police Bhaban | 82339.6968 | 74128.9984 | 8210.6985 | 11.0762 | OK
5 | Baitul Mukarram (OLD Water Works) |  | 11 | T-1 | DHK 00010 | 1 | 17727 | 17727.5 | 0.5 | 444.44 |  | 222.22 | 225.8357 | Ramna |  |  |  |  | Baitul Mukarram (OLD Water Works) | 225.8357 | 862.4929 | -636.6572 | -73.8159 | CHECK
6 | GPO | D3157 | 11 | T-1 | DHK 00060 | 1 | 1497.4 | 1929.2 | 431.8 | 444.44 |  | 191909.192 | 195031.712 | Ramna |  |  |  |  | GPO | 195031.712 | 162829.588 | 32202.124 | 19.7766 | OK
7 | Culvert Road | D315C | 11 | T-1 | 8536184 | 1 | 40701.5 | 40858.8 | 157.3 | 444.44 | 277980.176 | 277980.176 | 282503.1415 | Ramna | T-1 - (Sum of All feeders Under T-1) |  |  |  | Culvert Road | 282503.1415 | 230311.946 | 52191.1956 | 22.6611 | OK
8 | Secretariat (East) | D315E | 11 | T-1 | DHK00059 | 1 | 81752.7 | 81753.2 | 0.5 | 444.44 |  | 222.22 | 225.8357 | Ramna |  |  |  |  | Secretariat (East) | 225.8357 | 771.7042 | -545.8685 | -70.7355 | CHECK
9 | Siddik Bazar | B615S | 11 | T-1 | DHK00076 | 1 | 50249.5 | 52733.6 | 2484.1 | 444.44 |  | 1104033.404 | 1121996.9333 | Bangshal |  |  |  |  | Siddik Bazar | 1121996.9333 | 1067811.6528 | 54185.2805 | 5.0744 | OK
10 | Bokshi Bazar | D315X | 11 | T-1 | DHK 00206 | 1 | 93252.6 | 94143.4 | 890.8 | 444.44 |  | 395907.152 | 402348.8862 | Ramna |  |  |  |  | Bokshi Bazar | 402348.8862 | 372869.3158 | 29479.5704 | 7.9061 | OK
11 | Ramna 11 kV Sw/S Circuit-1 |  | 11 | T-1 | DHK00198 | 1 | 52687 | 53404 | 717 | 444.44 |  | 318663.48 | 323848.3963 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 323848.3963 | 334329.4998 | -10481.1035 | -3.135 | OK
12 | TNT RMU | D315Z | 11 | T-1 | DHK 00207 | 1 | 66649.9 | 67482.5 | 832.6 | 444.44 |  | 370040.744 | 376061.6105 | Ramna |  |  |  |  | TNT RMU | 376061.6105 | 389211.2873 | -13149.6768 | -3.3785 | OK
13 | DIT 11 kV Sw/S Circuit-1 |  | 11 | T-1 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | D315W | 11 | T-2 | DHK 00006 | 1.5 | 73641.9 | 73876.7 | 234.8 | 444.44 |  | 156531.768 | 159078.6683 | Ramna | CF=1.5 is Considered due to PT problem |  |  |  | Secretariat (West) | 159078.6683 | 161785.5176 | -2706.8493 | -1.6731 | OK
17 | Ramna 11 kV Sw/S Circuit-2 |  | 11 | T-2 | DHK00197 | 1.5 | 89267.5 | 89269.4 | 1.9 | 444.44 |  | 1266.654 | 1287.2635 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 1287.2635 | 1429.9225 | -142.659 | -9.9767 | OK
18 | Sayed Nazrul Islam Road | D315A | 11 | T-2 | DHK00186 | 1.5 | 41257.6 | 42745.5 | 1487.9 | 444.44 |  | 991923.414 | 1008062.8218 | Ramna |  |  |  |  | Sayed Nazrul Islam Road | 1008062.8218 | 950626.099 | 57436.7227 | 6.042 | OK
19 | Gulistan Complex | D3153 | 11 | T-2 | DHK00030 | 1.5 | 57286.7 | 57543.4 | 256.7 | 444.44 |  | 171131.622 | 173916.0739 | Ramna |  |  |  |  | Gulistan Complex | 173916.0739 | 132506.152 | 41409.9219 | 31.2513 | OK
20 | Mohanagor Nattomanso | D3152 | 11 | T-2 | DHK 00008 | 1.5 | 649.9 | 689.2 | 39.3 | 444.44 |  | 26199.738 | 26626.0292 | Ramna |  |  |  |  | Mohanagor Nattomanso | 26626.0292 | 23287.3094 | 3338.7199 | 14.3371 | OK
21 | DIT 11 kV Sw/S Circuit-2 |  | 11 | T-2 | DHK00196 | 1.5 | 30367 | 30641.4 | 274.4 | 444.44 |  | 182931.504 | 185907.9497 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-2 | 185907.9497 | 175403.8272 | 10504.1225 | 5.9885 | OK
22 | Jail | B678Z | 11 | T-2 | DHK00009 | 1.5 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | D315K | 11 | T-3 | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 |  | 0 | 0 | Ramna | T-3 - (Sum of All feeder Under T-3) |  |  |  | Kosturi Bazar | 0 | 29524.1095 | -29524.1095 | -100 | CHECK
24 | Kaptan Bazar | B124K | 11 | T-3 | HA021101251-02 | 1 | 8893370 | 9141543 | 248173 | 1 |  | 248173 | 252210.9783 | Narinda |  |  |  |  | Kaptan Bazar | 252210.9783 | 333271.2853 | -81060.3069 | -24.3226 | OK
25 | G.T.V | D315G | 11 | T-3 | HA-021101054-02 | 1 | 74683932 | 75024680 | 340748 | 1 |  | 340748 | 346292.2495 | Ramna |  |  |  |  | G.T.V | 346292.2495 | 354527.2958 | -8235.0463 | -2.3228 | OK
26 | Kazi Alauddin Road | B615K | 11 | T-3 | HA021100951-02 | 1 | 8786027 | 9258275 | 472248 | 1 |  | 472248 | 479931.8624 | Bangshal |  |  |  |  | Kazi Alauddin Road | 479931.8624 | 330616.7097 | 149315.1527 | 45.1626 | FAULT
28 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.4 | T-3 | 2436 | 1 | 68252 | 68252 | 0 | 10 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.4 | T-3 | 2437 | 1 | 90090 | 90303 | 213 | 10 |  | 2130 | 2164.6568 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 2164.6568 | 827.3206 | 1337.3363 | 161.6467 | FAULT
|  |  | 10: Grand Total | 5420060.6016 | 5333283.7 | 5420060.6016 | 1.6271
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 3380012.8779
[6 empty] | Lalbag | at 33 KV level
[6 empty] | Bangshal | at 33 KV level |  | 1601928.7957
[6 empty] | Motijheel | at 33 KV level |  | 185907.9497
[6 empty] | Narinda | at 33 KV level |  | 252210.9783
[6 empty] | Total = |  |  | 5420060.6016 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 |  | 33 | 0 | BD001825 | 1 | 913.91 | 924.13 | 10.22 | 240000 | 0 | 2452800 | 2457697.8956
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1732.79 | 1746.61 | 13.82 | 240000 | 0 | 3316800 | 3323423.1818
|  |  | 10: Total | 0 | 5769600 | 5781121.0774
ULLON 33 KV SIDE
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder.(import) |  | 33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAKRAIL 33 KV SIDE (RECEIVING) | [10 empty] | 5769600 | 5781121.0774
5 | 33 kV Dhanmondi-2 |  | 33 |  | 06604376 | 1 | 5445.65 | 5464.15 | 18.5 | 180000 | 3330000
2 | 33 kV Dhanmondi-1 |  | 33 |  | 06604375 | 1 | 2131.43 | 2138.4 | 6.97 | 180000 | 1254600
| 33 KV Kakrail From ULLON |  | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola |  | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
|  |  | 8: 0; 10: Total | 4584600
| KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| KAKRAIL 33 KV SIDE |  | 8: 0
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 |  | 0 | 0 |  |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 8: 0; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 4: 5781121.0774; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KAKRAIL 33 KV NET IMPORT |  | 5781121.0774
| ULLON 33 KV SIDE |  | 4: 0; 6: KAKRAIL 33 KV NET IMPORT; 9=8-7: 5781121.0774 | KAKRAIL KV NET IMPORT |  | 5788445.168
| Taltola 33 KV SIDE |  | 4: 0 | LOSS UNITS=> |  | -7324.0906
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.1267%
| TOTAL IMPORT |  | 4: 5781121.0774
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK00017 | 1 | 21327.6 | 21603.1 | 275.5 | 8888.89 | 2448889.195 |  | 2445790.6278
15 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK00018 | 1 | 8900.3 | 9276 | 375.7 | 8888.89 | 3339555.973 |  | 3335330.4496
|  |  | 7: 0; 8: 0; 10: Total | 5788445.168 |  | 5781121.0774
| KAKRAIL 11 KV SIDE |  | 7: 0; 8: 0
7 | Pioneer | D304P | 11 |  | 06604395 | 1 | 24342.07 | 24396.51 | 54.44 | 8000 |  | 435520 | 431273.701 | Ramna |  |  |  |  | Pioneer | 431273.701 | 423219.6512 | 8054.0498 | 1.903 | OK
8 | Pir Saheber Goli | D604L | 11 |  | DHK-00102 | 1 | 98876.5 | 100672.6 | 1796.1 | 444.444 |  | 798265.8684 | 790482.8147 | Rajarbag |  |  |  |  | Pir Saheber Goli | 790482.8147 | 772549.4723 | 17933.3423 | 2.3213 | OK
9 | Montri Para | C604B | 11 |  | DHK-00110 | 1 | 13080.9 | 13130.4 | 49.5 | 2222.22 |  | 109999.89 | 108927.3964 | Kakrail |  |  |  |  | Montri Para | 108927.3964 | 127068.5046 | -18141.1083 | -14.2766 | OK
10 | Baily Road 11 kV Sw/S-2 |  | 11 |  | 9119865 | 1 | 73065.6 | 73976.2 | 910.6 | 1000 |  | 910600 | 901721.6939 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-2 | 901721.6939 | 0 | 901721.6939 | #DIV/0! | #DIV/0!
11 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | D3046 | 11 |  | 1025651 | 1 | 30487.8 | 30689.4 | 201.6 | 1000 |  | 201600 | 199634.4097 | Ramna |  |  |  |  | High Court | 199634.4097 | 192022.3312 | 7612.0785 | 3.9642 | OK
13 | Secretaiat |  | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | D604N | 11 |  | 06604402 | 1 | 5852.63 | 5874.69 | 22.06 | 40000 |  | 882400 | 873796.6426 | Rajarbag |  |  |  |  | Shanti Nagar Bazar | 873796.6426 | 828920.0528 | 44876.5898 | 5.4139 | OK
17 | Tottho Bhovon |  | 11 |  | 9119867 | 1 | 33300.4 | 33421.3 | 120.9 | 1000 |  | 120900 | 119721.2308 | Kakrail |  |  |  |  | Tottho Bhovon | 119721.2308 | 114970.0758 | 4751.155 | 4.1325 | OK
18 | Central Police Hospital/ PNT (Circuit House) |  | 11 |  | DHK00199 | 1 | 80032.9 | 80210.4 | 177.5 | 2222.22 |  | 394444.05 | 390598.2395 | Kakrail |  |  |  |  | Central Police Hospital/ PNT (Circuit House) | 390598.2395 | 405763.0795 | -15164.84 | -3.7374 | OK
19 | Baily Road 11 kV Sw/S-1 |  | 11 |  | DHK00027 | 1 | 60175.9 | 60723.6 | 547.7 | 2222.22 |  | 1217109.894 | 1205243.1312 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-1 | 1205243.1312 | 2022056.4346 | -816813.3034 | -40.3952 | CHECK
20 | Bijoy Nagar | D304B | 11 |  | D1025656 | 1 | 71704.2 | 72297.5 | 593.3 | 1000 |  | 593300 | 587515.3536 | Ramna |  |  |  |  | Bijoy Nagar | 587515.3536 | 527301.0267 | 60214.3269 | 11.4193 | OK
21 | Shilpakala Academy | D304F | 11 |  | D0086137 | 1 | 28206.8 | 28310 | 103.2 | 1000 |  | 103200 | 102193.805 | Ramna |  |  |  |  | Shilpakala Academy | 102193.805 | 123080.8395 | -20887.0346 | -16.9702 | OK
22 | Judges Complex | C604JC | 11 |  | 06604344 | 1 | 690.43 | 692.15 | 1.72 | 40000 |  | 68800 | 68129.2033 | Kakrail |  |  |  |  | Judges Complex | 68129.2033 | 88001.7864 | -19872.5831 | -22.582 | OK
23 | Auxiliary Transformer, AT-1 |  | 11 |  | 39333 | 1 | 499707 | 499707 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Auxiliary Transformer, AT-2 |  | 11 |  | 39254 | 1 | 1235419 | 1237321 | 1902 | 1 |  | 1902 | 1883.4556 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-2 | 1883.4556 | 3167.2532 | -1283.7976 | -40.5335 | CHECK
|  |  | 10: Grand Total | 5781121.0774 | 5838041.7024 | 5781121.0774 | -0.975
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1320617.2693
[6 empty] | Rajarbag | at 33 KV level |  | 1664279.4572
[6 empty] | Kakrail | at 33 KV level |  | 2796224.3508
[6 empty] | Total = |  |  | 5781121.0774 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 |  | 33 | 0 | BD001920 | 1 | 783.4 | 792.87 | 9.47 | 240000 | 0 | 2272800 | 2277338.461
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 183.05 | 186.31 | 3.26 | 240000 | 0 | 782400 | 783962.3424
|  |  | 10: Total |  | 3055200 | 3061300.8035 | 0.19969
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 |  | 33 |  | BD017073 | 1 | 85250.13 | 87521.34 | 2271.21 | 1000 | 2271210
4 | 33 kV Dhanmondi Incoming Circuit-2 |  | 33 |  | BD017074 | 1 | 43875.2 | 44168.47 | 293.27 | 1000 | 293270
| 33 KV Ullon-1 Feeder |  | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 2564480 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0 |  | Total
[7 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017072 | 1 | 16311.89 | 18875.18 | 2563.29 | 888.89 |  | 2278482.8481
6 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017076 | 1 | 42242.09 | 43121.64 | 879.55 | 888.89 |  | 781823.1995
|  |  | 10: Total |  | 3060306.0476
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 3061300.8035; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3061300.8035
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 3061300.8035 | 33/11 KV XF HV SIDE |  | 3060306.0476
[11 empty] | LOSS UNITS=> |  | 994.7559
[11 empty] | LOSS % IN => |  | 0.03249%
| TOTAL IMPORT |  | 4: 3061300.8035
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD017081 | 1 | 90976.61 | 93235.93 | 2259.32 | 1000 | 2259320 |  | 2282636.8489
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD017082 | 1 | 36585.59 | 37356.3 | 770.71 | 1000 | 770710 |  | 778663.9546
|  |  | 7: 0; 8: 0; 10: Total | 3030030 |  | 3061300.8035
| BSMMU HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Jamuna (F1) | C6101JG | 11 |  | BD017073 | 1 | 0.4408 | 0.4517 | 0.0109 | 2000 |  | 21.8 | 21.9645 | Kakrail |  |  |  |  | 11 kV Jamuna (F1) | 21.9645 | 24.3781 | -2.4137 | -9.9009 | OK
9 | 11 kV Pukur Par (F2) | C6101PP | 11 |  | BD017074 | 1 | 3047.06 | 3065.02 | 17.96 | 2000 |  | 35920 | 36190.9742 | Kakrail |  |  |  |  | 11 kV Pukur Par (F2) | 36190.9742 | 38781.503 | -2590.5288 | -6.6798 | OK
10 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 |  | BD017075 | 1 | 1915.81 | 1950.68 | 34.87 | 2000 |  | 69740 | 70266.1063 | Kakrail |  |  |  |  | 11 kV BSMMU Convention center (F3) | 70266.1063 | 29253.7267 | 41012.3796 | 140.1954 | FAULT
11 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 |  | BD017076 | 1 | 3438.44 | 3484.18 | 45.74 | 2000 |  | 91480 | 92170.109 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 92170.109 | 80203.9675 | 11966.1416 | 14.9196 | OK
12 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 |  | BD017077 | 1 | 16013.45 | 16195.5 | 182.05 | 2000 |  | 364100 | 366846.7064 | Kakrail |  |  |  |  | 11 kV Holi Family Feeder (F5) | 366846.7064 | 389724.6483 | -22877.9419 | -5.8703 | OK
13 | 11 kV Navy House Feeder (F6) | C6101NH | 11 |  | BD017078 | 1 | 28368.92 | 28693.65 | 324.73 | 2000 |  | 649460 | 654359.4121 | Kakrail |  |  |  |  | 11 kV Navy House Feeder (F6) | 654359.4121 | 572316.6594 | 82042.7528 | 14.3352 | OK
14 | 11 kV Paribagh Feeder (F7) | C31016 | 11 |  | BD017079 | 1 | 35705.62 | 36132.95 | 427.33 | 2000 |  | 854660 | 861107.4049 | Paribag |  |  |  |  | 11 kV Paribagh Feeder (F7) | 861107.4049 | 847037.5945 | 14069.8104 | 1.6611 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 |  | BD017080 | 1 | 7316.36 | 7404.3 | 87.94 | 2000 |  | 175880 | 177206.8078 | Paribag |  |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 177206.8078 | 149722.1986 | 27484.6092 | 18.3571 | OK
18 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 |  | BD017083 | 1 | 2648.04 | 2692.86 | 44.82 | 2000 |  | 89640 | 90316.2284 | Paribag |  |  |  |  | 11 kV Oncology Bhaban (F9) | 90316.2284 | 86501.6447 | 3814.5837 | 4.4098 | OK
19 | Rupayan Trade Center | C6101RT | 11 |  | BD017084 | 1 | 1866.59 | 1944.89 | 78.3 | 2000 |  | 156600 | 157781.3629 | Kakrail |  |  |  |  | Rupayan Trade Center | 157781.3629 | 131702.7156 | 26078.6473 | 19.8011 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 |  | BD017085 | 1 | 2416.46 | 2457.04 | 40.58 | 2000 |  | 81160 | 81772.2568 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 81772.2568 | 99300.1502 | -17527.8934 | -17.6514 | OK
21 | 11 kV BSMMU RMU (F12) | C3101RM | 11 |  | BD017086 | 1 | 2411.95 | 2414.12 | 2.17 | 2000 |  | 4340 | 4372.7402 | Paribag |  |  |  |  | 11 kV BSMMU RMU (F12) | 4372.7402 | 60.9453 | 4311.7949 | 7074.8646 | FAULT
22 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 |  | BD017087 | 1 | 4705.28 | 4762.51 | 57.23 | 2000 |  | 114460 | 115323.4661 | Paribag |  |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 115323.4661 | 98751.6428 | 16571.8233 | 16.7813 | OK
23 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 |  | BD017088 | 1 | 1173.86 | 1189.09 | 15.23 | 2000 |  | 30460 | 30689.7849 | Paribag |  |  |  |  | 11 kV BCS Academy RMU (F14) | 30689.7849 | 29233.4116 | 1456.3732 | 4.9819 | OK
24 | Spare |  | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | C310113 | 11 |  | BD017090 | 1 | 2714.45 | 2870.38 | 155.93 | 2000 |  | 311860 | 314212.6171 | Paribag |  |  |  |  | BSMMU Super Specialist Hospital RMU | 314212.6171 | 313055.5062 | 1157.1109 | 0.36962 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKD4418 | 1 | 3207.96 | 3293.94 | 85.98 | 100 |  | 8598 | 8662.8618 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 8662.8618 | 8725.3303 | -62.4685 | -0.71594 | OK
27 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 1919.42 | 1919.42 | 0 | 100 |  | 0 | 0 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3061300.8035 | 3038379.8 | 3061300.8035 | 0.75438
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 1459408.8922
[6 empty] | Paribag | at 33 KV level |  | 1601891.9112
[6 empty] | Total = |  |  | 3061300.8035 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 |  | 132 |  | 8993518 | 1 | 0 | 11.816 | 11.816 | 960000 | 0 | 15494400
|  |  | 132 |  |  | 1 | 0.428 | 2.59 | 2.162 | 960000 | 2075520 | 0
3 | Kallyanpur to Lalbagh 2 |  | 132 |  | 5014660 | 1 | 393.184 | 408.474 | 15.29 | 960000 | 0 | 14678400
|  |  | 132 |  |  | 1 | 4.408 | 4.408 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 |  | 132 |  | 38992597 | 1 | 805.688 | 833.164 | 27.476 | 1440000 | 0 | 39565440
|  |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 2075520 | 69738240
|  |  | 10: Net Total | 67662720
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 |  | 132 | RECEIVE | 6604452 | 1 | 365858 | 378801 | 12943 | 1000 | 12943000
|  |  | 132 |  |  | 1 | 6797 | 6797 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) |  | 132 |  |  | 1 | 4661033 | 4700536 | 39503 | 1000 | 39503000
|  |  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar |  | 132 |  |  | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  |  | 1 | 695522 | 722099 | 26577 | 1000 |  | 26577000
| Kallyanpur-2 |  | 132 |  | 6604428 | 1 | 462652 | 476529 | 13877 | 1000 | 13877000
|  |  | 132 |  |  | 1 | 7156 | 7157 | 1 | 1000 |  | 1000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 66323000 | 26578000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 39745000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
6 | Kamrangirchar |  | 132 |  | SIEM491 | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  | SIEM491 | 1 | 695522 | 722099 | 26577 | 1000 | From Kamrangirchar | 26332800
|  |  | 7: 0; 8: 0; 10: Total |  | 26332800
| LALBAGH 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 | NET IMPORT | SIEM494 | 1 | 2338117 | 2357713 | 19596 | 1000 |  | 19596000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | SIEM499 | 1 | 2449415 | 2469576 | 20161 | 1000 |  | 20161000
|  |  | 10: Total | 66334000 | 39757000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 67662720; 6: EXPORT TO OTHER S/S; 9=8-7: 26332800 | 132 KV NET IMPORT |  | 41329920
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 41329920 | 132/33 KV GT LV SIDE |  | 39728000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1601920
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 3.876%
| 132 KV TOTAL IMPORT |  | 4: 67662720
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | SIEM0517 | 1 | 2337256 | 2356815 | 19559 | 1000 | 19559000
16 | 132/33 kV GT-2 Incoming (LV) |  | 33 |  | SIEM0518 | 1 | 2423522 | 2443691 | 20169 | 1000 | 20169000
|  |  | 7: 0; 8: 0; 10: Total | 39728000 |  | 0
| LALBAGH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SIEM0502 | 1 | 874827 | 880700 | 5873 | 2000 |  | 11746000 | 11753617.6912 |  | 23521244.4618 | Lalbagh New 33/11 kv ss | 0.545 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 11753617.6912 | 11860281.0892 | -106663.398 | -0.89933 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SIEM0501 | 1 | 868718 | 874598 | 5880 | 2000 |  | 11760000 | 11767626.7706 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 11767626.7706 | 11874295.6009 | -106668.8303 | -0.89832 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 23506000 | 23521244.4618 | [5 empty] | 33 KV Feeders | 23521244.4618 | 23734576.6901 | -213332.2283 | -0.89882 | OK
9 | Spare |  | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 7058574.7653 | Mitford 33/11 kv ss | 1.8768 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 |  | 33 |  | SIEM0513 | 1 | 332029 | 334522 | 2493 | 2000 |  | 4986000 | 4989233.5951 | [5 empty] | Mitford Circuit-1 | 4989233.5951 | 2947051.6143 | 2042181.9808 | 69.2958 | FAULT
12 | Azimpur Circuit-1 |  | 33 |  | SIEM0503 | 1 | 77848 | 77848 | 0 | 2000 |  | 0 | 0 |  | 0 | Azimpur 33/11 kv ss | 0.044131 |  | Azimpur Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Azimpur Circuit-2 |  | 33 |  | SIEM0507 | 1 | 91043 | 91043 | 0 | 2000 |  | 0 | 0 | [5 empty] | Azimpur Circuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Lalbagh old |  | 33 |  | SIEM0509 | 1 | 254423 | 258951 | 4528 | 2000 |  | 9056000 | 9061873.1322 |  | 9061873.1322 | Lalbagh old 33/11 kv ss | 1.101 |  | Lalbagh old | 9061873.1322 | 9187513.4906 | -125640.3584 | -1.3675 | OK
18 | Mitford Circuit-2 |  | 33 |  | SIEM0511 | 1 | 365758 | 366792 | 1034 | 2000 |  | 2068000 | 2069341.1702 | [5 empty] | Mitford Circuit-2 | 2069341.1702 | 870901.8018 | 1198439.3684 | 137.609 | FAULT
19 | 33/0.4 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKC7982 | 1 | 7737 | 7743.66 | 6.66 | 120 |  | 799.2 | 799.7183 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-1 | 799.7183 | 6956.4032 | -6156.6849 | -88.5039 | CHECK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHU02670 | 1 | 27106.6 | 27157 | 50.4 | 120 |  | 6048 | 6051.9223 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-2 | 6051.9223 | 0 | 6051.9223 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 16116847.2 | 16127299.5382 | [5 empty] | 0 | 16127299.5382 | 13012423.3099 | 3114876.2283 | 23.9377 | OK
|  |  | 9=8-7: Grand Total | 39648544 | 39622847.2 | 39648544 | 0.064853
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK98833 | 1 | 626229.4 | 632303.9 | 6074.5 | 2000 | 12149000 |  | 11761783.9842
11 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK98832 | 1 | 623112.5 | 629185.8 | 6073.3 | 2000 | 12146600 |  | 11759460.4776
|  |  | 7: 0; 8: 0; 10: Total | 24295600 |  | 23521244.4618
| LALBAGH 11 kV SIDE |  | 7: 0; 8: 0
3 | Chata Mosjid |  | 11 |  |  | 1 | 186386.5 | 188496.5 | 2110 | 1000 |  | 2110000 | 2121499.4576 | Kamrangirchar |  |  |  |  | Chata Mosjid | 2121499.4576 | 2104576.1621 | 16923.2955 | 0.80412 | OK
4 | AC mosjid | A3109X | 11 |  |  | 1 | 14088.621 | 15403.218 | 1314.597 | 1000 |  | 1314597 | 1321761.5272 | Lalbag |  |  |  |  | AC mosjid | 1321761.5272 | 1444428.2322 | -122666.705 | -8.4924 | OK
5 | Kazi Reaz Uddin Road | A3109K | 11 |  |  | 1 | 3815.7512 | 5901.9428 | 2086.1916 | 1000 |  | 2086191.6 | 2097561.3023 | Lalbag |  |  |  |  | Kazi Reaz Uddin Road | 2097561.3023 | 2053812.9926 | 43748.3097 | 2.1301 | OK
6 | Nazimuddin | A3109M | 11 |  |  | 1 | 8961.7128 | 9587.6336 | 625.9208 | 1000 |  | 625920.8 | 629332.0558 | Lalbag |  |  |  |  | Nazimuddin | 629332.0558 | 552316.6673 | 77015.3884 | 13.9441 | OK
7 | Kamal Bagh | A3109U | 11 |  |  | 1 | 2788.3572 | 4399.1324 | 1610.7752 | 1000 |  | 1610775.2 | 1619553.8925 | Lalbag |  |  |  |  | Kamal Bagh | 1619553.8925 | 1600011.3813 | 19542.5111 | 1.2214 | OK
8 | Rahamatganj | A3109B | 11 |  |  | 1 | 24671.398 | 26818.372 | 2146.974 | 1000 |  | 2146974 | 2158674.9651 | Lalbag |  |  |  |  | Rahamatganj | 2158674.9651 | 2182617.7764 | -23942.8112 | -1.097 | OK
9 | Water Works 11kV Sw/S-1 |  | 11 |  |  | 1 | 8925.3704 | 10419.22 | 1493.8496 | 1000 |  | 1493849.6 | 1501991.0503 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-1 | 1501991.0503 | 1492476.4844 | 9514.5659 | 0.6375 | OK
12 | City Colony | A3109J | 11 |  |  | 1 | 7217.068 | 9111.3624 | 1894.2944 | 1000 |  | 1894294.4 | 1904618.2664 | Lalbag |  |  |  |  | City Colony | 1904618.2664 | 1920551.3181 | -15933.0517 | -0.82961 | OK
13 | Water Works 11kV Sw/S-2 |  | 11 |  |  | 1 | 14394.01 | 16538.576 | 2144.566 | 1000 |  | 2144566 | 2156253.8416 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-2 | 2156253.8416 | 2167721.4514 | -11467.6098 | -0.52902 | OK
14 | Chun Goli | A3109H | 11 |  |  | 1 | 4256.7304 | 5262.686 | 1005.9556 | 1000 |  | 1005955.6 | 1011438.0378 | Lalbag |  |  |  |  | Chun Goli | 1011438.0378 | 860621.3663 | 150816.6715 | 17.5242 | OK
15 | Alir Ghat | A3109L | 11 |  |  | 1 | 133060.1 | 134991.2 | 1931.1 | 1000 |  | 1931100 | 1941624.4562 | Lalbag |  |  |  |  | Alir Ghat | 1941624.4562 | 1928077.5242 | 13546.932 | 0.70261 | OK
16 | Club Ghat | A3109C | 11 |  |  | 1 | 32758.904 | 35205.384 | 2446.48 | 1000 |  | 2446480 | 2459813.2668 | Lalbag |  |  |  |  | Club Ghat | 2459813.2668 | 2758945.8627 | -299132.5959 | -10.8423 | OK
17 | Debidas Ghat | A3109V | 11 |  |  | 1 | 9665.9152 | 12248.96 | 2583.0448 | 1000 |  | 2583044.8 | 2597122.3422 | Lalbag |  |  |  |  | Debidas Ghat | 2597122.3422 | 2668419.4712 | -71297.1289 | -2.6719 | OK
18 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 23521244.4618 | 23393749 | 23521244.4618 | 0.545
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 2121499.4576
[6 empty] | Lalbag | at 33 KV level |  | 21399745.0042
[6 empty] | Total = |  |  | 23521244.4618 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old |  | 33 | 0 | SIEM0509 | 1 | 254423 | 258951 | 4528 | 2000 | 0 | 9056000 | 9061873.1322
|  |  | 10: Total |  | 9056000 | 9061873.1322 | 0.064853
KAMRANGIRCHAR 33 KV SIDE
Total
| LALBAGH OLD 33 KV SIDE (RECEIVING) | [11 empty] | 9061873.1322
| 33 KV Lalbagh Incomming |  | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0 | 9061873.1322
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 4: 9061873.1322; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALBAGH OLD 33 KV NET IMPORT |  | 9061873.1322
|  |  | 6: LALBAGH OLD 33 KV NET IMPORT; 9=8-7: 9061873.1322 | 33 KV TX HV SIDE |  | 9061873.1322
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9061873.1322
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) |  | 11 |  | 8838010 | 1 | 88171.7 | 88171.7 | 0 | 1000 | 0 |  | 0
27 | 33/11 kV T1 Incoming (LV) |  | 11 |  | 06604426 | 1 | 36812.04 | 36961.45 | 149.41 | 16000 | 2390560 |  | 6092697.4752
28 | 33/11 kV T2 Incoming (LV) |  | 11 |  |  | 1 | 613209 | 614374 | 1165 | 1000 | 1165000 |  | 2969175.657
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 3555560 |  | 9061873.1322
| LALBAGH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [6 empty] | 280
15 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  | 180 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | A319R | 11 |  | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2209968.432 | 2234300.9651 | Lalbag | 190 |  | 100 |  | Sowari Ghat | 2234300.9651 | 2372343.4886 | -138042.5235 | -5.8188 | OK
17 | Novo Kumar (Kara Odidoptor) | A3202 | 11 |  | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 523413.576 | 529176.5444 | Lalbag | 45 |  | 33.3333 |  | Novo Kumar (Kara Odidoptor) | 529176.5444 | 499440.7344 | 29735.8099 | 5.9538 | OK
19 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  | 213.3333 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | A320A | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1046827.152 | 1058353.0887 | Lalbag | 90 |  |  |  | Eidgah | 1058353.0887 | 1123741.6525 | -65388.5638 | -5.8188 | OK
23 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | A3201 | 11 |  |  | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 1977340.176 | 1999111.3898 | Lalbag | 170 |  |  |  | Modumoti | 1999111.3898 | 2122623.1214 | -123511.7316 | -5.8188 | OK
25 | Lalbagh O/H | A320Y | 11 |  | 61389152 | 1 | 443916 | 444305 | 389 | 1000 | Estimated | 872355.96 | 881960.9073 | Lalbag | 75 |  |  |  | Lalbagh O/H | 881960.9073 | 874021.2853 | 7939.622 | 0.9084 | OK
26 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | A320G | 11 |  | 61389109 | 1 | 407526 | 408402 | 876 | 1000 |  | 876000 | 885645.0694 | Lalbag |  |  |  |  | Water Works 11 kV Sw/S-2 | 885645.0694 | 840530.0839 | 45114.9855 | 5.3674 | OK
31 | Islambagh | A320D | 11 |  | 61389186 | 1 | 504954 | 505646 | 692 | 1000 |  | 692000 | 699619.1644 | Lalbag |  |  |  |  | Islambagh | 699619.1644 | 757180.0278 | -57560.8633 | -7.602 | OK
32 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | A320F | 11 |  | 61389202 | 1 | 15832 | 15858 | 26 | 1000 |  | 26000 | 26286.2692 | Lalbag |  |  |  |  | WASA Low Lift Pump | 26286.2692 | 37156.0491 | -10869.7799 | -29.2544 | OK
34 | Shahi Mosjid | D920M | 11 |  | 06604459 | 1 | 36754.1 | 36846.51 | 92.41 | 8000 |  | 739280 | 747419.7339 | Azimpur |  |  |  |  | Shahi Mosjid | 747419.7339 | 755814.2919 | -8394.558 | -1.1107 | OK
35 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer |  | 0.415 |  | 5395822 | 1 | 82720.6 | 82720.6 | 0 | 1 |  | 0 | 0 | Lalbag |  |  |  |  | 33/0.4 kV Auxiliary Transformer | 0 | 7696.9258 | -7696.9258 | -100 | CHECK
|  |  | 10: Grand Total | 9061873.1322 | 8963185.296 | 9061873.1322 | 1.101
33/0.4 kV Auxiliary Transformer meter change at 30 April 2023
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Lalbag | at 33 KV level |  | 8314453.3983
[6 empty] | Azimpur | at 33 KV level |  | 747419.7339
[6 empty] | Total = |  |  | 9061873.1322 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 |  | 33 | 0 | SIEM0513 | 1 | 332029 | 334522 | 2493 | 2000 | 0 | 4986000 | 4989233.5951
18 | Mitford Circuit-2 |  | 33 | 0 | SIEM0511 | 1 | 365758 | 366792 | 1034 | 2000 | 0 | 2068000 | 2069341.1702
|  |  | 10: Total | 0 | 7054000 | 7058574.7653
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 1279.15 | 1288.5 | 9.35 | 540000 |  | 5049000
| Lalbagh Circuit-2 |  | 33 |  | DHK68131 | 1 | 1313.99 | 1315.83 | 1.84 | 540000 |  | 993600
|  |  | 7: 0; 8: 0; 10: Total |  | 6042600
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
1 | Kumartuly Circuit-1 |  | 33 |  | DHK-66493 | 1 | 1305659 | 1317957 | 12298 | 180 |  | 2214972 |  |  | From Kumertully End
6 | Kumartuly Circuit-2 |  | 33 |  | DHK-60914 | 1.1 | 799785.6 | 800133.2 | 347.6 | 180 |  | 68824.8 |  |  | From Kumertully End
|  |  | 7: 0; 8: 0; 10: Total |  | 2283796.8
[7 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-66494 | 1 | 3083631 | 3110898 | 27267 | 180 | From Downstream | 3109528.8
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHKA-2193 | 1 | 681.31 | 693.13 | 11.82 | 180000 |  | 2127600
|  |  | 10: Total | 9342371.5653 | 5237128.8
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 4: 7058574.7653; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5237128.8
| IMPORT-2 |  | 4: 2283796.8; 6: 33 KV NET IMPORT; 9=8-7: 5237128.8 | 33 KV TX HV SIDE |  | 5237128.8
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9342371.5653
11 KV SIDE of___MIDFORT 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK-66484 | 1 | 2893225 | 2909997 | 16772 | 180 | 3018960 |  | 3103785.3086
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK-66476 | 1 | 2163709 | 2175237 | 11528 | 180 | 2075040 |  | 2133343.4914
|  |  | 7: 0; 8: 0; 10: Total | 5094000 |  | 5237128.8
| MIDFORT 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | A319Z | 11 |  | DHK-60904 | 1 | 5415 | 21857.4 | 16442.4 | 60 | 32 | 364113.792 | 370947.5017 | Lalbag | Estimated |  |  |  | Chawk Bazar | 370947.5017 | 246855.923 | 124091.5787 | 50.2688 | FAULT
10 | Spare |  | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | B688D | 11 |  | DHK-66485 | 1 | 876789 | 880190 | 3401 | 60 |  | 204060 | 207889.8104 | Bangshal |  |  |  |  | Chatrabas | 207889.8104 | 310637.8801 | -102748.0697 | -33.0765 | OK
12 | Begum Bazar | B678G | 11 |  | DHK-66481 | 1 | 3867004 | 3889474 | 22470 | 60 |  | 1348200 | 1373503.0993 | Bangshal |  |  |  |  | Begum Bazar | 1373503.0993 | 1439942.349 | -66439.2497 | -4.614 | OK
13 | SCC ROAD | B688R | 11 |  | DHK-60901 | 1 | 214082.8 | 232175.1 | 18092.3 | 60 |  | 1085538 | 1105911.443 | Bangshal |  |  |  |  | SCC ROAD | 1105911.443 | 966855.8354 | 139055.6075 | 14.3822 | OK
16 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | B619A | 11 |  | DHK-61104 | 1 | 762604.6 | 771102.4 | 8497.8 | 60 |  | 509868 | 519437.2335 | Bangshal |  |  |  |  | Armanitola | 519437.2335 | 493501.4256 | 25935.8079 | 5.2555 | OK
18 | Mitford Hospital (RMU) |  | 11 |  | DHK-61101 | 1 | 433797 | 433797.1 | 0.1 | 60 |  | 6 | 6.1126 | Bangshal |  |  |  |  | Mitford Hospital (RMU) | 6.1126 | 225733.0342 | -225726.9216 | -99.9973 | CHECK
19 | Emamganj | B688I | 11 |  | DHK-68130 | 1 | 1516.11 | 1527.46 | 11.35 | 60000 |  | 681000 | 693781.0493 | Bangshal |  |  |  |  | Emamganj | 693781.0493 | 593633.738 | 100147.3113 | 16.8702 | OK
20 | Kamal Dho Road | A319T | 11 |  | DHK-68129 | 1 | 1226.82 | 1226.82 | 0 | 60000 |  | 0 | 0 | Lalbag |  |  |  |  | Kamal Dho Road | 0 | -608.8551 | 608.8551 | -100 | CHECK
21 | Spare |  | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | B688P | 11 |  | DHK-68127 | 1 | 1648.83 | 1664.56 | 15.73 | 60000 |  | 943800 | 961513.2956 | Bangshal |  |  |  |  | Panghat | 961513.2956 | 845090.9008 | 116422.3948 | 13.7763 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | U0004460 | 1 | 5846.88 | 5887.51 | 40.63 | 100 |  | 4063 | 4139.2546 | Bangshal |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4139.2546 | 4563.3691 | -424.1145 | -9.2939 | OK
|  |  | 10: Grand Total | 5237128.8 | 5140648.792 | 5237128.8 | 1.8768
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 4866181.2983
[6 empty] | Lalbag | at 33 KV level |  | 370947.5017
[6 empty] | Total = |  |  | 5237128.8 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 |  | 33 | 0 | SIEM0503 | 1 | 77848 | 77848 | 0 | 2000 | 0 | 0 | 0
15 | Azimpur Circuit-2 |  | 33 | 0 | SIEM0507 | 1 | 91043 | 91043 | 0 | 2000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 |  | 33 | 0 | BD001822 | 1 | 2118.25 | 2144.4 | 26.15 | 240000 | 0 | 6276000 | 6288532.2867
20 | Azimpur Circuit-2 |  | 33 | 0 | BD001857 | 0.95 | 1919.51 | 1933.54 | 14.03 | 240000 | From Downstream R Phase CT Problem | 4764231 | 4773744.4973
|  |  | 10: Total | 0 | 11040231 | 11062276.784
|  |  | 10: GRAND TOTAL |  | 11040231 | 11062276.784
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 864115 | 864115 | 0 | 180 |  | 0
| Dhanmondi Circuit-1 |  | 33 |  | DHK68131 | 1 | 1248047 | 1259694 | 11647 | 540 |  | 6289380
| Dhanmondi Circuit-2 |  | 33 |  |  | 1 | 189055 | 198342 | 9287 | 540 |  | 5014980
| Lalbagh Circuit-2 |  | 33 |  | DHK68132 | 1 | 10259 | 10259 | 0 | 180 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 11304360
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 |  | 3: 33; 6: 1; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK61094 | 1 | 555068 | 590068 | 35000 | 180 |  | 6300000
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK60919 | 1 | 637314 | 665207 | 27893 | 180 |  | 5020740
|  |  | 10: Total |  | 11320740 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | AZIMPUR 33 KV NET IMPORT |  | 11062276.784
| DHANMONDI 33 kV SIDE |  | 4: 11062276.784; 6: AZIMPUR 33 KV NET IMPORT; 9=8-7: 11062276.784 | 33 KV TX HV SIDE |  | 11320740
[11 empty] | LOSS UNITS=> |  | -258463.216
[11 empty] | LOSS % IN => |  | -2.336%
| TOTAL IMPORT |  | 4: 11062276.784
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) |  | 11 |  | DHK60909 | 1 | 558308 | 593350 | 35042 | 180 | 6307560 |  | 6150643.4441
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK60902 | 1 | 653490 | 681473 | 27983 | 180 | 5036940 |  | 4911633.3399
|  |  | 7: 0; 8: 0; 10: Total | 11344500 |  | 11062276.784
| AZIMPUR 11 KV SIDE |  | 7: 0; 8: 0
7 | Chadni chwok |  | 11 |  | DHK60916 | 1 | 473428 | 484246 | 10818 | 60 |  | 649080 | 649366.4481 | Paribag |  |  |  |  | Chadni chwok | 649366.4481 | 536263.7735 | 113102.6745 | 21.0909 | OK
8 | BGB |  | 11 |  | DHK61090 | 1 | 726294 | 729913 | 3619 | 60 |  | 217140 | 217235.8269 | Jigatola |  |  |  |  | BGB | 217235.8269 | 380481.4139 | -163245.587 | -42.905 | CHECK
9 | Pari Bibi Mazar | D920P | 11 |  | DHK61091 | 1 | 978510 | 1007094 | 28584 | 60 |  | 1715040 | 1715796.8712 | Azimpur |  |  |  |  | Pari Bibi Mazar | 1715796.8712 | 1652714.2274 | 63082.6438 | 3.8169 | OK
10 | Azimpur | D901P | 11 |  | DHK61086 | 1 | 429615 | 443570 | 13955 | 60 |  | 837300 | 837669.5122 | Azimpur |  |  |  |  | Azimpur | 837669.5122 | 1335819.9504 | -498150.4382 | -37.2917 | OK
11 | Aazd | D901Z | 11 |  | DHK61089 | 1 | 90027 | 101664 | 11637 | 60 |  | 698220 | 698528.1343 | Azimpur |  |  |  |  | Aazd | 698528.1343 | 763168.1621 | -64640.0278 | -8.47 | OK
12 | Dayra Sharif | D966D | 11 |  | DHK61088 | 1 | 598264 | 609253 | 10989 | 60 |  | 659340 | 659630.976 | Azimpur |  |  |  |  | Dayra Sharif | 659630.976 | 557582.0044 | 102048.9715 | 18.3021 | OK
13 | Naya palton | D966U | 11 |  | DHK86065 | 1 | 2045.23 | 2064.31 | 19.08 | 60000 |  | 1144800 | 1145305.2163 | Azimpur |  |  |  |  | Naya palton | 1145305.2163 | 1141260.4639 | 4044.7523 | 0.35441 | OK
16 | Viqarunnisa Noon School | D966V | 11 |  | DHK66477 | 1 | 1722998 | 1736553 | 13555 | 60 |  | 813300 | 813658.9207 | Azimpur |  |  |  |  | Viqarunnisa Noon School | 813658.9207 | 766843.7191 | 46815.2015 | 6.1049 | OK
17 | Subal Das Lane | D966W | 11 |  | DHK66480 | 1 | 4164565 | 4185323 | 20758 | 60 |  | 1245480 | 1246029.6478 | Azimpur |  |  |  |  | Subal Das Lane | 1246029.6478 | 1606279.69 | -360250.0422 | -22.4276 | OK
18 | Lalbagh | D920L | 11 |  | DHK61093 | 1 | 920565 | 943675 | 23110 | 60 |  | 1386600 | 1387211.926 | Azimpur |  |  |  |  | Lalbagh | 1387211.926 | 1330919.2077 | 56292.7183 | 4.2296 | OK
19 | Zahrul Haque Hall | D366J | 11 |  | DHK66497 | 1 | 1292347 | 1298527 | 6180 | 60 |  | 370800 | 370963.6392 | Ramna |  |  |  |  | Zahrul Haque Hall | 370963.6392 | 323939.0946 | 47024.5446 | 14.5165 | OK
20 | Eden College | D966E | 11 |  | DHK60917 | 1 | 971842 | 976460 | 4618 | 60 |  | 277080 | 277202.2793 | Azimpur |  |  |  |  | Eden College | 277202.2793 | 278913.5208 | -1711.2415 | -0.61354 | OK
21 | Nilkhet/ PWD-01 | D902N | 11 |  | DHK60918 | 1 | 533446 | 540356 | 6910 | 60 |  | 414600 | 414782.9688 | Azimpur |  |  |  |  | Nilkhet/ PWD-01 | 414782.9688 | 419136.0222 | -4353.0534 | -1.0386 | OK
22 | BUET | D366BU | 11 |  | DHK66496 | 1 | 1033226 | 1043678 | 10452 | 60 |  | 627120 | 627396.7568 | Ramna |  |  |  |  | BUET | 627396.7568 | 678997.9056 | -51601.1488 | -7.5996 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIG2780 | 1 | 408450 | 409947 | 1497 | 1 |  | 1497 | 1497.6606 | Azimpur |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 1497.6606 | 1723.4279 | -225.7672 | -13.0999 | OK
|  |  | 10: Grand Total | 11062276.784 | 11057397 | 11062276.784 | 0.044131
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 649366.4481
[6 empty] | Jigatola | at 33 KV level |  | 217235.8269
[6 empty] | Azimpur | at 33 KV level |  | 9197314.113
[6 empty] | Ramna | at 33 KV level |  | 998360.3961
[6 empty] | Total = |  |  | 11062276.784 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar |  | 132 |  | 38992596 | 1 | 1071.17 | 1089.136 | 17.966 | 1440000 | 0 | 25871040
|  |  | 132 |  |  | 1 | 0.021 | 0.029 | 0.008 | 1440000 | 11520 | 0
|  |  | 9=8-7: Total Import/Export | 11520 | 25871040
|  |  | 10: Net Total | 25859520
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj |  | 132 | RECEIVE |  | 1 | 5968.67 | 5995.68 | 27.01 | 960000 | 25929600
|  |  | 132 | RECEIVE |  | 1 | 91.71 | 91.72 | 0.01 | 960000 |  | 9600
| 132 kV Lalbagh |  | 132 |  |  | 1 | 3233.21 | 3260.64 | 27.43 | 960000 | 26332800
|  |  | 132 |  |  | 1 | 7.84 | 7.84 | 0 | 960000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 52262400 | 9600
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 52252800
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
5 | 132 kV Jigatola-1 |  | 132 |  | 42003953362 | 1 | 300.91 | 310.33 | 9.42 | 1440000 |  | 13564800
6 | 132 kV Jigatola-2 |  | 132 |  | 42003953364 | 1.07 | 294.01 | 303.22 | 9.21 | 1440000 |  | 14190768
|  |  | 7: 0; 8: 0; 10: Total |  | 27755568
| KAMRANGIRCHAR 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | 30799138 | 1 | 3445.1 | 3453.34 | 8.24 | 960000 |  | 7910400
2 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 |  | 30799148 | 1 | 3421.47 | 3429.05 | 7.58 | 960000 |  | 7276800
7 | 132/33 kV, 50/75 MVA GT-3 (HV) |  | 132 |  | BD001910 | 1 | 1225.94 | 1233.94 | 8 | 960000 |  | 7680000
|  |  | 10: Total |  | 22867200 | 50622768
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 4: 25859520; 6: EXPORT TO OTHER S/S; 9=8-7: 27755568 | 132 KV NET IMPORT |  | 24436752
| FROM LALBAGH 132/33 KV GRID |  | 4: 26332800; 6: 132 KV NET IMPORT; 9=8-7: 24436752 | 33 KV NET IMPORT |  | 25310400
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -873648
[11 empty] | LOSS % IN => |  | -3.575%
| 132 KV TOTAL IMPORT |  | 4: 52192320
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001914 | 1 | 2468.99 | 2487.03 | 18.04 | 480000 | 8659200 |  | 8360307.3408
14 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | 30799094 | 1 | 6992.95 | 7010.91 | 17.96 | 480000 | 8620800 |  | 8323232.8071
19 | 132/33 kV GT-2 Incoming |  | 33 |  | 30799150 | 1 | 6891.49 | 6908.22 | 16.73 | 480000 | 8030400 |  | 7753211.8521
|  |  | 7: 0; 8: 0; 10: Total | 25310400 |  | 24436752
| KAMRANGIRCHAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) |  | 33 |  | 30799129 | 1 | 7041.75 | 7065.12 | 23.37 | 240000 |  | 5608800 | 5588481.204 |  | 15426312.4721 | Kamrangir Char 33/11 kv ss | 1.3215 |  | 33/11 kV, 20/28 MVA T31 (HV) | 5588481.204 | 6516430.0289 | -927948.8249 | -14.2401 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) |  | 33 |  | 30799110 | 1 | 6936.81 | 6958.78 | 21.97 | 240000 |  | 5272800 | 5253698.419 | [5 empty] | 33/11 kV, 20/28 MVA T32 (HV) | 5253698.419 | 6402827.5766 | -1149129.1576 | -17.9472 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) |  | 33 |  | 30799137 | 1 | 4087.72 | 4100.96 | 13.24 | 240000 |  | 3177600 | 3166088.6239 | [5 empty] | 33/11 kV, 20/28 MVA T-33 (HV) | 3166088.6239 | 6753303.2273 | -3587214.6034 | -53.1179 | CHECK
11 | 33/11 kV Transformer T-4 (Spare) |  | 33 |  | 30799125 | 1 | 0 | 5.93 | 5.93 | 240000 |  | 1423200 | 1418044.2251 | [5 empty] | 33/11 kV Transformer T-4 (Spare) | 1418044.2251 | 0 | 1418044.2251 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 15482400 | 15426312.4721 | [5 empty] | 33 KV Feeders | 15426312.4721 | 19672560.8329 | -4246248.3608 | -21.5846 | OK
8 | Dhaka Uddyan 2 |  | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | 0.54186 |  | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Adabor- 1 |  | 33 |  | BD001912 | 1 | 428.24 | 428.24 | 0 | 240000 |  | 0 | 0 | [5 empty] | Adabor- 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Bossila-1 |  | 33 |  | 30799130 | 1 | 0 | 13.02 | 13.02 | 240000 |  | 3124800 | 3113479.9006 | [5 empty] | Bossila-1 | 3113479.9006 | 0 | 3113479.9006 | #DIV/0! | #DIV/0!
15 | Kurarghat-1 (Old Lalbagh-1) |  | 33 |  | 30799098 | 1 | 1761.99 | 1761.99 | 0 | 240000 | From Downstream | 3225600 | 3213914.7361 |  | 5896959.6274 | Kamrangir Char-2 33/11 kv ss | 0.49269 |  | Kurarghat-1 (Old Lalbagh-1) | 3213914.7361 | 101517.085 | 3112397.6511 | 3065.8856 | FAULT
16 | Zigatola Circuit-1 (BGB-1) |  | 33 |  | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 |  | 0 | 0 | [5 empty] | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 (Lalbagh Ckt-2) |  | 33 |  | 30799147 | 1 | 1646.33 | 1654.56 | 8.23 | 240000 | From Downstream | 2692800 | 2683044.8913 |  | 0 | BGB 33/11 kv ss | 0.93986 |  | Kamrangir Char-2 (Lalbagh Ckt-2) | 2683044.8913 | 5300642.0821 | -2617597.1908 | -49.3826 | CHECK
22 | Zigatola Circuit-2 (BGB-2) |  | 33 |  | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Grid Has No Reading | Zigatola Circuit-2 (BGB-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 9043200 | 9010439.5279 | [5 empty] | 0 | 9010439.5279 | 5402159.1671 | 3608280.3608 | 66.7933 | FAULT
|  |  | 9=8-7: Grand Total | 24436752 | 24525600 | 24436752 | -0.36227
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 5299200 |  | 5132747.5862
11 | 33/11 kV T-32 Incoming |  | 11 |  | 6604433 | 1 | 7840.41 | 7869.85 | 29.44 | 180000 | 5299200 |  | 5132747.5862
22 | 33/11 kV T-33 Incoming |  | 11 |  | DHK 95817 | 1 | 4824103 | 4853704 | 29601 | 180 | 5328180 |  | 5160817.2996
|  |  | 7: 0; 8: 0; 10: Total | 15926580 |  | 15426312.4721
| KAMRANGIRCHAR 11 kV SIDE |  | 7: 0; 8: 0
4 | Rasulpur | F120R | 11 |  | HA-021101042-02 | 1.5 | 99314921 | 99628473 | 313552 | 1 |  | 470328 | 476543.206 | Kamrangirchar |  |  |  |  | Rasulpur | 476543.206 | 747281.5913 | -270738.3853 | -36.2298 | OK
5 | Bheribadh | F120B | 11 |  | HA-021101105-02 | 1.5 | 77687448 | 78413126 | 725678 | 1 |  | 1088517 | 1102901.339 | Kamrangirchar |  |  |  |  | Bheribadh | 1102901.339 | 1866994.3592 | -764093.0202 | -40.9264 | CHECK
7 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 |  | 30799521 | 1.5 | 2663.91 | 2665.11 | 1.2 | 60000 |  | 108000 | 109427.179 | Kamrangirchar |  |  |  |  | Panna Tower 11 KV Faridpur Tower Express | 109427.179 | 162709.829 | -53282.65 | -32.747 | OK
8 | Panna Battery Express | F140E | 11 |  | DHK15431 | 1 | 5375.75 | 5382.23 | 6.48 | 60000 |  | 388800 | 393937.8444 | Kamrangirchar |  |  |  |  | Panna Battery Express | 393937.8444 | 877165.0182 | -483227.1738 | -55.0897 | CHECK
9 | Eidgah | F140I | 11 |  | 30799460 | 1 | 5589.33 | 5621.88 | 32.55 | 60000 |  | 1953000 | 1978808.1538 | Kamrangirchar |  |  |  |  | Eidgah | 1978808.1538 | 1994724.6335 | -15916.4797 | -0.79793 | OK
10 | Bot Tola Mazar | D840L | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | F140H | 11 |  | HA-021101055-02 | 1 | 13533389 | 15522799 | 1989410 | 1 |  | 1989410 | 2015699.2981 | Kamrangirchar |  |  |  |  | Huzur Para | 2015699.2981 | 1790122.1209 | 225577.1772 | 12.6012 | OK
13 | Kamrangirchar | F103K | 11 |  | HA-021101015-02 | 1 | 31631669 | 32048318 | 416649 | 1 |  | 416649 | 422154.8584 | Kamrangirchar |  |  |  |  | Kamrangirchar | 422154.8584 | 1105200.3969 | -683045.5384 | -61.8029 | CHECK
14 | Munshihati | F140T | 11 |  | HA-021100854-02 | 1 | 57816310 | 58111286 | 294976 | 1 |  | 294976 | 298873.9959 | Kamrangirchar |  |  |  |  | Munshihati | 298873.9959 | 663886.687 | -365012.6912 | -54.9812 | CHECK
15 | Jhawchar | F140J | 11 |  | HA-021101028-02 | 1 | 7831319 | 8178936 | 347617 | 1 |  | 347617 | 352210.6267 | Kamrangirchar |  |  |  |  | Jhawchar | 352210.6267 | 916198.0459 | -563987.4192 | -61.5574 | CHECK
16 | RMU Express | F140D | 11 |  | HA-021101248-02 | 1 | 9846204 | 10451988 | 605784 | 1 |  | 605784 | 613789.2056 | Kamrangirchar |  |  |  |  | RMU Express | 613789.2056 | 639128.4903 | -25339.2847 | -3.9647 | OK
17 | Koyla Ghat | F140C | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2010996.288 | 2037570.8407 | Kamrangirchar | 160 |  |  |  | Koyla Ghat | 2037570.8407 | 1922044.5384 | 115526.3023 | 6.0106 | OK
18 | Muslimbagh | F140M | 11 |  | HA-021100908-02 | 1 | 37215219 | 38199598 | 984379 | 1 |  | 984379 | 997387.1949 | Kamrangirchar |  |  |  |  | Muslimbagh | 997387.1949 | 1348865.5022 | -351478.3074 | -26.0573 | OK
19 | Noyagaon | F140Y | 11 |  | HA-021101087-02 | 1 | 19796598 | 20487577 | 690979 | 1 |  | 690979 | 700110.0252 | Kamrangirchar |  |  |  |  | Noyagaon | 700110.0252 | 1800043.7503 | -1099933.7251 | -61.1059 | CHECK
20 | Nurbagh | F140N | 11 |  | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2262370.824 | 2292267.1958 | Kamrangirchar | 180 |  |  |  | Nurbagh | 2292267.1958 | 2178317.1436 | 113950.0522 | 5.2311 | OK
21 | Ali Nagar | F140A | 11 |  | HA-021101022-02 | 1 | 34081371 | 35680798 | 1599427 | 1 |  | 1599427 | 1620562.8208 | Kamrangirchar |  |  |  |  | Ali Nagar | 1620562.8208 | 1505747.9542 | 114814.8666 | 7.6251 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKE6223 | 1 | 43873.75 | 43929.56 | 55.81 | 120 |  | 6697.2 | 6785.701 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 6785.701 | 0 | 6785.701 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHK37495 | 1 | 45794.4 | 45854.3 | 59.9 | 120 |  | 7188 | 7282.9867 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 7282.9867 | 15169.9389 | -7886.9523 | -51.9907 | CHECK
|  |  | 10: Total | 15426312.4721 | 15225118.312 | 15426312.4721 | 1.3215
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 15426312.4721
[6 empty] | Jigatola | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 15426312.4721 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: TOTAL |  | 0 | 0
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old |  | 33 | 0 | 43998033 | 1 | 331.2 | 364.295 | 33.095 | 270000 |  | 8935650 | 8717854.4115
|  |  | 10: TOTAL |  | 8935650 | 8935650
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 |  | 33 | 0 | 0 | 1 | 79.33 | 79.37 | 0.04 | 360000 | 0 | 14400 | 14359.6151
11 | BGB-2 |  | 33 | 0 | 0 | 1 | 345.7 | 355.04 | 9.34 | 360000 | 0 | 3362400 | 3352970.1342
|  |  | 10: Total | 0 | 3376800 | 3367329.7493
|  |  | 10: GRAND TOTAL |  | 12312450 | 12302979.7493
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 |  | 33 |  | 43998032 | 1 | 1047.72 | 1047.72 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old |  | 33 |  | 43998033 | 1 | 331.2 | 364.295 | 33.095 | 270000 | 8935650
| 33 kV Zigatola-1 |  | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 |  | 33 |  | 43998027 | 1 | 781.12 | 781.12 | 0 | 270000 | 0
| 33 kV Zigatola-2 |  | 33 |  | 43998031 | 1 | 460.08 | 471.581 | 11.501 | 270000 | 3105270
|  |  | 7: 0; 8: 0; 10: Total | 12040920 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BGB 33 KV SIDE |  | 7: 0; 8: 0
6 | 33/11 kV T1 |  | 33 |  | 43998028 | 1 | 890.1 | 916.56 | 26.46 | 270000 |  | 7144200
9 | 33/11 kV T2 |  | 33 |  | 43998029 | 1 | 928.492 | 946.635 | 18.143 | 270000 |  | 4898610
11 | 33/11 kV T3 |  | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 12042810
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 4: 12302979.7493; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BGB 33 KV NET IMPORT |  | 12302979.7493
|  |  | 6: BGB 33 KV NET IMPORT; 9=8-7: 12302979.7493 | 33 KV TX HV SIDE |  | 12042810
[11 empty] | LOSS UNITS=> |  | 260169.7493
[11 empty] | LOSS % IN => |  | 2.115%
| TOTAL IMPORT |  | 4: 12302979.7493
11 KV SIDE of___BGB 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming |  | 11 |  |  | 1 | 38406060 | 45492560 | 7086500 | 1 | 7086500 |  | 7150758.6825
29 | 33/11 kV T-2 Incoming |  | 11 |  |  | 1 | 48437480 | 53285570 | 4848090 | 1 | 4848090 |  | 4892051.3175
30 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 11934590 |  | 12042810
| BGB 11 KV SIDE |  | 7: 0; 8: 0
12 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | D920K | 11 |  |  | 1 | 12523740 | 12956970 | 433230 | 1 |  | 433230 | 437301.7528 | Azimpur |  |  |  |  | Nababgonj Park | 437301.7528 | 0 | 437301.7528 | #DIV/0! | #DIV/0!
16 | Kholamura Ghat | F1104O | 11 |  |  | 1 | 94560736 | 97301320 | 2740584 | 1 |  | 2740584 | 2766341.6358 | Kamrangirchar |  |  |  |  | Kholamura Ghat | 2766341.6358 | 2922234.8502 | -155893.2145 | -5.3347 | OK
17 | Khalpar | F1104L | 11 |  |  | 1 | 94084000 | 96060500 | 1976500 | 1 |  | 1976500 | 1995076.3206 | Kamrangirchar |  | 170 |  |  | Khalpar | 1995076.3206 | 1357000.7539 | 638075.5667 | 47.021 | FAULT
18 | Shahidnagar | D920S | 11 |  |  | 1 | 26032520 | 27374940 | 1342420 | 1 |  | 1342420 | 1355036.8603 | Azimpur |  | 64 |  |  | Shahidnagar | 1355036.8603 | 1306884.5014 | 48152.3589 | 3.6845 | OK
19 | BGB 1 No Gate | D9104G | 11 |  |  | 1 | 37153410 | 37725810 | 572400 | 1 |  | 572400 | 577779.7551 | Azimpur |  | 106 |  |  | BGB 1 No Gate | 577779.7551 | 0 | 577779.7551 | #DIV/0! | #DIV/0!
21 | Ganaktuli | D8104J | 11 |  |  | 1 | 27939600 | 28480330 | 540730 | 1 |  | 540730 | 545812.1016 | Jigatola |  | 35.3333 |  |  | Ganaktuli | 545812.1016 | 547461.301 | -1649.1994 | -0.30124 | OK
22 | Thana |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  | 99.3333 |  |  | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | D8104L | 11 |  |  | 1 | 39473749 | 40794581 | 1320832 | 1 | 40794581 | 1320832 | 1333245.9634 | Jigatola | 170-64 | 1137855.6 |  |  | Bot Tola Mazar | 1333245.9634 | 396033.3839 | 937212.5796 | 236.6499 | FAULT
24 | Sikder Medical | D8104K | 11 |  |  | 1 | 41542992 | 42216880 | 673888 | 1 |  | 673888 | 680221.5996 | Jigatola |  |  |  |  | Sikder Medical | 680221.5996 | 704444.667 | -24223.0675 | -3.4386 | OK
25 | Gas Field | F1104G | 11 |  |  | 1 | 65021220 | 66468860 | 1447640 | 1 |  | 1447640 | 1461245.7803 | Kamrangirchar |  |  |  |  | Gas Field | 1461245.7803 | 1418157.1729 | 43088.6075 | 3.0384 | OK
26 | Hazaribagh | D8104H | 11 |  |  | 1 | 47131648 | 48013400 | 881752 | 1 |  | 881752 | 890039.2289 | Jigatola |  |  |  |  | Hazaribagh | 890039.2289 | 821301.08 | 68738.1489 | 8.3694 | OK
27 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  |  | 1 | 2426.91 | 2460.78 | 33.87 | 10 |  | 338.7 | 341.8833 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-1 | 341.8833 | 375.1797 | -33.2964 | -8.8748 | OK
32 | 11/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  |  | 1 | 2008.62 | 2044.99 | 36.37 | 10 |  | 363.7 | 367.1183 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-2 | 367.1183 | 407.1099 | -39.9917 | -9.8233 | OK
|  |  | 10: Grand Total | 12042810 | 11930678.4 | 12042810 | 0.93986
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Azimpur | at 33 KV level |  | 2370827.3697
[6 empty] | Kamrangirchar | at 33 KV level |  | 6222663.7367
[6 empty] | Jigatola | at 33 KV level |  | 3449318.8935
[6 empty] | Total = |  |  | 12042810 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 |  | 132 | 0 | 42003953362 | 1 | 300.91 | 310.33 | 9.42 | 1440000 | 0 | 13564800 | 0
6 | 132 kV Jigatola-2 |  | 132 | 0 |  | 1.07 | 294.01 | 303.22 | 9.21 | 1440000 | 0 | 14190768 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 27755568
|  |  | 10: Net Total | 27755568
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 |  | 132 | RECEIVE | 6604452 | 1 | 361.07 | 372.37 | 11.3 | 1200000 | 13560000
| 132 kV Kamrangirchar 2 |  | 132 |  |  | 1 | 352.56 | 364.42 | 11.86 | 1200000 | 14232000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 27792000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 27792000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| JIGATOLA 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  |  | 1 | 305.02 | 316.73 | 11.71 | 1200000 |  | 14052000
3 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  |  | 1 | 408.89 | 420.21 | 11.32 | 1200000 |  | 13584000
|  |  | 10: Total |  | 27636000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 27755568; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 27755568
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 27755568 | 33 KV NET IMPORT |  | 27734400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 21168
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.07627%
| 132 KV TOTAL IMPORT |  | 4: 27755568
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  |  | 1 | 506.02 | 525.13 | 19.11 | 720000 | 13759200
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  |  | 1 | 678.24 | 697.65 | 19.41 | 720000 | 13975200
|  |  | 7: 0; 8: 0; 10: Total | 27734400 |  | 0
| JIGATOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  |  | 1 | 693.47 | 710.58 | 17.11 | 240000 |  | 4106400 | 4094883.5829 |  | 11633681.5291 | JIGATOLA NEW 3/11 KV SS | -0.058602 |  | 33/11 kV 28/35 MVA T-1 | 4094883.5829 | 4116565.097 | -21681.5141 | -0.52669 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  |  | 1 | 554.74 | 570.2 | 15.46 | 240000 |  | 3710400 | 3699994.1666 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 3699994.1666 | 3235811.6343 | 464182.5323 | 14.3452 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  |  | 1 | 465.93 | 481.97 | 16.04 | 240000 |  | 3849600 | 3838803.7796 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 3838803.7796 | 3513440.4432 | 325363.3364 | 9.2605 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 11666400 | 11633681.5291 | [5 empty] | 33 KV Feeders | 11633681.5291 | 10865817.1745 | 767864.3546 | 7.0668 | OK
2 | BGB-1 |  | 33 |  |  | 1 | 79.33 | 79.37 | 0.04 | 360000 |  | 14400 | 14359.6151 |  | 3367329.7493 | BGB 33/11 kv ss | 0.93986 |  | BGB-1 | 14359.6151 | 0 | 14359.6151 | #DIV/0! | #DIV/0!
2 | Spair |  | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 |  | 33 |  |  | 1 | 279.76 | 289.8 | 10.04 | 360000 |  | 3614400 | 3604263.3991 | [5 empty] | Dhaka Uddyan-1 | 3604263.3991 | 3098193.9058 | 506069.4932 | 16.3343 | OK
4 | Green Road -1 |  | 33 |  |  | 1 | 78.65 | 84.62 | 5.97 | 360000 |  | 2149200 | 2143172.559 |  | 8041384.476 | Dhaka Uddan 33/11 kv ss | 0.54186 |  | Green Road -1 | 2143172.559 | 4293673.1302 | -2150500.5712 | -50.0853 | CHECK
9 | Green Road -2 |  | 33 |  |  | 1 | 103.55 | 107.04 | 3.49 | 360000 |  | 1256400 | 1252876.4206 | [5 empty] | Green Road -2 | 1252876.4206 | 2175556.7867 | -922680.3661 | -42.4112 | CHECK
10 | Dhaka Uddyan-2 |  | 33 |  |  | 1 | 295.23 | 307.59 | 12.36 | 360000 |  | 4449600 | 4437121.0769 | [5 empty] | Dhaka Uddyan-2 | 4437121.0769 | 3916720.2216 | 520400.8553 | 13.2866 | OK
11 | BGB-2 |  | 33 |  |  | 1 | 345.7 | 355.04 | 9.34 | 360000 |  | 3362400 | 3352970.1342 |  | 1295955.266 | Jigatla Old 33/11 kv ss | 0.17082 |  | BGB-2 | 3352970.1342 | 0 | 3352970.1342 | #DIV/0! | #DIV/0!
12 | Jigatola Old |  | 33 |  |  | 1 | 45.89 | 49.5 | 3.61 | 360000 |  | 1299600 | 1295955.266 | [5 empty] | Jigatola Old | 1295955.266 | 1138038.7812 | 157916.4848 | 13.8762 | OK
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 16146000 | 16100718.4709 | [5 empty] | 0 | 16100718.4709 | 14622182.8255 | 1478535.6454 | 10.1116 | OK
|  |  | 9=8-7: Grand Total | 27734400 | 27812400 | 27734400 | -0.28045
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 259.17 | 275.83 | 16.66 | 250000 | 4165000 |  | 4117636.1648
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 273.54 | 288.63 | 15.09 | 250000 | 3772500 |  | 3729599.6234
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 214.2 | 229.52 | 15.32 | 250000 | 3830000 |  | 3786445.7409
|  |  | 7: 0; 8: 0; 10: Total | 11767500 |  | 11633681.5291
| JIGATOLA 11 kV SIDE |  | 7: 0; 8: 0
| Salek Garden |  | 11 |  | 2761 | 1 | 794.02 | 818.11 | 24.09 | 60000 |  | 1445400 | 1444552.9709 | Jigatola |  |  |  |  | Salek Garden | 1444552.9709 | 1253840.8307 | 190712.1402 | 15.2102 | OK
4 | Jigatola Local |  | 11 |  | 2850 | 1 | 611.33 | 628.17 | 16.84 | 60000 |  | 1010400 | 1009807.8883 | Jigatola |  |  |  |  | Jigatola Local | 1009807.8883 | 896547.408 | 113260.4803 | 12.633 | OK
5 | Modina Rayer Bazar |  | 11 |  | 2851 | 1 | 716.74 | 745.24 | 28.5 | 60000 |  | 1710000 | 1708997.9107 | Switching |  |  |  |  | Modina Rayer Bazar | 1708997.9107 | 1475567.609 | 233430.3017 | 15.8197 | OK
6 | City College |  | 11 |  | 2784 | 1 | 644.28 | 644.31 | 0.03 | 60000 |  | 1800 | 1798.9452 | Jigatola |  |  |  |  | City College | 1798.9452 | 506115.4723 | -504316.5271 | -99.6446 | CHECK
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office |  | 11 |  | 2836 | 1 | 521.18 | 537.81 | 16.63 | 60000 |  | 997800 | 997215.2721 | Jigatola |  |  |  |  | Post Office | 997215.2721 | 901970.0738 | 95245.1984 | 10.5597 | OK
11 | Leather Institute |  | 11 |  | 2835 | 1 | 58.33 | 59.04 | 0.71 | 60000 |  | 42600 | 42575.0357 | Jigatola |  |  |  |  | Leather Institute | 42575.0357 | 0 | 42575.0357 | #DIV/0! | #DIV/0!
12 | Mina Bazar |  | 11 |  | 2853 | 1 | 250.76 | 257.54 | 6.78 | 60000 |  | 406800 | 406561.6082 | Jigatola |  |  |  |  | Mina Bazar | 406561.6082 | 389226.8989 | 17334.7093 | 4.4536 | OK
13 | Mitali |  | 11 |  | 2852 | 1 | 560.49 | 573.49 | 13 | 60000 |  | 780000 | 779542.9066 | Switching |  |  |  |  | Mitali | 779542.9066 | 653129.9666 | 126412.9401 | 19.3549 | OK
14 | Road-2 |  | 11 |  | 2839 | 1 | 823.37 | 849.2 | 25.83 | 60000 |  | 1549800 | 1548891.7907 | Jigatola |  |  |  |  | Road-2 | 1548891.7907 | 1301439.7858 | 247452.0049 | 19.0137 | OK
15 | SS-2 |  | 11 |  | 2838 | 1 | 450.61 | 465.05 | 14.44 | 60000 |  | 866400 | 865892.2748 | Jigatola |  |  |  |  | SS-2 | 865892.2748 | 1573778.1113 | -707885.8366 | -44.98 | CHECK
16 | Spare |  | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar |  | 11 |  | 2843 | 1 | 655.46 | 674.37 | 18.91 | 60000 |  | 1134600 | 1133935.105 | Jigatola |  |  |  |  | Bou Bazar | 1133935.105 | 940531.2526 | 193403.8524 | 20.5633 | OK
18 | BGB |  | 11 |  | 2764 | 1 | 228.5 | 236.94 | 8.44 | 60000 |  | 506400 | 506103.2409 | Jigatola |  |  |  |  | BGB | 506103.2409 | 336205.278 | 169897.9629 | 50.534 | FAULT
19 | Dhamondi-12 |  | 11 |  | 2763 | 1 | 521.56 | 543.6 | 22.04 | 60000 |  | 1322400 | 1321625.051 | Dhanmondi |  |  |  |  | Dhamondi-12 | 1321625.051 | 637464.4877 | 684160.5633 | 107.3253 | FAULT
|  |  | 10: Total | 11767500 | 11774400 | 11767500 | -0.058602
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Jigatola | at 33 KV level |  | 9777286.3631 | Including Switching
[6 empty] | Dhanmondi | at 33 KV level |  | 1990213.6369
[6 empty] | Total = |  |  | 11767500 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [14 empty] | Month February-2024
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | 4: CF; 5: Number; 7: 2023-04-01; 8: 2023-04-01 | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar |  | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 28.5 | 60000 | 0 | 1710000 | 1708997.9107
13 | Mitali |  | 11 | 0 | 2852 | 1 | 560.49 | 573.49 | 13 | 60000 | 0 | 780000 | 779542.9066
|  |  | 10: Total |  | 2490000 | 2488540.8174
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 668980.62 | 668588.5859 | Dhanmondi | 55
3 | 11 kV Madina Masjid Feeder |  | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1094695.56 | 1094054.0497 | Jigatola | 90
3 | 11 kV Mitali |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 726323.82 | 725898.1818 | Jigatola | Switching Total - Madina - Rayer Bazar
2490000
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit |  | 33 | 0 | 214393/37-2711 | 1 | 49.8277 | 49.8277 | 0 | 1000 | Estimated | 1566000 | 1527830.6568
|  |  | 10: Total |  | 1566000 | 1527830.6568
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  |  | 3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 | NET IMPORT | DHK61073 | 1 | 4059.16 | 4064.34 | 5.18 | 240000 |  | 1243200
2 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
|  |  | 10: Total |  | 1243200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 1527830.6568
| Satmasjid 33 KV SIDE |  | 4: 1527830.6568; 6: 33 KV NET IMPORT; 9=8-7: 1527830.6568 | ZIGATOLA OLD 11 KV NET IMPORT |  | 1243200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 284630.6568
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 18.63%
| TOTAL IMPORT |  | 4: 1527830.6568
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0
16 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0
17 | 33/11 kV T-1 Incoming |  | 11 |  | DHK61028 | 1.32 | 1889.64 | 1894.45 | 4.81 | 180000 | 1142856
|  |  | 7: 0; 8: 0; 10: Total | 1142856 |  | 1243200
| ZIGATOLA OLD 11 KV SIDE |  | 7: 0; 8: 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | D803D | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | D803E | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | D803I | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | D803R | 11 |  | DHK60946 | 1 | 1218.95 | 1228.76 | 9.81 | 60000 |  | 588600 | 589605.4404 | Jigatola |  |  |  |  | Simanto Square | 589605.4404 | 539285.2665 | 50320.174 | 9.3309 | OK
12 | Post Office | D803P | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | D803S | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | D803G | 11 |  | DHK61070 | 1 | 3526.42 | 3536.26 | 9.84 | 60000 |  | 590400 | 591408.5152 | Jigatola |  |  |  |  | Green Road Via Park | 591408.5152 | 583222.5705 | 8185.9446 | 1.4036 | OK
15 | PWD Quarters 11 kV Saleq Grand | D803A | 11 |  | DHK61028 | 1 | 3637.35 | 3638.36 | 1.01 | 60000 |  | 60600 | 60703.5163 | Jigatola |  |  |  |  | PWD Quarters 11 kV Saleq Grand | 60703.5163 | 63799.373 | -3095.8567 | -4.8525 | OK
18 | Road No.-2 | D803T | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | D803H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | D803B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | D803C | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | D803M | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | D803Z | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  | 243284 | 1 | 86315 | 86442 | 127 | 10 |  | 1270 | 1272.1694 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 1272.1694 | 4032.6019 | -2760.4325 | -68.4529 | CHECK
25 | 33/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  | 412277 | 1 | 39896 | 39917 | 21 | 10 |  | 210 | 210.3587 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 210.3587 | 60.1881 | 150.1706 | 249.5022 | FAULT
|  |  | 10: Grand Total | 1243200 | 1241080 | 1243200 | 0.17082
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Jigatola | at 33 KV level |  | 1243200
[6 empty] | Total = |  |  | 1243200 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) |  | 33 | 0 | BD001912 | 1 | 428.24 | 428.24 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 |  | 33 | 0 | 0 | 1 | 279.76 | 289.8 | 10.04 | 360000 | 0 | 3614400 | 3604263.3991
10 | Dhaka Uddyan-2 |  | 33 | 0 | 0 | 1 | 295.23 | 307.59 | 12.36 | 360000 | 0 | 4449600 | 4437121.0769
|  |  | 10: Total | 0 | 8064000 | 8041384.476
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | RECEIVE | BD017107 | 1 | 90472.53 | 90472.53 | 0 | 1125 |  | 0
| 33 kV Jigatala Incoming Circuit-1 |  | 33 |  | BD017098 | 1 | 89164.22 | 92156.99 | 2992.77 | 1125 |  | 3366866.25
| 33 kV Jigatala Incoming Circuit-2 |  | 33 |  | BD017097 | 1 | 94149.43 | 97957.96 | 3808.53 | 1125 |  | 4284596.25
| 33 kV Kamrangirchar Circuit-2 (O/H) |  | 33 |  | BD017108 | 1 | 73739.06 | 73739.06 | 0 | 1125 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 7651462.5 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017100 | 1 | 2911.04 | 6291.98 | 3380.94 | 1000 |  | 3380940
3 | 33/11 kV, 28/35 MVA T-3 (Future) |  | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017109 | 1 | 89479.08 | 93777.47 | 4298.39 | 1000 |  | 4298390
|  |  | 10: Total |  | 7679330 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7679330
| JIGATOLA 33 KV SIDE |  | 4: 8041384.476; 6: 33 KV NET IMPORT; 9=8-7: 7679330 | 33 KV TX HV |  | 7679330
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 8041384.476
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD014060 | 1 | 1757.44 | 5116.87 | 3359.43 | 1000 | 3359430 |  | 3375632.6923
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD014061 | 1 | 88721.93 | 93004.97 | 4283.04 | 1000 | 4283040 |  | 4303697.3077
|  |  | 7: 0; 8: 0; 10: Total | 7642470 |  | 7679330
| DHAKA UDDYAN 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | G1103L | 11 |  | BD014031 | 1 | 50828.11 | 51042.64 | 214.53 | 1000 |  | 214530 | 215692.4534 | Adabor |  |  |  |  | D Block dhaka uddyan | 215692.4534 | 212820.8188 | 2871.6347 | 1.3493 | OK
8 | Dill Mohammad O/H | G1103DM | 11 |  | BD014027 | 1 | 27275.39 | 28232.64 | 957.25 | 1000 |  | 957250 | 962436.9601 | Adabor |  |  |  |  | Dill Mohammad O/H | 962436.9601 | 906080.9687 | 56355.9914 | 6.2198 | OK
9 | Turag O/H | G1103U | 11 |  | BD014028 | 1 | 29810.93 | 30322.94 | 512.01 | 1000 |  | 512010 | 514784.3802 | Adabor |  |  |  |  | Turag O/H | 514784.3802 | 456627.3521 | 58157.0281 | 12.7362 | OK
10 | Nabadoy O/H | G1103N | 11 |  | BD014025 | 1 | 41533.54 | 41984.31 | 450.77 | 1000 |  | 450770 | 453212.5448 | Adabor |  |  |  |  | Nabadoy O/H | 453212.5448 | 436281.6738 | 16930.871 | 3.8807 | OK
11 | Chandrima O/H | G1103CH | 11 |  | BD014024 | 1 | 9907.12 | 10527.40 | 620.28 | 1000 |  | 620280 | 623641.0526 | Adabor |  |  |  |  | Chandrima O/H | 623641.0526 | 643285.1357 | -19644.083 | -3.0537 | OK
12 | Shyamoli Housing Project-2 | G1103SH | 11 |  | BD014029 | 1 | 33170.52 | 33773.81 | 603.29 | 1000 |  | 603290 | 606558.9905 | Adabor |  |  |  |  | Shyamoli Housing Project-2 | 606558.9905 | 570944.9461 | 35614.0444 | 6.2377 | OK
13 | Spare |  | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare |  | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare |  | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | C2103U | 11 |  | BD013959 | 1 | 46607.12 | 47408.36 | 801.24 | 1000 |  | 801240 | 805581.6035 | Satmasjid |  |  |  |  | U Lab | 805581.6035 | 455743.1942 | 349838.4092 | 76.7622 | FAULT
19 | Akota | G1103AK | 11 |  | BD014020 | 1 | 8749.58 | 9084.98 | 335.4 | 1000 |  | 335400 | 337217.4003 | Adabor |  |  |  |  | Akota | 337217.4003 | 326123.6407 | 11093.7596 | 3.4017 | OK
20 | Burigonga O/H | G1103BU | 11 |  | BD014019 | 1 | 6950.61 | 7466.87 | 516.26 | 1000 |  | 516260 | 519057.4093 | Adabor |  |  |  |  | Burigonga O/H | 519057.4093 | 491541.5408 | 27515.8685 | 5.5979 | OK
21 | Garden City | C2103G | 11 |  | BD014021 | 1 | 97620.97 | 99383.31 | 1762.34 | 1000 |  | 1762340 | 1771889.4252 | Satmasjid |  |  |  |  | Garden City | 1771889.4252 | 1905259.7426 | -133370.3173 | -7.0001 | OK
22 | Avenue O/H | G1103AV | 11 |  | BD014017 | 1 | 18014.25 | 18677.34 | 663.09 | 1000 |  | 663090 | 666683.0231 | Adabor |  |  |  |  | Avenue O/H | 666683.0231 | 671286.8174 | -4603.7943 | -0.68582 | OK
23 | Chand Uddyan | C2103D | 11 |  | BD014018 | 1 | 11333.82 | 11532.03 | 198.21 | 1000 |  | 198210 | 199284.0218 | Satmasjid |  |  |  |  | Chand Uddyan | 199284.0218 | 192625.8492 | 6658.1726 | 3.4565 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4416 | 1 | 1995.36 | 2028.09 | 32.73 | 100 |  | 3273 | 3290.7351 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3290.7351 | 4108.3199 | -817.5848 | -19.9007 | OK
25 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4412 | 1 | 284.73 | 284.73 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 7679330 | 7637943 | 7679330 | 0.54186
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 4902574.9495
[6 empty] | Satmasjid | at 33 KV level |  | 2776755.0505
[6 empty] | Total = |  |  | 7679330 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
#REF! | #REF! |  | #REF! | IMPORT | #REF! | 1 | 13.502 | 18.567 | 5.065 | 180000 | 0 | 911700
#REF! | #REF! |  | #REF! |  | #REF! | 1 | 59.739 | 87.514 | 27.775 | 180000 | 0 | 4999500
#REF! | #REF! |  | #REF! |  |  | 1 | 0 | 0 | 0 | 180000 | 0 | 0
14 | Transformer-1 |  | 33 |  | 50147586E | 1 | 3362.081 | 3390.442 | 28.361 | 750000 | 0 | 21270750
15 | Transformer-2 |  | 33 |  | 50148569E | 1 | 3005.354 | 3034.23 | 28.876 | 750000 | 0 | 21657000
|  |  | 9=8-7: Total Import/Export | 0 | 48838950
|  |  | 10: Net Total | 48838950
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | 4: RECEIVE; 6: 1; 9=8-7: 0
| 33 KV GT-2 Incomming |  | 6: 1; 9=8-7: 0
| 33 KV Satmosjid-1 Incomming |  | 6: 1; 9=8-7: 0
Total Import/Export
|  |  | 9=8-7: Net Total | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 4: EXPORT |  | 0
| Feeder No.2 | [10 empty] | 0
|  |  | 10: Total |  | 0
SATMOSJID 132 KV SIDE
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 4: 48838950; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 48838950
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 48838950 | 33 KV NET IMPORT |  | 48838950
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 48838950
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming |  | 33 |  | 50147586 | 1 | 3232.217 | 3232.217 | 0 | 750000 | 0
10 | 132/33 kV, 80/120 MVA GT-2 Incoming |  | 33 |  | 50148569 | 1 | 2873.592 | 2873.592 | 0 | 750000 | 0
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 48838950
| SATMOSJID 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SICAM | 1 | 4214 | 4214 | 0 | 1000 | From Downstream | 5871600 | 5728486.8994 |  | -0.037889 | Satmasjid 3/11 kv ss | 11616781.3732 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 5728486.8994 | 6999151.4492 | -1270664.5498 | -18.1546 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SICAM | 1 | 4298 | 4298 | 0 | 1000 | From Downstream | 6035400 | 5888294.4738 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 5888294.4738 | 6461278.2194 | -572983.7456 | -8.868 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 11907000 | 11616781.3732 | [5 empty] | 33 KV Feeders | 11616781.3732 | 13460429.6686 | -1843648.2954 | -13.6968 | OK
6 | BGB |  | 33 |  | 214393/40-2711 | 1 | 8456.954 | 8456.954 | 0 | 1000 | From Downstream | 8935650 | 8717854.4115 |  | 0.93986 | BGB 33/11 KV SS | 8717854.4115 |  | BGB | 8717854.4115 | 9417344.3181 | -699489.9066 | -7.4277 | OK
| Asad Gate Circuit-1 |  | 33 |  | 214393/44-2711 | 1.5 | 7383.4 | 7383.4 | 0 | 1000 | Estimated | 5022116.1 | 4899708.1351 |  | 1.0914 | ASADGATE 33/11 KV SS | 9671667.6757 |  | Asad Gate Circuit-1 | 4899708.1351 | 4959942.6981 | -60234.563 | -1.2144 | OK
8 | Lalmatia Circuit-2 |  | 33 |  | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 6749190 | 6584686.7117 |  | 0.67882 | LALMATIA 33/11 KV SS | 6584686.7117 |  | Lalmatia Circuit-2 | 6584686.7117 | 7271666.7283 | -686980.0166 | -9.4474 | OK
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 4891176 | 4771959.5406 |  | 0.17082 | JIGATOLA OLD 33/11 KV SS | 1527830.6568 |  | Asad Gate Circuit-2 | 4771959.5406 | 4082325.4035 | 689634.1371 | 16.8932 | OK
13 | Jigatola U/G Circuit |  | 33 |  | 214393/37-2711 | 1 | 49.8277 | 49.8277 | 0 | 1000 | Estimated | 1566000 | 1527830.6568 |  | -0.66628 | JAPAN GARDEN 33/11 KV SS | 10720129.171 |  | Jigatola U/G Circuit | 1527830.6568 | 1556718.9285 | -28888.2717 | -1.8557 | OK
14 | Japan Garden City-2 |  | 33 |  | SICAM | 0.95 | 41020 | 41020 | 0 | 1000 | Estimated | 10987947 | 10720129.171 | [5 empty] | Japan Garden City-2 | 10720129.171 | 8385812.2548 | 2334316.9163 | 27.8365 | OK
|  |  | 10: Total |  | 38152079.1 | 37222168.6268 | [5 empty] | 0 | 37222168.6268 | 35673810.3314 | 1548358.2954 | 4.3403 | OK
|  |  | 9=8-7: Grand Total | 48838950 | 50059079.1 | 48838950 | -2.4374
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming |  | 11 |  | DHK60998 | 1 | 5089.6 | 5122.22 | 32.62 | 180000 | 5871600 |  | 5728486.8994
24 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61044 | 1 | 5183.51 | 5217.04 | 33.53 | 180000 | 6035400 |  | 5888294.4738
|  |  | 7: 0; 8: 0; 10: Total | 11907000 |  | 11616781.3732
| SATMOSJID 11 kV SIDE |  | 7: 0; 8: 0
16 | Lalmatia O/H | C209M | 11 |  | DHK61042 | 1 | 3244.77 | 3253.63 | 8.86 | 60000 |  | 531600 | 531398.58 | Satmasjid |  |  |  |  | Lalmatia O/H | 531398.58 | 719262.1967 | -187863.6168 | -26.1189 | OK
16 | Asad Avenue (South) | C209C | 11 |  | DHK 60999 | 1 | 2969.85 | 2978.17 | 8.32 | 60000 |  | 499200 | 499010.8562 | Satmasjid |  |  |  |  | Asad Avenue (South) | 499010.8562 | 585545.3707 | -86534.5145 | -14.7784 | OK
17 | Madrasha Road |  | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | C209H | 11 |  | DHK61002 | 1 | 2492.43 | 2503.14 | 10.71 | 60000 |  | 642600 | 642356.5228 | Satmasjid |  |  |  |  | Bashbari | 642356.5228 | 901214.7728 | -258858.2501 | -28.7233 | OK
19 | Road-27 | C209A | 11 |  | DHK61001 | 1 | 1492.16 | 1496.32 | 4.16 | 60000 |  | 249600 | 249505.4281 | Satmasjid |  |  |  |  | Road-27 | 249505.4281 | 529982.6713 | -280477.2432 | -52.922 | CHECK
20 | Boishakhi O/H | D209O | 11 |  | DHK61024 | 1 | 4293.22 | 4312.61 | 19.39 | 60000 |  | 1163400 | 1162959.1948 | Dhanmondi |  |  |  |  | Boishakhi O/H | 1162959.1948 | 1117359.7793 | 45599.4155 | 4.081 | OK
21 | Katasur O/H | C209K | 11 |  | DHK61003 | 1 | 3717.15 | 3729.42 | 12.27 | 60000 |  | 736200 | 735921.0583 | Satmasjid |  |  |  |  | Katasur O/H | 735921.0583 | 726589.1461 | 9331.9122 | 1.2843 | OK
22 | Nurjahan Road | D409I | 11 |  | DHK61000 | 1 | 1938.98 | 1950.01 | 11.03 | 60000 |  | 661800 | 661549.248 | Shyamoli |  |  |  |  | Nurjahan Road | 661549.248 | 774214.317 | -112665.069 | -14.5522 | OK
25 | polpar over head | D209W | 11 |  | DHK61003 | 1 | 1967.39 | 1983.57 | 16.18 | 60000 |  | 970800 | 970432.1698 | Dhanmondi |  |  |  |  | polpar over head | 970432.1698 | 1105758.7761 | -135326.6064 | -12.2383 | OK
26 | Satmosjid Housing | C209S | 11 |  | DHK61043 | 1 | 2887.27 | 2899.56 | 12.29 | 60000 |  | 737400 | 737120.6036 | Satmasjid |  |  |  |  | Satmosjid Housing | 737120.6036 | 999518.0102 | -262397.4066 | -26.2524 | OK
27 | Physical College | C209P | 11 |  | DHK61041 | 1 | 3473.23 | 3495.45 | 22.22 | 60000 |  | 1333200 | 1332694.8586 | Satmasjid |  |  |  |  | Physical College | 1332694.8586 | 1441577.2891 | -108882.4304 | -7.553 | OK
28 | Asad Avenue (North) | D409V | 11 |  | DHK61022 | 1 | 2754.07 | 2765.66 | 11.59 | 60000 |  | 695400 | 695136.5172 | Shyamoli |  |  |  |  | Asad Avenue (North) | 695136.5172 | 798026.9025 | -102890.3853 | -12.8931 | OK
29 | Spare Feeder |  | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | D209Z | 11 |  | DHK61023 | 1 | 1204.49 | 1222.87 | 18.38 | 60000 |  | 1102800 | 1102382.1558 | Dhanmondi |  |  |  |  | Ghraphic artch college | 1102382.1558 | 986695.8488 | 115686.3069 | 11.7246 | OK
31 | Mohammadpur O/H | D409W | 11 |  | DHK61025 | 1 | 2305.67 | 2322.25 | 16.58 | 60000 |  | 994800 | 994423.0763 | Shyamoli |  |  |  |  | Mohammadpur O/H | 994423.0763 | 1276110.3491 | -281687.2727 | -22.0739 | OK
32 | Bosila Feeder | C209V | 11 |  | DHK60997 | 1 | 4283.2 | 4309.7 | 26.5 | 60000 |  | 1590000 | 1589397.5587 | Satmasjid |  |  |  |  | Bosila Feeder | 1589397.5587 | 1495308.2511 | 94089.3075 | 6.2923 | OK
33 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIB 7375 | 1 | 6273.9 | 6319.12 | 45.22 | 60 |  | 2713.2 | 2712.172 | Satmasjid |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 2712.172 | 3265.9877 | -553.8157 | -16.9571 | OK
|  |  | 10: Total | 11907000 | 11911513.2 | 11907000 | -0.037889
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Satmasjid | at 33 KV level |  | 6320117.6382
[6 empty] | Shyamoli | at 33 KV level |  | 2351108.8415
[6 empty] | Dhanmondi | at 33 KV level |  | 3235773.5204
[6 empty] | Total = |  |  | 11907000 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 |  | 33 |  | 38992490 (new) | 1 | 1.581 | 4.837 | 3.256 | 180000 | 0 | 586080 | 586080
| Kallyanpur to Japangarden-2 |  | 33 |  | 8993669E | 1 | 1.39 | 1.39 | 0 | 180000 | 0 | 0 | 0
14 | Japan Garden City-2 |  | 33 |  | SICAM | 0.95 | 41020 | 41020 | 0 | 1000 | Estimated | 10987947 | 10720129.171
|  |  | 10: Total | 0 | 11574027 | 11306209.171
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G |  | 33 | RECEIVE | DHK86051 | 1 | 3112.36 | 3133.27 | 20.91 | 270000 |  | 5645700
| kallyanpur U/G-2 |  | 33 |  | DHK61100 | 1 | 2982.15 | 3000.66 | 18.51 | 270000 |  | 4997700
|  |  | 7: 0; 8: 0; 10: Total |  | 10643400
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33 KV Japan Genden City |  | 33 |  | DHK15681 | 1 | 855.55 | 907.12 | 51.57 | 18000 |  | 928260 | 928260 | Adabor | Customer Number:- 27111298
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 928260
[7 empty] | 0 | 0
| JAPAN GERDEN CITY 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61080 | 1 | 4446.24 | 4474.35 | 28.11 | 180000 |  | 5059800
3 | 33/11 kV 20/28 MVA T-1 (HV) |  | 33 |  | 86052 | 1 | 5230.9 | 5261.89 | 30.99 | 180000 |  | 5578200 |  |  | Check Meter
|  |  | 10: Total |  | 10638000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 4: 11566260; 6: Adabor NOCS; 9=8-7: 928260 | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 10638000
| IMPORT-2 |  | 6: JAPAN GERDEN CITY 33 KV NET IMPORT; 9=8-7: 10638000 | 33 KV TX HV SIDE |  | 10638000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 11566260
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK61079 | 1 | 5900.62 | 5935.65 | 35.03 | 160000 | 5604800 |  | 5576075.7145
10 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK61082 | 1 | 4950.73 | 4982.53 | 31.8 | 160000 | 5088000 |  | 5061924.2855
|  |  | 7: 0; 8: 0; 10: Total | 10692800 | 10643400 | 10638000
| JAPAN GERDEN CITY 11 KV SIDE |  | 7: 0; 8: 0
5 | Dhaka Uddyan | G186D | 11 |  | DHK86067 | 1 | 3255.51 | 3255.51 | 0 | 60000 |  | 0 | 0 | Adabor |  |  |  |  | Dhaka Uddyan | 0 | 31800 | -31800 | -100 | CHECK
| Shia Mosjid | D409H | 11 |  | DHK60950 | 1 | 3612.35 | 3634.81 | 22.46 | 60000 |  | 1347600 | 1338621.2464 | Shyamoli |  |  |  |  | Shia Mosjid | 1338621.2464 | 1173600 | 165021.2464 | 14.0611 | OK
6 | Shekhar Tek | G186S | 11 |  | DHK60977 | 1 | 2492.28 | 2516.63 | 24.35 | 60000 |  | 1461000 | 1451265.6879 | Adabor |  |  |  |  | Shekhar Tek | 1451265.6879 | 1188600 | 262665.6879 | 22.0987 | OK
7 | Madrasha Road | D434D | 11 |  | DHK61083 | 1 | 2126.47 | 2148.2 | 21.73 | 60000 |  | 1303800 | 1295113.0759 | Shyamoli |  |  |  |  | Madrasha Road | 1295113.0759 | 1098000 | 197113.0759 | 17.952 | OK
8 | Baitul Aman Housing | G186B | 11 |  | DHK668115 | 1 | 4293.9 | 4319.47 | 25.57 | 60000 |  | 1534200 | 1523977.9729 | Adabor |  |  |  |  | Baitul Aman Housing | 1523977.9729 | 1475400 | 48577.9729 | 3.2925 | OK
11 | Shyamoli Square | D486G | 11 |  | DHK86063 | 1 | 487.51 | 491.2 | 3.69 | 30000 |  | 110700 | 109962.431 | Shyamoli |  |  |  |  | Shyamoli Square | 109962.431 | 85500 | 24462.431 | 28.611 | OK
12 | Mohammadi Housing | G186E | 11 |  | DHK60948 | 1 | 3904.19 | 3920.87 | 16.68 | 60000 |  | 1000800 | 994131.8963 | Adabor |  |  |  |  | Mohammadi Housing | 994131.8963 | 1027200 | -33068.1037 | -3.2192 | OK
13 | Chand Housing | C286H | 11 |  | DHK60867 | 1 | 2244.2 | 2258.48 | 14.28 | 60000 |  | 856800 | 851091.3357 | Satmasjid |  |  |  |  | Chand Housing | 851091.3357 | 627600 | 223491.3357 | 35.6105 | OK
14 | PC Culture Housing |  | 11 |  | DHK60979 | 1 | 4268.17 | 4290.89 | 22.72 | 60000 |  | 1363200 | 1354117.3072 | Adabor |  |  |  |  | PC Culture Housing | 1354117.3072 | 1334400 | 19717.3072 | 1.4776 | OK
15 | Mehedibagh | G186H | 11 |  | DHK68121 | 1 | 2501.63 | 2530.44 | 28.81 | 60000 |  | 1728600 | 1717082.7297 | Adabor |  |  |  |  | Mehedibagh | 1717082.7297 | 1638000 | 79082.7297 | 4.828 | OK
16 | 33/11 kV Incoming (Spare) |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 |  | 0 | 0 | Adabor |  |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer |  | 11 |  |  | 1 | 670790 | 673444 | 2654 | 1 |  | 2654 | 2636.317 | Adabor |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 2636.317 | 3179 | -542.683 | -17.0709 | OK
|  |  | 10: Grand Total | 10638000 | 10709354 | 10638000 | -0.66628
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Adabor | at 33 KV level |  | 7043211.911
[6 empty] | Shyamoli | at 33 KV level |  | 2743696.7533
[6 empty] | Satmasjid | at 33 KV level |  | 851091.3357
[6 empty] | Total = |  |  | 10638000 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) |  | 132 |  | 42627810 | 1 | 250.518 | 268.606 | 18.088 | 960000 | 0 | 17364480
2 | Dhaka University-1 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) |  | 132 |  | 42627812 | 1 | 253.056 | 271.08 | 18.024 | 960000 | 0 | 17303040
3 | Dhaka University-2 (Imp) |  | 132 |  |  | 1 | 0.001 | 0.001 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 34667520
|  |  | 10: Net Total | 34667520
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 |  | 132 |  | 2877 | 1 | 200.47 | 214.98 | 14.51 | 1200000 | 17412000
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 156.45 | 179.01 | 22.56 | 1200000 |  | 27072000
| 132 kV Rampura 2 |  | 132 |  | 2811 | 1 | 202.4 | 216.85 | 14.45 | 1200000 | 17340000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 34752000 | 27072000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 7680000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhanmondi |  | 132 | 0 | SIEM0480 | 1 | 187780 | 215012 | 27232 | 1000 |  | 27232000
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 27232000
| DHAKA UNIVERSITY 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | 2752 | 1 | 231.09 | 234.19 | 3.1 | 1200000 |  | 3720000
4 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | 2867 | 1 | 249.06 | 252.18 | 3.12 | 1200000 |  | 3744000
|  |  | 10: Total |  | 7464000 | 34536000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 34667520; 6: EXPORT TO OTHER S/S; 9=8-7: 27232000 | 132 KV NET IMPORT |  | 7464000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 7464000 | 33 KV NET IMPORT |  | 7358400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 105600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.415%
| 132 KV TOTAL IMPORT |  | 4: 34667520
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  | 2769 | 1 | 382.12 | 387.19 | 5.07 | 720000 | 3650400
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  | 2830 | 1 | 411.44 | 416.59 | 5.15 | 720000 | 3708000
|  |  | 7: 0; 8: 0; 10: Total | 7358400 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  | 2751 | 1 | 41.35 | 42.02 | 0.67 | 240000 | From Downstream | 267500 | 268520.7356 |  | 2.0831 | DHAKA UNIVERSITY 33/11 KV SS | 969585.7143 |  | 33/11 kV 28/35 MVA T-1 | 268520.7356 | 162356.6007 | 106164.1349 | 65.3895 | FAULT
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  | 4253 | 1 | 69.55 | 71.4 | 1.85 | 240000 |  | 444000 | 445694.2304 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 445694.2304 | 382870.7898 | 62823.4406 | 16.4085 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  | 2808 | 1 | 28.72 | 29.78 | 1.06 | 240000 |  | 254400 | 255370.7482 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 255370.7482 | 264132.3803 | -8761.6321 | -3.3171 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 965900 | 969585.7143 | [5 empty] | 33 KV Feeders | 969585.7143 | 809359.7709 | 160225.9434 | 19.7966 | OK
2 | Spare |  | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 |  | 33 |  | 2804 | 1.4 | 192.5 | 197.68 | 5.18 | 360000 |  | 2610720 | 2620682.0747 |  | 0.053253 | BB AVENUE 33/11 KV SS | 4017030.0527 |  | BB Avenue-1 | 2620682.0747 | 2840634.7048 | -219952.6301 | -7.7431 | OK
3 | DMC Circuit-1 |  | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 | [5 empty] | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 |  | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | -0.045279 | DMC 33/11 KV SS | 2454992.2331 |  | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 |  | 33 |  | 2753 | 1 | 431.64 | 431.64 | 0 | 360000 |  | 0 | 0 | [5 empty] | Biddyut Bhaban Circuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | DMC Circuit-2 |  | 33 |  | 2803 | 1.05 | 346.28 | 352.75 | 6.47 | 360000 |  | 2445660 | 2454992.2331 |  | 0.48467 | BIDDYUT BHABAN 33/11 KV SS | 0 |  | DMC Circuit-2 | 2454992.2331 | 2354837.0998 | 100155.1333 | 4.2532 | OK
11 | BB Avenue-2 |  | 33 |  | 2820 | 1.2 | 217.85 | 221.07 | 3.22 | 360000 |  | 1391040 | 1396347.978 | [5 empty] | BB Avenue-2 | 1396347.978 | 1123168.4245 | 273179.5535 | 24.3222 | OK
12 | Spare |  | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 6447420 | 6472022.2857 | [5 empty] | 0 | 6472022.2857 | 6318640.2291 | 153382.0566 | 2.4275 | OK
|  |  | 9=8-7: Grand Total | 7441608 | 7413320 | 7441608 | 0.38158
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 52.59 | 53.66 | 1.07 | 250000 | 267500 |  | 273014.9248
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 65.07 | 66.82 | 1.75 | 250000 | 437500 |  | 446519.7368
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 26.51 | 27.49 | 0.98 | 250000 | 245000 |  | 250051.0526
|  |  | 7: 0; 8: 0; 10: Total | 950000 |  | 969585.7143
| DHAKA UNIVERSITY 11 kV SIDE |  | 7: 0; 8: 0
| Mokarom Bhabon | D3108MB | 11 |  | 2761 | 1 | 67.48 | 69.76 | 2.28 | 60000 |  | 136800 | 139649.7428 | Ramna |  |  |  |  | Mokarom Bhabon | 139649.7428 | 117558.3864 | 22091.3564 | 18.7918 | OK
4 | 11 kV Shaid Minar RMU | D3108SM | 11 |  | 2850 | 1 | 150.87 | 153.05 | 2.18 | 60000 |  | 130800 | 133524.7541 | Ramna |  |  |  |  | 11 kV Shaid Minar RMU | 133524.7541 | 112160.2972 | 21364.4568 | 19.0481 | OK
5 | 11 kV Shaidulla Hall | D3108SH | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | D3108MA | 11 |  | 2836 | 1 | 110.14 | 112.26 | 2.12 | 60000 |  | 127200 | 129849.7608 | Ramna |  |  |  |  | MBA Bhabon | 129849.7608 | 100164.5435 | 29685.2173 | 29.6365 | OK
11 | Suprime Court |  | 11 |  | 2835 | 1 | 75.41 | 77.13 | 1.72 | 60000 |  | 103200 | 105349.806 | Ramna |  |  |  |  | Suprime Court | 105349.806 | 97165.6051 | 8184.2009 | 8.4229 | OK
12 | Karjon Hall | D3108KH | 11 |  | 2853 | 1 | 82.55 | 85.39 | 2.84 | 60000 |  | 170400 | 173949.6796 | Ramna |  |  |  |  | Karjon Hall | 173949.6796 | 164341.8259 | 9607.8537 | 5.8463 | OK
13 | Spare |  | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | D3108SP | 11 |  | 2839 | 1 | 3.1 | 3.36 | 0.26 | 60000 |  | 15600 | 15924.9707 | Ramna |  |  |  |  | Swimming Pool | 15924.9707 | 10196.3907 | 5728.58 | 56.1824 | FAULT
15 | Spare |  | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU |  | 11 |  | 2772 | 1 | 106.3 | 110 | 3.7 | 60000 |  | 222000 | 226624.5826 | Ramna |  |  |  |  | Police Head Quarter RMU | 226624.5826 | 197929.9363 | 28694.6463 | 14.4974 | OK
17 | Spare |  | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare |  | 11 |  | 2764 | 1 | 4.08 | 4.81 | 0.73 | 60000 |  | 43800 | 44712.4177 | Ramna |  |  |  |  | Spare | 44712.4177 | 47983.0149 | -3270.5972 | -6.8162 | OK
19 | Spare |  | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 969585.7143 | 949800 | 969585.7143 | 2.0831
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 969585.7143
[6 empty] | Total = |  |  | 969585.7143 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 |  | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 |  | 33 | 0 | 2753 | 1 | 431.64 | 431.64 | 0 | 360000 | 0 | 0 | 0
| Motijheel Old 33 KV Side (Sending) |  | 10: Total | 0 | 0 | 0
| Motijheel Incoming |  | 33 | 0 | DHK-C9344 | 1 | 83333.72 | 88488.373 | 5154.653 | 270 | 0 | 1391756.31 |  | 0
P&T 33 KV Side (Sending)
| P&T Incoming |  | 33 | Export | BD017079 | 1 | 4739 | 6498 | 1759 | 1000 | 0 | 1759000
|  |  | 10: Total |  | 3150756.31
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 83333.72 | 88488.373 | 5154.653 | 270 | 0 | 1391756.31
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 21216.28 | 21216.28 | 0 | 270 |  | 0
| Dhaka University Incoming-1 |  | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 | From P&T END | 1759000
| Dhaka University Incoming-2 |  | 33 |  | DHK-C9343 | 1 | 76529.93 | 76529.93 | 0 | 270 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 3150756.31 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 |  | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-C9342 | 1 | 15299.16 | 20452.6 | 5153.44 | 270 |  | 1391428.8
3 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK-C9308 | 1 | 80333.67 | 86556.34 | 6222.67 | 270 |  | 1680120.9
|  |  | 10: Total |  | 3071549.7 | 3071549.7
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 4: 3150756.31; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3150756.31
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 3150756.31 | 33 KV TX HV SIDE |  | 3071549.7
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 79206.61
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.514%
| TOTAL IMPORT |  | 4: 3150756.31
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK-C9316 | 1 | 100122.47 | 100122.47 | 0 | 240 | 0 |  | 0
10 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK-C9377 | 1 | 38452.2 | 45430.27 | 6978.07 | 240 | 1674736.8 |  | 3150756.31
|  |  | 7: 0; 8: 0; 10: Total | 1674736.8 |  | 3150756.31
| BIDDYUT BHABAN 11 KV SIDE |  | 7: 0; 8: 0
6 | Segunbagicha | D394S | 11 |  | DHK-C9360 | 1 | 31840.5 | 36770.24 | 4929.74 | 60 |  | 295784.4 | 297217.9806 | Ramna |  |  |  |  | Segunbagicha | 297217.9806 | 341401.7306 | -44183.7499 | -12.9419 | OK
| Secretariat RMU | D394FB | 11 |  | DHK-C9379 | 1 | 84355.2 | 85730.16 | 1374.96 | 60 |  | 82497.6 | 82897.4418 | Ramna |  |  |  |  | Secretariat RMU | 82897.4418 | 71931.4615 | 10965.9803 | 15.245 | OK
7 | NBR RMU | D394NR | 11 |  | DHK-C9319 | 1 | 86985.63 | 90868.82 | 3883.19 | 60 |  | 232991.4 | 234120.6413 | Ramna |  |  |  |  | NBR RMU | 234120.6413 | 264247.6855 | -30127.0442 | -11.4011 | OK
8 | Ramna 11 kV Sw/S-2 |  | 11 |  | DHK-C9364 | 1 | 84979.32 | 97750.53 | 12771.21 | 60 |  | 766272.6 | 769986.4995 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-2 | 769986.4995 | 654039.5407 | 115946.9588 | 17.7278 | OK
11 | Ramna 11 kV Sw/S-1 |  | 11 |  | DHK-C9375 | 1 | 57712.71 | 58182.9 | 470.19 | 60 |  | 28211.4 | 28348.1324 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-1 | 28348.1324 | 0 | 28348.1324 | #DIV/0! | #DIV/0!
12 | Family Planning | D394FP | 11 |  | DHK-C9378 | 1 | 85649.71 | 89440.33 | 3790.62 | 60 |  | 227437.2 | 228539.5217 | Ramna |  |  |  |  | Family Planning | 228539.5217 | 220696.2725 | 7843.2492 | 3.5539 | OK
13 | Muktijuddho Montranalaya | D394MJ | 11 |  | DHK-C9376 | 1 | 15380.32 | 23102.1 | 7721.78 | 60 |  | 463306.8 | 465552.3128 | Ramna |  |  |  |  | Muktijuddho Montranalaya | 465552.3128 | 463016.929 | 2535.3838 | 0.54758 | OK
14 | Purana Palton | D394R | 11 |  | DHK-C9318 | 1 | 77924.2 | 81427.53 | 3503.33 | 60 |  | 210199.8 | 211218.577 | Ramna |  |  |  |  | Purana Palton | 211218.577 | 201300.5118 | 9918.0653 | 4.927 | OK
15 | Tip Top Feeder |  | 11 |  | DHK-C9318 | 1 | 15769.02 | 28227.41 | 12458.39 | 60 |  | 747503.4 | 751126.3307 | Kakrail |  |  |  |  | Tip Top Feeder | 751126.3307 | 665458.2263 | 85668.1044 | 12.8736 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT |  | 0.415 |  | DHKD3784 | 1 | 366020 | 368550 | 2530 | 1 |  | 2530 | 2542.2622 | Ramna |  |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 2542.2622 | 2880.0422 | -337.7801 | -11.7283 | OK
|  |  | 10: Grand Total | 3071549.7 | 3056734.6 | 3071549.7 | 0.48467
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2320423.3693
[6 empty] | Kakrail | at 33 KV level |  | 751126.3307
[6 empty] | Total = |  |  | 3071549.7 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 |  | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 |  | 33 | 0 | 2803 | 1.05 | 346.28 | 352.75 | 6.47 | 360000 | 0 | 2445660 | 2454992.2331
|  |  | 10: Total | 0 | 2445660 | 2454992.2331
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder |  | 33 | 0 | BD001840 | 1 | 484.37 | 493.4 | 9.03 | 240000 | 0 | 2167200 | 2171527.5927
|  |  | 10: Total |  | 2167200 | 2171527.5927
| DMCH 33 KV SIDE (RECEIVING) | [11 empty] | 4626519.8258
| 33 kV DU Incoming Circuit-1 |  | 33 |  | 00000072 | 1 | 3279890 | 3279890 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming |  | 33 |  | 00000082 | 1 | 6136720 | 8389870 | 2253150 | 1 |  | 2253150
| 33 kV DU Incoming Circuit-2 |  | 33 |  | 00000081 | 1 | 4467300 | 6859230 | 2391930 | 1 |  | 2391930
|  |  | 7: 0; 8: 0; 10: Total |  | 4645080 | 0
| DMCH 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DMCH 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | 00000069 | 1 | 2928160 | 5181760 | 2253600 | 1 |  | 2253600
2 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | 00000088 | 1 | 9894400 | 9894400 | 0 | 1 |  | 0
|  |  | 10: Total |  | 2253600
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 4: 2454992.2331; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4626519.8258
| DHANMONDI 33 kV SIDE |  | 4: 2171527.5927; 6: 33 KV NET IMPORT; 9=8-7: 4626519.8258 | 33 KV TX HV SIDE |  | 4626519.8258
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 4626519.8258
11 KV SIDE of___DMCH 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000056 | 1 | 141632672 | 143778864 | 2146192 | 1 | 2146192 |  | 2232032.0312
14 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000034 | 1 | 170034288 | 172336688 | 2302400 | 1 | 2302400 |  | 2394487.7945
|  |  | 7: 0; 8: 0; 10: Total | 4448592 |  | 4626519.8258
| DMCH 11 KV SIDE |  | 7: 0; 8: 0
6 | Nearest O/H | D398NE | 11 |  | 00000126 | 1 | 8336299 | 8445459 | 109160 | 1 |  | 109160 | 109110.5738 | Ramna |  |  |  |  | Nearest O/H | 109110.5738 | 103620.5102 | 5490.0636 | 5.2982 | OK
| Jagannath Hall | D398JA | 11 |  | 00000002 | 1 | 3181672 | 3244072 | 62400 | 1 |  | 62400 | 62371.7461 | Ramna |  |  |  |  | Jagannath Hall | 62371.7461 | 64828.5411 | -2456.7949 | -3.7897 | OK
7 | Samsun Nahar Hall | D398SN | 11 |  | 00000024 | 1 | 10868893 | 11037013 | 168120 | 1 |  | 168120 | 168043.8775 | Ramna |  |  |  |  | Samsun Nahar Hall | 168043.8775 | 181366.9249 | -13323.0473 | -7.3459 | OK
8 | Spare, 4L |  | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | A3983 | 11 |  | 00000023 | 1 | 23859342 | 24059182 | 199840 | 1 |  | 199840 | 199749.5152 | Lalbag |  |  |  |  | Board Office O/H, (5L) | 199749.5152 | 222501.681 | -22752.1658 | -10.2256 | OK
10 | OT- Complex | D398OT | 11 |  | 00000167 | 1 | 7522541 | 7697461 | 174920 | 1 |  | 174920 | 174840.7986 | Ramna |  |  |  |  | OT- Complex | 174840.7986 | 155370.7198 | 19470.0788 | 12.5314 | OK
11 | Alia Mdrasha O/H, (7L) | A3984 | 11 |  | 00000148 | 1 | 10039575 | 10103615 | 64040 | 1 |  | 64040 | 64011.0036 | Lalbag |  |  |  |  | Alia Mdrasha O/H, (7L) | 64011.0036 | 42908.876 | 21102.1276 | 49.1789 | FAULT
12 | Majed Sordar Road | B698J | 11 |  | 00000164 | 1 | 64831840 | 66168440 | 1336600 | 1 |  | 1336600 | 1335994.8057 | Bangshal |  |  |  |  | Majed Sordar Road | 1335994.8057 | 1324591.4203 | 11403.3854 | 0.8609 | OK
15 | Chankharpool, 9L | B698Q | 11 |  | 00000001 | 1 | 52091712 | 52823192 | 731480 | 1 |  | 731480 | 731148.7958 | Bangshal |  |  |  |  | Chankharpool, 9L | 731148.7958 | 644572.6762 | 86576.1196 | 13.4316 | OK
16 | Shahidullah College O/H, (10L) | A3986 | 11 |  | 00000003 | 1 | 14293560 | 14564044 | 270484 | 1 |  | 270484 | 270361.5285 | Lalbag |  |  |  |  | Shahidullah College O/H, (10L) | 270361.5285 | 292007.2179 | -21645.6893 | -7.4127 | OK
17 | Ananda Bazar | D398AB | 11 |  | 00000111 | 1 | 15493882 | 15623002 | 129120 | 1 |  | 129120 | 129061.5362 | Ramna |  |  |  |  | Ananda Bazar | 129061.5362 | 67251.0523 | 61810.4839 | 91.9101 | FAULT
18 | Hosseni Dalan O/H, (12L) | A3985 | 11 |  |  | 1 | 69.55 | 71.4 | 1.85 | 60000 | Estimated | 573456.6 | 573196.9466 | Lalbag | Load |  |  |  | Hosseni Dalan O/H, (12L) | 573196.9466 | 347228.9299 | 225968.0167 | 65.0775 | FAULT
19 | Badrun Nessa College | A398W | 11 |  | 00000006 | 1 | 21900706 | 22150383 | 249677 | 1 |  | 249677 | 249563.9496 | Lalbag |  |  |  |  | Badrun Nessa College | 249563.9496 | 261372.8699 | -11808.9203 | -4.518 | OK
20 | Dhaka Medical College, Unit-II | D398DM | 11 |  | 00000125 | 1 | 13442768 | 13442768 | 0 | 1 | Estimated | 217240 | 217141.6367 | Ramna | Load |  |  |  | Dhaka Medical College, Unit-II | 217141.6367 | 438463.9439 | -221322.3072 | -50.4767 | CHECK
21 | Spare, 15L |  | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | D398SH | 11 |  | 00000127 | 1 | 23060064 | 23402142 | 342078 | 1 |  | 342078 | 341923.1117 | Ramna |  |  |  |  | Sheikh Hasina National Burn Institute | 341923.1117 | 318090.2115 | 23832.9002 | 7.4925 | OK
23 | Aux. Transformer, AT-1 |  | 0.415 |  | DHKF-7804 | 1 | 2923.68 | 2923.68 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Aux. Transformer, AT-2 |  | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4626519.8258 | 4628615.6 | 4626519.8258 | -0.045279
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1202493.2807
[6 empty] | Lalbag | at 33 KV level |  | 1356882.9435
[6 empty] | Bangshal | at 33 KV level |  | 2067143.6015
[6 empty] | Total = |  |  | 4626519.8258 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 |  | 33 | 0 | 2804 | 1.4 | 192.5 | 197.68 | 5.18 | 360000 | 0 | 2610720 | 2620682.0747
11 | BB Avenue-2 |  | 33 |  | 2820 | 1.2 | 217.85 | 221.07 | 3.22 | 360000 | 0 | 1391040 | 1396347.978
|  |  | 10: Total | 0 | 4001760 | 4017030.0527
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 |  | 33 |  | BD 017078 | 1 | 33062.35 | 35556.74 | 2494.39 | 1125 |  | 2806188.75
| 33 kV Dhaka University-2 |  | 33 |  | BD 017090 | 1 | 78264.5 | 79493.3 | 1228.8 | 1125 |  | 1382400
|  |  | 7: 0; 8: 0; 10: Total | 0 | 4188588.75 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD 017093 | 1 | 116292.59 | 119107.5 | 2814.91 | 1000 |  | 2814910
3 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD 017094 | 1 | 63685.66 | 64917.7 | 1232.04 | 1000 |  | 1232040
|  |  | 10: Total |  | 4046950
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 4017030.0527; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BB AVENEU 33 KV NET IMPORT |  | 4017030.0527
|  |  | 6: BB AVENEU 33 KV NET IMPORT; 9=8-7: 4017030.0527 | 33 KV TX HV SIDE |  | 4046950
[11 empty] | LOSS UNITS=> |  | -29919.9473
[11 empty] | LOSS % IN => |  | -0.7448%
| TOTAL IMPORT |  | 4: 4017030.0527
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD 014052 | 1 | 116391.99 | 119176.2 | 2784.21 | 1000 | 2784210 |  | 2793668.2402
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD 014055 | 1 | 63081.78 | 64301 | 1219.22 | 1000 | 1219220 |  | 1223361.8125
|  |  | 7: 0; 8: 0; 10: Total | 4003430 |  | 4017030.0527
| BB AVENEU 11 KV SIDE |  | 7: 0; 8: 0
6 | Secratariet East | D363BS | 11 |  | BD 013966 | 1 | 4767.71 | 4874.78 | 107.07 | 1000 |  | 107070 | 107127.018 | Ramna |  |  |  |  | Secratariet East | 107127.018 | 107180.1737 | -53.1556 | -0.049595 | OK
| Taher Bag O/H | B163G | 11 |  | BD 014045 | 1 | 22237.12 | 22685.2 | 448.08 | 1000 |  | 448080 | 448318.6163 | Narinda |  |  |  |  | Taher Bag O/H | 448318.6163 | 502491.425 | -54172.8087 | -10.7808 | OK
7 | Al Raji Complex | D363AR | 11 |  | BD 013983 | 1 | 17531.62 | 17966.27 | 434.65 | 1000 |  | 434650 | 434881.4644 | Ramna |  |  |  |  | Al Raji Complex | 434881.4644 | 415679.6453 | 19201.8191 | 4.6194 | OK
8 | Raduni | D363RI | 11 |  | BD 013999 | 1 | 33159.17 | 33855.6 | 696.43 | 1000 |  | 696430 | 696800.8703 | Ramna |  |  |  |  | Raduni | 696800.8703 | 678307.0986 | 18493.7716 | 2.7265 | OK
9 | Sundor Bon Square O/H | B163D | 11 |  | BD 013954 | 1 | 15297.78 | 15663.4 | 365.62 | 1000 |  | 365620 | 365814.7038 | Narinda |  |  |  |  | Sundor Bon Square O/H | 365814.7038 | 358907.9483 | 6906.7555 | 1.9244 | OK
10 | Shromo Bhobon O/H | D363SB | 11 |  | BD 013985 | 1 | 15110.41 | 15350.3 | 239.89 | 1000 |  | 239890 | 240017.7488 | Ramna |  |  |  |  | Shromo Bhobon O/H | 240017.7488 | 224965.7144 | 15052.0343 | 6.6908 | OK
11 | Nawabpur Road | B163P | 11 |  | BD 013953 | 1 | 23709.12 | 24208.6 | 499.48 | 1000 |  | 499480 | 499745.9884 | Narinda |  |  |  |  | Nawabpur Road | 499745.9884 | 556908.629 | -57162.6406 | -10.2643 | OK
12 | Spair |  | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare |  | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | D363AP | 11 |  | BD 013984 | 1 | 13292.97 | 13673.3 | 380.33 | 1000 |  | 380330 | 380532.5373 | Ramna |  |  |  |  | Ahad Police Box | 380532.5373 | 329304.2587 | 51228.2787 | 15.5565 | OK
17 | Nearest O/H | D363NE | 11 |  | BD 013997 | 1 | 3134.09 | 3210.8 | 76.71 | 1000 |  | 76710 | 76750.8504 | Ramna |  |  |  |  | Nearest O/H | 76750.8504 | 76663.1031 | 87.7473 | 0.11446 | OK
18 | Natab Bhaban | D363NB | 11 |  | BD 014000 | 1 | 5718.35 | 5841.7 | 123.35 | 1000 |  | 123350 | 123415.6876 | Ramna |  |  |  |  | Natab Bhaban | 123415.6876 | 106896.0107 | 16519.6769 | 15.454 | OK
19 | Spare |  | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | D363AO | 11 |  | BD 013956 | 1 | 1466.68 | 1473.7 | 7.02 | 1000 |  | 7020 | 7023.7384 | Ramna |  |  |  |  | Awami League Party Office | 7023.7384 | 6921.3974 | 102.3409 | 1.4786 | OK
21 | Khaddar Bazar | D363KB | 11 |  | BD 014012 | 1 | 11770.14 | 12032.5 | 262.36 | 1000 |  | 262360 | 262499.7147 | Ramna |  |  |  |  | Khaddar Bazar | 262499.7147 | 245110.8375 | 17388.8772 | 7.0943 | OK
22 | Bangobondu National Stidium | D363NS | 11 |  | BD 014008 | 1 | 12229.98 | 12597.7 | 367.72 | 1000 |  | 367720 | 367915.8221 | Ramna |  |  |  |  | Bangobondu National Stidium | 367915.8221 | 347998.121 | 19917.7012 | 5.7235 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4418 | 1 | 1611.8 | 1673.62 | 61.82 | 100 |  | 6182 | 6185.2921 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 6185.2921 | 6468.7665 | -283.4744 | -4.3822 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 48.15 | 48.15 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4017030.0527 | 4014892 | 4017030.0527 | 0.053253
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2703150.7442
[6 empty] | Narinda | at 33 KV level |  | 1313879.3085
[6 empty] | Total = |  |  | 4017030.0527 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 |  | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
|  |  | 10: Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 |  | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 |  | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 |  | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 0
|  |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 0 | KALLYANPUR 11 KV NET IMPORT |  | 0
|  |  | 6: TOTAL EXPORT; 9=8-7: 0 | LOSS UNITS=> |  | 0
|  |  | 6: 132KV NET LOSS =>; 9=8-7: #DIV/0! | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 4: 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming |  | 11 |  | 74819926 | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  | 7: 0; 8: 0
A | From Kallyanpur S/S. |  | 7: 0; 8: 0
| 11 KV Gano Bhavan RMU | D534T | 11 |  | DHK14997 | 1 | 996.05 | 996.18 | 0.13 | 40000 |  | 5200 | 5330 | Shere b.nagar |  |  |  |  | 11 KV Gano Bhavan RMU | 5330 | 1640 | 3690 | 225 | FAULT
| 11 KV Beribandh Feeder. | G134K | 11 |  | DHK14960 | 1 | 9682.86 | 9688.09 | 5.23 | 40000 |  | 209200 | 214430 | Adabor |  |  |  |  | 11 KV Beribandh Feeder. | 214430 | 188190 | 26240 | 13.9434 | OK
| 11 KV Adabor O/H | D434A | 11 |  | DHK14957 | 1 | 4683.11 | 4698.53 | 15.42 | 40000 |  | 616800 | 632220 | Adabor |  |  |  |  | 11 KV Adabor O/H | 632220 | 865100 | -232880 | -26.9194 | OK
| 11 KV Mansurabad | G134M | 11 |  | 77816681 | 1 | 53300.91 | 53472.8 | 171.89 | 8000 |  | 1375120 | 1409498 | Adabor |  |  |  |  | 11 KV Mansurabad | 1409498 | 1315854 | 93644 | 7.1166 | OK
| 11 KV Ring Road Feeder | G134R | 11 |  | 77816675 | 1 | 42620.61 | 42702.034 | 81.424 | 8000 |  | 651392 | 667676.8 | Adabor |  |  |  |  | 11 KV Ring Road Feeder | 667676.8 | 639928 | 27748.8 | 4.3362 | OK
| 11 KV Sewarage Pump | G134P | 11 |  | DHK14959 | 1 | 2456.54 | 2510.39 | 53.85 | 40000 |  | 2154000 | 2207850 | Adabor |  |  |  |  | 11 KV Sewarage Pump | 2207850 | 2131590 | 76260 | 3.5776 | OK
| 11 KV Technical School (DPDC) | G134T | 11 |  | DHK15019 | 1 | 8461.48 | 8491.99 | 30.51 | 40000 |  | 1220400 | 1250910 | Adabor |  |  |  |  | 11 KV Technical School (DPDC) | 1250910 | 1184900 | 66010 | 5.5709 | OK
| 11 KV Goidertek (DPDC) | G134G | 11 |  | DHK14996 | 1 | 9445.51 | 9452.95 | 7.44 | 40000 |  | 297600 | 305040 | Adabor |  |  |  |  | 11 KV Goidertek (DPDC) | 305040 | 271830 | 33210 | 12.2172 | OK
B | From Agargaon S/S. |  | 3: 11 |  | 6529712 | 6692954.8
| 11 KV P.C Culture Housing | G186C | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H |  | 11 |  | DHK-15026 | 1 | 9242.88 | 9249.79 | 6.91 | 40000 |  | 276400 | 283310 | Shere b.nagar
| 11 KV Nearest RMU |  | 11 |  | DHK-15027 | 1 | 3882.98 | 3885.65 | 2.67 | 40000 |  | 106800 | 109470 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar |  | 11 |  | DHK-15025 | 1 | 3987.09 | 3987.82 | 0.73 | 40000 |  | 29200 | 29930 | Shere b.nagar
| 11 KV BICC Feeder. |  | 11 |  | DHK-15024 | 1 | 1038.93 | 1038.93 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV NEC Feeder. |  | 11 |  | DHK-15023 | 1 | 431.72 | 431.72 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV Manik Mia Feeder. |  | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
|  |  | 7: Export To Desco; 9=8-7: 0; 10: Grand Total |  | 412400 | 422710
[12 empty] | 6942112 | 7115664.8 | 2.5
DESCO | 11 kV Tolarbugh |  | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil |  | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy |  | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari |  | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H |  | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur |  | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S |  | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 0 | 0 | #DIV/0!
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 6687624.8
[6 empty] | Shere b.nagar | at 33 KV level |  | 428040
[6 empty] | Satmasjid | at 33 KV level
[6 empty] | DESCO | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 7115664.8 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 (Lalbagh Ckt-2) |  | 33 | 0 | 30799147 | 1 | 1646.33 | 1654.56 | 8.23 | 240000 | From Downstream | 2692800 | 5896959.6274
|  |  | 10: Total | 0 |  | 5896959.6274
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
|  |  | 10: Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming |  | 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
| Lalbagh Incoming |  | 3: 33; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 |  | 33 |  | BD017102 | 1 | 1561.83 | 1579.75 | 17.92 | 180000 |  | 3225600
1 | Transformer-02 |  | 33 |  | BD017105 | 1 | 2034.67 | 2049.63 | 14.96 | 180000 |  | 2692800
|  |  | 10: Total |  | 5918400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 5896959.6274; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 5896959.6274
| IMPORT-2 |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 5896959.6274 | KALLYANPUR 11 KV NET IMPORT |  | 5918400
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -21440.3726
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.3636%
| TOTAL IMPORT |  | 4: 5896959.6274
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 140
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 110
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 30
|  |  | 10: Total | 0 |  | 5918400 |  |  | 10
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 120
1 | Nizambag | F1114Z | 11 |  | 6604414 | 1 | 3907.2 | 3929.07 | 21.87 | 8000 | Estimated | 1592997.84 | 1600846.3691 | Kamrangirchar | 140 |  |  |  | Nizambag | 1600846.3691 | 853490.0177 | 747356.3514 | 87.5647 | FAULT
2 | Merry Stopes | F1114P | 11 |  | 6604287 | 1 | 21637.99 | 21649.31 | 11.32 | 8000 | Estimated | 284463.9 | 285865.4231 | Kamrangirchar | 25 |  |  |  | Merry Stopes | 285865.4231 | 98328.343 | 187537.08 | 190.7254 | FAULT
3 | Mujibur Ghat | F1114V | 11 |  | 6604387 | 1 | 4433.72 | 4433.72 | 0 | 8000 | Estimated | 313891.2 | 315437.7082 | Kamrangirchar | 80 | 10 days |  |  | Mujibur Ghat | 315437.7082 | 975417.1631 | -659979.4549 | -67.6613 | CHECK
4 | Madrasa | F1114U | 11 |  | 6604481 | 1 | 14283.77 | 14471.07 | 187.3 | 8000 | Estimated | 1592997.84 | 1600846.3691 | Kamrangirchar | 140 |  |  |  | Madrasa | 1600846.3691 | 1463125.7446 | 137720.6245 | 9.4128 | OK
5 | Thana | F1114Q | 11 |  | 6604443 | 1 | 10583.45 | 10693.55 | 110.1 | 8000 | Estimated | 1080962.82 | 1086288.6076 | Kamrangirchar | 95 |  |  |  | Thana | 1086288.6076 | 1158307.8811 | -72019.2735 | -6.2176 | OK
6 | Al-Hera |  | 11 |  | 6604372 | 1 |  | 0 | 0 | 8000 | Estimated | 227571.12 | 228692.3384 | Kamrangirchar | 20 |  |  |  | Al-Hera | 228692.3384 | 0 | 228692.3384 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | F1114W | 11 |  | 6604448 | 1 | 8387.85 | 8561.84 | 173.99 | 8000 | Estimated | 796498.92 | 800423.1845 | Kamrangirchar | 70 |  |  |  | Waz Uddin School | 800423.1845 | 853490.0177 | -53066.8331 | -6.2176 | OK
8 | 11/0.4 kV Auxiliary Transformer |  | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off |  | 10: Grand Total | 5918400 | 5889383.64 | 5918400 | 0.49269
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 5918400
[6 empty] | Total = |  |  | 5918400 | 0
33 KV SIDE of___ Bosila-1 (Shopnodanga) 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Kakrail Circuit-1 | 2457697.8956 | Month January-2024 | 893794.7699 | 57.1515 | FAULT
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | 1903-06-12 11:46 | 1903-06-19 01:26 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE Sending From Kamrangirchar 132/33
10 | Bossila-1 | 0 | 33 | 0 | 30799130 | 1 | 0 | 13.02 | 13.02 | 240000 | 0 | 3124800 | 3113479.9006 | 0
|  |  | 10: Total | 0 |  | 3113479.9006
Bosila-1 (Shopnodanga) 33 KV SIDE (RECEIVING)
33
|  |  | 10: Total | 0
Bosila-1 (Shopnodanga) 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming |  | 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
| Lalbagh Incoming |  | 3: 33; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0
Bosila-1 (Shopnodanga) 33 KV SIDE
| Transformer-01 |  | 33 |  | WP040129 | 1 | 304.43 | 459682 | 459377.57 | 1 |  | 459377.57
1 | Transformer-02 |  | 33 |  | WP040141 | 1 |  |  | 0 | 1 |  | 0
|  |  | 10: Total |  | 459377.57 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE Sending From Kamrangirchar 132/33 |  | 4: 3113479.9006; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 3113479.9006
| IMPORT-2 |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 3113479.9006 | KALLYANPUR 11 KV NET IMPORT |  | 3113479.9006
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 3113479.9006
11 KV SIDE of___Bosila-1 (Shopnodanga) 33/11 KV S/S | [14 empty] | Month February-2024 |  |  |  | Kakrail Circuit-1 | 2457697.8956 | Month January-2024 | 893794.7699 | 57.1515 | FAULT
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | 1903-06-12 11:46 | 1903-06-19 01:26 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Bosila-1 (Shopnodanga) 11 KV SIDE | [14 empty] | 140
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | WP042358 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 110
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | WP042359 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 30
|  |  | 10: Total | 0 |  | 3113479.9006 |  |  | 10
| Bosila-1 (Shopnodanga) 11 KV SIDE | [14 empty] | 120
1 | Mahadinagar |  | 11 |  | WP042358 | 1 | 148.6 | 841988 | 841839.4 | 1 |  | 841839.4 | 846977.0681 | Kamrangirchar |  |  |  |  | Mahadinagar | 846977.0681 | 853490.0177 | -6512.9496 | -0.7631 | OK
2 | Badsha Mia School |  | 11 |  | WP042375 | 1 | 59.32 | 1138613 | 1138553.68 | 1 |  | 1138553.68 | 1145502.1679 | Kamrangirchar |  |  |  |  | Badsha Mia School | 1145502.1679 | 98328.343 | 1047173.8249 | 1064.9766 | FAULT
3 | Shahjahan Sir |  | 11 |  | WP042361 | 1 | 41.37 | 384521 | 384479.63 | 1 |  | 384479.63 | 386826.0737 | Kamrangirchar |  |  |  |  | Shahjahan Sir | 386826.0737 | 975417.1631 | -588591.0894 | -60.3425 | CHECK
4 | Gazirghat |  | 11 |  | WP042395 | 1 | 41.83 | 729763 | 729721.17 | 1 |  | 729721.17 | 734174.5909 | Kamrangirchar |  |  |  |  | Gazirghat | 734174.5909 | 1463125.7446 | -728951.1537 | -49.8215 | CHECK
5 |  |  | 3: 11; 6: 1; 9=8-7: 0; 10: 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 0 | 0 | 1158307.8811 | -1158307.8811 | -100 | CHECK
6 |  |  | 3: 11; 6: 1; 9=8-7: 0; 10: 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 |  |  | 3: 11; 6: 1; 9=8-7: 0; 10: 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 0 | 0 | 853490.0177 | -853490.0177 | -100 | CHECK
8 |  |  | 3: 11; 6: 1; 9=8-7: 0; 10: 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3113479.9006 | 3094593.88 | 3113479.9006 | 0.61029
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 3113479.9006
[6 empty] | Total = |  |  | 3113479.9006 | 0
Note on G934: User: Grid CF=1.5
Note on G1887: User: Grd CF = 3

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) |  | 132 | IMPORT | 8993631 | 1 | 5990.061 | 6012.753 | 22.692 | 960000 | 0 | 21784320
| 132 KV Mogbazar-2 CKT(EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) |  | 132 |  | 8993659 | 1 | 5095.586 | 5112.965 | 17.379 | 960000 | 0 | 16683840
| 132 KV Mogbazar-1 CKT(EXP) |  | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 38468160
|  |  | 10: Net Total | 38468160
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE | 6604452 | 1 | 9560.15 | 9590.4 | 30.25 | 720000 | 21780000
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  | 6604428 | 1 | 5776.38 | 5799.8 | 23.42 | 720000 | 16862400
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
|  |  | 9=8-7: Total Import/Export | 38642400 | 0
|  |  | 9=8-7: Net Total | 38642400 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0 |  |  | future Scope
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0 |  |  | No meter
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 38642400
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 38468160; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 38468160
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 38468160 | MOGBAZAR 33 KV NET IMPORT |  | 38342400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 125760
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3269%
| 132 KV TOTAL IMPORT |  | 4: 38468160
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming |  | 33 | IMPORT | 76026303 | 1 | 10143.93 | 10171.03 | 27.1 | 480000 | 13008000 |  | 13050665.1978
| 132/33 KV GT-2 Incomming |  | 33 |  | 76026307 | 1 | 10139.04 | 10166.09 | 27.05 | 480000 | 12984000 |  | 13026586.4797
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 8338.35 | 8364.08 | 25.73 | 480000 | 12350400 |  | 12390908.3225
|  |  | 10: Total | 38342400 |  | 38468160
MOGBAZAR 33 kV SIDE
| 33/11 KV Transforfers |  | 4: EXPORT | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. |  | 33 |  | 6604465 | 1 | 7057.7 | 7067.94 | 10.24 | 180000 |  | 1843200 | 1846165.0081 |  | 11735247.2338 | MOGBAZAR 33/11 KV SS | 2.5754 | 33/11 KV Transformer No.1. | 1846165.0081 | 1645301.6114 | 200863.3968 | 12.2083 | OK
| 33/11 KV Transformer No.2. |  | 33 |  | 202006985 | 1 | 35675937033 | 35857375961 | 181438928 | 3 | T2 Incomer side | 3105000 | 3109994.7647 |  |  |  |  | 33/11 KV Transformer No.2. | 3109994.7647 | 2685352.321 | 424642.4437 | 15.8133 | OK
| 33/11 KV Transformer No.3. |  | 33 |  | 6604338 | 1 | 7203.63 | 7222.6 | 18.97 | 180000 |  | 3414600 | 3420092.7934 |  |  |  |  | 33/11 KV Transformer No.3. | 3420092.7934 | 3043000.5811 | 377092.2123 | 12.3921 | OK
| 33/11 KV Transformer No.4 |  | 33 |  |  | 1 | 1199646 | 1218466 | 18820 | 180000 | T4 Incomer side | 3353600 | 3358994.6676 |  |  |  |  | 33/11 KV Transformer No.4 | 3358994.6676 | 3124338.6469 | 234656.0206 | 7.5106 | OK
| 33 KV Feeders |  | 10: Total |  | 11716400 | 11735247.2338 |  |  |  |  | 33 KV Feeders | 11735247.2338 | 10497993.1604 | 1237254.0734 | 11.7856 | OK
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 |  | 76026300 | 1 | 6829.14 | 6842.6 | 13.46 | 360000 |  | 4845600 | 4853394.7284 |  | 13240464.6677 | Tejgoan 33/11 kv ss | 2.6069 | 33 kV Tejgaon U/G Feeder-1 | 4853394.7284 | 4478378.2137 | 375016.5147 | 8.3739 | OK
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 |  | 06604453 | 1 | 6704.04 | 6727.3 | 23.26 | 360000 |  | 8373600 | 8387069.9393 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 8387069.9393 | 8045291.6307 | 341778.3086 | 4.2482 | OK
10 | Bashundhara City |  | 33 |  | 660434 | 1 | 834.35 | 845.2 | 10.85 | 180000 |  | 1953000 | 1956141.6346 | Shere b.nagar | 3517108.6043 | Ispahani 33/11 kv ss | 0.6657 | Bashundhara City | 1956141.6346 | 1735012.7134 | 221128.9212 | 12.7451 | OK
11 | Ispahani-1 |  | 33 |  |  | 1 | 1939.84 | 1946.2 | 6.36 | 180000 | From Ispahani Downsteam Estimated | 2305460 | 2309168.6088 |  |  |  |  | Ispahani-1 | 2309168.6088 | 1100585.7677 | 1208582.8411 | 109.8127 | FAULT
12 | Ispahani-2 |  | 33 |  |  | 1 | 4016.4 | 4023.1 | 6.7 | 180000 |  | 1206000 | 1207939.9956 |  | 4549997.4614 | Green Road Dormatory 33/11 kv ss | 0.10994 | Ispahani-2 | 1207939.9956 | 2364784.6497 | -1156844.6541 | -48.9197 | CHECK
13 | 33 kV Green Road Dormitory |  | 33 |  | 76026305 | 1 | 8118.51 | 8131.2 | 12.69 | 180000 | Reading From G. Dormitory Side | 4542690 | 4549997.4614 |  |  |  |  | 33 kV Green Road Dormitory | 4549997.4614 | 1269212.7358 | 3280784.7256 | 258.4897 | FAULT
14 | 33 KV Khejurbagan |  | 33 |  |  | 1 | 6237.41 | 6237.8 | 0.39 | 180000 |  | 70200 | 70312.9251 | Shere b.nagar |  |  |  | 33 KV Khejurbagan
15 | 33 KV T&T-1 |  | 33 |  | 6604337 | 1.04 | 4708.57 | 4726 | 17.43 | 180000 |  | 3262896 | 3268144.7593 |  | 3275356.3414 | T&T 33/11 kv ss | 1.3904 | 33 KV T&T-1 | 3268144.7593 | 3076462.8222 | 191681.9372 | 6.2306 | OK
16 | 33 KV T&T-2 |  | 33 |  | 6604336 | 1 | 5758.86 | 5758.9 | 0.04 | 180000 |  | 7200 | 7211.5821 |  |  |  |  | 33 KV T&T-2 | 7211.5821 | 0 | 7211.5821 | #DIV/0! | #DIV/0!
17 | 33KV Karwan Bazar |  | 33 |  | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.60289 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | AT-1 |  | 33 |  | 6603338 | 1 | 2972.88 | 3074.3 | 101.42 | 80 |  | 8113.6 | 8126.6517 |  |  |  |  | AT-1 | 8126.6517 | 9493.4282 | -1366.7765 | -14.3971 | OK
19 | AT-2 |  | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 26574759.6 | 26617508.2862 |  |  |  |  | 0 | 26617508.2862 | 22183286.8396 | 4434221.4466 | 19.989 | OK
|  |  | 9=8-7: Grand Total | 38352755.52 | 38291159.6 | 38352755.52 | 0.16086
-0.3377
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2026454.5597
|  |  | 9=8-7: Total =; 10: 2026454.5597 | 70312.9251 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 |  | 11 | Import | 6604457 | 1 | 549926.4 | 551743.7 | 1817.3 | 1000 | 1817300 |  | 1832217.7374
2 | 33/11 kV Transformer-2 |  | 11 | Import | 30/11009-1101 | 1 | 606912.5 | 610017.5 | 3105 | 1000 | 3105000 |  | 3130488.1278
3 | 33/11 kV Transformer-3 |  | 11 | Import | 6604454 | 1 | 603832.7 | 607196.5 | 3363.8 | 1000 | 3363800 |  | 3391412.5489
4 | 33/11 kV Transformer-4 |  | 11 | Import |  | 1 | 1196.24 | 1217.2 | 20.96 | 160000 | 3353600 |  | 3381128.8197
|  |  | 7: 0; 8: 0; 10: Total | 11639700 |  | 11735247.2338
| MOGBAZAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 41136.9 | 41136.9 | 0 | 1000 |  | 0 | 0 | Kakrail |  |  |  | 11 kV Doctor's Lane | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 81608.6 | 81937.7 | 329.1 | 1000 |  | 329100 | 320804.0202 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 320804.0202 | 291760.8196 | 29043.2005 | 9.9545 | OK
3 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 |  | 11 | T-1 | 30/11004-1101 | 1 | 121644.9 | 121886.8 | 241.9 | 1000 |  | 241900 | 235802.1649 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 235802.1649 | 252158.3911 | -16356.2262 | -6.4865 | OK
7 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 136176.7 | 137436.2 | 1259.5 | 1000 |  | 1259500 | 1227750.4206 | Moghbazar |  |  |  | 11KV Ambagan | 1227750.4206 | 1074277.2921 | 153473.1285 | 14.2862 | OK
[7 empty] | 0 | 0
5 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 152262.9 | 153366.6 | 1103.7 | 1000 |  | 1103700 | 1075877.8398 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1075877.8398 | 897491.265 | 178386.5748 | 19.8761 | OK
3 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10433.8 | 10527.2 | 93.4 | 1000 |  | 93400 | 91045.5651 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 91045.5651 | 93945.2151 | -2899.65 | -3.0865 | OK
4 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 132251.8 | 133366 | 1114.2 | 1000 |  | 1114200 | 1086113.1549 | Kakrail |  |  |  | 11 kV Bangla Motor | 1086113.1549 | 1050201.374 | 35911.7809 | 3.4195 | OK
1 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 182592.9 | 183797 | 1204.1 | 1000 |  | 1204100 | 1173746.9483 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1173746.9483 | 687490.2978 | 486256.6505 | 70.7292 | FAULT
[7 empty] | 0 | 0
6 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 126698.4 | 127274.6 | 576.2 | 1000 | Estimated | 1137855.6 | 1109172.4426 | Kakrail | 100 |  |  | 11 kV Iskaton | 1109172.4426 | 1135510.6851 | -26338.2424 | -2.3195 | OK
5 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 92305.8 | 93305.9 | 1000.1 | 1000 |  | 1000100 | 974889.3971 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 974889.3971 | 881768.2165 | 93121.1806 | 10.5607 | OK
2 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124987.8 | 125221.7 | 233.9 | 1000 |  | 233900 | 228003.8296 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 228003.8296 | 193491.7662 | 34512.0634 | 17.8365 | OK
3 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 117806.9 | 118298.6 | 491.7 | 1000 |  | 491700 | 479305.186 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 479305.186 | 469726.0754 | 9579.1106 | 2.0393 | OK
4 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 45592.3 | 45896.4 | 304.1 | 1000 |  | 304100 | 296434.2222 | Kakrail |  |  |  | 11 kV BSRS Feeder | 296434.2222 | 268569.323 | 27864.8992 | 10.3753 | OK
2 | 11 kV Vumi Bhaban |  | 11 | T-3 | 21101039 | 1 | 9217.9 | 9274.5 | 56.6 | 1000 |  | 56600 | 55173.2226 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 55173.2226 | 55030.6699 | 142.5526 | 0.25904 | OK
5 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19580.9 | 19580.9 | 0 | 1000 | check | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 3341.1478 | -3341.1478 | -100 | CHECK
|  |  | 7: 0; 8: 0 | 8354118.414 | 8570155.6 | 8354118.414 | -2.5208 |  |  |  |  | 8354118.414 | 7354762.5388
1 | 11 kV TCB Feeder | C608P | 11 | T-4 |  | 1 | 37226.1 | 37317.2 | 91.1 | 1000 |  | 91100 | 109962.7341 | Kakrail |  |  |  | 11 kV TCB Feeder | 109962.7341 | 17261.2059 | 92701.5282 | 537.0513 | FAULT
2 | 11 kV Tejgaon SS-2 |  | 11 | T-4 |  | 1 | 37710.4 | 38269.9 | 559.5 | 1000 |  | 559500 | 675347.4173 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 675347.4173 | 975202.4512 | -299855.0339 | -30.748 | OK
3 | Holy Day Inn | C108HY | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 270030 | 325941.1316 | Tejgaon |  |  |  | Holy Day Inn | 325941.1316 | 253338.8211 | 72602.3105 | 28.6582 | OK
4 | Polly Bhabon-2 | C608PB | 11 | T-4 |  | 1 | 18386 | 18386 | 0 | 1000 | According to AMR meter reading | 8748 | 10559.3194 | Kakrail |  |  |  | Polly Bhabon-2 | 10559.3194 | 10550.4945 | 8.8249 | 0.083645 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 |  | 1 | 23357.9 | 24355.8 | 997.9 | 1000 |  | 997900 | 1204520.4428 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1204520.4428 | 1012843.0163 | 191677.4265 | 18.9247 | OK
6 | 11 kV Tejturibazar | C608X | 11 | T-4 |  | 1 | 3354.85 | 3370.19 | 15.34 | 1000 | Estimated | 307221.012 | 370832.7382 | Kakrail | 27 |  |  | 11 kV Tejturibazar | 370832.7382 | 365724.4924 | 5108.2457 | 1.3967 | OK
7 | Songsad |  | 11 | T-4 |  | 1 | 3864.8 | 3864.8 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Songsad | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Chennel 24 |  | 11 | T-4 |  | 1 | 7337.59 | 7353.27 | 15.68 | 1000 |  | 15680 | 18926.6265 | Moghbazar |  |  |  | Chennel 24 | 18926.6265 | 4476.7773 | 14449.8492 | 322.7735 | FAULT
8 | Sonargaon | C608K | 11 | T-4 |  | 1 | 43332 | 43490.8 | 158.8 | 1000 |  | 158800 | 191680.3751 | Kakrail |  |  |  | Sonargaon | 191680.3751 | 346671.8318 | -154991.4566 | -44.7084 | CHECK
| AT -1 |  | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 |  | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[11 empty] | 2907770.785 | 2408979.012 | 2907770.785 | 20.7055
|  |  | 10: Total | 11735247.2338 | 10979134.612 | 11261889.199 | 2.5754
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH | [13 empty] | AMR Meter Information
|  |  | 6: Moghbazar; 7: at 33 KV level; 9=8-7: 1474680.8767 | [13 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
|  |  | 6: Tejgaon; 7: at 33 KV level; 9=8-7: 4928627.7069 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 49050 | 3000
|  |  | 6: Kakrail; 7: at 33 KV level; 9=8-7: 4858580.6154 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 220980 | 3000
|  |  | 6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 0 | [13 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 8748 | 300
[6 empty] | Total = |  |  | 11261889.199 | 0
[27 empty] | Month = | 2024-02-01
AMR Meter Information
[24 empty] | Customer Name | Previous Total | Present Total
[24 empty] | Shah Garments | 1116.36 | 1132.71
[24 empty] | Habib Hotel | 3931.32 | 4004.98
[24 empty] | The Joint Director BRDB | 1748.4 | 1777.56
[25 empty] | 1116.36 | 1132.71 | 49050
[25 empty] | 3931.32 | 4004.98 | 220980
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [23 empty] | 1748.4 | 1777.56 | 8748
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
15 | 33 KV T&T-1 |  | 33 | 0 | 6604337 | 1.04 | 4708.57 | 4726 | 17.43 | 180000 | 0 | 3262896 | 3268144.7593
16 | 33 KV T&T-2 |  | 33 | 0 | 6604336 | 1 | 5758.86 | 5758.9 | 0.04 | 180000 | 0 | 7200 | 7211.5821
0 | Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 369.212 | 381.8754 | 12.6634 | 240000 | 0 | 3039216 | 3039887.7334
|  |  | 10: Total | 0 | 6309312 | 6315244.0748
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder |  | 33 | Import | DHK60891 | 1 | 25142 | 30935 | 5793 | 360 | 2085480
2 | 33 kV Moghbazar-2 Feeder |  | 33 | Import | DHK68131 | 1 | 898200 | 898200 | 0 | 360 | 0
| 33 kV Ullon Feeder |  | 33 | Import | DHK68132 | 1 | 397.69 | 414.72 | 17.03 | 180000 | 3065400
|  |  | 7: 0; 8: 0; 10: Total | 5150880 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 174514 | 191893 | 17379 | 180 |  | 3128220
4 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 940629 | 952005 | 11376 | 180 |  | 2047680 |  |  | Meter Problem
|  |  | 10: Total |  | 5175900 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 6315244.0748; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6315244.0748
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 6315244.0748 | 33/11 KV XF LV SIDE |  | 6225120
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 90124.0748
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.427%
| TOTAL IMPORT |  | 4: 6315244.0748
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 191568 | 209049 | 17481 | 180 | 3146580 |  | 3192134.5614 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 142662 | 159765 | 17103 | 180 | 3078540 |  | 3123109.5134 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 6225120 |  | 6315244.0748 | 1.4477 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 252304 | 265229 | 12925 | 60 |  | 775500 | 786282.6593 | Kakrail |  |  |  | 11 kV post office | 786282.6593 | 736632.0122 | 49650.6471 | 6.7402 | OK
2 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 534944 | 547858 | 12914 | 60 |  | 774840 | 785613.4825 | Kakrail |  |  |  | 11 kV anarkoli | 785613.4825 | 796668.3127 | -11054.8302 | -1.3876 | OK
3 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 974455 | 977621 | 3166 | 60 |  | 189960 | 192601.2301 | Moghbazar |  |  |  | 11 kV sonalibagh | 192601.2301 | 183214.2275 | 9387.0026 | 5.1235 | OK
4 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 2016391 | 2024815 | 8424 | 60 |  | 505440 | 512467.7077 | Moghbazar |  |  |  | 11 Kv desh tv | 512467.7077 | 515544.9865 | -3077.2789 | -0.5969 | OK
5 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 720.76 | 735.76 | 15 | 60000 |  | 900000 | 912513.7245 | Moghbazar |  |  |  | 11 Kv Btcl | 912513.7245 | 878015.6733 | 34498.0512 | 3.9291 | OK
1 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 934914 | 940400 | 5486 | 60 |  | 329160 | 333736.6862 | Kakrail |  |  |  | 11 kV century | 333736.6862 | 331417.4279 | 2319.2583 | 0.6998 | OK
2 | 11 kV cinema hall |  | 11 | Mogbazar | DHK60979 | 1 | 555813 | 566022 | 10209 | 60 |  | 612540 | 621056.8409 | Moghbazar |  |  |  | 11 kV cinema hall | 621056.8409 | 574972.3996 | 46084.4412 | 8.0151 | OK
3 | 11 kV malibagh bazar |  | 11 | Khailgaon | DHK61106 | 1 | 833874 | 849490 | 15616 | 60 |  | 936960 | 949987.6214 | Khilgaon |  |  |  | 11 kV malibagh bazar | 949987.6214 | 875336.5686 | 74651.0528 | 8.5283 | OK
4 | 11 kv Sherebangla | D1105G | 11 |  | DHK60915 | 1 | 807901 | 820487 | 12586 | 60 |  | 755160 | 765659.8491 | Moghbazar |  |  |  | 11 kv Sherebangla | 765659.8491 | 757821.2947 | 7838.5544 | 1.0344 | OK
5 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 380856 | 388308 | 7452 | 60 |  | 447120 | 453336.8183 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 453336.8183 | 416905.223 | 36431.5954 | 8.7386 | OK
6 | Auxiliary |  |  | Export | U0004461 | 1 | 8409.19 | 8441.86 | 32.67 | 60 |  | 1960.2 | 1987.4549 | Moghbazar |  |  |  | Auxiliary | 1987.4549 | 2258.9724 | -271.5175 | -12.0195 | OK
|  |  | 10: Grand Total | 6315244.0748 | 6228640.2 | 6315244.0748 | 1.3904
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 1905632.828
[6 empty] | Moghbazar | at 33 KV level |  | 3459623.6254
[6 empty] | Khilgaon | at 33 KV level |  | 949987.6214
[6 empty] | Total = |  |  | 6315244.0748 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 |  | 132 | IMPORT | 8993681 | 1 | 11.66 | 19.6365 | 7.9765 | 1440000 | 0 | 11486203.2
| Ullon-1 |  | 132 |  |  | 1 | 0 | 0.00054 | 0.00054 | 1440000 | 777.6 | 0
| Ullon-2 |  | 132 |  | 8993680 | 1 | 0 | 0.40918 | 0.40918 | 1440000 | 0 | 589219.2
| Ullon-2 |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 777.6 | 12075422.4
|  |  | 9=8-7: Net Total | 12074644.8
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) |  | 132 |  | 8993624 | 1 | 0 | 3.12 | 3.12 | 960000 | 0 | 5547840
| Maniknager-2 (new line to ullon) |  | 132 |  |  | 1 | 0 | 0.065 | 0.065 | 960000 | 62400 | 0
|  |  | 9=8-7: Total Import/Export | 62400 | 5547840
|  |  | 9=8-7: Net Total | 5485440
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 |  | 132 |  | 8993659 | 1 | 4467.512 | 4478.623 | 11.111 | 960000 | 0 | 10666560
| Ullon U/G-1 |  | 132 |  |  | 1 | 1.561 | 1.561 | 0 | 960000 | 0 | 0
| Ullon U/G-2 |  | 132 |  | 8993660 | 1 | 7.475 | 17.691 | 10.216 | 960000 | 0 | 9807360
| Ullon U/G-2 |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 20473920
|  |  | 9=8-7: Net Total | 20473920
| ULLON 132 KV SIDE (RECEIVING) | [9 empty] | 38034004.8
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) |  | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 9=8-7: Total Import/Export | 0 | 0
Net Total
| EXPORT TO OTHERS 132/33 KV SS | [13 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 |  | 132 |  |  | 1 | 1632768 | 1635373 | 2605 | 1000 |  | 2605000 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 |  | 132 |  |  | 1 | 2254582 | 2263314 | 8732 | 1000 |  | 8732000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 |  | 132 |  |  | 1 | 3010496 | 3019256 | 8760 | 1000 |  | 8760000 |  |  | 132 kV Ullon CKT-3 | 31978000
|  |  | 10: Total |  | 20097000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 17937004.8
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 4: 12074644.8; 6: EXPORT TO OTHER S/S; 9=8-7: 20097000 | 132 KV NET IMPORT |  | 17937004.8
| HORIPUR 132 SIDE (TARIFF POINT) |  | 4: 5485440; 6: 132 KV Net EXPORT; 9=8-7: 17937004.8 | 132/33 KV GT LV Side |  | 17787636
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 20473920 | LOSS UNITS=>(132 HV-33 LV) |  | 149368.8
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.8327%
| 132 KV TOTAL IMPORT |  | 4: 38034004.8
33 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | BD001812 | 1 | 2289.3054 | 2304.6673 | 15.3619 | 480000 | 7373712 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming |  | 33 | Import | BD001858 | 1 | 2208.3524 | 2223.3622 | 15.0098 | 480000 | 7204704 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming |  | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 3209220 |  |  |  | Estimated | [5 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 8: 0; 10: Total | 17787636 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE |  | 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1729.7276 | 1758.6594 | 28.9318 | 240000 |  | 6943632 | 6945166.6951 |  | 6945166.6951 | Taltola 33/11 kv ss | 0.46891 | Taltala-1 | 6945166.6951 | 5549414.4995 | 1395752.1955 | 25.1513 | OK
| Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 369.212 | 381.8754 | 12.6634 | 240000 |  | 3039216 | 3039887.7334 |  |  |  |  | Mgbazar T&T | 3039887.7334 | 2992324.2762 | 47563.4572 | 1.5895 | OK
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 |  | 0 | 0 |  | 3039887.7334 | Mgbazar T&T 33/11 kv ss | 1.3904 | Kakrail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Taltala-2 |  | 33 | Export | BD001837 | 1 | 2662.9397 | 2662.9397 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Taltala-2 | 0 | 436844.9622 | -436844.9622 | -100 | CHECK
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 0 | Kakrail 33/11 kv ss | -0.975 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 1.8571 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3331 | 79.3331 | 0 | 240000 | From Downstream | 3209220 | 3209929.308 |  | 0 | Tejgoan 33/11 kv ss | 2.6069 | Khailgaon | 3209929.308 | 2631582.7603 | 578346.5477 | 21.9771 | OK
4 | AT at GIS Building |  | 415 | Export | DHKE4577 | 1 | 161397 | 163131 | 1734 | 1 |  | 1734 | 1734.3833 |  | 3209929.308 | Khilgoan 33/11 kv ss | 1.5823 | AT at GIS Building | 1734.3833 | 1703.0758 | 31.3074 | 1.8383 | OK
|  |  | 7: 0; 8: 0; 10: TOTAL= |  | 13193802 | 13196718.1198 |  |  |  |  | 0 | 13196718.1198 | 11611869.5741 | 1584848.5457 | 13.6485 | OK
| 33 KV Local Feeder -1 |  | 33 | NET IMPORT |  | 1 | 1222.7866 | 1232.4921 | 9.7055 | 240000 |  | 2329320 | 2329834.8308 |  | 4555342.6082 | Ullon 33/11 kv ss | 0.33697 | 33 KV Local Feeder -1 | 2329834.8308 | 2562548.0805 | -232713.2496 | -9.0813 | OK
| 33KV Local Feeder- 2 |  | 33 |  |  | 1 | 943.1378 | 952.4087 | 9.2709 | 240000 |  | 2225016 | 2225507.7774 |  |  |  |  | 33KV Local Feeder- 2 | 2225507.7774 | 1853964.3454 | 371543.4319 | 20.0405 | OK
|  |  | 10: TOTAL= |  | 4554336 | 4555342.6082 |  |  |  |  | 0 | 4555342.6082 | 4416512.4259 | 138830.1823 | 3.1434 | OK
|  |  | 10: Grand Total | 17752060.728 | 17748138 | 17752060.728 | 0.022102
11 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 103 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 60 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 4554336 |  | 4555342.6082 |  |  | 43 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [14 empty] | 14.3333 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 568927.8 | 570844.9384 | Moghbazar | 50 | 74.3333 |  | West Malibagh | 570844.9384 | 552064.0532 | 18780.8851 | 3.4019 | OK
2 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1046827.152 | 1050354.6866 | Moghbazar | 92 |  |  | Ullon | 1050354.6866 | 1042787.6561 | 7567.0305 | 0.72565 | OK
3 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 933041.592 | 936185.6989 | Moghbazar | 82 |  |  | Mohanagar | 936185.6989 | 920106.7554 | 16078.9435 | 1.7475 | OK
4 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 512035.02 | 513760.4445 | Moghbazar | 45 |  |  | Bagichartek | 513760.4445 | 490723.6029 | 23036.8417 | 4.6945 | OK
1 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 933041.592 | 936185.6989 | Moghbazar | 82 |  |  | Mirbagh | 936185.6989 | 920106.7554 | 16078.9435 | 1.7475 | OK
2 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 546170.688 | 548011.1408 | Moghbazar | 48 |  |  | West Rampura | 548011.1408 | 490723.6029 | 57287.538 | 11.6741 | OK
3 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 |  | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 |  | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4555342.6082 | 4540043.844 | 4555342.6082 | 0.33697
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 4555342.6082
[6 empty] | Total = |  |  | 4555342.6082 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 |  | 132 | Export | 50146667 | 1 | 1919.913 | 1935.541 | 15.628 | 960000 | 0 | 15002880
2 | Rampura to Madartek-2 |  | 132 | Export | 50146668 | 1 | 1713.054 | 1728.469 | 15.415 | 960000 | 0 | 14798400
|  |  | 9=8-7: Total Import/Export | 0 | 29801280
|  |  | 9=8-7: Net Total | 29801280
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 |  | 132 | Import | SIEM0492 | 1 | 1700420 | 1715401 | 14981 | 1000 | 14981000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 |  | 132 | Import | SIEM0489 | 1 | 1649612 | 1664491 | 14879 | 1000 | 14879000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 29860000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 29860000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| MADERTEK 132 KV SIDE |  | 7: 0; 8: 0
3 | 133 kV GT-1 |  | 132 | Export |  | 1 | 1537059 | 1552063 | 15004 | 1000 |  | 15004000
4 | 133 kV GT-2 |  | 132 | Export |  | 1 | 1524535 | 1539439 | 14904 | 1000 |  | 14904000
|  |  | 10: Total |  | 29908000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 29801280; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 29801280
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 29801280 | 33 KV NET IMPORT |  | 29968000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -166720
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.5594%
| 132 KV TOTAL IMPORT |  | 4: 29801280
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0516 | 1 | 1685769 | 1700782 | 15013 | 1000 | 15013000 |  | 14929478.6652
2 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0515 | 3 | 559811 | 564796 | 4985 | 1000 | 14955000 |  | 14871801.3348
|  |  | 7: 0; 8: 0; 10: Total | 29968000 |  | 29801280
| MADERTEK 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kv Transforfers |  | 7: 0; 8: 0
1 | 33 kV T-1 |  | 33 | Import | SIEM0512 | 1 | 428868 | 431391 | 2523 | 2000 |  | 5046000 | 5037764.1166 |  | 11998384.6915 | Madartek 33/11 kv ss
2 | 33 kV T-3 |  | 33 | Export |  | 1 | 84551 | 85566 | 1015 | 2000 |  | 2030000 | 2026686.7136
2 | 33 kV T-2 |  | 33 | Export | SIEM0505 | 1 | 432115 | 434586 | 2471 | 2000 |  | 4942000 | 4933933.8613
| 33 kv Feeders |  | 7: 0; 8: 0; 10: Total |  | 12018000 | 11998384.6915 |  | 8823574.9628 | Banasree 33/11 kv ss
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 122292 | 124166 | 1874 | 2000 |  | 3748000 | 3741882.6613
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 377556 | 381222 | 3666 | 2000 |  | 7332000 | 7320032.997 |  | 7320032.997 | Goran 33/11 kv ss
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 40972 | 41249 | 277 | 6000 |  | 1662000 | 1659287.3487
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 107301 | 109846 | 2545 | 2000 |  | 5090000 | 5081692.3015 |  | 1659287.3487 | Amulia 33/11 kv ss
|  |  | 10: Total |  | 17832000 | 17802895.3085
|  |  | 9=8-7: Grand Total | 29801280 | 29850000 | 29801280 | -0.16322
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | GJU 71154 | 1 | 401607.7 | 404110.8 | 2503.1 | 2000 | 5006200 |  | 5035402.8437 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | GJU 71155 | 1 | 405029.6 | 407483.8 | 2454.2 | 2000 | 4908400 |  | 4937032.3435 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming |  | 11 | Import | 6604399 | 1 | 4783.07 | 4794.26 | 11.19 | 180000 | 2014200 |  | 2025949.5042 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 11928800 |  | 11998384.6915 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 19.1733 | 20.183 | 1.0096 | 1000000 |  | 1009624 | 1015289.519 | Mugdapara |  |  |  | Sobujbagh | 1015289.519 | 1018645.2215 | -3355.7025 | -0.32943 | OK
2 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 108640.5 | 109694.8 | 1054.3 | 1000 |  | 1054300 | 1060216.219 | Mugdapara |  |  |  | Madertek | 1060216.219 | 1045576.9001 | 14639.3189 | 1.4001 | OK
3 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 10038.7 | 11333.5 | 1294.8 | 1000 |  | 1294800 | 1302065.7881 | Mugdapara |  |  |  | Rajarbagh | 1302065.7881 | 1278475.055 | 23590.7331 | 1.8452 | OK
| Goran | A921G | 11 |  | X1390296 | 1 | 37628.5 | 38632.1 | 1003.6 | 1000 |  | 1003600 | 1009231.7153 | Bashabo |  |  |  | Goran | 1009231.7153 | 995677.3386 | 13554.3766 | 1.3613 | OK
5 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 16940.342 | 17797.798 | 857.456 | 1000 |  | 857456 | 862267.6262 | Mugdapara |  |  |  | Dhakhingaon | 862267.6262 | 821484.6094 | 40783.0168 | 4.9646 | OK
6 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | Manda | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 2023.5624 | 2195.3558 | 171.7934 | 1000 |  | 171793.4 | 172757.421 | Mugdapara |  |  |  | Green Model Town | 172757.421 | 187406.4551 | -14649.034 | -7.8167 | OK
1 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 6111.0168 | 6481.5268 | 370.51 | 1000 |  | 370510 | 372589.122 | Mugdapara |  |  |  | Biswa Road | 372589.122 | 372057.1666 | 531.9554 | 0.14298 | OK
2 | Mugdapara | B921P | 11 |  | X0854272 | 1 | 5258.7 | 5404.2 | 145.5 | 1000 |  | 145500 | 146316.4753 | Maniknagar |  |  |  | Mugdapara | 146316.4753 | 145473.3183 | 843.1569 | 0.5796 | OK
| Singapur | F221S | 11 |  | X1390302 (N) | 1 | 44586.9 | 45819.9 | 1233 | 1000 |  | 1233000 | 1239918.9965 | Banosree |  |  |  | Singapur | 1239918.9965 | 1267509.224 | -27590.2274 | -2.1767 | OK
| Trimohony | F221T | 11 |  | X1390308 | 1 | 37205.2 | 38505 | 1299.8 | 1000 |  | 1299800 | 1307093.8456 | Banosree |  |  |  | Trimohony | 1307093.8456 | 1512479.8534 | -205386.0077 | -13.5794 | OK
5 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 170.2634 | 1198.3345 | 1028.0711 | 1000 |  | 1028071.1 | 1033840.1352 | Mugdapara |  |  |  | Mayakanon | 1033840.1352 | 1000706.9327 | 33133.2024 | 3.311 | OK
6 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 8394.9392 | 8860.1024 | 465.1632 | 1000 |  | 465163.2 | 467773.4697 | Mugdapara |  |  |  | Ahmedbagh | 467773.4697 | 445453.3853 | 22320.0844 | 5.0106 | OK
1 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 766942 | 772268 | 5326 | 200 |  | 1065200 | 1071177.3845 | Mugdapara |  |  |  | Wasa Road | 1071177.3845 | 1094168.6102 | -22991.2257 | -2.1013 | OK
2 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 792410 | 797029 | 4619 | 200 |  | 923800 | 928983.9165 | Mugdapara |  |  |  | Nandipara | 928983.9165 | 888936.5428 | 40047.3736 | 4.5051 | OK
| AT-1 |  | 0.415 |  |  | 1 | 1121.79 | 1172.79 | 51 | 80 |  | 4080 | 4102.895 | Mugdapara |  |  |  | AT-1 | 4102.895 | 3701.4207 | 401.4743 | 10.8465 | OK
3 | AT-2 |  | 0.415 |  | 63394003 | 1 | 671.6 | 730.77 | 59.17 | 80 |  | 4733.6 | 4760.1627 | Mugdapara |  |  |  | AT-2 | 4760.1627 | 5134.021 | -373.8583 | -7.282 | OK
|  |  | 10: Total | 11998384.6915 | 11931431.3 | 11998384.6915 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 11998384.6915 | 11931431.3 | 11998384.6915 | 0.56115
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 2547012.8422
[6 empty] | Bashabo | at 33 KV level |  | 1009231.7153
[6 empty] | Maniknagar | at 33 KV level |  | 146316.4753
[6 empty] | Mugdapara | at 33 KV level |  | 8295823.6588
[6 empty] | Total = |  |  | 11998384.6915 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 | 0 | 76026300 | 1 | 6829.14 | 6842.6 | 13.46 | 360000 | 0 | 4845600 | 4853394.7284
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 | 0 | 06604453 | 1 | 6704.04 | 6727.3 | 23.26 | 360000 | 0 | 8373600 | 8387069.9393
0 | Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 13219200 | 13240464.6677
TEJGOAN 33 KV SIDE (RECEIVING)
|  |  | 7: 0; 8: 0; 10: Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 818538.6 | 836475.9 | 17937.3 | 270 |  | 4843071
2 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 740035.9 | 771033.8 | 30997.9 | 180 |  | 5579622
3 | 33/11 kV Transfomer-3 (T3) |  | 33 | Export | BD001872 | 1 | 1373.3735 | 1394.8981 | 21.5246 | 180000 |  | 3874428
|  |  | 10: Total |  | 14297121 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 13240464.6677; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TEJGOAN 33 KV NET IMPORT |  | 13240464.6677
| IMPORT-2 |  | 6: TEJGOAN 33 KV NET IMPORT; 9=8-7: 13240464.6677 | 33 KV TX HV Side |  | 14297121
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -1056656.3323
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -7.981%
| TOTAL IMPORT |  | 4: 13240464.6677
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 39553.5 | 63479.1 | 23925.6 | 180 | 4306608 |  | 5477931.8765 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 917605.2 | 929984.5 | 12379.3 | 180 | 2228274 |  | 2834326.4988 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming |  | 11 | Import | BD001875 | 1 | 235650.9 | 235650.9 | 0 | 1000 | 3874428 |  | 4928206.2924 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 10409310 |  | 13240464.6677 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | C110U | 11 |  | DHK60950 | 1 | 351484.6 | 365588.1 | 14103.5 | 60 |  | 846210 | 868270.1537 | Tejgaon |  |  |  | Nakhal Para Feeder | 868270.1537 | 777981.0035 | 90289.1501 | 11.6056 | OK
2 | Badda-Meghna Feeder | C110N | 11 |  | DHK60979 | 1 | 968577.3 | 976789.1 | 8211.8 | 60 |  | 492708 | 505552.5826 | Tejgaon |  |  |  | Badda-Meghna Feeder | 505552.5826 | 469013.0985 | 36539.4841 | 7.7907 | OK
3 | Rasulbagh Feeder | C110K | 11 |  | DHK60948 | 1 | 146096.4 | 165694.3 | 19597.9 | 60 |  | 1175874 | 1206528.2834 | Tejgaon |  |  |  | Rasulbagh Feeder | 1206528.2834 | 1135539.4567 | 70988.8267 | 6.2516 | OK
4 | Lukas | C171V | 11 |  | 8A021100948-02 | 1 | 77490225 | 78636044 | 1145819 | 1 |  | 1145819 | 1175689.7688 | Tejgaon |  |  |  | Lukas | 1175689.7688 | 1010954.3559 | 164735.4129 | 16.295 | OK
5 | PWD RMU |  | 11 |  |  | 1 | 663812.1 | 664891.07 | 1078.97 | 1 |  | 1078.97 | 1107.0981 | Tejgaon |  |  |  | PWD RMU | 1107.0981 | 1121.3203 | -14.2223 | -1.2684 | OK
1 | Civil Aviation Feeder |  | 11 |  | DHK60977 | 1 | 75045.2 | 104221.4 | 29176.2 | 60 |  | 1750572 | 1796208.2928 | Tejgaon |  |  |  | Civil Aviation Feeder | 1796208.2928 | 1647887.2922 | 148321.0006 | 9.0007 | OK
2 | Ahasanullah Eng. | C171L | 11 |  | DHK60867 | 1 | 920168.5 | 925616.4 | 5447.9 | 60 |  | 326874 | 335395.3962 | Tejgaon |  |  |  | Ahasanullah Eng. | 335395.3962 | 345298.926 | -9903.5298 | -2.8681 | OK
3 | New GMG Feeder | C110M | 11 |  | DHK61106 | 1 | 226666.6 | 250038.5 | 23371.9 | 60 |  | 1402314 | 1438871.4294 | Tejgaon |  |  |  | New GMG Feeder | 1438871.4294 | 1344265.9199 | 94605.5095 | 7.0377 | OK
4 | Shikajo | C171Z | 11 |  | HA021101036-02 | 1 | 67747307 | 68364188 | 616881 | 1 |  | 616881 | 632962.6933 | Tejgaon |  |  |  | Shikajo | 632962.6933 | 500012.7069 | 132949.9864 | 26.5893 | OK
5 | Kahinur |  | 11 |  |  | 1 | 629590.2 | 643107.3 | 13517.1 | 60 |  | 811026 | 832168.9293 | Tejgaon |  |  |  | Kahinur | 832168.9293 | 770227.3214 | 61941.6079 | 8.042 | OK
6 | Link road | C171X | 11 |  | 8A021100380-02 | 1 | 67053201 | 67314478 | 261277 | 1 |  | 261277 | 268088.3243 | Tejgaon |  |  |  | Link road | 268088.3243 | 237640.4803 | 30447.844 | 12.8126 | OK
7 | Shanta | C110E | 11 |  |  | 1 | 363300.9 | 370028.3 | 6727.4 | 60 |  | 403644 | 414166.741 | Tejgaon |  |  |  | Shanta | 414166.741 | 368965.1962 | 45201.5448 | 12.2509 | OK
1 | Karnafuly Feeder | C110Y | 11 |  | DHK61084 | 1 | 38208.8 | 38707.8 | 499 | 1000 |  | 499000 | 512008.611 | Tejgaon |  |  |  | Karnafuly Feeder | 512008.611 | 447459.6361 | 64548.9749 | 14.4257 | OK
2 | Butex | C110BT | 11 |  |  | 1 | 1556 | 1632.1 | 76.1 | 1000 |  | 76100 | 78083.8783 | Tejgaon |  |  |  | Butex | 78083.8783 | 78020.671 | 63.2074 | 0.081014 | OK
3 | OriON LAB | C171A | 11 |  |  | 1 | 8567709 | 8638421 | 70712 | 1 |  | 70712 | 72555.4166 | Tejgaon |  |  |  | OriON LAB | 72555.4166 | 53925.9927 | 18629.4239 | 34.5463 | OK
4 | Nina kabbo | C171Y | 11 |  | 201101025-2 | 1 | 18183943 | 18353070 | 169127 | 1 |  | 169127 | 173536.0328 | Tejgaon |  |  |  | Nina kabbo | 173536.0328 | 157354.7907 | 16181.2421 | 10.2833 | OK
5 | Satrong | C171S | 11 |  | HA021100515-2 | 1 | 43959 | 885436 | 841477 | 1 |  | 841477 | 863413.7674 | Tejgaon |  |  |  | Satrong | 863413.7674 | 773782.6044 | 89631.163 | 11.5835 | OK
6 | South East RMU |  | 11 |  |  | 1 | 1291.7 | 1351.4 | 59.7 | 1000 |  | 59700 | 61256.3408 | Tejgaon |  |  |  | South East RMU | 61256.3408 | 54029.8186 | 7226.5222 | 13.3751 | OK
7 | Rangs Bhaban |  | 11 |  | HA021100939-2 | 1 | 1190991 | 1287761 | 96770 | 1 |  | 96770 | 99292.732 | Tejgaon |  |  |  | Rangs Bhaban | 99292.732 | 85674.5593 | 13618.1728 | 15.8952 | OK
8 | Babli | C171R | 11 |  |  | 1 | 64050.3 | 65182.6 | 1132.3 | 1000 |  | 1132300 | 1161818.3371 | Tejgaon |  |  |  | Babli | 1161818.3371 | 1421205.9945 | -259387.6574 | -18.2512 | OK
| SPL |  | 11 |  |  | 1 | 6491.7 | 6879.1 | 387.4 | 1000 |  | 387400 | 397499.2703 | Tejgaon |  |  |  | SPL | 397499.2703 | 381333.5894 | 16165.6809 | 4.2392 | OK
9 | DNCC Hospital |  | 11 |  |  | 1 | 19236.1 | 19573.3 | 337.2 | 1000 |  | 337200 | 345990.5884 | Tejgaon |  |  |  | DNCC Hospital | 345990.5884 | 461975.1098 | -115984.5214 | -25.1062 | OK
| 11/.415 kv Local transformer |  | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
|  |  | 10: Grand Total | 13240464.6677 | 12904063.97 | 13240464.6677 | 2.6069
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Tejgaon | at 33 KV level |  | 13240464.6677
[6 empty] | Total = |  |  | 13240464.6677 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 |  | 33 | 0 | 214393/44-2711 | 1.5 | 7383.4 | 7383.4 | 0 | 1000 | Estimated | 5022116.1 | 4899708.1351
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 4891176 | 4771959.5406
|  |  | 10: Total |  | 9913292.1 | 9671667.6757
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 33 | Import | DHKC9350 | 1 | 60598.66 | 79011.25 | 18412.59 | 270 | 4971399.3
2 | Shatmasjid-2 |  | 33 | Import | DHKC9354 | 1 | 89239.65 | 107478.69 | 18239.04 | 270 | 4924540.8
|  |  | 7: 0; 8: 0; 10: Total | 9895940.1
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  | 7: 0; 8: 0
1 | Transfomer-1 (T1) |  | 33 | Export | DHKC9353 | 1 | 62034.92 | 80635.35 | 18600.43 | 180 |  | 3348077.4
2 | Transfomer-2 (T2) |  | 33 | Export | DHKC9305 | 1 | 47060.06 | 74478.89 | 27418.83 | 180 |  | 4935389.4
|  |  | 10: Total |  | 8283466.8 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 4: 9671667.6757; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | ASADGATE 33 KV NET IMPORT |  | 9895940.1
| IMPORT-2 |  | 6: ASADGATE 33 KV NET IMPORT; 9=8-7: 9895940.1 | ASADGATE 11 KV NET IMPORT |  | 9895940.1
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9671667.6757
11 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHKC9371 | 1 | 89244.34 | 101560.6 | 12316.26 | 180 | 3348077.4 |  |  |  | From Upstream | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHKC9337 | 1 | 46314.3 | 73487.5 | 27173.2 | 180 | 4891176 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming |  | 11 | Import |  | 1 | 0 | 6.7 | 6.7 | 240000 | 1608000
|  |  | 10: Total | 9847253.4 |  | 9895940.1 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE |  | 6: 1.086 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | D570T | 11 | T-3 | DHKC9332 | 1 | 88196.59 | 89964.8 | 1768.21 | 60 |  | 106092.6 | 107250.5214 | Shere b.nagar |  |  |  | Gonobhaban | 107250.5214 | 122369.9622 | -15119.4408 | -12.3555 | OK
2 | Town hall | D270R | 11 | T-1 | DHKC9339 | 1 | 62557.11 | 82632.87 | 20075.76 | 60 |  | 1204545.6 | 1217692.3145 | Shyamoli |  |  |  | Town hall | 1217692.3145 | 920494.8774 | 297197.4371 | 32.2867 | OK
3 | Sukrabad/South Plaza | D570S | 11 | T-1 | DHKC9324 | 1 | 4830.73 | 15312.4 | 10481.67 | 60 |  | 628900.2 | 635764.1754 | Shere b.nagar |  |  |  | Sukrabad/South Plaza | 635764.1754 | 615402.167 | 20362.0084 | 3.3087 | OK
4 | Wasa O/H | C270W | 11 | T-1 | DHKC9333 | 1 | 85676.5 | 96035.51 | 10359.01 | 60 |  | 621540.6 | 628324.2509 | Satmasjid |  |  |  | Wasa O/H | 628324.2509 | 614343.782 | 13980.4689 | 2.2757 | OK
5 | Bangabandhu Memorial Museum |  | 11 | T-1 | DHKC9334 | 1 | 16724.78 | 16819.36 | 94.58 | 60 |  | 5674.8 | 5736.7362 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 5736.7362 | 6110.3919 | -373.6557 | -6.1151 | OK
6 | Post Office | D470Q | 11 | T-3 | DHKC9330 | 1 | 70225.65 | 71903.05 | 1677.4 | 60 |  | 100644 | 101742.454 | Shyamoli |  |  |  | Post Office | 101742.454 | 0 | 101742.454 | #DIV/0! | #DIV/0!
7 | Rapa Plaza Feeder | D470W | 11 | T-3 | DHKC9351 | 1 | 69378.79 | 93104.74 | 23725.95 | 60 |  | 1423557 | 1439094.0602 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1439094.0602 | 1479185.5212 | -40091.461 | -2.7104 | OK
8 | Iqbal Road O/H | D470P | 11 | T-1 | DHKC9331 | 1 | 71246.62 | 85155.03 | 13908.41 | 60 |  | 834504.6 | 843612.5937 | Shyamoli |  |  |  | Iqbal Road O/H | 843612.5937 | 1013930.856 | -170318.2623 | -16.7978 | OK
9 | Shangshad Bhaban |  | 11 | T-2 | DHKC9370 | 1 | 24139.05 | 24273.39 | 134.34 | 60 |  | 8060.4 | 8148.3732 | Shere b.nagar |  |  |  | Shangshad Bhaban | 8148.3732 | 196.1183 | 7952.255 | 4054.826 | FAULT
10 | Jakir Hossain Road | C270J | 11 | T-2 | DHKC9373 | 1 | 5219.5 | 20350.99 | 15131.49 | 60 |  | 907889.4 | 917798.3339 | Satmasjid |  |  |  | Jakir Hossain Road | 917798.3339 | 670678.1043 | 247120.2296 | 36.8463 | OK
11 | New Colony O/H Feeder | C270N | 11 | T-2 | DHKC9369 | 1 | 72759.3 | 86310.66 | 13551.36 | 60 |  | 813081.6 | 821955.7777 | Satmasjid |  |  |  | New Colony O/H Feeder | 821955.7777 | 755010.2724 | 66945.5053 | 8.8668 | OK
12 | Aurangzeb Feeder | D470M | 11 | T-2 | DHKC9321 | 1 | 82718.83 | 98346.78 | 15627.95 | 60 |  | 937677 | 947911.0433 | Shyamoli |  | CF Corrected |  | Aurangzeb Feeder | 947911.0433 | 886695.1992 | 61215.8441 | 6.9038 | OK
13 | Asadgate Local Feeder | C270E | 11 | T-2 | DHKC9338 | 1 | 68343.91 | 79518.09 | 11174.18 | 60 |  | 670450.8 | 677768.2691 | Satmasjid |  |  |  | Asadgate Local Feeder | 677768.2691 | 490361.0738 | 187407.1954 | 38.2182 | OK
14 | Sonarbangla Road | D470R | 11 | T-2 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | D470H | 11 | T-2 | DHKC9366 | 1 | 37436.64 | 60570.87 | 23134.23 | 60 |  | 1388053.8 | 1403203.3693 | Shyamoli |  | CF Corrected |  | Humayun Road | 1403203.3693 | 1420833.1418 | -17629.7725 | -1.2408 | OK
16 | NHA | D470B | 11 | T-2 | DHKC9374 | 1 | 72931.85 | 75168.7 | 2236.85 | 60 |  | 134211 | 135675.8127 | Shyamoli |  | CF Corrected |  | NHA | 135675.8127 | 133251.9119 | 2423.9008 | 1.819 | OK
17 | Auxiliary transformer |  | 0.415 | T-2 |  | 1 | 680111 | 684327 | 4216 | 1 |  | 4216 | 4262.0145 | Satmasjid |  |  |  | Auxiliary transformer | 4262.0145 | 4198.0207 | 63.9937 | 1.5244 | OK
|  |  | 10: Grand Total | 9895940.1 | 9789099.4 | 9895940.1 | 1.0914
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 751163.07
[6 empty] | Dhanmondi | at 33 KV level |  | 1444830.7964
[6 empty] | Satmasjid | at 33 KV level |  | 3050108.6461
[6 empty] | Shyamoli | at 33 KV level |  | 4649837.5875
at 33 KV level
[6 empty] | Total = |  |  | 9895940.1 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 122292 | 124166 | 1874 | 2000 | 0 | 3748000 | 3741882.6613
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 107301 | 109846 | 2545 | 2000 | 0 | 5090000 | 5081692.3015
|  |  | 10: Total |  | 8838000 | 8823574.9628 | -0.16322
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import |  | 1 | 3084240 | 6799980 | 3715740 | 1 | 3715740
2 | Madertek Circuit-02 |  | 33 | Import |  | 1 | 3726060 | 8773540 | 5047480 | 1 | 5047480
3 | Ullon O/H |  | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 8763220 | 0 | 0
| BANASREE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BANASREE 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | 14 | 1 | 9124320 | 12841520 | 3717200 | 1 |  | 3717200
2 | Transformer-02 |  | 33 | Export | 74 | 1 | 595760 | 5643420 | 5047660 | 1 |  | 5047660 |  |  | Meter Problem
|  |  | 10: Total |  | 8764860
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 4: 8823574.9628; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 8823574.9628
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 8823574.9628 | 33 KV TX HV SIDE |  | 8764860
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 58714.9628
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.6654%
| TOTAL IMPORT |  | 4: 8823574.9628
11 KV SIDE of___BANASREE 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 3717200 |  | 3742101.169 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | 198 | 1 | 0 | 0 | 0 | 1 | 5047660 |  | 5081473.7939 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 8: 0; 10: Total | 8764860 |  | 8823574.9628 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE |  | 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | F292A | 11 |  | 141 | 1 | 5889040 | 7062540 | 1173500 | 1 |  | 1173500 | 1187172.5914 | Banosree |  |  |  | Angur Jora | 1187172.5914 | 895336.6304 | 291835.961 | 32.5951 | OK
2 | Block F-G Avenue | F299G | 11 |  | 68 | 1 | 7370560 | 7830960 | 460400 | 1 |  | 460400 | 465764.1765 | Banosree |  |  |  | Block F-G Avenue | 465764.1765 | 480429.4597 | -14665.2833 | -3.0525 | OK
3 | Banasree Main Road(Monpura) | F292P | 11 |  | 168 | 1 | 1529960 | 1901200 | 371240 | 1 |  | 371240 | 375565.3624 | Banosree |  |  |  | Banasree Main Road(Monpura) | 375565.3624 | 377379.2998 | -1813.9374 | -0.48067 | OK
4 | Baitul Kuddus | F292Q | 11 |  | 62 | 1 | 544440 | 1829560 | 1285120 | 1 |  | 1285120 | 1300093.0896 | Banosree |  |  |  | Baitul Kuddus | 1300093.0896 | 1340742.7704 | -40649.6808 | -3.0319 | OK
5 | Ideal | F214I | 11 |  |  | 1 | 1916520 | 2321480 | 404960 | 1 |  | 404960 | 409678.2383 | Banosree |  |  |  | Ideal | 409678.2383 | 418421.6214 | -8743.3832 | -2.0896 | OK
6 | Central Mosque | F292C | 11 |  | 46 | 1 | 209120 | 1371180 | 1162060 | 1 |  | 1162060 | 1175599.3026 | Banosree |  |  |  | Central Mosque | 1175599.3026 | 1149427.3814 | 26171.9212 | 2.277 | OK
7 | Larive | F299L | 11 |  | 47 | 1 | 5116560 | 5702000 | 585440 | 1 |  | 585440 | 592261.0327 | Banosree |  |  |  | Larive | 592261.0327 | 588286.7419 | 3974.2908 | 0.67557 | OK
8 | Bank Colony | A299K | 11 |  |  | 1 | 246920 | 1337360 | 1090440 | 1 |  | 1090440 | 1103144.8492 | Khilgaon |  |  |  | Bank Colony | 1103144.8492 | 1071261.1488 | 31883.7004 | 2.9763 | OK
9 | Salambagh | A299G | 11 |  |  | 1 | 8586160 | 9701240 | 1115080 | 1 |  | 1115080 | 1128071.9329 | Khilgaon |  |  |  | Salambagh | 1128071.9329 | 1082127.669 | 45944.2639 | 4.2457 | OK
10 | Titas Road | A299T | 11 |  |  | 1 | 6413520 | 7487200 | 1073680 | 1 |  | 1073680 | 1086189.5764 | Khilgaon |  |  |  | Titas Road | 1086189.5764 | 1042378.0189 | 43811.5575 | 4.203 | OK
11 | AT-1 |  | 0.415 |  | 7734 | 1 | 3637.89 | 3672.3 | 34.41 | 1 |  | 34.41 | 34.8109 | Banosree |  |  |  | AT-1 | 34.8109 | 32.64 | 2.171 | 6.6512 | OK
12 | AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 8823574.9628 | 8721954.41 | 8823574.9628 | 1.1651
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 5506168.6043
[6 empty] | Khilgaon | at 33 KV level |  | 3317406.3585
[6 empty] | Total = |  |  | 8823574.9628 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 377556 | 381222 | 3666 | 2000 | 0 | 7332000 | 7320032.997
ULLON 33 KV SIDE | bar: 4
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 7332000 | 7320032.997
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import | HA-030701133-03 | 1 | 64185090 | 71523788 | 7338698 | 1 | 7338698
2 | Ullon O/H |  | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
|  |  | 8: 0; 10: Total | 7338698 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| GORAN 33 KV SIDE |  | 8: 0
1 | Transformer-01 |  | 33 | Export | HA-030800176-03 | 1 | 32295580 | 34966184 | 2670604 | 1 |  | 2670604
2 | Transformer-02 |  | 33 | Export | HA-030701133-03 | 1 | 99408660 | 101744008 | 2335348 | 1 |  | 2335348
3 | Transformer-03 |  | 33 | Export | DHK-57075 | 1 | 12610.21 | 12707.09 | 96.88 | 120000 |  | 2326048 |  |  | Problem
|  |  | 10: Total |  | 7332000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 4: 7320032.997; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7320032.997
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 7320032.997 | 33 KV TX HV SIDE |  | 7332000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -11967.003
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.1635%
| TOTAL IMPORT |  | 4: 7320032.997
11 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
| GORAN 11 KV SIDE | [14 empty] | 175
| 33/11 kV Transfomer-1 Incoming |  | 11 | IMPORT |  | 1 | 72858260 | 75524686 | 2666426 | 1 | 2666426 |  | 2530711.9942 |  |  | 80
| 33/11 kV Transfomer-2 Incoming |  | 11 |  |  | 1 | 6486430 | 9214791 | 2728361 | 1 | 2728361 |  | 2589494.6671 |  |  | 95
| 33/11 kV Transfomer-3 Incoming |  | 11 |  |  | 1 | 91812120 | 94129916 | 2317796 | 1 | 2317796 |  | 2199826.3358 |  |  | 31.6667
|  |  | 7: 0; 8: 0; 10: Total | 7712583 |  | 7320032.997 |  |  | 111.6667
| GORAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Meradia | F214M | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estiimated | 1137855.6 | 1158986.604 | Banosree | 100 |  |  | Meradia | 1158986.604 | 1017252.8765 | 141733.7275 | 13.933 | OK
2 | Shipahibagh | A914S | 11 |  | HA-021001030-02 | 1 | 44871090 | 45650758 | 779668 | 1 |  | 779668 | 794147.1375 | Bashabo |  |  |  | Shipahibagh | 794147.1375 | 780874.3368 | 13272.8007 | 1.6997 | OK
3 | Farazi Hospital | F214F | 11 |  | HA-030701081-03 | 1 | 53897450 | 54546599 | 649149 | 1 |  | 649149 | 661204.282 | Banosree |  |  |  | Farazi Hospital | 661204.282 | 689973.7331 | -28769.4511 | -4.1696 | OK
4 | West Bansree | F214W | 11 |  | New Meter | 1 | 1715160 | 2703058 | 987898 | 1 |  | 987898 | 1006244.1562 | Banosree |  |  |  | West Bansree | 1006244.1562 | 986180.4079 | 20063.7484 | 2.0345 | OK
5 | Model School(Nearest) | F214D | 11 |  | HA-030701099-03 | 1 | 29276106 | 30608951 | 1332845 | 1 |  | 1332845 | 1357597.1329 | Banosree |  |  |  | Model School(Nearest) | 1357597.1329 | 1327650.9928 | 29946.1401 | 2.2556 | OK
6 | Bhuiyan Para | F214V | 11 |  | HA-021100508-02 | 1 | 64706638 | 64706638 | 0 | 1 | Estiimated | 1479212.28 | 1506682.5852 | Banosree | 130 |  |  | Bhuiyan Para | 1506682.5852 | 1536319.3028 | -29636.7176 | -1.9291 | OK
7 | Bonobithi (Ideal) School | F214B | 11 |  | HA-021100879-02 | 1 | 22891440 | 23707824 | 816384 | 1 |  | 816384 | 831544.9867 | Banosree |  |  |  | Bonobithi (Ideal) School | 831544.9867 | 824442.7501 | 7102.2365 | 0.86146 | OK
8 | AT-01 |  | 0.415 |  | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 |  | 0.415 |  | 3043146 | 1 | 5148.5 | 5193 | 44.5 | 80 |  | 3560 | 3626.1124 | Banosree |  |  |  | AT-02 | 3626.1124 | 3458.7723 | 167.3401 | 4.8381 | OK
|  |  | 10: Grand Total | 7320032.997 | 7186571.88 | 7320032.997 | 1.8571
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 6525885.8595
[6 empty] | Bashabo | at 33 KV level |  | 794147.1375
[6 empty] | Total = |  |  | 7320032.997 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 |  | 33 | 0 | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 6749190 | 6584686.7117
|  |  | 10: Total |  | 6749190 | 6584686.7117
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
2 | Shatmasjid-2 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
3 | Kallayanpur |  | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
|  |  | 10: Total | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 |  | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 |  | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 4: 6584686.7117; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALMATIA 33 KV NET IMPORT |  | 6584686.7117
| IMPORT-2 |  | 6: LALMATIA 33 KV NET IMPORT; 9=8-7: 6584686.7117 | LALMATIA 11 KV NET IMPORT |  | 6749190
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -164503.2883
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -2.498%
| TOTAL IMPORT |  | 4: 6584686.7117
11 KV SIDE of___LALMATIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | DHK000180 | 1 | 3111484 | 3139578 | 28094 | 90 | 2528460 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | DHK000177 | 1 | 3234805 | 3281702 | 46897 | 90 | 4220730 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 6749190 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 90 | 1024070.04 | 1031021.6096 | Dhanmondi | Estimated | 200 |  | Shankor O/H | 1031021.6096 | 986156.5854 | 44865.0242 | 4.5495 | OK
2 | Bangabobondhu museum | D207B | 11 | Export |  | 1 | 630081 | 630081 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 85 |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 89989535 | 90650326 | 660791 | 1 |  | 660791 | 665276.5669 | Dhanmondi |  | 115 |  | Road No-13/A | 665276.5669 | 976232.0912 | -310955.5243 | -31.8526 | OK
4 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 9575787 | 10165740 | 589953 | 1 |  | 589953 | 593957.7059 | Dhanmondi |  | 38.3333 |  | Jaforabad | 593957.7059 | 616675.0096 | -22717.3037 | -3.6838 | OK
5 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 123.3333 |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26546.3 | 26657.2 | 110.9 | 3333.33 |  | 369666.297 | 372175.6576 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 372175.6576 | 380721.3853 | -8545.7278 | -2.2446 | OK
1 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71863.1 | 72125 | 261.9 | 3333.33 |  | 872999.127 | 878925.2004 | Dhanmondi |  |  |  | Road No -15 | 878925.2004 | 882719.5917 | -3794.3914 | -0.42985 | OK
2 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79491.8 | 79491.8 | 0 | 3333.33 |  | 0 | 0 | Dhanmondi |  |  |  | Road No-27 South | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Road 25 | D207C | 11 | Export |  | 1 | 72062.7 | 72248.8 | 186.1 | 3333.3 |  | 620327.13 | 624538.0209 | Dhanmondi |  |  |  | Road 25 | 624538.0209 | 673603.913 | -49065.8921 | -7.2841 | OK
3 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38432.5 | 38501 | 68.5 | 3333.33 |  | 228333.105 | 229883.0707 | Dhanmondi |  |  |  | Ibne Sina | 229883.0707 | 184786.6884 | 45096.3824 | 24.4046 | OK
4 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 66976858 | 67892083 | 915225 | 1 |  | 915225 | 921437.7101 | Dhanmondi |  |  |  | Road No-31 (PARI) | 921437.7101 | 1258159.4304 | -336721.7203 | -26.763 | OK
5 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | 125 | 1422319.5 | 1431974.4578 | Dhanmondi | Estimated |  |  | Satmoszid Road West | 1431974.4578 | 1355965.3049 | 76009.1529 | 5.6055 | OK
|  |  | 10: Grand Total | 6749190 | 6703684.199 | 6749190 | 0.67882
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Dhanmondi | at 33 KV level |  | 6749190
[6 empty] | Total = |  |  | 6749190 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) |  | 33 | 0 | BD001918 | 1 | 2225.57 | 2241.26 | 15.69 | 240000 | 0 | 3765600 | 3773119.372
23 | Green Road Circuit-1 |  | 33 | 0 | BD001865 | 1 | 1566.28 | 1589.93 | 23.65 | 240000 | 0 | 5676000 | 5687334.1714
|  |  | 10: Total | 0 | 9441600 | 9460453.5434
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory |  | 3: 33; 4: EXPORT |  | 0
| Green Road Dormatory |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 5676000
| 33/11 KV Transformer No.2. |  | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 3765600
|  |  | 10: Total |  | 9441600
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 4: 9460453.5434; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | Green Road 33 KV NET IMPORT |  | 9460453.5434
| IMPORT-2 |  | 6: Green Road 33 KV NET IMPORT; 9=8-7: 9460453.5434 | Green Road 11 KV NET IMPORT |  | 9460453.5434
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 9460453.5434 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9460453.5434
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | 195
| Green Road 11 KV X-F SIDE | [14 empty] | 35
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 00138 | 1 | 3435776 | 3497154 | 61378 | 100 | 6137800 |  |  |  |  | 160
2 | Transfomer-2 Incoming |  | 11 | Import | HA-021101496 | 1 | 7060.3328 | 7467.224 | 406.8912 | 10000 | 3765600 |  |  |  |  | 53.3333
|  |  | 7: 0; 8: 0; 10: Total | 9903400 |  | 9460453.5434 |  |  | 88.3333
| Green Road 11 KV SIDE |  | 7: 0; 8: 0
1 | Lab aid/local RMU | C302L | 11 |  | 3C65883 | 1 | 83870 | 87751 | 3881 | 300 |  | 1164300 | 1177040.8083 | Paribag |  |  |  | Lab aid/local RMU | 1177040.8083 | 1057587.2788 | 119453.5295 | 11.2949 | OK
2 | Green View | C302V | 11 |  | DHK000151 | 1 | 68990.1 | 69185.4 | 195.3 | 3333.33 |  | 650999.349 | 658123.1641 | Paribag |  |  |  | Green View | 658123.1641 | 630919.372 | 27203.7921 | 4.3118 | OK
3 | Central Road | C302C | 11 |  | 65943 | 1 | 47189 | 50082 | 2893 | 300 |  | 867900 | 877397.3353 | Paribag |  |  |  | Central Road | 877397.3353 | 902974.6057 | -25577.2704 | -2.8326 | OK
4 | New Market | D802N | 11 |  | DHK000194 | 1 | 48560.4 | 48818.9 | 258.5 | 3333.33 |  | 861665.805 | 871094.9202 | Jigatola |  |  |  | New Market | 871094.9202 | 819653.0402 | 51441.88 | 6.2761 | OK
5 | DPH Feeder |  | 11 |  | HA-021100459 | 1 | 42295.5 | 42371.7 | 76.2 | 1 | 22 | 250328.232 | 253067.5466 | Paribag | Estimated |  |  | DPH Feeder | 253067.5466 | 247284.3988 | 5783.1478 | 2.3387 | OK
6 | Dhanmondi Rd 4(md Banglo | D802F | 11 |  | 6604464 | 1 | 4622.84 | 4651.5 | 28.66 | 60000 |  | 1719600 | 1738417.3958 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1738417.3958 | 1238731.1207 | 499686.2752 | 40.3386 | FAULT
1 | Green Road East | C302X | 11 |  | HA-021101050 | 1 | 2346095 | 3117617 | 771522 | 1 |  | 771522 | 779964.6814 | Paribag |  |  |  | Green Road East | 779964.6814 | 761158.9013 | 18805.7801 | 2.4707 | OK
2 | North Road | C302Z | 11 |  | HA-021100884 | 1 | 88545456 | 89511698 | 966242 | 1 |  | 966242 | 976815.4812 | Paribag |  |  |  | North Road | 976815.4812 | 980713.9797 | -3898.4986 | -0.39752 | OK
3 | Green road SS | C302W | 11 |  | DHK00135 | 1 | 24585820 | 25236846 | 651026 | 1 |  | 651026 | 658150.1067 | Paribag |  |  |  | Green road SS | 658150.1067 | 686945.8347 | -28795.728 | -4.1918 | OK
4 | Plane Moszid | C302A | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 90 | 1024070.04 | 1035276.3271 | Paribag | Estimated |  |  | Plane Moszid | 1035276.3271 | 803674.2962 | 231602.0309 | 28.8179 | OK
5 | Malancha | C302H | 11 |  | HA-021100953 | 1 | 40127485 | 40552881 | 425396 | 1 |  | 425396 | 430051.0622 | Paribag |  |  |  | Malancha | 430051.0622 | 425713.4414 | 4337.6208 | 1.0189 | OK
| AT -1 |  | 7: 22891; 8: 22891; 9=8-7: 0; 10: 1 |  | 5000 | 5054.7145 | Paribag |  |  |  | AT -1 | 5054.7145 | 5082.5994 | -27.8849 | -0.54864 | OK
|  |  | 10: Grand Total | 9460453.5434 | 9358049.426 | 9460453.5434 | 1.0943
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 6850941.2274
[6 empty] | Jigatola | at 33 KV level |  | 2609512.3161
[6 empty] | Total = |  |  | 9460453.5434 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory |  | 33 | 0 | 76026305 | 1 | 8118.51 | 8131.2 | 12.69 | 180000 | Reading From G. Dormitory Side | 4542690 | 4549997.4614
|  |  | 10: Total | 0 | 4542690 | 4549997.4614
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 |  | 33 | 0 | 0 | 1 | 78.65 | 84.62 | 5.97 | 360000 | 0 | 2149200 | 2143172.559
9 | Green Road -2 |  | 33 | 0 | 0 | 1 | 103.55 | 107.04 | 3.49 | 360000 | 0 | 1256400 | 1252876.4206
|  |  | 10: Total | 0 | 3405600 | 3396048.9796
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [10 empty] | 7948290 | 7946046.441
1 | Mogbazar Grid |  | 33 | Import | BD 017064 | 1 | 59735.06 | 64277.75 | 4542.69 | 1000 | 4542690
2 | Green Road SS |  | 33 | Import | BD 017070 | 1 | 32923.13 | 32923.13 | 0 | 1000 | 0
3 | Jigatola Ckt-1 |  | 33 | Import |  | 1 | 28044.42 | 30272.6 | 2228.18 | 1000 | 2228180
NEW | Jigatola Ckt-2 |  | 33 |  |  | 1 | 37131.32 | 38465.45 | 1334.13 | 1000 | 1334130 |  |  |  | NEW FOUND
|  |  | 7: 0; 8: 0; 10: Total | 8105000 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | BD 017065 | 1 | 70659.55 | 78296.23 | 7636.68 | 888.89 |  | 6788168.4852
2 | Transformer-02 |  | 33 | Export | BD 017069 | 1 | 26918.14 | 28426.64 | 1508.5 | 888.89 |  | 1340890.565
|  |  | 10: Total |  | 8129059.0502 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 7946046.441; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 7946046.441
|  |  | 6: GREEN ROAD DORMITORY 33 KV NET IMPORT; 9=8-7: 7946046.441 | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 7946046.441
|  |  | 6: TOTAL EXPORT; 9=8-7: 7946046.441 | LOSS UNITS=> |  | 0
|  |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 7946046.441
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD 014050 | 1 | 27768.31 | 34525.35 | 6757.04 | 1000 | 6757040
2 | Transformer-02 Incoming |  | 11 | Import | BD 014059 | 1 | 315.5 | 1636.51 | 1321.01 | 1000 | 1321010
|  |  | 7: 0; 8: 0; 10: Total | 8078050 |  | 7946046.441
| GREEN ROAD DORMITORY 11 KV SIDE |  | 7: 0; 8: 0
1 | North Dhanmondi | C31002 | 11 |  | BD 014039 | 1 | 24454.33 | 24800.46 | 346.13 | 2000 |  | 692260 | 693021.0838 | Paribag |  |  |  | North Dhanmondi | 693021.0838 | 646999.5384 | 46021.5454 | 7.1131 | OK
2 | Lake circus | C31004 | 11 |  | BD 014047 | 1 | 40180.55 | 40691.07 | 510.52 | 2000 |  | 1021040 | 1022162.5508 | Paribag |  |  |  | Lake circus | 1022162.5508 | 997214.4169 | 24948.1339 | 2.5018 | OK
3 | Bashir Uddin | C31003 | 11 |  | BD 014037 | 1 | 16256.19 | 16477.88 | 221.69 | 2000 |  | 443380 | 443867.4604 | Paribag |  |  |  | Bashir Uddin | 443867.4604 | 436278.7563 | 7588.7041 | 1.7394 | OK
4 | Raza Bazar | D5100R | 11 |  | BD 013939 | 1 | 24591.09 | 24953.77 | 362.68 | 2000 |  | 725360 | 726157.4746 | Shere b.nagar |  |  |  | Raza Bazar | 726157.4746 | 674061.5972 | 52095.8774 | 7.7287 | OK
5 | Rasel Squar | D5100RS | 11 |  | BD 013970 | 1 | 36953.14 | 37481.95 | 528.81 | 2000 |  | 1057620 | 1058782.7676 | Shere b.nagar |  |  |  | Rasel Squar | 1058782.7676 | 1005337.1163 | 53445.6513 | 5.3162 | OK
6 | Bow Bazar | D5100O | 11 |  | BD 013967 | 1 | 27679.89 | 28026.56 | 346.67 | 2000 |  | 693340 | 694102.2712 | Shere b.nagar |  |  |  | Bow Bazar | 694102.2712 | 682123.0702 | 11979.201 | 1.7562 | OK
7 | BRB Hospital | D5100S | 11 |  | BD 014003 | 1 | 14821.96 | 15069.96 | 248 | 2000 |  | 496000 | 496545.3119 | Shere b.nagar |  |  |  | BRB Hospital | 496545.3119 | 418074.1134 | 78471.1984 | 18.7697 | OK
8 | Green Road North | C31008 | 11 |  | BD 013969 | 1 | 18290.35 | 18578.83 | 288.48 | 2000 |  | 576960 | 577594.3208 | Paribag |  |  |  | Green Road North | 577594.3208 | 724552.9497 | -146958.6289 | -20.2827 | OK
1 | Water Bhaban | D5100PB | 11 |  | BD 014004 | 1 | 5892.83 | 5979.43 | 86.6 | 2000 |  | 173200 | 173390.4194 | Shere b.nagar |  |  |  | Water Bhaban | 173390.4194 | 165821.4387 | 7568.9807 | 4.5645 | OK
2 | Alamin Road | C31007 | 11 |  | BD 014006 | 1 | 20044 | 20202.42 | 158.42 | 2000 |  | 316840 | 317188.3399 | Paribag |  |  |  | Alamin Road | 317188.3399 | 338316.5525 | -21128.2126 | -6.2451 | OK
3 | Katal Bagan | C3100K | 11 |  |  | 1 | 12838.84 | 13439.45 | 600.61 | 2000 |  | 1201220 | 1202540.6442 | Paribag |  |  |  | Katal Bagan | 1202540.6442 | 1133279.8362 | 69260.8079 | 6.1115 | OK
4 | Eastern Pantho chaya | C310010 | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Kawran Bazar |  | 11 |  |  | 1 | 13.19 | 13.19 | 0 | 2000 |  | 0 | 0
5 | Kalabagan |  | 11 |  | BD 014005 | 1 | 6548.85 | 6635.97 | 87.12 | 2000 |  | 174240 | 174431.5628 | Paribag |  |  |  | Kalabagan | 174431.5628 | 194108.025 | -19676.4623 | -10.1369 | OK
6 | Univer Hospital | C310012 | 11 |  | BD 013963 | 1 | 1566.06 | 1656.03 | 89.97 | 2000 |  | 179940 | 180137.8295 | Paribag |  |  |  | Univer Hospital | 180137.8295 | 169923.606 | 10214.2235 | 6.0111 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 |  | BD 013971 | 1 | 10877.61 | 10970.57 | 92.96 | 2000 |  | 185920 | 186124.404 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 186124.404 | 151882.2334 | 34242.1705 | 22.5452 | OK
|  |  | 10: Grand Total | 7946046.441 | 7937320 | 7946046.441 | 0.10994
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 4797068.1963
[6 empty] | Shere b.nagar | at 33 KV level |  | 3148978.2447
[6 empty] | Total = |  |  | 7946046.441 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1729.7276 | 1758.6594 | 28.9318 | 240000 | 0 | 6943632 | 6945166.6951
2 | Taltala-2 |  | 33 |  | BD001837 | 1 | 2662.9397 | 2662.9397 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 6943632 | 6945166.6951
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming |  | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 |  | 0
| 33 KV Ullon-ckt-2 incoming |  | 3: 33; 6: 1; 9=8-7: 0; 10: 1000 |  | 0
|  |  | 10: Total |  | 0 | 6945166.6951
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) |  | 3: 33; 4: EXPORT |  | 0
| 33 KV Khilgaon Feeder(Import) |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
|  |  | 10: Total |  | 0 | 6945166.6951 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 4: 6945166.6951; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TALTOLA 33 KV NET IMPORT |  | 6945166.6951
| IMPORT-2 |  | 6: TALTOLA 33 KV NET IMPORT; 9=8-7: 6945166.6951 | TALTOLA 11 KV NET IMPORT |  | 6945166.6951
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 6945166.6951 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 6945166.6951
11 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming |  | 11 | Import | 06604431 | 1 | 8797.84 | 8841.1 | 43.26 | 160000 | 6921600
2 | Transformer-02 Incoming |  | 11 | Import | 06604341 | 1 | 9473.89 | 9473.89 | 0 | 160000 | 0
3 | Transformer-03 Incoming |  | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 6921600 |  | 6945166.6951
| TALTOLA 11 KV SIDE |  | 7: 0; 8: 0
1 | Matir Masjid | A229S | 11 |  | DHK00170 | 1 | 33985.2 | 35295.8 | 1310.6 | 888.8889 |  | 1164977.7778 | 1170440.5193 | Khilgaon |  |  |  | Matir Masjid | 1170440.5193 | 1162051.2612 | 8389.2582 | 0.72194 | OK
2 | Hajipara | A229P | 11 |  | DHK-00108 | 1 | 7902.6 | 8226.2 | 323.6 | 2222.2222 |  | 719111.1111 | 722483.1223 | Khilgaon |  |  |  | Hajipara | 722483.1223 | 693287.1642 | 29195.9581 | 4.2112 | OK
3 | Nearest Feeder | A929N | 11 |  | DHK-00106 | 1 | 92381.2 | 92686.4 | 305.2 | 2222.222 |  | 678222.1544 | 681402.4317 | Bashabo |  |  |  | Nearest Feeder | 681402.4317 | 231246.1023 | 450156.3294 | 194.6655 | FAULT
4 | Reazbagh | A229C | 11 |  | DHK-00109 | 1 | 99870.3 | 100329.8 | 459.5 | 2222.222 |  | 1021111.009 | 1025899.1394 | Khilgaon |  |  |  | Reazbagh | 1025899.1394 | 1033500.8727 | -7601.7333 | -0.73553 | OK
5 | Chowdhury Para | A229F | 11 |  | DHK-00107 | 1 | 53937 | 54150.3 | 213.3 | 2222.222 |  | 473999.9526 | 476222.6038 | Khilgaon |  |  |  | Chowdhury Para | 476222.6038 | 454144.7843 | 22077.8195 | 4.8614 | OK
6 | Model Colleg | A229D | 11 |  | 9122392 | 1 | 2615.34 | 2624.97 | 9.63 | 40000 |  | 385200 | 387006.256 | Khilgaon |  |  |  | Model Colleg | 387006.256 | 0 | 387006.256 | #DIV/0! | #DIV/0!
1 | East Rampura | A229B | 11 |  | DHK-00181 | 1 | 290.7 | 290.7 | 0 | 2222.222 |  | 0 | 0 | Khilgaon |  |  |  | East Rampura | 0 | 676.8179 | -676.8179 | -100 | CHECK
2 | Adarshabagh | A929A | 11 |  | DHK-00090 | 1 | 54102.3 | 54599.9 | 497.6 | 2222.222 |  | 1105777.6672 | 1110962.8113 | Bashabo |  |  |  | Adarshabagh | 1110962.8113 | 1073207.5205 | 37755.2908 | 3.518 | OK
3 | Khailgaon Govt Colony | A229K | 11 |  | DHK00167 | 1 | 78570.4 | 78980.2 | 409.8 | 2222.222 |  | 910666.5756 | 914936.8168 | Khilgaon |  |  |  | Khailgaon Govt Colony | 914936.8168 | 889789.8804 | 25146.9365 | 2.8262 | OK
4 | TV Road | A214T | 11 |  | 6604434 | 1 | 5190.73 | 5190.73 | 0 | 40000 |  | 0 | 0 | Khilgaon |  |  |  | TV Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Post Office |  | 11 |  | 06604476 | 1 | 6677.6 | 6688.82 | 11.22 | 40000 |  | 448800 | 450904.4851 | Bashabo |  |  |  | Post Office | 450904.4851 | 443045.0157 | 7859.4695 | 1.774 | OK
1 | Navana | A929V | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | A929P | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 |  | 0.415 |  | 9187958 | 1 | 919.21 | 980.28 | 61.07 | 80 |  | 4885.6 | 4908.5093 | Bashabo |  |  |  | AT-01 | 4908.5093 | 5310.0427 | -401.5335 | -7.5618 | OK
3 | AT-02 |  | 0.415 |  | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6945166.6951 | 6912751.8477 | 6945166.6951 | 0.46891
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Khilgaon | at 33 KV level |  | 4696988.4577
[6 empty] | Bashabo | at 33 KV level |  | 2248178.2373
[6 empty] | Total = |  |  | 6945166.6951 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 |  | 33 | Import | 35786569 | 1 | 2024.763 | 2034.166 | 9.403 | 180000 | 0 | 1692540 | 10808.12
2 | Sher-e-Banglanagar Ckt-02 |  | 33 | Import | 35786575 | 1 | 739.454 | 747.197 | 7.743 | 180000 | 0 | 1393740 | 8900.06
3 | Sangsad Bhaban (DPDC Ckt-03) |  | 33 |  | 3578 6580 | 1 | 111.818 | 113.188 | 1.37 | 180000 | 0 | 246600 | 1574.72 | Shere b.nagar
|  |  | 10: Total | 0 | 3332880 | 21282.9
|  |  | 10: Net Total | 3354162.9
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | DHK 66505 | 1 | 0 | 0 | 0 | 540 | 0
2 | Agargaon Ckt-02 |  | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0 | 0
| SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SHER-E-BANGLANAGAR 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 |  | 33 | Export | DHK 66500 | 1 | 806208 | 817215 | 11007 | 180 |  | 1981260
|  |  | 10: Total |  | 1981260 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 4: 3354162.9; 6: SHER-E-BANGLANAGAR NOCS; 9=8-7: 248174.72 | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 3105988.18
| IMPORT-2 |  | 6: SHER-E-BANGLANAGAR 33 KV NET IMPORT; 9=8-7: 3105988.18 | 33 KV TX HV SIDE |  | 3105988.18
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 3354162.9
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 66503 | 1 | 2298250 | 2307723 | 9473 | 180 | 1705140 |  | 1433311.8681
2 | Transfomer-2 Incoming |  | 11 | Import | DHK 66495 | 1 | 788889 | 799944 | 11055 | 180 | 1989900 |  | 1672676.3119
|  |  | 7: 0; 8: 0; 10: Total | 3695040 |  | 3105988.18
| SHER-E-BANGLANAGAR 11 KV SIDE |  | 7: 0; 8: 0
1 | Sher-e-Banglanagar Local |  | 11 |  | DHK 66503 | 1 | 87224 | 88011 | 787 | 60 | 11 kv bus-1 R Phase PT missing | 47220 | 47423.8712 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 47423.8712 | 58299.0972 | -10875.226 | -18.6542 | OK
2 | Mirpur Road East | D550F | 11 |  | DHK 60961 | 1 | 861495 | 865247 | 3752 | 60 |  | 225120 | 226091.9501 | Shere b.nagar |  |  |  | Mirpur Road East | 226091.9501 | 274779.1972 | -48687.2471 | -17.7187 | OK
3 | Gonobhaban school | D550E | 11 |  | DHK 66492 | 1 | 538182 | 539146 | 964 | 60 |  | 57840 | 58089.7228 | Shere b.nagar |  |  |  | Gonobhaban school | 58089.7228 | 83830.9415 | -25741.2187 | -30.7061 | OK
4 | Babor Road | D450B | 11 |  | DHK 66489 | 1 | 809511 | 815041 | 5530 | 60 |  | 331800 | 333232.5384 | Shyamoli |  |  |  | Babor Road | 333232.5384 | 453086.2792 | -119853.7407 | -26.4527 | OK
5 | College Gate | D450K | 11 |  | DHK 66487 | 1 | 2743173 | 2752409 | 9236 | 60 |  | 554160 | 556552.5723 | Shyamoli |  |  |  | College Gate | 556552.5723 | 891202.7474 | -334650.175 | -37.5504 | OK
6 | Parade ground |  | 11 |  | DHK 66490 | 1 | 938548 | 938644 | 96 | 60 |  | 5760 | 5784.8687 | Satmasjid |  |  |  | Parade ground | 5784.8687 | 3742.4527 | 2042.4159 | 54.5743 | FAULT
7 | Hospital RMU | D550H | 11 |  | DHK 66491 | 1 | 934179 | 937696 | 3517 | 60 |  | 211020 | 211931.0737 | Shere b.nagar |  |  |  | Hospital RMU | 211931.0737 | 276525.6752 | -64594.6014 | -23.3594 | OK
1 | Shamoly Square |  | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | D550D | 11 |  | DHK 60964 | 1 | 201092.5 | 202037.6 | 945.1 | 60 |  | 56706 | 56950.8268 | Shere b.nagar |  |  |  | Gonobhaban RMU | 56950.8268 | 65049.9758 | -8099.149 | -12.4507 | OK
3 | Krishi University | D550V | 11 |  | DHK 60963 | 1 | 398255.2 | 404088.9 | 5833.7 | 60 |  | 350022 | 351533.2115 | Shere b.nagar |  |  |  | Krishi University | 351533.2115 | 361119.5708 | -9586.3593 | -2.6546 | OK
4 | NEC | D550X | 11 |  | DHK 86073 | 1 | 56.16 | 58.43 | 2.27 | 60000 |  | 136200 | 136788.0402 | Shere b.nagar |  |  |  | NEC | 136788.0402 | 147649.1019 | -10861.0617 | -7.356 | OK
5 | Novo Theater/Army Musium | D550A | 11 |  | DHK 86074 | 1 | 456.07 | 467.79 | 11.72 | 60000 |  | 703200 | 706236.0489 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 706236.0489 | 682801.7652 | 23434.2837 | 3.4321 | OK
6 | Netor |  | 11 |  | DHK 60962 | 1 | 160020.5 | 164620.5 | 4600 | 60 |  | 276000 | 277191.6233 | Shere b.nagar |  |  |  | Netor | 277191.6233 | 255716.1915 | 21475.4318 | 8.3982 | OK
7 | BICC | D550VV | 11 |  |  | 1 | 56.16 | 58.43 | 2.27 | 60000 |  | 136200 | 136788.0402 | Shere b.nagar |  |  |  | BICC | 136788.0402 | 147649.1019 | -10861.0617 | -7.356 | OK
8 | Auxiliary |  | 0.415 |  |  | 1 | 5506.58 | 5529.71 | 23.13 | 60 |  | 1387.8 | 1393.7918 | Shere b.nagar |  |  |  | Auxiliary | 1393.7918 | 2197.8623 | -804.0706 | -36.5842 | OK
|  |  | 10: Grand Total | 3105988.18 | 3092635.8 | 3105988.18 | 0.43175
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 1793738.9317 | Including 41% of Novo Theatre
[6 empty] | Shyamoli | at 33 KV level |  | 889785.1108
[6 empty] | Satmasjid | at 33 KV level |  | 5784.8687
[6 empty] | Tejgaon | at 33 KV level |  | 416679.2689 | 59% of Novo Theatre
[6 empty] | Total = |  |  | 3105988.18 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | 0 | 5408352 | 5407603.7171
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 |  | ABB03918 | 1 | 320061 | 322314 | 2253 | 2000 | 0 | 4506000 | 4505376.5637
|  |  | 10: Total | 0 | 9914352 | 9912980.2809
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 |  | 33 | Import | 38 | 1 | 336400032 | 341808384 | 5408352 | 1 | 5408352
2 | Maniknagor Incoming-02 |  | 33 | Import | 15 | 1 | 250253824 | 254770912 | 4517088 | 1 | 4517088
|  |  | 7: 0; 8: 0; 10: Total | 9925440 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | 16 | 1 | 324996000 | 330402240 | 5406240 | 1 |  | 5406240
4 | Transformer-02 |  | 33 | Export | 196 | 1 | 261512400 | 266030400 | 4518000 | 1 |  | 4518000
|  |  | 10: Total |  | 9924240 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 4: 9912980.2809; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9912980.2809
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 9912980.2809 | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 9924240
[11 empty] | LOSS UNITS=> |  | -11259.7191
[11 empty] | LOSS % IN => |  | -0.1136%
| TOTAL IMPORT |  | 4: 9912980.2809
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | 192 | 1 | 322711168 | 328089152 | 5377984 | 1 | 5377984 |  | 5399223.7928
2 | Transformer-02 Incoming |  | 11 | Import | 118 | 1 | 259803328 | 264299328 | 4496000 | 1 | 4496000 |  | 4513756.488
|  |  | 7: 0; 8: 0; 10: Total | 9873984 |  | 9912980.2809
| MUGDAPARA HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
1 | City Corporation | A997Y | 11 |  | 93 | 1 | 45498128 | 46441248 | 943120 | 1 |  | 943120 | 945178.1823 | Bashabo |  |  |  | City Corporation | 945178.1823 | 123798.2877 | 821379.8946 | 663.4824 | FAULT
2 | Bot tola | B297L | 11 |  |  | 1 | 65267360 | 66613436 | 1346076 | 1 |  | 1346076 | 1349013.5582 | Maniknagar |  |  |  | Bot tola | 1349013.5582 | 1354052.5032 | -5038.945 | -0.37214 | OK
3 | Jhilpar | B997J | 11 |  | 145 | 1 | 39956424 | 40492100 | 535676 | 1 |  | 535676 | 536845.0123 | Mugdapara |  |  |  | Jhilpar | 536845.0123 | 549799.1663 | -12954.154 | -2.3562 | OK
4 | Central Bashaboo | A997C | 11 |  | 128 | 1 | 45762528 | 46705244 | 942716 | 1 |  | 942716 | 944773.3007 | Bashabo |  |  |  | Central Bashaboo | 944773.3007 | 977685.9863 | -32912.6856 | -3.3664 | OK
5 | Kadamtala | B997L | 11 |  | 8 | 1 | 20912708 | 21153428 | 240720 | 1 |  | 240720 | 241245.3262 | Mugdapara | PT Voltage Restored, CF=1 |  |  | Kadamtala | 241245.3262 | 360174.7446 | -118929.4183 | -33.0199 | OK
6 | Ansar VDP | A297A | 11 |  | 119 | 1 | 23402382 | 24000982 | 598600 | 1 |  | 598600 | 599906.3321 | Khilgaon |  |  |  | Ansar VDP | 599906.3321 | 985985.7719 | -386079.4398 | -39.1567 | OK
7 | Mugda Hospital Express-01 | B997H | 11 |  |  | 1 | 7334222 | 7471102 | 136880 | 1 |  | 136880 | 137178.7149 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 137178.7149 | 148451.1163 | -11272.4014 | -7.5933 | OK
8 | Boro Masjid | B997Z | 11 |  | 7 | 1 | 53562788 | 54202588 | 639800 | 1 |  | 639800 | 641196.2434 | Mugdapara | PT Voltage Restored, CF=1 |  |  | Boro Masjid | 641196.2434 | 787897.7465 | -146701.5031 | -18.6194 | OK
1 | Anandodhara | B297B | 11 |  | 120 | 1 | 51855752 | 52464832 | 609080 | 1 |  | 609080 | 610409.2028 | Maniknagar |  |  |  | Anandodhara | 610409.2028 | 615741.3741 | -5332.1713 | -0.86598 | OK
2 | Culvert | A997L | 11 |  | 117 | 1 | 47238964 | 48102164 | 863200 | 1 |  | 863200 | 865083.772 | Bashabo |  |  |  | Culvert | 865083.772 | 856270.8053 | 8812.9666 | 1.0292 | OK
3 | Mugda Hospital Express-02 |  | 11 |  | 97 | 1 | 4870948 | 4885388 | 14440 | 1 |  | 14440 | 14471.5126 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 14471.5126 | 0 | 14471.5126 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | A997J | 11 |  | 98 | 1 | 30580126 | 30755084 | 174958 | 1 |  | 174958 | 175339.813 | Bashabo |  |  |  | Jhor Pukur | 175339.813 | 624661.5892 | -449321.7762 | -71.9304 | CHECK
5 | T&T | B997T | 11 |  | 99 | 1 | 26413816 | 26756894 | 343078 | 1 |  | 343078 | 343826.7033 | Mugdapara |  |  |  | T&T | 343826.7033 | 336675.4629 | 7151.2405 | 2.1241 | OK
6 | Haider Ali | B297H | 11 |  | 9 | 1 | 79614568 | 81093520 | 1478952 | 1 |  | 1478952 | 1482179.5351 | Maniknagar |  |  |  | Haider Ali | 1482179.5351 | 1499220.6846 | -17041.1495 | -1.1367 | OK
| 11kv Tilpapara | A929T | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 1024070.04 | 1026304.8806 | Bashabo | 90 |  |  | 11kv Tilpapara | 1026304.8806 | 1436826.0805 | -410521.1999 | -28.5714
7 | AT-01 |  | 11 |  |  | 1 | 3318.67 | 3345.06 | 26.39 | 1 |  | 26.39 | 26.4476 | Mugdapara |  |  |  | AT-01 | 26.4476 | 24.6426 | 1.805 | 7.3249 | OK
8 | AT-02 |  | 11 |  |  | 1 | 17.34 | 19.08 | 1.74 | 1 |  | 1.74 | 1.7438 | Mugdapara |  |  |  | AT-02 | 1.7438 | 0 | 1.7438 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 9912980.2809 | 9891394.17 | 9912980.2809 | 0.21823
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bashabo | at 33 KV level |  | 3956679.9486
[6 empty] | Maniknagar | at 33 KV level |  | 3441602.296
[6 empty] | Mugdapara | at 33 KV level |  | 1914791.7041
[6 empty] | Khilgaon | at 33 KV level |  | 599906.3321
[6 empty] | Total = |  |  | 9912980.2809 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3331 | 79.3331 | 0 | 240000 | From Downstream | 3209220 | 3209929.308
MANKNAGAR 33 KV SIDE | bar: 4
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 282362 | 283050 | 688 | 2000 | 0 | 1376000 | 1375809.6209
|  |  | 10: Total | 0 | 4585220 | 4585738.9289
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming |  | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming |  | 33 |  |  | 1 | 97522 | 109408 | 11886 | 270 |  | 3209220
| 33 kV Maniknagor Incoming |  | 33 |  |  | 1.08 | 136878 | 144533 | 7655 | 180 |  | 1488132
|  |  | 7: 0; 8: 0; 10: Total |  | 4697352
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KHILGOAN 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer -01 |  | 33 | Export | DHK60982 | 1 | 868117 | 885955 | 17838 | 180 |  | 3210840
4 | Transformer -02 |  | 33 | Export | DHK60947 | 1 | 887243 | 894899 | 7656 | 180 |  | 1378080
|  |  | 10: Total |  | 4588920 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 4: 4585738.9289; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4585738.9289
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 4585738.9289 | 33 KV TX HV SIDE |  | 4588920
[11 empty] | LOSS UNITS=> |  | -3181.0711
[11 empty] | LOSS % IN => |  | -0.06937%
| TOTAL IMPORT |  | 4: 4585738.9289
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | 60
| KHILGOAN 11 KV SIDE | [14 empty] | 30
1 | Transformer-01 Incoming |  | 11 | Import | DHK60927 | 1 | 866539 | 883728 | 17189 | 180 | 3094020 |  | 3180449.7438 |  |  | 30
2 | Transformer-02 Incoming |  | 11 | Import | DHK60928 | 1 | 45328 | 52923 | 7595 | 180 | 1367100 |  | 1405289.1852 |  |  | 10
|  |  | 7: 0; 8: 0; 10: Total | 4461120 |  | 4585738.9289 |  |  | 40
| KHILGOAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Shantinagar s/s-1 |  | 11 |  | DHK60932 | 1 | 481372 | 507338 | 25966 | 60 |  | 1557960 | 1582612.367 | Rajarbag |  |  |  | Shantinagar s/s-1 | 1582612.367 | 1453002.4337 | 129609.9334 | 8.9201 | OK
2 | Gulbagh | D606G | 11 |  | DHK60934 | 1 | 210552 | 220922 | 10370 | 60 |  | 622200 | 632045.3765 | Rajarbag |  |  |  | Gulbagh | 632045.3765 | 600803.3792 | 31241.9973 | 5.2 | OK
3 | Rampura BTV | A206H | 11 |  | DHK60933 | 1 | 15382 | 19607 | 4225 | 60 |  | 253500 | 257511.2551 | Khilgaon |  |  |  | Rampura BTV | 257511.2551 | 79250.248 | 178261.0071 | 224.9343 | FAULT
4 | West Shantibag | D606W | 11 |  | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 477899.352 | 485461.3884 | Rajarbag | 42 |  |  | West Shantibag | 485461.3884 | 493949.9225 | -8488.5341 | -1.7185 | OK
1 | East Malibagh | D606E | 11 |  | DHK60929 | 1 | 690468 | 702800 | 12332 | 60 |  | 739920 | 751628.1179 | Rajarbag |  |  |  | East Malibagh | 751628.1179 | 735547.0753 | 16081.0427 | 2.1863 | OK
2 | Police Line | D606S | 11 |  | DHK60930 | 1 | 611483 | 615719 | 4236 | 60 |  | 254160 | 258181.6986 | Rajarbag |  |  |  | Police Line | 258181.6986 | 276370.7727 | -18189.0741 | -6.5814 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 |  | DHK61017 | 1 | 204786 | 206322 | 1536 | 60 |  | 92160 | 93618.293 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 93618.293 | 90275.8398 | 3342.4532 | 3.7025 | OK
4 | Benjir Bagan | D662R | 11 |  | DHK60985 | 1 | 179547 | 180938 | 1391 | 60 |  | 83460 | 84780.6286 | Rajarbag |  |  |  | Benjir Bagan | 84780.6286 | 99595.8152 | -14815.1866 | -14.8753 | OK
5 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 906572 | 913773 | 7201 | 60 |  | 432060 | 438896.6978 | Switching |  |  |  | Shantinagar s/s-2 | 438896.6978 | 379682.3951 | 59214.3027 | 15.5957 | OK
6 | AT-1 & AT-2 |  | 0.415 |  | ELIB 7374 | 1 | 2579.7 | 2648.35 | 68.65 | 60 |  | 4119 | 4184.177 | Rajarbag |  |  |  | AT-1 & AT-2 | 4184.177 | 4602.1186 | -417.9416 | -9.0815 | OK
|  |  | 10: Grand Total | 4588920 | 4517438.352 | 4588920 | 1.5823
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Rajarbag | at 33 KV level |  | 4208778.533 | Including Switching
[6 empty] | Khilgaon | at 33 KV level |  | 257511.2551
[6 empty] | Moghbazar | at 33 KV level |  | 66556.7552
[6 empty] | Kakrail | at 33 KV level |  | 56073.4567
[6 empty] | Total = |  |  | 4588920 | 0
11 KV SIDE of___Santinagar Switching S/S | [14 empty] | Month February-2024
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 906572 | 913773 | 7201 | 60 |  | 432060 | 438896.6978 | 1.5823
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder |  | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 311340 | 316266.4859 | Rajarbag
2 | 11 Fortune(MogBazar)-new |  | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 65520 | 66556.7552 | Moghbazar
3 | Centerpoint-Kakrail |  | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 55200 | 56073.4567 | Kakrail
[12 empty] | 432060 | 438896.6978 | 1.5823
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 |  | 33 | Import |  | 1 | 1186.857 | 1186.857 | 0 | 180000 | 0 | 0 | 0
2 | Sherebangla to Monipuripara-2 |  | 33 | Import |  | 1 | 930.081 | 964.575 | 34.494 | 180000 | 0 | 6208920 | 39648.53
|  |  | 10: Total | 0 | 6208920 | 39648.53
|  |  | 10: Net Total | 6248568.53
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | BD017103 | 1 | 50093.49 | 50093.49 | 0 | 1000 | 0
2 | Agargaon Ckt-02 |  | 33 | Import | BD017104 | 1 | 48770.26 | 54233.34 | 5463.08 | 1000 | 5463080
|  |  | 7: 0; 8: 0; 10: Total | 5463080 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONIPURIPARA 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | BD017102 | 1 | 50093.49 | 50093.49 | 0 | 1000 |  | 0 |  |  | OMF Corrected by Grid
4 | Transformer-02 |  | 33 | Export | BD017105 | 1 | 67925.33 | 74161.53 | 6236.2 | 1000 |  | 6236200 |  |  | OMF Corrected by Grid
|  |  | 10: Total |  | 6236200 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 4: 6248568.53; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6248568.53
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 6248568.53 | 33 KV TX HV SIDE |  | 6236200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 12368.53
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1979%
| TOTAL IMPORT |  | 4: 6248568.53
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD014058 | 1 | 12724.35 | 12724.35 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import | BD014062 | 1 | 66846.5 | 73040.4 | 6193.9 | 1000 | 6193900 |  | 6248568.53
|  |  | 7: 0; 8: 0; 10: Total | 6193900 | 0 | 6248568.53
| MONIPURIPARA 11 KV SIDE |  | 7: 0; 8: 0
1 | Spare |  | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | D572W | 11 |  | BD013947 | 1 | 34737.3 | 35145.8 | 408.5 | 1000 |  | 408500 | 414569.2893 | Shere b.nagar |  |  |  | Monipuripara west | 414569.2893 | 423673.0441 | -9103.7548 | -2.1488 | OK
3 | Biggan College | C672BC | 11 |  | BD013949 | 1 | 22925.68 | 23411.7 | 486.02 | 1000 |  | 486020 | 493241.0428 | Kakrail |  |  |  | Biggan College | 493241.0428 | 519020.9584 | -25779.9156 | -4.967 | OK
4 | Green Road South | D572G | 11 |  | BD013948 | 1 | 33271.48 | 33825.73 | 554.25 | 1000 |  | 554250 | 562484.7701 | Shere b.nagar |  |  |  | Green Road South | 562484.7701 | 541015.7704 | 21468.9998 | 3.9683 | OK
5 | BARC Building O/H | D572B | 11 |  | BD014010 | 1 | 14618.87 | 14620.53 | 1.66 | 1000 |  | 1660 | 1684.6635 | Shere b.nagar |  |  |  | BARC Building O/H | 1684.6635 | 1799.208 | -114.5445 | -6.3664 | OK
6 | Indira Road (Green Road North) | D572NN | 11 |  | BD014036 | 1 | 64945.32 | 65934.2 | 988.88 | 1000 |  | 988880 | 1003572.286 | Shere b.nagar |  |  |  | Indira Road (Green Road North) | 1003572.286 | 969055.4316 | 34516.8544 | 3.5619 | OK
7 | Chundrima Uddan | D572C | 11 |  | BD014035 | 1 | 33773.82 | 34549.23 | 775.41 | 1000 |  | 775410 | 786930.6551 | Shere b.nagar |  |  |  | Chundrima Uddan | 786930.6551 | 784555.7519 | 2374.9032 | 0.30271 | OK
8 | khamar bari RMU-1 Feeder |  | 11 |  | BD013940 | 1 | 1863.62 | 2084.35 | 220.73 | 1000 |  | 220730 | 224009.4963 | Shere b.nagar |  |  |  | khamar bari RMU-1 Feeder | 224009.4963 | 217360.4948 | 6649.0014 | 3.059 | OK
1 | Farmgate foot over bridge RMU |  | 11 |  | BD013946 | 1 | 635.81 | 825.3 | 189.49 | 1000 |  | 189490 | 192305.3479 | Tejgaon |  |  |  | Farmgate foot over bridge RMU | 192305.3479 | 180426.192 | 11879.1559 | 6.5839 | OK
2 | kawran Bazar North | C672K | 11 |  | BD013964 | 1 | 40777.26 | 40940.51 | 163.25 | 1000 |  | 163250 | 165675.4871 | Kakrail |  |  |  | kawran Bazar North | 165675.4871 | 135577.3957 | 30098.0914 | 22.1999 | OK
3 | NAM Bhanan RMU | D572NM | 11 |  | BD013950 | 1 | 20232.07 | 20852.88 | 620.81 | 1000 |  | 620810 | 630033.6854 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 630033.6854 | 638173.0005 | -8139.3151 | -1.2754 | OK
4 | Novo Theater |  | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | C172I | 11 |  | BD013962 | 1 | 40572.34 | 40789.94 | 217.6 | 1000 |  | 217600 | 220832.9923 | Tejgaon |  |  |  | Monipuripara Nearest | 220832.9923 | 241821.6368 | -20988.6445 | -8.6794 | OK
6 | Holy Cross | C172HC | 11 |  | BD013965 | 1 | 42526.73 | 43370.96 | 844.23 | 1000 |  | 844230 | 856773.1484 | Tejgaon |  |  |  | Holy Cross | 856773.1484 | 907680.2026 | -50907.0542 | -5.6085 | OK
7 | Honda Goli | C172HG | 11 |  | BD014011 | 1 | 18394.93 | 19009.47 | 614.54 | 1000 |  | 614540 | 623670.5289 | Tejgaon |  |  |  | Honda Goli | 623670.5289 | 595315.4624 | 28355.0665 | 4.763 | OK
8 | Navy Quarter | C172NQ | 11 |  | BD013941 | 1 | 6161.05 | 6178.85 | 17.8 | 1000 |  | 17800 | 18064.4635 | Tejgaon |  |  |  | Navy Quarter | 18064.4635 | 64488.4653 | -46424.0017 | -71.9881 | CHECK
9 | AT-01 |  | 0.415 |  |  | 1 | 2170.58 | 2170.58 | 0 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 739.45 | 790.83 | 51.38 | 1 |  | 51.38 | 52.1434 | Shere b.nagar |  |  |  | AT-02 | 52.1434 | 51.0955 | 1.0479 | 2.0509 | OK
|  |  | 10: Grand Total | 6193900 | 6103221.38 | 6193900 | 1.4858
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 3623336.9891
[6 empty] | Kakrail | at 33 KV level |  | 658916.5299
[6 empty] | Tejgaon | at 33 KV level |  | 1911646.481
[6 empty] | Total = |  |  | 6193900 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 |  | 33 | 0 | 0 | 1 | 1939.84 | 1946.2 | 6.36 | 180000 | From Ispahani Downsteam Estimated | 2305460 | 2309168.6088
12 | Ispahani-2 |  | 33 | 0 | 0 | 1 | 4016.4 | 4023.1 | 6.7 | 180000 | 0 | 1206000 | 1207939.9956
|  |  | 10: Total | 0 | 3511460 | 3517108.6043
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 |  | 33 | Import |  | 1 | 14753.89 | 17059.35 | 2305.46 | 1000 | 2305460
2 | Mogbazar Ckt-02 |  | 33 | Import |  | 1 | 54801.53 | 56006.68 | 1205.15 | 1000 | 1205150
|  |  | 7: 0; 8: 0; 10: Total | 3510610 | 0 | 0
| Ispahani 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| Ispahani 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export |  | 1 | 22048.66 | 24639.04 | 2590.38 | 888.8889 |  | 2302560.0288 |  | #DIV/0!
4 | Transformer-02 |  | 33 | Export |  | 1 | 55990.54 | 57345.49 | 1354.95 | 888.8889 |  | 1204400.0151
|  |  | 10: Total |  | 3506960.0438 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 4: 3517108.6043; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3517108.6043
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 3517108.6043 | 33 KV TX HV SIDE |  | 3506960.0438
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 10148.5605
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2885%
| TOTAL IMPORT |  | 4: 3517108.6043
11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import |  | 1 | 19231.91 | 21507.51 | 2275.6 | 1000 | 2275600 |  | 3007930.7955
2 | Transformer -02 Incoming |  | 11 | Import |  | 1 | 16249.91 | 16635.12 | 385.21 | 1000 | 385210 |  | 509177.8088 |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 2660810 | 3506960.0438 | 3517108.6043
| Ispahani 11 KV SIDE |  | 7: 0; 8: 0
1 | Doctor Goli | D1113D | 11 |  | BD013944 | 1 | 12159.11 | 12681.1 | 521.99 | 1000 |  | 521990 | 525464.8941 | Moghbazar |  |  |  | Doctor Goli | 525464.8941 | 435413.5519 | 90051.3422 | 20.6818 | OK
2 | Ispahani | D1113S | 11 |  | BD013947 | 1 | 13686.54 | 14257.9 | 571.36 | 1000 |  | 571360 | 575163.5509 | Moghbazar |  |  |  | Ispahani | 575163.5509 | 543652.9443 | 31510.6066 | 5.7961 | OK
3 | BTCL | C6113BT | 11 |  | BD013949 | 1 | 7657.92 | 8169.35 | 511.43 | 1000 |  | 511430 | 514834.5961 | Kakrail |  |  |  | BTCL | 514834.5961 | 516585.3241 | -1750.728 | -0.3389 | OK
4 | Vikarunnesa | C6113VQ | 11 |  | BD013948 | 1 | 10452.53 | 11019.56 | 567.03 | 1000 |  | 567030 | 570804.726 | Kakrail |  |  |  | Vikarunnesa | 570804.726 | 577218.0369 | -6413.3109 | -1.1111 | OK
5 | OASIS |  | 11 |  |  | 1 | 681.71 | 813.16 | 131.45 | 1000 |  | 131450 | 132325.0643 | Kakrail |  |  |  | OASIS | 132325.0643 | 139783.74 | -7458.6756 | -5.3359 | OK
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | D1113W | 11 |  |  | 1 | 12016.06 | 12585.13 | 569.07 | 1000 |  | 569070 | 572858.3063 | Moghbazar |  |  |  | Wireless | 572858.3063 | 608347.8726 | -35489.5663 | -5.8338 | OK
2 | Kazir Goli | C6113KG | 11 |  |  | 1 | 11748.83 | 12370.35 | 621.52 | 1000 |  | 621520 | 625657.4666 | Kakrail |  |  |  | Kazir Goli | 625657.4666 | 644368.9476 | -18711.481 | -2.9038 | OK
3 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3517108.6043 | 3493850 | 3517108.6043 | 0.6657
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 1673486.7513
[6 empty] | Kakrail | at 33 KV level |  | 1843621.853
[6 empty] | Total = |  |  | 3517108.6043 | 0
Note on K1232: User: Grid OMF = 1000
Note on K1233: User: Grid OMF = 1000

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 |  | 132 | IMPORT | 8993683 | 1 | 17.711 | 45.0887 | 27.3777 | 960000 | 0 | 26282582.4
| XFR- T2 |  | 132 |  | 8993682 | 1 | 11.007 | 38.1403 | 27.1333 | 960000 | 0 | 26047996.8
|  |  | 10: Total | 0 | 52330579.2
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** |  | 132 | P. Cell | 08993685 | 1 | 8517.554 | 8517.554 | 0 | 960000 | 0
| 132/33 kV Transformer-2(HV) ** |  | 132 | P. Cell | 08993684 | 1 | 8512.503 | 8512.503 | 0 | 960000 | 0
|  |  | 10: Total | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 4: 52330579.2; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 52330579.2
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 52330579.2 | 33 KV NET IMPORT |  | 53048640
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 52330579.2 | LOSS UNITS=>(132 HV-33 LV) |  | -718060.8
| IMPORT-4 |  | 6: Loss Units=> (132 IMP-132 EXP); 9=8-7: 0 | LOSS % IN => |  | -1.372%
| 132 KV TOTAL IMPORT |  | 4: 52330579.2; 6: 132 KV NET LOSS =>; 9=8-7: 0%
| 33 KV GT INCOMING-NOCS |  | 4: 53048640
| Loss Units=> (132 IMP-33 IMP) |  | 4: -718060.8
| LOSS % IN => |  | 4: -1.372%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | 4: IMPORT
3 | 132/33 kV Transformer, T-1 (LV) |  | 33 | PGCB | J2002016494 | 1 | 23181.186 | 23363.356 | 182.17 | 144000 | 26232480
4 | 132/33 kV Transformer, T-2 (LV) |  | 33 | PGCB | J2002016859 | 1 | 33146.601 | 33327.253 | 180.652 | 144000 | 26013888
| DPDC |  | 7: 0; 8: 0; 10: Total | 52246368
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | DPDC | 07389553 | 1 | 2000.74 | 2056.14 | 55.4 | 480000 | 26592000
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | DPDC | 07389485 | 1.038 | 1359.89 | 1411.99 | 52.1 | 480000 | 25958304
| P.Cell |  | 7: 0; 8: 0; 10: Total | 52550304
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | P.Cell | 08993674 | 1 | 11265.707 | 11321.15 | 55.443 | 480000 | 26612640
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | P.Cell | 8993667 | 1 | 11172.135 | 11227.21 | 55.075 | 480000 | 26436000
|  |  | 7: 0; 8: 0; 10: Total | 53048640
| SIDDHIRGANJ 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) |  | 33 | DPDC | 07389555 | 1 | 6113.363 | 6113.363 | 0 | 240000 | Estimated | 2644440 | 2646708.5412 |  | 8498123.8938 | Siddhirganj 33/11 kv ss | 0.73895 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 2646708.5412 | 2639437.6539 | 7270.8872 | 0.27547 | OK
|  |  | 33 | P.Cell | 08993675 | 1 | 5022.34 | 5022.34 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) |  | 33 | DPDC | 07389487 | 1 | 5972.18 | 5996.54 | 24.36 | 240000 |  | 5846400 | 5851415.3526 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 5851415.3526 | 5559327.4613 | 292087.8913 | 5.254 | OK
|  |  | 33 | P.Cell | 08993666 | 1 | 5236.416 | 5260.8 | 24.384 | 240000 |  | 5852160 | 5857180.2939 |  |  |  |  | 0 | 5857180.2939 | 5557402.9862 | 299777.3077 | 5.3942 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8490840 | 8498123.8938 |  |  |  |  | 33 KV Feeders | 8498123.8938 | 8198765.1152 | 299358.7786 | 3.6513 | OK
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4455.09 | 4485.24 | 30.15 | 240000 |  | 7236000 | 7242207.4254 |  | 12908664.2467 | Sarulia 33/11 kv ss | 2.1679 | 33 kV Sarulia-1 Feeder | 7242207.4254 | 6480188.7993 | 762018.626 | 11.7592 | OK
|  |  | 33 | P.Cell | 08993679 | 1 | 4455.873 | 4486.68 | 30.807 | 240000 |  | 7393680 | 7400022.6916 |  |  |  |  | 0 | 7400022.6916 | 6478504.8836 | 921517.808 | 14.2242 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) |  | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss | 1.1458 | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6353.14 | 6385.5 | 32.36 | 240000 |  | 7766400 | 7773062.4307 |  |  |  |  | 33 kV Demra-1 Feeder | 7773062.4307 | 7180697.7378 | 592364.6929 | 8.2494 | OK
|  |  | 33 | P.Cell | 08993676 | 1 | 5998.691 | 6031.1 | 32.409 | 240000 |  | 7778160 | 7784832.519 |  |  |  |  | 0 | 7784832.519 | 7180697.7378 | 604134.7813 | 8.4133 | OK
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5934.68 | 5974.4 | 39.72 | 240000 |  | 9532800 | 9540977.7425 |  | 17314040.1731 | Demra 33/11 kv ss | 0.10112 | 33 kV Demra-2 Feeder | 9540977.7425 | 9345732.2316 | 195245.5109 | 2.0891 | OK
|  |  | 33 | P.Cell | 08993665 | 1 | 5642.828 | 5682.61 | 39.782 | 240000 |  | 9547680 | 9555870.5073 |  |  |  |  | 0 | 9555870.5073 | 9342845.5189 | 213024.9884 | 2.2801 | OK
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder |  | 33 | DPDC | 7389486 | 1 | 4671.22 | 4695.7 | 24.48 | 240000 |  | 5875200 | 5880240.0588 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 5880240.0588 | 7137397.0479 | -1257156.9891 | -17.6137 | OK
|  |  | 33 | P.Cell | 08993678 | 1 | 3916.852 | 3941.385 | 24.533 | 240000 |  | 5887920 | 5892970.9707 |  |  |  |  | 0 | 5892970.9707 | 7134510.3352 | -1241539.3645 | -17.4019 | OK
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4140.36 | 4163.95 | 23.59 | 240000 |  | 5661600 | 5666456.8214 |  |  |  |  | 33 kV Sarulia-2 Feeder | 5666456.8214 | 5388530.2957 | 277926.5257 | 5.1577 | OK
|  |  | 33 | P.Cell | 08993663 | 1 | 3862.157 | 3885.8 | 23.643 | 240000 |  | 5674320 | 5679187.7333 |  |  |  |  | 0 | 5679187.7333 | 5386365.2612 | 292822.4721 | 5.4364 | OK
17 | 33 kV Adamjee EPZ Feeder |  | 33 | DPDC | ABB03919 | 1 | 387654.7 | 391490 | 3835.3 | 2000 |  | 7670600 | 7677180.2483 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 7677180.2483 | 7245648.7726 | 431531.4758 | 5.9557 | OK
|  |  | 10: Total | 52278248.6208 | 52233440 | 52278248.6208 | 0.085785
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 13557420.3071
[6 empty] | Total = |  |  | 13557420.3071 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | 4: IMPORT
8 | 33/11 kV Transformer-1 Incoming |  | 11 | New | XA587379 | 1 | 709821.8 | 712025.5 | 2203.7 | 1000 | 2644440 |  | 2683784.7254 |  | 1 Phase PT Out
9 | 33/11 kV Transformer-2 Incoming |  | 11 | New | DHKA9985 | 1 | 347314 | 353043.1 | 5729.1 | 1000 | 5729100 |  | 5814339.1684
|  |  | 7: 0; 8: 0; 10: Total | 8373540 |  | 8498123.8938
| SIDDHIRGANJ 11 kV SIDE |  | 4: EXPORT; 7: 0; 8: 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1.25 | 224037.5 | 225005.7 | 968.2 | 1000 |  | 1210250 | 1219193.0905 | Siddirgonj | 1 Phase PT Out |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 1219193.0905 | 1215735.951 | 3457.1395 | 0.28437 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1.25 | 17446.2 | 17495.1 | 48.9 | 1000 |  | 61125 | 61576.6806 | Siddirgonj | 1 Phase PT Out |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 61576.6806 | 67304.8091 | -5728.1285 | -8.5107 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1.25 | 115144.6 | 115785.2 | 640.6 | 1000 |  | 800750 | 806667.1078 | Siddirgonj | 1 Phase PT Out |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 806667.1078 | 803819.5531 | 2847.5547 | 0.35425 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1.25 | 181090.3 | 181522.8 | 432.5 | 1000 |  | 540625 | 544619.9253 | Siddirgonj | 1 Phase PT Out |  |  | 11 kV Ekata Steel Feeder (F-4) | 544619.9253 | 553654.0203 | -9034.0951 | -1.6317 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1.25 | 7471.9 | 7568.5 | 96.6 | 1000 |  | 120750 | 121642.2769 | Siddirgonj | 1 Phase PT Out |  |  | 11 kV Silo+Titas Feeder (F-5) | 121642.2769 | 99380.8281 | 22261.4488 | 22.4001 | OK
10 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 81835.9 | 82723.7 | 887.8 | 1000 |  | 887800 | 894360.36 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 894360.36 | 921540.4781 | -27180.118 | -2.9494 | OK
11 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) |  | 11 | T2 |  | 1 | 38.3337 | 58.7932 | 20.4595 | 40000 |  | 818380 | 824427.3839 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 824427.3839 | 514361.3002 | 310066.0837 | 60.2818 | FAULT
13 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 157475.6 | 158147.5 | 671.9 | 1000 |  | 671900 | 676864.9762 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 676864.9762 | 856227.3172 | -179362.341 | -20.948 | OK
14 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 121.6911 | 126.4018 | 4.7107 | 40000 |  | 188428 | 189820.3806 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 189820.3806 | 184300.0323 | 5520.3484 | 2.9953 | OK
15 | 11 kV Madrasha Road Feeder (F-11) |  | 11 | T2 | XA575919 | 1 | 53.16 | 186.67 | 133.51 | 8000 |  | 1068080 | 1075972.5314 | Siddirgonj | New meter |  |  | 11 kV Madrasha Road Feeder (F-11) | 1075972.5314 | 1043305.1747 | 32667.3567 | 3.1311 | OK
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 17778.3 | 18205.9 | 427.6 | 1000 |  | 427600 | 430759.7319 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 430759.7319 | 428567.2222 | 2192.5096 | 0.51159 | OK
17 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129896 | 129896 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 160068.2 | 161708.3 | 1640.1 | 1000 |  | 1640100 | 1652219.4486 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 1652219.4486 | 1510568.4289 | 141651.0198 | 9.3773 | OK
|  |  | 10: Total | 8498123.8938 | 8435788 | 8498123.8938 | 0.73895
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 8308303.5132
[6 empty] | Matuail | at 33 KV level |  | 189820.3806
[6 empty] | Total = |  |  | 8498123.8938 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6353.14 | 6385.5 | 32.36 | 240000 | 0 | 7766400 | 7773062.4307
0 | 0 |  | 33 | P.Cell | 08993676 | 1 | 5998.691 | 6031.1 | 32.409 | 240000 | 0 | 7778160 | 7784832.519
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5934.68 | 5974.4 | 39.72 | 240000 | 0 | 9532800 | 9540977.7425
0 | 0 |  | 33 | P.Cell | 08993665 | 1 | 5642.828 | 5682.61 | 39.782 | 240000 | 0 | 9547680 | 9555870.5073
|  |  | 10: Total | 0 | 17299200 | 17314040.1731
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 |  | 33 | Digital | DHK60885 | 3 | 458470.7 | 475234.5 | 16763.8 | 240 | 12069936
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) |  | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
|  |  | 7: 0; 8: 0; 10: Total | 12069936 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
10 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1027.67 | 1030.1 | 2.43 | 240000 |  | 583200 |  | Siddirgonj
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 583200
[7 empty] | 0 | 0
| DEMRA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60886 | 1 | 965836 | 995340.3 | 29504.3 | 240 |  | 7081032
8 | 33/11 kV, 10/14 MVA T-2 (HV) |  | 33 | Digital | 05002303 | 1 | 77.8 | 86.27 | 8.47 | 240000 |  | 2032800
9 | 33/11 kV, 20/28 MVA T-3 (HV) |  | 33 |  |  | 1 | 0 | 0 | 0 | 180 |  | 6928308
|  |  | 10: Total |  | 16042140 | 0
[6 empty] | 33 KV Export-Import |  |  | KWH
[6 empty] | Total Import |  |  | 17314040.1731
[6 empty] | Siddirgonj NOCS |  |  | 583200
[6 empty] | Net Import to Demra 33/11 KV SS |  |  | 16730840.1731
11 KV SIDE of___DEMRA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK60881 | 1 | 580317.6 | 619522.3 | 39204.7 | 180 | 7056846 |  | 7285007.7663
19 | 33/11 kV, 20/28 MVA T-3 Incoming. |  | 11 |  | DHK60925 | 1 | 971645.2 | 1010135.8 | 38490.6 | 180 | 6928308 |  | 7152313.879
| 33/11 kV, 10/14 MVA T-2 Incoming. |  | 11 |  |  | 1 | 22450.912 | 24672.599 | 2221.687 | 1000 | 2221687 |  | 2293518.5279
|  |  | 7: 0; 8: 0; 10: Total | 16206841 |  | 16730840.1731
| DEMRA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 |  | HA021101013-02 | 1 | 62386752 | 64648696 | 2261944 | 1 |  | 2261944 | 2264231.3054 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2264231.3054 | 2391584.9101 | -127353.6047 | -5.3251 | OK
12 | 11 kV DND (WASA) Feeder. | A816B | 11 |  | HA021100992-02 | 1 | 6463180 | 6468980 | 5800 | 1 |  | 5800 | 5805.865 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 5805.865 | 5456.4588 | 349.4062 | 6.4035 | OK
13 | 11 kV Local Feeder | A816D | 11 |  | HA021100794-02 | 1 | 15617269 | 16325156 | 707887 | 1 |  | 707887 | 708602.824 | Siddirgonj |  |  |  | 11 kV Local Feeder | 708602.824 | 672645.2076 | 35957.6164 | 5.3457 | OK
14 | 11 kV Mouchak Feeder | A816A | 11 |  | DHK60888 | 1 | 1107709.6 | 1137462.4 | 29752.8 | 60 |  | 1785168 | 1786973.1837 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 1786973.1837 | 1810495.0763 | -23521.8926 | -1.2992 | OK
15 | 11 kV Overhead-1 Feeder | A816C | 11 |  | HA021100829-02 | 1 | 80732532 | 81294895 | 562363 | 1 |  | 562363 | 562931.6683 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 562931.6683 | 389543.1007 | 173388.5676 | 44.5108 | FAULT
16 | 11 kV Provati Steel Feeder | A816Z | 11 |  | DHK60874 | 1 | 620995.2 | 624065.6 | 3070.4 | 60 |  | 184224 | 184410.2896 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 184410.2896 | 340543.0996 | -156132.81 | -45.8482 | CHECK
17 | 11 kV Islambagh Feeder. | E116I | 11 |  | DHKA2190 | 1 | 1267.4897 | 1293.659 | 26.1693 | 60000 |  | 1570158 | 1571745.7629 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 1571745.7629 | 1648945.851 | -77200.0881 | -4.6818 | OK
20 | 11 kV Taj Jute Feeder. | A816E | 11 |  | DHK61062 | 1 | 743003.7 | 763156.5 | 20152.8 | 60 |  | 1209168 | 1210390.7255 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1210390.7255 | 1220218.3679 | -9827.6425 | -0.8054 | OK
21 | 11 kV Al-Aksa Steel Feeder | A816S | 11 |  | DHK61061 | 1 | 938855.7 | 967430.2 | 28574.5 | 60 |  | 1714470 | 1716203.693 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1716203.693 | 1932793.8409 | -216590.1478 | -11.2061 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 |  | DHKA2189 | 1 | 1208.0447 | 1238.7475 | 30.7028 | 60000 |  | 1842168 | 1844030.8228 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 1844030.8228 | 1631573.2872 | 212457.5356 | 13.0216 | OK
23 | 11 kV Over Head Feeder-2. | E116V | 11 |  | HA021100488-02 | 1 | 37716071 | 38981989 | 1265918 | 1 |  | 1265918 | 1267198.1117 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 1267198.1117 | 1259081.3699 | 8116.7418 | 0.64466 | OK
24 | 11 kV Shimrail Express Feeder. | A8164 | 11 |  | HA021100511-02 | 1 | 8257879 | 8260815 | 2936 | 1 |  | 2936 | 2938.9689 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 2938.9689 | 1751.0727 | 1187.8962 | 67.8382 | FAULT
25 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 |  | HA021100413-02 | 1 | 82841955 | 83053097 | 211142 | 1 |  | 211142 | 211355.5094 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 211355.5094 | 155799.4192 | 55556.0902 | 35.6587 | OK
26 | 11 kV Siddhirgonj Mazar Feeder |  | 11 |  | HA021100393-02 | 1 | 28334.251 | 29040.997 | 706.746 | 1000 |  | 706746 | 707460.6702 | Siddirgonj |  |  |  | 11 kV Siddhirgonj Mazar Feeder | 707460.6702 | 701621.5068 | 5839.1634 | 0.83224 | OK
27 | 11 kV AST Beverage Feeder | A816J | 11 |  |  | 1 | 23850034 | 24496315 | 646281 | 1 |  | 646281 | 646934.5272 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 646934.5272 | 263535.9465 | 383398.5807 | 145.4825 | FAULT
28 | 11 kV Karim Market Feeder | E216K | 11 |  |  | 1 | 67122.502 | 68636.598 | 1514.096 | 1000 |  | 1514096 | 1515627.0724 | Matuail |  |  |  | 11 kV Karim Market Feeder | 1515627.0724 | 1401951.4847 | 113675.5876 | 8.1084 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 |  | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 16206841 | 16190469 | 16206841 | 0.10112
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 5351604.1407
[6 empty] | Demra | at 33 KV level |  | 1478553.6211
[6 empty] | Siddirgonj | at 33 KV level |  | 9376683.2382
[6 empty] | Total = |  |  | 16206841 | 0
33 KV SIDE of___ SARULIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4455.09 | 4485.24 | 30.15 | 240000 | 0 | 7236000 | 7242207.4254
0 | 0 |  | 33 | P.Cell | 08993679 | 1 | 4455.873 | 4486.68 | 30.807 | 240000 | 0 | 7393680 | 7400022.6916
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4140.36 | 4163.95 | 23.59 | 240000 | 0 | 5661600 | 5666456.8214
| 0 |  | 33 | P.Cell | 08993663 | 1 | 3862.157 | 3885.8 | 23.643 | 240000 | 0 | 5674320 | 5679187.7333
|  |  | 10: Total | 0 | 12897600 | 12908664.2467
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) |  | 33 |  | 30799103 | 1 | 4514.52 | 4537.85 | 23.33 | 240000 | 5599200
7 | 33 kV Siddhirgonj-1 Incoming (=L41) |  | 33 |  | 30799100 | 1 | 4471.76 | 4501.03 | 29.27 | 240000 | 7024800
|  |  | 7: 0; 8: 0; 10: Total | 12624000 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SARULIA 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV Transformer-1 (=T31) |  | 33 |  | 30799099 | 1 | 4886.84 | 4917.18 | 30.34 | 180000 |  | 5461200
5 | 33/11 kV Transformer-2 (=T32) |  | 33 |  | 30799139 | 1 | 4160.95 | 4180.09 | 19.14 | 180000 |  | 3445200
6 | 33/11 kV Transformer-3 (=T33) |  | 33 |  | 30799102 | 1 | 1840.2 | 1840.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
|  |  | 10: Total |  | 8906400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 4: 12908664.2467; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 12908664.2467
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 12908664.2467 | 33 KV NET Receiving |  | 12624000
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 12908664.2467 | LOSS UNITS=> |  | 284664.2467
| IMPORT-4 |  | 6: 132KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 2.205%
| TOTAL IMPORT |  | 4: 12908664.2467
11 KV SIDE of___SARULIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) |  | 11 |  | 2007754972 | 1 | 9573.48 | 9607.76 | 34.28 | 160000 | 5484800 |  | 7931690.4531
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) |  | 11 |  | 30799500 | 1 | 9064.03 | 9107.05 | 43.02 | 80000 | 3441600 |  | 4976973.7936
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) |  | 11 |  | HA021100368-02 | 1 | 66196180 | 66196180 | 0 | 1 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 8926400 |  | 12908664.2467
| SARULIA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 |  | 2007755114 | 1 | 6034.84 | 6071.31 | 36.47 | 60000 |  | 2188200 | 2235638.4098 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 2235638.4098 | 2167253.8322 | 68384.5776 | 3.1554 | OK
9 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 |  | 30799484 | 1 | 22.8458 | 23.0952 | 0.2494 | 60000 |  | 14964 | 15288.4074 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 15288.4074 | 16496.2847 | -1207.8773 | -7.3221 | OK
11 | 11 kV Konapara (=L13) **** | E183KL | 11 |  | DHKA2191 | 1 | 2297.792 | 2325.0065 | 27.2145 | 60000 |  | 1632870 | 1668269.3036 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 1668269.3036 | 1627629.3973 | 40639.9063 | 2.4969 | OK
12 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 |  | 575926 | 1 | 63859.6 | 65468 | 1608.4 | 1000 |  | 1608400 | 1643268.8138 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 1643268.8138 | 1600042.8683 | 43225.9455 | 2.7015 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 |  | 30799450 | 1 | 1838.66 | 1843.4 | 4.74 | 60000 |  | 284400 | 290565.5624 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 290565.5624 | 267278.5139 | 23287.0485 | 8.7127 | OK
14 | 11 kV Tengra Feeder (=L16) | E183T | 11 |  | 30799145 | 1 | 5710.51 | 5742.63 | 32.12 | 60000 |  | 1927200 | 1968980.1404 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 1968980.1404 | 1872159.0024 | 96821.1381 | 5.1716 | OK
16 | 11 kV Police Line Feeder (=L17) | E183PL | 11 |  | 30799480 | 1 | 3424.38 | 3439.36 | 14.98 | 60000 |  | 898800 | 918285.2585 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 918285.2585 | 856863.471 | 61421.7875 | 7.1682 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 |  | 30799119 | 1 | 1681.12 | 1686.61 | 5.49 | 60000 |  | 329400 | 336541.1261 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 336541.1261 | 321701.7407 | 14839.3854 | 4.6128 | OK
18 | 11 kV Spare Feeder (=F9) |  | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 |  | HA021100493-02 | 1 | 95230968 | 97024827 | 1793859 | 1 |  | 1793859 | 1832748.4152 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 1832748.4152 | 1739187.9417 | 93560.4735 | 5.3795 | OK
21 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 |  | HA021100518-02 | 1 | 50895377 | 51370624 | 475247 | 1 |  | 475247 | 485549.9714 | Demra |  |  |  | 11 kV Baser Pool Feeder (=L11) | 485549.9714 | 0 | 485549.9714 | #DIV/0! | #DIV/0!
22 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 |  | HA021100697-02 | 1 | 33817648 | 35299061 | 1481413 | 1 |  | 1481413 | 1513528.8381 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 1513528.8381 | 1400106.0427 | 113422.7954 | 8.101 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) |  | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) |  | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 12908664.2467 | 12634753 | 12908664.2467 | 2.1679
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Demra | at 33 KV level |  | 11265395.433
[6 empty] | Matuail | at 33 KV level |  | 1643268.8138
[6 empty] | Total = |  |  | 12908664.2467 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 57679.762 | 63139.348 | 5459.586 | 1000 | 0 | 5459586 | 5460563.2295
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 579.5569 | 600.7891 | 21.2322 | 240000 | 0 | 5095728 | 5096640.1013
| Siddhirganj 33 KV SIDE |  | 10: Total |  | 10555314 | 10557203.3308
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) |  | 33 |  | 84663042 | 1 | 587.04 | 608.26 | 21.22 | 240000 | 5092800
6 | 33 kV Shitalakhya-2 Feeder (Old) |  | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 5459586 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 |  | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 |  | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 10552386 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
11 | 33 kV ACI Pharmacuticles Feeder |  | 33 |  | DHKC4791 | 1 | 981.97 | 990.46 | 8.49 | 90000 |  | 764100 |  | N.Gonj (East)
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 764100
[7 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  | 7: 0; 8: 0
9 | 33/11 kV, 20/28 MVA T1 Transformer |  | 33 |  | DHKC 9363 | 1 | 41916.98 | 51094.35 | 9177.37 | 240 |  | 2202568.8 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer |  | 33 |  | DHKC 9361 | 1 | 74429.67 | 86482.99 | 12053.32 | 240 |  | 2892796.8 |  |  | Meter Problem
|  |  | 10: Total |  | 9788286 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 10557203.3308; 6: EXPORT TO N.Gonj (East); 9=8-7: 764100 | 33 KV NET IMPORT |  | 9793103.3308
| SIDDIRGANJ 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 9793103.3308 | 33 KV TX HV SIDE |  | 9788286
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 4817.3308
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.04919%
| TOTAL IMPORT |  | 4: 10557203.3308
11 KV SIDE of___KHANPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. |  | 11 |  | DHKC 9313 | 1 | 43102096.6 | 45587674.52 | 2485577.92 | 1 | 2485577.92 |  | 3207906.199
18 | 33/11 kV Transformer-2 Incoming. |  | 11 |  | DHKC 9346 | 1 | 62301074.12 | 62301074.12 | 0 | 1 | 0 |  | 0
24 | 33/11 kV 20/28 MVA T4 Incoming |  | 11 |  | 06604325 | 1 | 224.27 | 236.35 | 12.08 | 240000 | 2899200 |  | 3741730.073
30 | 33/11 kV 20/28 MVA T1 Incoming |  | 11 |  | 06604374 | 1 | 134.8 | 143.98 | 9.18 | 240000 | 2203200 |  | 2843467.0588
|  |  | 7: 0; 8: 0; 10: Total | 7587977.92 |  | 9793103.3308
| KHANPUR 11 KV SIDE |  | 7: 0; 8: 0
12 | 11 kV Khanpur Feeder | B723B | 11 |  | DHKC 9348 | 1 | 86923.13 | 103601.58 | 16678.45 | 60 |  | 1000707 | 1012173.2768 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1012173.2768 | 918289.8994 | 93883.3774 | 10.2237 | OK
13 | 11 kV Mission Para Feeder. | B723T | 11 |  | DHKC 9347 | 1 | 65601.86 | 79593.68 | 13991.82 | 60 |  | 839509.2 | 849128.444 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 849128.444 | 935490.5604 | -86362.1164 | -9.2317 | OK
14 | 11 kV Esha Kha Feeder | B723M | 11 |  | DHKC 9311 | 1 | 66957.6 | 77627.6 | 10670 | 60 |  | 640200 | 647535.5242 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 647535.5242 | 713273.6195 | -65738.0953 | -9.2164 | OK
15 | 11 kV New Hazigonj Feeder | B723F | 11 |  | DHKC 9314 | 1 | 345.95 | 367.79 | 21.84 | 60000 |  | 1310400 | 1325414.7936 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 1325414.7936 | 1294152.4735 | 31262.3201 | 2.4157 | OK
16 | 11 kV Spare Feeder. |  | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | B723H | 11 |  | 6604412 | 1 | 9.86 | 10.41 | 0.55 | 60000 |  | 33000 | 33378.1198 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 33378.1198 | 30279.6554 | 3098.4644 | 10.2328 | OK
20 | 11 kV Old Hajiganj Feeder. | B723E | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 |  | 06604389 | 1 | 10821.98 | 23295.95 | 12473.97 | 60 |  | 748438.2 | 757013.9365 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 757013.9365 | 746540.6657 | 10473.2708 | 1.4029 | OK
22 | 11 kV Spare Feeder. |  | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming |  | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | A723A | 11 |  | 6604415 | 1 | 467.5 | 495.02 | 27.52 | 40000 |  | 1100800 | 1113413.16 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1113413.16 | 1010129.3055 | 103283.8545 | 10.2248 | OK
26 | 11 kV Mondalpara Feeder. |  | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | B723C | 11 |  | 06604392 | 1 | 367.96 | 389.72 | 21.76 | 40000 |  | 870400 | 880373.1963 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 880373.1963 | 834911.0327 | 45462.1636 | 5.4452 | OK
28 | 11 kV Bishaw Road Feeder. | B723A | 11 |  | 06604393 | 1 | 366.72 | 383.73 | 17.01 | 40000 |  | 680400 | 688196.1428 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 688196.1428 | 670593.4358 | 17602.707 | 2.6249 | OK
29 | 11 kV Chasara Feeder. | A723B | 11 |  | 06604391 | 1 | 507.05 | 535.07 | 28.02 | 40000 |  | 1120800 | 1133642.3235 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 1133642.3235 | 1109850.3041 | 23792.0194 | 2.1437 | OK
31 | 11 kV Pathan Tully Feeder. | B723G | 11 |  | 06604388 | 1 | 96.85 | 105.87 | 9.02 | 40000 |  | 360800 | 364934.1098 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 364934.1098 | 358511.1204 | 6422.9894 | 1.7916 | OK
32 | 11 kV Spare Feeder. |  | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | B722J | 11 |  | 6604289 | 1 | 340.54 | 364.95 | 24.41 | 40000 |  | 976400 | 987587.7629 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 987587.7629 | 913638.1368 | 73949.6261 | 8.094 | OK
34 | 11 kV Spare Feeder. |  | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. |  | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. |  | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 |  | 0.415 |  | 412109 | 1 | 9309.8 | 9315.4 | 5.6 | 10 |  | 56 | 56.6417 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 56.6417 | 364.3652 | -307.7235 | -84.4547 | CHECK
38 | 33/0.415 kV Auxiliary Transformer-2 |  | 0.415 |  | 243285 | 1 | 6441.8 | 6467.1 | 25.3 | 10 |  | 253 | 255.8989 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 255.8989 | 86.8017 | 169.0972 | 194.8087 | FAULT
|  |  | 10: Grand Total | 9793103.3308 | 9682163.4 | 9793103.3308 | 1.1458
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (West) | at 33 KV level |  | 2247055.4835
[6 empty] | N.Gonj (East) | at 33 KV level |  | 7546047.8473
[6 empty] | Total = |  |  | 9793103.3308 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail |  | 132 | Impt | 8993555 | 1 | 19.763 | 41.6618 | 21.8988 | 1440000 | 0 | 31534286.4
|  |  | 132 | Expt |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar |  | 3: 132; 4: Impt; 6: 1; 9=8-7: 0 | 0 | 0
|  |  | 3: 132; 4: Expt; 6: 1; 9=8-7: 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 31534286.4
|  |  | 10: Net Total | 31534286.4
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder |  | 132 | Impt |  | 1 | 0 | 0 | 0 | 1 | 0
|  |  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  |  | 132 | Expt |  | 1 | 9004435 | 9004435 | 0 | 1 | 0
|  |  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder |  | 132 | Impt | HA040700237-03 | 1 | 60708902 | 60708902 | 0 | 1
|  |  | 132 |  | 06604364 | 1 | 6116.85 | 6120.84 | 3.99 | 960000 | 3830400
|  |  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
|  |  | 8: 0; 9=8-7: Total Import/Export | 3830400 | 0
|  |  | 8: 0; 9=8-7: Net Total | 3830400
| Matuail 132 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| Matuail 132 KV SIDE |  | 8: 0
4 | 132/33 KV Transformer, GT-1 |  | 132 | DPDC | H/A040700240-03 | 1 | 52838.225 | 68553.704 | 15715.479 | 1000 |  | 15715479
|  |  | 132 | P. Cell | 08993572 | 1 | 5051.982 | 5051.982 | 0 | 480000 |  | 0
5 | 132/33 KV Transformer, GT-2 |  | 132 | DPDC | H/A030700918-03 | 1 | 113799.201 | 113799.201 | 0 | 1000 |  | 0
|  |  | 132 | P. Cell | 08993577 | 1 | 5250.604 | 5283.433 | 32.829 | 480000 |  | 15757920
|  |  | 10: Total |  | 15715479
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 4: 31534286.4; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 31534286.4
| 132 KV Sending From Maniknagar |  | 4: 0; 6: 132 KV NET IMPORT; 9=8-7: 31534286.4 | 132/33 KV GT LV Side |  | 31518229
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 16057.4
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.05092%
| 132 KV TOTAL IMPORT |  | 4: 31534286.4
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | 4: IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 45030.509 | 60822.522 | 15792.013 | 1000 | 15792013
|  |  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 65154.134 | 80880.35 | 15726.216 | 1000 | 15726216
|  |  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 31518229 |  | 0
| MATUAIL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 |  | 33 | DPDC | H/A060300287-03 | 1.45 | 98752.817 | 104263.463 | 5510.646 | 1000 | From Downstream | 7990436.7 | 8015185.3751 |  | 12843112.6789 | Matuail 33/11 kv ss | 0.62521 | 33/11 KV Transformer, T-3 | 8015185.3751 | 7958622.25 | 56563.1251 | 0.71072 | OK
|  |  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 |  | 33 | DPDC | H/A060300190-03 | 1 | 97785.586 | 102633.071 | 4847.485 | 1000 |  | 4847485 | 4862499.0519 |  |  |  |  | 33/11 KV Transformer, T-4 | 4862499.0519 | 5369695 | -507195.9481 | -9.4455 | OK
|  |  | 33 | P. Cell | 08993581 | 1 | 6447.226 | 6473.965 | 26.739 | 180000 |  | 4813020 | 4827927.3039 |  |  |  |  | 0 | 4827927.3039 | 5390640 | -562712.6961 | -10.4387 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 12837921.7 | 12843112.6789 |  |  |  |  | 33 KV Feeders | 12843112.6789 | 13349262.25 | -506149.5711 | -3.7916 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 8535360 | 14105280 | 5569920 | 1 |  | 5569920 | 5587171.6403 |  | 12919973.3033 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 5587171.6403 | 5618880 | -31708.3597 | -0.56432 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.264 | 0.004 | 1000 |  | 6 | 6.0186 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 6.0186 | 0 | 6.0186 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC |  | 1 | 39.34 | 40.81 | 1.47 | 6000 | From Customer End | 8820 | 8847.3181 | Matuail | Customer Number 35568341 | From AMR Reading |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 8847.3181 | 13860 | -5012.6819 | -36.1665 | OK
|  |  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 | 13860 | 0 | 0 |  | 6.0186 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 44.915 | 5644.734 | 5599.819 | 1000 |  | 5599819 | 5617163.2461 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 5617163.2461 | 5603560 | 13603.2461 | 0.24276 | OK
|  |  | 33 | P. Cell | 08993580 | 1.5 | 1478.712 | 1499.424 | 20.712 | 180000 |  | 5592240 | 5609560.7718 |  |  |  |  | 0 | 5609560.7718 | 5596290 | 13270.7718 | 0.23714 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 5617163.2461 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 | DPDC | 00000154 | 1 | 1494640 | 8804800 | 7310160 | 1 | From Downstream | 7310160 | 7332801.6629 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 7332801.6629 | 6724560 | 608241.6629 | 9.0451 | OK
|  |  | 10: Total |  | 18488725 | 18545989.8861 |  |  |  |  | 0 | 18545989.8861 | 17960860 | 585129.8861 | 3.2578 | OK
|  |  | 9=8-7: Grand Total | 31423674.313 | 31326646.7 | 31389102.565 | 0.19937
[6 empty] | 33 KV EXPORT |  |  | KWH
[6 empty] | EXPORT TO Matuail |  |  | 8847.3181
[6 empty] | Total Export |  |  | 8847.3181 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426631 | 1 | 8117776 | 8208373 | 90597 | 90 | 8153730 |  | 8235871.6812
11 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | 51426633 | 1 | 7686250 | 7736931 | 50681 | 90 | 4561290 |  | 4607240.9978
|  |  | 7: 0; 8: 0; 10: Total | 12715020 |  | 12843112.6789
| MATUAIL 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Link Road Feeder | B741N | 11 | Backup | DHK66629 | 1 | 25282.82 | 25735.24 | 452.42 | 8000 |  | 3619360 | 3641988.6452 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 3641988.6452 | 0 | 3641988.6452 | #DIV/0! | #DIV/0!
|  |  | 11 |  | HA021100475-02 | 1 | 3617.14 | 5393.63 | 1776.49 | 1000 |  | 1776490 | 1787596.815 | N.Gonj (East) |  |  |  | 0 | 1787596.815 | 1834777.3994 | -47180.5844 | -2.5715 | OK
4 | 11 kV Lamapara Express Feeder | B723L | 11 |  | HA021100928-03 | 1 | 83442.772 | 84501.883 | 1059.111 | 1000 |  | 1059111 | 1065732.6809 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1065732.6809 | 1202097.8234 | -136365.1424 | -11.3439 | OK
5 | 11 kV Kutubpur Feeder*** | B741Q | 11 |  | DHK66616 | 1 | 18785.32 | 18919.7 | 134.38 | 8000 |  | 1075040 | 1081761.2708 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1081761.2708 | 1059892.9128 | 21868.358 | 2.0633 | OK
|  |  | 11 | Backup | XA575929 | 1 | 49188.4 | 50263.7 | 1075.3 | 1000 |  | 1075300 | 1082022.8964 | N.Gonj (East) |  |  |  | 0 | 1082022.8964 | 1060013.4374 | 22009.459 | 2.0763 | OK
6 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 |  | DHK66625 | 1 | 3631.91 | 3646.26 | 14.35 | 60000 | From Check Meter | 1093749 | 1100587.2416 | Fatullah | Reference Checked |  |  | 11 kV Ramarbagh Feeder (F1) | 1100587.2416 | 922012.825 | 178574.4166 | 19.3679 | OK
|  |  | 11 | Backup |  | 1 | 18708.405 | 19802.154 | 1093.749 | 1000 |  | 1093749 | 1100587.2416 | Fatullah |  |  |  | 0 | 1100587.2416 | 974106.5496 | 126480.692 | 12.9843 | OK
7 | 11 kV Tushardhara Feeder (F2) | E241T | 11 |  | DHK66623 | 1 | 4045.32 | 4080.1 | 34.78 | 60000 |  | 2086800 | 2099846.908 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2099846.908 | 2082664.2636 | 17182.6444 | 0.82503 | OK
8 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 |  | DHK66627 | 1 | 3369.81 | 3381.23 | 11.42 | 60000 |  | 685200 | 689483.9474 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 689483.9474 | 717723.7089 | -28239.7615 | -3.9346 | OK
|  |  | 11 | Backup |  | 1 | 81230.578 | 82074.24 | 843.662 | 1000 |  | 843662 | 848936.6696 | Matuail |  |  |  | 0 | 848936.6696 | 784727.325 | 64209.3446 | 8.1824 | OK
9 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 |  | HA021101044-02 | 1 | 67133.062 | 67308.119 | 175.057 | 1000 |  | 175057 | 176151.476 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 176151.476 | 179169.7907 | -3018.3147 | -1.6846 | OK
12 | 11 kV Shibu Market Feeder (F7) | B841B | 11 |  | DHK66624 | 1 | 2401.85 | 2405.22 | 3.37 | 60000 |  | 202200 | 203464.1771 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 203464.1771 | 183799.9422 | 19664.2349 | 10.6987 | OK
13 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 |  | HA060300286-03 | 1 | 8238.449 | 8238.449 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 0 | 601987.9988 | -601987.9988 | -100 | CHECK
14 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 |  | DHK66626 | 1 | 4603.97 | 4634.5 | 30.53 | 60000 |  | 1831800 | 1843252.6193 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 1843252.6193 | 1806060.4161 | 37192.2033 | 2.0593 | OK
15 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK6622 | 1 | 4311.94 | 4327.96 | 16.02 | 60000 |  | 961200 | 967209.5304 | Matuail |  |  |  | 0 | 967209.5304 | 969620.0232 | -2410.4928 | -0.2486 | OK
16 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 |  | DHKA2187 | 1 | 143.2655 | 148.8233 | 5.5578 | 60000 |  | 333468 | 335552.8794 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 335552.8794 | 346363.4584 | -10810.579 | -3.1212 | OK
17 | 11 kV Bhuighor Bazar |  | 11 |  | HA021100861-02 | 1 | 5007.34 | 5868.005 | 860.665 | 1000 |  | 860665 | 866045.9742 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 866045.9742 | 806459.9105 | 59586.0637 | 7.3886 | OK
18 | 11 kV Tokkar Math Feeder | B8416 | 11 |  | HA021200298-02 | 1 | 84494.857 | 85107.792 | 612.935 | 1000 |  | 612935 | 616767.1385 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 616767.1385 | 627491.9984 | -10724.86 | -1.7092 | OK
19 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 |  | XA575922 | 1 | 268.7 | 278.3 | 9.6 | 1000 |  | 9600 | 9660.0203 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 9660.0203 | 9139.7785 | 520.2417 | 5.6921 | OK
16 | 33/0.415 KV Transformer, AT-1 |  | 0.415 |  | 2001123043119 | 1 | 7750 | 7808 | 58 | 160 |  |  | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 KV Transformer, AT-2 |  | 0.415 |  | 2001123043157 | 1 | 4727.8 | 4727.8 | 0 | 160 |  | 0 | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 12843112.6789 | 12763315 | 12843112.6789 | 0.62521
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 3935090.7668
[6 empty] | Shyampur | at 33 KV level |  | 335552.8794
[6 empty] | Fatullah | at 33 KV level |  | 1930478.5774
[6 empty] | Matuail | at 33 KV level |  | 6641990.4553
[6 empty] | Total = |  |  | 12843112.6789 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 8535360 | 14105280 | 5569920 | 1 | 0 | 5569920 | 5587171.6403
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 |  | 00000154 | 1 | 1494640 | 8804800 | 7310160 | 1 | From Downstream | 7310160 | 7332801.6629
|  |  | 10: Total | 0 | 12880080 | 12919973.3033
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder |  | 33 |  | 00000079 | 1 | 378411200 | 385651520 | 7240320 | 1 | 7240320
7 | 33 kV Matuail-1 Feeder |  | 33 |  | 00000114 | 1 | 306407616 | 311933440 | 5525824 | 1 | 5525824
|  |  | 7: 0; 8: 0; 10: Total | 12766144 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000075 | 1 | 393137536 | 400380000 | 7242464 | 1 |  | 7242464
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000156 | 1 | 291759840 | 297285824 | 5525984 | 1 |  | 5525984
|  |  | 10: Total |  | 12768448
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 12919973.3033; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 12919973.3033
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 12919973.3033 | 33 KV TX HV Side |  | 12768448
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 151525.3033
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.173%
| TOTAL IMPORT |  | 4: 12919973.3033
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming |  | 11 |  | 00000144 | 1 | 391730976 | 398949792 | 7218816 | 1 | 7218816 |  | 7329630.5437
18 | 11 kV T-1 Incoming |  | 11 |  | 00000054 | 1 | 290052928 | 295558752 | 5505824 | 1 | 5505824 |  | 5590342.7596
|  |  | 7: 0; 8: 0; 10: Total | 12724640 |  | 12919973.3033
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Godnail (F16) | A8963 | 11 |  | 00000109 | 1 | 34819036 | 36125672 | 1306636 | 1 |  | 1306636 | 1325877.9256 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1325877.9256 | 1267100.9327 | 58776.9929 | 4.6387 | OK
2 | 11 kV M. Circus (F15) | B796C | 11 |  | 00000123 | 1 | 117011272 | 118224352 | 1213080 | 1 |  | 1213080 | 1230944.191 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1230944.191 | 1439707.0094 | -208762.8184 | -14.5004 | OK
3 | 11 kV Wapderpool (F14) | B723W | 11 |  | 00000190 | 1 | 61037372 | 61829048 | 791676 | 1 |  | 791676 | 803334.4655 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 803334.4655 | 807747.7986 | -4413.3332 | -0.54638 | OK
4 | 11 kV Chowdhury Bari (F13) | A896C | 11 |  | 00000191 | 1 | 111311768 | 113386280 | 2074512 | 1 |  | 2074512 | 2105061.9049 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2105061.9049 | 2122803.1132 | -17741.2083 | -0.83574 | OK
5 | 11 kV Ailpara (F12) | B7966 | 1 |  | 00000192 | 1 | 64386884 | 66223200 | 1836316 | 1 |  | 1836316 | 1863358.157 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 1863358.157 | 1617658.7416 | 245699.4154 | 15.1886 | OK
6 | 11 kV Spare (F11) |  | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) |  | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) |  | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) |  | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | A8962H | 11 |  | 00000197 | 1 | 22047826 | 23453782 | 1405956 | 1 |  | 1405956 | 1426660.5426 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1426660.5426 | 1166769.562 | 259890.9806 | 22.2744 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 |  | 00000198 | 1 | 4368189 | 4418549 | 50360 | 1 |  | 50360 | 51101.6169 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 51101.6169 | 64212.0772 | -13110.4603 | -20.4174 | OK
12 | 11 kV Lucky Bazar (F5) | B796Z | 11 |  | 00000199 | 1 | 96274088 | 97578320 | 1304232 | 1 |  | 1304232 | 1323438.5235 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1323438.5235 | 1347891.7655 | -24453.242 | -1.8142 | OK
13 | 11 kV Enayetnagar (F4) | A896Y | 11 |  | 00000200 | 1 | 39019104 | 40056704 | 1037600 | 1 |  | 1037600 | 1052880.0183 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1052880.0183 | 1078999.679 | -26119.6607 | -2.4207 | OK
14 | 11 kV Bhuiyapara (F3) | A896V | 11 |  | 00000201 | 1 | 72932584 | 73827656 | 895072 | 1 |  | 895072 | 908253.1069 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 908253.1069 | 1072141.0265 | -163887.9196 | -15.286 | OK
15 | 11 kV Arambagh (F2) | B796D | 11 |  | 00000202 | 1 | 13814126 | 14628804 | 814678 | 1 |  | 814678 | 826675.2 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 826675.2 | 841577.5302 | -14902.3302 | -1.7708 | OK
16 | 11 kV Spare (F1) |  | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 |  | 0.415 |  | 00000204 | 1 | 1830.36 | 1853.89 | 23.53 | 100 |  | 2353 | 2387.651 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 2387.651 | 2350.764 | 36.887 | 1.5691 | OK
18 | 11/0.415 kV Aux. Transformer-2 |  | 0.415 |  | 00000205 | 1 | 61.17 | 61.17 | 0 | 100 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 12919973.3033 | 12732471 | 12919973.3033 | 1.4726
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 6101239.805
[6 empty] | Siddirgonj | at 33 KV level |  | 6818733.4983
[6 empty] | Total = |  |  | 12919973.3033 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.264 | 0.004 | 1000 | 0 | 6 | 6.0186
0 | 0 |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side |  | 10: Total | 0 | 6 | 6.0186
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 828.66 | 851.49 | 22.83 | 360000 | 0 | 8218800 | 8214588.4704
0 | 0 |  | 33 | Backup | 041808904262 | 1 | 828.67 | 851.51 | 22.84 | 360000 | 0 | 8222400 | 8218186.6257
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 543.91 | 549.76 | 5.85 | 360000 | 0 | 2106000 | 2104920.8301
0 | 0 |  | 33 | Backup | 041808904258 | 1 | 544.11 | 549.97 | 5.86 | 360000 | 0 | 2109600 | 2108518.9854
|  |  | 10: Total | 0 | 10324800 | 10319509.3005
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) |  | 33 | Digital | DHK60875 | 1 | 444803.1 | 478923.3 | 34120.2 | 240 | 8188848
9 | 33 kV New Fatulla-2 |  | 33 | Digital | DHK2186 | 1 | 388.3421 | 394.2118 | 5.8697 | 360000 | 2113092
|  |  | 7: 0; 8: 0; 10: Total | 10301940 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  | 7: 0; 8: 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60980 | 1 | 65470.1 | 84979.2 | 19509.1 | 240 |  | 4682184
13 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 | Digital | DHK60952 | 1 | 576539.2 | 591105.2 | 14566 | 240 |  | 3495840 |  |  | Meter Problem
|  |  | 10: Total |  | 8178024 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 6.0186; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 10319515.3191
| New Fatullah 33 kv Side |  | 4: 10319509.3005; 6: 33 KV Net Import; 9=8-7: 10319515.3191 | 33 KV TX HV Side |  | 8178024
[11 empty] | LOSS UNITS=> |  | 2141491.3191
[11 empty] | LOSS % IN => |  | 20.75%
| TOTAL IMPORT |  | 4: 10319515.3191
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 | New | DHK61060 | 1 | 286472.1 | 311041.4 | 24569.3 | 180 | 4422474 |  | 4633906.5067 | [7 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 | New | DHK61054 | 1 | 487168.2 | 506573.2 | 19405 | 180 | 3492900 |  | 3659890.8297 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming |  | 11 | New | DHK60924 | 1.1 | 504269.3 | 509499.3 | 5230 | 180 | 1035540 |  | 1085047.7683 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming |  | 11 | New | DHK61051 | 1 | 58021.4 | 67996.4 | 9975 | 90 | 897750 |  | 940670.2145 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 9848664 |  | 10319515.3191 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | A717R | 11 | New |  | 1 | 79206654 | 79864949 | 658295 | 1 |  | 658295 | 658925.6265 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 658925.6265 | 544365.4981 | 114560.1284 | 21.0447 | OK
15 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 92516438 | 93349508 | 833070 | 1 |  | 833070 | 833868.0556 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 833868.0556 | 734193.3379 | 99674.7177 | 13.5761 | OK
16 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 253988.1 | 267690.1 | 13702 | 60 |  | 822120 | 822907.5658 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 822907.5658 | 751822.0823 | 71085.4835 | 9.4551 | OK
17 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 391310.2 | 401337.2 | 10027 | 60 |  | 601620 | 602196.3336 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 602196.3336 | 614880.4759 | -12684.1423 | -2.0629 | OK
19 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 135662.3 | 156105.3 | 20443 | 60 |  | 1226580 | 1227755.0262 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1227755.0262 | 1228977.05 | -1222.0239 | -0.099434 | OK
20 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 120216.4 | 129577.4 | 9361 | 60 |  | 561660 | 562198.0531 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 562198.0531 | 577554.6924 | -15356.6393 | -2.6589 | OK
23 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 699968.1 | 710675.1 | 10707 | 60 |  | 642420 | 643035.4187 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 643035.4187 | 681813.6257 | -38778.2069 | -5.6875 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 616583.2 | 635410.2 | 18827 | 60 |  | 1129620 | 1130702.1414 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1130702.1414 | 1213118.1146 | -82415.9731 | -6.7937 | OK
25 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 927864.3 | 956770.4 | 28906.1 | 60 |  | 1734366 | 1736027.4696 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 1736027.4696 | 1558577.5876 | 177449.8821 | 11.3854 | OK
26 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Dhaka Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 4060626 | 4501007 | 440381 | 1 |  | 440381 | 440802.8715 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 440802.8715 | 419238.6981 | 21564.1734 | 5.1437 | OK
28 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 26535184 | 26739064 | 203880 | 1 |  | 203880 | 204075.3108 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 204075.3108 | 181356.6758 | 22718.635 | 12.527 | OK
29 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 17345074 | 17738197 | 393123 | 1 |  | 393123 | 393499.5998 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 393499.5998 | 398817.0524 | -5317.4526 | -1.3333 | OK
30 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 19199164 | 19678202 | 479038 | 1 |  | 479038 | 479496.9038 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 479496.9038 | 465312.0212 | 14184.8826 | 3.0485 | OK
35 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 2782121.1 | 13885274 | 11103152.9 | 1 | Estimated | 583466 | 584024.9426 | Fatullah | Based on Grid Data |  |  | 11 kV Bishwa Road Feeder | 584024.9426 | 569321.714 | 14703.2286 | 2.5826 | OK
37 | 11 kV Spare Feeder |  | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 |  | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 13301808; 8: 13885274; 9=8-7: 583466; 10: Grand Total | 10319515.3191 | 10309639 | 10319515.3191 | 0.095797
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 7788343.8549
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1492793.6821
[6 empty] | Sytalakhya | at 33 KV level |  | 1038377.7822
[6 empty] | Total = |  |  | 10319515.3191 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder |  | 132 | Export | 041808902770 | 1 | 127.03 | 127.09 | 0.06 | 1200000 |  | 72000
|  |  | 132 |  | 041808904227 | 1 | 127.03 | 127.09 | 0.06 | 1200000 |  | 72000
|  |  | 132 | Import | 041808902770 | 1 | 333.3 | 352.01 | 18.71 | 1200000 | 22452000
|  |  | 132 |  | 041808904227 | 1 | 333.26 | 351.97 | 18.71 | 1200000 | 22452000
3 | 132 kV Haripur Feeder |  | 132 | Export | 041808902766 | 1 | 184.74 | 210.26 | 25.52 | 1200000 |  | 30624000
|  |  | 132 |  | 041808904230 | 1 | 184.81 | 210.35 | 25.54 | 1200000 |  | 30648000
|  |  | 132 | Import | 041808902766 | 1 | 722.71 | 723.83 | 1.12 | 1200000 | 1344000
|  |  | 132 |  | 041808904230 | 1 | 722.96 | 724.08 | 1.12 | 1200000 | 1344000
4 | 132 kV Aggreko Feeder |  | 132 | Export | 041808902768 | 1 | 34.31 | 35.2 | 0.89 | 1200000 |  | 1068000
|  |  | 132 |  | 041808904219 | 1 | 34.31 | 35.2 | 0.89 | 1200000 |  | 1068000
|  |  | 132 | Import | 041808902768 | 1 | 281.91 | 293.24 | 11.33 | 1200000 | 13596000
|  |  | 132 |  | 041808904219 | 1 | 281.91 | 293.24 | 11.33 | 1200000 | 13596000
6 | 132 kV Shyampur-2 Feeder |  | 132 | Export | 041808902793 | 1 | 120.8 | 120.87 | 0.07 | 1200000 |  | 84000
|  |  | 132 |  | 041808904278 | 1 | 120.82 | 120.88 | 0.06 | 1200000 |  | 72000
|  |  | 132 | Import | 041808902793 | 1 | 326.46 | 345.33 | 18.87 | 1200000 | 22644000
|  |  | 132 |  | 041808904278 | 1 | 326.52 | 345.39 | 18.87 | 1200000 | 22644000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 60036000 | 31848000
|  |  | 7: 0; 8: 0; 10: Net Total | 28188000 | 60900000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| FATULLAH 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | Export | 041808902767 | 1 | 676.2 | 690.94 | 14.74 | 1200000 |  | 17688000
|  |  | 132 | Export | 041808904228 | 1 | 676.74 | 690.76 | 14.02 | 1200000 |  | 16824000
5 | 132/33 kV, 80/120 MVA GT-2 |  | 132 | Export | 041808902792 | 1 | 523.71 | 533.18 | 9.47 | 1200000 |  | 11364000
|  |  | 132 | Export | 041808904251 | 1 | 523.51 | 532.97 | 9.46 | 1200000 |  | 11352000
|  |  | 10: Total |  | 29052000
| 132 KV IMPORT |  | 4: KWH | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 4: 28188000 | 132 KV NET IMPORT |  | 28188000
| IMPORT-2 | [9 empty] | 132/33 KV GT LV Side |  | 28087200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 100800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3576%
| 132 KV TOTAL IMPORT |  | 4: 28188000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902796 | 1 | 1122.9 | 1146.2 | 23.3 | 720000 | 16776000
|  |  | 33 | Backup | 041808904255 | 1 | 1122.9 | 1146.2 | 23.3 | 720000 | 16776000
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902802 | 1 | 869.11 | 884.82 | 15.71 | 720000 | 11311200
|  |  | 33 | Backup | 041808904281 | 1 | 868.88 | 884.59 | 15.71 | 720000 | 11311200
|  |  | 7: 0; 8: 0; 10: Total | 28087200 |  | 0
| FATULLAH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902868 | 1 | 891.74 | 907.79 | 16.05 | 240000 |  | 3852000 | 3850026.1337 |  | 8023886.2414 | New Fatullah 33/11 kv ss | 0.33871 | 33/11 kV, 28/35 MVA T-1 (=H5) | 3850026.1337 | 3952237.0697 | -102210.936 | -2.5862 | OK
|  |  | 33 | Backup | 041808904277 | 1 | 891.17 | 907.2 | 16.03 | 240000 |  | 3847200 | 3845228.5934 |  |  |  |  | 0 | 3845228.5934 | 3952237.0697 | -107008.4764 | -2.7075 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902824 | 1 | 801.67 | 819.07 | 17.4 | 240000 |  | 4176000 | 4173860.1076 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 4173860.1076 | 4686086.914 | -512226.8064 | -10.9308 | OK
|  |  | 33 | Backup | 041808904267 | 1 | 801.54 | 818.95 | 17.41 | 240000 |  | 4178400 | 4176258.8778 |  |  |  |  | 0 | 4176258.8778 | 4683688.7119 | -507429.8341 | -10.834 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 8028000 | 8023886.2414 |  |  |  |  | 33 KV Feeders | 8023886.2414 | 8638323.9838 | -614437.7424 | -7.1129 | OK
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 850.37 | 863.58 | 13.21 | 360000 |  | 4755600 | 4753163.1053 |  | 9743804.4581 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 4753163.1053 | 5622584.8362 | -869421.7309 | -15.463 | OK
|  |  | 33 | Backup | 041808904220 | 1 | 849.95 | 863.15 | 13.2 | 360000 |  | 4752000 | 4749564.95 |  |  |  |  | 0 | 4749564.95 | 5618987.533 | -869422.583 | -15.4729 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) |  | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 828.66 | 851.49 | 22.83 | 360000 |  | 8218800 | 8214588.4704 |  | 10319509.3005 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 8214588.4704 | 7899677.7353 | 314910.7351 | 3.9864 | OK
|  |  | 33 | Backup | 041808904262 | 1 | 828.67 | 851.51 | 22.84 | 360000 |  | 8222400 | 8218186.6257 |  |  |  |  | 0 | 8218186.6257 | 7896080.4321 | 322106.1935 | 4.0793 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 634.89 | 648.76 | 13.87 | 360000 |  | 4993200 | 4990641.3528 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 4990641.3528 | 6212542.5541 | -1221901.2013 | -19.6683 | OK
|  |  | 33 | Backup | 041808904219 | 1 | 635.27 | 649.15 | 13.88 | 360000 |  | 4996800 | 4994239.5081 |  |  |  |  | 0 | 4994239.5081 | 6216139.8573 | -1221900.3492 | -19.6569 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 543.91 | 549.76 | 5.85 | 360000 |  | 2106000 | 2104920.8301 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 2104920.8301 | 2039670.8907 | 65249.9395 | 3.199 | OK
|  |  | 33 | Backup | 041808904258 | 1 | 544.11 | 549.97 | 5.86 | 360000 |  | 2109600 | 2108518.9854 |  |  |  |  | 0 | 2108518.9854 | 2039670.8907 | 68848.0947 | 3.3755 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) |  | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 20073600 | 20063313.7586 |  |  |  |  | 0 | 20063313.7586 | 21774476.0162 | -1711162.2576 | -7.8586 | OK
|  |  | 9=8-7: Grand Total | 28087200 | 28101600 | 28087200 | -0.051243
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902832 | 1 | 853.69 | 869.05 | 15.36 | 250000 | 3840000 |  | 3847858.0289
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902765 | 1 | 767.37 | 784.04 | 16.67 | 250000 | 4167500 |  | 4176028.2124
|  |  | 7: 0; 8: 0; 10: Total | 8007500 |  | 8023886.2414
| FATULLAH 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) |  | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 1078.73 | 1099.46 | 20.73 | 60000 |  | 1243800 | 1248012.9185 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 1248012.9185 | 1373799.9394 | -125787.0209 | -9.1561 | OK
7 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 549.2 | 563.02 | 13.82 | 60000 |  | 829200 | 832008.6124 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 832008.6124 | 848842.2062 | -16833.5939 | -1.9831 | OK
8 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 586.35 | 593.29 | 6.94 | 60000 |  | 416400 | 417810.403 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 417810.403 | 413584.8196 | 4225.5834 | 1.0217 | OK
9 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1337.33 | 1359.7 | 22.37 | 60000 |  | 1342200 | 1346746.2126 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1346746.2126 | 1312996.3488 | 33749.8639 | 2.5704 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) |  | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) |  | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 250.63 | 264.89 | 14.26 | 60000 |  | 855600 | 858498.0327 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 858498.0327 | 696532.2217 | 161965.811 | 23.2532 | OK
16 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 114.82 | 119.87 | 5.05 | 60000 |  | 303000 | 304026.3019 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 304026.3019 | 281141.3548 | 22884.9471 | 8.14 | OK
17 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1283.61 | 1307.02 | 23.41 | 60000 |  | 1404600 | 1409357.5699 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1409357.5699 | 2028191.0587 | -618833.4888 | -30.5116 | OK
18 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1548.27 | 1574.97 | 26.7 | 60000 |  | 1602000 | 1607426.1903 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 1607426.1903 | 1683236.0345 | -75809.8442 | -4.5038 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 8023886.2414 | 7996800 | 8023886.2414 | 0.33871
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 8023886.2414
[6 empty] | Total = |  |  | 8023886.2414 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 850.37 | 863.58 | 13.21 | 360000 | 0 | 4755600 | 4753163.1053
0 | 0 |  | 33 | Backup | 041808904220 | 1 | 849.95 | 863.15 | 13.2 | 360000 | 0 | 4752000 | 4749564.95
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 634.89 | 648.76 | 13.87 | 360000 | 0 | 4993200 | 4990641.3528
0 | 0 |  | 33 | Backup | 041808904219 | 1 | 635.27 | 649.15 | 13.88 | 360000 | 0 | 4996800 | 4994239.5081
| DAPA 33 KV SIDE (RECEIVING) |  | 10: Total | 0 | 9748800 | 9743804.4581
5 | 33 kV New Fatullah Incoming Circuit-2 |  | 33 | Import |  | 1 | 228127328 | 233105584 | 4978256 | 1 | 4978256
6 | 33 kV Shyampur Incoming Circuit |  | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder |  | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  |  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 |  | 33 | Import |  | 1 | 305612992 | 310354464 | 4741472 | 1 | 4741472
|  |  | 7: 0; 8: 0; 10: Total | 9719728 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DAPA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) |  | 33 | Export | 00000135 | 1 | 319482240 | 324535200 | 5052960 | 1 |  | 5052960
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) |  | 33 | Export | 00000193 | 1 | 307470240 | 312132960 | 4662720 | 1 |  | 4662720
|  |  | 10: Total |  | 9715680 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 4: 9743804.4581; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9715680
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 9715680 | 33 KV TX HV SIDE |  | 9715680
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9743804.4581
11 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000035 | 1 | 305732160 | 310367552 | 4635392 | 1 | 4635392 |  | 4654601.2465
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000143 | 1 | 318125760 | 323165952 | 5040192 | 1 | 5040192 |  | 5061078.7535
|  |  | 7: 0; 8: 0; 10: Total | 9675584 |  | 9715680
| DAPA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV Katherpol Feeder | B8919 | 11 |  | 00000031 | 1 | 74107936 | 75499056 | 1391120 | 1 |  | 1391120 | 1398334.1219 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 1398334.1219 | 1565992 | -167657.8781 | -10.7062 | OK
12 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | B8918 | 11 |  | 00000032 | 1 | 75379016 | 76520056 | 1141040 | 1 |  | 1141040 | 1146957.2477 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1146957.2477 | 1688392 | -541434.7523 | -32.0681 | OK
14 | 11 kV Shiachar Feeder | B891G | 11 |  | 00000030 | 1 | 75050736 | 75786576 | 735840 | 1 |  | 735840 | 739655.9465 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 739655.9465 | 775000 | -35344.0535 | -4.5605 | OK
15 | 11 kV Sastapur Feeder | B8913 | 11 |  | 00000106 | 1 | 72981944 | 73300544 | 318600 | 1 |  | 318600 | 320252.2077 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 320252.2077 | 338920 | -18667.7923 | -5.508 | OK
17 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | B891JA | 11 |  | 00000172 | 1 | 7006920 | 7453942 | 447022 | 1 |  | 447022 | 449340.1833 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 449340.1833 | 1127415 | -678074.8167 | -60.1442 | CHECK
19 | 11 kV Hajibari Feeder |  | 11 |  | 00000105 | 1 | 1476956 | 2068515 | 591559 | 1 |  | 591559 | 594626.7287 | Fatullah |  |  |  | 11 kV Hajibari Feeder | 594626.7287 | 623399 | -28772.2713 | -4.6154 | OK
21 | 11 kV Railine Feeder |  | 11 |  |  | 1 | 1930995 | 2811513 | 880518 | 1 |  | 880518 | 885084.223 | Fatullah |  |  |  | 11 kV Railine Feeder | 885084.223 | 827958 | 57126.223 | 6.8997 | OK
22 | 11 kV Lalpur Feeder | B8911 | 11 |  | 00000044 | 1 | 87270824 | 87457064 | 186240 | 1 |  | 186240 | 187205.8103 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 187205.8103 | 187040 | 165.8103 | 0.08865 | OK
23 | 11 kV Kotaler Bag Feeder | B8912 | 11 |  | 00000050 | 1 | 94020488 | 95110648 | 1090160 | 1 |  | 1090160 | 1095813.3923 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 1095813.3923 | 1076072 | 19741.3923 | 1.8346 | OK
24 | 11 kV Idrakpur Feeder | B8915 | 11 |  | 00000021 | 1 | 81621160 | 82410480 | 789320 | 1 |  | 789320 | 793413.285 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 793413.285 | 821400 | -27986.715 | -3.4072 | OK
25 | 11 kV Isdair Feeder | B8914 | 11 |  | 00000029 | 1 | 44106812 | 44588012 | 481200 | 1 |  | 481200 | 483695.4249 | Fatullah |  |  |  | 11 kV Isdair Feeder | 483695.4249 | 494720 | -11024.5751 | -2.2284 | OK
26 | 11 kV Shah Fateullah Express |  | 11 |  | 0000051 | 1 | 7578901 | 7862421 | 283520 | 1 |  | 283520 | 284990.2886 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 284990.2886 | 1400836 | -1115845.7114 | -79.6557 | CHECK
27 | 11 kV Boubazar Feeder |  | 11 |  | 00000151 | 1 | 1726035 | 3051752 | 1325717 | 1 |  | 1325717 | 1332591.9526 | Fatullah |  |  |  | 11 kV Boubazar Feeder | 1332591.9526 | 1146597 | 185994.9526 | 16.2215 | OK
28 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKF 7522 | 1 | 3306 | 3343 | 37 | 100 |  | 3700 | 3719.1876 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 3719.1876 | 3300 | 419.1876 | 12.7027 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 9715680 | 9665556 | 9715680 | 0.51858
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 9715680
[6 empty] | Total = |  |  | 9715680 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 |  | 132 | IMPORT | 50501730 | 1 | 3046.435 | 3074.252 | 27.817 | 480000 | 0 | 13352160
2 | Tranformer 1 |  | 132 |  | 80505634 | 1 | 8633.535 | 8660.035 | 26.5 | 480000 | 0 | 12720000
3 | Tranformer 2 |  | 132 |  | 80505637 | 1 | 8586.77 | 8613.4 | 26.63 | 480000 | 0 | 12782400
4 | MI CEMENT |  | 132 |  | 38992489 (New) | 1 | 420.52 | 435.983 | 15.463 | 480000 | 0 | 7422240
|  |  | 9=8-7: Total Import/Export | 0 | 46276800
|  |  | 10: Net Total | 46276800
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 420.507 | 435.968 | 15.461 | 480000 |  | 7421280
|  |  | 132 | DPDC | 16402670 | 1 | 1945.437 | 1960.872 | 15.435 | 480000 |  | 7408800
|  |  | 10: Total |  | 7408800
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 38868000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 46276800; 6: EXPORT TO OTHER S/S; 9=8-7: 7408800 | 132 KV NET IMPORT |  | 38868000
| IMPORT-2 |  | 6: 132 KV NET IMPORT for Sitalakhya 33/11 KV; 9=8-7: 38868000 | GT (33 KV Side) |  | 25968192
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 12899808
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 33.19%
| 132 KV TOTAL IMPORT |  | 4: 46276800
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A030701130-03 | 1 | 73369.103 | 73369.103 | 0 | 1000 | 0
|  |  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  |  | 33 | DPDC | BD001913 | 1 | 1940.828 | 1967.1899 | 26.3619 | 480000 | 12653712
18 | 132/33 KV Transformer, GT-3 Incoming |  | 33 | DPDC | BD001915 | 1 | 3038.7494 | 3066.4879 | 27.7385 | 480000 | 13314480
|  |  | 7: 0; 8: 0; 10: Total | 25968192 |  | 0
| SITALAKHYA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 |  | 33 | DPDC | H/A030701089-03 | 1 | 21432.637 | 27886.587 | 6453.95 | 1000 |  | 6453950 | 6455105.214 |  | 9685418.315 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 6455105.214 | 7177015.4696 | -721910.2556 | -10.0586 | OK
|  |  | 33 | P. Cell | 08993597 | 1 | 6079.684 | 6106.611 | 26.927 | 240000 |  | 6462480 | 6463636.7408 |  |  |  |  | 0 | 6463636.7408 | 7177138.6209 | -713501.8801 | -9.9413 | OK
13 | 33/11 KV Transformer T-4 |  | 33 | DPDC | H/A030701087-03 | 1 | 96702.24 | 99931.975 | 3229.735 | 1000 |  | 3229735 | 3230313.101 |  |  |  |  | 33/11 KV Transformer T-4 | 3230313.101 | 3366980.0416 | -136666.9405 | -4.059 | OK
|  |  | 33 | P. Cell | 08993925 | 1 | 5798.362 | 5816.312 | 17.95 | 180000 |  | 3231000 | 3231578.3274 |  |  |  |  | 0 | 3231578.3274 | 3367617.8252 | -136039.4978 | -4.0396 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 9683685 | 9685418.315 |  |  |  |  | 33 KV Feeders | 9685418.315 | 10543995.5112 | -858577.1962 | -8.1428 | OK
10 | 33 KV Char Syedpur Feeder (F1) |  | 33 | DPDC | H/A030701083-03 | 1 | 42622.667 | 42622.67 | 0.003 | 1000 |  | 3 | 3.0005 |  | 363.065 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 3.0005 | 0 | 3.0005 | #DIV/0! | #DIV/0!
| 33 KV Char Syedpur Feeder (F1) |  | 33 | P. Cell | 08993596 | 1 | 2186.834 | 2186.836 | 0.002 | 180000 |  | 360 | 360.0644 |  |  |  |  | 33 KV Char Syedpur Feeder (F1) | 360.0644 | 0 | 360.0644 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 82041.299 | 89938.579 | 7897.28 | 1000 |  | 7897280 | 7898693.5604 |  | 7898693.5604 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 7898693.5604 | 8883938.7831 | -985245.2227 | -11.0902 | OK
| 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 10080.476 | 10124.406 | 43.93 | 180000 |  | 7907400 | 7908815.3718 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 7908815.3718 | 8878248.7918 | -969433.4199 | -10.9192 | OK
14 | 33 KV Shah Cement Feeder (F2) |  | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993926 | 1 | 2303.686 | 2303.686 | 0 | 180000 |  | 0 | 0 |  | 10557203.3308 | Khanpur 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 57679.762 | 63139.348 | 5459.586 | 1000 |  | 5459586 | 5460563.2295 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 5460563.2295 | 5736244.1797 | -275680.9503 | -4.8059 | OK
|  |  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1793.2502 | 1823.2765 | 30.0263 | 180000 |  | 5404734 | 5405701.4113 |  | 10606184.0964 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 5405701.4113 | 5715560.7658 | -309859.3545 | -5.4213 | OK
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 579.5569 | 600.7891 | 21.2322 | 240000 |  | 5095728 | 5096640.1013 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 5096640.1013 | 4703467.1965 | 393172.9048 | 8.3592 | OK
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1463.5042 | 1485.169 | 21.6648 | 240000 |  | 5199552 | 5200482.6851 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 5200482.6851 | 5173028.1507 | 27454.5345 | 0.53072 | OK
21 | 33/0.415 KV Transformer AT-1 |  | 0.415 | DPDC | 2001123043108 | 1 | 6601.2 | 6601.2 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 |  | 0.415 | DPDC | 2001123043171 | 1 | 4821.1 | 4843.2 | 22.1 | 160 |  | 3536 | 3536.6329 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 3536.6329 | 4405.413 | -868.7801 | -19.7207 | OK
|  |  | 10: Total |  | 29060776 | 29065977.685 |  |  |  |  | 0 | 29065977.685 | 30216644.4888 | -1150666.8038 | -3.8081 | OK
|  |  | 9=8-7: Grand Total | 38751396 | 38744461 | 38751396 | 0.017899
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 3536.6329
[6 empty] | Total = |  |  | 3536.6329
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | DHK 9372 | 1 | 52837.222 | 88515.0166 | 35677.7946 | 180 | 6422003.028 |  | 6441416.401 |  |  |  |  | 33/11 kV Transformer, T-3 Incoming | 6441416.401 | 7169536.971 | -728120.57 | -10.1558 | OK
10 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | DHK 9368 | 1 | 28854.5908 | 46822.5076 | 17967.9168 | 180 | 3234225.024 |  | 3244001.914 |  |  |  |  | 33/11 kV Transformer, T-4 Incoming | 3244001.914 | 3374458.5402 | -130456.6262 | -3.866 | OK
|  |  | 7: 0; 8: 0; 10: Total | 9656228.052 |  | 9685418.315
| SITALAKHYA 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Bholail Feeder (F-3) | E330V | 11 |  | DHK 9335 | 1 | 77455.415 | 108437.6691 | 30982.2541 | 60 |  | 1858935.246 | 1858324.9967 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 1858324.9967 | 2013674.4126 | -155349.4159 | -7.7147 | OK
4 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 |  | DHK 9336 | 1 | 68565.3996 | 80596.998 | 12031.5984 | 60 |  | 721895.904 | 721658.9208 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 721658.9208 | 955009.3094 | -233350.3887 | -24.4344 | OK
5 | 11 kV Baburail Feeder (F-5) | A730R | 11 |  | DHK 9322 | 1 | 50469.7377 | 69584.4928 | 19114.7551 | 60 |  | 1146885.306 | 1146508.8077 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 1146508.8077 | 1148290.4515 | -1781.6438 | -0.15516 | OK
6 | 11 kV Goghchar Feeder (F-1) | E330G | 11 |  | DHK 9323 | 1 | 22798.1622 | 36757.1711 | 13959.0089 | 60 |  | 837540.534 | 837265.5871 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 837265.5871 | 867815.5092 | -30549.9221 | -3.5203 | OK
7 | 11 kV Norshinghopur (F-2) | E330N | 11 |  | DHK 9365 | 1 | 42671.5983 | 63259.5479 | 20587.9496 | 60 |  | 1235276.976 | 1234871.4606 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1234871.4606 | 1546668.4472 | -311796.9866 | -20.1593 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 |  | DHK 9367 | 1 | 48332.3462 | 59007.8114 | 10675.4652 | 60 |  | 640527.912 | 640317.6402 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 640317.6402 | 633130.6001 | 7187.0401 | 1.1352 | OK
11 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 |  | H/A030701125-03 | 1 | 74234.025 | 74352.257 | 118.232 | 1000 |  | 118232 | 118193.1869 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 118193.1869 | 123250.1728 | -5056.9858 | -4.103 | OK
12 | 11 kV Kashipur Feeder (F-7) | E317K | 11 |  | H/A030800169-03 | 1 | 43340.071 | 44353.535 | 1013.464 | 1000 |  | 1013464 | 1013131.3011 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1013131.3011 | 988679.7738 | 24451.5273 | 2.4731 | OK
13 | 11 kV Spare Feeder (F-6) |  | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | A730D | 11 |  | H/A030701098-03 | 1 | 83745.993 | 84409.069 | 663.076 | 1000 |  | 663076 | 662858.3261 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 662858.3261 | 669681.2156 | -6822.8895 | -1.0188 | OK
15 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 |  | H/A030800205-03 | 1 | 99929.399 | 100789.088 | 859.689 | 1000 |  | 859689 | 859406.7822 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 859406.7822 | 984065.5944 | -124658.8122 | -12.6677 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 |  | H/A030701091-03 | 1 | 58318.957 | 58912.033 | 593.076 | 1000 |  | 593076 | 592881.3056 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 592881.3056 | 613730.0246 | -20848.719 | -3.3971 | OK
|  |  | 10: Total | 9685418.315 | 9688598.878 | 9685418.315 | -0.032828
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 977599.9691
[6 empty] | Sytalakhya | at 33 KV level |  | 6898451.2121
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1809367.1338
[6 empty] | Total = |  |  | 9685418.315 | 0
MI CEMENT 132/33 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 420.507 | 435.968 | 15.461 | 480000 | 7421280 |  | 7422240
|  |  | 132 | DPDC | 16402670 | 1 | 1945.437 | 1960.872 | 15.435 | 480000 | 7408800
2 | 132/33 kV Transformer (132 kV Side) |  | 132 |  | 06502030 | 1 | 3872.278 | 3903.32 | 31.042 | 240000 |  | 7450080
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 7408800 | 7450080
[7 empty] | 0 | 0 |  | Net Total
[7 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) |  | 33 |  | 14718815 | 1 | 7643.069 | 7704.548 | 61.479 | 120000 | 7377480
4 | 33 kV Outgoing Feeder-1 |  | 33 |  | 11745824 | 1 | 3871.181 | 3875.574 | 4.393 | 120000 |  | 527160
5 | 33 kV Outgoing Feeder-2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 6850320
|  |  | 9=8-7: Total Import/Export | 7377480 | 7377480
|  |  | 9=8-7: Net Total | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 7422240
[6 empty] | Total = |  |  | 7422240
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1793.2502 | 1823.2765 | 30.0263 | 180000 | 0 | 5404734 | 5405701.4113
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1463.5042 | 1485.169 | 21.6648 | 240000 | 0 | 5199552 | 5200482.6851
|  |  | 10: Total | 0 | 10604286 | 10606184.0964
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder |  | 33 |  | 00000188 | 1 | 354095296 | 359517952 | 5422656 | 1 | 5422656
7 | 33 kV Shitalakhya-1 Feeder |  | 33 |  | 00000153 | 1 | 351748160 | 356949008 | 5200848 | 1 | 5200848
|  |  | 7: 0; 8: 0; 10: Total | 10623504 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000116 | 1 | 358773376 | 364185240 | 5411864 | 1 |  | 5411864
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000194 | 1 | 346861920 | 352098496 | 5236576 | 1 |  | 5236576
|  |  | 10: Total |  | 10648440
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 10606184.0964; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10606184.0964
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 10606184.0964 | 33 KV TX HV SIDE |  | 10648440
[11 empty] | LOSS UNITS=> |  | -42255.9036
[11 empty] | LOSS % IN => |  | -0.3984%
| TOTAL IMPORT |  | 4: 10606184.0964
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming |  | 11 |  | 00000055 | 1 | 345207584 | 350418784 | 5211200 | 1 | 5211200 |  | 5252198.7743
19 | 11 kV T-2 Incoming |  | 11 |  | 00000017 | 1 | 356001184 | 361313376 | 5312192 | 1 | 5312192 |  | 5353985.3222
|  |  | 7: 0; 8: 0; 10: Total | 10523392 |  | 10606184.0964
| MONDOLPARA 11 KV SIDE |  | 7: 0; 8: 0
9 | 11 kV River View | B793U | 11 |  | 00000061 | 1 | 973316 | 1554356 | 581040 | 1 |  | 581040 | 584945.4383 | N.Gonj (East) |  |  |  | 11 kV River View | 584945.4383 | 599013.8573 | -14068.419 | -2.3486 | OK
10 | 11 kV Railgate B.B. Road | B793F | 11 |  | 00000191 | 1 | 26175216 | 26608216 | 433000 | 1 |  | 433000 | 435910.3931 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 435910.3931 | 431605.906 | 4304.487 | 0.99732 | OK
11 | 11 kV DIT | A722D | 11 |  | 00000174 | 1 | 152106944 | 154077504 | 1970560 | 1 |  | 1970560 | 1983805.0443 | N.Gonj (West) |  |  |  | 11 kV DIT | 1983805.0443 | 1892651.3817 | 91153.6626 | 4.8162 | OK
12 | 11 kV Dalpatti | B7227 | 11 |  | 00000182 | 1 | 7996260 | 8685539 | 689279 | 1 |  | 689279 | 693911.9626 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 693911.9626 | 731072.4862 | -37160.5235 | -5.083 | OK
13 | 11 kV South Chasara | A793S | 11 |  | 00000043 | 1 | 107368256 | 108895656 | 1527400 | 1 |  | 1527400 | 1537666.3611 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 1537666.3611 | 1531701.7545 | 5964.6066 | 0.38941 | OK
14 | 11 kV Spare |  | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | B7225 | 11 |  | 00000019 | 1 | 270279 | 284999 | 14720 | 1 |  | 14720 | 14818.9399 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 14818.9399 | 17228.8103 | -2409.8703 | -13.9874 | OK
17 | 11 kV Spare |  | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | B7229 | 11 |  | 00000173 | 1 | 12029731 | 13087848 | 1058117 | 1 |  | 1058117 | 1065229.0933 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1065229.0933 | 1166392.4718 | -101163.3785 | -8.6732 | OK
20 | 11 kV Nitaigonj | B722G | 11 |  | 00000189 | 1 | 62416688 | 63026568 | 609880 | 1 |  | 609880 | 613979.2853 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 613979.2853 | 690524.2593 | -76544.974 | -11.0851 | OK
21 | 11 kV Shahid Nagar | E323T | 11 |  | 00000020 | 1 | 63774244 | 64601524 | 827280 | 1 |  | 827280 | 832840.5311 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 832840.5311 | 869546.5268 | -36705.9957 | -4.2213 | OK
22 | 11 kV Bangla Bazar | A793Z | 11 |  | 00000139 | 1 | 77532128 | 78510408 | 978280 | 1 |  | 978280 | 984855.4719 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 984855.4719 | 997084.1061 | -12228.6342 | -1.2264 | OK
23 | 11 kV Vogoban Gonj | B7228 | 11 |  | 00000181 | 1 | 4974668 | 5301627 | 326959 | 1 |  | 326959 | 329156.6425 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 329156.6425 | 369994.7525 | -40838.11 | -11.0375 | OK
24 | 11 kV Tanbazar | B722I | 11 |  | 00000138 | 1 | 53665148 | 54277388 | 612240 | 1 |  | 612240 | 616355.1479 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 616355.1479 | 620555.9224 | -4200.7745 | -0.67694 | OK
25 | 11 kV SS Road | A793O | 11 |  | 00000175 | 1 | 72509304 | 73412984 | 903680 | 1 |  | 903680 | 909754.0508 | N.Gonj (West) |  |  |  | 11 kV SS Road | 909754.0508 | 968444.7395 | -58690.6887 | -6.0603 | OK
26 | 11 kV Spare |  | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 |  | 0.415 |  |  | 1 | 2729.32 | 2758.68 | 29.36 | 100 |  | 2936 | 2955.7342 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 2955.7342 | 2771.9421 | 183.7921 | 6.6304 | OK
28 | 33/0.415 kV Auxiliary-2 |  | 0.415 |  |  | 1 | 4.17 | 4.17 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 10606184.0964 | 10535371 | 10606184.0964 | 0.67215
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 832840.5311
[6 empty] | N.Gonj (East) | at 33 KV level |  | 4354306.9029
[6 empty] | N.Gonj (West) | at 33 KV level |  | 5419036.6624
[6 empty] | Total = |  |  | 10606184.0964 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 82041.299 | 89938.579 | 7897.28 | 1000 | 0 | 7897280 | 7898693.5604
0 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 10080.476 | 10124.406 | 43.93 | 180000 | 0 | 7907400 | 7908815.3718
| MATUAIL 33 KV SIDE |  | 10: Total |  | 7897280 | 7898693.5604
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 44.915 | 5644.734 | 5599.819 | 1000 | 0 | 5599819 | 5617163.2461
0 | 0 |  | 33 | P. Cell | 08993580 | 1.5 | 1478.712 | 1499.424 | 20.712 | 180000 | 0 | 5592240 | 5609560.7718
|  |  | 10: Total | 0 | 5599819 | 5617163.2461
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) |  | 10: Total |  | 13497099 | 13515856.8066
3 | 33 kV Matuail Feeder |  | 33 | Digital | ABB03910 | 1.5 | 88478.7716 | 89399.1057 | 920.3341 | 4000 | 5522004.66
6 | 33 kV Shitalakhya Feeder |  | 33 | Old | HA030800161-03 | 1 | 82625.967 | 90501.704 | 7875.737 | 1000 | 7875737
|  |  | 33 | New | DHKA2199 | 1 | 4473.2987 | 4512.3645 | 39.0658 | 180000 | 7031844
|  |  | 7: 0; 8: 0; 10: Total | 13397741.66 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 20/28 MVA Transformer-3 |  | 33 | Old | HA021100524-02 | 1 | 38793.806 | 44393.821 | 5600.015 | 1000 |  | 5600015
|  |  | 33 | New | DHKA2200 | 1 | 4472.6821 | 4502.0939 | 29.4118 | 180000 |  | 5294124
7 | 33/11 kV, 10/14 MVA Transformer-2 |  | 33 | Old | HA030800199-03 | 1 | 70624.567 | 74505.903 | 3881.336 | 1000 |  | 3881336
|  |  | 33 | New | DHKA2195 | 1 | 4802.5008 | 4843.3305 | 40.8297 | 90000 |  | 3674673
8 | 33/11 kV, 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03909 | 1 | 456189.121 | 460016.0326 | 3826.9116 | 1000 |  | 3826911.62
|  |  | 10: Total |  | 13002371.62
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 7898693.5604; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 13515856.8066
| MATUAIL 33 KV SIDE |  | 4: 5617163.2461; 6: 33 KV NET IMPORT; 9=8-7: 13515856.8066 | 33 KV TX HV SIDE |  | 13002371.62
[11 empty] | LOSS UNITS=> |  | 513485.1866
[11 empty] | LOSS % IN => |  | 3.799%
| TOTAL IMPORT |  | 4: 13515856.8066
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | 51426632 | 1 | 4073572 | 4116330 | 42758 | 90 | 3848220 |  | 4510623.4933
16 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | DHKA2192 | 1 | 4193.7005 | 4236.8347 | 43.1342 | 90000 | 3882078 |  | 4550309.5534
22 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426630 | 1 | 4375892 | 4418122 | 42230 | 90 | 3800700 |  | 4454923.7598
|  |  | 7: 0; 8: 0; 10: Total | 11530998 |  | 13515856.8066
| NARAYANGONJ BSCIC 11 KV SIDE |  | 7: 0; 8: 0
10 | 11 kV Masdair Feeder (F-8) | A727M | 11 |  | XA575914 | 1 | 229632.2 | 231707.3 | 2075.1 | 1000 |  | 2075100 | 2098989.5568 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 2098989.5568 | 2114160.9709 | -15171.4141 | -0.71761 | OK
11 | 11 kV Narayangonj (F-7) | A727N | 11 |  | XA575915 | 1 | 174073.5 | 175376.8 | 1303.3 | 1000 |  | 1303300 | 1318304.2212 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1318304.2212 | 1433628.8234 | -115324.6022 | -8.0442 | OK
12 | 11 kV Nearest Feeder (F-6) | A727B | 11 |  | XA575927 | 1 | 111780.3 | 112632.8 | 852.5 | 1000 |  | 852500 | 862314.3931 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 862314.3931 | 1034978.077 | -172663.6839 | -16.6828 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 |  | XA575916 | 1 | 123435.1 | 124470.2 | 1035.1 | 1000 |  | 1035100 | 1047016.5728 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1047016.5728 | 1052639.8189 | -5623.2461 | -0.5342 | OK
14 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 |  | XA575912 | 1 | 60091.3 | 60190.9 | 99.6 | 1000 |  | 99600 | 100746.6435 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 100746.6435 | 424285.5032 | -323538.8598 | -76.255 | CHECK
15 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 |  | DHK66615 | 1 | 293.277 | 309.5082 | 16.2313 | 60000 |  | 973876.68 | 985088.4203 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 985088.4203 | 931115.7309 | 53972.6894 | 5.7966 | OK
17 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 |  | XA575920 | 1 | 237301.7 | 237737.5 | 435.8 | 1000 |  | 435800 | 440817.1408 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 440817.1408 | 776813.8721 | -335996.7313 | -43.2532 | CHECK
18 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 |  | XA575929 | 1 | 27035.8 | 28020.2 | 984.4 | 1000 |  | 984400 | 995732.8899 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 995732.8899 | 1047492.6827 | -51759.7929 | -4.9413 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 |  | HA021100913-02 | 1 | 50963.735 | 52907.64 | 1943.905 | 1000 |  | 1943905 | 1966284.1764 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 1966284.1764 | 1986570.5288 | -20286.3524 | -1.0212 | OK
20 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 |  | HA021100682-02 | 1 | 73152.506 | 75288.503 | 2135.997 | 1000 |  | 2135997 | 2160587.6326 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2160587.6326 | 2078760.7847 | 81826.8479 | 3.9363 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 |  | HA021100455-02 | 1 | 64616.288 | 66130.592 | 1514.304 | 1000 |  | 1514304 | 1531737.4015 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1531737.4015 | 1597056.4538 | -65319.0523 | -4.09 | OK
23 | 11/0.415 KV Transformer,AT-1 |  | 0.415 | Analog | 2001123043161 | 1 | 4158.3 | 4198.6 | 40.3 | 160 |  | 6448 | 6522.2325 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 6522.2325 | 9333.4737 | -2811.2412 | -30.12 | OK
24 | 11/0.415 KV Transformer,AT-2 |  | 0.415 | Analog | 2001123043118 | 1 | 4131.2 | 4141.8 | 10.6 | 160 |  | 1696 | 1715.5252 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 1715.5252 | 662.063 | 1053.4622 | 159.1181 | FAULT
|  |  | 10: Grand Total | 13515856.8066 | 13362026.68 | 13515856.8066 | 1.1512
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 440817.1408
[6 empty] | N.Gonj (West) | at 33 KV level |  | 13075039.6658
[6 empty] | Total = |  |  | 13515856.8066 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) |  | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  |  | IMPORT | 42627811 | 1 | 331.961 | 347.483 | 15.522 | 960000 | 0 | 14901120
| Madonganj to Charsyedpur-2 |  |  |  | 42627824 | 1 | 277.138 | 299.056 | 21.918 | 960000 | 0 | 21041280
|  |  | 9=8-7: Total Import/Export | 0 | 35942400 | 0
|  |  | 10: Net Total | 35942400
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 |  | 132 |  | 041808902821 | 1 | 272.99 | 285.4 | 12.41 | 1200000 | 14892000
|  |  | 132 |  | 041808904222 | 3 | 90.36 | 94.46 | 4.1 | 1200000 | 14760000
| 132 kV Madanganj Circuit-2 |  | 132 |  | 041808902865 | 1 | 221.6 | 239.15 | 17.55 | 1200000 | 21060000
|  |  | 132 |  | 041808904240 | 1 | 221.67 | 239.23 | 17.56 | 1200000 | 21072000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 35952000 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 35952000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 kV Shah Cement |  | 132 | EXPORT | 042003953369 | 1 | 57.56 | 68.69 | 11.13 | 1200000 |  | 13356000 |  | Sytalakhya | Main Meter
| 133 kV Shah Cement |  | 132 |  | 042003953379 | 1 | 57.61 | 68.75 | 11.14 | 1200000 |  | 13368000 |  |  | Check Meter
|  |  | 7: 0; 8: 0; 10: Total |  | 13356000
| CHAR SYEDPUR 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | EXPORT | 041808902864 | 1 | 223.56 | 235.95 | 12.39 | 1200000 |  | 14868000
|  |  | 132 |  | 041808904224 | 1 | 223.41 | 235.79 | 12.38 | 1200000 |  | 14856000
7 | 132/33 kV, 80/120 MVA GT-2 |  | 132 |  | 041808902848 | 1 | 213.36 | 219.79 | 6.43 | 1200000 |  | 7716000
|  |  | 132 |  | 041808904244 | 1 | 213.46 | 219.89 | 6.43 | 1200000 |  | 7716000
|  |  | 10: Total | 35940000 | 22584000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 35942400; 6: Sytalakhya NOCS; 9=8-7: 13356000 | 132 KV NET IMPORT |  | 22584000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 22584000 | 132/33 KV LV SIDE |  | 22478400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 105600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4676%
| 132 KV TOTAL IMPORT |  | 4: 35942400
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902859 | 1 | 370.21 | 390.78 | 20.57 | 720000 | 14810400 |  | 14879976.9379
|  |  | 33 | Backup | 041808904285 | 1 | 370.21 | 390.78 | 20.57 | 720000 | 14810400 |  | 14879976.9379
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902812 | 1 | 353.77 | 364.42 | 10.65 | 720000 | 7668000 |  | 7704023.0621
|  |  | 33 | Backup | 041808904276 | 1 | 353.79 | 364.44 | 10.65 | 720000 | 7668000 |  | 7704023.0621
|  |  | 7: 0; 8: 0; 10: Total | 22478400 |  | 22584000
| CHAR SYEDPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902875 | 1 | 271.44 | 282.56 | 11.12 | 240000 |  | 2668800 | 2669079.5205 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2669079.5205 | 2646548.644 | 22530.8765 | 0.85133 | OK
|  |  | 33 | Backup | 041808904241 | 1 | 271.36 | 282.47 | 11.11 | 240000 |  | 2666400 | 2666679.2691 |  |  |  |  | 0 | 2666679.2691 | 2648945.8801 | 17733.3891 | 0.66945 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902844 | 3 | 76.82 | 78.56 | 1.74 | 240000 |  | 1252800 | 1252931.2138 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 1252931.2138 | 1416766.5295 | -163835.3158 | -11.564 | OK
|  |  | 33 | Backup | 041808904259 | 3 | 76.82 | 78.56 | 1.74 | 240000 |  | 1252800 | 1252931.2138 |  |  |  |  | 0 | 1252931.2138 | 1416766.5295 | -163835.3158 | -11.564 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 3921600 | 3922010.7342 |  |  |  |  | 33 KV Feeders | 3922010.7342 | 4063315.1735 | -141304.4392 | -3.4776 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) |  | 33 | Main | 041808902866 | 1 | 414.31 | 436.67 | 22.36 | 360000 |  | 8049600 | 8050443.0861 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 8050443.0861 | 6760205.7754 | 1290237.3107 | 19.0858 | OK
|  |  | 33 | Backup | 041808904221 | 1 | 414.51 | 436.88 | 22.37 | 360000 |  | 8053200 | 8054043.4631 |  |  |  |  | 0 | 8054043.4631 | 6763801.6295 | 1290241.8336 | 19.0757 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) |  | 33 | Main | 041808902876 | 1 | 145.66 | 157.03 | 11.37 | 360000 |  | 4093200 | 4093628.707 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 4093628.707 | 3678558.781 | 415069.9261 | 11.2835 | OK
|  |  | 33 | Backup | 041808904237 | 1 | 145.66 | 157.03 | 11.37 | 360000 |  | 4093200 | 4093628.707 |  |  |  |  | 0 | 4093628.707 | 3678558.781 | 415069.9261 | 11.2835 | OK
11 | 33 kV Crown Cement-1 (=H3) |  | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Crown Cement-1 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) |  | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904232 | 1 | 43.8 | 43.8 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Outgoing Feeder-6 (=H12) |  | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Crown Cement-2 (=H13) |  | 33 | Main | 041808902857 | 1 | 12.92 | 30.73 | 17.81 | 360000 |  | 6411600 | 6412271.5279 | Sytalakhya |  |  |  | 33 kV Crown Cement-2 (=H13) | 6412271.5279 | 4275470.5675 | 2136800.9604 | 49.9781 | FAULT
|  |  | 33 | Backup | 041808904234 | 1 | 12.92 | 30.73 | 17.81 | 360000 |  | 6411600 | 6412271.5279 |  |  |  |  | 0 | 6412271.5279 | 4275470.5675 | 2136800.9604 | 49.9781 | FAULT
20 | 33 kV Shah Cement VRM (=H14) |  | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904242 | 1 | 499.7 | 499.7 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/0.415 kV Transformer AT-1 |  |  |  |  | 1 | 2097.69 | 2143.63 | 45.94 | 1 |  | 45.94 | 45.9448 | [5 empty] | 45.9448 | 49.7027
|  |  | 10: Total |  | 18554445.94 | 18556389.2658 |  |  |  |  | 0 | 18556389.2658 | 14714284.8265 | 3842104.4392 | 26.1114 | OK
|  |  | 9=8-7: Grand Total | 22478400 | 22476045.94 | 22478400 | 0.010474
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902756 | 1 | 259.36 | 269.99 | 10.63 | 250000 | 2657500 |  | 2669076.4472
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902778 | 1 | 167.52 | 172.51 | 4.99 | 250000 | 1247500 |  | 1252934.2871
|  |  | 7: 0; 8: 0; 10: Total | 3905000 |  | 3922010.7342
| CHAR SYEDPUR 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 |  | 041808902749 | 1 | 508.18 | 519.12 | 10.94 | 60000 |  | 656400 | 653568.887 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 653568.887 | 698675.0469 | -45106.1599 | -6.456 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) |  | 11 |  | 041808902759 | 1 | 556.24 | 579.04 | 22.8 | 60000 |  | 1368000 | 1362099.6914 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1362099.6914 | 1333889.1251 | 28210.5663 | 2.1149 | OK
7 | 11 kV RMU Hygene Express -1 (=F4) |  | 11 |  | 041808902748 | 1 | 16.81 | 27.37 | 10.56 | 60000 |  | 633600 | 630867.2255 | Sytalakhya |  |  |  | 11 kV RMU Hygene Express -1 (=F4) | 630867.2255 | 622521.8844 | 8345.3411 | 1.3406 | OK
8 | 11 kV Outgoing Feeder-5 (=F5) |  | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) |  | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 |  | 041808902786 | 1 | 415.39 | 432.02 | 16.63 | 60000 |  | 997800 | 993496.3977 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 993496.3977 | 1029880.865 | -36384.4673 | -3.5329 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 |  | 041808902789 | 1 | 244.79 | 248.97 | 4.18 | 60000 |  | 250800 | 249718.2768 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 249718.2768 | 378348.2521 | -128629.9753 | -33.9978 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) |  | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) |  | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) |  | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) |  | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907976 | 1 | 2097.69 | 2143.63 | 45.94 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 3889750.4784 | 3906600 | 3889750.4784 | -0.43131
-0.43131
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 22446093.7993
[6 empty] | Total = |  |  | 22446093.7993 | 18556343.3209
33 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 40972 | 41249 | 277 | 6000 | 0 | 1662000 | 1659287.3487
FROM Kazla 33 KV SIDE
| 33 kV Amulia Feeder | 0 | 33 | Main | 41812909523 | 1 | 32.61 | 40.74 | 8.13 | 360000 | 0 | 2926800 | 2922917.0149
|  |  | 10: Total |  | 4588800 | 4582204.3637
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving |  | 33 |  | 30799095 | 1 | 1446.3 | 1455.61 | 9.31 | 180000 | 1675800
| 33 kV Kazla |  |  |  | 952612101236 | 1 | 66.15 | 82.32 | 16.17 | 240000 | 3880800
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 5556600 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AMULIA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transformer, T-1 |  | 33 |  | DHKA2194 | 1 | 434.7591 | 444.2407 | 9.4816 | 240000 |  | 2275584
4 | 33/11 kV Transformer, T-2 |  | 33 |  | DHKA2198 | 1 | 612.319 | 621.8955 | 9.5765 | 240000 |  | 2298360
|  |  | 10: Total |  | 4573944 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 4: 4582204.3637; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4582204.3637
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4582204.3637 | 33 KV TX HV SIDE |  | 4573944
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 8260.3637
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1803%
| TOTAL IMPORT |  | 4: 4582204.3637
11 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | HA021100461-02 | 1 | 36559402 | 38858595 | 2299193 | 1 | 2299193 |  | 2302121.7006
11 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | HA021100478-02 | 1 | 104888438 | 107165620 | 2277182 | 1 | 2277182 |  | 2280082.6631
|  |  | 7: 0; 8: 0; 10: Total | 4576375 |  | 4582204.3637
| AMULIA 11 KV SIDE |  | 7: 0; 8: 0
5 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 73882730 | 74325242 | 442512 | 1 |  | 442512 | 443229.6649 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 443229.6649 | 444985.9723 | -1756.3074 | -0.39469 | OK
6 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 20944489 | 21858886 | 914397 | 1 |  | 914397 | 915879.9668 | Demra |  |  |  | 11 kV Kayetpara Feeder | 915879.9668 | 960756.4223 | -44876.4555 | -4.671 | OK
8 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 3860132 | 4231387 | 371255 | 1 |  | 371255 | 371857.1004 | Demra |  |  |  | 11 kV Paity Feeder | 371857.1004 | 423117.4909 | -51260.3904 | -12.1149 | OK
9 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 76995070 | 78048613 | 1053543 | 1 |  | 1053543 | 1055251.6334 | Demra |  |  |  | 11 kV Bamuil Feeder | 1055251.6334 | 1731137.401 | -675885.7676 | -39.0429 | OK
12 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 17610226 | 18107260 | 497034 | 1 |  | 497034 | 497840.0885 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 497840.0885 | 496862.708 | 977.3805 | 0.19671 | OK
13 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra |  | 1 | 52653434 | 52789052 | 135618 | 1 |  | 135618 | 135837.9449 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 135837.9449 | 163268.6536 | -27430.7087 | -16.801 | OK
14 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 18396671 | 19548850 | 1152179 | 1 |  | 1152179 | 1154047.601 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1154047.601 | 1129687.3519 | 24360.2491 | 2.1564 | OK
15 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4573944 | 4566538 | 4573944 | 0.16192
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Mugdapara | at 33 KV level |  | 941069.7534
[6 empty] | Demra | at 33 KV level |  | 3632874.2466
[6 empty] | Total = |  |  | 4573944 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MOGBAZAR T&T 11 KV SIDE | [9 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder |  | 33 |  | 8993 841 | 1 | 96.731 | 198.152 | 101.421 | 36000 | 3585 | 3651156 | 3654741 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 3654741 | 1986206 | 1668535 | 84.0061 | FAULT
13 | 33 kV Mondol Para (Premire cement) Feeder |  | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 3651156 | 3654741 | 0.098188
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 3654741
[6 empty] | Total = |  |  | 3654741 | 0
Note on H481: User: Meter was faulty and New meter is installed properly in 12.07.23
Note on I481: User: Grid has no reading at FEB-24

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 |  | 132 | IMPORT | 50147584 | 1 | 3415.423 | 3451.422 | 35.999 | 1920000 | 0 | 69118080
| Maniknagar-2 |  | 132 |  | 50147585 | 1 | 3406.368 | 3427.255 | 20.887 | 1920000 | 0 | 40103040
|  |  | 9=8-7: Total Import/Export | 0 | 109221120
|  |  | 10: Net Total | 109221120
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 109221120
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 |  | 132 | EXPORT | 06604331 | 1 | 8991.16 | 9013.11 | 21.95 | 480000 |  | 10536000 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 |  | 132 |  | 06604334 | 1 | 9091.46 | 9113.63 | 22.17 | 480000 |  | 10641600
| 132kV Motijheel Circuit-1 |  | 132 |  | 06604332 | 1 | 1876.92 | 1883.29 | 6.37 | 1440000 |  | 9172800
| 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1.07 | 1671.56 | 1677.39 | 5.83 | 1440000 |  | 8982864
| 132 kV Kazla Circuit-1 |  | 132 |  | ABB03905 | 1 | 914884 | 935121 | 20237 | 1000 |  | 20237000
| 132 kV Kazla Circuit-2 |  | 132 |  | ABB03904 | 1 | 707711 | 731008.6 | 23297.6 | 1000 | From Downstream | 23297600 |  |  | R Phase PT Missing
| 132 KV Metro Rail -1 |  | 132 |  | 42627805 | 1 | 0.245 | 1.685 | 1.44 | 480000 |  | 691200 |  | Motijheel | KVARH Reading Shown Seperately
| 132 KV Metro Rail -2 |  | 132 |  | 42627793 | 1 | 2.335 | 2.335 | 0 | 480000 |  | 0 |  | Motijheel
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 83559064
| MANIKNAGAR 132 KV SIDE |  | 7: 0; 8: 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 13091000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) |  | 132 | Export | ABB03903 | 1 | 429427 | 442420 | 12993 | 1000 |  | 12993000 |  |  | 26084000
|  |  | 10: Total | 109643064 | 26084000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 4: 109221120; 6: EXPORT TO OTHER S/S; 9=8-7: 82867864 | 132 KV NET IMPORT |  | 25662056
| IMPORT-2 |  | 6: Motijheel NOCS; 9=8-7: 691200 | 33 KV NET IMPORT |  | 26097000
| IMPORT-3 |  | 6: 132 KV NET IMPORT; 9=8-7: 25662056 | LOSS UNITS=>(132 HV-33 LV) |  | -434944
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.695%
| 132 KV TOTAL IMPORT |  | 4: 109221120
KVARH For Metro Rail
|  | Previous | 3: Present; 4: Total KVARH; 5: Remark
| 132 KV Metro Rail -1 | 10.335 | 3: 10.335; 4: 0; 5: Leading PF
| 132 KV Metro Rail -2 | 12.829 | 3: 15.68; 4: 1368480; 5: Leading PF
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) |  | 33 | Digital | ABB03907 | 1 | 166078 | 179169 | 13091 | 1000 | 13091000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) |  | 33 | Digital | ABB03906 | 1 | 336757 | 349763 | 13006 | 1000 | 13006000
|  |  | 7: 0; 8: 0; 10: Total | 26097000
| Maniknagar 33 kV SIDE |  | 7: 0; 8: 0 |  |  |  |  | 4126429.8988
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 7176366.1627 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK00121 | 1 | 12396.1 | 12937.9 | 541.8 | 4444 |  | 2407759.2 | 2407426.0699 |  |  |  |  | 0 | 2407426.0699 | 2432374.7491 | -24948.6793 | -1.0257 | OK | 4161360.0577
7 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Digital | ABB03913 | 1 | 400778 | 400778 | 0 | 2000 | From Downstream | 4769600 | 4768940.0929 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 4768940.0929 | 4963184.789 | -194244.6961 | -3.9137 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 7177359.2 | 7176366.1627 |  |  |  |  | 33 KV Feeders | 7176366.1627 | 7395559.5381 | -219193.3754 | -2.9639 | OK
2 |  |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 6591987.8267 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder |  | 33 |  | DHK86054 | 1 | 2558.33 | 2574.8 | 16.47 | 270000 |  | 4446900 | 4446284.7406 |  |  |  |  | 33kV Motijheel-1 Feeder | 4446284.7406 | 4083759.1631 | 362525.5776 | 8.8773 | OK
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 |  | 5408352 | 5407603.7171 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 5407603.7171 | 5512943.0418 | -105339.3247 | -1.9108 | OK
|  |  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 9912980.2809 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 | Digital | ABB03918 | 1 | 320061 | 322314 | 2253 | 2000 |  | 4506000 | 4505376.5637 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 4505376.5637 | 5144322.92 | -638946.3562 | -12.4204 | OK
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 282362 | 283050 | 688 | 2000 |  | 1376000 | 1375809.6209 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 1375809.6209 | 1587977.615 | -212167.9941 | -13.3609 | OK
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 294508 | 295581 | 1073 | 2000 |  | 2146000 | 2145703.0861 |  | 1375809.6209 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 2145703.0861 | 1974405.6277 | 171297.4583 | 8.6759 | OK
12 | 33kV Water Treatment Plant |  | 33 | Digital | 80379618 | 1 | 22980 | 23500 | 520 | 2000 |  | 1040000 | 1039856.1088 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 1039856.1088 | 960032.0942 | 79824.0146 | 8.3147 | OK
|  |  | 10: Total |  | 18923252 | 18920633.8373 |  |  |  |  | 0 | 18920633.8373 | 19263440.4619 | -342806.6246 | -1.7796 | OK
|  |  | 9=8-7: Grand Total | 26097000 | 26100611.2 | 26097000 | -0.013836
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 1039856.1088
[6 empty] | Total = |  |  | 1039856.1088 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 |  | 11 | Import | 6604357 | 1 | 5659.68 | 5689.49 | 29.81 | 160000 | 4769600 |  | 4768940.0929
9 | 11kV 10/14 MVA Transformer T-1 |  | 11 | Import | DHK00121 | 1 | 12396.1 | 12937.9 | 541.8 | 4444 | 2407759.2 |  | 2407426.0699
|  |  | 7: 0; 8: 0; 10: Total | 7177359.2 |  | 7176366.1627
| MANIKNAGAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nearest Feeder | B2110N | 11 |  | HA021101060-02 | 1 | 83718205 | 84713406 | 995201 | 1 |  | 995201 | 992049.9593 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 992049.9593 | 1025794.0549 | -33744.0956 | -3.2896 | OK
2 | 11kV Spare |  | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | B2110C | 11 |  | HA021100937-02 | 1 | 81563466 | 82075352 | 511886 | 1 |  | 511886 | 510265.2484 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 510265.2484 | 511602.0618 | -1336.8134 | -0.2613 | OK
4 | 11 kV R K Mission Road Feeder | B2110R | 11 |  | HA021101035-02 | 1 | 21945140 | 22852524 | 907384 | 1 |  | 907384 | 904511.0086 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 904511.0086 | 935614.7008 | -31103.6922 | -3.3244 | OK
5 | 11 kV Janapath Feeder | B2110J | 11 |  | HA021100864-02 | 1 | 38085422 | 39323924 | 1238502 | 1 |  | 1238502 | 1234580.611 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 1234580.611 | 1290170.4571 | -55589.8461 | -4.3087 | OK
6 | 11 kV Dhalpur Feeder | B2110D | 11 |  | HA021100851-02 | 1 | 90597737 | 91088256 | 490519 | 1 |  | 490519 | 488965.9013 | Maniknagar |  | 11 |  | 11 kV Dhalpur Feeder | 488965.9013 | 486376.4127 | 2589.4886 | 0.5324 | OK
7 | 11kV WTP | B2110O | 11 |  | X0599387 | 1 | 3614.4 | 4237.1 | 622.7 | 1000 |  | 622700 | 620728.3852 | Maniknagar |  | 9 |  | 11kV WTP | 620728.3852 | 693300.0424 | -72571.6572 | -10.4676 | OK
10 | 11kV Kamalapur Water pumping | B2110F | 11 |  | HA021100474-02 | 1 | 7724215 | 7746131 | 21916 | 1 |  | 21916 | 21846.6088 | Maniknagar |  | 9.6667 |  | 11kV Kamalapur Water pumping | 21846.6088 | 21434.4004 | 412.2083 | 1.9231 | OK
11 | 11 kV Wasa Road Feeder | B2110A | 11 |  | HA021001011-02 | 1 | 30335894 | 31468609 | 1132715 | 1 |  | 1132715 | 1129128.5575 | Maniknagar |  |  |  | 11 kV Wasa Road Feeder | 1129128.5575 | 1149650.5718 | -20522.0142 | -1.7851 | OK
12 | 11kV Sutikhalpar Feeder | B2110K | 11 |  | HA021101047-02 | 1 | 85232802 | 86501631 | 1268829 | 1 |  | 1268829 | 1264811.5886 | Maniknagar |  |  |  | 11kV Sutikhalpar Feeder | 1264811.5886 | 1275488.8091 | -10677.2205 | -0.83711 | OK
13 | 11kV Spare |  | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare |  | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare |  | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 |  | 0.415 |  | AH14044078 | 1 | 428437 | 434808.3 | 6371.3 | 1 |  | 6371.3 | 6351.127 | Maniknagar |  |  |  | Axuxilary -1 | 6351.127 | 1388.5133 | 4962.6136 | 357.4048 | FAULT
| Axuxilary -2 |  | 0.415 |  | AH14044072 | 1 | 402099 | 405236.1 | 3137.1 | 1 |  | 3137.1 | 3127.1672 | Maniknagar |  |  |  | Axuxilary -2 | 3127.1672 | 4739.5139 | -1612.3467 | -34.0192 | OK
13 | AT-1 |  | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 7176366.1627 | 7199160.4 | 7176366.1627 | -0.31662
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 7176366.1627
[6 empty] | Total = |  |  | 7176366.1627 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder |  | 33 | 0 | DHK86054 | 1 | 2558.33 | 2574.8 | 16.47 | 270000 | 0 | 4446900 | 4446284.7406
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 294508 | 295581 | 1073 | 2000 | 0 | 2146000 | 2145703.0861
|  |  | 10: Total | 0 | 6592900 | 6591987.8267
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 |  | 33 | Import | DHK86054 | 1 | 2558.33 | 2574.8 | 16.47 | 270000 | 4446900
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) |  | 33 | Import | DHK68120 | 1 | 2225.42 | 2233.32 | 7.9 | 270000 | 2133000 |  |  |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 6579900 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33kV Biddyut Bhaban Circuit |  | 33 | Export |  | 1 | 509961 | 512289 | 2328 | 600 | Estimated | 1396800 |  |  | From remote end
|  |  | 7: 0; 8: 0; 10: Total |  | 1396800
[7 empty] | 0 | 0
| Motijheel 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK86053 | 1 | 3093.07 | 3108.33 | 15.26 | 180000 |  | 2746800
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) |  | 33 | Export | DHK86055 | 1 | 2411.78 | 2423.64 | 11.86 | 180000 |  | 2134800
|  |  | 10: Total | 6278400 | 4881600
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 4: 6579900; 6: EXPORT TO OTHER S/S; 9=8-7: 1396800 | 33 KV NET IMPORT |  | 5183100
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5183100 | 33 KV TX HV SIDE |  | 4881600
[11 empty] | LOSS UNITS=> |  | 301500
[11 empty] | LOSS % IN => |  | 5.817%
| TOTAL IMPORT |  | 4: 6579900
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 |  | 11 | Import | DHK86059 | 1 | 3497.76 | 3512 | 14.24 | 160000 | 2278400 |  | 2674179.1304 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 |  | 11 | Import | DHK86057 | 1 | 2705.23 | 2718.59 | 13.36 | 160000 | 2137600 |  | 2508920.8696
|  |  | 7: 0; 8: 0; 10: Total | 4416000 |  | 5183100
| MOTIJHEEL 11 KV SIDE |  | 7: 0; 8: 0
6 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 |  | DHK86058 | 1 | 1785.77 | 1796 | 10.23 | 60000 |  | 613800 | 620196.8668 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 620196.8668 | 596539.0356 | 23657.8312 | 3.9658 | OK
7 | 11kV Station Road Feeder | A175H | 11 |  | DHK86075 | 1 | 2384.56 | 2385.46 | 0.9 | 60000 |  | 54000 | 54562.7742 | Motijheel |  |  |  | 11kV Station Road Feeder | 54562.7742 | 52918.7854 | 1643.9888 | 3.1066 | OK
8 | 11kV Box Culvert Road Feeder | A175F | 11 |  | DHK86071 | 1 | 3323.76 | 3344.52 | 20.76 | 60000 |  | 1245600 | 1258581.3251 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1258581.3251 | 1222544.2131 | 36037.112 | 2.9477 | OK
9 | 11kV Mohamedan Club Feeder | A174V | 11 |  | DHK86062 | 1 | 1750.28 | 1758.05 | 7.77 | 60000 |  | 466200 | 471058.6173 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 471058.6173 | 431769.181 | 39289.4363 | 9.0996 | OK
10 | 11kV Amina Ahmed Co. |  | 11 |  | DHK95754 | 1 | 127579 | 129815 | 2236 | 60 |  | 134160 | 135558.1813 | Motijheel |  | 137 |  | 11kV Amina Ahmed Co. | 135558.1813 | 132597.6385 | 2960.5428 | 2.2327 | OK
11 | 11kV Bangabhaban -1 |  | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  | 0 |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | A175SB | 11 |  | DHK95753 | 1 | 98361 | 104817 | 6456 | 60 |  | 387360 | 391396.967 | Motijheel |  | 137 |  | 11kV Sonali Bank | 391396.967 | 295022.2287 | 96374.7383 | 32.6669 | OK
15 | 11kV NCC Bank Feeder | A133S | 11 |  | DHK68123 | 1 | 340.63 | 343.14 | 2.51 | 60000 |  | 150600 | 152169.5147 | Motijheel |  | 45.6667 |  | 11kV NCC Bank Feeder | 152169.5147 | 150938.8084 | 1230.7063 | 0.81537 | OK
16 | 11kV IFIC BANK Feeder |  | 11 |  | DHK68116 | 1 | 436.24 | 441.2 | 4.96 | 60000 |  | 297600 | 300701.5112 | Ramna |  | 45.6667 |  | 11kV IFIC BANK Feeder | 300701.5112 | 288046.5706 | 12654.9406 | 4.3934 | OK
17 | 11kV Arambagh Feeder | A174X | 11 |  | DHK68117 | 1 | 3472.29 | 3485.51 | 13.22 | 60000 |  | 793200 | 801466.5278 | Motijheel |  |  |  | 11kV Arambagh Feeder | 801466.5278 | 746275.1443 | 55191.3835 | 7.3956 | OK
18 | 11kV Nikotborti Feeder | A175K | 11 |  | DHK68114 | 1 | 1447.93 | 1450.29 | 2.36 | 60000 |  | 141600 | 143075.719 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 143075.719 | 129290.2144 | 13785.5047 | 10.6625 | OK
19 | 11kV Agrani Bank Feeder | A174O | 11 |  | DHK95756 | 1 | 386701 | 388991 | 2290 | 60 |  | 137400 | 138831.9477 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 138831.9477 | 134161.148 | 4670.7997 | 3.4815 | OK
20 | 11kV Bangladesh Bank-2 | A133D | 11 |  | DHK95755 | 1 | 552 | 552 | 0 | 60000 | Estimated | 706255.2 | 713615.6113 | Motijheel | 60 |  |  | 11kV Bangladesh Bank-2 | 713615.6113 | 495490.8554 | 218124.7559 | 44.022 | FAULT
21 | 11kV PDB Design Feeder 14 |  | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 |  | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT |  | 0.415 |  | ELIC5429 | 1 | 435945 | 437810 | 1865 | 1 |  | 1865 | 1884.4366 | Motijheel |  |  |  | 11/0.4 kV AT | 1884.4366 | 2306.1766 | -421.7401 | -18.2874 | OK
|  |  | 10: Grand Total | 5183100 | 5129640.2 | 5183100 | 1.0422
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 4882398.4888
[6 empty] | Ramna | at 33 KV level |  | 300701.5112
[6 empty] | Total = |  |  | 5183100 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 |  | 132 | 0 | 06604332 | 1 | 1876.92 | 1883.29 | 6.37 | 1440000 | 0 | 9172800
2 | 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1.07 | 1671.56 | 1677.39 | 5.83 | 1440000 | 0 | 8982864
|  |  | 9=8-7: Total Import/Export | 0 | 18155664
|  |  | 10: Net Total | 18155664
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 |  | 132 | Imp/Main | 41812909527 | 1 | 380.71 | 388.35 | 7.64 | 1200000 | 9168000
|  |  | 132 | Imp/Backup | 41812909575 | 1 | 380.8 | 388.88 | 8.08 | 1200000 | 9696000
5 | 132 kV Mniknagar Circuit-2 |  | 132 | Imp/Main | 41812909512 | 1 | 181.85 | 188.85 | 7 | 1200000 | 8400000
|  |  | 132 | Imp/Backup | 41812909591 | 1 | 181.89 | 188.89 | 7 | 1200000 | 8400000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 17568000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 17568000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1.4 | 44.12 | 45.2 | 1.08 | 1200000 |  | 1814400
|  |  | 132 | Exp/Backup | 41812909570 | 1.4 | 44.12 | 45.2 | 1.08 | 1200000 |  | 1814400
7 | 132 kV Bangabhaban Circuit-2 |  | 132 | Exp/Main | 41812909559 | 1 | 101.35 | 103.02 | 1.67 | 1200000 |  | 2004000
|  |  | 132 | Exp/Backup | 41812909569 | 1 | 101.36 | 103.03 | 1.67 | 1200000 |  | 2004000
|  |  | 7: 0; 8: 0; 10: Total |  | 3818400
| MOTIJHEEL 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41812909509 | 1 | 265.11 | 271.67 | 6.56 | 1200000 |  | 7872000
|  |  | 132 | Exp/Backup | 41812909594 | 1 | 265.11 | 271.67 | 6.56 | 1200000 |  | 7872000
6 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41812909508 | 1 | 152.05 | 157.39 | 5.34 | 1200000 |  | 6408000
|  |  | 132 | Exp/Backup | 41812909592 | 1 | 152.01 | 157.34 | 5.33 | 1200000 |  | 6396000
|  |  | 10: Total | 18098400 | 14280000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 4: 18155664; 6: EXPORT TO OTHER S/S; 9=8-7: 3818400 | 132 KV NET IMPORT |  | 14280000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 14280000 | 33 KV NET IMPORT |  | 14054400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 225600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.58%
| 132 KV TOTAL IMPORT |  | 4: 18155664
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41812909543 | 1 | 438.94 | 449.7 | 10.76 | 720000 | 7747200
|  |  | 33 | Backup | 41812909617 | 1 | 439.24 | 450.01 | 10.77 | 720000 | 7754400
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41812909468 | 1 | 250.8 | 259.56 | 8.76 | 720000 | 6307200
|  |  | 33 | Backup | 41812909600 | 1 | 250.76 | 259.51 | 8.75 | 720000 | 6300000
|  |  | 7: 0; 8: 0; 10: Total | 14054400 |  | 0
| MOTIJHEEL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) |  | 33 | Main | 41812909546 | 1 | 154.63 | 160.43 | 5.8 | 240000 |  | 1392000 | 1391049.8294 |  | 2887627.5768 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1391049.8294 | 1196188.3579 | 194861.4714 | 16.2902 | OK
|  |  | 33 | Backup | 41812909616 | 1 | 154.58 | 160.38 | 5.8 | 240000 |  | 1392000 | 1391049.8294 |  |  |  |  | 0 | 1391049.8294 | 1196188.3579 | 194861.4714 | 16.2902 | OK
17 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41812909482 | 1 | 257.19 | 263.43 | 6.24 | 240000 |  | 1497600 | 1496577.7474 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 1496577.7474 | 1687306.3423 | -190728.5949 | -11.3037 | OK
|  |  | 33 | Backup | 42003953371 | 1 | 257.24 | 263.48 | 6.24 | 240000 |  | 1497600 | 1496577.7474 |  |  |  |  | 0 | 1496577.7474 | 1684875.0652 | -188297.3177 | -11.1757 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 2889600 | 2887627.5768 |  |  |  |  | 33 KV Feeders | 2887627.5768 | 2883494.7003 | 4132.8765 | 0.14333 | OK
10 | 33 kV Spare Feeder 1 |  | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 |  | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 499.21 | 510.62 | 11.41 | 360000 |  | 4107600 | 4104796.1775 |  | 6946854.8805 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 4104796.1775 | 4288772.8931 | -183976.7157 | -4.2897 | OK
|  |  | 33 | Backup | 41812909610 | 1 | 499.4 | 510.8 | 11.4 | 360000 |  | 4104000 | 4101198.6348 |  |  |  |  | 0 | 4101198.6348 | 4146543.1798 | -45344.545 | -1.0936 | OK
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 300.28 | 306.56 | 6.28 | 360000 |  | 2260800 | 2259256.7918 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 2259256.7918 | 2272028.497 | -12771.7052 | -0.56213 | OK
|  |  | 33 | Backup | 41812909595 | 1 | 300.41 | 306.69 | 6.28 | 360000 |  | 2260800 | 2259256.7918 |  | 4219917.5427 | Kamlapur Railway 33/11 kv ss |  | 0 | 2259256.7918 | 2275675.4127 | -16418.6209 | -0.72148 | OK
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 132.19 | 137.64 | 5.45 | 360000 |  | 1962000 | 1960660.7509 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 1960660.7509 | 1965687.576 | -5026.8252 | -0.25573 | OK
|  |  | 33 | Backup | 41621865733 | 1 | 132.21 | 137.66 | 5.45 | 360000 |  | 1962000 | 1960660.7509 |  |  |  |  | 0 | 1960660.7509 | 1965687.576 | -5026.8252 | -0.25573 | OK
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 173.79 | 181.69 | 7.9 | 360000 |  | 2844000 | 2842058.7031 |  |  |  |  | 33 kV P & T - 2 Feeder | 2842058.7031 | 2582016.3336 | 260042.3694 | 10.0713 | OK
|  |  | 33 | Backup | 41812909598 | 1 | 173.74 | 181.64 | 7.9 | 360000 |  | 2844000 | 2842058.7031 |  |  |  |  | 0 | 2842058.7031 | 2582016.3336 | 260042.3694 | 10.0713 | OK
20 | 33 kV Spare Feeder 9 |  | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 |  | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) |  | 0.415 |  |  | 1 | 1564.41 | 1564.41 | 0 | 300 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 11174400 | 11166772.4232 |  |  |  |  | 0 | 11166772.4232 | 11108505.2997 | 58267.1235 | 0.52453 | OK
|  |  | 9=8-7: Grand Total | 14054400 | 14064000 | 14054400 | -0.068259
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) |  | 11 |  | 41812909493 | 1 | 147.31 | 152.83 | 5.52 | 250000 | 1380000 |  | 1392113.906
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) |  | 11 |  | 41812909496 | 1 | 245.68 | 251.61 | 5.93 | 250000 | 1482500 |  | 1495513.6708
|  |  | 7: 0; 8: 0; 10: Total | 2862500 |  | 2887627.5768
| MOTIJHEEL 11 kV SIDE |  | 7: 0; 8: 0
2 | 11 kV Central Weman | A1111CW | 11 |  | 41812909492 | 1 | 200.24 | 205.61 | 5.37 | 60000 |  | 322200 | 324540.8139 | Motijheel |  |  |  | 11 kV Central Weman | 324540.8139 | 349687.3512 | -25146.5373 | -7.1911 | OK
3 | 11 kV Spare Feeder 2 |  | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len |  | 11 |  | 41812909499 | 1 | 325.78 | 333.94 | 8.16 | 60000 |  | 489600 | 493156.9909 | Swamibag |  |  |  | 11 kV K. M. Das Len | 493156.9909 | 513488.2684 | -20331.2774 | -3.9594 | OK
5 | 11 kV Gopibag | A1111GP | 11 |  | 41812909517 | 1 | 49.57 | 54.64 | 5.07 | 60000 |  | 304200 | 306410.0422 | Motijheel |  |  |  | 11 kV Gopibag | 306410.0422 | 89569.0408 | 216841.0013 | 242.0937 | FAULT
6 | 11kV SPICE TV | B1111E | 11 |  | 41812909518 | 1 | 37.24 | 41.63 | 4.39 | 60000 |  | 263400 | 265313.6262 | Narinda |  |  |  | 11kV SPICE TV | 265313.6262 | 241713.7129 | 23599.9133 | 9.7636 | OK
7 | 11 kV Spare Feeder 6 |  | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 |  | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 |  | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 |  | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 |  | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 |  | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | A1111SK | 11 |  | 41812909473 | 1 | 424.77 | 430.33 | 5.56 | 60000 |  | 333600 | 336023.636 | Motijheel |  |  |  | 11 kV South Kamlapur | 336023.636 | 328828.8075 | 7194.8285 | 2.188 | OK
14 | 11 kV Spare Feeder 11 |  | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | A1111AC | 11 |  | 41812909514 | 1 | 239.5 | 246.18 | 6.68 | 60000 |  | 400800 | 403711.8504 | Motijheel |  |  |  | 11 kV Answer Camp | 403711.8504 | 409195.5496 | -5483.6992 | -1.3401 | OK
16 | 11 kV Shapla Chattar | A1111SC | 11 |  | 41812909516 | 1 | 232.07 | 240.26 | 8.19 | 60000 |  | 491400 | 494970.0681 | Motijheel |  |  |  | 11 kV Shapla Chattar | 494970.0681 | 628823.7456 | -133853.6775 | -21.2864 | OK
17 | 11 kV Sayedabad |  | 11 |  | 41812909497 | 1 | 128.21 | 132.57 | 4.36 | 60000 |  | 261600 | 263500.5491 | Swamibag |  |  |  | 11 kV Sayedabad | 263500.5491 | 322080.4551 | -58579.906 | -18.188 | OK
22 | 33/0.4 kV Aux Transformer |  | 0.415 |  | 41901920686 | 1 | 1564.41 | 1564.41 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 107.7691 | -107.7691 | -100 | CHECK
|  |  | 10: Total | 2887627.5768 | 2866800 | 2887627.5768 | 0.72651
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Motijheel | at 33 KV level |  | 1865656.4105
[7 empty] | Swamibag | at 33 KV level |  | 756657.54
[7 empty] | Narinda | at 33 KV level |  | 265313.6262
|  |  | 7: Total =; 10: 2887627.5768 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 499.21 | 510.62 | 11.41 | 360000 | 0 | 4107600 | 4104796.1775
0 | 0 |  | 33 | Backup | 41812909610 | 1 | 499.4 | 510.8 | 11.4 | 360000 | 0 | 4104000 | 4101198.6348
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 173.79 | 181.69 | 7.9 | 360000 | 0 | 2844000 | 2842058.7031
0 | 0 |  | 33 | Backup | 41812909598 | 1 | 173.74 | 181.64 | 7.9 | 360000 | 0 | 2844000 | 2842058.7031
|  |  | 10: Total | 0 | 6948000 | 6943257.3379
P&T 33 KV SIDE (Sending) | bar: 4
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 6943257.3379
P&T 33 KV SIDE (Receiving)
5 | 33 kV Bidyut Bhaban Circuit |  | 33 | Import | BD017079 | 1 | 15811 | 15811 | 0 | 1000 | 0
|  |  | 33 | Export | BD017079 | 1 | 4739 | 6498 | 1759 | 1000 |  | 1759000
7 | 33 kV Motijheel Circuit-1 |  | 33 | Import | BD017081 | 1 | 79164 | 83465 | 4301 | 1000 | 4301000
8 | 33 kV Motijheel Circuit-2 |  | 33 | Import | BD017082 | 1 | 21372.33 | 21372.33 | 0 | 1000 | 2844000
11 | 33 kV Kamlapur Circuit |  | 33 | Import | BD017085 | 1 | 12870 | 12870 | 0 | 1000 | 0
|  |  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 7145000 | 1759000 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33 kV Bidyut Bhaban Circuit |  | 33 | Import | BD017079 | 1 | 15811 | 15811 | 0 | 1000 | 0
| 33 kV Bidyut Bhaban Circuit |  | 33 | Export | BD017079 | 1 | 4739 | 6498 | 1759 | 1000 |  | 1759000
|  |  | 7: 0; 8: 0; 10: Total |  | 1759000
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | BD017080 | 1 | 70086 | 72956 | 2870 | 888.88 |  | 2551085.6
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | BD017084 | 1 | 29663 | 33018 | 3355 | 888.88 |  | 2982192.4
|  |  | 10: Total |  | 5533278 | 7292278
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Sending Side |  | 4: 6943257.3379; 6: EXPORT TO OTHER S/S; 9=8-7: 1759000 | 33 KV NET IMPORT |  | 5184257.3379
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 5184257.3379 | 33 KV TX HV SIDE |  | 5533278
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -349020.6621
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -6.732%
| TOTAL IMPORT |  | 4: 6943257.3379
11 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
P&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 |  | 11 | Import | BD014056 | 1 | 83013 | 85447 | 2434 | 1000 | 2434000 |  | 2373679.9023 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | BD014057 | 1 | 14592 | 17474 | 2882 | 1000 | 2882000 |  | 2810577.4356
|  |  | 7: 0; 8: 0; 10: Total | 5316000 |  | 5184257.3379
| P&T 11 KV SIDE |  | 7: 0; 8: 0
12 | Inner Circular Road Feeder | A161Z | 11 |  | BD014042 | 1 | 44268 | 44708 | 440 | 1000 |  | 440000 | 440281.5947 | Motijheel |  |  |  | Inner Circular Road Feeder | 440281.5947 | 440281.5307 | 0.064012 | 1.4539e-05 | OK
13 | NSI New Building Expres Feeder | D361NS | 11 |  | BD013982 | 1 | 11504 | 11706 | 202 | 1000 |  | 202000 | 202129.2776 | Ramna |  |  |  | NSI New Building Expres Feeder | 202129.2776 | 186034.4496 | 16094.828 | 8.6515 | OK
14 | Police Hospital RMU Feeder | D661H | 11 |  | BD014044 | 1 | 4203 | 4222 | 19 | 1000 |  | 19000 | 19012.1598 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 19012.1598 | 97151.3237 | -78139.1639 | -80.4304 | CHECK
15 | Kakrail 33/11 kV Substation U/G Feeder |  | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | D661J | 11 |  | BD014013 | 1 | 39937 | 40796 | 859 | 1000 |  | 859000 | 859549.7497 | Rajarbag |  |  |  | Jonaki O/H Feeder | 859549.7497 | 871261.3389 | -11711.5892 | -1.3442 | OK
17 | Nayapalton Overhead Feeder | D361N | 11 |  | BD014014 | 1 | 28341 | 28851 | 510 | 1000 |  | 510000 | 510326.3939 | Ramna |  |  |  | Nayapalton Overhead Feeder | 510326.3939 | 489890.7172 | 20435.6766 | 4.1715 | OK
18 | Masjid Gali Over Head Feeder | D361MG | 11 |  | BD014016 | 1 | 18062 | 18556 | 494 | 1000 |  | 494000 | 494316.154 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 494316.154 | 512628.2611 | -18312.107 | -3.5722 | OK
19 | Spare Feeder (Feeder-8) |  | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) |  | 11 |  | BD013988 | 1 | 13.18 | 13.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | D361MW | 11 |  | BD014015 | 1 | 26552 | 27093 | 541 | 1000 |  | 541000 | 541346.2335 | Ramna |  |  |  | Mid Way Over Head Feeder | 541346.2335 | 539499.9038 | 1846.3297 | 0.34223 | OK
24 | Palton Thana Over Head Feeder | D661F | 11 |  | BD014033 | 1 | 28700 | 29433 | 733 | 1000 |  | 733000 | 733469.1112 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 733469.1112 | 677992.2163 | 55476.8949 | 8.1825 | OK
25 | Police Hospital (South) U/G Feeder 7 |  | 11 |  | BD014034 | 1 | 13024 | 13181 | 157 | 1000 |  | 157000 | 157100.4781 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 157100.4781 | 53743.2854 | 103357.1927 | 192.3165 | FAULT
26 | China Town Express Feeder | D361CT | 11 |  | BD013943 | 1 | 7445 | 7603 | 158 | 1000 |  | 158000 | 158101.1181 | Ramna |  |  |  | China Town Express Feeder | 158101.1181 | 146760.5102 | 11340.6079 | 7.7273 | OK
27 | Fakirapul Bazar O/H Feeder | A161FB | 11 |  | BD014032 | 1 | 35244 | 36215 | 971 | 1000 |  | 971000 | 971621.4283 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 971621.4283 | 948775.6929 | 22845.7354 | 2.4079 | OK
28 | PWD Ouarter (RMU) | A161PW | 11 |  | BD013937 | 1 | 2954 | 3061 | 107 | 1000 |  | 107000 | 107068.4787 | Motijheel |  |  |  | PWD Ouarter (RMU) | 107068.4787 | 113687.7192 | -6619.2405 | -5.8223 | OK
29 | Postal Quarter RMU | A161PO | 11 |  | BD013945 | 1 | 3593 | 3710 | 117 | 1000 |  | 117000 | 117074.8786 | Motijheel |  |  |  | Postal Quarter RMU | 117074.8786 | 117821.8181 | -746.9395 | -0.63396 | OK
30 | 11/0.4 kV AT-1 |  | 0.415 |  | DHKH4409 | 1 | 1497 | 1535 | 38 | 100 |  | 3800 | 3802.432 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 3802.432 | 0 | 3802.432 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV AT-2 |  | 0.415 |  | DHKH4411 | 1 | 684 | 692 | 8 | 100 |  | 800 | 800.512 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 800.512 | 4030.7464 | -3230.2344 | -80.1399 | CHECK
|  |  | 10: Grand Total | 5316000 | 5312600 | 5316000 | 0.063999
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 1636046.3803
[6 empty] | Ramna | at 33 KV level |  | 1906219.1771
[6 empty] | Rajarbag | at 33 KV level |  | 1773734.4426
[6 empty] | Total = |  |  | 5316000 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 300.28 | 306.56 | 6.28 | 360000 | 0 | 2260800 | 2259256.7918
0 | 0 |  | 33 | Backup | 41812909595 | 1 | 300.41 | 306.69 | 6.28 | 360000 | 0 | 2260800 | 2259256.7918
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 132.19 | 137.64 | 5.45 | 360000 | 0 | 1962000 | 1960660.7509
0 | 0 |  | 33 | Backup | 41621865733 | 1 | 132.21 | 137.66 | 5.45 | 360000 | 0 | 1962000 | 1960660.7509
|  |  | 10: Total | 0 | 4222800 | 4219917.5427
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 |  | 33 | Import | 101 | 1 | 399.6 | 408 | 8.4 | 270000 | 2268000
6 | 33 kV Motijheel Circuit-2 |  | 33 | Import | 113 | 1 | 175.9 | 183.2 | 7.3 | 270000 | 1971000
|  |  | 7: 0; 8: 0; 10: Total | 4239000 | 0 | 0
[7 empty] | 0 | 0
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0
[7 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  | 7: 0; 8: 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | 103 | 1 | 388.6 | 398.1 | 9.5 | 240000 |  | 2280000
4 | 33 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | 104 | 1 | 204.9 | 213.1 | 8.2 | 240000 |  | 1968000
|  |  | 10: Total |  | 4248000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Kamalapur Railway 33 KV SIDE (Sending) |  | 4: 4219917.5427; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4219917.5427
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 4219917.5427 | 33 KV TX HV SIDE |  | 4248000
[11 empty] | LOSS UNITS=> |  | -28082.4573
[11 empty] | LOSS % IN => |  | -0.6655%
| TOTAL IMPORT |  | 4: 4219917.5427
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | 42 | 1 | 462.8 | 474.1 | 11.3 | 200000 | 2260000 |  | 2259955.8404
10 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | 64 | 1 | 243.1 | 252.9 | 9.8 | 200000 | 1960000 |  | 1959961.7023
|  |  | 7: 0; 8: 0; 10: Total | 4220000 |  | 4219917.5427
| KAMALAPUR RAILWAY 11 KV SIDE |  | 7: 0; 8: 0
1 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 494.8 | 507.4 | 12.6 | 40000 |  | 504000 | 509026.9426 | Rajarbag |  |  |  | Amtola O/H Feeder | 509026.9426 | 489447.7453 | 19579.1973 | 4.0003 | OK
2 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 86 | 87.8 | 1.8 | 40000 |  | 72000 | 72718.1347 | Rajarbag |  |  |  | Police Telecom | 72718.1347 | 84945.4765 | -12227.3418 | -14.3943 | OK
3 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 362.6 | 373.7 | 11.1 | 40000 |  | 444000 | 448428.4971 | Rajarbag |  |  |  | Railway Colony O/H | 448428.4971 | 428772.405 | 19656.0921 | 4.5843 | OK
4 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 828.8 | 846.8 | 18 | 40000 |  | 720000 | 727181.3466 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 727181.3466 | 691698.8798 | 35482.4668 | 5.1298 | OK
5 | 11 KV Majar Feeder |  | 11 |  | 96 | 1 | 89 | 94.3 | 5.3 | 40000 |  | 212000 | 214114.5076 | Motijheel |  |  |  | 11 KV Majar Feeder | 214114.5076 | 210341.1798 | 3773.3278 | 1.7939 | OK
7 | 11 kV Feeder-6 |  | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 377.6 | 384.2 | 6.6 | 40000 |  | 264000 | 266633.1604 | Rajarbag |  |  |  | Momenbagh O/H | 266633.1604 | 262926.4748 | 3706.6856 | 1.4098 | OK
9 | 11 kV Feeder-8 |  | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 248.2 | 252.9 | 4.7 | 40000 |  | 188000 | 189875.1294 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 189875.1294 | 177980.9983 | 11894.1311 | 6.6828 | OK
12 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 402.3 | 413.2 | 10.9 | 40000 |  | 436000 | 440348.7043 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 440348.7043 | 448997.5185 | -8648.8141 | -1.9262 | OK
13 | 11 kV Feeder-11 |  | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway |  | 11 | Motijheel | 150 | 1 | 81.7 | 85 | 3.3 | 40000 |  | 132000 | 133316.5802 | Motijheel |  |  |  | Dhaka Railway | 133316.5802 | 133485.7487 | -169.1685 | -0.12673 | OK
15 | Jasimuddin Feeder-13 |  | 11 |  | 91 | 1 | 340.9 | 361.8 | 20.9 | 40000 |  | 836000 | 844338.3413 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 844338.3413 | 784734.4016 | 59603.9397 | 7.5954 | OK
16 | Police Box Feeder-14 |  | 11 |  | 18 | 1 | 146.7 | 155.9 | 9.2 | 40000 |  | 368000 | 371670.466 | Motijheel |  |  |  | Police Box Feeder-14 | 371670.466 | 364052.042 | 7618.424 | 2.0927 | OK
17 | 11 kV Feeder-15 |  | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 |  | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) |  | 0.415 |  | DHKF 7632 | 1 | 1106.01 | 1129.25 | 23.24 | 100 |  | 2324 | 2347.1798 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 2347.1798 | 2617.1297 | -269.9499 | -10.3147 | OK
20 | Auxiliary -1 (AT-2 ) |  | 0.415 |  | DHKF 7733 | 1 | 156.6 | 156.61 | 0.01 | 100 |  | 1 | 1.01 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 1.01 | 0 | 1.01 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4220000 | 4178325 | 4220000 | 0.99741
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Rajarbag | at 33 KV level |  | 2656560.1048
[6 empty] | Motijheel | at 33 KV level |  | 1563439.8952
[6 empty] | Total = |  |  | 4220000 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1.4 | 44.12 | 45.2 | 1.08 | 1200000 | 0 | 1814400 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 |  | 132 |  | 41812909559 | 1 | 101.35 | 103.02 | 1.67 | 1200000 | 0 | 2004000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
|  |  | 10: Total | 0 | 3818400 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
|  |  | 10: Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
BANGABHABAN 33 KV SIDE
|  |  | 3: 132; 4: NET IMPORT |  | 0
|  |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 4: 3818400; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 3818400
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 3818400 | 33 KV TX HV SIDE |  | 3818400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 3818400
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) |  | 11 | Import | 4150744 | 1 | 1534403 | 1536399.4 | 1996.4 | 1000 | 1996400 |  | 2327721.0785
12 | 11 kV 28/35 MVA Transformer (GT-1) |  | 11 | Import | 4150742 | 1 | 1448941.1 | 1450219.6 | 1278.5 | 1000 | 1278500 |  | 1490678.9215
|  |  | 7: 0; 8: 0; 10: Total | 3274900 |  | 3818400
| BANGABHABAN 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV DIT S/S-1 Feeder |  | 11 | Motijheel | 4150750 | 1 | 220648.42 | 221265.34 | 616.92 | 1000 | Estimated | 568927.8 | 573471.5104 | Motijheel | 50 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 573471.5104 | 671817.8752 | -98346.3648 | -14.6388 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 |  | 11 | Motijheel | 4150743 | 1 | 24395.39 | 24419.88 | 24.49 | 1000 |  | 24490 | 24685.588 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 24685.588 | 17985.9592 | 6699.6288 | 37.2492 | OK
3 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder |  | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation |  | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder |  | 11 | Ramna | 4150754 | 1 | 33909.49 | 33913.48 | 3.99 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 512035.02 | 516124.3594 | Motijheel | 45 | Meter Bad |  | 11 kV Modhumita via Ovisar | 516124.3594 | 610743.5229 | -94619.1636 | -15.4925 | OK
8 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16152.87 | 16186.18 | 33.31 | 1000 |  | 33310 | 33576.0285 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 33576.0285 | 25547.8952 | 8028.1333 | 31.4239 | OK
9 | 11 kV Motijheel-1 Feeder |  | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 252560.28 | 253417.92 | 857.64 | 1000 |  | 857640 | 864489.4944 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 864489.4944 | 644351.2568 | 220138.2376 | 34.1643 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 |  | 11 | Motijheel | 4150737 | 1 | 15369.61 | 15481.23 | 111.62 | 1000 |  | 111620 | 112511.447 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 112511.447 | 117285.3253 | -4773.8784 | -4.0703 | OK
14 | 11 kV Motijheel-2 Feeder |  | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 227571.12 | 229388.6042 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 229388.6042 | 305371.7615 | -75983.1573 | -24.8822 | OK
16 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 165578.1 | 165757.59 | 179.49 | 1000 |  | 179490 | 180923.487 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 180923.487 | 198307.5023 | -17384.0153 | -8.7662 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20826.96 | 20863.36 | 36.4 | 1000 | Estimated | 113785.56 | 114694.3021 | Motijheel | 10 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 114694.3021 | 183223.0569 | -68528.7548 | -37.4018 | OK
18 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82655.11 | 82655.11 | 0 | 1000 | Estimated | 170678.34 | 172041.4531 | Motijheel | 15 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 172041.4531 | 244297.4092 | -72255.9561 | -29.577 | OK
19 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 124388.29 | 124552.01 | 163.72 | 1000 |  | 163720 | 165027.5407 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 165027.5407 | 147502.9419 | 17524.5988 | 11.8808 | OK
20 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 274234.07 | 274721.65 | 487.58 | 1000 |  | 487580 | 491474.0307 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 491474.0307 | 449187.0294 | 42287.0013 | 9.4141 | OK
21 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 82533.39 | 82695.01 | 161.62 | 1000 |  | 161620 | 162910.7692 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 162910.7692 | 145072.6783 | 17838.0909 | 12.296 | OK
22 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 193032.75 | 193032.75 | 0 | 1000 | Estimated | 170678.34 | 172041.4531 | Motijheel | 15 | Meter Bad |  | 11 kV BCIC Feeder | 172041.4531 | 244297.4092 | -72255.9561 | -29.577 | OK
23 | 11/0.4 kV AT-1 |  | 0.415 |  | 63412931 | 1 | 94429.4 | 94429.4 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 0 | 2787.1709 | -2787.1709 | -100 | CHECK
24 | 11/0.4 kV AT-2 |  | 0.415 |  | 63403117 | 1 | 29520.2 | 34458 | 4937.8 | 1 | Estimated | 5000 | 5039.9322 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5039.9322 | 5021.2058 | 18.7264 | 0.37295 | OK
|  |  | 10: Grand Total | 3818400 | 3788146.18 | 3818400 | 0.79864
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 0
[6 empty] | Ramna | at 33 KV level |  | 0
[6 empty] | Swamibag | at 33 KV level |  | 0
[6 empty] | Motijheel | at 33 KV level |  | 3818400
[6 empty] | Total = |  |  | 3818400 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
0 | 132 kV Narinda Circuit-1 | 0 | 132 | EXPORT | 06604331 | 1 | 8991.16 | 9013.11 | 21.95 | 480000 | 0 | 10536000 | 0 | 0 | Wrong Reading by Grid
0 | 132 kV Narinda Circuit-2 | 0 | 132 |  |  | 1 | 9091.46 | 9113.63 | 22.17 | 480000 | 0 | 10641600 | 0 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 21177600
|  |  | 10: Net Total | 21177600
NARINDA 132 KV SIDE (RECEIVING)
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 21177600
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 21177600
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 4: 21177600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 21177600
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 21177600 | 33 KV NET IMPORT |  | 21216000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -38400
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.1813%
| 132 KV TOTAL IMPORT |  | 4: 21177600
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming |  | 33 | Import | 06604301 | 1 | 9457.3 | 9479.42 | 22.12 | 480000 | 10617600
7 | 132/33 kV 50/75 MVA GT-2 Incoming |  | 33 | Import | 06604304 | 1 | 9281.37 | 9303.45 | 22.08 | 480000 | 10598400
|  |  | 7: 0; 8: 0; 10: Total | 21216000 |  | 0
| NARINDA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 |  | 33 | Export | 06604300 | 1 | 9947.78 | 9972.7 | 24.92 | 180000 | From Downstream | 4556800 | 4564428.5454 |  | 9726656.1946 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 4564428.5454 | 4230443.444 | 333985.1015 | 7.8948 | OK
8 | 33 kV 20/28 MVA Transformer T-4 |  | 33 | Export | 06604303 | 1 | 10092.4 | 10121.14 | 28.74 | 180000 | From Downstream | 5153600 | 5162227.6492 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 5162227.6492 | 4763297.9206 | 398929.7285 | 8.3751 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 9710400 | 9726656.1946 |  |  |  |  | 33 KV Feeders | 9726656.1946 | 8993741.3646 | 732914.83 | 8.1492 | OK
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1058400 | 1060171.869 |  | 1060171.869 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1060171.869 | 1038580.344 | 21591.525 | 2.0789 | OK
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | From Downstream | 1570300 | 1572928.8415 |  |  |  |  | 33 kV Bangshal-1 Feeder | 1572928.8415 | 1592894.7654 | -19965.9239 | -1.2534 | OK
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  |  | 0 |  | 5102527.8727 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5806.36 | 5814.87 | 8.51 | 180000 |  | 1531800 | 1534364.3886 |  |  |  |  | 33 kV Kumertully-1 Feeder | 1534364.3886 | 2946288.4495 | -1411924.0609 | -47.9221 | CHECK
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5731.83 | 5752.51 | 20.68 | 180000 |  | 3722400 | 3728631.6752 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 3728631.6752 | 4895904.1829 | -1167272.5077 | -23.8418 | OK
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder |  | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 3523700 | 3529599.0312 |  | 5262996.0638 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 3529599.0312 | 3169390.8937 | 360208.1375 | 11.3652 | OK
|  |  | 10: Total |  | 11406600 | 11425695.8054 |  |  |  |  | 0 | 11425695.8054 | 13643058.6354 | -2217362.83 | -16.2527 | OK
|  |  | 9=8-7: Grand Total | 21152352 | 21117000 | 21152352 | 0.16741
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 | Import | 06604351 | 1 | 11188.32 | 11216.8 | 28.48 | 160000 | 4556800 |  | 4564428.5454
9 | 33/11 kV 20/28 MVA T-4 Incoming |  | 11 | Import | 06604295 | 1 | 11536.11 | 11568.32 | 32.21 | 160000 | 5153600 |  | 5162227.6492
|  |  | 7: 0; 8: 0; 10: Total | 9710400 |  | 9726656.1946
| NARINDA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bonogram Feeder | B124B | 11 |  | 06604467 | 1 | 25406.9 | 25482.9 | 76 | 8000 |  | 608000 | 614884.5864 | Narinda |  |  |  | 11 kV Bonogram Feeder | 614884.5864 | 513078.8188 | 101805.7676 | 19.8421 | OK
2 | 11 kV Sha Saheb Len Feeder | B524H | 11 |  | 06604469 | 1 | 17141.59 | 17196.38 | 54.79 | 8000 |  | 438320 | 443283.2433 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 443283.2433 | 384423.798 | 58859.4453 | 15.3111 | OK
3 | 11 kV Sadiabad Water Treatment | B224W | 11 |  | 06604354 | 1 | 543.82 | 543.82 | 0 | 40000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 0 | 405.5959 | -405.5959 | -100 | CHECK
4 | 11 kV Manashi Feeder | B124M | 11 |  | 06604353 | 1 | 5664.95 | 5680.64 | 15.69 | 40000 |  | 627600 | 634706.5237 | Narinda |  |  |  | 11 kV Manashi Feeder | 634706.5237 | 510239.6475 | 124466.8763 | 24.3938 | OK
5 | 11 kV Jatrabari Feeder | B524E | 11 |  | 06604324 | 1 | 3673.34 | 3702.77 | 29.43 | 40000 |  | 1177200 | 1190529.8275 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 1190529.8275 | 1049276.6041 | 141253.2234 | 13.462 | OK
6 | 11 kV Wari Feeder | B124W | 11 |  | 06604291 | 1 | 8754.52 | 8775.32 | 20.8 | 40000 |  | 832000 | 841421.013 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 841421.013 | 870408.8104 | -28987.7974 | -3.3304 | OK
7 | 11 kV Narinda Feeder | B124N | 11 |  | 06604348 | 1 | 7483.85 | 7504.19 | 20.34 | 40000 |  | 813600 | 822812.6637 | Narinda |  |  |  | 11 kV Narinda Feeder | 822812.6637 | 799429.5271 | 23383.1365 | 2.925 | OK
10 | 11 kV Distillary Feeder | B524D | 11 |  | 06604347 | 1 | 6158.21 | 6176.79 | 18.58 | 40000 |  | 743200 | 751615.501 | Swamibag |  |  |  | 11 kV Distillary Feeder | 751615.501 | 707359.2569 | 44256.2441 | 6.2565 | OK
11 | 11 kV Thatari Bazar Feeder | B124T | 11 |  | 06604296 | 1 | 5158.07 | 5173.07 | 15 | 40000 |  | 600000 | 606793.9997 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 606793.9997 | 510645.2434 | 96148.7564 | 18.8289 | OK
12 | 11 kV Swamibagh Feeder | B524C | 11 |  | 06604352 | 1 | 7958.04 | 7977.17 | 19.13 | 40000 |  | 765200 | 773864.6143 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 773864.6143 | 753191.5941 | 20673.0203 | 2.7447 | OK
13 | 11 kV Tipu Sultan Feeder | B124S | 11 |  | 06604322 | 1 | 6516.74 | 6533.9 | 17.16 | 40000 |  | 686400 | 694172.3357 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 694172.3357 | 672478.0091 | 21694.3266 | 3.226 | OK
14 | 11 kV Spare |  | 11 |  | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | B124F | 11 |  | DHK00089 | 1 | 48074.3 | 50229.8 | 2155.5 | 444.44 |  | 957990.42 | 968838.0644 | Narinda |  |  |  | 11 kV Folder Street Feeder | 968838.0644 | 873509.6438 | 95328.4207 | 10.9133 | OK
16 | 11 kV Bhajohari Feeder | B124V | 11 |  | DHK27842 | 1 | 443129 | 448780 | 5651 | 80 |  | 452080 | 457199.0523 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 457199.0523 | 433419.7832 | 23779.2691 | 5.4864 | OK
17 | 11 kV Lal mohon shaha Feeder | B124L | 11 |  | DHK00086 | 1 | 46086.3 | 47411.7 | 1325.4 | 444.44 |  | 589060.776 | 595730.9073 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 595730.9073 | 558545.0408 | 37185.8665 | 6.6576 | OK
18 | 11 kV Dupkhola Feeder | B524A | 11 |  | 8838024/8838029 | 1 | 39744.7 | 40071.8 | 327.1 | 1000 |  | 327100 | 330803.8622 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 330803.8622 | 357329.9916 | -26526.1294 | -7.4234 | OK
1 | 11/0.4 kV Aux Transformer-1 |  | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 |  | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 9726656.1946 | 9617751.196 | 9726656.1946 | 1.1323
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Narinda | at 33 KV level |  | 6236559.1463
[6 empty] | Maniknagar | at 33 KV level |  | 0
[6 empty] | Swamibag | at 33 KV level |  | 3490097.0483
[6 empty] | Total = |  |  | 9726656.1946 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5806.36 | 5814.87 | 8.51 | 180000 | 0 | 1531800 | 1534364.3886
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5731.83 | 5752.51 | 20.68 | 180000 | 0 | 3722400 | 3728631.6752
| MITFORD 33 KV SIDE | [10 empty] | 5254200 | 5262996.0638 | bar: 4
1 | Kumartuly Circuit-1 |  | 33 | 0 | DHK-66493 | 1 | 1305659 | 1317957 | 12298 | 180 | 0 | 2214972 | 2214972
6 | Kumartuly Circuit-2 |  | 33 | 0 | DHK-60914 | 1.1 | 799785.6 | 800133.2 | 347.6 | 180 | 0 | 68824.8 | 68824.8
|  |  | 10: Total |  | 2283796.8 | 2283796.8
| KUMERTULY 33 KV SIDE (RECEIVING) | [10 empty] | 7537996.8 | 7546792.8638
5 | 33 kV Mitford Circuit-1 |  | 33 | Import | DHK60965 | 1 | 300007 | 312312.4 | 12305.4 | 180 | 2214972
6 | 33 kV Narinda Circuit-1 |  | 33 | Import | DHK60959 | 1 | 28445.4 | 31318.8 | 2873.4 | 540 | 1551636
9 | 33 kV Mitford Circuit-2 |  | 33 | Import | DHK86072 | 1 | 1800.87 | 1801.22 | 0.35 | 180000 | 63000
10 | 33 kV Narinda Circuit-2 |  | 33 | Import | DHK60957 | 1 | 957187.2 | 964112.2 | 6925 | 540 | 3739500
|  |  | 7: 0; 8: 0; 10: Total | 7569108 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
|  |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 2277972
[7 empty] | 0 | 0
| KUMERTULY 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK60960 | 1 | 256254.6 | 276165.6 | 19911 | 180 |  | 3583980
8 | 33/11 kV 20/28 MVA Transformer (T-2) |  | 33 | Export | DHK60958 | 1 | 459310.6 | 479733.5 | 20422.9 | 180 |  | 3676122
|  |  | 10: Total |  | 7260102
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 9824764.8638; 6: EXPORT TO OTHER S/S; 9=8-7: 2277972 | 33 KV NET IMPORT |  | 7546792.8638
| MITFORD 33 KV SIDE |  | 6: 33 KV NET IMPORT; 9=8-7: 7546792.8638 | 33 KV TX HV SIDE |  | 7569108
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -22315.1362
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.2957%
| TOTAL IMPORT |  | 4: 9824764.8638
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 | Import | 06604403 | 1 | 7379.66 | 7401.91 | 22.25 | 160000 | 3583980 |  | 3730913.334 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 | Import | 06604410 | 1 | 6850.7 | 6873.61 | 22.91 | 160000 | 3665600 |  | 3815879.5298
|  |  | 7: 0; 8: 0; 10: Total | 7249580 |  | 7546792.8638
| KUMERTULY 11 KV SIDE |  | 7: 0; 8: 0
11 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 64111.2 | 64292.9 | 181.7 | 2222.22 |  | 403777.374 | 408963.7094 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 408963.7094 | 377524.4019 | 31439.3075 | 8.3278 | OK
12 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4753.64 | 4774.93 | 21.29 | 40000 |  | 851600 | 862538.4119 | Banglabazar |  |  |  | 11kV Islampur Feeder | 862538.4119 | 790375.0918 | 72163.3201 | 9.1303 | OK
13 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5212.68 | 5222.65 | 9.97 | 40000 |  | 398800 | 403922.4033 | Banglabazar |  | 95 |  | 11kV Majar O/H Feeder | 403922.4033 | 358783.3707 | 45139.0326 | 12.5811 | OK
15 | 11kV Spare |  | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  | 30 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5586.22 | 5605.76 | 19.54 | 40000 |  | 781600 | 791639.2939 | Banglabazar |  | 65 |  | 11kV Sadarghat Feeder | 791639.2939 | 664173.9512 | 127465.3427 | 19.1916 | OK
17 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.96 | 1020.13 | 6.17 | 40000 | 255057 | 246800 | 249970.0329 | Bangshal | Import From Banglabazar | 21.6667 |  | 11kV Mitford Hospital Feeder | 249970.0329 | 10516.7617 | 239453.2712 | 2276.8727 | FAULT
18 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4230.07 | 4248.01 | 17.94 | 40000 |  | 717600 | 726817.2432 | Banglabazar |  | 51.6667 |  | 11kV Zindabahar Feeder | 726817.2432 | 744667.6274 | -17850.3842 | -2.3971 | OK
21 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 739606.14 | 749106.042 | Banglabazar | 65 |  |  | 11kV Police fari Feeder | 749106.042 | 688791.1664 | 60314.8757 | 8.7566 | OK
22 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 6038.9 | 6057.45 | 18.55 | 40000 |  | 742000 | 751530.6501 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 751530.6501 | 663364.9696 | 88165.6805 | 13.2907 | OK
23 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8428.9 | 8456.57 | 27.67 | 40000 |  | 1106800 | 1121016.3389 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1121016.3389 | 1098192.6173 | 22823.7217 | 2.0783 | OK
24 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3809.84 | 3814.8 | 4.96 | 40000 |  | 198400 | 200948.3571 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 200948.3571 | 188088.2383 | 12860.1188 | 6.8373 | OK
25 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7366.02 | 7385.57 | 19.55 | 40000 |  | 782000 | 792044.4317 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 792044.4317 | 802914.3077 | -10869.8759 | -1.3538 | OK
26 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3622.49 | 3627.41 | 4.92 | 40000 |  | 196800 | 199327.8058 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 199327.8058 | 195773.5642 | 3554.2417 | 1.8155 | OK
27 | 11/0.4 kV AT-1 |  | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 |  | 0.415 |  | 05378636 | 1 | 180125 | 181249.2 | 1124.2 | 2 |  | 2248.4 | 2277.2797 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 2277.2797 | 2284.5642 | -7.2846 | -0.31886 | OK
|  |  | 10: Grand Total | 7260102 | 7168031.914 | 7260102 | 1.2845
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 505027.0329
[6 empty] | Banglabazar | at 33 KV level |  | 6755074.9671
[6 empty] | Total = |  |  | 7260102 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | From Downstream | 1570300 | 1572928.8415
11 | 33 kV Bangshal-2 Feeder |  | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 3523700 | 3529599.0312
|  |  | 10: Total | 0 | 5094000 | 5102527.8727
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 |  | 33 | Import | Mat-152447/1191738/007 | 1 | 131822700 | 133393000 | 1570300 | 1 | 1570300
5 | 33 kV Narinda Circuit-2 |  | 33 | Import | Mat-152447/1191738/002 | 1 | 266105400 | 269629100 | 3523700 | 1 | 3523700
|  |  | 7: 0; 8: 0; 10: Total | 5094000 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) |  | 33 | Export | Mat-152447/1191738/009 | 1 | 139067200 | 140647800 | 1580600 | 1 |  | 1580600 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) |  | 33 | Export | Mat-152447/1191738/004 | 1 | 263635200 | 267170700 | 3535500 | 1 |  | 3535500 |  |  | #VALUE!
|  |  | 10: Total |  | 5116100
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 5102527.8727; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5102527.8727
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5102527.8727 | 33 KV TX HV SIDE |  | 5116100
[11 empty] | LOSS UNITS=> |  | -13572.1273
[11 empty] | LOSS % IN => |  | -0.266%
| TOTAL IMPORT |  | 4: 5102527.8727
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 |  | 11 | Import | 340180016886 | 1 | 139111708 | 140698927 | 1587219 | 1 | 1587219 |  | 1578076.5274 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 |  | 11 | Import | 340180012685 | 1 | 267075769 | 270620639 | 3544870 | 1 | 3544870 |  | 3524451.3453
|  |  | 7: 0; 8: 0; 10: Total | 5132089 |  | 5102527.8727
| BANGSHAL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 42162552 | 42601022 | 438470 | 1 |  | 438470 | 435555.0089 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 435555.0089 | 420582.2469 | 14972.762 | 3.56 | OK
2 | 11 kV Spare Feeder |  | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder |  | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 56411721 | 57130789 | 719068 | 1 |  | 719068 | 714287.5661 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 714287.5661 | 683565.1793 | 30722.3868 | 4.4944 | OK
5 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 24405397 | 24842589 | 437192 | 1 |  | 437192 | 434285.5051 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 434285.5051 | 548862.4638 | -114576.9587 | -20.8753 | OK
8 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 54134428 | 55139107 | 1004679 | 1 |  | 1004679 | 997999.7965 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 997999.7965 | 824147.9865 | 173851.81 | 21.0947 | OK
9 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 67942920 | 68550161 | 607241 | 1 |  | 607241 | 603204.0029 | Bangshal |  |  |  | 11 kV French Road Feeder | 603204.0029 | 582791.0148 | 20412.9881 | 3.5026 | OK
10 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 33735643 | 34106584 | 370941 | 1 |  | 370941 | 368474.9482 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 368474.9482 | 314720.5073 | 53754.441 | 17.0801 | OK
11 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 70381721 | 71284889 | 903168 | 1 |  | 903168 | 897163.6515 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 897163.6515 | 788002.5988 | 109161.0527 | 13.8529 | OK
12 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 56327460 | 56981121 | 653661 | 1 |  | 653661 | 649315.3982 | Narinda |  |  |  | 11 kV Suritolla Feeder | 649315.3982 | 596681.6516 | 52633.7466 | 8.8211 | OK
13 | AT-1 |  | 0.415 |  | DHK-4415 | 1 | 823.77 | 823.77 | 0 | 100 |  | 0 | 0 | Bangshal |  |  |  | AT-1 | 0 | 2433.7995 | -2433.7995 | -100 | CHECK
14 | AT-2 |  | 0.415 |  | DHK-4410 | 1 | 791.91 | 814.48 | 22.57 | 100 |  | 2257 | 2241.9952 | Bangshal |  |  |  | AT-2 | 2241.9952 | 498.2107 | 1743.7845 | 350.0094 | FAULT
|  |  | 10: Grand Total | 5102527.8727 | 5136677 | 5102527.8727 | -0.66481
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 3738924.9083
[6 empty] | Banglabazar | at 33 KV level |  | 714287.5661
[6 empty] | Narinda | at 33 KV level |  | 649315.3982
[6 empty] | Total = |  |  | 5102527.8727 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING) Maniknagar 132
0 | 132 kV Kazla Circuit-1 | 0 | 132 | 0 | ABB03905 | 1 | 914884 | 935121 | 20237 | 1000 | 0 | 20237000
0 | 132 kV Kazla Circuit-2 | 0 | 132 |  |  | 1 | 707711 | 731008.6 | 23297.6 | 1000 | From Downstream | 23297600
|  |  | 9=8-7: Total Import/Export | 0 | 43534600
|  |  | 10: Net Total | 43534600
KAZLA 132 KV SIDE (RECEIVING)
3 | 132kV Maniknagar Circuit-1 |  | 132 | Main | 41812909505 | 1 | 764.81 | 781.67 | 16.86 | 1200000 | 20232000
|  |  | 132 | Backup | 41812909603 | 1 | 764.77 | 781.64 | 16.87 | 1200000 | 20244000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 |  | 132 | Main | 41812909540 | 1 | 588.58 | 607.96 | 19.38 | 1200000 | 23256000
|  |  | 132 | Backup | 41812909587 | 1 | 588.6 | 607.98 | 19.38 | 1200000 | 23256000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 43488000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 43488000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| KAZLA 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Main | 41812909542 | 1 | 765.54 | 782.42 | 16.88 | 1200000 |  | 20256000 |  |  | #DIV/0!
|  |  | 132 | Backup | 41812909589 | 1 | 765.99 | 782.88 | 16.89 | 1200000 |  | 20268000
7 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Main | 41812909501 | 1 | 588.06 | 607.43 | 19.37 | 1200000 |  | 23244000 |  |  | 100
|  |  | 132 | Backup | 41812909606 | 1 | 587.99 | 607.36 | 19.37 | 1200000 |  | 23244000
|  |  | 10: Total |  | 43500000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) Maniknagar 132 |  | 4: 43534600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 43534600
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 43534600 | 33 KV NET IMPORT |  | 43358400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 176200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4047%
| 132 KV TOTAL IMPORT |  | 4: 43534600
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) |  | 33 | Main | 41812909533 | 1 | 1270.95 | 1298.96 | 28.01 | 720000 | 20167200
|  |  | 33 | Backup | 41812909582 | 1 | 1271.05 | 1299.05 | 28 | 720000 | 20160000
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) |  | 33 | Main | 41812909479 | 1 | 976.96 | 1009.17 | 32.21 | 720000 | 23191200
|  |  | 33 | Backup | 41812909622 | 1 | 976.82 | 1009.03 | 32.21 | 720000 | 23191200
|  |  | 7: 0; 8: 0; 10: Total | 43358400 |  | 0
| KAZLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 |  | 33 | Main | 41812909465 | 1 | 1288.22 | 1313.93 | 25.71 | 240000 |  | 6170400 | 6162213.7313 |  | 23717691.9403 | Kazla 33/11 kv ss | 0.76269 | 33/11 kV 20/28 MVA T-1 | 6162213.7313 | 6024981.507 | 137232.2244 | 2.2777 | OK
|  |  | 33 | Backup | 41812909596 | 1 | 1287.87 | 1313.58 | 25.71 | 240000 |  | 6170400 | 6162213.7313 |  |  |  |  | 0 | 6162213.7313 | 6022568.6189 | 139645.1124 | 2.3187 | OK
13 | 33/11 kV 28/35 MVA T-5 |  | 33 | Main | 41812909536 | 1 | 169 | 174.95 | 5.95 | 360000 |  | 2142000 | 2139158.209 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 2139158.209 | 1994251.9886 | 144906.2204 | 7.2662 | OK
|  |  | 33 | Backup | 41812909578 | 1 | 154.58 | 160.38 | 5.8 | 360000 |  | 2088000 | 2085229.8507 |  |  |  |  | 0 | 2085229.8507 | 1780711.3945 | 304518.4562 | 17.1009 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 | Main | 41812909554 | 1 | 1237.39 | 1260.25 | 22.86 | 240000 |  | 5486400 | 5479121.194 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 5479121.194 | 5856079.3422 | -376958.1481 | -6.437 | OK
|  |  | 33 | Backup | 41812909613 | 1 | 1236.17 | 1259 | 22.83 | 240000 |  | 5479200 | 5471930.7463 |  |  |  |  | 0 | 5471930.7463 | 5851253.566 | -379322.8198 | -6.4828 | OK
17 | 33/11 kV 20/28 MVA T-3 |  | 33 | Main | 41812909544 | 1 | 1093.06 | 1121.78 | 28.72 | 240000 |  | 6892800 | 6883655.3234 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 6883655.3234 | 6833299.0099 | 50356.3135 | 0.73693 | OK
|  |  | 33 | Backup | 41812909614 | 1 | 1093.09 | 1121.81 | 28.72 | 240000 |  | 6892800 | 6883655.3234 |  |  |  |  | 0 | 6883655.3234 | 6830886.1218 | 52769.2016 | 0.77251 | OK
22 | 33/11 kV 10/14 MVA T-4 |  | 33 | Main | 41812909506 | 1 | 577.89 | 590.63 | 12.74 | 240000 |  | 3057600 | 3053543.4826 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 3053543.4826 | 3066780.735 | -13237.2524 | -0.43163 | OK
|  |  | 33 | Backup | 41812909602 | 1 | 578.05 | 590.84 | 12.79 | 240000 |  | 3069600 | 3065527.5622 |  |  |  |  | 0 | 3065527.5622 | 3066780.735 | -1253.1728 | -0.040863 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 23749200 | 23717691.9403 |  |  |  |  | 33 KV Feeders | 23717691.9403 | 23775392.5826 | -57700.6423 | -0.24269 | OK
10 | 33 kV Shahriar Steel Feeder |  | 33 | Main | 41812909534 | 1 | 692.92 | 710.82 | 17.9 | 360000 |  | 6444000 | 6435450.7463 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 6435450.7463 | 7271238.1943 | -835787.4481 | -11.4944 | OK
|  |  | 33 | Backup | 41812909580 | 1 | 692.87 | 710.78 | 17.91 | 360000 |  | 6447600 | 6439045.9701 |  |  |  |  | 0 | 6439045.9701 | 7271238.1943 | -832192.2242 | -11.445 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | A418S | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 |  | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 |  | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 |  | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Amulia Feeder |  | 33 | Main | 41812909523 | 1 | 32.61 | 40.74 | 8.13 | 360000 |  | 2926800 | 2922917.0149 |  |  |  |  | 33 kV Amulia Feeder | 2922917.0149 | 3257398.8924 | -334481.8775 | -10.2684 | OK
|  |  | 33 | Backup | 41812909565 | 1 | 32.58 | 40.7 | 8.12 | 360000 |  | 2923200 | 2919321.791 |  |  |  |  | 0 | 2919321.791 | 3253779.5603 | -334457.7693 | -10.2791 | OK
21 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 806.02 | 834.62 | 28.6 | 360000 |  | 10296000 | 10282340.2985 | Kazla |  |  |  | 33 kV Zahir Steel | 10282340.2985 | 8831170.3306 | 1451169.9679 | 16.4324 | OK
|  |  | 33 | Backup | 41812909563 | 1 | 806.32 | 834.93 | 28.61 | 360000 |  | 10299600 | 10285935.5224 |  |  |  |  | 0 | 10285935.5224 | 8834789.6627 | 1451145.8597 | 16.4254 | OK
| Auxiliary Transformer-3 (AT-3) |  | 0.415 |  |  | 1 | 2995.78 | 3058.9 | 63.12 | 160 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 19666800 | 19640708.0597 |  |  |  |  | 0 | 19640708.0597 | 19359807.4174 | 280900.6423 | 1.4509 | OK
|  |  | 9=8-7: Grand Total | 43358400 | 43416000 | 43358400 | -0.13267
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | KAZLA at 33 KV level |  |  | 16717791.0448
[7 empty] | Kazla 33/11 KV Substation |  |  | 26640608.9552
|  |  | 9=8-7: Total =; 10: 43358400 | 0
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK-61009 | 1 | 8123956 | 8165919 | 41963 | 180 | 6170400 |  | 6162213.7313
30 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK-61124 | 1 | 62141.9 | 91940.2 | 29798.3 | 180 | 5363694 |  | 5479121.194
24 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 |  | DHK-61015 | 1 | 690839.9 | 729450.7 | 38610.8 | 180 | 6949944 |  | 6883655.3234
39 | 33/11 kV 10/14 MVA T-4 Incoming |  | 11 |  | 8L55984 | 1 | 34289.4 | 34993.9 | 704.5 | 4000 | 2818000 |  | 3053543.4826
42 | 33/11 kv 28/35 MVA T-5 Incomer |  | 11 |  | DHK00112 | 1 | 26833.3 | 29245.8 | 2412.5 | 888.8 | 2144230 |  | 2139158.209
|  |  | 7: 0; 8: 0; 10: Total | 23446268 |  | 23717691.9403
| KAZLA 11 kV SIDE |  | 7: 0; 8: 0 | [5 empty] | 120
17 | 11 kV Nayanagor Feeder | A418N | 11 |  | DHK-61125 | 1 | 978699.2 | 994230.3 | 15531.1 | 60 |  | 931866 | 938973.2616 | Kazla |  | 60 |  | 11 kV Nayanagor Feeder | 938973.2616 | 919761.8478 | 19211.4139 | 2.0887 | OK
18 | 11 kV Madrasa Bazar Feeder | A418B | 11 |  | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1024070.04 | 1031880.5339 | Kazla | 90 | 60 |  | 11 kV Madrasa Bazar Feeder | 1031880.5339 | 981079.3043 | 50801.2296 | 5.1781 | OK
19 | 11 kV Kazla Feeder | A418K | 11 |  | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 910284.48 | 917227.1412 | Kazla | 80 | 20 |  | 11 kV Kazla Feeder | 917227.1412 | 858444.3912 | 58782.75 | 6.8476 | OK
20 | 11 kV Sayedabad Feeder | B218S | 11 |  | HA021101239-02 | 1 | 36964704 | 36964704 | 0 | 1000 | Estimated | 796498.92 | 802573.7486 | Maniknagar | 70 | 80 |  | 11 kV Sayedabad Feeder | 802573.7486 | 797126.9347 | 5446.8139 | 0.68331 | OK
21 | 11 kV Zenith Feeder | old | 11 |  | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | B318P | 11 |  | HA-021200060 | 1 | 124359.6 | 125421.6 | 1062 | 1000 |  | 1062000 | 1070099.7824 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 1070099.7824 | 981079.3043 | 89020.4782 | 9.0737 | OK
23 | 11 kV Matuail Feeder | A418M | 11 |  | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1365426.72 | 1375840.7118 | Kazla | 120 |  |  | 11 kV Matuail Feeder | 1375840.7118 | 1471618.9564 | -95778.2446 | -6.5084 | OK
25 | 11 kV Kutubkhali Feeder | B326C | 11 |  | DHK-61117 | 1 | 925127.6 | 950243.5 | 25115.9 | 60 |  | 1506954 | 1518447.4082 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 1518447.4082 | 1530760.1301 | -12312.7219 | -0.80435 | OK
26 | 11 kV Mridhabari Feeder | A418R | 11 |  | DHK-61118 | 1 | 765154.9 | 786583.2 | 21428.3 | 60 |  | 1285698 | 1295503.9078 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1295503.9078 | 1283193.2141 | 12310.6937 | 0.95938 | OK
27 | 11 kV Muslim Nagar Feeder | A418U | 11 |  | DHK-61011 | 1 | 257414.9 | 288975.2 | 31560.3 | 60 |  | 1893618 | 1908060.4612 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 1908060.4612 | 1919968.4246 | -11907.9634 | -0.62022 | OK
28 | 11 kV Jatrabari Thana Feeder | A418H | 11 |  | DHK-61010 | 1 | 121954 | 140076.8 | 18122.8 | 60 |  | 1087368 | 1095661.262 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 1095661.262 | 1033841.7159 | 61819.5461 | 5.9796 | OK
29 | 11 kV Mirhazirbag Feeder | B518D | 11 |  | DHK-61008 | 1 | 413011.9 | 432336.8 | 19324.9 | 60 |  | 1159494 | 1168337.3608 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 1168337.3608 | 1095285.787 | 73051.5737 | 6.6696 | OK
31 | 11 kV Mukti Sharani Feeder | B318T | 11 |  | DHK-61014 | 1 | 255768.2 | 277319.8 | 21551.6 | 60 |  | 1293096 | 1302958.3317 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 1302958.3317 | 1234586.0356 | 68372.296 | 5.5381 | OK
32 | 11 kV Kadamtali Feeder | B418K | 11 |  | DHK-61006 | 1 | 534192.9 | 557719.4 | 23526.5 | 60 |  | 1411590 | 1422356.0752 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 1422356.0752 | 1299375.4421 | 122980.6331 | 9.4646 | OK
33 | 11kV Rayerbagh Feeder | E218R | 11 |  | DHK-61012 | 1 | 500356.9 | 504174.2 | 3817.3 | 60 |  | 229038 | 230784.8531 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 230784.8531 | 763293.0113 | -532508.1583 | -69.7646 | CHECK
34 | 11 kV Donia Feeder | B318D | 11 |  | DHK-61013 | 1 | 2100163 | 2100163 | 0 | 60 |  | 0 | 0 | Jurain |  |  |  | 11 kV Donia Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Nimtoli Feeder | A418T | 11 |  | HA-021100855-02 | 1 | 37786069 | 38891345 | 1105276 | 1 |  | 1105276 | 1113705.8447 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1113705.8447 | 1180097.802 | -66391.9573 | -5.626 | OK
36 | 11 kV Gobindapur Feeder | A441G | 11 |  | HA-021101057-02 | 1 | 31752696 | 33259887 | 1507191 | 1 |  | 1507191 | 1518686.2158 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 1518686.2158 | 1374337.9751 | 144348.2407 | 10.5031 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 |  | 9A56136 | 1 | 4203 | 4323.9 | 120.9 | 10000 |  | 1209000 | 1218220.9387 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1218220.9387 | 1179639.0535 | 38581.8853 | 3.2707 | OK
38 | 11 kV Samad Nagar Gate (Old) | old | 11 |  | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | A418D | 11 |  | 8K55676 | 1 | 1252.4 | 1475.1 | 222.7 | 4000 |  | 890800 | 897594.0548 | Kazla |  |  |  | 11 kV Dharmik Para | 897594.0548 | 939274.9933 | -41680.9386 | -4.4376 | OK
41 | 11 kV Sheikhdi Feeder | A418I | 11 |  | 9A56133 | 2 | 17993.4 | 18085 | 91.6 | 4000 |  | 732800 | 738389.0024 | Kazla | CF due to 16 days Reading Freezing |  |  | 11 kV Sheikhdi Feeder | 738389.0024 | 942098.0612 | -203709.0588 | -21.6229 | OK
43 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 |  | T-5 Sum | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | A418Z | 11 |  | 61903661 | 1 | 23269.7 | 23269.7 | 0 | 2000 | 2126000 | 0 | 0 | Kazla |  |  |  | 11 kV Jenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
45 | 11 KV Samad Nagor Gate | A418A | 11 |  | 61903675 | 1 | 21504.2 | 22164 | 659.8 | 2000 |  | 1319600 | 1329664.4754 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1329664.4754 | 1206256.5501 | 123407.9253 | 10.2307 | OK
46 | 11 KV Bibir Bagicha | B218I | 11 |  | 61903557 | 1 | 39760.2 | 40163.4 | 403.2 | 2000 |  | 806400 | 812550.3433 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 812550.3433 | 773722.2305 | 38828.1128 | 5.0184 | OK
47 | 33/0.4 kV AT-1 |  | 0.415 |  | 503043 | 1 | 96242 | 96242 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 |  | 0.415 |  | 503044 | 1 | 96796 | 96796 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-2 | 0 | 2691.9968 | -2691.9968 | -100 | CHECK
23 | Auxiliary Transformer |  | 0.415 |  | 41901920685 | 1 | 2995.78 | 3058.9 | 63.12 | 160 |  | 10099.2 | 10176.2257 | Kazla |  |  |  | Auxiliary Transformer | 10176.2257 | 7859.4208 | 2316.8049 | 29.4781 | OK
|  |  | 10: Total | 23717691.9403 | 23538168.36 | 23717691.9403 | 0.76269
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 230784.8531
[6 empty] | Jurain | at 33 KV level |  | 3891505.5223
[6 empty] | Swamibag | at 33 KV level |  | 1168337.3608
[6 empty] | Maniknagar | at 33 KV level |  | 1615124.0918
[6 empty] | Shyampur | at 33 KV level |  | 1422356.0752
[6 empty] | Kazla | at 33 KV level |  | 15389584.0371
[6 empty] | Total = |  |  | 23717691.9403 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT |  | 132 |  | 8993532 | 1 | 2234.461 | 2234.461 | 0 | 960000 | 0 | 0
|  |  | 132 |  |  | 1 | 667.558 | 667.558 | 0 | 960000 | 0 | 0
1 | Tranformer - 1 at Shyampur 230/132 |  | 132 |  | 38992560 | 1 | 1669.918 | 1703.709 | 33.791 | 1920000 | 0 | 64878720
|  |  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 |  | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  |  | 132 |  | 38992559 | 1 | 1760.133 | 1793.761 | 33.628 | 1920000 | 0 | 64565760
| Aggrekko 100 MW (Brammhongao) |  | 132 |  | PN-1711A04601 | 1 | 23.277 | 37.391 | 14.114 | 960000 | 0 | 13549440
|  |  | 132 |  |  | 1 | 3.862 | 4.961 | 1.099 | 960000 | 1055040 | 0
| Madanganj-Fatullah Exp |  | 132 |  | 38992544 | 1 | 36.313 | 37.711 | 1.398 | 960000 | 0 | 1342080
| Madanganj-Fatullah Imp |  | 132 |  | 38992544 | 1 | 182.56 | 214.283 | 31.723 | 960000 | 30454080 | 0
|  |  | 9=8-7: Total Import/Export | 31509120 | 144336000
|  |  | 10: Net Total | 112826880
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) |  | 132 | Import | 08993727 | 1 | 9449.569 | 9506.982 | 57.413 | 720000 | 41337360
|  |  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) |  | 132 | Import | 08993726 | 1 | 7173.553 | 7233.435 | 59.882 | 720000 | 43115040
|  |  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 84452400 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 84452400
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 132 |  |  |  | 0 | 0
|  |  | 132 |  |  |  | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 29052000
| SHYAMPUR 132 KV SIDE |  | 7: 0; 8: 0
5 | 132 kV 80/120 MVA ( GT-1) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) |  | 132 | Export | ABB3902 | 1 | 2486388.1 | 2486388.1 | 0 | 1300 |  | 0
|  |  | 10: Total |  | 55400400
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 4: 112826880; 6: EXPORT TO OTHER S/S; 9=8-7: 28087200 | 132 KV NET IMPORT |  | 84739680
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 84739680 | 33 KV NET IMPORT |  | 81302784
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 3436896
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 4.056%
| 132 KV TOTAL IMPORT |  | 4: 112826880
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) |  | 33 | Import | BD001826 | 1 | 3638.31 | 3669.258 | 30.948 | 480000 | 14855040
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) |  | 33 | Import | BD001850 | 1 | 3693.7939 | 3741.7834 | 47.9895 | 480000 | 23034960
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) |  | 33 | Import | BD001835 | 1 | 3214.9541 | 3259.934 | 44.9799 | 480000 | 21590352
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) |  | 33 | Import | BD001831 | 1 | 4098.5898 | 4144.0532 | 45.4634 | 480000 | 21822432
|  |  | 7: 0; 8: 0; 10: Total | 81302784
| SHYAMPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) |  | 33 | Export | BD001808 | 1 | 2308.9079 | 2340.102 | 31.1941 | 240000 |  | 7486584 | 7489687.8251 |  | 23647855.9824 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7489687.8251 | 8049016.8666 | -559329.0415 | -6.949 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) |  | 33 | Export | BD001834 | 1 | 2120.76 | 2152.3378 | 31.5778 | 240000 |  | 7578672 | 7581814.0034 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7581814.0034 | 8012769.8801 | -430955.8767 | -5.3784 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) |  | 33 | Export | BD001846 | 1 | 1567.6729 | 1587.623 | 19.9501 | 240000 |  | 4788024 | 4790009.0427 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 4790009.0427 | 5096893.1833 | -306884.1406 | -6.021 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) |  | 33 | Export | BD001847 | 1 | 1389.81 | 1405.5799 | 15.7699 | 240000 |  | 3784776 | 3786345.1112 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 3786345.1112 | 3837760.7883 | -51415.6771 | -1.3397 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 23638056 | 23647855.9824 |  |  |  |  | 33 KV Feeders | 23647855.9824 | 24996440.7183 | -1348584.7359 | -5.3951 | OK
1 | 33 kV Rani RRM Feeder |  | 33 | Export | BD001809 | 1 | 795.3914 | 802.1699 | 6.7785 | 240000 |  | 1626840 | 1627514.4634 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 1627514.4634 | 2056494.036 | -428979.5726 | -20.8598 | OK
2 | 33 kV Postogola Feeder-1. |  | 33 | Export | BD001804 | 1 | 1564.546 | 1564.55 | 0.004 | 240000 |  | 960 | 960.398 |  | 960.398 | Postogola 33/11 kv s/s | Grid Has No Reading | 33 kV Postogola Feeder-1. | 960.398 | 480.4107 | 479.9873 | 99.9119 | FAULT
5 | 33 kV Prime Textile Feeder. |  | 33 | Export | BD001810 | 1 | 510.637 | 510.637 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 120.1027 | -120.1027 | -100 | CHECK
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1433.9139 | 1460.4226 | 26.5087 | 240000 | From Downstream | 6362088 | 6364725.626 |  | 11318458.518 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 6364725.626 | 5148537.3324 | 1216188.2936 | 23.622 | OK
7 | 33 kV Nondolalpur -2 feeder |  | 33 | Export | BD001807 | 1 | 1242.769 | 1263.401 | 20.632 | 240000 |  | 4951680 | 4953732.892 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 4953732.892 | 4843980.9761 | 109751.9159 | 2.2657 | OK
8 | 33 kV Postogola Feeder-2. |  | 33 | Export | BD001830 | 1 | 2131.902 | 2131.902 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Postogola Feeder-2. | 0 | 1441.2321 | -1441.2321 | -100 | CHECK
11 | 33 kV Rahima Steel feeder |  | 33 | Export | BD001803 | 1 | 690.9685 | 702.6719 | 11.7034 | 240000 |  | 2808816 | 2809980.4929 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2809980.4929 | 3094685.5552 | -284705.0623 | -9.1998 | OK
12 | 33 kV Salam Steel Feeder |  | 33 | Export | BD001849 | 1 | 1373.5909 | 1415.526 | 41.9351 | 240000 |  | 10064424 | 10068596.5588 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 10068596.5588 | 9975944.1398 | 92652.419 | 0.92876 | OK
13 | 33 kV Fatullah Feeder-2. |  | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 4801.99 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.05 | 2748.7229 | 2780.7041 | 31.9812 | 240000 |  | 8059262.4 | 8062603.6489 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8062603.6489 | 8373173.4985 | -310569.8496 | -3.7091 | OK
17 | 33 kV Akhter Steel Feeder |  | 33 | Export | BD001828 | 1 | 691.9165 | 691.9365 | 0.02 | 240000 | Prime Textile | 4800 | 4801.99 | Fatullah | 16457250.5009 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 4801.99 | 1801.5401 | 3000.4499 | 166.5492 | FAULT
18 | 33 kV Steel Famus feeder |  | 33 | Export | BD001806 | 1 | 178.6475 | 187.0834 | 8.4359 | 240000 |  | 2024616 | 2025455.3753 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 2025455.3753 | 2243638.0198 | -218182.6445 | -9.7245 | OK
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.906 | 1544.91 | 0.004 | 240000 |  | 960 | 960.398 |  | 960.398 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 960.398 | 1681.4374 | -721.0394 | -42.8823 | CHECK
20 | 33 kV Rani Kamal Steel Feeder |  | 33 | Export | BD001829 | 1 | 1672.456 | 1700.5059 | 28.0499 | 240000 |  | 6731976 | 6734766.976 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 6734766.976 | 6694042.5391 | 40724.4369 | 0.60837 | OK
23 | 33 kV Shyampur BSCIC-2. |  | 33 | Export | BD001827 | 1 | 2702.2438 | 2737.207 | 34.9632 | 240000 |  | 8391168 | 8394646.852 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 8394646.852 | 8751593.4786 | -356946.6266 | -4.0786 | OK
24 | 33 kV Chakda Steel Feeder |  | 33 | Export | BD001832 | 1 | 2604.5029 | 2645.9221 | 41.4192 | 240000 |  | 9940608 | 9944729.2265 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 9944729.2265 | 11174809.0139 | -1230079.7874 | -11.0076 | OK
23 | Aux Tr-1 |  | 0.44kv | Export | DHKG9742 | 1.025 | 355.623 | 357.514 | 1.891 | 2400 |  | 4651.86 | 4651.86 | Fatullah
24 | Aux Tr-2 |  | 0.44kv | Export | DHKG9743 | 1.025 | 133.786 | 137.425 | 3.639 | 2400 |  | 8951.94 | 8951.94 | Fatullah
|  |  | 10: Total |  | 60981802.2 | 61007078.6977 |  |  |  |  | 0 | 61007078.6977 | 62378329.6722 | -1371250.9745 | -2.1983 | OK
|  |  | 9=8-7: Grand Total | 84654940.32 | 84619858.2 | 84654934.6801 | 0.041452
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 33211043.0928
[6 empty] | Fatullah | at 33 KV level |  | 18405.79
[7 empty] | Export to Other SS |  | 51425485.7973
[6 empty] | Total = |  |  | 84654934.6801 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | BD001926 | 1 | 3152.34 | 3198.904 | 46.564 | 160000 | 7450240 |  | 7483409.2179 |  | 7450240
16 | 11 kV 20/28 MVA Transformer-2 |  | 11 |  | BD001952 | 1 | 3163.87 | 3211.08 | 47.21 | 160000 | 7553600 |  | 7587229.387
27 | 11 kV20/28 MVA Transformer-3 |  | 11 |  | BD001927 | 1 | 2215.7 | 2245.5 | 29.8 | 160000 | 4768000 |  | 4789227.6156 |  | 1724472
36 | 11 kV 20/28 MVA Transformer-4 |  | 11 |  | BD001927 | 1 | 2079.69 | 2103.26 | 23.57 | 160000 | 3771200 |  | 3787989.7618 |  | 1724472
|  |  | 7: 0; 8: 0; 10: Total | 23543040 |  | 23647855.9824
| SHYAMPUR 11 kV SIDE |  | 7: 0; 8: 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur |  | 1 | 885.4112 | 928.523 | 43.1118 | 40000 |  | 1724472 | 1731294.1357 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1731294.1357 | 1773018.0469 | -41723.9112 | -2.3533 | OK
6 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | B426E | 11 |  | BD001943 | 1 | 1132.88 | 1147.74 | 14.86 | 40000 |  | 594400 | 596751.4893 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 596751.4893 | 639466.1203 | -42714.631 | -6.6797 | OK
8 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1648.4 | 1671.48 | 23.08 | 40000 |  | 923200 | 926852.2458 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 926852.2458 | 915003.4686 | 11848.7772 | 1.2949 | OK
10 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1521.28 | 1534.69 | 13.41 | 40000 |  | 536400 | 538522.0371 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 538522.0371 | 638253.078 | -99731.0409 | -15.6256 | OK
11 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1442.71 | 1458.11 | 15.4 | 40000 |  | 616000 | 618436.9405 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 618436.9405 | 607324.5147 | 11112.4257 | 1.8297 | OK
12 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3653.66 | 3713.44 | 59.78 | 40000 |  | 2391200 | 2400659.7598 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2400659.7598 | 2343340.7532 | 57319.0065 | 2.446 | OK
13 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2391.92 | 2437.96 | 46.04 | 40000 |  | 1841600 | 1848885.5025 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1848885.5025 | 1893470.7423 | -44585.2398 | -2.3547 | OK
15 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 508.47 | 511.61 | 3.14 | 40000 |  | 125600 | 126096.8827 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 126096.8827 | 151831.1287 | -25734.246 | -16.9493 | OK
17 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3421.82 | 3471.12 | 49.3 | 40000 |  | 1972000 | 1979801.3743 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1979801.3743 | 2074623.7556 | -94822.3813 | -4.5706 | OK
18 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2156.92 | 2186.86 | 29.94 | 40000 |  | 1197600 | 1202337.792 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1202337.792 | 1261644.3788 | -59306.5868 | -4.7007 | OK
19 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1664.56 | 1706.02 | 41.46 | 40000 |  | 1658400 | 1664960.7501 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1664960.7501 | 2201953.0355 | -536992.2854 | -24.3871 | OK
20 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 942.91 | 967.25 | 24.34 | 40000 |  | 973600 | 977451.6319 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 977451.6319 | 1044742.7664 | -67291.1345 | -6.4409 | OK
22 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1410.22 | 1420.84 | 10.62 | 40000 |  | 424800 | 426480.5395 | Shyampur |  |  |  | 11 kV Delpara Feeder | 426480.5395 | 499275.3782 | -72794.8387 | -14.5801 | OK
23 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3356.67 | 3403.54 | 46.87 | 40000 |  | 1874800 | 1882216.8441 | Shyampur |  |  |  | 11 kV Wasa Feeder | 1882216.8441 | 1814341.8208 | 67875.0233 | 3.741 | OK
24 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1141.41 | 1149.59 | 8.18 | 40000 |  | 327200 | 328494.4268 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 328494.4268 | 260281.9349 | 68212.4919 | 26.2072 | OK
26 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2145.18 | 2170.65 | 25.47 | 40000 |  | 1018800 | 1022830.4463 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1022830.4463 | 1107804.9019 | -84974.4555 | -7.6705 | OK
28 | 11 kV Spare Feeder | spare | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1471.2 | 1486.17 | 14.97 | 40000 |  | 598800 | 601168.896 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 601168.896 | 827921.4879 | -226752.5919 | -27.3882 | OK
30 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1470.28 | 1494.86 | 24.58 | 40000 |  | 983200 | 987089.6102 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 987089.6102 | 1109813.2501 | -122723.64 | -11.058 | OK
31 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2424.49 | 2446.259 | 21.769 | 40000 |  | 870760 | 874204.7894 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 874204.7894 | 816192.7341 | 58012.0553 | 7.1076 | OK
35 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 179.09 | 179.796 | 0.706 | 40000 |  | 28240 | 28351.7195 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 28351.7195 | 3615.0269 | 24736.6926 | 684.2741 | FAULT
37 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1318.14 | 1335.45 | 17.31 | 40000 |  | 692400 | 695139.1844 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 695139.1844 | 792895.8942 | -97756.7099 | -12.3291 | OK
39 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3961.57 | 4010.77 | 49.2 | 40000 |  | 1968000 | 1975785.55 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 1975785.55 | 2056548.6213 | -80763.0713 | -3.9271 | OK
40 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1138.63 | 1143.96 | 5.33 | 40000 |  | 213200 | 214043.4346 | Shyampur |  |  |  | 11 kV Igloo Feeder | 214043.4346 | 163077.879 | 50965.5556 | 31.2523 | OK
41 | 11/0.4 kV Aux Transformer, T-1 |  | 0.415 | DPDC | DHK20964 | 1 | 514432.1 | 530255 | 15822.9 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) |  | 0.415 | DPDC | DHK26108 | 1 | 65952.1 | 65952.1 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) |  | 0.415 |  |  | 1 | 640912 | 646898 | 5986 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 |  | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 23647855.9824 | 23554672 | 23647855.9824 | 0.39561
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 744533.8231
[6 empty] | Shyampur | at 33 KV level |  | 22903322.1592
[6 empty] | Total = |  |  | 23647855.9824 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.05 | 2748.7229 | 2780.7041 | 31.9812 | 240000 | 0 | 8059262.4 | 8062603.6489
23 | 33 kV Shyampur BSCIC-2. |  | 33 |  | BD001827 | 1 | 2702.2438 | 2737.207 | 34.9632 | 240000 | 0 | 8391168 | 8394646.852
|  |  | 10: Total | 0 | 16450430.4 | 16457250.5009
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 |  | 33 | Import | DHK61071 | 1 | 1006470.9 | 1006470.9 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-2 |  | 33 | Import | DHK61067 | 1 | 924566.9 | 956465.8 | 31898.9 | 270 | 8612703
|  |  | 7: 0; 8: 0; 10: Total | 8612703 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  | 7: 0; 8: 0
2 | 33 kV 20/28 MVA Transformer-1 |  | 33 | Export | DHK61068 | 1 | 1024311.6 | 1024311.6 | 0 | 180 |  | 0
3 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Export | DHK61066 | 1 | 730036.7 | 730036.7 | 0 | 180 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 16457250.5009; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 16457250.5009
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 16457250.5009 | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 16457250.5009
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 4: 16457250.5009
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK61019 | 1.05 | 209563.2 | 250785.4 | 41222.2 | 180 | 7790995.8 |  | 7854339.6055 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK61018 | 1 | 997871.5 | 1045280 | 47408.5 | 180 | 8533530 |  | 8602910.8954
|  |  | 7: 0; 8: 0; 10: Total | 16324525.8 |  | 16457250.5009
| SHYAMPUR BISIC 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nama shyampur Feeder |  | 11 | Shympur | HA-021101066-02 | 1 | 49050602 | 50526250 | 1475648 | 1 |  | 1475648 | 1472388.9525 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 1472388.9525 | 1369470.1894 | 102918.7631 | 7.5152 | OK
2 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 25352647 | 25888911 | 536264 | 1 |  | 536264 | 535079.6323 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 535079.6323 | 513962.2186 | 21117.4136 | 4.1087 | OK
3 | 11 kV H. R Steel |  | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) |  | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 611106.2 | 639043.5 | 27937.3 | 60 |  | 1676238 | 1672535.9388 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1672535.9388 | 1425925.7015 | 246610.2373 | 17.2947 | OK
6 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 728502.7 | 746070.8 | 17568.1 | 60 |  | 1054086 | 1051757.9947 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1051757.9947 | 992641.7614 | 59116.2333 | 5.9554 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 742996.5 | 760500 | 17503.5 | 60 |  | 1050210 | 1047890.5551 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1047890.5551 | 987729.1626 | 60161.3924 | 6.0909 | OK
8 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 463549.2 | 484253.6 | 20704.4 | 60 |  | 1242264 | 1239520.3935 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1239520.3935 | 1417396.8001 | -177876.4066 | -12.5495 | OK
9 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 599333.5 | 622666.5 | 23333 | 60 |  | 1399980 | 1396888.0693 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 1396888.0693 | 1760485.185 | -363597.1157 | -20.6532 | OK
12 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 119817.6 | 156765.8 | 36948.2 | 60 |  | 2216892 | 2211995.8755 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2211995.8755 | 2082378.5231 | 129617.3524 | 6.2245 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 391926.2 | 412196.4 | 20270.2 | 60 |  | 1216212 | 1213525.9308 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1213525.9308 | 1247860.6551 | -34334.7243 | -2.7515 | OK
14 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 556070.7 | 573450.5 | 17379.8 | 60 |  | 1042788 | 1040484.9469 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 1040484.9469 | 1184378.4913 | -143893.5444 | -12.1493 | OK
15 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 748024.9 | 775050 | 27025.1 | 60 |  | 1621506 | 1617924.8173 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 1617924.8173 | 1536098.7544 | 81826.0629 | 5.3269 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 932193.5 | 943773.6 | 11580.1 | 60 |  | 694806 | 693271.4838 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 693271.4838 | 752548.3412 | -59276.8574 | -7.8768 | OK
17 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 132355.9 | 161715.8 | 29359.9 | 60 |  | 1761594 | 1757703.4255 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1757703.4255 | 1853891.1932 | -96187.7677 | -5.1884 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| SUB-Station not match |  | 10: Grand Total | 16950968.016 | 16988488 | 16950968.016 | -0.22086 |  |  |  | SUB-Station not match
| bscic 33/11 kv ss | [16 empty] | bscic 33/11 kv ss
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 5683138.7023
[6 empty] | Jurain | at 33 KV level |  | 11267829.3137
[6 empty] | Total = |  |  | 16950968.016 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1433.9139 | 1460.4226 | 26.5087 | 240000 | From Downstream | 6362088 | 6364725.626
7 | 33 kV Nondolalpur -2 feeder |  | 33 |  | BD001807 | 1 | 1242.769 | 1263.401 | 20.632 | 240000 | 0 | 4951680 | 4953732.892
|  |  | 10: Total | 0 | 11313768 | 11318458.518
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) |  | 33 | Import | 00000084 | 1 | 344144640 | 350498880 | 6354240 | 1 | 6354240
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) |  | 33 | Import | 00000070 | 1 | 318843360 | 323801984 | 4958624 | 1 | 4958624
|  |  | 7: 0; 8: 0; 10: Total | 11312864 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NANDALALPUR 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 28/35 MVA T-1 |  | 33 | Export | 00000086 | 1 | 344321024 | 350671680 | 6350656 | 1 |  | 6350656
5 | 33 kV, 28/35 MVA T-2 |  | 33 | Export | 00000083 | 1 | 318272480 | 323228352 | 4955872 | 1 |  | 4955872
|  |  | 10: Total |  | 11306528 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 4: 11318458.518; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11318458.518
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 11318458.518 | 33 KV TX HV SIDE |  | 11306528
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 11930.518
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1054%
| TOTAL IMPORT |  | 4: 11318458.518
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. |  | 11 |  | 00000036 | 1 | 342307360 | 348630784 | 6323424 | 1 | 6323424 |  | 6357246.9796 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000033 | 1 | 316891552 | 321826368 | 4934816 | 1 | 4934816 |  | 4961211.5384
|  |  | 7: 0; 8: 0; 10: Total | 11258240 |  | 11318458.518
| NANDALALPUR 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Spare | spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | B889Z | 11 |  | 00000026 | 1 | 8820818 | 9206898 | 386080 | 1 |  | 386080 | 389654.3551 | Fatullah |  |  |  | 11 kV Khaza Moinuddin | 389654.3551 | 402828.4716 | -13174.1165 | -3.2704 | OK
10 | 11 kV Chitashal | B489Q | 11 |  | 00000027 | 1 | 37064908 | 37511028 | 446120 | 1 |  | 446120 | 450250.2095 | Shyampur |  |  |  | 11 kV Chitashal | 450250.2095 | 499792.4948 | -49542.2853 | -9.9126 | OK
11 | 11 kV Local Feeder | B489G | 11 |  | 00000157 | 1.5 | 19432112 | 19560472 | 128360 | 1 | Estimated | 341356.68 | 344516.9835 | Shyampur | 30 |  |  | 11 kV Local Feeder | 344516.9835 | 366892.6717 | -22375.6881 | -6.0987 | OK
12 | 11 kV Rasel Germants |  | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 |  | 00000121 | 1 | 86458552 | 88835864 | 2377312 | 1 |  | 2377312 | 2399321.3174 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2399321.3174 | 1808871.6613 | 590449.6562 | 32.6419 | OK
14 | 11 kV Nandalalpur | B890X | 11 |  | 00000010 | 1 | 88538464 | 90142376 | 1603912 | 1 |  | 1603912 | 1618761.1272 | Fatullah |  |  |  | 11 kV Nandalalpur | 1618761.1272 | 973812.9121 | 644948.2151 | 66.2292 | FAULT
15 | 11 kV Sharif Bagh | B489SB | 11 |  | 00000132 | 1 | 80714720 | 81823560 | 1108840 | 1 |  | 1108840 | 1119105.7167 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1119105.7167 | 1085733.2265 | 33372.4903 | 3.0737 | OK
18 | 11 kV Spare | spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | B890Y | 11 |  | 00000158 | 1 | 71063584 | 71687344 | 623760 | 1 |  | 623760 | 629534.8128 | Fatullah |  |  |  | 11 KV Nayamati | 629534.8128 | 729356.23 | -99821.4172 | -13.6862 | OK
20 | 11 kV Pulpar | B889S | 11 |  | 00000160 | 1 | 13525447 | 15039563 | 1514116 | 1 |  | 1514116 | 1528133.7897 | Fatullah |  |  |  | 11 kV Pulpar | 1528133.7897 | 1267285.0049 | 260848.7848 | 20.5833 | OK
21 | 11 kV Shahi Bazar | B489X | 11 |  | 00000170 | 1 | 44797452 | 45356488 | 559036 | 1 |  | 559036 | 564211.5936 | Shyampur |  |  |  | 11 kV Shahi Bazar | 564211.5936 | 420927.8461 | 143283.7475 | 34.04 | OK
22 | 11 kV Pagla Bazar | B890G | 11 |  | 00000060 | 1 | 53705668 | 54194108 | 488440 | 1 |  | 488440 | 492962.011 | Fatullah |  |  |  | 11 kV Pagla Bazar | 492962.011 | 446265.5628 | 46696.4482 | 10.4638 | OK
23 | 11 kV Delpara bazar | B489M | 11 |  | 00000063 | 1 | 88033984 | 89240144 | 1206160 | 1 |  | 1206160 | 1217326.7119 | Shyampur |  |  |  | 11 kV Delpara bazar | 1217326.7119 | 1352583.6238 | -135256.9119 | -9.9999 | OK
24 | 11 kV Bhuighor (Board mill) | E289C | 11 |  | 00000146 | 1 | 47761524 | 48318124 | 556600 | 1 |  | 556600 | 561753.0409 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 561753.0409 | 635132.0988 | -73379.0578 | -11.5534 | OK
25 | 11 kV Spare |  | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 |  | 11 |  | 7803 | 1 | 2684 | 2707.7 | 23.7 | 100 |  | 2370 | 2391.9416 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 2391.9416 | 2513.6624 | -121.7207 | -4.8424 | OK
27 | 33/0.415 kV, 200 kVA AT-2 |  | 11 |  | 7805 | 1 | 89 | 94.3 | 5.3 | 100 |  | 530 | 534.9068 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 534.9068 | 522.8418 | 12.065 | 2.3076 | OK
|  |  | 10: Grand Total | 11318458.518 | 11214632.68 | 11318458.518 | 0.92581
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 3698338.0637
[6 empty] | Fatullah | at 33 KV level |  | 4659046.0959
[6 empty] | Matuail | at 33 KV level |  | 2961074.3584
[6 empty] | Total = |  |  | 11318458.518 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 |  | 132 | Import | 4262 7826 | 1 | 438.262 | 455.625 | 17.363 | 960000 | 0 | 16668480
[6 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 |  | 132 |  | 4262 7815 | 1 | 175.272 | 180.139 | 4.867 | 960000 | 0 | 4672320
2 | [5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 21340800
|  |  | 10: Net Total | 21340800
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 |  | 132 | Main | 41808902823 | 1 | 350.34 | 364.22 | 13.88 | 1200000 | 16656000
|  |  | 132 | Backup | 41808904269 | 1 | 350.41 | 364.29 | 13.88 | 1200000 | 16656000
4 | 132kV Hasnabad Circuit-2 |  | 132 | Imp/Main | 41808902845 | 1 | 140.1 | 143.99 | 3.89 | 1200000 | 4668000
|  |  | 132 | Imp/Backup | 41808904256 | 1 | 140.14 | 144.03 | 3.89 | 1200000 | 4668000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 21324000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 21324000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| POSTOGOLA 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41808902871 | 1 | 361.42 | 375.29 | 13.87 | 1200000 |  | 16644000
|  |  | 132 | Exp/Backup | 41808904257 | 1 | 361.5 | 375.36 | 13.86 | 1200000 |  | 16632000
5 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41808902846 | 1 | 128.85 | 132.74 | 3.89 | 1200000 |  | 4668000
|  |  | 132 | Exp/Backup | 41808904243 | 1 | 128.85 | 132.74 | 3.89 | 1200000 |  | 4668000
|  |  | 10: Total |  | 21312000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 21340800; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 21340800
|  |  | 6: 132 KV NET IMPORT; 9=8-7: 21340800 | 33 KV NET IMPORT |  | 21218400
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 122400
[11 empty] | LOSS % IN => |  | 0.5735%
| 132 KV TOTAL IMPORT |  | 4: 21340800
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE |  | 10: Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41808902807 | 1 | 600.29 | 623.33 | 23.04 | 720000 | 16588800
|  |  | 33 | Backup | 41808904286 | 1 | 600.43 | 623.45 | 23.02 | 720000 | 16574400
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41808902869 | 1 | 213.26 | 219.69 | 6.43 | 720000 | 4629600
|  |  | 33 | Backup | 41808904268 | 1 | 213.29 | 219.72 | 6.43 | 720000 | 4629600
|  |  | 7: 0; 8: 0; 10: Total | 21218400 |  | 21340800
| POSTOGOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 |  | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss | 1.8472 | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 527.95 | 543.64 | 15.69 | 360000 |  | 5648400 | 5656186.1492 |  | 10126339.6387 | IG Gate 33/11 kv ss | 1.4998 | 33 kV IG Gate Ckt-2 | 5656186.1492 | 5511449.9736 | 144736.1756 | 2.6261 | OK
|  |  | 33 | Backup | 41808904225 | 1 | 527.97 | 543.82 | 15.85 | 360000 |  | 5706000 | 5713865.5491 |  |  |  |  | 0 | 5713865.5491 | 5511449.9736 | 202415.5755 | 3.6726 | OK
8 | 33 kV Spare Feeder 2 |  | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 |  | 33 | Main | 41808902810 | 1 | 674.64 | 705.49 | 30.85 | 360000 |  | 11106000 | 11121309.2864 |  |  |  |  | 33kV Postogola circuit-1 | 11121309.2864 | 10750953.4025 | 370355.8839 | 3.4449 | OK
|  |  | 33 | Backup | 41808904252 | 1 | 674.61 | 705.44 | 30.83 | 360000 |  | 11098800 | 11114099.3614 |  |  |  |  | 0 | 11114099.3614 | 10732823.6328 | 381275.7286 | 3.5524 | OK
14 | 31 kV Spare Feeder 4 |  | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 |  | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 |  | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1 | 424.92 | 437.32 | 12.4 | 360000 |  | 4464000 | 4470153.4895 |  |  |  |  | 33 kV IG Gate Ckt-1 | 4470153.4895 | 4387404.2553 | 82749.2342 | 1.8861 | OK
|  |  | 33 | Backup | 41812909573 | 1 | 424.82 | 437.22 | 12.4 | 360000 |  | 4464000 | 4470153.4895 |  |  |  |  | 0 | 4470153.4895 | 4376526.3935 | 93627.096 | 2.1393 | OK
|  |  | 10: Total |  | 21268800 | 21298118.4 |  | All Backup Meters Added |  |  | 0 | 21298118.4 | 20620800 | 677318.4 | 3.2846 | OK
|  |  | 9=8-7: Grand Total | 21298118.4 | 21268800 | 21298118.4 | 0.13785
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola |  | 33 | Import | BD001804 | 1 | 674.61 | 705.44 | 30.83 | 360000 | 11098800 |  | 11114099.3614
2 | 33 kV Postogola Circuit-2 at Shyampur |  | 33 | Import | BD001830 | 1 | 2131.902 | 2131.9 | -0.002 | 240000 | -480 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 11098320 |  | 11114099.3614
| POSTOGOLA 33 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) |  | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) |  | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0
| POSTOGOLA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK61027 | 1 | 469005.8 | 496298.2 | 27292.4 | 180 |  | 4912632 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60870 | 1 | 965841.7 | 1000431 | 34589.3 | 180 |  | 6226074
|  |  | 7: 0; 8: 0; 10: Total |  | 11138706
| POSTOGOLA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV 20/28 MVA T-1 Incoming. |  | 11 |  | DHK61005 | 1.165 | 1010657.7 | 1010657.7 | 0 | 180 | 0 |  | #DIV/0! |  | 22277412
9 | 11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK60861 | 1.165 | 1038479.9 | 1038479.9 | 0 | 180 | 0 |  | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | #DIV/0!
| POSTOGOLA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 68603944 | 69356979 | 753035 | 1 |  | 753035 | 766944.6993 | Postogola |  |  |  | 11 kV Station Road Feeder | 766944.6993 | 737584.4324 | 29360.2669 | 3.9806 | OK
2 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 2469.7 | 3314.1 | 844.4 | 1000 |  | 844400 | 859997.3495 | Jurain |  |  |  | 11 kV Samon & Sons Feeder. | 859997.3495 | 893758.2817 | -33760.9322 | -3.7774 | OK
3 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 26932943 | 27319153 | 386210 | 1 |  | 386210 | 393343.8848 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 393343.8848 | 438805.162 | -45461.2771 | -10.3602 | OK
4 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 82148708 | 83065054 | 916346 | 1 |  | 916346 | 933272.3014 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 933272.3014 | 909857.0079 | 23415.2934 | 2.5735 | OK
5 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 487008.3 | 494591.1 | 7582.8 | 60 |  | 454968 | 463371.9495 | Postogola |  |  |  | 11 kV Cyca Feeder | 463371.9495 | 446819.6527 | 16552.2967 | 3.7045 | OK
6 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 966474.7 | 978748.4 | 12273.7 | 60 |  | 736422 | 750024.832 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 750024.832 | 718393.3477 | 31631.4843 | 4.4031 | OK
7 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 857587.6 | 870988.1 | 13400.5 | 60 |  | 804030 | 818881.6544 | Postogola |  |  |  | 11 kV Munshi Bari | 818881.6544 | 778178.9459 | 40702.7085 | 5.2305 | OK
8 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 531085.9 | 532049.3 | 963.4 | 60 |  | 57804 | 58871.7276 | Postogola |  |  |  | 11 kV Cantonment Feeder | 58871.7276 | 59976.3705 | -1104.6429 | -1.8418 | OK
9 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 975578.9 | 998174.5 | 22595.6 | 60 |  | 1355736 | 1380778.5015 | Postogola |  |  |  | 11 kV DIT Feeder. | 1380778.5015 | 1491415.2858 | -110636.7843 | -7.4182 | OK
10 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 495051.3 | 511122.6 | 16071.3 | 60 |  | 964278 | 982089.6781 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 982089.6781 | 758406.3132 | 223683.365 | 29.4939 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 49734483 | 50750371 | 1015888 | 1 |  | 1015888 | 1034652.9932 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 1034652.9932 | 929342.4564 | 105310.5367 | 11.3317 | OK
12 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 20898.3 | 22454.9 | 1556.6 | 1000 |  | 1556600 | 1585352.7644 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 1585352.7644 | 1530384.1315 | 54968.6329 | 3.5918 | OK
13 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 64278986 | 65251735 | 972749 | 1 |  | 972749 | 990717.1504 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 990717.1504 | 953613.6246 | 37103.5257 | 3.8908 | OK
14 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 217.2 | 308.4 | 91.2 | 1000 |  | 91200 | 92884.6024 | Postogola |  |  |  | 11 kV Rajabari Feeder. | 92884.6024 | 84309.0782 | 8575.5242 | 10.1715 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 |  | 11 |  | ELIB67385 | 1 | 666.1 | 701.88 | 35.78 | 80 |  | 2862.4 | 2915.2729 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 2915.2729 | 3420.7742 | -505.5013 | -14.7774 | OK
|  |  | 10: Total | 11114099.3614 | 10912528.4 | 11114099.3614 | 1.8472
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Postogola | at 33 KV level |  | 6258662.6913
[6 empty] | Jurain | at 33 KV level |  | 4855436.6701
[6 empty] | Total = |  |  | 11114099.3614 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.906 | 1544.91 | 0.004 | 240000 | 0 | 960 | 960.398
| Postogola 33 KV SIDE |  | 10: Total | 0 | 960 | 960.398
7 | 33 kV IG Gate Ckt-2 |  | 33 | Backup | 41808904225 | 1 | 527.97 | 543.82 | 15.85 | 360000 | 0 | 5706000 | 5713865.5491
17 | 33 kV IG Gate Ckt-1 |  | 33 | Backup | 41812909573 | 1 | 424.82 | 437.22 | 12.4 | 360000 | 0 | 4464000 | 4470153.4895
|  |  | 10: Total | 0 | 10170000 | 10184019.0386
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 |  | 33 | Import | DHK60973 | 1 | 337437.7 | 345823.8 | 8386.1 | 540 | 4528494
6 | 33 kV Postogola Incoming Feeder-2 |  | 33 | Import | DHK60966 | 1 | 534901.9 | 545342.5 | 10440.6 | 540 | 5637924
|  |  | 7: 0; 8: 0; 10: Total | 10166418 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| IG GATE 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK60893 | 1 | 976844.7 | 1001648.4 | 24803.7 | 180 |  | 4464666
5 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60975 | 1 | 638288.2 | 671349.8 | 33061.6 | 180 |  | 5951088
|  |  | 10: Total |  | 10415754
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 4: 10184019.0386; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10184019.0386
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 10184019.0386 | 33 KV TX HV SIDE |  | 10415754
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -231734.9614
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -2.275%
| TOTAL IMPORT |  | 4: 10184019.0386
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month February-2024 |  |  | Name of Feeders. | Month February-2024 | Month January-2024 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK68139 | 1 | 3911.05 | 3935.08 | 24.03 | 180000 | 4325400 |  | 6330108.0574 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK68137 | 1 | 4534.46 | 4549.09 | 14.63 | 180000 | 2633400 |  | 3853910.9812
|  |  | 7: 0; 8: 0; 10: Total | 6958800 |  | 10184019.0386
| IG GATE 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Feeder-1 |  | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 |  | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | A619R | 11 |  | DHK60970 | 1 | 385192.6 | 402446.4 | 17253.8 | 60 |  | 1035228 | 1050754.3313 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 1050754.3313 | 993748.355 | 57005.9763 | 5.7365 | OK
4 | 11 kV Alom Gonj | A581A | 11 |  | DHK60894 | 1 | 531417.9 | 537217.3 | 5799.4 | 60 |  | 347964 | 353182.7579 | Postogola |  |  |  | 11 kV Alom Gonj | 353182.7579 | 341849.6279 | 11333.1301 | 3.3152 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 |  | DHK60895 | 1 | 681848.5 | 698964.4 | 17115.9 | 60 |  | 1026954 | 1042356.2379 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1042356.2379 | 998356.1619 | 44000.076 | 4.4073 | OK
6 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 |  | DHK68133 | 1 | 3746.38 | 3765.72 | 19.34 | 60000 |  | 1160400 | 1177803.6587 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1177803.6587 | 1144988.569 | 32815.0897 | 2.866 | OK
7 | 11 kV Doyaganj | B587Y | 11 |  | DHK68134 | 1 | 2516.51 | 2535.08 | 18.57 | 60000 |  | 1114200 | 1130910.7519 | Swamibag |  |  |  | 11 kV Doyaganj | 1130910.7519 | 888864.7379 | 242046.014 | 27.2309 | OK
10 | 11 kV Faridabad | A587F | 11 |  | DHK68140 | 1 | 880.02 | 891.93 | 11.91 | 60000 |  | 714600 | 725317.5582 | Postogola |  |  |  | 11 kV Faridabad | 725317.5582 | 718721.0108 | 6596.5474 | 0.91782 | OK
11 | 11 kV Gandaria | A524D | 11 |  | DHK60969 | 1 | 539206 | 558384.7 | 19178.7 | 60 |  | 1150722 | 1167980.5082 | Postogola |  |  |  | 11 kV Gandaria | 1167980.5082 | 1163546.9506 | 4433.5576 | 0.38104 | OK
12 | 11 kV Walter Road | A687W | 11 |  | DHK68136 | 1 | 1099.91 | 1113.41 | 13.5 | 60000 |  | 810000 | 822148.3657 | Banglabazar |  |  |  | 11 kV Walter Road | 822148.3657 | 765344.025 | 56804.3407 | 7.4221 | OK
13 | 11 kV Murgitola Feeder (F-11) | B587G | 11 |  | DHK68138 | 1 | 4084.44 | 4107.26 | 22.82 | 60000 |  | 1369200 | 1389735.2374 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 1389735.2374 | 1315132.2961 | 74602.9413 | 5.6727 | OK
14 | 11 kV Feeder-12 |  | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 |  | DHK60899 | 1 | 808791.9 | 825043.7 | 16251.8 | 60 |  | 975108 | 989732.6526 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 989732.6526 | 1020953.1865 | -31220.5339 | -3.058 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 |  | DHK60967 | 1 | 245164.3 | 254436.4 | 9272.1 | 60 |  | 556326 | 564669.7675 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 564669.7675 | 535098.9942 | 29570.7733 | 5.5262 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB2774 | 1 | 288325 | 289470 | 1145 | 1 |  | 1145 | 1162.1727 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1162.1727 | 1372.4524 | -210.2797 | -15.3215 | OK
|  |  | 10: Grand Total | 10415754 | 10261847 | 10415754 | 1.4998
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Swamibag | at 33 KV level |  | 3510378.6419
[6 empty] | Banglabazar | at 33 KV level |  | 3050706.3556
[6 empty] | Postogola | at 33 KV level |  | 3854669.0025
[6 empty] | Total = |  |  | 10415754 | 0
Note on J393: No Reading Due to PT Out
Note on J650: No Reading due to PT Open
Note on M650: Energy From Bangshal SS End
Note on M655: Energy From Bangshal SS End

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [6 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [14 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month February-2024
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total |  | Zone-Circle-Division wise Import & System loss at 33kv level for the Month February-2024 | [13 empty] | FINAL |  |  |  |  | Date: 03.03.2024 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 4858580.6154 | 11261889.199 | 13288343.7587 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 4928627.7069 |  |  | North | 178375090.3704 | Tejgaon | 36194333.9763 | Tejgaon | 20497418.1246 | 19304440.9923 | 1192977.1322 | 6.1798 | North | 178375090.3704 | 167059179.28 | 6.3439 | Tejgaon | 36194333.9763 | 33919814 | 6.2842 | Tejgaon | 20497418.1246 | 19264195 | 6.0165 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 0 | [6 empty] | Kakrail | 15696915.8518 | 15011429.3617 | 685486.4901 | 4.5664 | [8 empty] | Kakrail | 15696915.8518 | 14655619 | 6.6338 | 2 | Tejgaon | 19264195 | 251644 | 19515839 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | 10316695.309
|  |  |  | Maghbazar | 1474680.8767 |  |  |  |  | Moghbazar | 21051490.6416 | Moghbazar | 11229690.6168 | 10672816.3192 | 556874.2976 | 5.2177 |  |  |  |  | Moghbazar | 21051490.6416 | 19237570 | 8.6166 | Moghbazar | 11229690.6168 | 10261004 | 8.6261 | 3 | Kakrail | 14655619 | 253191 | 14908810 | A1 | Motijheel | 13663776 | 157085 | 13820861
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 9460453.5434 | [5 empty] | Khilgaon | 9821800.0249 | 9369790.2057 | 452009.8192 | 4.8241 | [8 empty] | Khilgaon | 9821800.0249 | 8976566 | 8.6057 | 4 | Moghbazar | 10261004 | 86090 | 10347094 | A2 | Khilgaon | 8976566 | 65235 | 9041801
|  |  |  | Jigatola | 2609512.3161 |  |  |  |  | Satmasjid | 27430533.8525 | Satmosjid | 13003857.5391 | 13121826.1877 | -117968.6486 | -0.89903 |  |  |  |  | Satmasjid | 27430533.8525 | 25669838.98 | 6.4187 | Satmosjid | 13003857.5391 | 12066628.98 | 7.2073 | 5 | Khilgaon | 8976566 | 65235 | 9041801 | A3 | Lalbag | 30670902 | 117664 | 30788566
|  |  |  | Paribagh | 6850941.2274 | [6 empty] | Sherebanglanagar | 14426676.3134 | 13799704.7765 | 626971.5369 | 4.5434 | [8 empty] | Sherebangla nagar | 14426676.3134 | 13603210 | 5.7079 | 6 | Satmosjid | 12066628.98 | 128827 | 12195455.98 | A4 | Kazla | 30491119.1 | 131575 | 30622694.1
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 6749190 |  |  |  | Dhanmondi | 30716561.3532 | Dhanmondi | 13420007.9536 | 13258311.6925 | 161696.261 | 1.2196 |  |  |  |  | Dhanmondi | 30716561.3532 | 29501172.36 | 3.9568 | Dhanmondi | 13420007.9536 | 13969201.3 | -4.0923 | 7 | Sherebanglanagar | 13603210 | 98847 | 13702057 | A5 | Postogola | 9816475 | 168706 | 9985181
[12 empty] | Jhigatala | 17296553.3996 | 15716141.8061 | 1580411.5935 | 10.056 | [8 empty] | Jhigatala | 17296553.3996 | 15531971.06 | 10.2019 | 8 | Dhanmondi | 13969201.3 | 235089 | 14204290.3 | A6 | Banglabazar | 9695465.85 | 197604 | 9893069.85
|  |  |  | Jigatola | 0 |  |  |  |  | Azimpur | 32786070.5931 | Azimpur | 12315561.2166 | 11917841.4788 | 397719.7378 | 3.3372 |  |  |  |  | Azimpur | 32786070.5931 | 30240328.94 | 7.7647 | Azimpur | 12315561.2166 | 11160921 | 9.3755 | 9 | Jhigatala | 15531971.06 | 253502.5396 | 15785473.5996 | A7 | N.Gonj (West) | 22435170 | 193060 | 22628230
|  |  |  | Dhanmondi | 6749190 | [6 empty] | Paribagh | 20470509.3764 | 19464342.6901 | 1006166.6864 | 5.1693 | [8 empty] | Paribagh | 20470509.3764 | 19079407.94 | 6.7956 | 10 | Azimpur | 11160921 | 48858 | 11209779 | A8 | Siddirgonj | 37217695 | 525823 | 37743518
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 13240464.6677 | 13240464.6677 |  |  |  | Shamoly | 30196099.9536 | Shyamoli | 10634428.2931 | 10924946.5814 | -290518.2883 | -2.6592 |  |  |  |  | Shamoly | 30196099.9536 | 28490455 | 5.6486 | Shyamoli | 10634428.2931 | 10051610 | 5.4805 | 11 | Paribagh | 19079407.94 | 157630.7376 | 19237038.6776 | A9 | Bashabo | 8012487.88 | 24717 | 8037204.88
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 8287536.0603 | [5 empty] | Adabor | 19561671.6605 | 18928032.214 | 633639.4465 | 3.3476 | [8 empty] | Adabor | 19561671.6605 | 18438845 | 5.7399 | 12 | Shyamoli | 10051610 | 190135 | 10241745 | B1 | Narinda | 7906061.16 | 40966 | 7947027.16
|  |  |  | RAMNA | 683637.0797 |  |  | Central | 179657000.5316 | Lalbagh | 64244384.4147 | Lalbagh | 31442028.8478 | 31677000.5392 | -234971.6915 | -0.74177 | Central | 179657000.5316 | 169536444.67 | 5.6333 | Lalbagh | 64244384.4147 | 61607696 | 4.1042 | Lalbagh | 31442028.8478 | 30670902 | 2.4525 | 13 | Adabor | 18438845 | 517459 | 18956304 | B2 | Maniknagar | 13652651.52 | 108999 | 13761650.52
|  |  |  | Kakrail | 1032657.3871 | [6 empty] | Kamrangirchar | 32802355.567 | 32737728.1062 | 64627.4607 | 0.19741 | [8 empty] | Kamrangirchar | 32802355.567 | 30936794 | 5.6873 | 14 | Lalbagh | 30670902 | 117664 | 30788566 | B3 | Jurain | 18773604.23 | 615054 | 19388658.23
|  |  |  | Paribagh | 6571241.5935 |  |  |  |  | Ramna | 26088553.9573 | Ramna | 15785201.4197 | 15191630.534 | 593570.8857 | 3.9072 |  |  |  |  | Ramna | 26088553.9573 | 24725384 | 5.2252 | Ramna | 15785201.4197 | 15059405 | 4.598 | 15 | Kamrangirchar | 30936794 | 110168 | 31046962 | B4 | Shyampur | 68696884 | 287839 | 68984723
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 2741463.4061 | [5 empty] | Rajarbagh | 10303352.5377 | 9901636.0225 | 401716.5152 | 4.0571 | [8 empty] | Rajarbagh | 10303352.5377 | 9665979 | 6.1861 | 16 | Ramna | 15059405 | 444899 | 15504304 | B5 | Swamibag | 7920893 | 11553 | 7932446
|  |  |  | Kakrail | 334673.6078 |  |  |  |  | Bashabo | 22587304.3447 | Bashabo | 8008237.0387 | 7548603.1055 | 459633.9331 | 6.089 |  |  |  |  | Bashabo | 22587304.3447 | 22015337.66 | 2.5322 | Bashabo | 8008237.0387 | 8012487.88 | -0.053081 | 17 | Rajarbagh | 9665979 | 202060 | 9868039 | B6 | Bangshal | 11466120 | 174587 | 11640707
|  |  |  | Paribagh | 0 | [6 empty] | Bonoseeri | 14579067.306 | 14415324.4579 | 163742.8481 | 1.1359 | [8 empty] | Bonossri | 14579067.306 | 14002849.78 | 3.9524 | 18 | Bashabo | 8012487.88 | 24717 | 8037204.88 | B7 | N.Gonj (East) | 22013499 | 4389591 | 26403090
|  |  |  | Shere Bangla Nagar | 2406789.7983 |  |  |  |  | Motijheel | 25794734.2408 | Motijheel | 14643049.1245 | 13800329.6534 | 842719.4711 | 6.1065 |  |  |  |  | Motijheel | 25794734.2408 | 24199487 | 6.1844 | Motijheel | 14643049.1245 | 13663776 | 6.6876 | 19 | Bnossri | 14002849.78 | 80440 | 14083289.78 | B8 | Fateullah | 25809986 | 523366 | 26333352
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1601928.7957 | 5420060.6016 | [5 empty] | Mughdapara | 11151685.1163 | 11286617.8798 | -134932.7636 | -1.1955 | [8 empty] | Mughdapara | 11151685.1163 | 10535711 | 5.5236 | 20 | Motijheel | 13663776 | 157085 | 13820861 | B9 | Mugdapara | 10535711 | 64160 | 10599871
|  |  |  | Lalbagh | 0 |  |  |  |  | Banglabazar | 23299274.5256 | Banglabazar | 10520068.8888 | 10162579.9989 | 357488.89 | 3.5177 |  |  |  |  | Banglabazar | 23299274.5256 | 21161585.85 | 9.1749 | Banglabazar | 10520068.8888 | 9695465.85 | 7.8384 | 21 | Mughdapara | 10535711 | 64160 | 10599871 | C1 | Tejgaon | 19264195 | 251644 | 19515839
|  |  |  | Narinda | 252210.9783 | [6 empty] | Bongshal | 12779205.6368 | 11740106.5812 | 1039099.0556 | 8.8508 | [8 empty] | Bongshal | 12779205.6368 | 11466120 | 10.2752 | 22 | Banglabazar | 9695465.85 | 197604 | 9893069.85 | C2 | Satmasjid | 12066628.98 | 128827 | 12195455.98
|  |  |  | Motijheel | 185907.9497 |  |  |  |  | Narinda | 17642749.0485 | Narinda | 8717278.4575 | 8031729.1762 | 685549.2813 | 8.5355 |  |  |  |  | Narinda | 17642749.0485 | 15826954.16 | 10.292 | Narinda | 8717278.4575 | 7906061.16 | 9.3059 | 23 | Bongshal | 11466120 | 174587 | 11640707 | C3 | Paribagh | 19079407.94 | 157630.7376 | 19237038.6776
|  |  |  | RAMNA | 3380012.8779 | [6 empty] | Swamibagh | 8925470.591 | 8407385.9755 | 518084.6154 | 6.1623 | [8 empty] | Swamibagh | 8925470.591 | 7920893 | 11.2552 | 24 | Narinda | 7906061.16 | 40966 | 7947027.16 | C6 | Kakrail | 14655619 | 253191 | 14908810
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 |  | South | 351652198.9662 | Kazla | 45526640.2166 | Kazla | 32107375.0819 | 31402572.2319 | 704802.85 | 2.2444 | South | 351652198.9662 | 341932830.54 | 2.7639 | Kazla | 45526640.2166 | 44143770.62 | 3.0375 | Kazla | 32107375.0819 | 30491119.1 | 5.0339 | 25 | Swamibagh | 7920893 | 11553 | 7932446 | D1 | Moghbazar | 10261004 | 86090 | 10347094
|  | Khillgaon 33/11KV S/S |  | Kakrail | 56073.4567 | 4588920 | [5 empty] | Maniknagar | 13419265.1347 | 13541334.2736 | -122069.139 | -0.90146 | [8 empty] | Maniknagar | 13419265.1347 | 13652651.52 | -1.7392 | 26 | Kazla | 30491119.1 | 131575 | 30622694.1 | D2 | Dhanmondi | 13969201.3 | 235089 | 14204290.3
|  |  |  | Khilgaon | 257511.2551 |  |  |  |  | Shyampur | 84281141.2926 | Shyampur | 67253750.9726 | 70740222.4839 | -3486471.5113 | -4.9286 |  |  |  |  | Shyampur | 84281141.2926 | 84620395 | -0.40253 | Shyampur | 67253750.9726 | 68696884 | -2.1458 | 27 | Maniknagar | 13652651.52 | 108999 | 13761650.52 | D3 | Ramna | 15059405 | 444899 | 15504304
| 9 |  |  | Maghbazaar | 66556.7552 | [6 empty] | Matuail | 17027390.32 | 17009680.0308 | 17710.2892 | 0.10412 | [8 empty] | Matuail | 17027390.32 | 15923511 | 6.483 | 28 | Shyampur | 68696884 | 287839 | 68984723 | D4 | Shyamoli | 10051610 | 190135 | 10241745
|  |  |  | Rajarbagh | 4208778.533 |  |  |  |  | Postogola | 30128103.1999 | Postogola | 10113331.6938 | 9942513.7178 | 170817.9759 | 1.7181 |  |  |  |  | Postogola | 30128103.1999 | 28590079.23 | 5.1049 | Postogola | 10113331.6938 | 9816475 | 2.9353 | 29 | Matuail | 15923511 | 488818 | 16412329 | D5 | Shere b.nagar | 13603210 | 98847 | 13702057
| 10 | Goran 33/11KV S/S |  | Bashabo | 794147.1375 | 7320032.997 | [5 empty] | Jurain | 20014771.5061 | 19533269.9541 | 481501.552 | 2.465 | [8 empty] | Jurain | 20014771.5061 | 18773604.23 | 6.2013 | 30 | Postogola | 9816475 | 168706 | 9985181 | D6 | Rajarbag | 9665979 | 202060 | 9868039
|  |  |  | Khilgaon | [5 empty] | Narayangonj | 47721677.9186 | Narayangonj-West | 24043292.6275 | 24319848.9477 | -276556.3202 | -1.1372 |  |  |  |  | Narayangonj | 47721677.9186 | 44448669 | 6.8585 | Narayangonj- West | 24043292.6275 | 22435170 | 6.6884 | 31 | Jurain | 18773604.23 | 615054 | 19388658.23 | D8 | Jhigatala | 15531971.06 | 253502.5396 | 15785473.5996
|  |  |  | Banosree | 6525885.8595 | [6 empty] | Narayangonj-East | 23678385.2911 | 24271349.8218 | -592964.5306 | -2.4431 | [8 empty] | Narayangonj- East | 23678385.2911 | 22013499 | 7.0312 | 32 | Narayangonj-West | 22435170 | 193060 | 22628230 | D9 | Azimpur | 11160921 | 48858 | 11209779
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 4696988.4577 | 6945166.6951 |  |  |  | Demra | 55021163.8575 | Demra | 16376823.3007 | 16091524.3355 | 285298.9652 | 1.773 |  |  |  |  | Demra | 55021163.8575 | 51925827.69 | 5.6257 | Demra | 16376823.3007 | 14708132.69 | 10.1893 | 33 | Narayangonj-East | 22013499 | 4389591 | 26403090 | E1 | Demra | 14708132.69 | 234668 | 14942800.69
|  |  |  | Maghbazar | 0 | [6 empty] | Siddhirgonj | 38644340.5568 | 38752302.1818 | -107961.625 | -0.27859 | [8 empty] | Siddhirgonj | 38644340.5568 | 37217695 | 3.6917 | 34 | Damra | 14708132.69 | 234668 | 14942800.69 | E2 | Matuail | 15923511 | 488818 | 16412329
|  |  |  | Bashabo | 2248178.2373 |  |  |  |  | Fatullah | 88973472.4811 | Fatulla | 24856488.1413 | 26679382.7343 | -1822894.593 | -6.8326 |  |  |  |  | Fatullah | 88973472.4811 | 88204089 | 0.86473 | Fatulla | 24856488.1413 | 25809986 | -3.836 | 35 | Siddhirgonj | 37217695 | 525823 | 37743518 | E3 | Sytalakha | 62394103 | 267055 | 62661158
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 11907000 | [5 empty] | Shitalakha | 64116984.3398 | 63644086.5962 | 472897.7436 | 0.74303 | [8 empty] | Sytalakhya | 64116984.3398 | 62394103 | 2.6871 | 36 | Fatulla | 25809986 | 523366 | 26333352 | F1 | Kamrangirchar | 30936794 | 110168 | 31046962
|  |  |  | Shyamoli | 2351108.8415 |  |  | TOTAL=> | 709684289.8682 | TOTAL=> | 709684289.8682 | TOTAL=> | 709684289.8682 | 702318383.6459 | 7365906.2223 | 1.0488 |  | 709684289.8682 | 678528454.49 |  | TOTAL=> | 709684289.8682 | 678528454.49 |  | Total=> | 709684289.8682 | 678528454.49 | 4.3901 | 37 | Shitalokko | 62394103 | 267055 | 62661158 | F2 | Banosree | 14002849.78 | 80440 | 14083289.78
|  |  |  | Shere Bangla Nagar | 0 | [24 empty] | Total => | 678528454.49 | 11846965.2772 | 690375419.7672 | G1 | Adabor | 18438845 | 517459 | 18956304
|  |  |  | Satmosjid | 6320117.6382 | [15 empty] | 132KV Import => |  |  |  |  | 713621944.2397 | [8 empty] | Total => | 678528454.49 | 11846965.2772 | 690375419.7672
|  |  |  | Dhanmondi NOCS | 3235773.5204 |  |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 713621944.2397 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 709684289.8682
|  | Civil Aviation |  | Tejgaon | 0 | 0 |  | 33kv import of DPDC=> |  |  |  |  | 709684289.8682 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.55178
| 13 | Japan garden Building |  | Adabor | 928260 | 928260 |  | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.55178 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 678528454.49
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 | [5 empty] | 3937654.3715 | [8 empty] | System loss at 132kv level => |  |  |  |  | 4.9177
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 1243200 | 1243200
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 6687624.8 | 7115664.8
| 16 |  |  | Shere Bangla Nagar | 428040
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 15426312.4721 | 15426312.4721
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 747419.7339 | 9061873.1322
|  |  |  | Lalbagh | 8314453.3983
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 4555342.6082
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 4555342.6082
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 1320617.2693 | 5781121.0774
|  |  |  | Rajarbaghl | 1664279.4572
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 2796224.3508 | 2796224.3508
|  | Banshal 33/11 KV S/S |  | Bangshal | 3738924.9083 | 5102527.8727
|  |  |  | Banglabazar | 714287.5661
|  |  |  | Narinda | 649315.3982
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 7043211.911 | 10638000 | 11566260
|  |  |  | Shamoly | 2743696.7533
|  |  |  | Satmosjit | 851091.3357
|  | Azimpur 33/11 KV |  | jigatola | 217235.8269 | 11062276.784
|  |  |  | Azimpur | 9197314.113
|  |  |  | RAMNA | 998360.3961
|  |  |  | Paribagh | 649366.4481
|  | T&T 33/11 KV |  | Kakrail | 1905632.828 | 6315244.0748
|  |  |  | Mogbazar | 3459623.6254
|  |  |  | Khilgaon | 949987.6214
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 2041913.6517 | 3354162.9
|  |  |  | Shamoly | 889785.1108
|  |  |  | Tejgaon | 416679.2689
|  |  |  | Satmosjit | 5784.8687
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 21399745.0042 | 23521244.4618
|  |  |  | Kamrangirchar | 2121499.4576
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 2320423.3693 | 3071549.7
|  |  |  | Kakrail | 751126.3307
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1444830.7964 | 9895940.1
|  |  |  | Shere Bangla Nagar | 751163.07
|  |  |  | Shamoly | 4649837.5875
|  |  |  | Satmosjit | 3050108.6461
|  | Banasree 33/11SS |  | Khilgaon | 3317406.3585 | 8823574.9628
|  |  |  | Bansree | 5506168.6043
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 599906.3321 | 9912980.2809
|  |  |  | Bashabo | 3956679.9486
|  |  |  | Mugdapara | 1914791.7041
|  |  |  | Maniknagor | 3441602.296
|  | DMC |  | Bangshal | 2067143.6015 | 4626519.8258
|  |  |  | RAMNA | 1202493.2807
|  |  |  | Lalbagh | 1356882.9435
|  | Green Road Dormatory |  | Paribagh | 4797068.1963 | 7946046.441
|  |  |  | Shere Bangla Nagar | 3148978.2447
|  | BSMMU 33/11KV S/S |  | Kakrail | 1459408.8922 | 3061300.8035
|  |  |  | Paribagh | 1601891.9112
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 4902574.9495 | 7679330
|  |  |  | Satmasjid | 2776755.0505
|  | Dhaka University 33/11 KV SS |  | RAMNA | 969585.7143 | 969585.7143
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 3623336.9891 | 6193900
|  |  |  | Kakrail | 658916.5299
|  |  |  | Tejgaon | 1911646.481
|  | BGB 33/11 KV SS |  | Kamrangirchar | 6222663.7367 | 12042810
|  |  |  | Jigatola | 3449318.8935
|  |  |  | Azimpur | 2370827.3697
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2026454.5597 | 2026454.5597
|  | BB Avenue 33/11 KV SS |  | Narinda | 1313879.3085 | 4017030.0527
|  |  |  | Ramna | 2703150.7442
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 9777286.3631 | 11767500
|  |  |  | Dhanmondi | 1990213.6369
|  | Ispahani 33/11 KV SS |  | Moghbazar | 1673486.7513 | 3517108.6043
|  |  |  | Kakrail | 1843621.853
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 5918400 | 5918400
|  | Bosila-1(Shopnodanga) 33/11 kv |  | Kamrangirchar | 3113479.9006 | 3113479.9006
|  |  |  | Total=> | 296610918.2988 | 299407142.6496
NORTH ZONE TOTAL=>
|  | NOCS |  | 296610918.2988 |  | 200857461
|  | diff |  |  | -296610918.2988
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 3818400
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 3818400
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 0 | 9726656.1946
|  |  |  | Swamibagh | 3490097.0483
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 6236559.1463
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 7260102
|  |  |  | Bangshall | 505027.0329
|  |  |  | Banglabazar | 6755074.9671
| 4 | Maderteck 33/11KV S/S |  | Banosree | 2547012.8422 | 11998384.6915
|  |  |  | Bashabo | 1009231.7153
|  |  |  | Maniknagar | 146316.4753
|  |  |  | Mugdapara | 8295823.6588
| 5 | Kazla 33/11KV S/S |  | Matual | 230784.8531 | 23717691.9403 | 40435482.9851
|  |  |  | Jurain | 3891505.5223
|  |  |  | Swamibagh | 1168337.3608
|  |  |  | Maniknagar | 1615124.0918
|  |  |  | Shyampur | 1422356.0752
|  |  |  | Kazla | 15389584.0371
|  | Shyampur 132/11KV S/S |  | Shyampur | 33211043.0928 | 33229448.8828 | 56877304.8652
|  |  |  | Fatullah. | 18405.79
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 23647855.9824
|  |  |  | Fatullah | 744533.8231
|  |  |  | Shyampur | 22903322.1592
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 5683138.7023 | 16950968.016
|  |  |  | Jurain | 11267829.3137
| 8 | Postogola 33/11KV S/S |  | Jurain | 4855436.6701 | 11114099.3614
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 6258662.6913
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 7788343.8549 | 10319515.3191
|  |  |  | Narayanganj (West) | 1492793.6821
|  |  |  | Shitalakhy | 1038377.7822
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 977599.9691 | 9688954.9479
|  |  |  | Shitalakhy | 6898451.2121
|  |  |  | Narayanganj (West) | 1809367.1338
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 3536.6329
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 440817.1408
| 11 |  |  | Narayanganj (West) | 13075039.6658 | 13515856.8066
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 13557420.3071 | 13557420.3071 | 22055544.2009
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 8308303.5132 | 8498123.8938
|  |  |  | Matuail | 189820.3806
| 14 | Sarulia 33/11KV S/S |  | Demra | 11265395.433 | 12908664.2467
|  |  |  | Matuail | 1643268.8138
|  | Demra 33/11KV S/S |  | Matuail | 5351604.1407 | 16790041
| 15 |  |  | Demra | 1478553.6211
|  |  |  | Siddhirganj | 9959883.2382
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 832840.5311 | 10606184.0964
| 16 |  |  | Narayanganj (East) | 4354306.9029
|  |  |  | Narayanganj (West) | 5419036.6624
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 2247055.4835 | 10557203.3308
|  |  |  | Narayanganj (East) | 8310147.8473
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 3935090.7668 | 12851959.997
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 335552.8794
|  |  |  | Fatullah | 1930478.5774
|  |  |  | Matuail | 6650837.7734
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 3654741 | 3654741
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 1039856.1088 | 8216222.2715 | 8907422.2715
|  |  |  | Maniknagar | 7176366.1627
|  | IG Gate 33/11 kv |  | Swamibagh | 3510378.6419 | 10415754
|  |  |  | Banglabazr | 3050706.3556
|  |  |  | Postogola | 3854669.0025
|  | Motijil 33/11kv |  | kamlapur | 4882398.4888 | 5183100
|  |  |  | RAMNA | 300701.5112
|  | Mitford 33/11kv |  | Banshal | 4866181.2983 | 5237128.8
|  |  |  | Lalbagh | 370947.5017
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 3698338.0637 | 11318458.518
|  |  |  | Fatullah | 4659046.0959
|  |  |  | Matuail | 2961074.3584
|  | MI CEMENT |  | Shitalakhy | 7422240 | 7422240
|  | Dapa 33/11 kV |  | Fatullah | 9715680 | 9715680
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 6101239.805 | 12919973.3033
|  |  |  | Siddhirganj | 6818733.4983
|  | Amulia 33/11 KV SS |  | Mugdapara | 941069.7534 | 4573944
|  |  |  | Demra | 3632874.2466
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 8023886.2414 | 8023886.2414
|  | P&T 33/11 KV SS |  | Motijeel | 1636046.3803 | 5316000
|  |  |  | RAMNA | 1906219.1771
|  |  |  | Rajarbagh | 1773734.4426
|  | Kazla 132/33 KV SS |  | Kazla | 16717791.0448 | 16717791.0448
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 2656560.1048 | 4220000
|  |  |  | Motijeel | 1563439.8952
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 22446093.7993 | 22446093.7993 | 35802093.7993
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 1865656.4105 | 2887627.5768
|  |  |  | Swamibagh | 756657.54
|  |  |  | Narinda | 265313.6262
|  | 132 KV Shah Cement |  | Sitalakhya | 13356000 | 13356000
|  | 132 KV Metro Rail |  | Motijeel | 691200 | 691200
|  |  |  | Total=> | 413073371.5694 | 312205175.6039 |  | 709684289.8682
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 413073371.5694
| Diff zone&Nocs |  |  |  | 99525870.7557
|  |  |  | Diff= | 0

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 20497418.1246 | 20497418.1246 | 0 | 0
Kakrail | 15696915.8518 | 15696915.8518 | 0 | 0
Moghbazar | 11229690.6168 | 11229690.6168 | 0 | 0
Khilgaon | 9821800.0249 | 9821800.0249 | 0 | 0
Satmosjid | 13003857.5391 | 13003857.5391 | 0 | 0
Sherebanglanagar | 14426676.3134 | 14426676.3134 | 0 | 0
Dhanmondi | 13420007.9536 | 13420007.9536 | 0 | 0
Jhigatala | 17296553.3996 | 17296553.3996 | 0 | 0
Azimpur | 12315561.2166 | 12315561.2166 | 0 | 0
Paribagh | 20470509.3764 | 20470509.3764 | 0 | 0
Shyamoli | 10634428.2931 | 10634428.2931 | 0 | 0
Adabor | 19561671.6605 | 19561671.6605 | 0 | 0
Lalbagh | 31442028.8478 | 31442028.8478 | 0 | 0
Kamrangirchar | 32802355.567 | 32802355.567 | 0 | 0
Ramna | 15785201.4197 | 15785201.4197 | 0 | 0
Rajarbagh | 10303352.5377 | 10303352.5377 | 0 | 0
Bashabo | 8008237.0387 | 8008237.0387 | 0 | 0
Bonoseeri | 14579067.306 | 14579067.306 | 0 | 0
Motijheel | 14643049.1245 | 14643049.1245 | 0 | 0
Mughdapara | 11151685.1163 | 11151685.1163 | 0 | 0
Banglabazar | 10775125.8888 | 10520068.8888 | -255057 | -2.4245 | -255057
Bongshal | 12524148.6368 | 12779205.6368 | 255057 | 1.9959 | 255057
Narinda | 8717278.4575 | 8717278.4575 | 0 | 0
Swamibagh | 8925470.591 | 8925470.591 | 0 | 0
Kazla | 32107375.0819 | 32107375.0819 | 0 | 0
Maniknagar | 13419265.1347 | 13419265.1347 | 0 | 0
Shyampur | 67253750.9726 | 67253750.9726 | 0 | 0
Matuail | 17027390.32 | 17027390.32 | 0 | 0
Postogola | 10113331.6938 | 10113331.6938 | 0 | 0
Jurain | 20014771.5061 | 20014771.5061 | 0 | 0
Narayangonj-West | 24043292.6275 | 24043292.6275 | 0 | 0
Narayangonj-East | 23678385.2911 | 23678385.2911 | 0 | 0
Damra | 16376823.3007 | 16376823.3007 | 0 | 0
Siddhirgonj | 38644340.5568 | 38644340.5568 | 0 | 0
Fatulla | 24856488.1413 | 24856488.1413 | 0 | 0
Shitalakha | 64116984.3398 | 64116984.3398 | 0 | 0
TOTAL=> | 709684289.8682 | 709684289.8682 | 0 | 0

## SS List (hidden)
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2350.93 | 2364.83 | 13.9 | 720000 | 10008000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2318.9 | 2332.75 | 13.85 | 720000 | 9972000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2090.21 | 2111.95 | 21.74 | 720000 | 15652800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1955.87 | 1979.75 | 23.88 | 480000 | 11462400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2224.38 | 2240.56 | 16.18 | 240000 | 0 | 3883200 | 3890954.2027 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2532.16 | 2550.37 | 18.21 | 240000 | 0 | 4370400 | 4379127.0723 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1550.75 | 1562.31 | 11.56 | 240000 | 0 | 2774400 | 2779940.0855 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 913.91 | 924.13 | 10.22 | 240000 | 0 | 2452800 | 2457697.8956 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1924.77 | 1936.17 | 11.4 | 240000 | 0 | 2736000 | 2741463.4061 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1259.49 | 1266.06 | 6.57 | 240000 | 0 | 1576800 | 1579948.6472 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.91 | 462.91 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 484.37 | 493.4 | 9.03 | 240000 | 0 | 2167200 | 2171527.5927 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2225.57 | 2241.26 | 15.69 | 240000 | 0 | 3765600 | 3773119.372 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1732.79 | 1746.61 | 13.82 | 240000 | 0 | 3316800 | 3323423.1818 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 783.4 | 792.87 | 9.47 | 240000 | 0 | 2272800 | 2277338.461 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2118.25 | 2144.4 | 26.15 | 240000 | 0 | 6276000 | 6288532.2867 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 0.95 | 1919.51 | 1933.54 | 14.03 | 240000 | From Downstream R Phase CT Problem | 4764231 | 4773744.4973 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 183.05 | 186.31 | 3.26 | 240000 | 0 | 782400 | 783962.3424 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1566.28 | 1589.93 | 23.65 | 240000 | 0 | 5676000 | 5687334.1714 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.03.2024 | Reading at 00.00hr 01.03.2024 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2350.93 | 2364.83 | 13.9 | 720000 | 10008000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2318.9 | 2332.75 | 13.85 | 720000 | 9972000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2090.21 | 2111.95 | 21.74 | 720000 | 15652800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1955.87 | 1979.75 | 23.88 | 480000 | 11462400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2224.38 | 2240.56 | 16.18 | 240000 | 0 | 3883200 | 3890954.2027 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2532.16 | 2550.37 | 18.21 | 240000 | 0 | 4370400 | 4379127.0723 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1550.75 | 1562.31 | 11.56 | 240000 | 0 | 2774400 | 2779940.0855 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 913.91 | 924.13 | 10.22 | 240000 | 0 | 2452800 | 2457697.8956 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1924.77 | 1936.17 | 11.4 | 240000 | 0 | 2736000 | 2741463.4061 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1259.49 | 1266.06 | 6.57 | 240000 | 0 | 1576800 | 1579948.6472 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.91 | 462.91 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 484.37 | 493.4 | 9.03 | 240000 | 0 | 2167200 | 2171527.5927 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2225.57 | 2241.26 | 15.69 | 240000 | 0 | 3765600 | 3773119.372 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1732.79 | 1746.61 | 13.82 | 240000 | 0 | 3316800 | 3323423.1818 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 783.4 | 792.87 | 9.47 | 240000 | 0 | 2272800 | 2277338.461 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2118.25 | 2144.4 | 26.15 | 240000 | 0 | 6276000 | 6288532.2867 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 0.95 | 1919.51 | 1933.54 | 14.03 | 240000 | From Downstream R Phase CT Problem | 4764231 | 4773744.4973 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 183.05 | 186.31 | 3.26 | 240000 | 0 | 782400 | 783962.3424 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1566.28 | 1589.93 | 23.65 | 240000 | 0 | 5676000 | 5687334.1714 | 0 | Dhanmondi 132/33/11KV S/S