## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month August-2023 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 532 | 1 | 960000 | 2227.617 | 2227.617 | 0 |  | 0 | 1950.36 | 1950.36 | 0 |  | 0 | -71040 | -1246080 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 666.546 | 666.62 | 0.074 | 71040 |  | 374.461 | 375.759 | 1.298 | 1246080 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 289.542 | 319.579 | 30.037 |  | 28835520 | 129.381 | 142.794 | 13.413 |  | 12876480 | 28835520 | 12876480 | 0.91 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 133.648 | 142.531 | 8.883 |  | 8527680 | 46.369 | 49.067 | 2.698 |  | 2590080 | 8527680 | 2590080 | 0.96 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Exp | PN-1711A04601 | 1 | 960000 | 363.871 | 363.871 | 0 |  | 0 | 211.998 | 211.998 | 0 |  | 0 | 0 | 0 |  |  | 0
|  |  | 132 | Imp |  |  | 960000 | 5.419 | 5.419 | 0 | 0 |  | 4.069 | 4.069 | 0 | 0 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 71040 | 37363200 |  |  | Total=> | 1246080 | 15466560 | 37292160 | 14220480 | 0.93 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 8993 624 | 1 | 960000 | 4793.7 | 4818.99 | 25.29 |  | 24278400 | 2384.979 | 2389.746 | 4.767 |  | 4576320 | 24278400 | 4576320 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 11.003 | 11.003 | 0 | 0 |  | 7.78 | 7.78 | 0 | 0 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 24278400 |  |  | Total=> | 0 | 4576320 | 24278400 | 4576320 | 0.98 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 8993 518 | 1 | 960000 | 1115.068 | 1133.719 | 18.651 |  | 17904960 | 760.831 | 767.159 | 6.328 |  | 6074880 | 17904960 | 6072960 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 70.056 | 70.056 | 0 | 0 |  | 141.149 | 141.151 | 0.002 | 1920 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 291.99 | 310.946 | 18.956 |  | 18197760 | 114.738 | 121.332 | 6.594 |  | 6330240 | 18197760 | 6327360 | 0.94 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.361 | 4.361 | 0 | 0 |  | 30.491 | 30.494 | 0.003 | 2880
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 0 | 36102720 |  |  | Total=> | 4800 | 12405120 | 36102720 | 12400320 | 0.95
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 2821.29 | 2864.027 | 42.737 |  | 20513760 | 1151.132 | 1166.254 | 15.122 |  | 7258560 | 20513760 | 7258560 | 0.94 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8421.345 | 8461.981 | 40.636 |  | 19505280 | 4938.272 | 4957.723 | 19.451 |  | 9336480 | 19505280 | 9336480 | 0.9 | 0 | 0
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8373.619 | 8414.47 | 40.851 |  | 19608480 | 4897.776 | 4917.333 | 19.557 |  | 9387360 | 19608480 | 9387360 | 0.9 | 0 | 0
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 278.728 | 300.247 | 21.519 |  | 10329120 | 53.77 | 57.534 | 3.764 |  | 1806720 | 10329120 | 1806720 | 0.99 | 0 | 0
[10 empty] | Total=> | 0 | 69956640 |  |  | Total=> | 0 | 27789120 | 69956640 | 27789120 | 0.93
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 8993 683 | 1 | 960000 | 8336.501 | 8374.227 | 37.726 |  | 36216960 | 4648.827 | 4665.32 | 16.493 |  | 15833280 | 36216960 | 15833280 | 0.92 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 8993 682 | 1 | 960000 | 8326.822 | 8364.206 | 37.384 |  | 35888640 | 4643.449 | 4659.86 | 16.411 |  | 15754560 | 35888640 | 15754560 | 0.92 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 8993 681 | 1 | 1440000 | 2642.939 | 2668.601 | 25.662 |  | 36953280 | 1373.998 | 1379.932 | 5.934 |  | 8544960 | 36953280 | 8544960 | 0.97 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 9.184 | 9.184 | 0 | 0 |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 8993 680 | 1 | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 22.279 | 22.279 | 0 | 0 |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 8993 555 | 1 | 1440000 | 2779.681 | 2809.435 | 29.754 |  | 42845760 | 1295.83 | 1308.771 | 12.941 |  | 18635040 | 42845760 | 18635040 | 0.92 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 771.699 | 771.699 | 0 | 0 |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 0 | 151904640 |  |  | Total=> | 0 | 58767840 | 151904640 | 58767840 | 0.93 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993 631 | 1 | 960000 | 5799.375 | 5841.503 | 42.128 |  | 40442880 | 2961.515 | 2980.879 | 19.364 |  | 18589440 | 40442880 | 18589440 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4947.971 | 4980.479 | 32.508 |  | 31207680 | 2515.748 | 2530.474 | 14.726 |  | 14136960 | 31207680 | 14136960 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4400.359 | 4415.048 | 14.689 |  | 14101440 | 1769.916 | 1771.512 | 1.596 |  | 1532160 | 14101440 | 1532160 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.561 | 1.561 | 0 | 0 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993 660 | 1 | 960000 | 4084.578 | 4098.55 | 13.972 |  | 13413120 | 1631.928 | 1634.163 | 2.235 |  | 2145600 | 13413120 | 2145600 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.33 | 1.33 | 0 | 0 |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 5014 6667 | 1 | 960000 | 1786.459 | 1814.41 | 27.951 |  | 26832960 | 653.682 | 665.022 | 11.34 |  | 10886400 | 26832960 | 10886400 | 0.93 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 5014 6668 | AMR | 960000 | 1580.626 | 1608.469 | 27.843 |  | 26729280 | 678.916 | 690.233 | 11.317 |  | 10864320 | 26729280 | 10864320 | 0.93 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 4262 7810 | 1 | 960000 | 157.05 | 175.359 | 18.309 |  | 17576640 | 2.506 | 2.984 | 0.478 |  | 458880 | 17576640 | 458880 | 1 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 59.408 | 61.056 | 1.648 | 1582080 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 4262 7812 | 1 | 960000 | 158.41 | 176.915 | 18.505 |  | 17764800 | 1.812 | 2.11 | 0.298 |  | 286080 | 17764800 | 286080 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 62.793 | 64.73 | 1.937 | 1859520
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 0 | 188068800 |  |  | Total=> | 3441600 | 58899840 | 188068800 | 55458240 | 0.96 |  | 0
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3181.398 | 3226.15 | 44.752 |  | 85923840 | 1611.006 | 1628.558 | 17.552 |  | 33699840 | 85923840 | 33699840 | 0.93 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3174.787 | 3218.346 | 43.559 |  | 83633280 | 1608.456 | 1625.606 | 17.15 |  | 32928000 | 83633280 | 32928000 | 0.93 | 0 | 0
[10 empty] | Total=> |  | 169557120 |  |  | Total=> | 0 | 66627840 | 169557120 | 66627840 | 0.93
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1441.023 | 1475.868 | 34.845 |  | 66902400 | 708.263 | 720.794 | 12.531 |  | 24059520 | 66902400 | 24059520 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1532.023 | 1566.65 | 34.627 |  | 66483840 | 748.233 | 760.789 | 12.556 |  | 24107520 | 66483840 | 24107520 | 0.94 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 133386240 |  |  | Total=> | 0 | 48167040 | 133386240 | 48167040 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 891.973 | 925.846 | 33.873 |  | 48777120 | 197.156 | 200.925 | 3.769 |  | 5427360 | 48777120 | 5425920 | 0.99 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.021 | 0 | 0 |  | 0.835 | 0.836 | 0.001 | 1440
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 609.476 | 643.19 | 33.714 |  | 48548160 | 251.93 | 267.605 | 15.675 |  | 22572000 | 48548160 | 22572000 | 0.91 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.831 | 0.831 | 0 | 0 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 0 | 97325280 |  |  | Total=> | 1440 | 27999360 | 97325280 | 27997920 | 0.96
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 259.986 | 272.674 | 12.688 |  | 12180480 | 67.655 | 70.658 | 3.003 |  | 2882880 | 12180480 | 2882880 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 171.744 | 186.579 | 14.835 |  | 14241600 | 38.247 | 42.205 | 3.958 |  | 3799680 | 14241600 | 3799680 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 32.177 | 32.187 | 0.01 |  | 9600 | 16.205 | 16.211 | 0.006 |  | 5760 | 9600 | 5760
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 18.041 | 18.041 | 0 | 0 |  | 14.511 | 14.511 | 0 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[10 empty] | Total=> | 0 | 26431680 |  |  | Total=> | 0 | 6688320 | 26431680 | 6688320 | 0.97
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 71040 | 934374720 |  |  |  | 4693920 | 327387360
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 934303680 |  |  |  |  | 322693440 | 934303680 | 322693440 | 0.95 |  | 0 |  | 0.94521
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 934303680 |  | 322693440 |  | 0.95 | 0
[8 empty] | PDB Unit |  | 934303680 |  | KWH
[8 empty] | PGCB Unit |  | 934303680 |  | KWH
33 KV LEVEL | [10 empty] | Month August-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Exp | 8993 841 | 1 | 18000 | 29344.892 | 29344.892 | 0 |  | 0 | 7711.314 | 7711.314 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Shah Cement |  | 33 | Exp | 8993 841 | 1 | 36000 | 39374.588 | 39440.16 | 65.572 |  | 2360592 | 10394.464 | 10414.557 | 20.093 |  | 723348 | 2360592 | 723348 | 0.95612 | 0 | 0 | 0
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 2360592 |  |  | Total=> | 0 | 723348 | 2360592 | 723348 | 0.95612 |  | 0 | 0
6 | Jigatala (JP garden) | Kallyanpur | 33 | Exp | 8993834 (old) | 1 | 180000 | 1072.053 | 1072.053 | 0 |  | 0 | 547.36 | 547.36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.22 | 1.28 | 0.06 |  | 10800 | 0.103 | 0.103 | 0 |  | 0 | 10800 | 0 | 0 | 0 | 0 | 0
7 | Shere Bangla |  | 33 | Exp | 8993 833 | 1 | 180000 | 317.19 | 317.734 | 0.544 |  | 97920 | 244.204 | 244.376 | 0.172 |  | 30960 | 97920 | 30960 | 0.95348 | 0 | 0 | 0
8 | Satmosjid-1 |  | 33 | Exp | 8993 638E | 1 | 180000 | 4191.915 | 4199.888 | 7.973 |  | 1435140 | 2255.39 | 2256.123 | 0.733 |  | 131940 | 1435140 | 131940 | 0.9958 | 0 | 0 | 0
9 | Satmosjid -2 |  | 33 | Exp | 8993 669E | 1 | 180000 | 5801.534 | 5848.148 | 46.614 |  | 8390520 | 2641.666 | 2657.404 | 15.738 |  | 2832840 | 8390520 | 2832840 | 0.94746 | 0 | 0 | 0
10 | Kallayanpur T3 |  | 33 | Exp | 8993 831 | 1 | 180000 | 6518.449 | 6541.77 | 23.321 |  | 4197780 | 3183.572 | 3192.261 | 8.689 |  | 1564020 | 4197780 | 1564020 | 0.93707 | 0 | 0 | 0
11 | Kallayanpur T4 |  | 33 | Exp | 8993 839 | 1 | 180000 | 8670.191 | 8728.462 | 58.271 |  | 10488780 | 4041.326 | 4065.187 | 23.861 |  | 4294980 | 10488780 | 4294980 | 0.92542 | 0 | 0 | 0
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 116.135 | 143.388 | 27.253 |  | 4905540 | 29.486 | 36.389 | 6.903 |  | 1242540 | 4905540 | 1242540 | 0.96939 | 0 | 0 | 0
| Exp to Desco at 11 KV | [9 empty] | 8074556.4 |  |  |  |  | 1293025.2 |  | -8074556.4 | -1293025.2 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Exp | 8993 836E | 1 | 180000 | 5452.879 | 5452.879 | 0 |  | 0 | 2686.619 | 2686.619 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | Total=> | 8074556.4 | 29526480 |  |  | Total=> | 1293025.2 | 10097280 | 21451923.6 | 8804254.8 | 0.92512 |  |  | 0
SATMOSJID 132/33KV SS
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3141.193 | 3188.097 | 46.904 |  | 35178000 | 1579.213 | 1597.37 | 18.157 |  | 13617750 | 35178000 | 13617750 | 0.93256 | 0 | 0 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 2781.285 | 2828.681 | 47.396 |  | 35547000 | 1375.53 | 1393.883 | 18.353 |  | 13764750 | 35547000 | 13764750 | 0.93253 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 70725000 |  |  | Total=> | 0 | 27382500 | 70725000 | 27382500 | 0.93255 | 0 | 0 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1 | 180000 | 1910.455 | 1934.95 | 24.495 |  | 4409100 | 643.896 | 648.789 | 4.893 |  | 880740 | 4409100 | 880740 | 0.98063 | 0 | 0 | 3357
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1 | 180000 | 663.099 | 678.859 | 15.76 |  | 2836800 | 46.672 | 48.103 | 1.431 |  | 257580 | 2836800 | 257580 | 0.9959 | 0 | 0 | 2160
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1 | 180000 | 106.915 | 106.915 | 0 |  | 0 | 4.16 | 4.16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 1 | 180000 | 1061.83 | 1097.56 | 35.73 |  | 6431400 | 447.236 | 459.149 | 11.913 |  | 2144340 | 6431400 | 2144340 | 0.94866 | 0 | 0 | 4896
20 | Monipuripara-2 |  |  |  |  | 1 | 180000 | 766.09 | 790.448 | 24.358 |  | 4384440 | 280.977 | 286.953 | 5.976 |  | 1075680 | 4384440 | 1075680 | 0.9712 | 0 | 0 | 3338
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 18061740 |  |  | Total=> | 0 | 4358340 | 18061740 | 4358340 | 0.9721 |  | 0 | 13751
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 403596.2 | 408804 | 5207.8 |  | 5337.995 | 258560 | 262073.4 | 3513.4 |  | 3601.235 | 5337.995 | 3601.235 | 0.82899 | 0.06 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 374573.2 | 378951 | 4377.8 |  | 4487.245 | 131463.5 | 132901.7 | 1438.2 |  | 1474.155 | 4487.245 | 1474.155 | 0.95005 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 9825.24 |  |  | Total=> | 0 | 5075.39 | 9825.24 | 5075.39 | 0.88846 |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 343.416 | 345.49 | 2.074 |  | 5102.04 | 218.717 | 220.755 | 2.038 |  | 5013.48 | 5102.04 | 5013.48 | 0.71327 | 0 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 95.379 | 102.714 | 7.335 |  | 18044.1 | 52.31 | 55.582 | 3.272 |  | 8049.12 | 18044.1 | 8049.12 | 0.91326 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 23146.14 |  |  | Total=> | 0 | 13062.6 | 23146.14 | 13062.6 | 0.87089 |  |  | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 8074556.4 | 120706783.38 |  |  |  | 1293025.2 | 42579605.99 | [5 empty] | 13751 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 112632226.98 |  |  |  |  | 41286580.79 | 112632226.98 | 41286580.79 | 0.93891 |  | 0 |  | 0.93891
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 756860 |  |  | 113389086.98
33 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 112632226.98 |  | 41286580.79 |  | 0.93891 | 0
[8 empty] | PDB Unit |  | 112632226.98 |  | KWH
[8 empty] | PGCB Unit |  | 112632226.98 |  | KWH
11 KV LEVEL | [10 empty] | Month August-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [9 empty] | Total=> |  | 0 |  |  |  |  | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 1502 6 | 1 | 40000 | 9179.18 | 9192.48 | 13.3 |  | 532000 | 3461.52 | 3465.62 | 4.1 |  | 164000 | 545300 | 168100 | 0.95562 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 1502 7 | 1 | 40000 | 3863.97 | 3867.99 | 4.02 |  | 160800 | 1263.16 | 1263.32 | 0.16 |  | 6400 | 164820 | 6560 | 0.99921 | 1 |  | 6400 | RMU Feeder KVARH Back Calculation as per KWH Percentage
3a | PD Betar |  | 11 | Imp | 2612 100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612 100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 1502 5 | 1 | 40000 | 3977.36 | 3978.44 | 1.08 |  | 43200 | 1887.8 | 1888.77 | 0.97 |  | 38800 | 44280 | 39770 | 0.74398 | 1.2097
5 | BICC - U/G |  | 11 | Exp | 1502 4 | 1 | 40000 | 1038.1 | 1038.13 | 0.03 |  | 1200 | 297.32 | 297.32 | 0 |  | 0 | 1230 | 0 | 0 | 1
6 | NEC |  | 11 | Exp | 1502 3 | 1 | 40000 | 431.56 | 431.59 | 0.03 |  | 1200 | 56.29 | 56.3 | 0.01 |  | 400 | 1230 | 410 | 0.94868 | 1
7 | Manikmia Avenue |  | 11 | Exp | 7602 6327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 738400 |  |  |  | 0 | 209600 | 756860 | 214840 | 0.96199
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 738400 |  |  |  | 0 | 209600
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 738400 |  |  |  |  | 209600
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 756860 |  |  |  |  | 214840 | 756860 | 214840 | 0.96199 |  | 0 |  | 0.96199
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 756860 |  | 214840 |  | 0.96199 | 0
[8 empty] | PDB Unit |  | 756860 |  | KWH
[8 empty] | PGCB Unit |  | 756860 |  | KWH

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month August-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 934303680 | 8.1335 | 7599158981 |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 934303680 | 934303680 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 7599158981 | 7599158981 | 0
2a | 33kv | 112632226.98 | 8.22 | 925836906 |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 112632226.98 | 112632226.98 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 925836906 | 925836906 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 756860 | 8.22 | 6221389 |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 756860 | 756860 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 6221389 | 6221389 | 0
2c | Bus Loss Units (33kv) | 13749.5 | 8.22 | 113021 |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 13749.5 | 13749.5 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 113021 | 113021 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 113402836.48 |  | 932171316 |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 113402836.48 | 113402836.48 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 932171316 | 932171316 | 0
4 | TOTAL 132kv & 33kv (1+3) | 1047706516.48 |  | 8531330297 |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 1047706516.48 | 1047706516.48 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 8531330297 | 8531330297 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 0 | 8.22 | 0 |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 0 |  | 0 |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 0 | 0 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 0 | 0 | 0
8 | TOTAL Billed Amount => (4+7) | 1047706516.48 |  | 8531330297 |  | 8669086249.94 | 10 | সর্বমোট (৬+৯) | 1047706516.48 | 1047706516.48 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 8531330297 | 8531330297 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 511879818 | Source Tax
10 | NET BILL TOTAL => (8-9) |  |  | 8019450479
11*** | 23th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  | 137755952.94 | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 8157206431.94
"In word: Taka Seven Hundred Ninety Seven Crore Thirteen Lac Twenty Three Thousand Two Hundred Three and Poisa Ninety Four"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | #VALUE!
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Paid
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94 | Certified For Payment
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0
| Total | 3306142870.56
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month August-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [8 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[11 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month August-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 934303680 | 0.2886 | 269640042.048 |  |  | 1 | 132 †Kwf (GbvwR©) | 934303680 | 934303680 | 934303680 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 7599158981 | 269640042.048 | 269640042.048 | 0
2a | 33kv Level | 112632226.98 | 0.2944 | 33158927.6229 |  |  | 2 | 33 †Kwf (GbvwR©) | 112632226.98 | 112632226.98 | 112632226.98 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 925836906 | 33158927.6229 | 33158927.6229 | 0 |  | 33KV Amount (2+3+4) => | 33385795.0597
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 756860 | 0.2944 | 222819.584 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 756860 | 756860 | 756860 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 6221389 | 222819.584 | 222819.584 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 13749.5 | 0.2944 | 4048.2528 |  |  | 4 | 33 ‡Kwf evm jm | 13749.5 | 13749.5 | 13749.5 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 113021 | 4047.8528 | 4048.2528 | -0.4 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 113402836.48 | 0.2944 | 33385795.4597 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 113402836.48 | 113402836.48 | 113402836.48 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 932171316 | 33385795.0597 | 33385795.4597 | -0.4
4 | TOTAL=> (1+3) | 1047706516.48 |  | 303025837.5077 |  |  | 6 | me©‡gvU (1+5) | 1047706516.48 | 1047706516.48 | 1047706516.48 | 0 |  |  | 6 | me©‡gvU (1+5) | 8531330297 | 303025837.1077 | 303025837.5077 | -0.4
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 10th Installment ) |  |  | 25993419.79 |  |  | ‡gvU (GbvwR©) |  | 1047692766.98 | 1047692766.98 | 1047692766.98 | 0 |  |  | ‡gvU (GbvwR©) |  | 8531217276 | 303021789.2549 | 33385795.4597 | 269635993.7952
7 | Grand TOTAL=> (4-5+6) |  |  | 327519257.2977
| CERTIFIED UNITS |  |  | 1047706516.48
| CERTIFIED TAKA |  |  | 303025837.5077
| CERTIFIED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 10th Installment of Wheeling Charge Due) |  |  | 327519257.2977
evsjv
In word: Taka Thirty Two Crore Four Lac Eighty Two Thousand Seven Hundred and Eighty
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Paid
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Paid
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06 | Certified For Payment
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check
[6 empty] | Month August-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 133347946.14 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 133157712 | Fatullah Grid | 40219200 | 190234.14 | 0.1427%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 0 |  |  |  | Shyampur Grid | 92938512
|  |  | 132 | Import |  | 71040 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 28835520 | 37363200 | Postogola 132/33 KV Grid | 37238400 | Postogola Grid | 37238400 | 124800 | 0.334%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 8527680
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 71040 | 37363200
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 24278400 | 124087680 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 123697727.616 | Ullon Grid | 27428927.616 | 389952.384 | 0.3143%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 78600000
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 24278400 |  |  |  | DU Grid | 17668800
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 17904960 | 133428000 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 131184657 | Lalbagh Grid | 48235857 | 2243343 | 1.681%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 34449600
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 18197760 |  |  |  | Jigatola Grid | 48499200
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 36102720
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 20513760 | 59627520 | Sitalakhya 132/33 KV Grid | 59792976 | Sitalakhya Grid | 59792976 | -165456 | -0.2775%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 19505280
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 19608480
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 10329120 | 10329120 | Sitalakhya NOCS | 10329120 | Sitalakhya NOCS | 10329120 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 69956640
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 36216960 | 72105600 | Siddirganj 132/33 KV Grid | 72105600 | Siddirganj Grid | 72105600 | 0 | 0%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 35888640
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 36953280 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 42845760 | 42845760 | Matuail 132/33 KV Grid | 42250986.204 | Matuail Grid | 42250986.204 | 594773.796 | 1.388%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 151904640
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 40442880 | 71650560 | Moghbazar 132/33 KV Grid | 71248262.4 | Moghbazar Gird | 71248262.4 | 402297.6 | 0.5615%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 31207680
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 14101440 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 13413120
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 26832960 | 53562240 | Madartek 132/33 KV Grid | 53562240 | Madartek Grid | 53562240 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 26729280
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 17576640 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 17764800
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 188068800
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 85923840 | 169557120 | Maniknagar 132/33 KV Grid | 169653795.2 | Kazla Grid | 58492800 | -96675.2 | -0.05702%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 83633280 |  |  |  | Motijheel Grid | 23299200
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 169557120 |  |  |  | Narinda Grid | 39223795.2
[11 empty] | Bangabhaban Grid | 5820000
[11 empty] | Maniknagar Grid | 42818000
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 66902400 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 66483840
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 133386240
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 48777120 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 48548160
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 97325280
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 12180480 | 26422080 | Charsyedpur 132/33 KV Grid | 26330400 | Charsyedpur Grid | 26330400 | 91680 | 0.347%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 14241600
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 9600 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 0 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 0 | 26431680 | 934326826.14 |  | 930551876.42 |  | 930551876.42 | 3774949.72 | 0.404%
[9 empty] | 33 KV Transmission Loss |  | 112511160.84 | 114710088.9235 | -2198928.0835 | -1.954%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 756860 | 755630 | 1230 | 0.1625%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 1047594846.98 | 1046017595.3435 | 1577251.6365 | 0.1506%
[9 empty] | From Summary Sheet |  |  |  | 5277956.8632 | 0.5038%
[9 empty] | Mismatch in KWH |  |  |  | -3700705.2268
| 33 KV LEVEL |  |  |  |  | Month August-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 2360592 | 2360592 | Sitalakhya NOCS | 2360592 | Sitalakhya NOCS | 2360592 | 0 | 0%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 2360592
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 10800 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 10800 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 10800
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 97920
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 1435140 | 80550660 | Shatmasjid 132/33 KV Grid | 82211573.376 | Asadgate SS | 17514993.376 | -1660913.376 | -2.062%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 8390520 |  |  |  | Lalmatia SS | 14660370
[11 empty] | Japan Garden SS | 17148800
[11 empty] | Jigatola Old SS | 2277600
[11 empty] | Shatmasjid SS | 21537000
[11 empty] | BGB SS | 9072810
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 4197780 | 11517543.6 | Adabor NOCS | 11877454 | Adabor NOCS | 11877454 | -359910.4 | -3.125%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 10488780
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 4905540
| Export to Desco at 11 KV |  |  |  |  | 8074556.4 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 0 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 8074556.4 | 29526480
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 35178000 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 35547000
AGARGAON 132/33KV SS | [5 empty] | 0 | 70725000
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 4409100 | 7245900 | Sherebanglanagar 33/11 KV SS | 7426800 | Sherebanglanagar SS | 7426800 | -180900 | -2.497%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 2836800
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 0 | 6431400 | 10815840 | Monipuripara 33/11 KV SS | 10824074 | Monipuripara SS | 10824074 | -8234 | -0.07613%
20 | Monipuripara-2 |  |  |  |  | 0 | 4384440
| Maniknagar 230/132 kv |  |  |  |  | 0 | 18061740
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 5337.995 | 9825.24 | Maniknagar 33/11 KV SS | 9595.5475 | Maniknagar 33/11 KV SS | 9595.5475 | 229.6925 | 2.338%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 4487.245
Shyampur 230/132 kv | [5 empty] | 0 | 9825.24
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 5102.04 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 18044.1
[6 empty] | 0 | 23146.14
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 8074556.4 | 120706783.38 | 112511160.84 |  | 114710088.9235 |  | 114710088.9235 | -2198928.0835 | -1.954%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 532000 | 756860 | Sherebanglanagar NOCS | 755630 | Sherebanglanagar NOCS | 755630 | 1230 | 0.1625%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 160800
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 43200
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 1200
6 | NEC |  | 11 | Export | 15023 | 0 | 1200
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 738400
TOTAL => | [5 empty] | 0 | 738400 | 756860 |  | 755630 |  | 755630 | 1230 | 0.1625%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 116.133 | 86.616 |  | 29.517 | 180000 | 5313060 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Previous | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8670.191 | 8617.568 |  | 52.623 | 180000 | 9472140 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.68 | 995.74 | 0.06
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6518.449 | 6495.578 |  | 22.871 | 180000 | 4116780 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9633.08 | 9646.16 | 13.08
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4319.26 | 4419.91 | 100.65
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 3664.1 | 3408.3 |  | 262.195 | 8000 | 2097560 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 51326.05 | 51898.42 | 572.37
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 41632.55 | 41923.11 | 290.56
03 |  | 11 KV Bashir Uddin |  | 74819925 | 581.163 | 394.664 |  | 191.1615 | 16000 | 3058583.6 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 1991.3 | 2112.81 | 121.51
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8076.21 | 8192.03 | 115.82
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1125.19 | 1125.19 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9341.2 | 9369.92 | 28.72
05 |  | 11 KV Lalkuthy |  | DHK15018 | 995.15 | 995.15 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9575.06 | 9510.27 |  | 66.4097 | 40000 | 2656390 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [6 empty] | 0
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 51898.42 | 51616.27 |  | 289.2038 | 8000 | 2313630 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  |  | 0
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8192.03 | 8133.47 |  | 60.024 | 40000 | 2400960 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  |  | 0
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2112.81 | 2054.75 |  | 59.5115 | 40000 | 2380460 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  |  | 0
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  |  | 0
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.701 | 3273.696 |  | 0.005125 | 40000 | 205 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  |  | 0
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9646.16 | 9640.43 |  | 5.8732 | 40000 | 234930 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  |  | 0
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9369.92 | 9355.62 |  | 14.6575 | 40000 | 586300 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  |  | 0
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4419.91 | 4371.7 |  | 49.4153 | 40000 | 1976610 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  |  | 0
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.74 | 995.71 |  | 0.03075 | 40000 | 1230 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 41923.11 | 41775.56 |  | 151.2388 | 8000 | 1209910 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 7812738.6 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 11089241.4 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [134 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [174 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[137 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.22066 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 6.4099 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.0278 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.95024 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.0269 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | -0.14892 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.032224 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.1718 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.72315 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.7957 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.070408 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.74731 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 1.1413 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 1.5 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 3.0565 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.36408 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.24021 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 0.21781 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.13914 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 2.1711 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.12321 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.1185 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.064901 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.9508 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | -1.985 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.10871 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 1.7549 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 1 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -2.6717 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.5712 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | 1.1808 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | 0.74913 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.56541 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 1.2174 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.90308 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | -0.25931 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | -0.81695 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.41807 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 1.7781 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 1.0713 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | 0.074283 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | -0.13885 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.34882 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.22403 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.95272 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.20884 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.2584 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 1.444 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 1.0687 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 0.10378 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.041539 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 1.0708 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | 0.13595 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.211 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.010028 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | -0.42556 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -1.9122 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -0.048314 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 0.29445 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | -0.86273 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.064233 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.25381 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.2284 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.41499 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.57602 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | -0.26653 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 1.0739 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.1039 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.23019 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 0.74837 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.4865 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 0.18209 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 0.096193 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | -0.64219 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 1.8284 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.16433 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | -0.8103 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.3703 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | -0.12622 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | 0.038802 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 1.4646 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | 1.1051 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.12694 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.40336 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.80075 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.15019 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.72448 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 0 | 0.033974

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) | 132 | IMPORT |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000
| 132 KV DHANMONDI-3 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000
[8 empty] | Total Import/Export |  | 0 | 0
[9 empty] | Net Total | 60810000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 | 132 |  | SIEM0480 | 1 | 1632756 | 1632756 | 0 | 1000 | 0
| 132 kV Dhaka University | 132 |  | SIEM0480 | 1 | 79348 | 96919 | 17571 | 1000 | 17571000
3 | 132 kV Dhaka University | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 | 132 |  | SIEM0481 | 1 | 2131079 | 2161566 | 30487 | 1000 | 30487000
8 | 132 kV Ullon Circuit-3 | 132 |  | SIEM0484 | 1 | 2887068 | 2917391 | 30323 | 1000 | 30323000
[6 empty] | 0 | 0 | Total Import/Export |  | 78381000 | 0
[6 empty] | 0 | 0 | Net Total |  | 78381000
| DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 132 KV Dhaka University (Export) | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) | 132 |  |  | 1 | 79348 | 96919 | 17571 | 1000 |  | 17571000
[6 empty] | 0 | 0 |  | Total |  | 17571000
| DHANMONDI 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) | 132 | NET IMPORT | SIEM0487 | 1 | 869330 | 886482 | 17152 | 1000 |  | 17152000
5 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | SIEM0496 | 1 | 1463850 | 1472967 | 9117 | 2000 |  | 18234000
9 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | SIEM0493 | 1 | 1334171 | 1343240 | 9069 | 2000 |  | 18138000
10 | 132/33kV, 80/120 MVA GT-3 (HV) | 132 |  | SIEM0497 | 1 | 1298503 | 1310910 | 12407 | 2000 |  | 24814000
[9 empty] | Total |  | 78338000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 78338000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 78338000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 78338000 |  | 132/33 kv GT LV Side |  | 78600000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -262000
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.3344%
| 132 KV TOTAL IMPORT |  | 78338000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2234.48 | 2259.85 | 25.37 | 720000 | 18266400
12 | 132/33 kV GT-2 Incoming | 33 |  | BD001818 | 1 | 2203.57 | 2228.85 | 25.28 | 720000 | 18201600
17 | 132/33 kV GT-3 Incoming | 33 |  | BD001863 | 1 | 1933.1 | 1967.67 | 34.57 | 720000 | 24890400
24 | 132/33 kV GT-4 Incoming | 33 |  | BD001916 | 1 | 1802.6 | 1838.52 | 35.92 | 480000 | 17241600
[6 empty] | 0 | 0 |  | Total | 78600000 |  | 0
| DHANMONDI 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [6 empty] | 15280922.5567 | Dhanmondi 33/11 kv ss | 0.1718 |  | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 | 33 |  | BD001861 | 1 | 2082.67 | 2113.89 | 31.22 | 240000 |  | 7492800 | 7495214.4889 | [5 empty] | 33/11 kV 20/28 MVA T-1 | 7495214.4889 | 7271355.7389 | 223858.75 | 3.0786 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 |  | BD001892 | 1 | 2383.66 | 2416.09 | 32.43 | 240000 |  | 7783200 | 7785708.0678 | [5 empty] | 33/11 kV 20/28 MVA T-2 | 7785708.0678 | 8092625.1123 | -306917.0445 | -3.7926 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 15276000 | 15280922.5567 | [5 empty] | 33 KV Feeders | 15280922.5567 | 15363980.8512 | -83058.2945 | -0.5406 | OK
5 | New Ramna Circuit-1 | 33 |  | BD001919 | 1 | 1460.93 | 1476.87 | 15.94 | 240000 |  | 3825600 | 3826832.766 |  | 8148224.848 | New Ramna 33/11 kv ss | 1.7957 |  | New Ramna Circuit-1 | 3826832.766 | 2353344.9882 | 1473487.7778 | 62.6125 | FAULT
8 | Kakrail Circuit-1 | 33 |  | BD001825 | 1 | 826.76 | 848.87 | 22.11 | 240000 |  | 5306400 | 5308109.9408 | [5 empty] | Kakrail Circuit-1 | 5308109.9408 | 5434305.8247 | -126195.8839 | -2.3222 | OK
9 | Kawran Bazar Circuit-1 | 33 |  | BD001820 | 1 | 1843.63 | 1860.74 | 17.11 | 240000 |  | 4106400 | 4107723.2513 |  | 10621021.4283 | Kakrail 33/11 kv ss | 1.1413 |  | Kawran Bazar Circuit-1 | 4107723.2513 | 4173585.2953 | -65862.044 | -1.5781 | OK
10 | New Ramna Circuit-2 | 33 |  | BD001816 | 1 | 1192.37 | 1210.37 | 18 | 240000 |  | 4320000 | 4321392.082 | [5 empty] | New Ramna Circuit-2 | 4321392.082 | 3837393.1542 | 483998.9279 | 12.6127 | OK
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 |  | 0 | 0 |  | 4107723.2513 | Kawran Bazar 33/11 kv ss | 0.72315 |  | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder | 33 |  | BD001840 | 1 | 405.5 | 420.58 | 15.08 | 240000 |  | 3619200 | 3620366.2554 | [5 empty] | DMC Hospital Feeder | 3620366.2554 | 3390737.8809 | 229628.3745 | 6.7722 | OK
15 | Green Road Circuit-2 (U/G) | 33 |  | BD001918 | 1 | 2087.7 | 2116.15 | 28.45 | 240000 |  | 6828000 | 6830200.263 |  | 3620366.2554 | DMC Hospital 33/11 kv ss | 0.74913 |  | Green Road Circuit-2 (U/G) | 6830200.263 | 6704631.8438 | 125568.4192 | 1.8729 | OK
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1612.37 | 1634.5 | 22.13 | 240000 |  | 5311200 | 5312911.4875 | [5 empty] | Kakrail Circuit-2 | 5312911.4875 | 5575986.7985 | -263075.3109 | -4.718 | OK
18 | BSMMU Hospital Circuit-1 | 33 |  | BD001920 | 1 | 710.95 | 725.99 | 15.04 | 240000 |  | 3609600 | 3610763.1619 |  | 14330216.2987 | Green Road 33/11 kv ss | 1.0278 |  | BSMMU Hospital Circuit-1 | 3610763.1619 | 3859005.5061 | -248242.3442 | -6.4328 | OK
19 | Azimpur Circuit-1 | 33 |  | BD001822 | 1 | 1978.52 | 2016.45 | 37.93 | 240000 |  | 9103200 | 9106133.4262 | [5 empty] | Azimpur Circuit-1 | 9106133.4262 | 8671355.8696 | 434777.5566 | 5.014 | OK
20 | Azimpur Circuit-2 | 33 |  | BD001857 | 1 | 1809.7 | 1843.76 | 34.06 | 240000 |  | 8174400 | 8177034.1286 |  | 5183269.7251 | BSMMU 33/11 kv ss | 1.2174 |  | Azimpur Circuit-2 | 8177034.1286 | 1279931.5089 | 6897102.6197 | 538.865 | FAULT
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 151.65 | 158.2 | 6.55 | 240000 |  | 1572000 | 1572506.5632 | [5 empty] | BSMMU Hospital Circuit-2 | 1572506.5632 | 1541681.1045 | 30825.4587 | 1.9995 | OK
23 | Green Road Circuit-1 | 33 |  | BD001865 | 1 | 1411.09 | 1442.33 | 31.24 | 240000 |  | 7497600 | 7500016.0357 |  | 17283167.5547 | Azimpur 33/11 kv ss | 1.9508 |  | Green Road Circuit-1 | 7500016.0357 | 7602745.1352 | -102729.0995 | -1.3512 | OK
26 | 33/0.4 kV, 500 kVA AT-1 | 0.4 |  | 84.2659 | 1 | 316189 | 318696 | 2507 | 10 |  | 25070 | 25078.0786 | Paribag |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 25078.0786 | 24914.239 | 163.8396 | 0.65761 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 |  | 84.2673 | 1 | 478688 | 478689 | 1 | 10 |  | 10 | 10.0032 | Paribag |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 10.0032 | 0 | 10.0032 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 63298680 | 63319077.4433 | [6 empty] | 63319077.4433 | 54449619.1488 | 8869458.2945 | 16.2893 | OK
[8 empty] | Grand Total |  | 78600000 | 78574680 | 78600000 | 0.032224
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming | 11 | IMPORT | DHK60884 | 1 | 890566.5 | 933673.09 | 43106.59 | 180 | 7759186.2 |  | 7807222.3224
16 | 33/11 kV Transformer-1 Incoming | 11 |  | DHK60976 | 1 | 495947.4 | 537212.49 | 41265.09 | 180 | 7427716.2 |  | 7473700.2343
[6 empty] | 0 | 0 |  | Total | 15186902.4 |  | 15280922.5567
| DHANMONDI 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 6440974 | 7753091 | 1312117 | 1 |  | 1312117 | 1314371.1616 | Paribag |  |  |  |  | 11 kV Balaka Feeder | 1314371.1616 | 1273734.3863 | 40636.7753 | 3.1904 | OK
5 | 11 kV Mogbazar O/H | 11 |  | HA021100463-02 | 1 | 47694141 | 49253485 | 1559344 | 1 |  | 1559344 | 1562022.8871 | Paribag |  |  |  |  | 11 kV Mogbazar O/H | 1562022.8871 | 1571851.4764 | -9828.5893 | -0.62529 | OK
6 | 11 kV Panthopath Feeder | 11 |  | HA021101078-02 | 1 | 61262551 | 63457175 | 2194624 | 1 |  | 2194624 | 2198394.2713 | Paribag |  |  |  |  | 11 kV Panthopath Feeder | 2198394.2713 | 2202528.7234 | -4134.4521 | -0.18771 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 |  | DHK60882 | 1 | 215574 | 222720.32 | 7146.32 | 60 |  | 428779.2 | 429515.8245 | Paribag |  |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 429515.8245 | 406161.3393 | 23354.4852 | 5.7501 | OK
8 | 11 kV P G Hospital Feeder | 11 |  | DHK60889 | 1 | 283084.6 | 287093.97 | 4009.37 | 60 |  | 240562.2 | 240975.4757 | Paribag |  |  |  |  | 11 kV P G Hospital Feeder | 240975.4757 | 236479.8549 | 4495.6208 | 1.9011 | OK
9 | 11 kV Abdul Monem Ltd | 11 |  | DHK60890 | 1 | 699.41 | 706.8 | 7.39 | 60000 |  | 443400 | 444161.7425 | Paribag |  |  |  |  | 11 kV Abdul Monem Ltd | 444161.7425 | 451511.4107 | -7349.6682 | -1.6278 | OK
10 | 11 kV Surjasen Hall Feeder | 11 |  | DHK60880 | 1 | 552176.6 | 564493.19 | 12316.59 | 60 |  | 738995.4 | 740264.9629 | Ramna |  |  |  |  | 11 kV Surjasen Hall Feeder | 740264.9629 | 797710.3468 | -57445.3839 | -7.2013 | OK
11 | 11 kV Azimpur-1 Feeder | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | 11 |  | DHK60873 | 1 | 928405.7 | 938763.25 | 10357.55 | 60 |  | 621453 | 622520.63 | Ramna |  |  |  |  | 11 kV TSC Feeder | 622520.63 | 596411.0072 | 26109.6228 | 4.3778 | OK
13 | 11 kV SCADA Bhaban | 11 |  | DHK60883 | 1 | 28176.9 | 28300.61 | 123.71 | 60 |  | 7422.6 | 7435.3517 | Paribag |  |  |  |  | 11 kV SCADA Bhaban | 7435.3517 | 6184.9227 | 1250.4291 | 20.2174 | OK
14 | 11 kV DPH Sw/S-2 | 11 |  | DHK60871 | 1 | 493864.3 | 513287.05 | 19422.75 | 60 |  | 1165365 | 1167367.0478 | Paribag |  |  |  |  | 11 kV DPH Sw/S-2 | 1167367.0478 | 1168612.8044 | -1245.7566 | -0.1066 | OK
17 | 11 kV New Elephant Road Feeder | 11 |  | DHK60981 | 1 | 82214.7 | 100470.64 | 18255.94 | 60 |  | 1095356.4 | 1097238.176 | Paribag |  |  |  |  | 11 kV New Elephant Road Feeder | 1097238.176 | 1271574.285 | -174336.109 | -13.7103 | OK
18 | 11 kV Dhanmondi O/H Feeder | 11 |  | DHK61110 | 1 | 404842.1 | 430127.06 | 25284.96 | 60 |  | 1517097.6 | 1519703.9096 | Paribag |  |  |  |  | 11 kV Dhanmondi O/H Feeder | 1519703.9096 | 1444426.5973 | 75277.3123 | 5.2116 | OK
19 | 11 kV Sonargaon Feeder | 11 |  | DHK61115 | 1 | 340916.2 | 369960.07 | 29043.87 | 60 |  | 1742632.2 | 1745625.9685 | Paribag |  |  |  |  | 11 kV Sonargaon Feeder | 1745625.9685 | 1732224.4313 | 13401.5372 | 0.77366 | OK
20 | 11 kV Museum Feeder | 11 |  | DHK61107 | 1 | 547755.5 | 550080.6 | 2325.1 | 60 |  | 139506 | 139745.6654 | Ramna |  |  |  |  | 11 kV Museum Feeder | 139745.6654 | 147111.9421 | -7366.2767 | -5.0073 | OK
21 | 11 kV Shanta property | 11 |  | DHK61112 | 1 | 342098.2 | 345525.51 | 3427.31 | 60 |  | 205638.6 | 205991.8784 | Paribag |  |  |  |  | 11 kV Shanta property | 205991.8784 | 207014.0635 | -1022.185 | -0.49378 | OK
22 | 11 kV BIRDEM RMU Feeder | 11 |  | DHK61108 | 1 | 701416.8 | 716987.97 | 15571.17 | 60 |  | 934270.2 | 935875.2367 | Kakrail |  |  |  |  | 11 kV BIRDEM RMU Feeder | 935875.2367 | 955769.4815 | -19894.2448 | -2.0815 | OK
23 | 11 kV Azimpur-2 Feeder | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 | 11 |  | DHK60978 | 1 | 782449.9 | 797585.77 | 15135.87 | 60 |  | 908152.2 | 909712.3671 | Kakrail |  |  |  |  | 11 kV DPH Sw/S-1 | 909712.3671 | 894673.7786 | 15038.5885 | 1.6809 | OK
[9 empty] | Total | 15280922.5567 | 15254715.6 | 15280922.5567 | 0.1718
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag at 33 KV level |  |  | 11957891.7764
[6 empty] | Azimpur at 33 KV level |  |  | 0
[6 empty] | Ramna at 33 KV level |  |  | 1502531.2583
[6 empty] | Kakrail at 33 KV level |  |  | 1845587.6038
[6 empty] | Total = |  |  | 15306010.6385 | -1.4481e-10
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1843.63 | 1860.74 | 17.11 | 240000 | 0 | 4106400 | 4107723.2513
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 4106400 | 4107723.2513
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar | 33 | 0 | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
KAWRANBAZAR 33 KV SIDE (RECEIVING)
1 | 33 kV Dhanmondi Circuit-1 | 33 |  | DHK61036 | 1 | 3420.84 | 3435.98 | 15.14 | 270000 | 4087800
5 | 33 kV Dhanmondi Circuit-2 | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar | 33 |  | DHK 61038 | 1 | 1059.48 | 1059.48 | 0 | 270000 | 0
[6 empty] | 0 | 0 |  | Total | 4087800 | 0 | 4107723.2513
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | DHK61039 | 1 | 5135.19 | 5157.88 | 22.69 | 180000 |  | 4084200
3 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
[9 empty] | Total |  | 4084200
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4107723.2513 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 4107723.2513
| MOGBAZAR 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 4107723.2513 |  | 33 KV TX HV SIDE |  | 4084200
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 23523.2513
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5727%
| TOTAL IMPORT |  | 4107723.2513
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK00182 | 1 | 14055.6 | 14457.4 | 401.8 | 10000 | 4018000 |  | 4107723.2513
15 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
[6 empty] | 0 | 0 |  | Total | 4018000 |  | 4107723.2513
| KAWRANBAZAR 11 KV SIDE |  |  |  |  | 0 | 0
6 | WASA Bhaban | 11 |  | 8536188 | 1.18 | 2503.3 | 271216 | 268712.7 | 1000 | 1024440 | 1024440 | 1031848.2658 | Shere b.nagar | From Customer End | 80 |  |  | WASA Bhaban | 1031848.2658 | 1051553.1772 | -19704.9114 | -1.8739 | OK
7 | Sangsad Bhaban | 11 |  | 8536178 | 1.18 | 572139 | 576073 | 3934 | 44 |  | 204253.28 | 205730.3432 | Shere b.nagar |  | 20 |  |  | Sangsad Bhaban | 205730.3432 | 203697.4272 | 2032.916 | 0.99801 | OK
8 | Air Port Road (West) | 11 |  | 8536182 | 1.18 | 1503.6 | 2353.2 | 849.6 | 1000 |  | 1002528 | 1009777.8086 | Shere b.nagar |  | 60 |  |  | Air Port Road (West) | 1009777.8086 | 1128128.4372 | -118350.6286 | -10.4909 | OK
9 | ICC (PM Office) | 11 |  | 8536193 | 1.18 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  | 20 |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | 11 |  | DHK00183 | 1.18 | 15757.4 | 16418.4 | 661 | 444.44 |  | 346654.3112 | 349161.1513 | Shere b.nagar |  | 40 |  |  | (UTC) Tower | 349161.1513 | 363430.7232 | -14269.5719 | -3.9264 | OK
11 | Sonargaon Hotel | 11 |  | 8536190 | 1.18 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 109995.2784 | 110790.7123 | Kakrail | 7 days load Estimated |  |  |  | Sonargaon Hotel | 110790.7123 | 63163.9823 | 47626.7299 | 75.4017 | FAULT
12 | Panthopath | 11 |  | 8536184 | 1.18 | 35309.1 | 36316 | 1006.9 | 1000 |  | 1188142 | 1196734.0813 | Shere b.nagar |  |  |  |  | Panthopath | 1196734.0813 | 1204221.3334 | -7487.2521 | -0.62175 | OK
13 | Titas Bhaban | 11 |  | DHK00190 | 1.18 | 55753.9 | 56134 | 380.1 | 444.44 |  | 199339.3399 | 200780.8678 | Kakrail |  |  |  |  | Titas Bhaban | 200780.8678 | 155748.3677 | 45032.5001 | 28.9136 | OK
16 | Green Road Dormatory s/s | 11 |  | DHK00021 | 1.18 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | [5 empty] | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 | 11 |  | 85-12906 | 1.18 | 68557 | 68801 | 244 | 10 |  | 2879.2 | 2900.021 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-1 | 2900.021 | 3641.847 | -741.826 | -20.3695 | OK
27 | Aux. Transformer, AT-2 | 11 |  | 85-12909 | 1.18 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 4107723.2513 | 4078231.4095 | 4107723.2513 | 0.72315
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail at 33 KV level |  |  | 311571.5801
[5 empty] | Shere b.nagar at 33 KV level |  |  | 3796151.6712
[5 empty] | Total = |  |  | 4107723.2513 | 0
[8 empty] | Customer Name | Customer Number | Feeder name | Consumption | OMF
[8 empty] | Square Hospital | 27529489 | Wasa Bhaban | 1024440 | 6000
[8 empty] | NOCS Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[8 empty] | ShereBangla Nagar | 2489.44 | 2609.01 | 973.04 | 1024.21
[10 empty] | 2609.01 | 1024.21
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1460.93 | 1476.87 | 15.94 | 240000 | 0 | 3825600 | 3826832.766
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1192.37 | 1210.37 | 18 | 240000 | 0 | 4320000 | 4321392.082
[9 empty] | Total | 0 | 8145600 | 8148224.848
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1553400 | 1556644.1182
[9 empty] | Total | 0 | 1553400 | 1556644.1182
NEW RAMNA 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 9704868.9662
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  |  | 0 |  |  | 0
| Feeder No.2 | 33 | [5 empty] | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.3. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 9704868.9662 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 8148224.848 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9704868.9662
| NARINDA 33 KV SIDE |  | 1556644.1182 |  | 33 KV NET IMPORT |  |  | 9704868.9662 |  | 33 KV TX HV SIDE |  | 9704868.9662
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 9704868.9662
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK 00002 | 1 | 25162.8 | 25537.6 | 374.8 | 10000 | 3748000 |  | 3805034.7182
15 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK 00007 | 1 | 13547.4 | 13973.2 | 425.8 | 10000 | 4258000 |  | 4322795.579
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming | 11 |  | DHKA2182 | 1 | 597.09 | 605.72 | 8.63 | 180000 | 1553400 |  | 1577038.669
[7 empty] | 0 |  | Total | 9559400 |  | 9704868.9662
| NEW RAMNA 11 KV SIDE | [5 empty] | 0
4 | Police Bhaban | 11 |  | DHK 00005 | 1 | 73369.4 | 73629.9 | 260.5 | 444.44 |  | 115776.62 | 117855.6107 | Ramna |  |  |  |  | Police Bhaban | 117855.6107 | 121266.9463 | -3411.3355 | -2.8131 | OK
5 | Water Works | 11 |  | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Lalbag |  |  |  |  | Water Works | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | GPO | 11 |  | DHK 00060 | 1 | 98412.6 | 98961 | 548.4 | 444.44 |  | 243730.896 | 248107.5506 | Ramna |  |  |  |  | GPO | 248107.5506 | 224260.1714 | 23847.3791 | 10.6338 | OK
7 | Culvert Road | 11 |  | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 85 | 1033879.14 | 1052444.418 | Ramna | Estimated |  |  |  | Culvert Road | 1052444.418 | 990314.9211 | 62129.4969 | 6.2737 | OK
8 | Secretariat (East) | 11 |  | DHK00059 | 1 | 81723.1 | 81725.2 | 2.1 | 444.44 |  | 933.324 | 950.0836 | Ramna |  |  |  |  | Secretariat (East) | 950.0836 | 1673.5834 | -723.4998 | -43.2306 | CHECK
9 | Siddik Bazar | 11 |  | DHK00076 | 1 | 30335.3 | 33421.2 | 3085.9 | 444.44 |  | 1371497.396 | 1396125.2558 | Bangshal |  |  |  |  | Siddik Bazar | 1396125.2558 | 499406.3237 | 896718.9321 | 179.557 | FAULT
10 | Bokshi Bazar | 11 |  | DHK 00206 | 1 | 86520.6 | 87765.4 | 1244.8 | 444.44 |  | 553238.912 | 563173.3752 | Ramna |  |  |  |  | Bokshi Bazar | 563173.3752 | 477921.1318 | 85252.2434 | 17.8381 | OK
11 | Ramna 11 kV Sw/S Circuit-1 | 11 |  | DHK00198 | 1 | 46678.5 | 47830.6 | 1152.1 | 444.44 |  | 512039.324 | 521233.9697 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 521233.9697 | 36728.3702 | 484505.5996 | 1319.159 | FAULT
12 | TNT RMU | 11 |  | DHK 00207 | 1 | 61321.1 | 62258.6 | 937.5 | 444.44 |  | 416662.5 | 424144.4724 | Ramna |  |  |  |  | TNT RMU | 424144.4724 | 438569.3066 | -14424.8342 | -3.2891 | OK
13 | DIT 11 kV Sw/S Circuit-1 | 11 |  | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | 11 |  | DHK 00006 | 1 | 69075.5 | 70229.9 | 1154.4 | 444.44 |  | 513061.536 | 522274.5375 | Ramna |  |  |  |  | Secretariat (West) | 522274.5375 | 534325.4145 | -12050.877 | -2.2553 | OK
17 | Ramna 11 kV Sw/S Circuit-2 | 11 |  | DHK00197 | 1 | 86438.2 | 89193.3 | 2755.1 | 444.44 |  | 1224476.644 | 1246464.4649 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 1246464.4649 | 757545.2503 | 488919.2145 | 64.5399 | FAULT
18 | Sayed Nazrul Islam Road | 11 |  | DHK00186 | 1 | 27519.2 | 30378.4 | 2859.2 | 444.44 |  | 1270742.848 | 1293561.4671 | Ramna |  |  |  |  | Sayed Nazrul Islam Road | 1293561.4671 | 1334026.873 | -40465.4059 | -3.0333 | OK
19 | Gulistan Complex | 11 |  | DHK00030 | 1 | 54911.6 | 55416.5 | 504.9 | 444.44 |  | 224397.756 | 228427.247 | Ramna |  |  |  |  | Gulistan Complex | 228427.247 | 210464.4166 | 17962.8304 | 8.5349 | OK
20 | Mohanagor Nattomanso | 11 |  | DHK 00008 | 1 | 99993.3 | 100150.4 | 157.1 | 444.44 |  | 69821.524 | 71075.3031 | Ramna |  |  |  |  | Mohanagor Nattomanso | 71075.3031 | 68978.774 | 2096.5291 | 3.0394 | OK
21 | DIT 11 kV Sw/S Circuit-2 | 11 |  | DHK00196 | 1 | 26040.2 | 27096.1 | 1055.9 | 444.44 |  | 469284.196 | 477711.0916 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-2 | 477711.0916 | 494476.0375 | -16764.9459 | -3.3904 | OK
22 | Jail | 11 |  | DHK00009 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | 11 |  | HA021100713-02 | 1 | 76731766 | 76840413 | 108647 | 1 |  | 108647 | 110597.9648 | Ramna |  |  |  |  | Kosturi Bazar | 110597.9648 | 782852.0054 | -672254.0406 | -85.8724 | CHECK
24 | Kaptan Bazar | 11 |  | HA021101251-02 | 1 | 6664226 | 7099755 | 435529 | 1 |  | 435529 | 443349.7565 | Narinda |  |  |  |  | Kaptan Bazar | 443349.7565 | 434935.9868 | 8413.7696 | 1.9345 | OK
25 | G.T.V | 11 |  | HA-021101054-02 | 1 | 71762722 | 72361607 | 598885 | 1 |  | 598885 | 609639.126 | Ramna |  |  |  |  | G.T.V | 609639.126 | 653967.7221 | -44328.5961 | -6.7784 | OK
26 | Kazi Alauddin Road | 11 |  | HA021100951-02 | 1 | 6674283 | 7041683 | 367400 | 1 |  | 367400 | 373997.3699 | Bangshal |  |  |  |  | Kazi Alauddin Road | 373997.3699 | 641935.1027 | -267937.7328 | -41.7391 | CHECK
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 |  | 2436 | 1 | 67423 | 67423 | 0 | 10 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 |  | 2437 | 1 | 88807 | 89174 | 367 | 10 |  | 3670 | 3735.9019 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 3735.9019 | 3663.8273 | 72.0746 | 1.9672 | OK
[9 empty] | Grand Total | 9704868.9662 | 9533673.616 | 9704868.9662 | 1.7957
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 7013685.4924
[5 empty] | Lalbag | at 33 KV level |  | 0
[5 empty] | Bangshal | at 33 KV level |  | 1770122.6257
[5 empty] | Motijheel | at 33 KV level |  | 477711.0916
[5 empty] | Narinda | at 33 KV level |  | 443349.7565
[5 empty] | Total = |  |  | 9704868.9662 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 826.76 | 848.87 | 22.11 | 240000 | 0 | 5306400 | 5308109.9408
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1612.37 | 1634.5 | 22.13 | 240000 | 0 | 5311200 | 5312911.4875
[9 empty] | Total | 0 | 10617600 | 10621021.4283
ULLON 33 KV SIDE
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9096 | 1163.9096 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder.(import) | 33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
KAKRAIL 33 KV SIDE (RECEIVING)
5 | 33 kV Dhanmondi-2 | 33 |  | 06604376 | 1 | 5285.05 | 5314.36 | 29.31 | 180000 | 5275800
2 | 33 kV Dhanmondi-1 | 33 |  | 06604375 | 1 | 2039.54 | 2068.31 | 28.77 | 180000 | 5178600
| 33 KV Kakrail From ULLON | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
[9 empty] | Total | 10454400 | 0 | 0
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 10621021.4283 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KAKRAIL 33 KV NET IMPORT |  | 10621021.4283
| ULLON 33 KV SIDE |  | 0 |  | KAKRAIL 33 KV NET IMPORT |  |  | 10621021.4283 |  | KAKRAIL KV NET IMPORT |  | 10423112.414
| Taltola 33 KV SIDE |  | 0 | [6 empty] | LOSS UNITS=> |  | 197909.0143
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.863%
| TOTAL IMPORT |  | 10621021.4283
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK00017 | 1 | 19004 | 19591.4 | 587.4 | 8888.89 | 5221333.986 |  | 5320474.1489
15 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK00018 | 1 | 5696.9 | 6282.1 | 585.2 | 8888.89 | 5201778.428 |  | 5300547.2794
[6 empty] | 0 | 0 |  | Total | 10423112.414 |  | 10621021.4283
| KAKRAIL 11 KV SIDE |  |  |  |  | 0 | 0
7 | Pioneer | 11 |  | 06604395 | 1 | 23854.78 | 23959.84 | 105.06 | 8000 |  | 840480 | 850072.0555 | Ramna |  |  |  |  | Pioneer | 850072.0555 | 872559.2 | -22487.1445 | -2.5771 | OK
8 | Pir Saheber Goli | 11 |  | DHK-00102 | 1 | 83183.5 | 86508.9 | 3325.4 | 444.444 |  | 1477954.0776 | 1494821.3647 | Rajarbag |  |  |  |  | Pir Saheber Goli | 1494821.3647 | 1589289.5218 | -94468.1571 | -5.944 | OK
9 | Montri Para | 11 |  | DHK-00110 | 1 | 12700.2 | 12787.7 | 87.5 | 2222.22 |  | 194444.25 | 196663.3629 | Kakrail |  |  |  |  | Montri Para | 196663.3629 | 206488.6824 | -9825.3195 | -4.7583 | OK
10 | Baily Road 11 kV Sw/S-2 | 11 |  | 9119865 | 1 | 65421.2 | 67803.2 | 2382 | 1000 |  | 2382000 | 2409184.7946 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-2 | 2409184.7946 | 2711345 | -302160.2054 | -11.1443 | OK
11 | Jamuna U/G 11 KV Jonaki O/H | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | 11 |  | 1025651 | 1 | 29238.4 | 29559.9 | 321.5 | 1000 |  | 321500 | 325169.1484 | Ramna |  |  |  |  | High Court | 325169.1484 | 265125 | 60044.1484 | 22.6475 | OK
13 | Secretaiat | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | 11 |  | 06604402 | 1 | 5671.14 | 5708.48 | 37.34 | 40000 |  | 1493600 | 1510645.8477 | Rajarbag |  |  |  |  | Shanti Nagar Bazar | 1510645.8477 | 1601052 | -90406.1523 | -5.6467 | OK
17 | Tottho Bhovon | 11 |  | 9119867 | 1 | 32298 | 32532.2 | 234.2 | 1000 |  | 234200 | 236872.8291 | Kakrail |  |  |  |  | Tottho Bhovon | 236872.8291 | 224220 | 12652.8291 | 5.643 | OK
18 | Central Police Hospital/ PNT (Circuit House) | 11 |  | DHK00199 | 1 | 78681.8 | 78985.3 | 303.5 | 2222.22 |  | 674443.77 | 682140.9217 | Kakrail |  |  |  |  | Central Police Hospital/ PNT (Circuit House) | 682140.9217 | 703183.7413 | -21042.8196 | -2.9925 | OK
19 | Baily Road 11 kV Sw/S-1 | 11 |  | DHK00027 | 1 | 55889.6 | 56427.3 | 537.7 | 2222.22 |  | 1194887.694 | 1208524.4599 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-1 | 1208524.4599 | 1467416.3104 | -258891.8504 | -17.6427 | OK
20 | Bijoy Nagar | 11 |  | D1025656 | 1 | 66935.36 | 67951.3 | 1015.94 | 1000 |  | 1015940 | 1027534.5089 | Ramna |  |  |  |  | Bijoy Nagar | 1027534.5089 | 1059146.6 | -31612.0911 | -2.9847 | OK
21 | Shilpakala Academy | 11 |  | D0086137 | 1 | 25965.1 | 26476.8 | 511.7 | 1000 |  | 511700 | 517539.8234 | Ramna |  |  |  |  | Shilpakala Academy | 517539.8234 | 576508 | -58968.1766 | -10.2285 | OK
22 | Judges Complex | 11 |  | 06604344 | 1 | 674.7 | 678.06 | 3.36 | 40000 |  | 134400 | 135933.8524 | Kakrail |  |  |  |  | Judges Complex | 135933.8524 | 151904 | -15970.1476 | -10.5133 | OK
23 | Auxiliary Transformer, AT-1 | 11 |  | 39333 | 1 | 492441 | 492441 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Auxiliary Transformer, AT-2 | 11 |  | 39254 | 1 | 1195010 | 1220636 | 25626 | 1 |  | 25626 | 25918.4591 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-2 | 25918.4591 | 0 | 25918.4591 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10621021.4283 | 10501175.7916 | 10621021.4283 | 1.1413
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2720315.5362
[5 empty] | Rajarbag | at 33 KV level |  | 3005467.2124
[5 empty] | Kakrail | at 33 KV level |  | 4895238.6797
[5 empty] | Total = |  |  | 10621021.4283 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 710.95 | 725.99 | 15.04 | 240000 | 0 | 3609600 | 3610763.1619
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 151.65 | 158.2 | 6.55 | 240000 | 0 | 1572000 | 1572506.5632
[9 empty] | Total |  | 5181600 | 5183269.7251 | 0.032224
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 | 33 |  | BD017073 | 1 | 67868.12 | 71441.3 | 3573.18 | 1000 | 3573180
4 | 33 kV Dhanmondi Incoming Circuit-2 | 33 |  | BD017074 | 1 | 36358.02 | 37915.27 | 1557.25 | 1000 | 1557250
| 33 KV Ullon-1 Feeder | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
[6 empty] | 0 | 0 |  | Total | 5130430 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total
[6 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017072 | 1 | 96695.65 | 100727.66 | 4032.01 | 888.89 |  | 3584013.3689
6 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017076 | 1 | 33755.06 | 35513.47 | 1758.41 | 888.89 |  | 1563033.0649
[9 empty] | Total |  | 5147046.4338
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 5183269.7251 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 5183269.7251
[5 empty] | 33 KV NET IMPORT |  |  | 5183269.7251 |  | 33/11 KV XF HV SIDE |  | 5147046.4338
[10 empty] | LOSS UNITS=> |  | 36223.2913
[10 empty] | LOSS % IN => |  | 0.6989%
| TOTAL IMPORT |  | 5183269.7251
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD017081 | 1 | 73678.91 | 77231.95 | 3553.04 | 1000 | 3553040 |  | 3610244.899
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD017082 | 1 | 29149.7 | 30697.8 | 1548.1 | 1000 | 1548100 |  | 1573024.8261
[6 empty] | 0 | 0 |  | Total | 5101140 |  | 5183269.7251
| BSMMU HOSPITAL 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV Jamuna (F1) | 11 |  | BD017073 | 1 | 0.3748 | 0.3857 | 0.0109 | 2000 |  | 21.8 | 22.0654 | Kakrail |  |  |  |  | 11 kV Jamuna (F1) | 22.0654 | 24.7258 | -2.6605 | -10.7598 | OK
9 | 11 kV Pukur Par (F2) | 11 |  | BD017074 | 1 | 2928.46 | 2949.81 | 21.35 | 2000 |  | 42700 | 43219.8277 | Kakrail |  |  |  |  | 11 kV Pukur Par (F2) | 43219.8277 | 44627.1399 | -1407.3122 | -3.1535 | OK
10 | 11 kV BSMMU Convention center (F3) | 11 |  | BD017075 | 1 | 1753.43 | 1769.15 | 15.72 | 2000 |  | 31440 | 31822.749 | Kakrail |  |  |  |  | 11 kV BSMMU Convention center (F3) | 31822.749 | 77353.7092 | -45530.9602 | -58.8607 | CHECK
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 |  | BD017076 | 1 | 3017.58 | 3106.11 | 88.53 | 2000 |  | 177060 | 179215.5198 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 179215.5198 | 177543.6485 | 1671.8713 | 0.94167 | OK
12 | 11 kV Holi Family Feeder (F5) | 11 |  | BD017077 | 1 | 14405.79 | 14750.36 | 344.57 | 2000 |  | 689140 | 697529.5567 | Kakrail |  |  |  |  | 11 kV Holi Family Feeder (F5) | 697529.5567 | 750881.7825 | -53352.2258 | -7.1053 | OK
13 | 11 kV Navy House Feeder (F6) | 11 |  | BD017078 | 1 | 26649.82 | 26964.47 | 314.65 | 2000 |  | 629300 | 636961.0675 | Kakrail |  |  |  |  | 11 kV Navy House Feeder (F6) | 636961.0675 | 681006.1346 | -44045.0671 | -6.4676 | OK
14 | 11 kV Paribagh Feeder (F7) | 11 |  | BD017079 | 1 | 31963.13 | 32752.23 | 789.1 | 2000 |  | 1578200 | 1597412.9298 | Paribag |  |  |  |  | 11 kV Paribagh Feeder (F7) | 1597412.9298 | 1675286.7504 | -77873.8207 | -4.6484 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 |  | BD017080 | 1 | 6399.81 | 6611.65 | 211.84 | 2000 |  | 423680 | 428837.8596 | Paribag |  |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 428837.8596 | 457910.6397 | -29072.78 | -6.349 | OK
18 | 11 kV Oncology Bhaban (F9) | 11 |  | BD017083 | 1 | 2293.72 | 2364.53 | 70.81 | 2000 |  | 141620 | 143344.075 | Paribag |  |  |  |  | 11 kV Oncology Bhaban (F9) | 143344.075 | 137962.1897 | 5381.8852 | 3.901 | OK
19 | Rupayan Trade Center | 11 |  | BD017084 | 1 | 1218.74 | 1358.01 | 139.27 | 2000 |  | 278540 | 281930.9324 | Kakrail |  |  |  |  | Rupayan Trade Center | 281930.9324 | 302057.3893 | -20126.457 | -6.6631 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 |  | BD017085 | 1 | 2119.1 | 2175.83 | 56.73 | 2000 |  | 113460 | 114841.2565 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 114841.2565 | 122402.9977 | -7561.7412 | -6.1777 | OK
21 | 11 kV BSMMU RMU (F12) | 11 |  | BD017086 | 1 | 2052.22 | 2138.01 | 85.79 | 2000 |  | 171580 | 173668.8065 | Paribag |  |  |  |  | 11 kV BSMMU RMU (F12) | 173668.8065 | 174287.0734 | -618.2669 | -0.35474 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 |  | BD017087 | 1 | 4149.43 | 4268.96 | 119.53 | 2000 |  | 239060 | 241970.3048 | Paribag |  |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 241970.3048 | 234654.3262 | 7315.9786 | 3.1178 | OK
23 | 11 kV BCS Academy RMU (F14) | 11 |  | BD017088 | 1 | 1022.96 | 1055.98 | 33.02 | 2000 |  | 66040 | 66843.9677 | Paribag |  |  |  |  | 11 kV BCS Academy RMU (F14) | 66843.9677 | 56065.3573 | 10778.6104 | 19.2251 | OK
24 | Spare | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | 11 |  | BD017090 | 1 | 1402.07 | 1664.04 | 261.97 | 2000 |  | 523940 | 530318.42 | Paribag |  |  |  |  | BSMMU Super Specialist Hospital RMU | 530318.42 | 510819.9335 | 19498.4865 | 3.8171 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKD4418 | 1 | 2759.07 | 2905.71 | 146.64 | 100 |  | 14664 | 14842.5188 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 14842.5188 | 15407.4195 | -564.9007 | -3.6664 | OK
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 1666.67 | 1671.49 | 4.82 | 100 |  | 482 | 487.8678 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 487.8678 | 0 | 487.8678 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 5183269.7251 | 5120927.8 | 5183269.7251 | 1.2174
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 1985542.975
[5 empty] | Paribag | at 33 KV level |  | 3197726.7501
[5 empty] | Total = |  |  | 5183269.7251 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 | 132 |  | 8993518 | 1 | 1115.068 | 1133.719 | 18.651 | 960000 | 0 | 17904960
|  | 132 |  |  | 1 | 70.056 | 70.056 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 | 132 |  | 5014660 | 1 | 291.99 | 310.946 | 18.956 | 960000 | 0 | 18197760
|  | 132 |  |  | 1 | 4.361 | 4.361 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 | 132 |  | 38992597 | 1 | 609.476 | 643.19 | 33.714 | 1440000 | 0 | 48548160
|  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 84650880
[9 empty] | Net Total | 84650880
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 | 132 | RECEIVE | 6604452 | 1 | 272557 | 289835 | 17278 | 1000 | 17278000
|  | 132 |  |  | 1 | 6755 | 6755 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) | 132 |  |  | 1 | 4379040 | 4427504 | 48464 | 1000 | 48464000
|  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar | 132 |  |  | 1 | 7525 | 7526 | 1 | 1000 | 1000
|  | 132 |  |  | 1 | 510202 | 544738 | 34536 | 1000 |  | 34536000
| Kallyanpur-2 | 132 |  | 6604428 | 1 | 370818 | 388018 | 17200 | 1000 | 17200000
|  | 132 |  |  | 1 | 7111 | 7111 | 0 | 1000 |  | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 82943000 | 34536000
[6 empty] | 0 | 0 | Net Total |  | 48407000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
6 | Kamrangirchar | 132 |  | SIEM491 | 1 | 7525 | 7526 | 1 | 1000 | 1000
|  | 132 |  | SIEM491 | 1 | 510202 | 544738 | 34536 | 1000 |  | 34536000
[6 empty] | 0 | 0 |  | Total |  | 34536000
| LALBAGH 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 | NET IMPORT | SIEM494 | 1 | 2196773 | 2221264 | 24491 | 1000 |  | 24491000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | SIEM499 | 1 | 2308886 | 2332821 | 23935 | 1000 |  | 23935000
[9 empty] | Total |  | 48426000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 84650880 |  | EXPORT TO OTHER S/S |  |  | 34536000 |  | 132 KV NET IMPORT |  | 50114880
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 50114880 |  | 132/33 KV GT LV SIDE |  | 48381000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1733880
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 3.46%
| 132 KV TOTAL IMPORT |  | 84650880
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) | 33 |  | SIEM0517 | 1 | 2196215 | 2220641 | 24426 | 1000 | 24426000
16 | 132/33 kV GT-2 Incoming (LV) | 33 |  | SIEM0518 | 1 | 2282897 | 2306852 | 23955 | 1000 | 23955000
[6 empty] | 0 | 0 |  | Total | 48381000 |  | 0
| LALBAGH 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [10 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SIEM0502 | 1 | 837341 | 844032 | 6691 | 2000 |  | 13382000 | 13396547.2226 |  | 27157490.14 | Lalbagh New 33/11 kv ss | 1.7549 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 13396547.2226 | 11377882.4218 | 2018664.8007 | 17.742 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SIEM0501 | 1 | 830673 | 837546 | 6873 | 2000 |  | 13746000 | 13760942.9174 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 13760942.9174 | 11693934.7113 | 2067008.2061 | 17.6759 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 27128000 | 27157490.14 | [5 empty] | 33 KV Feeders | 27157490.14 | 23071817.1331 | 4085673.0069 | 17.7085 | OK
9 | Spare | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 9228020.647 | Mitford 33/11 kv ss | -0.64219 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 | 33 |  | SIEM0513 | 1 | 319597 | 322454 | 2857 | 2000 |  | 5714000 | 5720211.5401 | [5 empty] | Mitford Circuit-1 | 5720211.5401 | 5352758.2023 | 367453.3378 | 6.8647 | OK
12 | Azimpur Circuit-1 | 33 |  | SIEM0503 | 1 | 70586 | 70644 | 58 | 2000 |  | 116000 | 116126.1006 |  | 118128.2747 | Azimpur 33/11 kv ss | 1.9508 |  | Azimpur Circuit-1 | 116126.1006 | 116758.1706 | -632.0701 | -0.54135 | OK
15 | Azimpur Circuit-2 | 33 |  | SIEM0507 | 1 | 85038 | 85039 | 1 | 2000 |  | 2000 | 2002.1741 | [5 empty] | Azimpur Circuit-2 | 2002.1741 | 6683398.7333 | -6681396.5591 | -99.97 | CHECK
17 | Lalbagh old | 33 |  | SIEM0509 | 1 | 222464 | 228318 | 5854 | 2000 |  | 11708000 | 11720727.4609 |  | 11720727.4609 | Lalbagh old 33/11 kv ss | 0.12321 |  | Lalbagh old | 11720727.4609 | 9793594.8305 | 1927132.6304 | 19.6775 | OK
18 | Mitford Circuit-2 | 33 |  | SIEM0511 | 1 | 358806 | 360558 | 1752 | 2000 |  | 3504000 | 3507809.1068 | [5 empty] | Mitford Circuit-2 | 3507809.1068 | 3339686.2947 | 168122.8121 | 5.0341 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKC7982 | 1 | 7276.67 | 7372.32 | 95.65 | 120 |  | 11478 | 11490.4774 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-1 | 11490.4774 | 11986.6354 | -496.1579 | -4.1393 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHU02670 | 1 | 27089.5 | 27089.5 | 0 | 120 |  | 0 | 0 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 21055478 | 21078366.86 | [5 empty] | 0 | 21078366.86 | 25298182.8669 | -4219816.0069 | -16.6803 | OK
[8 empty] | Grand Total |  | 48235857 | 48183478 | 48235857 | 0.10871
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK98833 | 1 | 589023.51 | 595704.6 | 6681.09 | 2000 | 13362180 |  | 13409606.8649
11 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK98832 | 1 | 585396.17 | 592245.8 | 6849.63 | 2000 | 13699260 |  | 13747883.2751
[6 empty] | 0 | 0 |  | Total | 27061440 |  | 27157490.14
| LALBAGH 11 kV SIDE |  |  |  |  | 0 | 0
3 | Chata Mosjid | 11 |  |  | 1 | 171770.4353 | 174270.4 | 2499.9647 | 1000 |  | 2499964.71 | 2543835.8742 | Kamrangirchar |  | 320 |  |  | Chata Mosjid | 2543835.8742 | 2199148.6226 | 344687.2515 | 15.6737 | OK
4 | AC mosjid | 11 |  |  | 1 | 6488.7556 | 7869.7 | 1380.9444 | 1000 |  | 1380944.4 | 1405178.1975 | Lalbag |  | 150 |  |  | AC mosjid | 1405178.1975 | 1152835.6866 | 252342.5109 | 21.8889 | OK
5 | Kazi Reaz Uddin Road | 11 |  |  | 1 | 20836.008 | 23184.964 | 2348.956 | 1000 |  | 2348956 | 2390177.1556 | Lalbag |  | 170 |  |  | Kazi Reaz Uddin Road | 2390177.1556 | 2000565.9387 | 389611.2169 | 19.4751 | OK
6 | Nazimuddin | 11 |  |  | 1 | 4687.9236 | 5597.3048 | 909.3812 | 1000 |  | 909381.2 | 925339.67 | Lalbag |  | 56.6667 |  |  | Nazimuddin | 925339.67 | 477977.0793 | 447362.5908 | 93.595 | FAULT
7 | Kamal Bagh | 11 |  |  | 1 | 14900.122 | 16557.14 | 1657.018 | 1000 |  | 1657018 | 1686096.534 | Lalbag |  | 206.6667 |  |  | Kamal Bagh | 1686096.534 | 1618577.1268 | 67519.4071 | 4.1715 | OK
8 | Rahamatganj | 11 |  |  | 1 | 10837.383 | 13289.972 | 2452.589 | 1000 |  | 2452589 | 2495628.7814 | Lalbag |  |  |  |  | Rahamatganj | 2495628.7814 | 2157043.5386 | 338585.2428 | 15.6967 | OK
9 | Water Works 11kV Sw/S-1 | 11 |  |  | 1 | 22372.9274 | 646.4972 | -21726.4302 | 1000 | Estimated | 1946125.44 | 1980277.4376 | Lalbag | 160 |  |  |  | Water Works 11kV Sw/S-1 | 1980277.4376 | 1747210.9883 | 233066.4493 | 13.3393 | OK
12 | City Colony | 11 |  |  | 1 | 24326.885 | 26507.92 | 2181.035 | 1000 |  | 2181035 | 2219309.3581 | Lalbag |  |  |  |  | City Colony | 2219309.3581 | 1859682.1079 | 359627.2502 | 19.3381 | OK
13 | Water Works 11kV Sw/S-2 | 11 |  |  | 1 | 35515.332 | 1663.5993 | -33851.7327 | 1000 | Estimated | 2554289.64 | 2599114.1368 | Lalbag | 210 |  |  |  | Water Works 11kV Sw/S-2 | 2599114.1368 | 2790703.3917 | -191589.2549 | -6.8653 | OK
14 | Chun Goli | 11 |  |  | 1 | 7124.165 | 8090.5632 | 966.3982 | 1000 |  | 966398.2 | 983357.245 | Lalbag |  |  |  |  | Chun Goli | 983357.245 | 754718.4448 | 228638.8002 | 30.2946 | OK
15 | Alir Ghat | 11 |  |  | 1 | 121324.8 | 123425.3 | 2100.5 | 1000 |  | 2100500 | 2137361.0725 | Lalbag |  |  |  |  | Alir Ghat | 2137361.0725 | 1734165.991 | 403195.0814 | 23.2501 | OK
16 | Club Ghat | 11 |  |  | 1 | 16270.969 | 19197.12 | 2926.151 | 1000 |  | 2926151 | 2977501.1852 | Lalbag |  |  |  |  | Club Ghat | 2977501.1852 | 2317579.0304 | 659922.1548 | 28.4746 | OK
17 | Debidas Ghat | 11 |  |  | 1 | 29072.95 | 31744.334 | 2671.384 | 1000 |  | 2671384 | 2718263.3522 | Lalbag |  |  |  |  | Debidas Ghat | 2718263.3522 | 2261609.1864 | 456654.1658 | 20.1916 | OK
18 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 27061440 | 26594736.59 | 27061440 | 1.7549
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 2543835.8742
[5 empty] | Lalbag | at 33 KV level |  | 24517604.1258
[5 empty] | Total = |  |  | 27061440 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old | 33 | 0 | SIEM0509 | 1 | 222464 | 228318 | 5854 | 2000 | 0 | 11708000 | 11720727.4609
[9 empty] | Total |  | 11708000 | 11720727.4609 | 0.10871
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 | 33 | 0 | 30799098 | 1 | 1759.2 | 1759.82 | 0.62 | 240000 | 0 | 148800 | 148592.9595
[9 empty] | Total |  | 148800 | 148592.9595
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
[9 empty] | Total |  | 0 | 11869320.4204
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 11720727.4609 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALBAGH OLD 33 KV NET IMPORT |  | 11869320.4204
| KAMRANGIRCHAR 33 KV SIDE |  | 148592.9595 |  | LALBAGH OLD 33 KV NET IMPORT |  |  | 11869320.4204 |  | 33 KV TX HV SIDE |  | 11869320.4204
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 11869320.4204
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) | 11 |  | 8838010 | 1 | 80354.8 | 83997.3 | 3642.5 | 1000 | 3642500 |  | 5086628.1742
27 | 33/11 kV T1 Incoming (LV) | 11 |  | 06604426 | 1 | 35775.5 | 35962.94 | 187.44 | 16000 | 2999040 |  | 4188058.0259
28 | 33/11 kV T2 Incoming (LV) | 11 |  |  | 1 | 603996 | 605854 | 1858 | 1000 | 1858000 |  | 2594634.2203
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total | 8499540 |  | 11869320.4204
| LALBAGH OLD 11 KV SIDE |  |  |  |  | 0 | 0
15 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 120 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | 11 |  | 8838019 | 1 | 77211.8 | 80010.7 | 2798.9 | 1000 |  | 2798900 | 2802348.4469 | Lalbag |  | 100 |  |  | Sowari Ghat | 2802348.4469 | 2329233.6447 | 473114.8022 | 20.312 | OK
17 | Novo Kumar (Kara Odidoptor) | 11 |  | 8838014 | 1 | 81145.3 | 81727.2 | 581.9 | 1000 | Estimated | 559511.064 | 560200.422 | Lalbag | 45 | 20 |  |  | Novo Kumar (Kara Odidoptor) | 560200.422 | 121854.324 | 438346.0981 | 359.7296 | FAULT
19 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 6.6667 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 106.6667 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1429861.608 | 1431623.3008 | Lalbag | 115 |  |  |  | Eidgah | 1431623.3008 | 1096688.9157 | 334934.385 | 30.5405 | OK
23 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | 11 |  |  | 1 | 91067.8 | 96407.8 | 5340 | 444.44 | Estimated | 2113708.464 | 2116312.7055 | Lalbag | 170 |  |  |  | Modumoti | 2116312.7055 | 1584106.2116 | 532206.4939 | 33.5966 | OK
25 | Lalbagh O/H | 11 |  | 61389152 | 1 | 440978 | 441573 | 595 | 1000 | Estimated | 1243357.92 | 1244889.8267 | Lalbag | 100 |  |  |  | Lalbagh O/H | 1244889.8267 | 1181986.9425 | 62902.8842 | 5.3218 | OK
26 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | 11 |  | 61389109 | 1 | 401739 | 402783 | 1044 | 1000 |  | 1044000 | 1045286.2834 | Lalbag |  |  |  |  | Water Works 11 kV Sw/S-2 | 1045286.2834 | 874589.6653 | 170696.6181 | 19.5173 | OK
31 | Islambagh | 11 |  | 61389186 | 1 | 500001 | 500941 | 940 | 1000 |  | 940000 | 941158.1479 | Lalbag |  |  |  |  | Islambagh | 941158.1479 | 774407.5731 | 166750.5748 | 21.5327 | OK
32 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | 11 |  | 61389202 | 1 | 15534 | 15590 | 56 | 1000 |  | 56000 | 56068.996 | Lalbag |  |  |  |  | WASA Low Lift Pump | 56068.996 | 57103.7926 | -1034.7965 | -1.8121 | OK
34 | Shahi Mosjid | 11 |  | 06604459 | 1 | 35827.5 | 36034.94 | 207.44 | 8000 |  | 1659520 | 1661564.6485 | Azimpur |  |  |  |  | Shahi Mosjid | 1661564.6485 | 1773623.7611 | -112059.1126 | -6.3181 | OK
35 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer | 0.415 |  | 5395822 | 1 | 28617 | 38472.5 | 9855.5 | 1 |  | 9855.5 | 9867.6427 | Lalbag |  |  |  |  | 33/0.4 kV Auxiliary Transformer | 9867.6427 | 0 | 9867.6427 | #DIV/0! | #DIV/0!
[6 empty] | 4391673 | 4391673 |  | Grand Total | 11869320.4204 | 11854714.556 | 11869320.4204 | 0.12321
33/0.4 kV Auxiliary Transformer meter change at 30 April 2023
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Lalbag | at 33 KV level |  | 10207755.7719
[5 empty] | Azimpur | at 33 KV level |  | 1661564.6485
[5 empty] | Total = |  |  | 11869320.4204 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 | 33 | 0 | SIEM0513 | 1 | 319597 | 322454 | 2857 | 2000 | 0 | 5714000 | 5720211.5401
18 | Mitford Circuit-2 | 33 | 0 | SIEM0511 | 1 | 358806 | 360558 | 1752 | 2000 | 0 | 3504000 | 3507809.1068
[9 empty] | Total | 0 | 9218000 | 9228020.647
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 1231 | 1241.88 | 10.88 | 540000 |  | 5875200
| Lalbagh Circuit-2 | 33 |  | DHK68131 | 1 | 1292.58 | 1299.06 | 6.48 | 540000 |  | 3499200
[6 empty] | 0 | 0 |  | Total |  | 9374400
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
1 | Kumartuly Circuit-1 | 33 |  | DHK-66493 | 1 | 1286272 | 1288507 | 2235 | 180 |  | 402300
6 | Kumartuly Circuit-2 | 33 |  | DHK-60914 | 1 | 761041 | 761041 | 0 | 180 |  | 0
[6 empty] | 0 | 0 |  | Total |  | 402300
[6 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-66494 | 1 | 2844826 | 2899052 | 54226 | 180 | From Downstream | 5957640
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHKA-2193 | 1 | 578.7117 | 596.5583 | 17.8466 | 180000 |  | 3212388
[9 empty] | Total |  | 9170028
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 9228020.647 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9228020.647
| IMPORT-2 |  | 402300 |  | 33 KV NET IMPORT |  |  | 9228020.647 |  | 33 KV TX HV SIDE |  | 9170028
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 57992.647
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.6284%
| TOTAL IMPORT |  | 9630320.647
11 KV SIDE of___MIDFORT 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK-66484 | 1 | 2748746 | 2781844 | 33098 | 180 | 5957640 |  | 6005761.9037
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK-66476 | 1 | 2061887 | 2079645 | 17758 | 180 | 3196440 |  | 3222258.7433
[6 empty] | 0 | 0 |  | Total | 9154080 |  | 9228020.647
| MIDFORT 11 KV SIDE |  |  |  |  | 0 | 0
7 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | 11 |  | DHK-60904 | 1 | 971432 | 980258.2 | 8826.2 | 60 |  | 529572 | 526171.1474 | Lalbag |  |  |  |  | Chawk Bazar | 526171.1474 | 480516.9276 | 45654.2198 | 9.5011 | OK
10 | Spare | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | 11 |  | DHK-66485 | 1 | 816427 | 839123 | 22696 | 60 |  | 1361760 | 1353014.9285 | Bangshal |  |  |  |  | Chatrabas | 1353014.9285 | 1237900.3837 | 115114.5448 | 9.2992 | OK
12 | Begum Bazar | 11 |  | DHK-66481 | 1 | 3667458 | 3708499 | 41041 | 60 |  | 2462460 | 2446646.3554 | Bangshal |  |  |  |  | Begum Bazar | 2446646.3554 | 2397460.098 | 49186.2574 | 2.0516 | OK
13 | SCC ROAD | 11 |  | DHK-60901 | 1 | 74915 | 103137 | 28222 | 60 |  | 1693320 | 1682445.687 | Bangshal |  |  |  |  | SCC ROAD | 1682445.687 | 1526989.2348 | 155456.4523 | 10.1806 | OK
16 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | 11 |  | DHK-61104 | 1 | 684884 | 701514.5 | 16630.5 | 60 |  | 997830 | 991422.0466 | Bangshal |  |  |  |  | Armanitola | 991422.0466 | 974917.2355 | 16504.8111 | 1.6929 | OK
18 | Mitford Hospital (RMU) | 11 |  | DHK-61101 | 1 | 392201 | 401444.2 | 9243.2 | 60 |  | 554592 | 551030.4718 | Bangshal |  |  |  |  | Mitford Hospital (RMU) | 551030.4718 | 539101.6117 | 11928.86 | 2.2127 | OK
19 | Emamganj | 11 |  | DHK-68130 | 1 | 1450.67 | 1453.5 | 2.83 | 60000 |  | 169800 | 168709.5633 | Bangshal |  |  |  |  | Emamganj | 168709.5633 | 161982.5873 | 6726.9759 | 4.1529 | OK
20 | Kamal Dho Road | 11 |  | DHK-68129 | 1 | 1225.4 | 1226.82 | 1.42 | 60000 |  | 85200 | 84652.8551 | Lalbag |  |  |  |  | Kamal Dho Road | 84652.8551 | 538371.2175 | -453718.3625 | -84.2761 | CHECK
21 | Spare | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | 11 |  | DHK-68127 | 1 | 1528.54 | 1552.36 | 23.82 | 60000 |  | 1429200 | 1420021.8363 | Bangshal |  |  |  |  | Panghat | 1420021.8363 | 1363598.8715 | 56422.9648 | 4.1378 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | U0004460 | 1 | 5594.68 | 5633.99 | 39.31 | 100 |  | 3931 | 3905.7556 | Bangshal |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 3905.7556 | 3927.8323 | -22.0768 | -0.56206 | OK
[9 empty] | Grand Total | 9228020.647 | 9287665 | 9228020.647 | -0.64219
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 8617196.6445
[5 empty] | Lalbag | at 33 KV level |  | 610824.0025
[5 empty] | Total = |  |  | 9228020.647 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 | 33 | 0 | SIEM0503 | 1 | 70586 | 70644 | 58 | 2000 | 0 | 116000 | 116126.1006
15 | Azimpur Circuit-2 | 33 | 0 | SIEM0507 | 1 | 85038 | 85039 | 1 | 2000 | 0 | 2000 | 2002.1741
[9 empty] | Total | 0 | 118000 | 118128.2747
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1978.52 | 2016.45 | 37.93 | 240000 | 0 | 9103200 | 9106133.4262
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1809.7 | 1843.76 | 34.06 | 240000 | 0 | 8174400 | 8177034.1286
[9 empty] | Total | 0 | 17277600 | 17283167.5547
[9 empty] | GRAND TOTAL |  | 17395600 | 17401295.8295
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 783543 | 784153 | 610 | 180 |  | 109800
| Dhanmondi Circuit-1 | 33 |  | DHK68131 | 1 | 1185844 | 1202718 | 16874 | 540 |  | 9111960
| Dhanmondi Circuit-2 | 33 |  |  | 1 | 135546 | 150545 | 14999 | 540 |  | 8099460
| Lalbagh Circuit-2 | 33 |  | DHK68132 | 1 | 943609 | 943627 | 18 | 180 |  | 3240
[6 empty] | 0 | 0 |  | Total |  | 17324460 | #REF!
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  | 1 | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK61094 | 1 | 287638 | 338943 | 51305 | 180 |  | 9234900
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK60919 | 1 | 409946 | 454991 | 45045 | 180 |  | 8108100
[9 empty] | Total |  | 17343000 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 118128.2747 |  | EXPORT TO OTHER S/S |  |  | 0 |  | AZIMPUR 33 KV NET IMPORT |  | 17401295.8295
| DHANMONDI 33 kV SIDE |  | 17283167.5547 |  | AZIMPUR 33 KV NET IMPORT |  |  | 17401295.8295 |  | 33 KV TX HV SIDE |  | 17343000
[10 empty] | LOSS UNITS=> |  | 58295.8295
[10 empty] | LOSS % IN => |  | 0.335%
| TOTAL IMPORT |  | 17401295.8295
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) | 11 |  | DHK60909 | 1 | 290518 | 341890 | 51372 | 180 | 9246960 |  | 9258055.9804
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK60902 | 1 | 425353 | 470539 | 45186 | 180 | 8133480 |  | 8143239.8491
[6 empty] | 0 | 0 |  | Total | 17380440 |  | 17401295.8295
| AZIMPUR 11 KV SIDE |  |  |  |  | 0 | 0
7 | Chadni chwok | 11 |  | DHK60916 | 1 | 409665 | 421688 | 12023 | 60 |  | 721380 | 735452.5478 | Paribag |  |  |  |  | Chadni chwok | 735452.5478 | 623153.8648 | 112298.683 | 18.021 | OK
8 | BGB | 11 |  | DHK61090 | 1 | 676712 | 689645 | 12933 | 60 |  | 775980 | 791117.6745 | Jigatola |  |  |  |  | BGB | 791117.6745 | 677536.8748 | 113580.7997 | 16.7638 | OK
9 | Pari Bibi Mazar | 11 |  | DHK61091 | 1 | 780093 | 817084 | 36991 | 60 |  | 2219460 | 2262756.8158 | Azimpur |  |  |  |  | Pari Bibi Mazar | 2262756.8158 | 2133225.2763 | 129531.5395 | 6.0721 | OK
10 | Azimpur | 11 |  | DHK61086 | 1 | 301821 | 320730 | 18909 | 60 |  | 1134540 | 1156672.3968 | Azimpur |  |  |  |  | Azimpur | 1156672.3968 | 1153479.4596 | 3192.9372 | 0.27681 | OK
11 | Aazd | 11 |  | DHK61089 | 1 | 982542 | 1004577 | 22035 | 60 |  | 1322100 | 1347891.2826 | Azimpur |  |  |  |  | Aazd | 1347891.2826 | 1333174.551 | 14716.7316 | 1.1039 | OK
12 | Dayra Sharif | 11 |  | DHK61088 | 1 | 515887 | 532893 | 17006 | 60 |  | 1020360 | 1040264.9944 | Azimpur |  |  |  |  | Dayra Sharif | 1040264.9944 | 1036318.7466 | 3946.2478 | 0.38079 | OK
13 | Naya palton | 11 |  | DHK86065 | 1 | 1899.17 | 1928.02 | 28.85 | 60000 |  | 1731000 | 1764768.0283 | Azimpur |  |  |  |  | Naya palton | 1764768.0283 | 1711787.3638 | 52980.6645 | 3.095 | OK
16 | Viqarunnisa Noon School | 11 |  | DHK66477 | 1 | 1609302 | 1633628 | 24326 | 60 |  | 1459560 | 1488032.8269 | Azimpur |  |  |  |  | Viqarunnisa Noon School | 1488032.8269 | 1499973.4477 | -11940.6207 | -0.79606 | OK
17 | Subal Das Lane | 11 |  | DHK66480 | 1 | 4005845 | 4031972 | 26127 | 60 |  | 1567620 | 1598200.8415 | Azimpur |  |  |  |  | Subal Das Lane | 1598200.8415 | 1506117.3895 | 92083.4519 | 6.114 | OK
18 | Lalbagh | 11 |  | DHK61093 | 1 | 726292 | 766602 | 40310 | 60 |  | 2418600 | 2465781.6021 | Azimpur |  |  |  |  | Lalbagh | 2465781.6021 | 2471750.3893 | -5968.7871 | -0.24148 | OK
19 | Zahrul Haque Hall | 11 |  | DHK66497 | 1 | 1239080 | 1251280 | 12200 | 60 |  | 732000 | 746279.7208 | Ramna |  |  |  |  | Zahrul Haque Hall | 746279.7208 | 668533.8709 | 77745.8499 | 11.6293 | OK
20 | Eden College | 11 |  | DHK60917 | 1 | 933261 | 941486 | 8225 | 60 |  | 493500 | 503127.1069 | Azimpur |  |  |  |  | Eden College | 503127.1069 | 450271.8574 | 52855.2495 | 11.7385 | OK
21 | Nilkhet/ PWD-01 | 11 |  | DHK60918 | 1 | 478017 | 489152 | 11135 | 60 |  | 668100 | 681133.1714 | Azimpur |  |  |  |  | Nilkhet/ PWD-01 | 681133.1714 | 683984.9722 | -2851.8008 | -0.41694 | OK
22 | BUET | 11 |  | DHK66496 | 1 | 962739 | 976076 | 13337 | 60 |  | 800220 | 815830.544 | Ramna |  |  |  |  | BUET | 815830.544 | 798043.2987 | 17787.2453 | 2.2289 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIG2780 | 1 | 389374 | 393284 | 3910 | 1 |  | 3910 | 3986.2756 | Azimpur |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 3986.2756 | 4092.9197 | -106.6441 | -2.6056 | OK
[9 empty] | Grand Total | 17401295.8295 | 17068330 | 17401295.8295 | 1.9508
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 735452.5478
[5 empty] | Jigatola | at 33 KV level |  | 791117.6745
[5 empty] | Azimpur | at 33 KV level |  | 14312615.3423
[5 empty] | Ramna | at 33 KV level |  | 1562110.2648
[5 empty] | Total = |  |  | 17401295.8295 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | #REF! |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar | 132 |  | 38992596 | 1 | 891.973 | 925.846 | 33.873 | 1440000 | 0 | 48777120
|  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 48777120
[9 empty] | Net Total | 48777120
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj | 132 | RECEIVE |  | 1 | 5699.08 | 5750.04 | 50.96 | 960000 | 48921600
|  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh | 132 |  |  | 1 | 3040.28 | 3076.27 | 35.99 | 960000 | 34550400
|  | 132 |  |  | 1 | 7.78 | 7.78 | 0 | 960000 |  | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 83472000 | 0
[6 empty] | 0 | 0 | Net Total |  | 83472000
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
5 | 132 kV Jigatola-1 | 132 |  | 42003953362 | 1 | 211.08 | 228.16 | 17.08 | 1440000 |  | 24595200
6 | 132 kV Jigatola-2 | 132 |  | 42003953364 | 1 | 206.51 | 223.14 | 16.63 | 1440000 |  | 23947200
[6 empty] | 0 | 0 |  | Total |  | 48542400
| KAMRANGIRCHAR 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | 30799138 | 1 | 3382.6 | 3394.32 | 11.72 | 960000 |  | 11251200
2 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | 30799148 | 1 | 3360.22 | 3371.94 | 11.72 | 960000 |  | 11251200
7 | 132/33 kV, 50/75 MVA GT-3 (HV) | 132 |  | BD001910 | 1 | 1160.29 | 1172.77 | 12.48 | 960000 |  | 11980800
[9 empty] | Total |  | 34483200 | 83025600
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 48777120 |  | EXPORT TO OTHER S/S |  |  | 48542400 |  | 132 KV NET IMPORT |  | 34785120
| FROM LALBAGH 132/33 KV GRID |  | 34550400 |  | 132 KV NET IMPORT |  |  | 34785120 |  | 33 KV NET IMPORT |  | 34449600
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 335520
[10 empty] | LOSS % IN => |  | 0.9646%
| 132 KV TOTAL IMPORT |  | 83327520
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming | 33 |  | BD001914 | 1 | 2335.32 | 2360.25 | 24.93 | 480000 | 11966400 |  | 12082946.1
14 | 132/33 kV GT-1 Incoming (LV) | 33 |  | 30799094 | 1 | 6864.81 | 6888.44 | 23.63 | 480000 | 11342400 |  | 11452868.6861
19 | 132/33 kV GT-2 Incoming | 33 |  | 30799150 | 1 | 6765.59 | 6788.8 | 23.21 | 480000 | 11140800 |  | 11249305.2139
[6 empty] | 0 | 0 |  | Total | 34449600 |  | 34785120
| KAMRANGIRCHAR 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [10 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) | 33 |  | 30799129 | 1 | 6839.64 | 6877.8 | 38.16 | 240000 |  | 9158400 | 9145656.9918 |  | 27746140.1976 | Kamrangir Char 33/11 kv ss | 2.1711 |  | 33/11 kV, 20/28 MVA T31 (HV) | 9145656.9918 | 8166327.3371 | 979329.6547 | 11.9923 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) | 33 |  | 30799110 | 1 | 6736.43 | 6774.65 | 38.22 | 240000 |  | 9172800 | 9160036.9556 | [5 empty] | 33/11 kV, 20/28 MVA T32 (HV) | 9160036.9556 | 8058275.3729 | 1101761.5827 | 13.6724 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) | 33 |  | 30799137 | 1 | 3879 | 3918.39 | 39.39 | 240000 |  | 9453600 | 9440446.2502 | [5 empty] | 33/11 kV, 20/28 MVA T-33 (HV) | 9440446.2502 | 8509692.4677 | 930753.7825 | 10.9376 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 27784800 | 27746140.1976 | [5 empty] | 33 KV Feeders | 27746140.1976 | 24734295.1776 | 3011845.0199 | 12.1768 | OK
8 | Dhaka Uddyan 2 | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | 0.90308 |  | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 | 33 |  | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 |  | 0 | 0 | [5 empty] | Dhaka Uddyan 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare Feeder -2 | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 | 33 |  | 30799098 | 1 | 1759.2 | 1759.82 | 0.62 | 240000 |  | 148800 | 148592.9595 |  | 6633956.6439 | Kamrangir Char-2 33/11 kv ss | 0.22403 |  | Lalbagh Circuit-1 | 148592.9595 | 0 | 148592.9595 | #DIV/0! | #DIV/0!
16 | Zigatola Circuit-1 (BGB-1) | 33 |  | 30799088 | 1 | 5961.15 | 5961.44 | 0.29 | 240000 |  | 69600 | 69503.1585 | [5 empty] | Zigatola Circuit-1 (BGB-1) | 69503.1585 | 0 | 69503.1585 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 | 33 |  | 30799147 | 1 | 1516.92 | 1543.98 | 27.06 | 240000 |  | 6494400 | 6485363.6844 |  | 69503.1585 | BGB 33/11 kv ss | 1.7781 |  | Kamrangir Char-2 | 6485363.6844 | 6050909.9939 | 434453.6905 | 7.18 | OK
22 | Zigatola Circuit-2 (BGB-2) | 33 |  | 30799131 | 1.35 | 1865.53 | 1865.53 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Grid Has No Reading | Zigatola Circuit-2 (BGB-2) | 0 | 155594.8284 | -155594.8284 | -100 | CHECK
[9 empty] | Total |  | 6712800 | 6703459.8024 | [5 empty] | 0 | 6703459.8024 | 6206504.8224 | 496954.9801 | 8.007 | OK
[8 empty] | Grand Total |  | 34449600 | 34497600 | 34449600 | -0.13914
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 9181800 |  | 9232062.7469
11 | 33/11 kV T-32 Incoming | 11 |  | 6604433 | 1 | 7572.47 | 7623.48 | 51.01 | 180000 | 9181800 |  | 9232062.7469
22 | 33/11 kV T-33 Incoming | 11 |  | DHK 95817 | 1 | 4551195 | 4602481 | 51286 | 180 | 9231480 |  | 9282014.7037
[6 empty] | 0 | 0 |  | Total | 27595080 |  | 27746140.1976
| KAMRANGIRCHAR 11 kV SIDE |  |  |  |  | 0 | 0
4 | Rasulpur | 11 |  | HA-021101042-02 | 1 | 91923561 | 93474113 | 1550552 | 1 |  | 1550552 | 1584215.5272 | Kamrangirchar |  |  |  |  | Rasulpur | 1584215.5272 | 1403442.4135 | 180773.1137 | 12.8807 | OK
5 | Bheribadh | 11 |  | HA-021101105-02 | 1 | 64458541 | 67023775 | 2565234 | 1 |  | 2565234 | 2620926.9562 | Kamrangirchar |  |  |  |  | Bheribadh | 2620926.9562 | 2327005.5404 | 293921.4158 | 12.6309 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | 11 |  | 30799521 | 1 | 2634.51 | 2640.43 | 5.92 | 60000 |  | 355200 | 362911.631 | Kamrangirchar |  |  |  |  | Panna Tower 11 KV Faridpur Tower Express | 362911.631 | 314576.4303 | 48335.2007 | 15.3652 | OK
8 | Panna Battery Express | 11 |  | DHK15431 | 1 | 5278.8 | 5298.71 | 19.91 | 60000 |  | 1194600 | 1220535.5698 | Kamrangirchar |  |  |  |  | Panna Battery Express | 1220535.5698 | 1068349.9537 | 152185.6161 | 14.2449 | OK
9 | Eidgah | 11 |  | 30799460 | 1 | 5369.43 | 5409.9 | 40.47 | 60000 |  | 2428200 | 2480917.8558 | Kamrangirchar |  |  |  |  | Eidgah | 2480917.8558 | 2121576.0406 | 359341.8152 | 16.9375 | OK
10 | Bot Tola Mazar | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | 11 |  | HA-021101055-02 | 1 | 1275461 | 3393397 | 2117936 | 1 |  | 2117936 | 2163917.8156 | Kamrangirchar |  |  |  |  | Huzur Para | 2163917.8156 | 1832748.4977 | 331169.3179 | 18.0695 | OK
13 | Kamrangirchar | 11 |  | HA-021101015-02 | 1 | 21147055 | 23145473 | 1998418 | 1 |  | 1998418 | 2041804.9994 | Kamrangirchar |  |  |  |  | Kamrangirchar | 2041804.9994 | 1873617.2189 | 168187.7805 | 8.9766 | OK
14 | Munshihati | 11 |  | HA-021100854-02 | 1 | 51488293 | 52835781 | 1347488 | 1 |  | 1347488 | 1376742.8712 | Kamrangirchar |  |  |  |  | Munshihati | 1376742.8712 | 1392932.3343 | -16189.4632 | -1.1623 | OK
15 | Jhawchar | 11 |  | HA-021101028-02 | 1 | 250925 | 1779953 | 1529028 | 1 |  | 1529028 | 1562224.2267 | Kamrangirchar |  |  |  |  | Jhawchar | 1562224.2267 | 1438582.214 | 123642.0127 | 8.5947 | OK
16 | RMU Express | 11 |  | HA-021101248-02 | 1 | 5919945 | 6564561 | 644616 | 1 |  | 644616 | 658611.0471 | Kamrangirchar |  |  |  |  | RMU Express | 658611.0471 | 606779.6203 | 51831.4268 | 8.5421 | OK
17 | Koyla Ghat | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2136683.556 | 2183072.3937 | Kamrangirchar | 170 |  |  |  | Koyla Ghat | 2183072.3937 | 1900877.505 | 282194.8887 | 14.8455 | OK
18 | Muslimbagh | 11 |  | HA-021100908-02 | 1 | 26159019 | 27875253 | 1716234 | 1 |  | 1716234 | 1753494.5949 | Kamrangirchar |  |  |  |  | Muslimbagh | 1753494.5949 | 1596522.772 | 156971.823 | 9.8321 | OK
19 | Noyagaon | 11 |  | HA-021101087-02 | 1 | 5869693 | 8700121 | 2830428 | 1 |  | 2830428 | 2891878.4964 | Kamrangirchar |  |  |  |  | Noyagaon | 2891878.4964 | 2674100.301 | 217778.1954 | 8.144 | OK
20 | Nurbagh | 11 |  | HA-021100982-02 | 1 | 23098305 | 25365051 | 2266746 | 1 |  | 2266746 | 2315958.5809 | Kamrangirchar |  |  |  |  | Nurbagh | 2315958.5809 | 1868573.9135 | 447384.6674 | 23.9426 | OK
21 | Ali Nagar | 11 |  | HA-021101022-02 | 1 | 22030169 | 24482441 | 2452272 | 1 |  | 2452272 | 2505512.4752 | Kamrangirchar |  |  |  |  | Ali Nagar | 2505512.4752 | 2290198.0816 | 215314.3936 | 9.4016 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKE6223 | 1 | 43047.09 | 43238.07 | 190.98 | 120 |  | 22917.6 | 23415.1565 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 23415.1565 | 24412.3409 | -997.1844 | -4.0848 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 27746140.1976 | 27156553.156 | 27746140.1976 | 2.1711
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 27746140.1976
[5 empty] | Jigatola | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 27746140.1976 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.44 | 0.29 | 240000 | 0 | 69600 | 69503.1585
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1865.53 | 1865.53 | 0 | 240000 | 0 | 0 | 0
[9 empty] | TOTAL |  | 69600 | 69503.1585
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old | 33 | 0 | 43998033 | 1 | 182.259 | 215.862 | 33.603 | 270000 |  | 9072810 | 8830410.3485
[9 empty] | TOTAL |  | 9072810 | 9072810
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 | 33 | 0 | 0 | 1 | 78.02 | 79.31 | 1.29 | 360000 | 0 | 464400 | 464744.971
11 | BGB-2 | 33 | 0 | 0 | 1 | 252.12 | 274.65 | 22.53 | 360000 | 0 | 8110800 | 8116824.9591
[9 empty] | Total | 0 | 8575200 | 8581569.9302
[9 empty] | GRAND TOTAL |  | 17717610 | 17723883.0887
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 | 33 |  | 43998032 | 1 | 1043.59 | 1043.851 | 0.261 | 270000 | 70470
8 | 33 kV Satmojid Via Zigatola Old | 33 |  | 43998033 | 1 | 182.259 | 215.862 | 33.603 | 270000 | 9072810
| 33 kV Zigatola-1 | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 | 33 |  | 43998027 | 1 | 756.089 | 756.089 | 0 | 270000 | 0
| 33 kV Zigatola-2 | 33 |  | 43998031 | 1 | 335.616 | 365.293 | 29.677 | 270000 | 8012790
[6 empty] | 0 | 0 |  | Total | 17156070 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| BGB 33 KV SIDE |  |  |  |  | 0 | 0
6 | 33/11 kV T1 | 33 |  | 43998028 | 1 | 757.421 | 791.306 | 33.885 | 270000 |  | 9148950
9 | 33/11 kV T2 | 33 |  | 43998029 | 1 | 758.561 | 788.226 | 29.665 | 270000 |  | 8009550
11 | 33/11 kV T3 | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
[9 empty] | Total |  | 17158500
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 17723883.0887 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BGB 33 KV NET IMPORT |  | 17723883.0887
[5 empty] | BGB 33 KV NET IMPORT |  |  | 17723883.0887 |  | 33 KV TX HV SIDE |  | 17158500
[10 empty] | LOSS UNITS=> |  | 565383.0887
[10 empty] | LOSS % IN => |  | 3.19%
| TOTAL IMPORT |  | 17723883.0887
11 KV SIDE of___BGB 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming | 11 |  |  | 1 | 2906198 | 11984320 | 9078122 | 1 | 9078122 |  | 9152993.7395
29 | 33/11 kV T-2 Incoming | 11 |  |  | 1 | 2984199 | 10924220 | 7940021 | 1 | 7940021 |  | 8005506.2605
30 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
[6 empty] | 0 | 0 |  | Total | 17018143 |  | 17158500
| BGB 11 KV SIDE |  |  |  |  | 0 | 0
12 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | 11 |  |  | 1 | 9205025 | 10229090 | 1024065 | 1 |  | 1024065 | 1042273.5833 | Azimpur |  |  |  |  | Nababgonj Park | 1042273.5833 | 1021134.2367 | 21139.3466 | 2.0702 | OK
16 | Kholamura Ghat | 11 |  |  | 1 | 77275264 | 80077104 | 2801840 | 1 |  | 2801840 | 2851658.6512 | Kamrangirchar |  |  |  |  | Kholamura Ghat | 2851658.6512 | 2502740.2728 | 348918.3784 | 13.9415 | OK
17 | Khalpar | 11 |  |  | 1 | 84269168 | 85938304 | 1669136 | 1 |  | 1669136 | 1698814.3914 | Kamrangirchar |  |  |  |  | Khalpar | 1698814.3914 | 1298185.7875 | 400628.6039 | 30.8607 | OK
18 | Shahidnagar | 11 |  |  | 1 | 16043430 | 17993510 | 1950080 | 1 |  | 1950080 | 1984753.7699 | Azimpur |  |  |  |  | Shahidnagar | 1984753.7699 | 1856790.3941 | 127963.3758 | 6.8916 | OK
19 | BGB 1 No Gate | 11 |  |  | 1 | 32661410 | 34102440 | 1441030 | 1 |  | 1441030 | 1466652.5091 | Azimpur |  |  |  |  | BGB 1 No Gate | 1466652.5091 | 1458588.073 | 8064.4361 | 0.55289 | OK
21 | Ganaktuli | 11 |  |  | 1 | 23467080 | 24390290 | 923210 | 1 |  | 923210 | 939625.3117 | Jigatola |  |  |  |  | Ganaktuli | 939625.3117 | 882817.4598 | 56807.852 | 6.4348 | OK
22 | Thana | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | 11 |  |  | 1 | 32354152 | 34382472 | 2028320 | 1 |  | 2028320 | 2064384.9311 | Jigatola |  |  |  |  | Bot Tola Mazar | 2064384.9311 | 2207948.9744 | -143564.0433 | -6.5021 | OK
24 | Sikder Medical | 11 |  |  | 1 | 35690888 | 36890712 | 1199824 | 1 |  | 1199824 | 1221157.6998 | Jigatola |  |  |  |  | Sikder Medical | 1221157.6998 | 1181050.1989 | 40107.5009 | 3.3959 | OK
25 | Gas Field | 11 |  |  | 1 | 53961540 | 56136408 | 2174868 | 1 |  | 2174868 | 2213538.6558 | Kamrangirchar |  |  |  |  | Gas Field | 2213538.6558 | 2063276.8361 | 150261.8197 | 7.2827 | OK
26 | Hazaribagh | 11 |  |  | 1 | 39936160 | 41443472 | 1507312 | 1 |  | 1507312 | 1534113.0489 | Jigatola |  |  |  |  | Hazaribagh | 1534113.0489 | 1525507.7666 | 8605.2822 | 0.56409 | OK
27 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 |  |  | 1 | 2117.04 | 2177.16 | 60.12 | 10 |  | 601.2 | 611.8898 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-1 | 611.8898 | 0 | 611.8898 | #DIV/0! | #DIV/0!
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 |  |  | 1 | 1699.35 | 1754.23 | 54.88 | 10 |  | 548.8 | 558.558 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-2 | 558.558 | 0 | 558.558 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 17018143 | 16720835 | 17018143 | 1.7781
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Azimpur | at 33 KV level |  | 4494850.3101
[5 empty] | Kamrangirchar | at 33 KV level |  | 6764011.6984
[5 empty] | Jigatola | at 33 KV level |  | 5759280.9915
[5 empty] | Total = |  |  | 17018143 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 | 132 | 0 | 42003953362 | 1 | 211.08 | 228.16 | 17.08 | 1440000 | 0 | 24595200 | 0
6 | 132 kV Jigatola-2 | 132 | 0 |  | 1 | 206.51 | 223.14 | 16.63 | 1440000 | 0 | 23947200 | 0
[8 empty] | Total Import/Export |  | 0 | 48542400
[9 empty] | Net Total | 48542400
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 | 132 | RECEIVE | 6604452 | 1 | 253.22 | 273.7 | 20.48 | 1200000 | 24576000
| 132 kV Kamrangirchar 2 | 132 |  |  | 1 | 247.55 | 267.83 | 20.28 | 1200000 | 24336000
[6 empty] | 0 | 0 | Total Import/Export |  | 48912000 | 0
[6 empty] | 0 | 0 | Net Total |  | 48912000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| JIGATOLA 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  |  | 1 | 198.23 | 218.32 | 20.09 | 1200000 |  | 24108000
3 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  |  | 1 | 302.73 | 323.06 | 20.33 | 1200000 |  | 24396000
[9 empty] | Total |  | 48504000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 48542400 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 48542400
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 48542400 |  | 33 KV NET IMPORT |  | 48499200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 43200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.08899%
| 132 KV TOTAL IMPORT |  | 48542400
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  |  | 1 | 328.71 | 361.82 | 33.11 | 720000 | 23839200
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  |  | 1 | 502.09 | 536.34 | 34.25 | 720000 | 24660000
[6 empty] | 0 | 0 |  | Total | 48499200 |  | 0
| JIGATOLA 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [10 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  |  | 1 | 551.66 | 576.88 | 25.22 | 240000 |  | 6052800 | 6057296.2116 |  | 19130199.9703 | JIGATOLA NEW 3/11 KV SS | -0.13885 |  | 33/11 kV 28/35 MVA T-1 | 6057296.2116 | 7886688.2616 | -1829392.05 | -23.1959 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  |  | 1 | 409.12 | 441.45 | 32.33 | 240000 |  | 7759200 | 7764963.7795 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 7764963.7795 | 7168410.6421 | 596553.1374 | 8.322 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  |  | 1 | 344.55 | 366.65 | 22.1 | 240000 |  | 5304000 | 5307939.9792 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 5307939.9792 | 5097376.8394 | 210563.1398 | 4.1308 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 19116000 | 19130199.9703 | [5 empty] | 33 KV Feeders | 19130199.9703 | 20152475.7431 | -1022275.7729 | -5.0727 | OK
2 | BGB-1 | 33 |  |  | 1 | 78.02 | 79.31 | 1.29 | 360000 |  | 464400 | 464744.971 |  | 8581569.9302 | BGB 33/11 kv ss | 1.7781 |  | BGB-1 | 464744.971 | 8195547.638 | -7730802.6669 | -94.3293 | CHECK
2 | Spair | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 | 33 |  |  | 1 | 189.31 | 207.16 | 17.85 | 360000 |  | 6426000 | 6430773.4363 | [5 empty] | Dhaka Uddyan-1 | 6430773.4363 | 6543509.1132 | -112735.6769 | -1.7229 | OK
4 | Green Road -1 | 33 |  |  | 1 | 23.42 | 23.76 | 0.34 | 360000 |  | 122400 | 122490.9226 |  | 13502822.8792 | Dhaka Uddan 33/11 kv ss | 0.90308 |  | Green Road -1 | 122490.9226 | 79010.5381 | 43480.3845 | 55.0311 | FAULT
9 | Green Road -2 | 33 |  |  | 1 | 37.21 | 50.73 | 13.52 | 360000 |  | 4867200 | 4870815.5103 | [5 empty] | Green Road -2 | 4870815.5103 | 5024351.9481 | -153536.4378 | -3.0558 | OK
10 | Dhaka Uddyan-2 | 33 |  |  | 1 | 196.11 | 215.74 | 19.63 | 360000 |  | 7066800 | 7072049.4429 | [5 empty] | Dhaka Uddyan-2 | 7072049.4429 | 7638882.4829 | -566833.04 | -7.4204 | OK
11 | BGB-2 | 33 |  |  | 1 | 252.12 | 274.65 | 22.53 | 360000 |  | 8110800 | 8116824.9591 |  | 2291300.7874 | Jigatla Old 33/11 kv ss | 0.21781 |  | BGB-2 | 8116824.9591 | 7559871.9448 | 556953.0144 | 7.3672 | OK
12 | Jigatola Old | 33 |  |  | 1 | 16.82 | 23.18 | 6.36 | 360000 |  | 2289600 | 2291300.7874 | [5 empty] | Jigatola Old | 2291300.7874 | 2355950.5918 | -64649.8044 | -2.7441 | OK
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 29347200 | 29369000.0297 | [5 empty] | 0 | 29369000.0297 | 37397124.2569 | -8028124.2271 | -21.4672 | OK
[8 empty] | Grand Total |  | 48499200 | 48463200 | 48499200 | 0.074283
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 123.48 | 147.86 | 24.38 | 250000 | 6095000 |  | 6084726.3572
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 134.01 | 165.23 | 31.22 | 250000 | 7805000 |  | 7791844.0062
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 98.11 | 119.16 | 21.05 | 250000 | 5262500 |  | 5253629.607
[6 empty] | 0 | 0 |  | Total | 19162500 |  | 19130199.9703
| JIGATOLA 11 kV SIDE |  |  |  |  | 0 | 0
| Salek Garden | 11 |  | 2761 | 1 | 593.11 | 635.73 | 42.62 | 60000 |  | 2557200 | 2553649.2193 | Jigatola |  |  |  |  | Salek Garden | 2553649.2193 | 2650896.5462 | -97247.3269 | -3.6685 | OK
4 | Jigatola Local | 11 |  | 2850 | 1 | 469.67 | 499.39 | 29.72 | 60000 |  | 1783200 | 1780723.9511 | Jigatola |  |  |  |  | Jigatola Local | 1780723.9511 | 1886527.6034 | -105803.6523 | -5.6084 | OK
5 | Modina Rayer Bazar | 11 |  | 2851 | 1 | 628.51 | 628.51 | 0 | 60000 |  | 0 | 0 | Switching | Grid has No Reading |  |  |  | Modina Rayer Bazar | 0 | 1517895.7729 | -1517895.7729 | -100 | CHECK
6 | City College | 11 |  | 2784 | 1 | 510.17 | 539.43 | 29.26 | 60000 |  | 1755600 | 1753162.2749 | Jigatola |  |  |  |  | City College | 1753162.2749 | 1830510.0213 | -77347.7464 | -4.2255 | OK
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office | 11 |  | 2836 | 1 | 386.41 | 413.89 | 27.48 | 60000 |  | 1648800 | 1646510.5712 | Jigatola |  |  |  |  | Post Office | 1646510.5712 | 1676311.0857 | -29800.5144 | -1.7777 | OK
11 | Leather Institute | 11 |  | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 |  | 0 | 0 | Jigatola | Grid has No Reading |  |  |  | Leather Institute | 0 | 57222.2613 | -57222.2613 | -100 | CHECK
12 | Mina Bazar | 11 |  | 2853 | 1 | 194.57 | 206.27 | 11.7 | 60000 |  | 702000 | 701025.2432 | Jigatola |  |  |  |  | Mina Bazar | 701025.2432 | 763766.6032 | -62741.36 | -8.2147 | OK
13 | Mitali | 11 |  | 2852 | 1 | 368.1 | 419.56 | 51.46 | 60000 |  | 3087600 | 3083312.7364 | Switching |  |  |  |  | Mitali | 3083312.7364 | 2269615.5842 | 813697.1522 | 35.8518 | OK
14 | Road-2 | 11 |  | 2839 | 1 | 624.12 | 663.52 | 39.4 | 60000 |  | 2364000 | 2360717.4857 | Jigatola |  |  |  |  | Road-2 | 2360717.4857 | 2376832.0316 | -16114.546 | -0.67798 | OK
15 | SS-2 | 11 |  | 2838 | 1 | 291.23 | 312 | 20.77 | 60000 |  | 1246200 | 1244469.5984 | Jigatola |  |  |  |  | SS-2 | 1244469.5984 | 1139024.1692 | 105445.4292 | 9.2575 | OK
16 | Spare | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar | 11 |  | 2843 | 1 | 502.69 | 534.72 | 32.03 | 60000 |  | 1921800 | 1919131.4991 | Jigatola |  |  |  |  | Bou Bazar | 1919131.4991 | 1882311.2263 | 36820.2729 | 1.9561 | OK
18 | BGB | 11 |  | 2764 | 1 | 179.28 | 186.72 | 7.44 | 60000 |  | 446400 | 445780.1547 | Jigatola |  |  |  |  | BGB | 445780.1547 | 580655.3671 | -134875.2124 | -23.2281 | OK
19 | Dhamondi-12 | 11 |  | 2763 | 1 | 400.32 | 427.72 | 27.4 | 60000 |  | 1644000 | 1641717.2362 | Dhanmondi |  |  |  |  | Dhamondi-12 | 1641717.2362 | 1520907.4708 | 120809.7654 | 7.9433 | OK
[9 empty] | Total | 19130199.9703 | 19156800 | 19130199.9703 | -0.13885
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Jigatola | at 33 KV level |  | 17488482.734 | Including Switching
[5 empty] | Dhanmondi | at 33 KV level |  | 1641717.2362
[5 empty] | Total = |  |  | 19130199.9703 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [13 empty] | Month August-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | CF | Number |  | 2023-04-01 | 2023-04-01 |  |  | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 0 | 60000 | 0 | 0 | 0 |  | 0
13 | Mitali | 11 | 0 | 2852 | 1 | 368.1 | 419.56 | 51.46 | 60000 | 0 | 3087600 | 3083312.7364 |  | 130
[9 empty] | Total |  | 3087600 | 3083312.7364
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 0 | 0 | Dhanmondi | Load Zero
3 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1581226.92 | 1579031.3193 | Jigatola
3 | 11 kV Mitali | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1506373.08 | 1504281.4171 | Jigatola | Switching Total - Madina - Rayer Bazar
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.44 | 0.29 | 240000 | 0 | 69600 | 69503.1585
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1865.53 | 1865.53 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 69600 | 69503.1585
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit | 33 | 0 | 214393/37-2711 | 1 | 10131.445 | 18744730 | 18734598.555 | 1000 | Estimated | 1566000 | 1524160.9386
[9 empty] | Total |  | 1566000 | 1524160.9386
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 | NET IMPORT | DHK61073 | 1 | 4015.71 | 4025.2 | 9.49 | 240000 |  | 2277600
2 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
[9 empty] | Total |  | 2277600
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 1524160.9386
| Satmasjid 33 KV SIDE |  | 1524160.9386 |  | 33 KV NET IMPORT |  |  | 1524160.9386 |  | ZIGATOLA OLD 11 KV NET IMPORT |  | 2277600
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -753439.0614
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -49.43%
| TOTAL IMPORT |  | 1524160.9386
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0
16 | 33/11 kV T-2 Incoming | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0
17 | 33/11 kV T-1 Incoming | 11 |  | DHK61028 | 1.32 | 1848.08 | 1857.19 | 9.11 | 180000 | 2164536
[6 empty] | 0 | 0 |  | Total | 2164536 |  | 2277600
| ZIGATOLA OLD 11 KV SIDE |  |  |  |  | 0 | 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Lalmatia SW |  |  |  |  | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | 11 |  | DHK60946 | 1 | 1141.66 | 1157 | 15.34 | 60000 |  | 920400 | 922404.6994 | Jigatola |  |  |  |  | Simanto Square | 922404.6994 | 967800 | -45395.3006 | -4.6906 | OK
12 | Post Office | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | 11 |  | DHK61070 | 1 | 3437.43 | 3458.66 | 21.23 | 60000 |  | 1273800 | 1276574.4307 | Jigatola |  |  |  |  | Green Road Via Park | 1276574.4307 | 1342800 | -66225.5693 | -4.9319 | OK
15 | PWD Quarters 11 kV Saleq Grand | 11 |  | DHK61028 | 1 | 3630.54 | 3631.76 | 1.22 | 60000 |  | 73200 | 73359.435 | Jigatola |  |  |  |  | PWD Quarters 11 kV Saleq Grand | 73359.435 | 68400 | 4959.435 | 7.2506 | OK
18 | Road No.-2 | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 |  | 243284 | 1 | 84159 | 84683 | 524 | 10 |  | 5240 | 5251.4131 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 5251.4131 | 3680 | 1571.4131 | 42.7014 | FAULT
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 |  | 412277 | 1 | 39663 | 39664 | 1 | 10 |  | 10 | 10.0218 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 10.0218 | 1650 | -1639.9782 | -99.3926 | CHECK
[9 empty] | Grand Total | 2277600 | 2272650 | 2277600 | 0.21781
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Jigatola | at 33 KV level |  | 2277600
[5 empty] | Total = |  |  | 2277600 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) | 33 | 0 | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 | 33 | 0 | 0 | 1 | 189.31 | 207.16 | 17.85 | 360000 | 0 | 6426000 | 6430773.4363
10 | Dhaka Uddyan-2 | 33 | 0 | 0 | 1 | 196.11 | 215.74 | 19.63 | 360000 | 0 | 7066800 | 7072049.4429
[9 empty] | Total | 0 | 13492800 | 13502822.8792
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | RECEIVE | BD017107 | 1 | 90469.03 | 90469.03 | 0 | 1125 |  | 0
| 33 kV Jigatala Incoming Circuit-1 | 33 |  | BD017098 | 1 | 60324.25 | 65964.43 | 5640.18 | 1125 |  | 6345202.5
| 33 kV Jigatala Incoming Circuit-2 | 33 |  | BD017097 | 1 | 62541.61 | 68793.91 | 6252.3 | 1125 |  | 7033837.5
| 33 kV Kamrangirchar Circuit-2 (O/H) | 33 |  | BD017108 | 1 | 73739.05 | 73739.05 | 0 | 1125 |  | 0
[6 empty] | 0 | 0 |  | Total |  | 13379040 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017100 | 1 | 70364.07 | 76742.04 | 6377.97 | 1000 |  | 6377970
3 | 33/11 kV, 28/35 MVA T-3 (Future) | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017109 | 1 | 53777.98 | 60834.8 | 7056.82 | 1000 |  | 7056820
[9 empty] | Total |  | 13434790 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 13502822.8792
| JIGATOLA 33 KV SIDE |  | 13502822.8792 |  | 33 KV NET IMPORT |  |  | 13502822.8792 |  | 33 KV TX HV |  | 13434790
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 68032.8792
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5038%
| TOTAL IMPORT |  | 13502822.8792
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD014060 | 1 | 69356.95 | 75708.29 | 6351.34 | 1000 | 6351340 |  | 6705963.0493
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD014061 | 1 | 53746.81 | 60184.24 | 6437.43 | 1000 | 6437430 |  | 6796859.8299
[6 empty] | 0 | 0 |  | Total | 12788770 |  | 13502822.8792
| DHAKA UDDYAN 11 KV SIDE |  |  |  |  | 0 | 0
7 | Spare | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | 11 |  | BD014031 | 1 | 48979.01 | 49358.52 | 379.51 | 1000 |  | 379510 | 382937.2777 | Adabor |  |  |  |  | D Block dhaka uddyan | 382937.2777 | 364723.8055 | 18213.4722 | 4.9938 | OK
8 | Dill Mohammad O/H | 11 |  | BD014027 | 1 | 17844.24 | 19845.66 | 2001.42 | 1000 |  | 2001420 | 2019494.4174 | Adabor |  |  |  |  | Dill Mohammad O/H | 2019494.4174 | 1931376.746 | 88117.6714 | 4.5624 | OK
9 | Turag O/H | 11 |  | BD014028 | 1 | 26177.65 | 26940.95 | 763.3 | 1000 |  | 763300 | 770193.2072 | Adabor |  |  |  |  | Turag O/H | 770193.2072 | 703573.3851 | 66619.8221 | 9.4688 | OK
10 | Nabadoy O/H | 11 |  | BD014025 | 1 | 35784.32 | 36623.52 | 839.2 | 1000 |  | 839200 | 846778.6447 | Adabor |  |  |  |  | Nabadoy O/H | 846778.6447 | 874784.3247 | -28005.6801 | -3.2014 | OK
11 | Chandrima O/H | 11 |  | BD014024 | 1 | 4855.8 | 5884.34 | 1028.54 | 1000 |  | 1028540 | 1037828.5358 | Adabor |  |  |  |  | Chandrima O/H | 1037828.5358 | 998647.327 | 39181.2087 | 3.9234 | OK
12 | Shyamoli Housing Project-2 | 11 |  | BD014029 | 1 | 26451.58 | 27785.59 | 1334.01 | 1000 |  | 1334010 | 1346057.1733 | Adabor |  |  |  |  | Shyamoli Housing Project-2 | 1346057.1733 | 1686564.4606 | -340507.2873 | -20.1894 | OK
13 | Spare | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | 11 |  | BD013959 | 1 | 37965.55 | 39475.91 | 1510.36 | 1000 |  | 1510360 | 1523999.7543 | Satmasjid |  |  |  |  | U Lab | 1523999.7543 | 2168216.2175 | -644216.4632 | -29.7118 | OK
19 | Akota | 11 |  | BD014020 | 1 | 6085.32 | 6634.04 | 548.72 | 1000 |  | 548720 | 553675.3788 | Adabor |  |  |  |  | Akota | 553675.3788 | 518552.2147 | 35123.1642 | 6.7733 | OK
20 | Burigonga O/H | 11 |  | BD014019 | 1 | 4671.23 | 5080.63 | 409.4 | 1000 |  | 409400 | 413097.2082 | Adabor |  |  |  |  | Burigonga O/H | 413097.2082 | 391376.3535 | 21720.8547 | 5.5499 | OK
21 | Garden City | 11 |  | BD014021 | 1 | 83851.34 | 86636.25 | 2784.91 | 1000 |  | 2784910 | 2810059.9564 | Satmasjid |  |  |  |  | Garden City | 2810059.9564 | 2804225.2436 | 5834.7128 | 0.20807 | OK
22 | Avenue O/H | 11 |  | BD014017 | 1 | 12957.25 | 13982.44 | 1025.19 | 1000 |  | 1025190 | 1034448.2826 | Adabor |  |  |  |  | Avenue O/H | 1034448.2826 | 977183.594 | 57264.6886 | 5.8602 | OK
23 | Chand Uddyan | 11 |  | BD014018 | 1 | 8233.6 | 8987.27 | 753.67 | 1000 |  | 753670 | 760476.2406 | Satmasjid |  |  |  |  | Chand Uddyan | 760476.2406 | 759432.9748 | 1043.2658 | 0.13737 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4416 | 1 | 1797.78 | 1835.21 | 37.43 | 100 |  | 3743 | 3776.8023 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3776.8023 | 3734.949 | 41.8533 | 1.1206 | OK
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 13502822.8792 | 13381973 | 13502822.8792 | 0.90308
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 8408286.9279
[5 empty] | Satmasjid | at 33 KV level |  | 5094535.9513
[5 empty] | Total = |  |  | 13502822.8792 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [13 empty] | #REF! |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 | 33 | IMPORT | 8993 638E | 1 | 4191.915 | 4199.888 | 7.973 | 180000 | 0 | 1435140
9 | Satmosjid -2 | 33 |  | 8993 669E | 1 | 5801.534 | 5848.148 | 46.614 | 180000 | 0 | 8390520
13 | Lalmatia | 33 |  |  | 1 | 5452.879 | 5452.879 | 0 | 180000 | 0 | 0
14 | Transformer-1 | 33 |  | 50147586E | 1 | 3141.193 | 3188.097 | 46.904 | 750000 | 0 | 35178000
15 | Transformer-2 | 33 |  | 50148569E | 1 | 2781.285 | 2828.681 | 47.396 | 750000 | 0 | 35547000
[8 empty] | Total Import/Export |  | 0 | 80550660
[9 empty] | Net Total | 80550660
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | RECEIVE |  | 1 |  |  | 0
| 33 KV GT-2 Incomming |  |  |  | 1 |  |  | 0
| 33 KV Satmosjid-1 Incomming |  |  |  | 1 |  |  | 0
Total Import/Export
[8 empty] | Net Total |  | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | EXPORT | [7 empty] | 0
| Feeder No.2 | [9 empty] | 0
[9 empty] | Total |  | 0
SATMOSJID 132 KV SIDE
[9 empty] | Total |  | 0
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 80550660 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 80550660
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 80550660 |  | 33 KV NET IMPORT |  | 80550660
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 80550660
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming | 33 |  | 50147586 | 1 | 3141.193 | 3188.097 | 46.904 | 750000 | 35178000
10 | 132/33 kV, 80/120 MVA GT-2 Incoming | 33 |  | 50148569 | 1 | 2781.285 | 2828.681 | 47.396 | 750000 | 35547000
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
[6 empty] | 0 | 0 |  | Total | 70725000 |  | 80550660
| SATMOSJID 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [10 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SICAM | 1 | 48.81 | 4214 | 4165.19 | 1000 | From Downstream | 10681200 | 10395828.747 |  | -0.24021 | Satmasjid 3/11 kv ss | 20961592.6792 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 10395828.747 | 9337624.6623 | 1058204.0848 | 11.3327 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SICAM | 1 | 50.44 | 4298 | 4247.56 | 1000 | From Downstream | 10855800 | 10565763.9321 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 10565763.9321 | 10263423.2695 | 302340.6626 | 2.9458 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 21537000 | 20961592.6792 | [5 empty] | 33 KV Feeders | 20961592.6792 | 19601047.9318 | 1360544.7474 | 6.9412 | OK
6 | BGB | 33 |  | 214393/40-2711 | 1 | 35.2954 | 39.1331 | 3.8377 | 1000 | From Downstream | 9072810 | 8830410.3485 |  | 1.7781 | BGB 33/11 KV SS | 8830410.3485 |  | BGB | 8830410.3485 | 0 | 8830410.3485 | #DIV/0! | #DIV/0!
| Asad Gate Circuit-1 | 33 |  | 214393/44-2711 | 1 | 63.8262 | 72.4663 | 8.6401 | 1000 | Estimated | 8725694.4 | 8492568.689 |  | 1 | ASADGATE 33/11 KV SS | 16943044.2575 |  | Asad Gate Circuit-1 | 8492568.689 | 9412540.6838 | -919971.9947 | -9.7739 | OK
8 | Lalmatia Circuit-2 | 33 |  | SICAM | 1 | 105.9 | 8040 | 7934.1 | 1000 | Estimated | 14660370 | 14268686.6539 |  | 0.95024 | LALMATIA 33/11 KV SS | 14268686.6539 |  | Lalmatia Circuit-2 | 14268686.6539 | 14559556.8645 | -290870.2106 | -1.9978 | OK
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 8682445.8 | 8450475.5685 |  | 0.21781 | JIGATOLA OLD 33/11 KV SS | 1524160.9386 |  | Asad Gate Circuit-2 | 8450475.5685 | 8830773.02 | -380297.4515 | -4.3065 | OK
13 | Jigatola U/G Circuit | 33 |  | 214393/37-2711 | 1 | 10131.445 | 18744730 | 18734598.555 | 1000 | Estimated | 1566000 | 1524160.9386 |  | -0.064901 | JAPAN GARDEN 33/11 KV SS | 18022765.1222 |  | Jigatola U/G Circuit | 1524160.9386 | 1558925.3967 | -34764.4581 | -2.23 | OK
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 18517500 | 18022765.1222 | [5 empty] | Japan Garden City-2 | 18022765.1222 | 19015306.1033 | -992540.9811 | -5.2197 | OK
[9 empty] | Total |  | 61224820.2 | 59589067.3208 | [5 empty] | 0 | 59589067.3208 | 53377102.0682 | 6211965.2526 | 11.6379 | OK
[8 empty] | Grand Total |  | 80550660 | 82761820.2 | 80550660 | -2.6717
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming | 11 |  | DHK60998 | 1 | 4796.15 | 4855.49 | 59.34 | 180000 | 10681200 |  | 10395828.747
24 | 33/11 kV T-2 Incoming | 11 |  | DHK61044 | 1 | 4884.97 | 4945.28 | 60.31 | 180000 | 10855800 |  | 10565763.9321
[6 empty] | 0 | 0 |  | Total | 21537000 |  | 20961592.6792
| SATMOSJID 11 kV SIDE |  |  |  |  | 0 | 0
16 | Lalmatia O/H | 11 |  | DHK61042 | 1 | 3147.3 | 3168.078 | 20.778 | 60000 |  | 1246680 | 1243685.3152 | Satmasjid |  |  |  |  | Lalmatia O/H | 1243685.3152 | 1300189.4979 | -56504.1826 | -4.3458 | OK
16 | Asad Avenue (South) | 11 |  | DHK 60999 | 1 | 2897.6 | 2897.6 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Asad Avenue (South) | 0 | 99461.5008 | -99461.5008 | -100 | CHECK
17 | Madrasha Road | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | 11 |  | DHK61002 | 1 | 2370.58 | 2398.83 | 28.25 | 60000 |  | 1695000 | 1690928.3933 | Satmasjid |  |  |  |  | Bashbari | 1690928.3933 | 1784914.5226 | -93986.1294 | -5.2656 | OK
19 | Road-27 | 11 |  | DHK61001 | 1 | 1438.38 | 1447.74 | 9.36 | 60000 |  | 561600 | 560250.965 | Satmasjid |  |  |  |  | Road-27 | 560250.965 | 379271.8673 | 180979.0976 | 47.7175 | FAULT
20 | Boishakhi O/H | 11 |  | DHK61024 | 1 | 4091.98 | 4141.2 | 49.22 | 60000 |  | 2953200 | 2946106.036 | Dhanmondi |  |  |  |  | Boishakhi O/H | 2946106.036 | 2918535.965 | 27570.071 | 0.94465 | OK
21 | Katasur O/H | 11 |  | DHK61003 | 1 | 3605.55 | 3629.26 | 23.71 | 60000 |  | 1422600 | 1419182.7329 | Satmasjid |  |  |  |  | Katasur O/H | 1419182.7329 | 1436799.27 | -17616.5371 | -1.2261 | OK
22 | Nurjahan Road | 11 |  | DHK61000 | 1 | 1817.79 | 1841.57 | 23.78 | 60000 |  | 1426800 | 1423372.644 | Shyamoli |  |  |  |  | Nurjahan Road | 1423372.644 | 1464960.0563 | -41587.4124 | -2.8388 | OK
25 | polpar over head | 11 |  | DHK61003 | 1 | 1797.61 | 1833.4 | 35.79 | 60000 |  | 2147400 | 2142241.6706 | Dhanmondi |  |  |  |  | polpar over head | 2142241.6706 | 2168380.5497 | -26138.879 | -1.2055 | OK
26 | Satmosjid Housing | 11 |  | DHK61043 | 1 | 2802.53 | 2825.54 | 23.01 | 60000 |  | 1380600 | 1377283.6223 | Satmasjid |  |  |  |  | Satmosjid Housing | 1377283.6223 | 608153.1522 | 769130.4701 | 126.4699 | FAULT
27 | Physical College | 11 |  | DHK61041 | 1 | 3261.37 | 3305.7 | 44.33 | 60000 |  | 2659800 | 2653410.8203 | Satmasjid |  |  |  |  | Physical College | 2653410.8203 | 2677671.3668 | -24260.5465 | -0.90603 | OK
28 | Asad Avenue (North) | 11 |  | DHK61022 | 1 | 2725.37 | 2725.37 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Asad Avenue (North) | 0 | 3594.994 | -3594.994 | -100 | CHECK
29 | Spare Feeder | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | 11 |  | DHK61023 | 1 | 1069.16 | 1097.82 | 28.66 | 60000 |  | 1719600 | 1715469.3009 | Dhanmondi |  |  |  |  | Ghraphic artch college | 1715469.3009 | 1620743.1298 | 94726.1711 | 5.8446 | OK
31 | Mohammadpur O/H | 11 |  | DHK61025 | 1 | 2160.67 | 2188.23 | 27.56 | 60000 |  | 1653600 | 1649627.8414 | Shyamoli |  |  |  |  | Mohammadpur O/H | 1649627.8414 | 1683655.5249 | -34027.6835 | -2.0211 | OK
32 | Bosila Feeder | 11 |  | DHK60997 | 1 | 4059.26 | 4104.49 | 45.23 | 60000 |  | 2713800 | 2707281.1054 | Satmasjid |  |  |  |  | Bosila Feeder | 2707281.1054 | 2444595.9223 | 262685.1832 | 10.7455 | OK
33 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIB 7375 | 1 | 5698.37 | 5834.69 | 136.32 | 60 |  | 8179.2 | 8159.5525 | Satmasjid |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 8159.5525 | 8272.6804 | -113.1279 | -1.3675 | OK
[9 empty] | Total | 21537000 | 21588859.2 | 21537000 | -0.24021
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Satmasjid | at 33 KV level |  | 11660182.507
[5 empty] | Shyamoli | at 33 KV level |  | 3073000.4854
[5 empty] | Dhanmondi | at 33 KV level |  | 6803817.0076
[5 empty] | Total = |  |  | 21537000 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 | 33 |  | 38992490 (new) | 1 | 1.22 | 1.28 | 0.06 | 180000 | 0 | 10800 | 10800
| Kallyanpur to Japangarden-2 | 33 |  | 8993669E | 1 | 5801.534 | 5848.148 | 46.614 | 180000 | 0 | 8390520 | 8390520
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 18517500 | 18022765.1222
[9 empty] | Total | 0 | 26918820 | 26424085.1222
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G | 33 | RECEIVE | DHK86051 | 1 | 2953 | 2985.07 | 32.07 | 270000 |  | 8658900
| kallyanpur U/G-2 | 33 |  | DHK61100 | 1 | 2838.71 | 2869.74 | 31.03 | 270000 |  | 8378100
[6 empty] | 0 | 0 |  | Total |  | 17037000
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 33 KV Japan Genden City | 33 |  | DHK15681 | 1 | 442.67 | 523.32 | 80.65 | 18000 |  | 1451700 | 1451700 | Adabor
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total |  | 1451700
[6 empty] | 0 | 0
| JAPAN GERDEN CITY 33 KV SIDE |  |  |  |  | 0 | 0
| 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61080 | 1 | 4230.59 | 4277.15 | 46.56 | 180000 |  | 8380800
3 | 33/11 kV 20/28 MVA T-1 (HV) | 33 |  | 86052 | 1 | 4991.08 | 5039.33 | 48.25 | 180000 |  | 8685000
[9 empty] | Total |  | 17065800 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 18517500 |  | Adabor NOCS |  |  | 1451700 |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 17065800
| IMPORT-2 |  |  |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  |  | 17065800 |  | 33 KV TX HV SIDE |  | 17065800
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 18517500
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK61079 | 1 | 5630.52 | 5685.03 | 54.51 | 160000 | 8721600 |  | 8679387.5536
10 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK61082 | 1 | 4706.89 | 4759.56 | 52.67 | 160000 | 8427200 |  | 8386412.4464
[6 empty] | 0 | 0 |  | Total | 17148800 |  | 17065800
| JAPAN GERDEN CITY 11 KV SIDE |  |  |  |  | 0 | 0
5 | Dhaka Uddyan | 11 |  | DHK86067 | 1 | 3250.6 | 3251.37 | 0.77 | 60000 |  | 46200 | 46170.0157 | Adabor |  |  |  |  | Dhaka Uddyan | 46170.0157 | 47362.5115 | -1192.4958 | -2.5178 | OK
| Shia Mosjid | 11 |  | DHK60950 | 1 | 3431.26 | 3469.82 | 38.56 | 60000 |  | 2313600 | 2312098.4465 | Shyamoli |  |  |  |  | Shia Mosjid | 2312098.4465 | 2316566.3838 | -4467.9373 | -0.19287 | OK
6 | Shekhar Tek | 11 |  | DHK60977 | 1 | 2346.34 | 2380.53 | 34.19 | 60000 |  | 2051400 | 2050068.6174 | Adabor |  |  |  |  | Shekhar Tek | 2050068.6174 | 2089945.7593 | -39877.1419 | -1.908 | OK
7 | Madrasha Road | 11 |  | DHK61083 | 1 | 1969.45 | 1994.77 | 25.32 | 60000 |  | 1519200 | 1518214.0214 | Shyamoli |  |  |  |  | Madrasha Road | 1518214.0214 | 1459844.4991 | 58369.5223 | 3.9983 | OK
8 | Baitul Aman Housing | 11 |  | DHK668115 | 1 | 4071 | 4117.69 | 46.69 | 60000 |  | 2801400 | 2799581.8586 | Adabor |  |  |  |  | Baitul Aman Housing | 2799581.8586 | 2963454.3569 | -163872.4983 | -5.5298 | OK
11 | Shyamoli Square | 11 |  | DHK86063 | 1 | 458.1 | 463.85 | 5.75 | 30000 |  | 172500 | 172388.0455 | Shyamoli |  |  |  |  | Shyamoli Square | 172388.0455 | 167267.6038 | 5120.4417 | 3.0612 | OK
12 | Mohammadi Housing | 11 |  | DHK60948 | 1 | 3785.19 | 3816.33 | 31.14 | 60000 |  | 1868400 | 1867187.3865 | Adabor |  |  |  |  | Mohammadi Housing | 1867187.3865 | 2007211.2456 | -140023.8591 | -6.976 | OK
13 | Chand Housing | 11 |  | DHK60867 | 1 | 2161.88 | 2175.16 | 13.28 | 60000 |  | 796800 | 796282.8675 | Satmasjid |  |  |  |  | Chand Housing | 796282.8675 | 850127.1046 | -53844.2371 | -6.3337 | OK
14 | PC Culture Housing | 11 |  | DHK60979 | 1 | 4067.35 | 4110.13 | 42.78 | 60000 |  | 2566800 | 2565134.1168 | Adabor |  |  |  |  | PC Culture Housing | 2565134.1168 | 2719447.494 | -154313.3773 | -5.6744 | OK
15 | Mehedibagh | 11 |  | DHK68121 | 1 | 2259.27 | 2309.58 | 50.31 | 60000 |  | 3018600 | 3016640.8933 | Adabor |  |  |  |  | Mehedibagh | 3016640.8933 | 3040793.1415 | -24152.2482 | -0.79427 | OK
16 | 33/11 kV Incoming (Spare) | 11 |  |  | 1 | 0 | 0 | 0 | 160000 |  | 0 | 0 | Adabor |  |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer | 11 |  |  | 1 | 647547 | 652584 | 5037 | 1 |  | 5037 | 5033.7309 | Adabor |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 5033.7309 | 5179.9 | -146.1691 | -2.8219 | OK
[9 empty] | Grand Total | 17148800 | 17159937 | 17148800 | -0.064901
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Adabor | at 33 KV level |  | 12349816.6191
[5 empty] | Shyamoli | at 33 KV level |  | 4002700.5134
[5 empty] | Satmasjid | at 33 KV level |  | 796282.8675
[5 empty] | Total = |  |  | 17148800 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | #REF! |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) | 132 |  | 42627810 | 1 | 157.05 | 175.359 | 18.309 | 960000 | 0 | 17576640
2 | Dhaka University-1 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) | 132 |  | 42627812 | 1 | 158.41 | 176.915 | 18.505 | 960000 | 0 | 17764800
3 | Dhaka University-2 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 35341440
[9 empty] | Net Total | 35341440
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 | 132 |  | 2877 | 1 | 125.9 | 140.36 | 14.46 | 1200000 |  | 17352000
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 | 132 |  | 2811 | 1 | 126.72 | 141.53 | 14.81 | 1200000 |  | 17772000
[6 empty] | 0 | 0 | Total Import/Export |  | 0 | 35124000
[6 empty] | 0 | 0 | Net Total |  | 35124000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 132 KV Dhanmondi | 132 | 0 | SIEM0480 | 1 | 79348 | 96919 | 17571 | 1000 |  | 17571000
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total |  | 17571000
| DHAKA UNIVERSITY 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | 2752 | 1 | 200.96 | 208.39 | 7.43 | 1200000 |  | 8916000
4 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | 2867 | 1 | 219.01 | 226.41 | 7.4 | 1200000 |  | 8880000
[9 empty] | Total |  | 17796000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 35341440 |  | EXPORT TO OTHER S/S |  |  | 17571000 |  | 132 KV NET IMPORT |  | 17796000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 17796000 |  | 33 KV NET IMPORT |  | 17668800
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 127200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.7148%
| 132 KV TOTAL IMPORT |  | 35341440
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  | 2769 | 1 | 332.48 | 344.76 | 12.28 | 720000 | 8841600
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  | 2830 | 1 | 361.7 | 373.96 | 12.26 | 720000 | 8827200
[6 empty] | 0 | 0 |  | Total | 17668800 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [10 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  | 2751 | 1 | 32.6 | 34.22 | 1.62 | 240000 |  | 388800 | 387791.8045 |  | -0.81695 | DHAKA UNIVERSITY 33/11 KV SS | 1938959.0226 |  | 33/11 kV 28/35 MVA T-1 | 387791.8045 | 440508.7167 | -52716.9122 | -11.9673 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  | 4253 | 1 | 50.74 | 54.95 | 4.21 | 240000 |  | 1010400 | 1007779.9364 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 1007779.9364 | 954013.9558 | 53765.9807 | 5.6358 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  | 2808 | 1 | 18.57 | 20.84 | 2.27 | 240000 |  | 544800 | 543387.2816 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 543387.2816 | 503507.3655 | 39879.9161 | 7.9204 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 1944000 | 1938959.0226 | [5 empty] | 33 KV Feeders | 1938959.0226 | 1898030.038 | 40928.9846 | 2.1564 | OK
2 | Spare | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 | 33 |  | 2804 | 1.5 | 147.58 | 156.91 | 9.33 | 360000 |  | 5038200 | 5025135.4669 |  | 1.0713 | BB AVENUE 33/11 KV SS | 7552963.526 |  | BB Avenue-1 | 5025135.4669 | 4130446.7857 | 894688.6812 | 21.6608 | OK
3 | DMC Circuit-1 | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 | [5 empty] | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | 0.74913 | DMC 33/11 KV SS | 3853716.964 |  | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 | 33 |  | 2753 | 1 | 408.2 | 420.24 | 12.04 | 360000 |  | 4334400 | 4323160.4874 | [5 empty] | Biddyut Bhaban Circuit-2 | 4323160.4874 | 0 | 4323160.4874 | #DIV/0! | #DIV/0!
10 | DMC Circuit-2 | 33 |  | 2803 | 1.03 | 300.04 | 310.46 | 10.42 | 360000 |  | 3863736 | 3853716.964 |  | 1.8284 | BIDDYUT BHABAN 33/11 KV SS | 4323160.4874 |  | DMC Circuit-2 | 3853716.964 | 4272970.6888 | -419253.7248 | -9.8118 | OK
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 184 | 191.04 | 7.04 | 360000 |  | 2534400 | 2527828.0591 | [5 empty] | BB Avenue-2 | 2527828.0591 | 1412952.4875 | 1114875.5716 | 78.904 | FAULT
12 | Spare | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 15770736 | 15729840.9774 | [5 empty] | 0 | 15729840.9774 | 9816369.962 | 5913471.0154 | 60.2409 | FAULT
[8 empty] | Grand Total |  | 17668800 | 17714736 | 17668800 | -0.25931
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 40.3 | 42.56 | 2.26 | 250000 | 565000 |  | 540326.4354
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 47.3 | 51.28 | 3.98 | 250000 | 995000 |  | 951548.3243
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 17.3 | 19.17 | 1.87 | 250000 | 467500 |  | 447084.2629
[6 empty] | 0 | 0 |  | Total | 2027500 |  | 1938959.0226
| DHAKA UNIVERSITY 11 kV SIDE |  |  |  |  | 0 | 0
| Mokarom Bhabon | 11 |  | 2761 | 1 | 50 | 53.49 | 3.49 | 60000 |  | 209400 | 207689.3161 | Ramna |  |  |  |  | Mokarom Bhabon | 207689.3161 | 186304.8566 | 21384.4595 | 11.4782 | OK
4 | 11 kV Shaid Minar RMU | 11 |  | 2850 | 1 | 116.8 | 122.87 | 6.07 | 60000 |  | 364200 | 361224.6845 | Ramna |  |  |  |  | 11 kV Shaid Minar RMU | 361224.6845 | 367165.7402 | -5941.0557 | -1.6181 | OK
5 | 11 kV Shaidulla Hall | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | 11 |  | 2836 | 1 | 90.5 | 95.21 | 4.71 | 60000 |  | 282600 | 280291.312 | Ramna |  |  |  |  | MBA Bhabon | 280291.312 | 263125.3657 | 17165.9463 | 6.5239 | OK
11 | Suprime Court | 11 |  | 2835 | 1 | 50 | 55.93 | 5.93 | 60000 |  | 355800 | 352893.3079 | Ramna |  |  |  |  | Suprime Court | 352893.3079 | 353253.3645 | -360.0566 | -0.10193 | OK
12 | Karjon Hall | 11 |  | 2853 | 1 | 55.9 | 61.8 | 5.9 | 60000 |  | 354000 | 351108.0129 | Ramna |  |  |  |  | Karjon Hall | 351108.0129 | 342970.3043 | 8137.7086 | 2.3727 | OK
13 | Spare | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | 11 |  | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | Swimming Pool | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU | 11 |  | 2772 | 1 | 72.1 | 80.07 | 7.97 | 60000 |  | 478200 | 474293.3666 | Ramna |  |  |  |  | Police Head Quarter RMU | 474293.3666 | 554680.3686 | -80387.002 | -14.4925 | OK
17 | Spare | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare | 11 |  | 2764 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Spare | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 2027500 | 2044200 | 2027500 | -0.81695
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2027500
[5 empty] | Total = |  |  | 2027500 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 | 33 | 0 | 2753 | 1 | 408.2 | 420.24 | 12.04 | 360000 | 0 | 4334400 | 4323160.4874
[9 empty] | Total | 0 | 4334400 | 4323160.4874
0 | 33kV Biddyut Bhaban Circuit | 33 | Export | 0 | 1 | 486697 | 487353 | 656 | 600 | 0 | 393600 | 0 | 0
[9 empty] | Total | 0 | 393600 | 0
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 31669.53 | 33133.036 | 1463.506 | 270 | 0 | 395146.62
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 21216.15 | 21216.15 | 0 | 270 |  | 0
| Dhaka University Incoming-1 | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58473.3 | 58694.04 | 220.74 | 270 | 59599.8
| Dhaka University Incoming-2 | 33 |  | DHK-C9343 | 1 | 45329.41 | 61839.52 | 16510.11 | 270 |  | 4457729.7
[6 empty] | 0 | 0 |  | Total |  | 4852876.32 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58473.3 | 58694.04 | 220.74 | 270 |  | 59599.8
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total |  | 59599.8
[6 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-C9342 | 1 | 76426.69 | 81527.25 | 5100.56 | 270 |  | 1377151.2
3 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK-C9308 | 1 | 19008.37 | 31640.93 | 12632.56 | 270 |  | 3410791.2
[9 empty] | Total |  | 4787942.4 | 4847542.2
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 4852876.32 |  | EXPORT TO OTHER S/S |  |  | 59599.8 |  | 33 KV NET IMPORT |  | 4793276.52
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 4793276.52 |  | 33 KV TX HV SIDE |  | 4787942.4
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 5334.12
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1113%
| TOTAL IMPORT |  | 4852876.32
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK-C9316 | 1 | 56646.38 | 62345.89 | 5699.51 | 240 | 1367882.4 |  | 1374742.0387
10 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK-C9377 | 1 | 69701.91 | 83874.73 | 14172.82 | 240 | 3401476.8 |  | 3418534.4813
[6 empty] | 0 | 0 |  | Total | 4769359.2 |  | 4793276.52
| BIDDYUT BHABAN 11 KV SIDE |  |  |  |  | 0 | 0
6 | Segunbagicha | 11 |  | DHK-C9360 | 1 | 82917.41 | 93600.91 | 10683.5 | 60 |  | 641010 | 652730.1844 | Ramna |  |  |  |  | Segunbagicha | 652730.1844 | 660791.8145 | -8061.63 | -1.22 | OK
| Secretariat RMU | 11 |  | DHK-C9379 | 1 | 71809.95 | 74577.49 | 2767.54 | 60 |  | 166052.4 | 169088.4911 | Ramna |  |  |  |  | Secretariat RMU | 169088.4911 | 173479.2405 | -4390.7494 | -2.531 | OK
7 | NBR RMU | 11 |  | DHK-C9319 | 1 | 51570.08 | 59233.63 | 7663.55 | 60 |  | 459813 | 468220.1905 | Ramna |  |  |  |  | NBR RMU | 468220.1905 | 479026.3146 | -10806.1241 | -2.2559 | OK
8 | Ramna 11 kV Sw/S-2 | 11 |  | DHK-C9364 | 1 | 8506.79 | 9654.36 | 1147.57 | 60 |  | 68854.2 | 70113.1256 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-2 | 70113.1256 | 552257.97 | -482144.8443 | -87.3043 | CHECK
11 | Ramna 11 kV Sw/S-1 | 11 |  | DHK-C9375 | 1 | 46623.88 | 51466.11 | 4842.23 | 60 |  | 290533.8 | 295845.9008 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-1 | 295845.9008 | 960645.5509 | -664799.6502 | -69.2034 | CHECK
12 | Family Planning | 11 |  | DHK-C9378 | 1 | 49313.12 | 57130.46 | 7817.34 | 60 |  | 469040.4 | 477616.3037 | Ramna |  |  |  |  | Family Planning | 477616.3037 | 472965.3149 | 4650.9888 | 0.98337 | OK
13 | Muktijuddho Montranalaya | 11 |  | DHK-C9376 | 1 | 42919.82 | 58952.06 | 16032.24 | 60 |  | 961934.4 | 979522.345 | Ramna |  |  |  |  | Muktijuddho Montranalaya | 979522.345 | 1003580.0431 | -24057.6982 | -2.3972 | OK
14 | Purana Palton | 11 |  | DHK-C9318 | 1 | 49147.44 | 54862.84 | 5715.4 | 60 |  | 342924 | 349193.9997 | Ramna |  |  |  |  | Purana Palton | 349193.9997 | 350733.9486 | -1539.9488 | -0.43906 | OK
15 | Tip Top Feeder | 11 |  | DHK-C9318 | 1 | 89567.58 | 111275.28 | 21707.7 | 60 |  | 1302462 | 1326276.1291 | Kakrail |  |  |  |  | Tip Top Feeder | 1326276.1291 | 1389761.4375 | -63485.3085 | -4.5681 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 |  | DHKD3784 | 1 | 341182 | 345768 | 4586 | 1 |  | 4586 | 4669.8501 | Ramna |  |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 4669.8501 | 4947.3654 | -277.5152 | -5.6094 | OK
[9 empty] | Grand Total | 4793276.52 | 4707210.2 | 4793276.52 | 1.8284
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 3467000.3909
[5 empty] | Kakrail | at 33 KV level |  | 1326276.1291
[5 empty] | Total = |  |  | 4793276.52 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 | 33 | 0 | 2803 | 1.03 | 300.04 | 310.46 | 10.42 | 360000 | 0 | 3863736 | 3853716.964
[9 empty] | Total | 0 | 3863736 | 3853716.964
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 405.5 | 420.58 | 15.08 | 240000 | 0 | 3619200 | 3620366.2554
[9 empty] | Total |  | 3619200 | 3620366.2554
| DMCH 33 KV SIDE (RECEIVING) | [10 empty] | 7474083.2194
| 33 kV DU Incoming Circuit-1 | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
[7 empty] | 0 |  | Total |  | 0 | 0
| DMCH 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
0
| DMCH 33 KV SIDE | [5 empty] | 0
| 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | 00000069 | 1 | 125486880 | 129070320 | 3583440 | 1 |  | 3583440
2 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
[9 empty] | Total |  | 3583440
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 3853716.964 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 7474083.2194
| DHANMONDI 33 kV SIDE |  | 3620366.2554 |  | 33 KV NET IMPORT |  |  | 7474083.2194 |  | 33 KV TX HV SIDE |  | 7474083.2194
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7474083.2194
11 KV SIDE of___DMCH 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000056 | 1 | 124262264 | 127816064 | 3553800 | 1 | 3553800 |  | 3629101.919
14 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000034 | 1 | 152062880 | 155828080 | 3765200 | 1 | 3765200 |  | 3844981.3004
[6 empty] | 0 | 0 |  | Total | 7319000 |  | 7474083.2194
| DMCH 11 KV SIDE |  |  |  |  | 0 | 0
6 | Nearest O/H | 11 |  | 00000126 | 1 | 7294622 | 7520221 | 225599 | 1 |  | 225599 | 227289.0317 | Ramna |  |  |  |  | Nearest O/H | 227289.0317 | 224820.1739 | 2468.8579 | 1.0981 | OK
| Jagannath Hall | 11 |  | 00000002 | 1 | 2654153 | 2759593 | 105440 | 1 |  | 105440 | 106229.8836 | Ramna |  |  |  |  | Jagannath Hall | 106229.8836 | 110593.2428 | -4363.3592 | -3.9454 | OK
7 | Samsun Nahar Hall | 11 |  | 00000024 | 1 | 9370297 | 9697616 | 327319 | 1 |  | 327319 | 329771.0476 | Ramna |  |  |  |  | Samsun Nahar Hall | 329771.0476 | 322680.6125 | 7090.4352 | 2.1974 | OK
8 | Spare, 4L | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | 11 |  | 00000023 | 1 | 21315228 | 21866026 | 550798 | 1 |  | 550798 | 554924.1978 | Lalbag |  |  |  |  | Board Office O/H, (5L) | 554924.1978 | 600144.1706 | -45219.9728 | -7.5349 | OK
10 | OT- Complex | 11 |  | 00000167 | 1 | 6148345 | 6392704 | 244359 | 1 |  | 244359 | 246189.5687 | Ramna |  |  |  |  | OT- Complex | 246189.5687 | 446170.5101 | -199980.9414 | -44.8216 | CHECK
11 | Alia Mdrasha O/H, (7L) | 11 |  | 00000148 | 1 | 9394377 | 9536497 | 142120 | 1 |  | 142120 | 143184.6648 | Lalbag |  |  |  |  | Alia Mdrasha O/H, (7L) | 143184.6648 | 77701.5086 | 65483.1562 | 84.2753 | FAULT
12 | Majed Sordar Road | 11 |  | 00000164 | 1 | 55060864 | 56822140 | 1761276 | 1 |  | 1761276 | 1774470.2621 | Bangshal |  |  |  |  | Majed Sordar Road | 1774470.2621 | 1602752.7729 | 171717.4892 | 10.7139 | OK
15 | Chankharpool, 9L | 11 |  | 00000001 | 1 | 46801764 | 48003364 | 1201600 | 1 |  | 1201600 | 1210601.5564 | Bangshal |  |  |  |  | Chankharpool, 9L | 1210601.5564 | 1176945.2408 | 33656.3156 | 2.8596 | OK
16 | Shahidullah College O/H, (10L) | 11 |  | 00000003 | 1 | 12842169 | 13105088 | 262919 | 1 |  | 262919 | 264888.6074 | Lalbag |  |  |  |  | Shahidullah College O/H, (10L) | 264888.6074 | 263222.0224 | 1666.585 | 0.63315 | OK
17 | Ananda Bazar | 11 |  | 00000111 | 1 | 14878044 | 15022203 | 144159 | 1 |  | 144159 | 145238.9396 | Ramna |  |  |  |  | Ananda Bazar | 145238.9396 | 167074.5674 | -21835.6278 | -13.0694 | OK
18 | Hosseni Dalan O/H, (12L) | 11 |  |  | 1 | 50.74 | 54.95 | 4.21 | 60000 | Estimated | 1032221.88 | 1039954.5727 | Lalbag | Estimated from Grid SAS Data |  |  |  | Hosseni Dalan O/H, (12L) | 1039954.5727 | 1170127.1783 | -130172.6057 | -11.1247 | OK
19 | Badrun Nessa College | 11 |  | 00000006 | 1 | 19521592 | 20028432 | 506840 | 1 |  | 506840 | 510636.8949 | Lalbag |  |  |  |  | Badrun Nessa College | 510636.8949 | 522687.5196 | -12050.6248 | -2.3055 | OK
20 | Dhaka Medical College, Unit-II | 11 |  | 00000125 | 1 | 11679371 | 12004431 | 325060 | 1 |  | 325060 | 327495.1248 | Ramna |  |  |  |  | Dhaka Medical College, Unit-II | 327495.1248 | 332597.3491 | -5102.2244 | -1.5341 | OK
21 | Spare, 15L | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | 11 |  | 00000127 | 1 | 20301830 | 20882750 | 580920 | 1 |  | 580920 | 585271.851 | Ramna |  |  |  |  | Sheikh Hasina National Burn Institute | 585271.851 | 637362.5402 | -52090.6892 | -8.1729 | OK
23 | Aux. Transformer, AT-1 | 0.415 |  | DHKF-7804 | 1 | 2637.73 | 2716.51 | 78.78 | 100 |  | 7878 | 7937.0165 | Ramna |  |  |  |  | Aux. Transformer, AT-1 | 7937.0165 | 8829.1604 | -892.1439 | -10.1045 | OK
24 | Aux. Transformer, AT-2 | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7474083.2194 | 7418508.88 | 7474083.2194 | 0.74913
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 1975422.4635
[5 empty] | Lalbag | at 33 KV level |  | 2513588.9375
[5 empty] | Bangshal | at 33 KV level |  | 2985071.8185
[5 empty] | Total = |  |  | 7474083.2194 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 | 33 | 0 | 2804 | 1.5 | 147.58 | 156.91 | 9.33 | 360000 | 0 | 5038200 | 5025135.4669
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 184 | 191.04 | 7.04 | 360000 | 0 | 2534400 | 2527828.0591
[9 empty] | Total | 0 | 7572600 | 7552963.526
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 | 33 |  | BD 017078 | 1 | 0 | 0 | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 | 33 |  | BD 017090 | 1 | 66181.63 | 68637.19 | 2455.56 | 1125 |  | 2762505
[6 empty] | 0 | 0 |  | Total | 0 | 2762505 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
0
0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD 017093 | 1 | 91945.85 | 96989.49 | 5043.64 | 1000 |  | 5043640
3 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD 017094 | 1 | 51573.85 | 54035.49 | 2461.64 | 1000 |  | 2461640
[9 empty] | Total |  | 7505280
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 7552963.526 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BB AVENEU 33 KV NET IMPORT |  | 7552963.526
[5 empty] | BB AVENEU 33 KV NET IMPORT |  |  | 7552963.526 |  | 33 KV TX HV SIDE |  | 7505280
[10 empty] | LOSS UNITS=> |  | 47683.526
[10 empty] | LOSS % IN => |  | 0.6313%
| TOTAL IMPORT |  | 7552963.526
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD 014052 | 1 | 92175.35 | 97190.74 | 5015.39 | 1000 | 5015390 |  | 5076256.6652
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD 014055 | 1 | 51052.95 | 53499.96 | 2447.01 | 1000 | 2447010 |  | 2476706.8607
[6 empty] | 0 | 0 |  | Total | 7462400 |  | 7552963.526
| BB AVENEU 11 KV SIDE |  |  |  |  | 0 | 0
6 | Secratariet East | 11 |  | BD 013966 | 1 | 3666.02 | 3904.68 | 238.66 | 1000 |  | 238660 | 241216.6768 | Ramna |  |  |  |  | Secratariet East | 241216.6768 | 260076.7434 | -18860.0666 | -7.2517 | OK
| Taher Bag O/H | 11 |  | BD 014045 | 1 | 18336.98 | 19122.89 | 785.91 | 1000 |  | 785910 | 794329.1648 | Narinda |  |  |  |  | Taher Bag O/H | 794329.1648 | 678707.287 | 115621.8778 | 17.0356 | OK
7 | Al Raji Complex | 11 |  | BD 013983 | 1 | 13753.92 | 14539.29 | 785.37 | 1000 |  | 785370 | 793783.38 | Ramna |  |  |  |  | Al Raji Complex | 793783.38 | 773675.1898 | 20108.1901 | 2.599 | OK
8 | Raduni | 11 |  | BD 013999 | 1 | 27128.05 | 28415.36 | 1287.31 | 1000 |  | 1287310 | 1301100.4786 | Ramna |  |  |  |  | Raduni | 1301100.4786 | 623159.8339 | 677940.6447 | 108.7908 | FAULT
9 | Sundor Bon Square O/H | 11 |  | BD 013954 | 1 | 12696.85 | 13211.17 | 514.32 | 1000 |  | 514320 | 519829.721 | Narinda |  |  |  |  | Sundor Bon Square O/H | 519829.721 | 434096.0289 | 85733.6921 | 19.7499 | OK
10 | Shromo Bhobon O/H | 11 |  | BD 013985 | 1 | 12636.31 | 13147.42 | 511.11 | 1000 |  | 511110 | 516585.3335 | Ramna |  |  |  |  | Shromo Bhobon O/H | 516585.3335 | 525134.9167 | -8549.5833 | -1.6281 | OK
11 | Nawabpur Road | 11 |  | BD 013953 | 1 | 19355.25 | 20250.6 | 895.35 | 1000 |  | 895350 | 904941.5553 | Narinda |  |  |  |  | Nawabpur Road | 904941.5553 | 800366.4326 | 104575.1227 | 13.0659 | OK
12 | Spair | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | 11 |  | BD 013984 | 1 | 10672.48 | 11126.54 | 454.06 | 1000 |  | 454060 | 458924.1778 | Ramna |  |  |  |  | Ahad Police Box | 458924.1778 | 366641.2546 | 92282.9232 | 25.1698 | OK
17 | Nearest O/H | 11 |  | BD 013997 | 1 | 2505.26 | 2621.4 | 116.14 | 1000 |  | 116140 | 117384.1651 | Ramna |  |  |  |  | Nearest O/H | 117384.1651 | 114763.3233 | 2620.8418 | 2.2837 | OK
18 | Natab Bhaban | 11 |  | BD 014000 | 1 | 4804.84 | 4980.23 | 175.39 | 1000 |  | 175390 | 177268.8886 | Ramna |  |  |  |  | Natab Bhaban | 177268.8886 | 180013.0381 | -2744.1495 | -1.5244 | OK
19 | Spare | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | 11 |  | BD 013956 | 1 | 1408.1 | 1413.62 | 5.52 | 1000 |  | 5520 | 5579.1337 | Ramna |  |  |  |  | Awami League Party Office | 5579.1337 | 3568.1872 | 2010.9466 | 56.3577 | FAULT
21 | Khaddar Bazar | 11 |  | BD 014012 | 1 | 9709.64 | 10114.75 | 405.11 | 1000 |  | 405110 | 409449.7945 | Ramna |  |  |  |  | Khaddar Bazar | 409449.7945 | 392931.5775 | 16518.2169 | 4.2038 | OK
22 | Bangobondu National Stidium | 11 |  | BD 014008 | 1 | 6536.3 | 7820.82 | 1284.52 | 1000 |  | 1284520 | 1298280.5904 | Ramna |  |  |  |  | Bangobondu National Stidium | 1298280.5904 | 390265.4601 | 908015.1303 | 232.666 | FAULT
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4418 | 1 | 1124.63 | 1260.11 | 135.48 | 100 |  | 13548 | 13693.1347 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 13693.1347 | 0 | 13693.1347 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 41.9 | 47.81 | 5.91 | 100 |  | 591 | 597.3312 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 597.3312 | 0 | 597.3312 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7552963.526 | 7472909 | 7552963.526 | 1.0713
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 5333863.0848
[5 empty] | Narinda | at 33 KV level |  | 2219100.4411
[5 empty] | Total = |  |  | 7552963.526 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
[9 empty] | Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 0
[5 empty] | KALLYANPUR 33 KV NET IMPORT |  |  | 0 |  | KALLYANPUR 11 KV NET IMPORT |  | 0
[5 empty] | TOTAL EXPORT |  |  | 0 |  | LOSS UNITS=> |  | 0
[5 empty] | 132KV NET LOSS => |  |  | #DIV/0! |  | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming | 11 |  | 74819926 | 1 | 0 | 0 | 0
[6 empty] | 0 | 0 |  | Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  |  |  |  | 0 | 0
A | From Kallyanpur S/S. |  |  |  |  | 0 | 0
| 11 KV Gano Bhavan RMU | 11 |  | DHK14997 | 1 | 995.74 | 995.77 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar |  |  |  |  | 11 KV Gano Bhavan RMU | 1230 | 1230 | 0 | 0 | OK
| 11 KV Beribandh Feeder. | 11 |  | DHK14960 | 1 | 9646.16 | 9652 | 5.84 | 40000 |  | 233600 | 239440 | Adabor |  |  |  |  | 11 KV Beribandh Feeder. | 239440 | 234930 | 4510 | 1.9197 | OK
| 11 KV Adabor O/H | 11 |  | DHK14957 | 1 | 4419.91 | 4471.1 | 51.19 | 40000 |  | 2047600 | 2098790 | Adabor |  |  |  |  | 11 KV Adabor O/H | 2098790 | 1976610 | 122180 | 6.1813 | OK
| 11 KV Mansurabad | 11 |  | 77816681 | 1 | 51898.42 | 52193.9 | 295.48 | 8000 |  | 2363840 | 2422936 | Adabor |  |  |  |  | 11 KV Mansurabad | 2422936 | 2313630 | 109306 | 4.7244 | OK
| 11 KV Ring Road Feeder | 11 |  | 77816675 | 1 | 41923.11 | 42067.8 | 144.69 | 8000 |  | 1157520 | 1186458 | Adabor |  |  |  |  | 11 KV Ring Road Feeder | 1186458 | 1209910 | -23452 | -1.9383 | OK
| 11 KV Sewarage Pump | 11 |  | DHK14959 | 1 | 2112.81 | 2184.81 | 72 | 40000 |  | 2880000 | 2952000 | Adabor |  |  |  |  | 11 KV Sewarage Pump | 2952000 | 2380460 | 571540 | 24.0096 | OK
| 11 KV Technical School (DPDC) | 11 |  | DHK15019 | 1 | 8192.03 | 8249.67 | 57.64 | 40000 |  | 2305600 | 2363240 | Adabor |  |  |  |  | 11 KV Technical School (DPDC) | 2363240 | 2400960 | -37720 | -1.571 | OK
| 11 KV Goidertek (DPDC) | 11 |  | DHK14996 | 1 | 9369.92 | 9384.91 | 14.99 | 40000 |  | 599600 | 614590 | Adabor |  |  |  |  | 11 KV Goidertek (DPDC) | 614590 | 586300 | 28290 | 4.8252 | OK
B | From Agargaon S/S. | 11 | [9 empty] | 0
| 11 KV P.C Culture Housing | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H | 11 |  | DHK-15026 | 1 | 9179.18 | 9192.48 | 13.3 | 40000 |  | 532000 | 545300 | Shere b.nagar
| 11 KV Nearest RMU | 11 |  | DHK-15027 | 1 | 3863.97 | 3867.99 | 4.02 | 40000 |  | 160800 | 164820 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar | 11 |  | DHK-15025 | 1 | 3977.36 | 3978.44 | 1.08 | 40000 |  | 43200 | 44280 | Shere b.nagar
| 11 KV BCFCC Feeder. | 11 |  | DHK-15024 | 1 | 1038.1 | 1038.13 | 0.03 | 40000 |  | 1200 | 1230
| 11 KV NEC Feeder. | 11 |  | DHK-15023 | 1 | 431.56 | 431.59 | 0.03 | 40000 |  | 1200 | 1230
| 11 KV Manik Mia Feeder. | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0
[6 empty] | Export To Desco |  | 0 | Grand Total | 0 | 12327360 | 12635544 | 2.5
DESCO | 11 kV Tolarbugh | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 0 | 0 | 0 | #DIV/0!
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 11877454
[5 empty] | Shere b.nagar | at 33 KV level |  | 755630
[5 empty] | Satmasjid | at 33 KV level
[5 empty] | DESCO | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 12633084 | -2460
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 | 33 | 0 | 30799147 | 1 | 1516.92 | 1543.98 | 27.06 | 240000 | 0 | 6494400 | 6485363.6844
[9 empty] | Total | 0 |  | 6485363.6844
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
[9 empty] | Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming | 33 | EXPORT |  |  |  |  | 0 | 240000 |  | 0
| Lalbagh Incoming | 33 | [5 empty] | 0 | 240000 |  | 0
[9 empty] | Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 6485363.6844 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 6485363.6844
| IMPORT-2 |  |  |  | KALLYANPUR 33 KV NET IMPORT |  |  | 6485363.6844 |  | KALLYANPUR 11 KV NET IMPORT |  | 6485363.6844
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6485363.6844
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month August-2023 |  |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Kamrangirchar-2 11 KV SIDE | [13 empty] | 120
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 60
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 60
[9 empty] | Total | 0 |  | 6485363.6844 |  |  | 20
| Kamrangirchar-2 11 KV SIDE | [13 empty] | 80
1 | Nizambag | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1155511.98 | 1158100.6579 | Kamrangirchar | 95 |  |  |  | Nizambag | 1158100.6579 | 1095738.2283 | 62362.4297 | 5.6914 | OK
2 | Merry Stopes | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 328408.668 | 329144.3975 | Kamrangirchar | 27 |  |  |  | Merry Stopes | 329144.3975 | 365246.0761 | -36101.6786 | -9.8842 | OK
3 | Mujibur Ghat | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1340958.6566 | Kamrangirchar | 110 |  |  |  | Mujibur Ghat | 1340958.6566 | 1217486.9203 | 123471.7362 | 10.1415 | OK
4 | Madrasa | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1459594.08 | 1462863.989 | Kamrangirchar | 120 |  |  |  | Madrasa | 1462863.989 | 1424459.6968 | 38404.2922 | 2.6961 | OK
5 | Thana | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1219053.3241 | Kamrangirchar | 100 |  |  |  | Thana | 1219053.3241 | 1217486.9203 | 1566.4038 | 0.12866 | OK
6 | Al-Hera | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 973062.72 | 975242.6593 | Kamrangirchar | 80 |  |  |  | Waz Uddin School | 975242.6593 | 730492.1522 | 244750.5071 | 33.5049 | OK
8 | 11/0.4 kV Auxiliary Transformer | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off | [7 empty] | Grand Total | 6485363.6844 | 6470867.088 | 6485363.6844 | 0.22403
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 6485363.6844
[5 empty] | Total = |  |  | 6485363.6844 | 0
Note on F935: User: Grid CF=1.5

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) | 132 | IMPORT | 8993631 | 1 | 5799.375 | 5841.503 | 42.128 | 960000 | 0 | 40442880
| 132 KV Mogbazar-2 CKT(EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) | 132 |  | 8993659 | 1 | 4947.971 | 4980.479 | 32.508 | 960000 | 0 | 31207680
| 132 KV Mogbazar-1 CKT(EXP) | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 71650560
[9 empty] | Net Total | 71650560
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE | 6604452 | 1 | 9305.1 | 9361.52 | 56.42 | 720000 | 40622400
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  | 6604428 | 1 | 5577.9 | 5621.68 | 43.78 | 720000 | 31521600
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
[8 empty] | Total Import/Export |  | 72144000 | 0
[8 empty] | Net Total |  | 72144000 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0 |  |  | future Scope
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0 |  |  | No meter
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 72144000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 71650560 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 71650560
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 71650560 |  | MOGBAZAR 33 KV NET IMPORT |  | 71534400
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 116160
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1621%
| 132 KV TOTAL IMPORT |  | 71650560
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming | 33 | IMPORT | 76026303 | 1 | 9915.9 | 9966.09 | 50.19 | 480000 | 24091200 |  | 24130320.1127
| 132/33 KV GT-2 Incomming | 33 |  | 76026307 | 1 | 9911 | 9961.13 | 50.13 | 480000 | 24062400 |  | 24101473.3463
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 8119.3 | 8168.01 | 48.71 | 480000 | 23380800 |  | 23418766.541
[6 empty] | 0 | 0 |  | Total | 71534400 |  | 71650560
| MOGBAZAR 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. | 33 |  | 6604465 | 1 | 6975.8 | 6992.32 | 16.52 | 180000 |  | 2973600 | 2980161.6352 |  | 19826152.6597 | MOGBAZAR 33/11 KV SS | 6.4099 | 33/11 KV Transformer No.1. | 2980161.6352 | 2875900.9036 | 104260.7316 | 3.6253 | OK
| 33/11 KV Transformer No.2. | 33 |  | 202006985 | 1 | 35658246233 | 35659797492 | 1551259 | 3 | T2 Incomer side | 5003100 | 5014139.991 |  |  |  |  | 33/11 KV Transformer No.2. | 5014139.991 | 5008513.4094 | 5626.5815 | 0.11234 | OK
| 33/11 KV Transformer No.3. | 33 |  | 6604338 | 1 | 7041.7 | 7072.15 | 30.45 | 180000 |  | 5481000 | 5493094.5395 |  |  |  |  | 33/11 KV Transformer No.3. | 5493094.5395 | 5508972.1153 | -15877.5758 | -0.28821 | OK
| 33/11 KV Transformer No.4 | 33 |  |  | 1 | 1030741 | 1066922 | 36181 | 180000 | T4 Incomer side | 6324800 | 6338756.494 |  |  |  |  | 33/11 KV Transformer No.4 | 6338756.494 | 7069847.548 | -731091.054 | -10.341 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 19782500 | 19826152.6597 |  |  |  |  | 33 KV Feeders | 19826152.6597 | 20463233.9763 | -637081.3166 | -3.1133 | OK
8 | 33 kV Tejgaon U/G Feeder-1 | 33 |  | 76026300 | 1 | 6718.6 | 6741.53 | 22.93 | 360000 |  | 8254800 | 8273015.29 |  | 22942915.0586 | Tejgoan 33/11 kv ss | 1.0269 | 33 kV Tejgaon U/G Feeder-1 | 8273015.29 | 8350441.9432 | -77426.6532 | -0.92722 | OK
9 | 33 kV Tejgaon U/G Feeder-2 | 33 |  | 06604453 | 1 | 6514.5 | 6555.16 | 40.66 | 360000 |  | 14637600 | 14669899.7685 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 14669899.7685 | 14566157.1917 | 103742.5768 | 0.71222 | OK
10 | Bashundhara City | 33 |  | 660434 | 1 | 765.8 | 778.29 | 12.49 | 180000 |  | 2248200 | 2253160.9458 | Shere b.nagar | 6144328.4077 | Ispahani 33/11 kv ss | 0.34882 | Bashundhara City | 2253160.9458 | 2286948.2926 | -33787.3468 | -1.4774 | OK
11 | Ispahani-1 | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Ispahani-2 | 33 |  |  | 1.04 | 3858.6 | 3891.35 | 32.75 | 180000 |  | 6130800 | 6144328.4077 |  | 8888059.4768 | Green Road Dormatory 33/11 kv ss | 0.56541 | Ispahani-2 | 6144328.4077 | 6206654.4391 | -62326.0314 | -1.0042 | OK
13 | 33 kV Green Road Dormitory | 33 |  | 76026305 | 1 | 8045.2 | 8069.92 | 24.72 | 180000 | Reading From G. Dormitory Side | 8868490 | 8888059.4768 |  |  |  |  | 33 kV Green Road Dormitory | 8888059.4768 | 9269973.1514 | -381913.6745 | -4.1199 | OK
14 | 33 KV T&T-1 | 33 |  | 6604337 | 1 | 4566.5 | 4598.07 | 31.57 | 180000 |  | 5682600 | 5695139.3961 |  | 11193645.8514 | T&T 33/11 kv ss | -0.14892 | 33 KV T&T-1 | 5695139.3961 | 6005504.4704 | -310365.0743 | -5.168 | OK
13 | 33 KV T&T-2 | 33 |  | 6604336 | 1 | 5655.5 | 5685.98 | 30.48 | 180000 |  | 5486400 | 5498506.4553 |  |  |  |  | 33 KV T&T-2 | 5498506.4553 | 5606828.8568 | -108322.4015 | -1.932 | OK
14 | 33KV Karwan Bazar | 33 |  | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.72315 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | AT-1 | 33 |  | 6603338 | 1 | 1961 | 1961 | 0 | 80 |  | 0 | 0 |  |  |  |  | AT-1 | 0 | 17057.6784 | -17057.6784 | -100 | CHECK
20 | AT-2 | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 51308890 | 51422109.7403 |  |  |  |  | 0 | 51422109.7403 | 52309566.0237 | -887456.2834 | -1.6965 | OK
[8 empty] | Grand Total |  | 71248262.4 | 71091390 | 71248262.4 | 0.22066
-0.3377
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2253160.9458
[8 empty] | Total = | 2253160.9458 | 0 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 | 11 | Import | 6604457 | 1 | 535345 | 538232.4 | 2887.4 | 1000 | 2887400 |  | 2928305.6693
2 | 33/11 kV Transformer-2 | 11 | Import | 30/11009-1101 | 1 | 580337.2 | 585340.3 | 5003.1 | 1000 | 5003100 |  | 5073978.6984
3 | 33/11 kV Transformer-3 | 11 | Import | 6604454 | 1 | 575028.8 | 580362.7 | 5333.9 | 1000 | 5333900 |  | 5409465.1275
4 | 33/11 kV Transformer-4 | 11 | Import |  | 1 | 1008.39 | 1047.92 | 39.53 | 160000 | 6324800 |  | 6414403.1644
[6 empty] | 0 | 0 |  | Total | 19549200 |  | 19826152.6597
| MOGBAZAR 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40464.9 | 40634.2 | 169.3 | 1000 |  | 169300 | 177316.5531 | Moghbazar |  |  |  | 11 kV Doctor's Lane | 177316.5531 | 65016.8533 | 112299.6998 | 172.724 | FAULT
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 80645.6 | 80720.7 | 75.1 | 1000 |  | 75100 | 78656.0729 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 78656.0729 | 96666.9717 | -18010.8988 | -18.6319 | OK
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 119512.5 | 119910.2 | 397.7 | 1000 |  | 397700 | 416531.5604 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 416531.5604 | 434303.9973 | -17772.4368 | -4.0922 | OK
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 125254.8 | 127520.1 | 2265.3 | 1000 |  | 2265300 | 2372564.6062 | Moghbazar |  |  |  | 11KV Ambagan | 2372564.6062 | 2579216.4264 | -206651.8203 | -8.0122 | OK
[6 empty] | 0 | 0
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 144229.5 | 145820.4 | 1590.9 | 1000 |  | 1590900 | 1666230.9769 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1666230.9769 | 1593234.7726 | 72996.2043 | 4.5816 | OK
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9654.6 | 9811.6 | 157 | 1000 |  | 157000 | 164434.1337 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 164434.1337 | 177991.6827 | -13557.5489 | -7.617 | OK
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 122581.3 | 124562.5 | 1981.2 | 1000 |  | 1981200 | 2075012.1387 | Kakrail |  |  |  | 11 kV Bangla Motor | 2075012.1387 | 2269581.709 | -194569.5704 | -8.5729 | OK
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 173266.6 | 174312.8 | 1046.2 | 1000 |  | 1046200 | 1095738.7944 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1095738.7944 | 1085008.9734 | 10729.821 | 0.98892 | OK
[6 empty] | 0 | 0
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 119411.5 | 120973.1 | 1561.6 | 1000 | Estimated | 1921798.872 | 2012798.2977 | Kakrail | 158 |  |  | 11 kV Iskaton | 2012798.2977 | 1909092.2251 | 103706.0726 | 5.4322 | OK
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 84471.2 | 85985.5 | 1514.3 | 1000 |  | 1514300 | 1586003.8772 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1586003.8772 | 1603212.6065 | -17208.7293 | -1.0734 | OK
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 123156.6 | 123510.7 | 354.1 | 1000 |  | 354100 | 370867.0494 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 370867.0494 | 398147.7603 | -27280.7109 | -6.8519 | OK
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 113333.9 | 114193.6 | 859.7 | 1000 |  | 859700 | 900407.8011 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 900407.8011 | 994564.7368 | -94156.9357 | -9.4672 | OK
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43654.2 | 328.5 | 1000 |  | 328500 | 344054.8595 | Kakrail |  |  |  | 11 kV BSRS Feeder | 344054.8595 | 0 | 344054.8595 | #DIV/0! | #DIV/0!
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8577.9 | 8722.2 | 144.3 | 1000 |  | 144300 | 151132.7739 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 151132.7739 | 165331.6353 | -14198.8614 | -8.5881 | OK
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  |  | 13411749.4952 | 12805398.872 | 13411749.4952 | 4.7351 |  |  |  |  | 13411749.4952 | 13371370.3506
1 | 11 kV TCB Feeder | 11 | T-4 |  | 1 | 35701.5 | 36240.7 | 539.2 | 1000 |  | 539200 | 593608.4852 | Kakrail |  |  |  | 11 kV TCB Feeder | 593608.4852 | 1091208.9552 | -497600.47 | -45.6008 | CHECK
2 | 11 kV Tejgaon SS-2 | 11 | T-4 |  | 1 | 30139.8 | 31397.9 | 1258.1 | 1000 |  | 1258100 | 1385049.7687 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1385049.7687 | 1574127.4074 | -189077.6387 | -12.0116 | OK
3 | Holy Day Inn | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 525840 | 578900.3818 | Tejgaon |  |  |  | Holy Day Inn | 578900.3818 | 542740.3295 | 36160.0523 | 6.6625 | OK
4 | Polly Bhabon-2 | 11 | T-4 |  | 1 | 18361.1 | 18383 | 21.9 | 1000 | Consumer meter damaged, 12 months average | 25557 | 28135.8532 | Kakrail |  |  |  | Polly Bhabon-2 | 28135.8532 | 27898.691 | 237.1622 | 0.85008 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 |  | 1 | 15062.1 | 16752.8 | 1690.7 | 1000 |  | 1690700 | 1861301.6803 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1861301.6803 | 1854771.9565 | 6529.7238 | 0.35205 | OK
6 | 11 kV Tejturibazar | 11 | T-4 |  | 1 | 130665.9 | 131432.7 | 766.8 | 1000 |  | 766800 | 844174.6782 | Kakrail |  |  |  | 11 kV Tejturibazar | 844174.6782 | 788742.3253 | 55432.3529 | 7.0279 | OK
7 | Songsad | 11 | T-4 |  | 1 | 2920.7 | 3299.2 | 378.5 | 1000 |  | 378500 | 416692.9 | Shere b.nagar |  |  |  | Songsad | 416692.9 | 475259.7411 | -58566.8411 | -12.3231 | OK
| Chennel 24 | 11 | T-4 |  | 1 | 7312.34 | 7319.22 | 6.88 | 1000 |  | 6880 | 7574.2329 | Moghbazar |  |  |  | Chennel 24 | 7574.2329 | 3766.4072 | 3807.8257 | 101.0997 | FAULT
8 | Sonargaon | 11 | T-4 |  | 1 | 39618 | 40252.9 | 634.9 | 1000 |  | 634900 | 698965.1841 | Kakrail |  |  |  | Sonargaon | 698965.1841 | 733347.8124 | -34382.6283 | -4.6884 | OK
| AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 6414403.1644 | 5826477 | 6414403.1644 | 10.0906
[9 empty] | Total | 19826152.6597 | 18631875.872 | 19826152.6597 | 6.4099
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | [14 empty] | AMR Meter Information
[5 empty] | Moghbazar | at 33 KV level |  | 2928322.4416 | [14 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
[5 empty] | Tejgaon | at 33 KV level |  | 7122678.34 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 94320 | 3000
[5 empty] | Kakrail | at 33 KV level |  | 9358458.9781 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 431520 | 3000
[5 empty] | Shere b.nagar | at 33 KV level |  | 416692.9 | [14 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 25557 | 300
[5 empty] | Total = |  |  | 19826152.6597 | 0
AMR Meter Information
[23 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[23 empty] | Shah Garments | 771.43 | 791.52 | 206.17 | 217.52
[23 empty] | Habib Hotel | 2528.57 | 2634.99 | 829.95 | 867.37
[23 empty] | The Joint Director BRDB | 1161.08 | 1235.07 | 232.15 | 243.35
[25 empty] | 791.52 | 217.52
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [23 empty] | 2634.99 | 867.37
[25 empty] | 1235.07 | 243.35
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 | 33 | 0 | 6604337 | 1 | 4566.5 | 4598.07 | 31.57 | 180000 | 0 | 5682600 | 5695139.3961
13 | 33 KV T&T-2 | 33 | 0 | 6604336 | 1 | 5655.5 | 5685.98 | 30.48 | 180000 | 0 | 5486400 | 5498506.4553
0 | Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 11169000 | 11193645.8514
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder | 33 | Import | DHK60891 | 1 | 977836 | 988335 | 10499 | 360 | 3779640
2 | 33 kV Moghbazar-2 Feeder | 33 | Import | DHK68131 | 1 | 888130 | 898200 | 10070 | 360 | 3625200
| 33 kV Ullon Feeder | 33 | Import | DHK68132 | 1 | 349.75 | 349.75 | 0 | 180000 | 0
[6 empty] | 0 | 0 |  | Total | 7404840 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 1031989 | 1031989 | 0 | 180 |  | 0
4 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 840001 | 860319 | 20318 | 180 |  | 5486400 |  |  | Meter Problem
[9 empty] | Total |  | 5486400 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 11193645.8514 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 11193645.8514
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 11193645.8514 |  | 33/11 KV XF LV SIDE |  | 11210580
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -16934.1486
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.1513%
| TOTAL IMPORT |  | 11193645.8514
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 48176 | 79863 | 31687 | 180 | 5703660 |  | 5695044.3328 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 991150 | 1021744 | 30594 | 180 | 5506920 |  | 5498601.5186 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 11210580 |  | 11193645.8514 | -0.15106 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 156809 | 179420 | 22611 | 60 |  | 1356660 | 1354639.697 | Kakrail |  |  |  | 11 kV post office | 1354639.697 | 1410640.1386 | -56000.4416 | -3.9699 | OK
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 423860 | 446690 | 22830 | 60 |  | 1369800 | 1367760.1292 | Kakrail |  |  |  | 11 kV anarkoli | 1367760.1292 | 1475917.0544 | -108156.9251 | -7.3281 | OK
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 944778 | 951155 | 6377 | 60 |  | 382620 | 382050.2122 | Moghbazar |  |  |  | 11 kV sonalibagh | 382050.2122 | 390823.0756 | -8772.8634 | -2.2447 | OK
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1943262 | 1958537 | 15275 | 60 |  | 916500 | 915135.1719 | Moghbazar |  |  |  | 11 Kv desh tv | 915135.1719 | 946635.0529 | -31499.881 | -3.3276 | OK
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 590.39 | 618.3 | 27.91 | 60000 |  | 1674600 | 1672106.229 | Moghbazar |  |  |  | 11 Kv Btcl | 1672106.229 | 1759482.372 | -87376.143 | -4.966 | OK
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 885274 | 895318 | 10044 | 60 |  | 602640 | 601742.5641 | Kakrail |  |  |  | 11 kV century | 601742.5641 | 617435.7813 | -15693.2172 | -2.5417 | OK
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 470250 | 488103 | 17853 | 60 |  | 1071180 | 1069584.8264 | Moghbazar |  |  |  | 11 kV cinema hall | 1069584.8264 | 1086052.1721 | -16467.3457 | -1.5163 | OK
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 697644 | 726493 | 28849 | 60 |  | 1730940 | 1728362.3289 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1728362.3289 | 1686240.4748 | 42121.8541 | 2.498 | OK
4 | 11 kv Sherebangla | 11 |  | DHK60915 | 1 | 694633 | 717945 | 23312 | 60 |  | 1398720 | 1396637.0623 | Moghbazar |  |  |  | 11 kv Sherebangla | 1396637.0623 | 1544547.6466 | -147910.5842 | -9.5763 | OK
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 320497 | 332275 | 11778 | 60 |  | 706680 | 705627.6304 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 705627.6304 | 690498.0173 | 15129.6131 | 2.1911 | OK
6 | Auxiliary |  | Export | U0004461 | 1 | 8095.99 | 8095.99 | 0 | 60 |  | 0 | 0 | Moghbazar |  |  |  | Auxiliary | 0 | 4061.5417 | -4061.5417 | -100 | CHECK
[9 empty] | Grand Total | 11193645.8514 | 11210340 | 11193645.8514 | -0.14892
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 3324142.3903
[5 empty] | Moghbazar | at 33 KV level |  | 6141141.1322
[5 empty] | Khilgaon | at 33 KV level |  | 1728362.3289
[5 empty] | Total = |  |  | 11193645.8514 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 | 132 | IMPORT | 8993681 | 1 | 2642.939 | 2668.601 | 25.662 | 1440000 | 0 | 36953280
| Ullon-1 | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 36953280
[8 empty] | Net Total |  | 36953280
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) | 132 |  | 8993624 | 1 | 4793.7 | 4818.99 | 25.29 | 960000 | 0 | 24278400
| Maniknager-2 (new line to ullon) | 132 |  |  | 1 | 11.003 | 11.003 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 24278400
[8 empty] | Net Total |  | 24278400
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 | 132 |  | 8993659 | 1 | 4400.359 | 4415.048 | 14.689 | 960000 | 0 | 14101440
| Ullon U/G-1 | 132 |  |  | 1 | 1.561 | 1.561 | 0 | 960000 | 0 | 0
| Ullon U/G-2 | 132 |  | 8993660 | 1 | 4084.578 | 4098.55 | 13.972 | 960000 | 0 | 13413120
| Ullon U/G-2 | 132 |  |  | 1 | 1.33 | 1.33 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 27514560
[8 empty] | Net Total |  | 27514560
ULLON 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
| EXPORT TO OTHERS 132/33 KV SS | [12 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 | 132 |  |  | 1 | 1632756 | 1632756 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 | 132 |  |  | 1 | 2131079 | 2161566 | 30487 | 1000 |  | 30487000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 | 132 |  |  | 1 | 2887068 | 2917391 | 30323 | 1000 |  | 30323000 |  |  | 132 kV Ullon CKT-3 | 31978000
[9 empty] | Total |  | 60810000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 27936240
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 36953280 |  | EXPORT TO OTHER S/S |  |  | 60810000 |  | 132 KV NET IMPORT |  | 27936240
| HORIPUR 132 SIDE (TARIFF POINT) |  | 24278400 |  | 132 KV Net EXPORT |  |  | 27936240 |  | 132/33 KV GT LV Side |  | 27456384
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 27514560 | [6 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 479856
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.718%
| 132 KV TOTAL IMPORT |  | 88746240
33 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming | 33 | Import | BD001812 | 1 | 2157.486 | 2186.3546 | 28.8686 | 480000 | 13856928 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming | 33 | Import | BD001858 | 1 | 2079.276 | 2107.6082 | 28.3322 | 480000 | 13599456 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 27456384 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1564.8785 | 1597.0678 | 32.1893 | 240000 |  | 7725432 | 7730871.3347 |  | 15818849.9251 | Taltola 33/11 kv ss | 0.36408 | Taltala-1 | 7730871.3347 | 7471725.0456 | 259146.289 | 3.4684 | OK
| Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Mgbazar T&T | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9096 | 1163.9096 | 0 | 240000 |  | 0 | 0 |  | 0 | Mgbazar T&T 33/11 kv ss | -0.14892 | Kakrail | 0 | 312.7997 | -312.7997 | -100 | CHECK
2 | Taltala-2 | 33 | Export | BD001837 | 1 | 2529.1788 | 2562.855 | 33.6762 | 240000 |  | 8082288 | 8087978.5904 |  |  |  |  | Taltala-2 | 8087978.5904 | 8043234.0764 | 44744.514 | 0.5563 | OK
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 0 | Kakrail 33/11 kv ss | 1.1413 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 3.0565 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon | 33 | Export | BD001895 | 1 | 62.0687 | 74.9348 | 12.8661 | 240000 |  | 3087864 | 3090038.1083 |  | 0 | Tejgoan 33/11 kv ss | 1.0269 | Khailgaon | 3090038.1083 | 35803.5297 | 3054234.5786 | 8530.5404 | FAULT
4 | AT at GIS Building | 415 | Export | DHKE4577 | 1 | 144728 | 148109 | 3381 | 1 |  | 3381 | 3383.3805 |  | 3090038.1083 | Khilgoan 33/11 kv ss | 1.5 | AT at GIS Building | 3383.3805 | 3573.1345 | -189.754 | -5.3106 | OK
[6 empty] | 0 | 0 |  | TOTAL= |  | 18898965 | 18912271.4139 |  |  |  |  | 0 | 18912271.4139 | 15554648.5859 | 3357622.828 | 21.586 | OK
| 33 KV Local Feeder -1 | 33 | NET IMPORT |  | 1 | 1134.3375 | 1152.3613 | 18.0238 | 240000 |  | 4325712 | 4328757.6543 |  | 8516656.2021 | Ullon 33/11 kv ss | 0.74731 | 33 KV Local Feeder -1 | 4328757.6543 | 4402510.7716 | -73753.1173 | -1.6753 | OK
| 33KV Local Feeder- 2 | 33 |  |  | 1 | 862.7688 | 880.2061 | 17.4373 | 240000 |  | 4184952 | 4187898.5478 |  |  |  |  | 33KV Local Feeder- 2 | 4187898.5478 | 4268680.6424 | -80782.0946 | -1.8924 | OK
[9 empty] | TOTAL= |  | 8510664 | 8516656.2021 |  |  |  |  | 0 | 8516656.2021 | 8671191.4141 | -154535.212 | -1.7822 | OK
[9 empty] | Grand Total | 27428927.616 | 27409629 | 27428927.616 | 0.070408
11 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 134 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 82 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 8510664 |  | 8516656.2021 |  |  | 52 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [13 empty] | 17.3333 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 973062.72 | 980334.5269 | Moghbazar | 80 | 99.3333 |  | West Malibagh | 980334.5269 | 1038100.3806 | -57765.8537 | -5.5646 | OK
2 | Ullon | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1824492.6 | 1838127.2379 | Moghbazar | 150 |  |  | Ullon | 1838127.2379 | 1648747.6632 | 189379.5746 | 11.4863 | OK
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1642043.34 | 1654314.5141 | Moghbazar | 135 |  |  | Mohanagar | 1654314.5141 | 1770877.1198 | -116562.6057 | -6.5822 | OK
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1094695.56 | 1102876.3427 | Moghbazar | 90 |  |  | Bagichartek | 1102876.3427 | 1282359.2936 | -179482.9509 | -13.9963 | OK
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1702859.76 | 1715585.422 | Moghbazar | 140 |  |  | Mirbagh | 1715585.422 | 1648747.6632 | 66837.7588 | 4.0539 | OK
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 1216328.4 | 1225418.1586 | Moghbazar | 100 |  |  | West Rampura | 1225418.1586 | 1282359.2936 | -56941.1351 | -4.4403 | OK
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 8516656.2021 | 8453482.38 | 8516656.2021 | 0.74731
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 8516656.2021
[5 empty] | Total = |  |  | 8516656.2021 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 | 132 | Export | 50146667 | 1 | 1786.459 | 1814.41 | 27.951 | 960000 | 0 | 26832960
2 | Rampura to Madartek-2 | 132 | Export | 50146668 | 1 | 1580.626 | 1608.469 | 27.843 | 960000 | 0 | 26729280
[8 empty] | Total Import/Export |  | 0 | 53562240
[8 empty] | Net Total |  | 53562240
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 | 132 | Import | SIEM0492 | 1 | 1572642 | 1599419 | 26777 | 1000 | 26777000
|  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 | 132 | Import | SIEM0489 | 1 | 1522099 | 1548897 | 26798 | 1000 | 26798000
|  | 132 | Export |  | 1 | 0 | 0 | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 53575000 | 0
[6 empty] | 0 | 0 | Net Total |  | 53575000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 |  |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| MADERTEK 132 KV SIDE |  |  |  |  | 0 | 0
3 | 133 kV GT-1 | 132 | Export |  | 1 | 1408768 | 1435687 | 26919 | 1000 |  | 26919000
4 | 133 kV GT-2 | 132 | Export |  | 1 | 1397199 | 1423886 | 26687 | 1000 |  | 26687000
[9 empty] | Total |  | 53606000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 53562240 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 53562240
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 53562240 |  | 33 KV NET IMPORT |  | 53824000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -261760
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.4887%
| 132 KV TOTAL IMPORT |  | 53562240
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0516 | 1 | 1557416 | 1584339 | 26923 | 1000 | 26923000 |  | 26792066.5042
2 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0515 | 3 | 517113 | 526080 | 8967 | 1000 | 26901000 |  | 26770173.4958
[6 empty] | 0 | 0 |  | Total | 53824000 |  | 53562240
| MADERTEK 33 KV SIDE |  |  |  |  | 0 | 0
| 33/11 kv Transforfers |  |  |  |  | 0 | 0
1 | 33 kV T-1 | 33 | Import | SIEM0512 | 1 | 407868 | 412276 | 4408 | 2000 |  | 8816000 | 8819662.0814 |  | 21302845.3224 | Madartek 33/11 kv ss
2 | 33 kV T-3 | 33 | Export |  | 1 | 75919 | 77680 | 1761 | 2000 |  | 3522000 | 3523463.0049
2 | 33 kV T-2 | 33 | Export | SIEM0505 | 1 | 410747 | 415225 | 4478 | 2000 |  | 8956000 | 8959720.2361
| 33 kv Feeders |  |  |  |  | 0 | 0 |  | Total |  | 21294000 | 21302845.3224 |  | 15228323.0721 | Banasree 33/11 kv ss
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 103409 | 108232 | 4823 | 2000 |  | 9646000 | 9650006.8554
1 | Goran | 33 | Export | SIEM0510 | 1 | 349987 | 354917 | 4930 | 2000 |  | 9860000 | 9864095.749 |  | 9864095.749 | Goran 33/11 kv ss
3 | Amulia | 33 | Export | SIEM0505 | 1 | 36382 | 37576 | 1194 | 6000 |  | 7164000 | 7166975.8566
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 90976 | 93764 | 2788 | 2000 |  | 5576000 | 5578316.2167 |  | 7166975.8566 | Amulia 33/11 kv ss
[9 empty] | Total |  | 32246000 | 32259394.6776
[8 empty] | Grand Total |  | 53562240 | 53540000 | 53562240 | 0.041539
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | GJU 71154 | 1 | 380729.6 | 385103.7 | 4374.1 | 2000 | 8748200 |  | 8814504.9071 |  | Consumption of Other NOCS | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | GJU 71155 | 1 | 383760.4 | 388211.6 | 4451.2 | 2000 | 8902400 |  | 8969873.6294 |  | 6621655.9454 | [5 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming | 11 | Import | 6604399 | 1 | 4687.77 | 4707.17 | 19.4 | 180000 | 3492000 |  | 3518466.7858 |  | Consumption of Mugpadara Check | [5 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 21142600 |  | 21302845.3224 |  | 14520944.0546 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 10.3885 | 12.208 | 1.8195 | 1000000 |  | 1819539 | 1839023.3133 | Mugdapara | Opening Conveted to GWH from MWH |  |  | Sobujbagh | 1839023.3133 | 1914129.2674 | -75105.9541 | -3.9238 | OK
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 99487.1 | 101422 | 1934.9 | 1000 |  | 1934900 | 1955619.6426 | Mugdapara |  |  |  | Madertek | 1955619.6426 | 2015001.2811 | -59381.6385 | -2.947 | OK
3 | Rajarbagh | 11 | Mugdapara | DHKD9104 | 1 | 0.9 | 1970.5 | 1969.6 | 1000 | 29 days reading Converted | 2105434.4828 | 2127980.2733 | Mugdapara | Meter Replaced on 03.08.23 |  |  | Rajarbagh | 2127980.2733 | 2037129.655 | 90850.6182 | 4.4597 | OK
| Goran | 11 |  | X1390296 | 1 | 28663.4 | 30567.9 | 1904.5 | 1000 |  | 1904500 | 1924894.1079 | Bashabo |  |  |  | Goran | 1924894.1079 | 2047460.5279 | -122566.42 | -5.9863 | OK
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 9771.1 | 11288.809 | 1517.709 | 1000 |  | 1517709 | 1533961.2033 | Mugdapara | From GWH to MWH |  |  | Dhakhingaon | 1533961.2033 | 1583000.8619 | -49039.6587 | -3.0979 | OK
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar | Cable Fault No Load |  |  | Manda | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 744.7806 | 984.8526 | 240.072 | 1000 |  | 240072 | 242642.782 | Mugdapara |  |  |  | Green Model Town | 242642.782 | 236939.3158 | 5703.4662 | 2.4071 | OK
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 3045.3432 | 3710.108 | 664.7648 | 1000 |  | 664764.8 | 671883.3535 | Mugdapara |  |  |  | Biswa Road | 671883.3535 | 576962.6065 | 94920.747 | 16.4518 | OK
2 | Mugdapara | 11 |  | X0854272 | 1 | 3885.1 | 4144.6 | 259.5 | 1000 |  | 259500 | 262278.8244 | Maniknagar |  |  |  | Mugdapara | 262278.8244 | 99804.6 | 162474.2244 | 162.7923 | FAULT
| Singapur | 11 |  | X1390302 (N) | 1 | 33574.1 | 35882.3 | 2308.2 | 1000 |  | 2308200 | 2332917.0805 | Banosree |  |  |  | Singapur | 2332917.0805 | 2449510.2642 | -116593.1836 | -4.7599 | OK
| Trimohony | 11 |  | X1390308 | 1 | 26608.8 | 28688.1 | 2079.3 | 1000 |  | 2079300 | 2101565.9326 | Banosree |  |  |  | Trimohony | 2101565.9326 | 2104795.0854 | -3229.1528 | -0.15342 | OK
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 12357.722 | 14286.038 | 1928.316 | 1000 |  | 1928316 | 1948965.1387 | Mugdapara | Closing Conveted to MWH from GWH |  |  | Mayakanon | 1948965.1387 | 1816135.3069 | 132829.8318 | 7.3139 | OK
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 4655.1844 | 5501.0628 | 845.8784 | 1000 |  | 845878.4 | 854936.3865 | Mugdapara |  |  |  | Ahmedbagh | 854936.3865 | 710891.4812 | 144044.9053 | 20.2626 | OK
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 720580 | 730251 | 9671 | 200 |  | 1934200 | 1954912.1468 | Mugdapara |  |  |  | Wasa Road | 1954912.1468 | 1661387.6173 | 293524.5295 | 17.6674 | OK
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 754033 | 761617 | 7584 | 200 |  | 1516800 | 1533042.4693 | Mugdapara |  |  |  | Nandipara | 1533042.4693 | 1508090.9874 | 24951.4819 | 1.6545 | OK
| AT-1 | 0.415 |  |  | 1 | 502.11 | 657.61 | 155.5 | 80 |  | 12440 | 12573.2122 | Mugdapara |  |  |  | AT-1 | 12573.2122 | 11708.7885 | 864.4237 | 7.3827 | OK
3 | AT-2 | 0.415 |  | 63394003 | 1 | 233.54 | 303.41 | 69.87 | 80 |  | 5589.6 | 5649.4556 | Mugdapara |  |  |  | AT-2 | 5649.4556 | 6156.9427 | -507.4872 | -8.2425 | OK
[9 empty] | Total | 21302845.3224 | 21077143.2828 | 21302845.3224 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 21302845.3224 | 21077143.2828 | 21302845.3224 | 1.0708
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 4434483.0131
[5 empty] | Bashabo | at 33 KV level |  | 1924894.1079
[5 empty] | Maniknagar | at 33 KV level |  | 262278.8244
[5 empty] | Mugdapara | at 33 KV level |  | 14681189.377
[5 empty] | Total = |  |  | 21302845.3224 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 | 33 | 0 | 76026300 | 1 | 6718.6 | 6741.53 | 22.93 | 360000 | 0 | 8254800 | 8273015.29
9 | 33 kV Tejgaon U/G Feeder-2 | 33 | 0 | 06604453 | 1 | 6514.5 | 6555.16 | 40.66 | 360000 | 0 | 14637600 | 14669899.7685
0 | Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 22892400 | 22942915.0586
TEJGOAN 33 KV SIDE (RECEIVING)
[6 empty] | 0 | 0 |  | Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 668563.1 | 701455.9 | 32892.8 | 270 |  | 8881056
2 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 486279.6 | 540611.2 | 54331.6 | 180 |  | 9779688
3 | 33/11 kV Transfomer-3 (T3) | 33 | Export | BD001872 | 1 | 216375 | 223451.2 | 7076.2 | 180000 |  | 7076200
[9 empty] | Total |  | 25736944 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 22942915.0586 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TEJGOAN 33 KV NET IMPORT |  | 22942915.0586
| IMPORT-2 |  |  |  | TEJGOAN 33 KV NET IMPORT |  |  | 22942915.0586 |  | 33 KV TX HV Side |  | 25736944
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -2794028.9414
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -12.18%
| TOTAL IMPORT |  | 22942915.0586
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 834789.6 | 877562.9 | 42773.3 | 180 | 7699194 |  | 7911506.1409 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 749140.6 | 791095.2 | 41954.6 | 180 | 7551828 |  | 7760076.392 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming | 11 | Import | BD001875 | 1 | 216375 | 223451.2 | 7076.2 | 1000 | 7076200 |  | 7271332.5257 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 22327222 |  | 22942915.0586 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | 11 |  | DHK60950 | 1 | 228050.8 | 254232.5 | 26181.7 | 60 |  | 1570902 | 1587033.6595 | Tejgaon |  |  |  | Nakhal Para Feeder | 1587033.6595 | 1590100.5899 | -3066.9305 | -0.19288 | OK
2 | Badda-Meghna Feeder | 11 |  | DHK60979 | 1 | 901418.5 | 914102.7 | 12684.2 | 60 |  | 761052 | 768867.2754 | Tejgaon |  |  |  | Badda-Meghna Feeder | 768867.2754 | 797427.1133 | -28559.838 | -3.5815 | OK
3 | Rasulbagh Feeder | 11 |  | DHK60948 | 1 | 991762.3 | 1023637.7 | 31875.4 | 60 |  | 1912524 | 1932163.7903 | Tejgaon |  |  |  | Rasulbagh Feeder | 1932163.7903 | 1821935.9992 | 110227.7911 | 6.05 | OK
4 | Lukas | 11 |  | 8A021100948-02 | 1 | 66843300 | 69201106 | 2357806 | 1 |  | 2357806 | 2382018.4101 | Tejgaon |  |  |  | Lukas | 2382018.4101 | 2450636.3287 | -68617.9186 | -2.8 | OK
5 | PWD RMU | 11 |  |  | 1 | 654515.2 | 656351.3 | 1836.1 | 1 |  | 1836.1 | 1854.955 | Tejgaon |  |  |  | PWD RMU | 1854.955 | 1876.4622 | -21.5072 | -1.1462 | OK
1 | Civil Aviation Feeder | 11 |  | DHK60977 | 1 | 840529.6 | 886999.5 | 46469.9 | 60 |  | 2788194 | 2816826.0828 | Tejgaon |  |  |  | Civil Aviation Feeder | 2816826.0828 | 2972868.5519 | -156042.4691 | -5.2489 | OK
2 | Ahasanullah Eng. | 11 |  | DHK60867 | 1 | 870599.2 | 881620.2 | 11021 | 60 |  | 661260 | 668050.5071 | Tejgaon |  |  |  | Ahasanullah Eng. | 668050.5071 | 681476.0179 | -13425.5108 | -1.9701 | OK
3 | New GMG Feeder | 11 |  | DHK61106 | 1 | 46250.7 | 86429.3 | 40178.6 | 60 |  | 2410716 | 2435471.7452 | Tejgaon |  |  |  | New GMG Feeder | 2435471.7452 | 2366892.1845 | 68579.5607 | 2.8975 | OK
4 | Shikajo | 11 |  | HA021101036-02 | 1 | 63571582 | 64377118 | 805536 | 1 |  | 805536 | 813808.0835 | Tejgaon |  |  |  | Shikajo | 813808.0835 | 877169.4199 | -63361.3365 | -7.2234 | OK
5 | Kahinur | 11 |  |  | 1 | 518848.9 | 541140.5 | 22291.6 | 60 |  | 1337496 | 1351230.8033 | Tejgaon |  |  |  | Kahinur | 1351230.8033 | 1347009.4431 | 4221.3602 | 0.31339 | OK
6 | Link road | 11 |  | 8A021100380-02 | 1 | 64330013 | 64751580 | 421567 | 1 |  | 421567 | 425896.0895 | Tejgaon |  |  |  | Link road | 425896.0895 | 415317.8944 | 10578.1951 | 2.547 | OK
7 | Shanta | 11 |  |  | 1 | 310614.7 | 321223.3 | 10608.6 | 60 |  | 636516 | 643052.4099 | Tejgaon |  |  |  | Shanta | 643052.4099 | 671568.0547 | -28515.6449 | -4.2461 | OK
1 | Karnafuly Feeder | 11 |  | DHK61084 | 1 | 34410.6 | 35120 | 709.4 | 1000 |  | 709400 | 716684.8588 | Tejgaon |  |  |  | Karnafuly Feeder | 716684.8588 | 722759.1976 | -6074.3388 | -0.84044 | OK
2 | Butex | 11 |  |  | 1 | 991.5 | 1093.4 | 101.9 | 1000 |  | 101900 | 102946.4154 | Tejgaon |  |  |  | Butex | 102946.4154 | 100374.7899 | 2571.6256 | 2.562 | OK
3 | OriON LAB | 11 |  |  | 1 | 8102262 | 8195184 | 92922 | 1 |  | 92922 | 93876.22 | Tejgaon |  |  |  | OriON LAB | 93876.22 | 95833.6401 | -1957.4201 | -2.0425 | OK
4 | Nina kabbo | 11 |  | 201101025-2 | 1 | 16842033 | 17125110 | 283077 | 1 |  | 283077 | 285983.9298 | Tejgaon |  |  |  | Nina kabbo | 285983.9298 | 281438.971 | 4544.9587 | 1.6149 | OK
5 | Satrong | 11 |  | HA021100515-2 | 1 | 91425148 | 93305530 | 1880382 | 1 |  | 1880382 | 1899691.7228 | Tejgaon |  |  |  | Satrong | 1899691.7228 | 1806807.9399 | 92883.7828 | 5.1408 | OK
6 | South East RMU | 11 |  |  | 1 | 729.2 | 858.1 | 128.9 | 1000 |  | 128900 | 130223.6796 | Tejgaon |  |  |  | South East RMU | 130223.6796 | 128807.568 | 1416.1115 | 1.0994 | OK
7 | Rangs Bhaban | 11 |  | HA021100939-2 | 1 | 432458 | 583380 | 150922 | 1 |  | 150922 | 152471.8244 | Tejgaon |  |  |  | Rangs Bhaban | 152471.8244 | 163396.3968 | -10924.5724 | -6.6859 | OK
8 | Babli | 11 |  |  | 1 | 56089.7 | 58307.6 | 2217.9 | 1000 |  | 2217900 | 2240675.7095 | Tejgaon |  |  |  | Babli | 2240675.7095 | 2109084.7983 | 131590.9112 | 6.2392 | OK
| SPL | 11 |  |  | 1 | 3911.5 | 4372.4 | 460.9 | 1000 |  | 460900 | 465633.0017 | Tejgaon |  |  |  | SPL | 465633.0017 | 455733.9249 | 9899.0768 | 2.1721 | OK
9 | DNCC Hospital | 11 |  |  | 1 | 14537.1 | 15555.1 | 1018 | 1000 |  | 1018000 | 1028453.8853 | Tejgaon |  |  |  | DNCC Hospital | 1028453.8853 | 1058083.8484 | -29629.9631 | -2.8003 | OK
| 11/.415 kv Local transformer | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
[9 empty] | Grand Total | 22942915.0586 | 22709708.1 | 22942915.0586 | 1.0269
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Tejgaon | at 33 KV level |  | 22942915.0586
[5 empty] | Total = |  |  | 22942915.0586 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 | 33 | 0 | 214393/44-2711 | 1 | 63.8262 | 72.4663 | 8.6401 | 1000 | Estimated | 8725694.4 | 8492568.689
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 8682445.8 | 8450475.5685
[9 empty] | Total |  | 17408140.2 | 16943044.2575
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import | DHKC9350 | 1 | 111497.5 | 111497.5 | 0 | 270 | 0
2 | Shatmasjid-2 | 33 | Import | DHKC9354 | 1 | 123054.55 | 123054.55 | 0 | 270 | 0
[6 empty] | 0 | 0 |  | Total | 0
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transfomer-1 (T1) | 33 | Export | DHKC9353 | 1 | 37395.2 | 86210.32 | 48815.12 | 180 |  | 8786721.6
2 | Transfomer-2 (T2) | 33 | Export | DHKC9305 | 1 | 49274.9 | 98033.95 | 48759.05 | 180 |  | 8776629
[9 empty] | Total |  | 17563350.6 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 16943044.2575 |  | EXPORT TO OTHER S/S |  |  | 0 |  | ASADGATE 33 KV NET IMPORT |  | 16943044.2575
| IMPORT-2 |  |  |  | ASADGATE 33 KV NET IMPORT |  |  | 16943044.2575 |  | ASADGATE 11 KV NET IMPORT |  | 17514993.376
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -571949.1185
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -3.376%
| TOTAL IMPORT |  | 16943044.2575
11 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHKC9371 | 1 | 10301.87 | 58777.95 | 48476.08 | 180 | 8725694.4 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHKC9337 | 1 | 50526.32 | 98762.13 | 48235.81 | 180 | 8682445.8 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 17408140.2 |  | 16943044.2575 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | 11 |  | DHKC9332 | 1 | 72755.2 | 76114.19 | 3358.99 | 60 |  | 201539.4 | 203554.794 | Shere b.nagar |  |  |  | Gonobhaban | 203554.794 | 226219.392 | -22664.598 | -10.0189 | OK
2 | Rapa Plaza Feeder | 11 |  | DHKC9339 | 1 | 76499.17 | 95633.85 | 19134.68 | 60 |  | 1148080.8 | 1159561.608 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1159561.608 | 1233509.5584 | -73947.9504 | -5.9949 | OK
3 | Shukrabad/ South Plaza | 11 |  | DHKC9324 | 1 | 15754.76 | 35056.28 | 19301.52 | 60 |  | 1158091.2 | 1169672.112 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 1169672.112 | 1195401.7152 | -25729.6032 | -2.1524 | OK
4 | Wasa O/H | 11 |  | DHKC9333 | 1 | 442.81 | 16726.09 | 16283.28 | 60 |  | 976996.8 | 986766.768 | Satmasjid |  |  |  | Wasa O/H | 986766.768 | 1324483.5744 | -337716.8064 | -25.498 | OK
5 | Bangabandhu Memorial Museum | 11 |  | DHKC9334 | 1 | 15376.97 | 15731.68 | 354.71 | 60 |  | 21282.6 | 21495.426 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 21495.426 | 21201.264 | 294.162 | 1.3875 | OK
6 | Iqbal Road O/H | 11 |  | DHKC9330 | 1 | 72221.61 | 98671.81 | 26450.2 | 60 |  | 1587012 | 1602882.12 | Shyamoli |  |  |  | Iqbal Road O/H | 1602882.12 | 1776423.3984 | -173541.2784 | -9.7691 | OK
7 | Town Hall | 11 |  | DHKC9351 | 1 | 798.64 | 35835.26 | 35036.62 | 60 |  | 2102197.2 | 2123219.172 | Shyamoli |  |  |  | Town Hall | 2123219.172 | 2353752.1728 | -230533.0008 | -9.7943 | OK
8 | Post Office | 11 |  | DHKC9331 | 1 | 64790.66 | 89748.19 | 24957.53 | 60 |  | 1497451.8 | 1512426.318 | Shyamoli |  |  |  | Post Office | 1512426.318 | 1672604.0352 | -160177.7172 | -9.5765 | OK
9 | Shangshad Bhaban | 11 |  | DHKC9370 | 1 | 11515.28 | 15559.57 | 4044.29 | 60 |  | 242657.4 | 245083.974 | Shere b.nagar |  |  |  | Shangshad Bhaban | 245083.974 | 292942.1376 | -47858.1636 | -16.3371 | OK
10 | Jakir Hossain Road | 11 |  | DHKC9373 | 1 | 8235.46 | 30815.6 | 22580.14 | 60 |  | 1354808.4 | 1368356.484 | Satmasjid |  |  |  | Jakir Hossain Road | 1368356.484 | 1603359.2736 | -235002.7896 | -14.6569 | OK
11 | New Colony O/H Feeder | 11 |  | DHKC9369 | 1 | 86475.56 | 110299.15 | 23823.59 | 60 |  | 1429415.4 | 1443709.554 | Satmasjid |  |  |  | New Colony O/H Feeder | 1443709.554 | 1041715.3824 | 401994.1716 | 38.5896 | OK
12 | Aurangzeb Feeder | 11 |  | DHKC9321 | 1 | 69565.32 | 95588.91 | 26023.59 | 60 |  | 1561415.4 | 1577029.554 | Shyamoli |  |  |  | Aurangzeb Feeder | 1577029.554 | 1636123.104 | -59093.55 | -3.6118 | OK
13 | Asadgate Local Feeder | 11 |  | DHKC9338 | 1 | 67929.33 | 99997.41 | 32068.08 | 60 |  | 1924084.8 | 1943325.648 | Satmasjid |  |  |  | Asadgate Local Feeder | 1943325.648 | 2129079.8592 | -185754.2112 | -8.7246 | OK
14 | Sonarbangla Road | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | 11 |  | DHKC9366 | 1 | 78786.74 | 110191.48 | 31404.74 | 60 |  | 1884284.4 | 1903127.244 | Shyamoli |  |  |  | Humayun Road | 1903127.244 | 1920389.3856 | -17262.1416 | -0.89889 | OK
16 | NHA | 11 |  | DHKC9374 | 1 | 57115.39 | 61032.09 | 3916.7 | 60 |  | 235002 | 237352.02 | Shyamoli |  |  |  | NHA | 237352.02 | 264138.5376 | -26786.5176 | -10.1411 | OK
17 | Auxiliary transformer | 0.415 |  |  | 1 | 633994 | 651252 | 17258 | 1 |  | 17258 | 17430.58 | Satmasjid |  |  |  | Auxiliary transformer | 17430.58 | 0 | 17430.58 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 17514993.376 | 17341577.6 | 17514993.376 | 1
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 1618310.88
[5 empty] | Dhanmondi | at 33 KV level |  | 1181057.034
[5 empty] | Satmasjid | at 33 KV level |  | 5759589.034
[5 empty] | Shyamoli | at 33 KV level |  | 8956036.428
at 33 KV level
[5 empty] | Total = |  |  | 17514993.376 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 103409 | 108232 | 4823 | 2000 | 0 | 9646000 | 9650006.8554
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 90976 | 93764 | 2788 | 2000 | 0 | 5576000 | 5578316.2167
[9 empty] | Total |  | 15222000 | 15228323.0721 | 0.041539
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import |  | 1 | 15589610 | 15589610 | 0 | 1 | 0
2 | Madertek Circuit-02 | 33 | Import |  | 1 | 11242090 | 11242090 | 0 | 1 | 0
3 | Ullon O/H | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
[9 empty] | Total | 0 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 | 33 | Export | 14 | 1 | 11612560 | 11612560 | 0 | 1 |  | 0
2 | Transformer-02 | 33 | Export | 74 | 1 | 8110080 | 13639440 | 5529360 | 1 |  | 5529360 |  |  | Meter Problem
[9 empty] | Total |  | 5529360
| 33 KV IMPORT |  | KWH |  | 33 KV Import |  |  | KWH |  | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 15228323.0721 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 15228323.0721
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 15228323.0721 |  | 33 KV TX HV SIDE |  | 5529360
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 9698963.0721
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 63.69%
| TOTAL IMPORT |  | 15228323.0721
11 KV SIDE of___BANASREE 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 0 |  | 0 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | 198 | 1 |  |  | 0 | 1 | 5529360 |  | 15228323.0721 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 5529360 |  | 15228323.0721 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | 11 |  | 141 | 1 | 6021560 | 8183640 | 2162080 | 1 |  | 2162080 | 2196051.2126 | Banosree |  |  |  | Angur Jora | 2196051.2126 | 2182461.1184 | 13590.0943 | 0.6227 | OK
2 | Block F-G Avenue | 11 |  | 68 | 1 | 8177840 | 10767760 | 2589920 | 1 |  | 2589920 | 2630613.5558 | Banosree |  |  |  | Block F-G Avenue | 2630613.5558 | 2686465.1418 | -55851.586 | -2.079 | OK
3 | Banasree Main Road(Monpura) | 11 |  | 168 | 1 | 6283880 | 8050960 | 1767080 | 1 |  | 1767080 | 1794844.8609 | Banosree |  |  |  | Banasree Main Road(Monpura) | 1794844.8609 | 1857089.8973 | -62245.0364 | -3.3518 | OK
4 | Baitul Kuddus | 11 |  | 62 | 1 | 9606640 | 11812880 | 2206240 | 1 |  | 2206240 | 2240905.0671 | Banosree |  |  |  | Baitul Kuddus | 2240905.0671 | 2321761.5567 | -80856.4896 | -3.4825 | OK
5 | Ideal | 11 |  |  | 1 | 8292520 | 9057960 | 765440 | 1 |  | 765440 | 777466.8098 | Banosree |  |  |  | Ideal | 777466.8098 | 813387.6289 | -35920.8191 | -4.4162 | OK
6 | Central Mosque | 11 |  | 46 | 1 | 42320 | 2164440 | 2122120 | 1 |  | 2122120 | 2155463.3498 | Banosree |  |  |  | Central Mosque | 2155463.3498 | 2252151.7613 | -96688.4115 | -4.2932 | OK
7 | Larive | 11 |  | 47 | 1 | 9603880 | 10720120 | 1116240 | 1 |  | 1116240 | 1133778.6787 | Banosree |  |  |  | Larive | 1133778.6787 | 1209136.6977 | -75358.019 | -6.2324 | OK
8 | Bank Colony | 11 |  |  | 1 | 4697520 | 5431800 | 734280 | 1 |  | 734280 | 745817.2151 | Khilgaon |  |  |  | Bank Colony | 745817.2151 | 791659.8328 | -45842.6177 | -5.7907 | OK
9 | Salambagh | 11 |  |  | 1 | 3153240 | 4168440 | 1015200 | 1 |  | 1015200 | 1031151.1096 | Khilgaon |  |  |  | Salambagh | 1031151.1096 | 794065.0493 | 237086.0603 | 29.8573 | OK
10 | Titas Road | 11 |  |  | 1 | 2347080 | 2861160 | 514080 | 1 |  | 514080 | 522157.3704 | Khilgaon |  |  |  | Titas Road | 522157.3704 | 387724.9431 | 134432.4273 | 34.6721 | OK
11 | AT-1 | 0.415 |  | 7734 | 1 | 3332.3 | 3405 | 72.7 | 1 |  | 72.7 | 73.8423 | Banosree |  |  |  | AT-1 | 73.8423 | 76.0089 | -2.1666 | -2.8505 | OK
12 | AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15228323.0721 | 14992752.7 | 15228323.0721 | 1.5712
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 12929197.377
[5 empty] | Khilgaon | at 33 KV level |  | 2299125.6951
[5 empty] | Total = |  |  | 15228323.0721 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran | 33 | Export | SIEM0510 | 1 | 349987 | 354917 | 4930 | 2000 | 0 | 9860000 | 9864095.749
ULLON 33 KV SIDE
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 9860000 | 9864095.749
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import | HA-030701133-03 | 1 | 108926360 | 108926360 | 0 | 1 | 0
2 | Ullon O/H | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
[6 empty] | 0 | 0 |  | Total | 0 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| GORAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transformer-01 | 33 | Export | HA-030800176-03 | 1 | 15424360 | 18327416 | 2903056 | 1 |  | 2903056
2 | Transformer-02 | 33 | Export | HA-030701133-03 | 1 | 81116710 | 83967811 | 2851101 | 1 |  | 2851101
3 | Transformer-03 | 33 | Export | DHK-57075 | 1 | 11776.31 | 11947.18 | 170.87 | 120000 |  | 4105843 |  |  | Problem
[9 empty] | Total |  | 9860000
| 33 KV IMPORT |  | KWH |  | 33 KV IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 9864095.749 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9864095.749
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 9864095.749 |  | 33 KV TX HV SIDE |  | 9860000
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 4095.749
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.04152%
| TOTAL IMPORT |  | 9864095.749
11 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming | 11 | IMPORT |  | 1 | 56020760 | 58918038 | 2897278 | 1 | 2897278 |  | 2907020.6534
| 33/11 kV Transfomer-2 Incoming | 11 |  |  | 1 | 88643160 | 91487648 | 2844488 | 1 | 2844488 |  | 2854053.1369
| 33/11 kV Transfomer-3 Incoming | 11 |  |  | 1 | 71856420 | 75945691 | 4089271 | 1 | 4089271 |  | 4103021.9587
[6 empty] | 0 | 0 |  | Total | 9831037 |  | 9864095.749
| GORAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | Meradia | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | Meradia | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Shipahibagh | 11 |  | HA-021001030-02 | 1 | 37940830 | 39395508 | 1454678 | 1 |  | 1454678 | 1499139.6523 | Bashabo |  |  |  | Shipahibagh | 1499139.6523 | 1654071.9922 | -154932.3399 | -9.3667 | OK
3 | Farazi Hospital | 11 |  | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | Farazi Hospital | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | West Bansree | 11 |  | New Meter | 1 | 93104250 | 94964796 | 1860546 | 1 |  | 1860546 | 1917412.8456 | Banosree |  |  |  | West Bansree | 1917412.8456 | 1975561.8751 | -58149.0295 | -2.9434 | OK
5 | Model School(Nearest) | 11 |  | HA-030701099-03 | 1 | 17587620 | 19995869 | 2408249 | 1 |  | 2408249 | 2481856.1691 | Banosree |  |  |  | Model School(Nearest) | 2481856.1691 | 2525253.4223 | -43397.2531 | -1.7185 | OK
6 | Bhuiyan Para | 11 |  | HA-021100508-02 | 1 | 55705410 | 58016858 | 2311448 | 1 |  | 2311448 | 2382096.4852 | Banosree |  |  |  | Bhuiyan Para | 2382096.4852 | 2607870.9453 | -225774.46 | -8.6574 | OK
7 | Bonobithi (Ideal) School | 11 |  | HA-021100879-02 | 1 | 15718670 | 17216488 | 1497818 | 1 |  | 1497818 | 1543598.2091 | Banosree |  |  |  | Bonobithi (Ideal) School | 1543598.2091 | 1587554.1504 | -43955.9412 | -2.7688 | OK
8 | AT-01 | 0.415 |  | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 | 0.415 |  | 3043146 | 1 | 4782.5 | 4866.6 | 84.1 | 80 |  | 6728 | 6933.6386 | Banosree |  |  |  | AT-02 | 6933.6386 | 6257.2038 | 676.4348 | 10.8105 | OK
[9 empty] | Grand Total | 9831037 | 9539467 | 9831037 | 3.0565
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 8331897.3477
[5 empty] | Bashabo | at 33 KV level |  | 1499139.6523
[5 empty] | Total = |  |  | 9831037 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 | 33 | 0 | SICAM | 1 | 105.9 | 8040 | 7934.1 | 1000 | Estimated | 14660370 | 14268686.6539
[9 empty] | Total |  | 14660370 | 14268686.6539
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import |  | 1 |  |  | 0 |  | 0
2 | Shatmasjid-2 | 33 | Import |  | 1 |  |  | 0 |  | 0
3 | Kallayanpur | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
[9 empty] | Total | 0 | 0 | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 14268686.6539 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALMATIA 33 KV NET IMPORT |  | 14268686.6539
| IMPORT-2 |  |  |  | LALMATIA 33 KV NET IMPORT |  |  | 14268686.6539 |  | LALMATIA 11 KV NET IMPORT |  | 14660370
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -391683.3461
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -2.745%
| TOTAL IMPORT |  | 14268686.6539
11 KV SIDE of___LALMATIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | DHK000180 | 1 | 2789889 | 2865007 | 75118 | 90 | 6760620 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | DHK000177 | 1 | 2791019 | 2878794 | 87775 | 90 | 7899750 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 14660370 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1459594.08 | 1473463.6679 | Dhanmondi | Estimated | 165 |  | Shankor O/H | 1473463.6679 | 1695740.7049 | -222277.037 | -13.108 | OK
2 | Bangabobondhu museum | 11 | Export |  | 1 | 627449 | 627449 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 90 |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 80492544 | 82759173 | 2266629 | 1 |  | 2266629 | 2288167.324 | Dhanmondi |  | 75 |  | Road No-13/A | 2288167.324 | 2330507.8061 | -42340.4821 | -1.8168 | OK
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 978738 | 3352637 | 2373899 | 1 |  | 2373899 | 2396456.6421 | Dhanmondi |  | 25 |  | Jaforabad | 2396456.6421 | 1846222.5257 | 550234.1163 | 29.8032 | OK
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 115 |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25639.6 | 25827.6 | 188 | 3333.33 |  | 626666.04 | 632620.8461 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 632620.8461 | 655652.5794 | -23031.7333 | -3.5128 | OK
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 69712.4 | 70131.2 | 418.8 | 3333.33 |  | 1395998.604 | 1409263.8848 | Dhanmondi |  |  |  | Road No -15 | 1409263.8848 | 1205565.6057 | 203698.2792 | 16.8965 | OK
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 77687.3 | 78143.5 | 456.2 | 3333.33 |  | 1520665.146 | 1535115.0531 | Dhanmondi |  |  |  | Road No-27 South | 1535115.0531 | 1547367.0274 | -12251.9742 | -0.79179 | OK
| Road 25 | 11 | Export |  | 1 | 70235.1 | 70612.1 | 377 | 3333.3 |  | 1256654.1 | 1268595.2792 | Dhanmondi |  |  |  | Road 25 | 1268595.2792 | 1429491.6026 | -160896.3234 | -11.2555 | OK
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37836.9 | 37971.8 | 134.9 | 3333.33 |  | 449666.217 | 453939.1071 | Dhanmondi |  |  |  | Ibne Sina | 453939.1071 | 448887.9755 | 5051.1316 | 1.1253 | OK
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 60236116 | 61190386 | 954270 | 1 |  | 954270 | 963337.8167 | Dhanmondi |  |  |  | Road No-31 (PARI) | 963337.8167 | 1202715.5447 | -239377.7279 | -19.9031 | OK
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 69402203 | 71620534 | 2218331 | 1 |  | 2218331 | 2239410.379 | Dhanmondi |  |  |  | Satmoszid Road West | 2239410.379 | 2263478.6281 | -24068.2491 | -1.0633 | OK
[9 empty] | Grand Total | 14660370 | 14522373.187 | 14660370 | 0.95024
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Dhanmondi | at 33 KV level |  | 14660370
[5 empty] | Total = |  |  | 14660370 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2087.7 | 2116.15 | 28.45 | 240000 | 0 | 6828000 | 6830200.263
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1411.09 | 1442.33 | 31.24 | 240000 | 0 | 7497600 | 7500016.0357
[9 empty] | Total | 0 | 14325600 | 14330216.2987
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 | 33 |  |  | 1 | 0 | 0 | 0 | 3000
[9 empty] | Total | 0 | 0 | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory | 33 | EXPORT | [7 empty] | 0
| Green Road Dormatory | 33 | [8 empty] | 0
Total
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0 | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 14330216.2987 |  | EXPORT TO OTHER S/S |  |  | 0 |  | Green Road 33 KV NET IMPORT |  | 14330216.2987
| IMPORT-2 |  |  |  | Green Road 33 KV NET IMPORT |  |  | 14330216.2987 |  | Green Road 11 KV NET IMPORT |  | 14330216.2987
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 14330216.2987 |  | LOSS UNITS=> |  | 0
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 14330216.2987
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 00138 | 1 | 3023673 | 3105868 | 82195 | 100 | 8219500
2 | Transfomer-2 Incoming | 11 | Import | HA-021101496 | 1 | 3394.4208 | 4144.8028 | 750.382 | 10000 | 6828000
[6 empty] | 0 | 0 |  | Total | 15047500 |  | 14330216.2987
| Green Road 11 KV SIDE |  |  |  |  | 0 | 0 | [7 empty] | 134
1 | Lab aid/local RMU | 11 |  | 3C65883 | 1 | 59173 | 64063 | 4890 | 300 |  | 1467000 | 1482077.1317 | Paribag |  | 35 |  | Lab aid/local RMU | 1482077.1317 | 1556841.7376 | -74764.6059 | -4.8023 | OK
2 | Green View | 11 |  | DHK000151 | 1 | 67239.7 | 67603.9 | 364.2 | 3333.33 |  | 1213998.786 | 1226475.691 | Paribag |  | 99 |  | Green View | 1226475.691 | 1233531.7182 | -7056.0272 | -0.57202 | OK
3 | Central Road | 11 |  | 65943 | 1 | 21383 | 26887 | 5504 | 300 |  | 1651200 | 1668170.2521 | Paribag |  | 33 |  | Central Road | 1668170.2521 | 1747192.6716 | -79022.4195 | -4.5228 | OK
4 | New Market | 11 |  | DHK000194 | 1 | 46585.3 | 46951.6 | 366.3 | 3333.33 |  | 1220998.779 | 1233547.6266 | Jigatola |  | 68 |  | New Market | 1233547.6266 | 1104020.9274 | 129526.6992 | 11.7323 | OK
5 | DPH Feeder | 11 |  | HA-021100459 | 1 | 41611.3 | 41739.9 | 128.6 | 1 | 20 | 243265.68 | 245765.8495 | Paribag | Estimated |  |  | DPH Feeder | 245765.8495 | 244229.1636 | 1536.686 | 0.6292 | OK
6 | Dhanmondi Rd 4(md Banglo | 11 |  | 6604464 | 1 | 4502.72 | 4526.74 | 24.02 | 60000 |  | 1441200 | 1456011.9715 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1456011.9715 | 1566178.5714 | -110166.5999 | -7.0341 | OK
1 | Green Road East | 11 |  | HA-021101050 | 1 | 95327346 | 96835494 | 1508148 | 1 |  | 1508148 | 1523648.0314 | Paribag |  |  |  | Green Road East | 1523648.0314 | 1576340.6608 | -52692.6294 | -3.3427 | OK
2 | North Road | 11 |  | HA-021100884 | 1 | 80273857 | 81964658 | 1690801 | 1 |  | 1690801 | 1708178.2525 | Paribag |  |  |  | North Road | 1708178.2525 | 1755468.3191 | -47290.0666 | -2.6939 | OK
3 | Green road SS | 11 |  | DHK00135 | 1 | 18489919 | 19740764 | 1250845 | 1 |  | 1250845 | 1263700.5929 | Paribag |  |  |  | Green road SS | 1263700.5929 | 1250797.3933 | 12903.1997 | 1.0316 | OK
4 | Plane Moszid | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 85 | 1033879.14 | 1044504.8605 | Paribag | Estimated |  |  | Plane Moszid | 1044504.8605 | 976916.6543 | 67588.2062 | 6.9185 | OK
5 | Malancha | 11 |  | HA-021100953 | 1 | 33261839 | 34719938 | 1458099 | 1 |  | 1458099 | 1473084.6514 | Paribag |  |  |  | Malancha | 1473084.6514 | 1290839.3587 | 182245.2927 | 14.1184 | OK
| AT -1 |  |  |  |  | 22891 | 22891 |  | 1 |  | 5000 | 5051.3876 | Paribag |  |  |  | AT -1 | 5051.3876 | 5019.8031 | 31.5845 | 0.6292 | OK
[9 empty] | Grand Total | 14330216.2987 | 14184435.385 | 14330216.2987 | 1.0278
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 11640656.7006
[5 empty] | Jigatola | at 33 KV level |  | 2689559.5981
[5 empty] | Total = |  |  | 14330216.2987 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory | 33 | 0 | 76026305 | 1 | 8045.2 | 8069.92 | 24.72 | 180000 | Reading From G. Dormitory Side | 8868490 | 8888059.4768
[9 empty] | Total | 0 | 8868490 | 8888059.4768
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 | 33 | 0 | 0 | 1 | 23.42 | 23.76 | 0.34 | 360000 | 0 | 122400 | 122490.9226
9 | Green Road -2 | 33 | 0 | 0 | 1 | 37.21 | 50.73 | 13.52 | 360000 | 0 | 4867200 | 4870815.5103
[9 empty] | Total | 0 | 4989600 | 4993306.4329
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [9 empty] | 13858090 | 13881365.9098
1 | Mogbazar Grid | 33 | Import | BD 017064 | 1 | 33396.14 | 42264.63 | 8868.49 | 1000 | 8868490
2 | Green Road SS | 33 | Import | BD 017070 | 1 | 32911.2 | 32911.3 | 0.1 | 1000 | 100
3 | Jigatola Ckt-1 | 33 | Import |  | 1 | 8369.32 | 8490.31 | 120.99 | 1000 | 120990
NEW | Jigatola Ckt-2 | 33 |  |  | 1 | 13367.86 | 18226.6 | 4858.74 | 1000 | 4858740 |  |  |  | NEW FOUND
[6 empty] | 0 | 0 |  | Total | 13848320 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transformer-01 | 33 | Export | BD 017065 | 1 | 108288.53 | 108288.53 | 0 | 888.89 |  | 0
2 | Transformer-02 | 33 | Export | BD 017069 | 1 | 100094.22 | 105577.05 | 5482.83 | 888.89 |  | 4873632.7587
[9 empty] | Total |  | 4873632.7587 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 13881365.9098 |  | EXPORT TO OTHER S/S |  |  | 0 |  | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 13881365.9098
[5 empty] | GREEN ROAD DORMITORY 33 KV NET IMPORT |  |  | 13881365.9098 |  | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 13881365.9098
[5 empty] | TOTAL EXPORT |  |  | 13881365.9098 |  | LOSS UNITS=> |  | 0
[5 empty] | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 13881365.9098
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD 014050 | 1 | 81822.15 | 90802.1 | 8979.95 | 1000 | 8979950
2 | Transformer-02 Incoming | 11 | Import | BD 014059 | 1 | 76642.86 | 81484.56 | 4841.7 | 1000 | 4841700
[6 empty] | 0 | 0 |  | Total | 13821650 |  | 13881365.9098
| GREEN ROAD DORMITORY 11 KV SIDE |  |  |  |  | 0 | 0
1 | North Dhanmondi | 11 |  | BD 014039 | 1 | 22196.95 | 22423.12 | 226.17 | 2000 |  | 452340 | 454897.5939 | Paribag |  |  |  | North Dhanmondi | 454897.5939 | 484039.8994 | -29142.3055 | -6.0206 | OK
2 | Lake circus | 11 |  | BD 014047 | 1 | 35647.16 | 36603.22 | 956.06 | 2000 |  | 1912120 | 1922931.395 | Paribag |  |  |  | Lake circus | 1922931.395 | 2034236.8602 | -111305.4652 | -5.4716 | OK
3 | Bashir Uddin | 11 |  | BD 014037 | 1 | 14464.14 | 14837.5 | 373.36 | 2000 |  | 746720 | 750942.0597 | Paribag |  |  |  | Bashir Uddin | 750942.0597 | 792213.6477 | -41271.5879 | -5.2097 | OK
4 | Raza Bazar | 11 |  | BD 013939 | 1 | 21277.2 | 21926.2 | 649 | 2000 |  | 1298000 | 1305339.0743 | Shere b.nagar |  |  |  | Raza Bazar | 1305339.0743 | 1333290.6732 | -27951.599 | -2.0964 | OK
5 | Rasel Squar | 11 |  | BD 013970 | 1 | 32377.3 | 33320.15 | 942.85 | 2000 |  | 1885700 | 1896362.0126 | Shere b.nagar |  |  |  | Rasel Squar | 1896362.0126 | 1946515.3317 | -50153.3191 | -2.5766 | OK
6 | Bow Bazar | 11 |  | BD 013967 | 1 | 24214.38 | 24825.05 | 610.67 | 2000 |  | 1221340 | 1228245.6279 | Shere b.nagar |  |  |  | Bow Bazar | 1228245.6279 | 1315379.6859 | -87134.058 | -6.6243 | OK
7 | BRB Hospital | 11 |  | BD 014003 | 1 | 12842.2 | 13270.32 | 428.12 | 2000 |  | 856240 | 861081.3012 | Shere b.nagar |  |  |  | BRB Hospital | 861081.3012 | 841735.8151 | 19345.4861 | 2.2983 | OK
8 | Green Road North | 11 |  | BD 013969 | 1 | 15378.01 | 15977.85 | 599.84 | 2000 |  | 1199680 | 1206463.1592 | Paribag |  |  |  | Green Road North | 1206463.1592 | 1244662.5143 | -38199.3551 | -3.0691 | OK
1 | Water Bhaban | 11 |  | BD 014004 | 1 | 5081.77 | 5261.2 | 179.43 | 2000 |  | 358860 | 360889.0448 | Shere b.nagar |  |  |  | Water Bhaban | 360889.0448 | 369844.7631 | -8955.7183 | -2.4215 | OK
2 | Alamin Road | 11 |  | BD 014006 | 1 | 18531.9 | 18834.18 | 302.28 | 2000 |  | 604560 | 607978.2671 | Paribag |  |  |  | Alamin Road | 607978.2671 | 645158.196 | -37179.9289 | -5.7629 | OK
3 | Katal Bagan | 11 |  |  | 1 | 7743.31 | 8822.65 | 1079.34 | 2000 |  | 2158680 | 2170885.4799 | Paribag |  |  |  | Katal Bagan | 2170885.4799 | 2232426.2667 | -61540.7868 | -2.7567 | OK
4 | Eastern Pantho chaya | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan | 11 |  | BD 014005 | 1 | 5746.51 | 5906.28 | 159.77 | 2000 |  | 319540 | 321346.724 | Paribag |  |  |  | Kalabagan | 321346.724 | 343995.7229 | -22648.9989 | -6.5841 | OK
6 | Univer Hospital | 11 |  | BD 013963 | 1 | 885.22 | 1021.63 | 136.41 | 2000 |  | 272820 | 274362.5626 | Paribag |  |  |  | Univer Hospital | 274362.5626 | 281740.4351 | -7377.8725 | -2.6187 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 |  | BD 013971 | 1 | 9775.84 | 10034.2 | 258.36 | 2000 |  | 516720 | 519641.6074 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 519641.6074 | 508095.8262 | 11545.7813 | 2.2724 | OK
[9 empty] | Grand Total | 13881365.9098 | 13803320 | 13881365.9098 | 0.56541
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 8229448.8489
[5 empty] | Shere b.nagar | at 33 KV level |  | 5651917.0608
[5 empty] | Total = |  |  | 13881365.9098 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1564.8785 | 1597.0678 | 32.1893 | 240000 | 0 | 7725432 | 7730871.3347
2 | Taltala-2 | 33 |  | BD001837 | 1 | 2529.1788 | 2562.855 | 33.6762 | 240000 | 0 | 8082288 | 8087978.5904
[9 empty] | Total | 0 | 15807720 | 15818849.9251
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 | 0 | 0
| 33 KV Ullon-ckt-2 incoming | 33 |  |  | 1 |  |  | 0 | 1000 | 0 | 0
[9 empty] | Total | 0 | 0 | 15818849.9251
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) | 33 | EXPORT | [7 empty] | 0
| 33 KV Khilgaon Feeder(Import) | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
[9 empty] | Total |  | 0 | 15818849.9251 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 15818849.9251 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TALTOLA 33 KV NET IMPORT |  | 15818849.9251
| IMPORT-2 |  |  |  | TALTOLA 33 KV NET IMPORT |  |  | 15818849.9251 |  | TALTOLA 11 KV NET IMPORT |  | 15818849.9251
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 15818849.9251 |  | LOSS UNITS=> |  | 0
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 15818849.9251
11 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming | 11 | Import | 06604431 | 1 | 8555.67 | 8603.61 | 47.94 | 160000 | 7670400
2 | Transformer-02 Incoming | 11 | Import | 06604341 | 1 | 9269.53 | 9320.63 | 51.1 | 160000 | 8176000
3 | Transformer-03 Incoming | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
[6 empty] | 0 | 0 |  | Total | 15846400 |  | 15818849.9251
| TALTOLA 11 KV SIDE |  |  |  |  | 0 | 0
1 | Matir Masjid | 11 |  | DHK00170 | 1 | 22583.2 | 24920.8 | 2337.6 | 888.8889 |  | 2077866.6667 | 2085431.7227 | Khilgaon |  |  |  | Matir Masjid | 2085431.7227 | 2167154.5553 | -81722.8326 | -3.771 | OK
2 | Hajipara | 11 |  | DHK-00108 | 1 | 3643.3 | 4685.3 | 1042 | 2222.2222 |  | 2315555.5556 | 2323985.9847 | Khilgaon |  |  |  | Hajipara | 2323985.9847 | 2257545.6108 | 66440.3738 | 2.943 | OK
3 | Nearest Feeder | 11 |  | DHK-00106 | 1 | 90788.1 | 91084.5 | 296.4 | 2222.222 |  | 658666.6008 | 661064.6612 | Bashabo |  |  |  | Nearest Feeder | 661064.6612 | 0 | 661064.6612 | #DIV/0! | #DIV/0!
4 | Reazbagh | 11 |  | DHK-00109 | 1 | 95946.5 | 96741.7 | 795.2 | 2222.222 |  | 1767110.9344 | 1773544.5971 | Khilgaon |  |  |  | Reazbagh | 1773544.5971 | 1831021.0001 | -57476.4029 | -3.139 | OK
5 | Chowdhury Para | 11 |  | DHK-00107 | 1 | 52456 | 52718.7 | 262.7 | 2222.222 |  | 583777.7194 | 585903.1258 | Khilgaon |  |  |  | Chowdhury Para | 585903.1258 | 625509.6106 | -39606.4848 | -6.3319 | OK
6 | Model Colleg | 11 |  | 9122392 | 1 | 2506.21 | 2537.32 | 31.11 | 40000 |  | 1244400 | 1248930.587 | Khilgaon |  |  |  | Model Colleg | 1248930.587 | 1283320.9871 | -34390.4001 | -2.6798 | OK
1 | East Rampura | 11 |  | DHK-00181 | 1 | 98303.2 | 98770.2 | 467 | 2222.222 |  | 1037777.674 | 1041555.9945 | Khilgaon |  |  |  | East Rampura | 1041555.9945 | 1373711.9053 | -332155.9107 | -24.1794 | OK
2 | Adarshabagh | 11 |  | DHK-00090 | 1 | 49532.6 | 50492 | 959.4 | 2222.222 |  | 2131999.7868 | 2139761.9297 | Bashabo |  |  |  | Adarshabagh | 2139761.9297 | 2323799.4344 | -184037.5047 | -7.9197 | OK
3 | Khailgaon Govt Colony | 11 |  | DHK00167 | 1 | 75071.6 | 75784.9 | 713.3 | 2222.222 |  | 1585110.9526 | 1590881.9934 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1590881.9934 | 1651220.4486 | -60338.4553 | -3.6542 | OK
4 | TV Road | 11 |  | 6604434 | 1 | 5070.34 | 5102.73 | 32.39 | 40000 |  | 1295600 | 1300316.995 | Khilgaon |  |  |  | TV Road | 1300316.995 | 1457589.2313 | -157272.2363 | -10.7899 | OK
5 | Tilpa Para | 11 |  | 06604476 | 1 | 6562.81 | 6589.4 | 26.59 | 40000 |  | 1063600 | 1067472.334 | Bashabo |  |  |  | Tilpa Para | 1067472.334 | 544086.3384 | 523385.9955 | 96.1954 | FAULT
1 | Navana | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 | 0.415 |  | 9187958 | 1 | 288.03 | 288.03 | 0 | 80 |  | 0 | 0 | Bashabo |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | AT-02 | 0.415 |  | 9187959 | 1 | 123.08 | 123.08 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15818849.9251 | 15761465.8902 | 15818849.9251 | 0.36408
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Khilgaon | at 33 KV level |  | 11950551.0003
[5 empty] | Bashabo | at 33 KV level |  | 3868298.9248
[5 empty] | Total = |  |  | 15818849.9251 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 | 33 | Import | 35786569 | 1 | 1910.455 | 1934.95 | 24.495 | 180000 | 0 | 4409100 | 3357
2 | Sher-e-Banglanagar Ckt-02 | 33 | Import | 35786575 | 1 | 663.099 | 678.859 | 15.76 | 180000 | 0 | 2836800 | 2160
[9 empty] | Total | 0 | 7245900 | 5517
[9 empty] | Net Total | 7251417
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
[9 empty] | Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 | 33 | Export | DHK 66500 | 1 | 729434.44 | 745495 | 16060.56 | 180 |  | 2890900.8
[9 empty] | Total |  | 2890900.8 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 7251417 |  | EXPORT TO OTHER S/S |  |  | 0 |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 7251417
| IMPORT-2 |  |  |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  |  | 7251417 |  | 33 KV TX HV SIDE |  | 7251417
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7251417
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 66503 | 1 | 2183030 | 2208145 | 25115 | 180 | 4520700 |  | 4413944.2064
2 | Transfomer-2 Incoming | 11 | Import | DHK 66495 | 1 | 711772 | 727917 | 16145 | 180 | 2906100 |  | 2837472.7936
[6 empty] | 0 | 0 |  | Total | 7426800 |  | 7251417
| SHER-E-BANGLANAGAR 11 KV SIDE |  |  |  |  | 0 | 0
1 | Sher-e-Banglanagar Local | 11 |  | DHK 66503 | 1 | 78207 | 80683 | 2476 | 60 |  | 148560 | 145611.0642 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 145611.0642 | 127632.9783 | 17978.0859 | 14.0858 | OK
2 | Mirpur Road East | 11 |  | DHK 60961 | 1 | 825101 | 835227 | 10126 | 60 |  | 607560 | 595499.8531 | Shere b.nagar |  |  |  | Mirpur Road East | 595499.8531 | 565408.7832 | 30091.0699 | 5.322 | OK
3 | Gonobhaban school | 11 |  | DHK 66492 | 1 | 526229 | 529711 | 3482 | 60 |  | 208920 | 204772.9102 | Shere b.nagar |  |  |  | Gonobhaban school | 204772.9102 | 187053.4171 | 17719.4931 | 9.473 | OK
4 | Babor Road | 11 |  | DHK 66489 | 1 | 741733 | 755796 | 14063 | 60 |  | 843780 | 827030.8546 | Shyamoli |  |  |  | Babor Road | 827030.8546 | 821146.7988 | 5884.0558 | 0.71657 | OK
5 | College Gate | 11 |  | DHK 66487 | 1 | 2623105 | 2657171 | 34066 | 60 |  | 2043960 | 2003387.1217 | Shyamoli |  |  |  | College Gate | 2003387.1217 | 2118896.2632 | -115509.1415 | -5.4514 | OK
6 | Parade ground | 11 |  | DHK 66490 | 1 | 938265 | 938267 | 2 | 60 |  | 120 | 117.618 | Satmasjid |  |  |  | Parade ground | 117.618 | 1062.133 | -944.515 | -88.9262 | CHECK
7 | Hospital RMU | 11 |  | DHK 66491 | 1 | 893230 | 904485 | 11255 | 60 |  | 675300 | 661895.205 | Shere b.nagar |  |  |  | Hospital RMU | 661895.205 | 606359.9098 | 55535.2953 | 9.1588 | OK
1 | Shamoly Square | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | 11 |  | DHK 60964 | 1 | 192801.1 | 194454.7 | 1653.6 | 60 |  | 99216 | 97246.5492 | Shere b.nagar |  |  |  | Gonobhaban RMU | 97246.5492 | 98796.0682 | -1549.519 | -1.5684 | OK
3 | Krishi University | 11 |  | DHK 60963 | 1 | 350091.4 | 360437.8 | 10346.4 | 60 |  | 620784 | 608461.3549 | Shere b.nagar |  |  |  | Krishi University | 608461.3549 | 589560.5067 | 18900.8482 | 3.2059 | OK
4 | NEC | 11 |  | DHK 86073 | 1 | 34.66 | 39.37 | 4.71 | 60000 |  | 282600 | 276990.3524 | Shere b.nagar |  |  |  | NEC | 276990.3524 | 279104.941 | -2114.5886 | -0.75763 | OK
5 | Novo Theater/Army Musium | 11 |  | DHK 86074 | 1 | 362.71 | 381.55 | 18.84 | 60000 |  | 1130400 | 1107961.4094 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 1107961.4094 | 1197849.958 | -89888.5486 | -7.5042 | OK
6 | Netor | 11 |  | DHK 60962 | 1 | 114054.4 | 124560.4 | 10506 | 60 |  | 630360 | 617847.27 | Shere b.nagar |  |  |  | Netor | 617847.27 | 628517.1836 | -10669.9136 | -1.6976 | OK
7 | BICC | 11 |  |  | 1 | 34.66 | 39.37 | 4.71 | 60000 |  | 282600 | 276990.3524 | Shere b.nagar |  |  |  | BICC | 276990.3524 | 279104.941 | -2114.5886 | -0.75763 | OK
8 | Auxiliary | 0.415 |  |  | 1 | 5228.9 | 5279.71 | 50.81 | 60 |  | 3048.6 | 2988.0849 | Shere b.nagar |  |  |  | Auxiliary | 2988.0849 | 4296.3279 | -1308.243 | -30.4503 | OK
[9 empty] | Grand Total | 7426800 | 7577208.6 | 7426800 | -1.985
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 3942567.1741 | Including 41% of Novo Theatre
[5 empty] | Shyamoli | at 33 KV level |  | 2830417.9764
[5 empty] | Satmasjid | at 33 KV level |  | 117.618
[5 empty] | Tejgaon | at 33 KV level |  | 653697.2316 | 59% of Novo Theatre
[5 empty] | Total = |  |  | 7426800 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 8936192 | 9031697.5082
6 | 33kV Mugdapara Hospital-2 Feeder | 33 |  | ABB03918 | 1 | 297786 | 302279 | 4493 | 2000 | 0 | 8986000 | 9082037.8309
[9 empty] | Total | 0 | 17922192 | 18113735.3391
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 | 33 | Import | 38 | 1 | 290773248 | 299709440 | 8936192 | 1 | 8936192
2 | Maniknagor Incoming-02 | 33 | Import | 15 | 1 | 205869872 | 214806592 | 8936720 | 1 | 8936720
[6 empty] | 0 | 0 |  | Total | 17872912 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export | 16 | 1 | 279390240 | 288322080 | 8931840 | 1 |  | 8931840
4 | Transformer-02 | 33 | Export | 196 | 1 | 217124880 | 226062480 | 8937600 | 1 |  | 8937600
[9 empty] | Total |  | 17869440 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 18113735.3391 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18113735.3391
[5 empty] | 33 KV NET IMPORT |  |  | 18113735.3391 |  | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 17869440
[10 empty] | LOSS UNITS=> |  | 244295.3391
[10 empty] | LOSS % IN => |  | 1.349%
| TOTAL IMPORT |  | 18113735.3391
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | 192 | 1 | 277339136 | 286225728 | 8886592 | 1 | 8886592 |  | 9049332.1533
2 | Transformer-02 Incoming | 11 | Import | 118 | 1 | 215608912 | 224510304 | 8901392 | 1 | 8901392 |  | 9064403.1857
[6 empty] | 0 | 0 |  | Total | 17787984 |  | 18113735.3391
| MUGDAPARA HOSPITAL 11 KV SIDE |  |  |  |  | 0 | 0
1 | City Corporation | 11 |  | 93 | 1 | 40386420 | 41951856 | 1565436 | 1 |  | 1565436 | 1583920.0344 | Bashabo |  |  |  | City Corporation | 1583920.0344 | 672002.1574 | 911917.877 | 135.7016 | FAULT
2 | Bot tola | 11 |  |  | 1 | 53690908 | 56049584 | 2358676 | 1 |  | 2358676 | 2386526.2912 | Maniknagar |  |  |  | Bot tola | 2386526.2912 | 2395209.9678 | -8683.6766 | -0.36254 | OK
3 | Jhilpar | 11 |  | 145 | 1 | 34782876 | 35789952 | 1007076 | 1 |  | 1007076 | 1018967.1456 | Mugdapara |  |  |  | Jhilpar | 1018967.1456 | 1203846.2525 | -184879.1069 | -15.3574 | OK
4 | Central Bashaboo | 11 |  | 128 | 1 | 37782388 | 38835864 | 1053476 | 1 |  | 1053476 | 1065915.018 | Bashabo |  |  |  | Central Bashaboo | 1065915.018 | 2018436.7723 | -952521.7542 | -47.1911 | CHECK
5 | Kadamtala | 11 |  | 8 | 1.5 | 18572154 | 19006514 | 434360 | 1 |  | 651540 | 659233.1205 | Mugdapara |  |  |  | Kadamtala | 659233.1205 | 895857.2066 | -236624.0861 | -26.4131 | OK
6 | Ansar VDP | 11 |  | 119 | 1 | 19018394 | 19583192 | 564798 | 1 |  | 564798 | 571466.9061 | Khilgaon |  |  |  | Ansar VDP | 571466.9061 | 611327.4182 | -39860.5121 | -6.5203 | OK
7 | Mugda Hospital Express-01 | 11 |  |  | 1 | 5903745 | 6214345 | 310600 | 1 |  | 310600 | 314267.439 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 314267.439 | 307500.5637 | 6766.8753 | 2.2006 | OK
8 | Boro Masjid | 11 |  | 7 | 1.22 | 47940324 | 49075360 | 1135036 | 1 |  | 1384743.92 | 1401094.4155 | Mugdapara |  |  |  | Boro Masjid | 1401094.4155 | 1717015.7129 | -315921.2974 | -18.3994 | OK
1 | Anandodhara | 11 |  | 120 | 1 | 46909724 | 47889764 | 980040 | 1 |  | 980040 | 991611.9155 | Maniknagar |  |  |  | Anandodhara | 991611.9155 | 1008287.8477 | -16675.9322 | -1.6539 | OK
2 | Culvert | 11 |  | 117 | 1 | 38905824 | 40800540 | 1894716 | 1 |  | 1894716 | 1917088.0393 | Bashabo |  |  |  | Culvert | 1917088.0393 | 2175998.5274 | -258910.4881 | -11.8985 | OK
3 | Mugda Hospital Express-02 | 11 |  | 97 | 1 | 4845548 | 4845548 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | 11 |  | 98 | 1 | 26401136 | 27342334 | 941198 | 1 |  | 941198 | 952311.2849 | Bashabo |  |  |  | Jhor Pukur | 952311.2849 | 1695311.8425 | -743000.5576 | -43.8268 | CHECK
5 | T&T | 11 |  | 99 | 1 | 23345024 | 23934662 | 589638 | 1 |  | 589638 | 596600.2068 | Mugdapara |  |  |  | T&T | 596600.2068 | 721459.9725 | -124859.7657 | -17.3065 | OK
6 | Haider Ali | 11 |  | 9 | 1 | 67435952 | 69907712 | 2471760 | 1 |  | 2471760 | 2500945.5412 | Maniknagar |  |  |  | Haider Ali | 2500945.5412 | 2687168.9248 | -186223.3836 | -6.9301 | OK
| 11kv Tilpapara | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 2128574.7 | 2153708.0482 | Bashabo | 175 |  |  | 11kv Tilpapara | 2153708.0482 | 2169910.6664 | -16202.6183 | -0.7467
7 | AT-01 | 11 |  |  | 1 | 2964 | 3043 | 79 | 1 |  | 79 | 79.9328 | Mugdapara |  |  |  | AT-01 | 79.9328 | 89.8242 | -9.8914 | -11.012 | OK
8 | AT-02 | 11 |  |  | 1 | 17.34 | 17.34 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-02 | 0 | 0.34315 | -0.34315 | -100 | CHECK
[9 empty] | Grand Total | 18113735.3391 | 17902351.62 | 18113735.3391 | 1.1808
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bashabo | at 33 KV level |  | 7672942.4249
[5 empty] | Maniknagar | at 33 KV level |  | 5879083.7479
[5 empty] | Mugdapara | at 33 KV level |  | 3990242.2602
[5 empty] | Khilgaon | at 33 KV level |  | 571466.9061
[5 empty] | Total = |  |  | 18113735.3391 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon | 33 | Export | BD001895 | 1 | 62.0687 | 74.9348 | 12.8661 | 240000 | 0 | 3087864 | 3090038.1083
MANKNAGAR 33 KV SIDE
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 270635 | 272335 | 1700 | 2000 | 0 | 3400000 | 3436337.4833
[9 empty] | Total | 0 | 6487864 | 6526375.5916
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming | 33 |  |  | 1 | 56639 | 68088 | 11449 | 270 |  | 3091230
| 33 kV Maniknagor Incoming | 33 |  |  | 1.08 | 1007578 | 1007578 | 0 | 180 |  | 0
[6 empty] | 0 | 0 |  | Total |  | 3091230
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| KHILGOAN 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer -01 | 33 | Export | DHK60982 | 1 | 806720 | 823895 | 17175 | 180 |  | 3091500
4 | Transformer -02 | 33 | Export | DHK60947 | 1 | 757892 | 776585 | 18693 | 180 |  | 3364740
[9 empty] | Total |  | 6456240 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 6526375.5916 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 6456240
[5 empty] | 33 KV NET IMPORT |  |  | 6456240 |  | 33 KV TX HV SIDE |  | 6456240
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6526375.5916
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | DHK60927 | 1 | 807403 | 823983 | 16580 | 180 | 2984400 |  | 3052047.4211
2 | Transformer-02 Incoming | 11 | Import | DHK60928 | 1 | 916998 | 935491 | 18493 | 180 | 3328740 |  | 3404192.5789
[6 empty] | 0 | 0 |  | Total | 6313140 |  | 6456240
| KHILGOAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | Shantinagar s/s-1 | 11 |  | DHK60932 | 1 | 324830 | 343950 | 19120 | 60 |  | 1147200 | 1164408 | Rajarbag |  |  |  | Shantinagar s/s-1 | 1164408 | 2916346.3506 | -1751938.3506 | -60.0731 | CHECK
2 | Gulbagh | 11 |  | DHK60934 | 1 | 122528 | 140286 | 17758 | 60 |  | 1065480 | 1081462.2 | Rajarbag |  |  |  | Gulbagh | 1081462.2 | 329175.3109 | 752286.8891 | 228.5369 | FAULT
3 | Rampura BTV | 11 |  | DHK60933 | 1 | 14073 | 14073 | 0 | 60 |  | 0 | 0 | Khilgaon |  |  |  | Rampura BTV | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | West Shantibag | 11 |  | DHK60926 | 1 | 520515 | 535058 | 14543 | 60 |  | 872580 | 885668.7 | Rajarbag |  |  |  | West Shantibag | 885668.7 | 934072.7507 | -48404.0507 | -5.182 | OK
1 | East Malibagh | 11 |  | DHK60929 | 1 | 585478 | 605416 | 19938 | 60 |  | 1196280 | 1214224.2 | Rajarbag |  |  |  | East Malibagh | 1214224.2 | 1558104.7013 | -343880.5013 | -22.0704 | OK
2 | Police Line | 11 |  | DHK60930 | 1 | 565142 | 575003 | 9861 | 60 |  | 591660 | 600534.9 | Rajarbag |  |  |  | Police Line | 600534.9 | 624772.6414 | -24237.7414 | -3.8794 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 |  | DHK61017 | 1 | 192855 | 195323 | 2468 | 60 |  | 148080 | 150301.2 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 150301.2 | 152458.8445 | -2157.6445 | -1.4152 | OK
4 | Benjir Bagan | 11 |  | DHK60985 | 1 | 164032 | 167244 | 3212 | 60 |  | 192720 | 195610.8 | Rajarbag |  |  |  | Benjir Bagan | 195610.8 | 195480.6318 | 130.1682 | 0.066589 | OK
5 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 846900 | 859196 | 12296 | 60 |  | 737760 | 748826.4 | Switching |  |  |  | Shantinagar s/s-2 | 748826.4 | 735135.562 | 13690.838 | 1.8624 | OK
6 | AT-1 & AT-2 | 0.415 |  | ELIB 7374 | 1 | 1983.75 | 2093.26 | 109.51 | 60 |  | 6570.6 | 6669.159 | Rajarbag |  |  |  | AT-1 & AT-2 | 6669.159 | 7349.5039 | -680.3449 | -9.257 | OK
[9 empty] | Grand Total | 6047705.559 | 5958330.6 | 6047705.559 | 1.5
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Rajarbag | at 33 KV level |  | 5896383.269 | Including Switching
[5 empty] | Khilgaon | at 33 KV level |  | 0
[5 empty] | Moghbazar | at 33 KV level |  | 107474.29
[5 empty] | Kakrail | at 33 KV level |  | 43848
[5 empty] | Total = |  |  | 6047705.559 | 0
11 KV SIDE of___Santinagar Switching S/S | [13 empty] | Month August-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 846900 | 859196 | 12296 | 60 |  | 737760 | 748826.4 | 1.5
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 588674 | 597504.11 | Rajarbag
2 | 11 Fortune(MogBazar)-new | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 105886 | 107474.29 | Moghbazar
3 | Centerpoint-Kakrail | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 43200 | 43848 | Kakrail
[11 empty] | 737760 | 748826.4 | 1.5
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 | 33 | Import |  | 1 | 1061.83 | 1097.56 | 35.73 | 180000 | 0 | 6431400 | 4896
2 | Sherebangla to Monipuripara-2 | 33 | Import |  | 1 | 766.09 | 790.448 | 24.358 | 180000 | 0 | 4384440 | 3338
[9 empty] | Total | 0 | 10815840 | 8234
[9 empty] | Net Total | 10824074
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | BD017103 | 1 | 30067.25 | 35790.8 | 5723.55 | 1000 | 5723550
2 | Agargaon Ckt-02 | 33 | Import | BD017104 | 1 | 22470.96 | 26369.5 | 3898.54 | 1000 | 3898540
[6 empty] | 0 | 0 |  | Total | 9622090 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| MONIPURIPARA 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export | BD017102 | 1 | 91686.77 | 98142.5 | 6455.73 | 888.8889 |  | 5738426.7384
4 | Transformer-02 | 33 | Export | BD017105 | 1 | 38306.04 | 42707.08 | 4401.04 | 888.8889 |  | 3912035.6045
[6 empty] | 0 | 0 |  | Total |  | 9650462.3429 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 10824074 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10824074
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 10824074 |  | 33 KV TX HV SIDE |  | 9650462.3429
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 1173611.6571
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 10.84%
| TOTAL IMPORT |  | 10824074
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD014058 | 1 | 90991.47 | 97428.88 | 6437.41 | 1000 | 6437410 |  | 6442811.115
2 | Transformer -02 Incoming | 11 | Import | BD014062 | 1 | 37404.46 | 41782.05 | 4377.59 | 1000 | 4377590 |  | 4381262.885
[6 empty] | 0 | 0 |  | Total | 10815000 | 0 | 10824074
| MONIPURIPARA 11 KV SIDE |  |  |  |  | 0 | 0
1 | Spare | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | 11 |  | BD013947 | 1 | 30306.07 | 31132.65 | 826.58 | 1000 |  | 826580 | 830035.6978 | Shere b.nagar |  |  |  | Monipuripara west | 830035.6978 | 847623.509 | -17587.8112 | -2.075 | OK
3 | Biggan College | 11 |  | BD013949 | 1 | 18139.4 | 19012.35 | 872.95 | 1000 |  | 872950 | 876599.5577 | Kakrail |  |  |  | Biggan College | 876599.5577 | 835521.2072 | 41078.3505 | 4.9165 | OK
4 | Green Road South | 11 |  | BD013948 | 1 | 28643.32 | 29611.68 | 968.36 | 1000 |  | 968360 | 972408.44 | Shere b.nagar |  |  |  | Green Road South | 972408.44 | 975210.3173 | -2801.8773 | -0.28731 | OK
5 | BARC Building O/H | 11 |  | BD014010 | 1 | 12825.53 | 13424.05 | 598.52 | 1000 |  | 598520 | 601022.2433 | Shere b.nagar |  |  |  | BARC Building O/H | 601022.2433 | 634425.9824 | -33403.7391 | -5.2652 | OK
6 | Green Road North | 11 |  | BD014036 | 1 | 57019.83 | 58901.44 | 1881.61 | 1000 |  | 1881610 | 1889476.4806 | Shere b.nagar |  |  |  | Green Road North | 1889476.4806 | 1966221.9789 | -76745.4983 | -3.9032 | OK
7 | Chundrima Uddan | 11 |  | BD014035 | 1 | 29068.98 | 30066.87 | 997.89 | 1000 |  | 997890 | 1002061.8966 | Shere b.nagar |  |  |  | Chundrima Uddan | 1002061.8966 | 1070591.3324 | -68529.4358 | -6.4011 | OK
8 | RMU-1 Feeder | 11 |  | BD013940 | 1 | 283.07 | 545 | 261.93 | 1000 |  | 261930 | 263025.0554 | Shere b.nagar |  |  |  | RMU-1 Feeder | 263025.0554 | 137015.3458 | 126009.7096 | 91.9676 | FAULT
1 | Spare-03 | 11 |  | BD013946 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-03 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | 11 |  | BD013964 | 1 | 40221.55 | 40298.72 | 77.17 | 1000 |  | 77170 | 77492.626 | Kakrail |  |  |  | kawran Bazar North | 77492.626 | 79448.9981 | -1956.3721 | -2.4624 | OK
3 | NAM Bhanan RMU | 11 |  | BD013950 | 1 | 15281.88 | 16243.17 | 961.29 | 1000 |  | 961290 | 965308.8823 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 965308.8823 | 1005888.2452 | -40579.3629 | -4.0342 | OK
4 | Novo Theater | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | 11 |  | BD013962 | 1 | 37303.94 | 38123.77 | 819.83 | 1000 |  | 819830 | 823257.478 | Tejgaon |  |  |  | Monipuripara Nearest | 823257.478 | 844317.6909 | -21060.2129 | -2.4943 | OK
6 | Holy Cross | 11 |  | BD013965 | 1 | 36115.46 | 37352.96 | 1237.5 | 1000 |  | 1237500 | 1242673.6384 | Tejgaon |  |  |  | Holy Cross | 1242673.6384 | 1267377.9768 | -24704.3385 | -1.9492 | OK
7 | Honda Goli | 11 |  | BD014011 | 1 | 13245.54 | 14300.32 | 1054.78 | 1000 |  | 1054780 | 1059189.7376 | Tejgaon |  |  |  | Honda Goli | 1059189.7376 | 1074102.0051 | -14912.2675 | -1.3883 | OK
8 | Navy Quarter | 11 |  | BD013941 | 1 | 5132.94 | 5353.54 | 220.6 | 1000 |  | 220600 | 221522.2664 | Tejgaon |  |  |  | Navy Quarter | 221522.2664 | 200143.5254 | 21378.7409 | 10.6817 | OK
9 | AT-01 | 0.415 |  |  | 1 | 1913.87 | 1989.96 | 76.09 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 585.48 | 585.48 | 0 | 1 |  | 0 | 0 | Shere b.nagar |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10824074 | 10779010 | 10824074 | 0.41807
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 6523338.696
[5 empty] | Kakrail | at 33 KV level |  | 954092.1837
[5 empty] | Tejgaon | at 33 KV level |  | 3346643.1203
[5 empty] | Total = |  |  | 10824074 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 | 33 | 0 | 0 | 1.04 | 3858.6 | 3891.35 | 32.75 | 180000 | 0 | 6130800 | 6144328.4077
[9 empty] | Total | 0 | 6130800 | 6144328.4077
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 | 33 | Import |  | 1 | 26193.26 | 32313.42 | 6120.16 | 1000 | 6120160
[6 empty] | 0 | 0 |  | Total | 6120160 | 0 | 0
| Ispahani 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| Ispahani 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 | 33 | Export |  | 1 | 23804.91 | 30691.04 | 6886.13 | 888.8889 |  | 6121004.521
[9 empty] | Total |  | 6121004.521 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 6144328.4077 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 6144328.4077
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 6144328.4077 |  | 33 KV TX HV SIDE |  | 6121004.521
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 23323.8868
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3796%
| TOTAL IMPORT |  | 6144328.4077
11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming | 11 | Import |  | 1 | 6871.6 | 8879.59 | 2007.99 | 1000 | 6121004.521 |  | 6144328.4077 |  | From Upstream
[6 empty] | 0 | 0 |  | Total | 6121004.521 | 0 | 6144328.4077
| Ispahani 11 KV SIDE |  |  |  |  | 0 | 0
1 | Doctor Goli | 11 |  | BD013944 | 1 | 7728.79 | 8689.39 | 960.6 | 1000 |  | 960600 | 963950.8063 | Moghbazar |  |  |  | Doctor Goli | 963950.8063 | 948233.0953 | 15717.711 | 1.6576 | OK
2 | Ispahani | 11 |  | BD013947 | 1 | 8623.82 | 9707.76 | 1083.94 | 1000 |  | 1083940 | 1087721.0462 | Moghbazar |  |  |  | Ispahani | 1087721.0462 | 1055882.4039 | 31838.6423 | 3.0154 | OK
3 | BTCL | 11 |  | BD013949 | 1 | 4485.67 | 5033.71 | 548.04 | 1000 |  | 548040 | 549951.6967 | Kakrail |  |  |  | BTCL | 549951.6967 | 529591.2713 | 20360.4254 | 3.8446 | OK
4 | Vikarunnesa | 11 |  | BD013948 | 1 | 5237.35 | 6385.39 | 1148.04 | 1000 |  | 1148040 | 1152044.6426 | Kakrail |  |  |  | Vikarunnesa | 1152044.6426 | 1148347.0254 | 3697.6172 | 0.32199 | OK
5 | OASIS | 11 |  |  | 1 | 4.29 | 113.31 | 109.02 | 1000 |  | 109020 | 109400.2883 | Kakrail |  |  |  | OASIS | 109400.2883 | 4342.8205 | 105057.4677 | 2419.1068 | FAULT
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | 11 |  |  | 1 | 6771.63 | 7852.04 | 1080.41 | 1000 |  | 1080410 | 1084178.7327 | Moghbazar |  |  |  | Wireless | 1084178.7327 | 1047125.901 | 37052.8317 | 3.5385 | OK
2 | Kazir Goli | 11 |  |  | 1 | 6092.57 | 7285.49 | 1192.92 | 1000 |  | 1192920 | 1197081.1949 | Kakrail |  |  |  | Kazir Goli | 1197081.1949 | 1203659.779 | -6578.5841 | -0.54655 | OK
3 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 6144328.4077 | 6122970 | 6144328.4077 | 0.34882
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 3135850.5852
[5 empty] | Kakrail | at 33 KV level |  | 3008477.8225
[5 empty] | Total = |  |  | 6144328.4077 | 0

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 | 132 | IMPORT | 8993683 | 1 | 8336.501 | 8374.227 | 37.726 | 960000 | 0 | 36216960
| XFR- T2 | 132 |  | 8993682 | 1 | 8326.822 | 8364.206 | 37.384 | 960000 | 0 | 35888640
[9 empty] | Total | 0 | 72105600
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** | 132 | P. Cell | 08993685 | 1 | 8336.492 | 8374.219 | 37.727 | 960000 | 36217920
| 132/33 kV Transformer-2(HV) ** | 132 | P. Cell | 08993684 | 1 | 8326.819 | 8364.201 | 37.382 | 960000 | 35886720
[9 empty] | Total | 72104640
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 72105600 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 72105600
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 72105600 |  | 33 KV NET IMPORT |  | 72935040
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 72105600 |  | LOSS UNITS=>(132 HV-33 LV) |  | -829440
| IMPORT-4 |  |  |  | Loss Units=> (132 IMP-132 EXP) |  |  | 0 |  | LOSS % IN => |  | -1.15%
| 132 KV TOTAL IMPORT |  | 72105600 |  | 132 KV NET LOSS => |  |  | 0%
| 33 KV GT INCOMING-NOCS |  | 72935040
| Loss Units=> (132 IMP-33 IMP) |  | -829440
| LOSS % IN => |  | -1.15%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | IMPORT
3 | 132/33 kV Transformer, T-1 (LV) | 33 | PGCB | J2002016494 | 1 | 21858.207 | 22108.939 | 250.732 | 144000 | 36105408
4 | 132/33 kV Transformer, T-2 (LV) | 33 | PGCB | J2002016859 | 1 | 31835.056 | 32083.682 | 248.626 | 144000 | 35802144
| DPDC |  |  |  |  | 0 | 0 |  | Total | 71907552
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | DPDC | 07389553 | 1 | 1603.3 | 1679 | 75.7 | 480000 | 36336000
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | DPDC | 07389485 | 1.038 | 995.7 | 1064.66 | 68.96 | 480000 | 34358630.4
| P.Cell |  |  |  |  | 0 | 0 |  | Total | 70694630.4
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | P.Cell | 08993674 | 1 | 10868.572 | 10945.51 | 76.938 | 480000 | 36930240
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | P.Cell | 8993667 | 1 | 10777.96 | 10852.97 | 75.01 | 480000 | 36004800
[7 empty] | 0 |  | Total | 72935040
| SIDDHIRGANJ 33 kV SIDE | [5 empty] | 0
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 33 | DPDC | 07389555 | 1 | 5636.56 | 5665.7 | 29.14 | 240000 |  | 6993600 | 6964577.0654 |  | 14679626.7452 | Siddhirganj 33/11 kv ss | 0.57602 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 6964577.0654 | 7169668.8084 | -205091.743 | -2.8605 | OK
|  | 33 | P.Cell | 08993675 | 1 | 4993.2 | 5022.34 | 29.14 | 240000 |  | 6993600 | 6964577.0654 |  |  |  |  | 0 | 6964577.0654 | 7171110.9141 | -206533.8487 | -2.8801 | OK
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 33 | DPDC | 07389487 | 1 | 5808.12 | 5840.4 | 32.28 | 240000 |  | 7747200 | 7715049.6798 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 7715049.6798 | 7864283.0509 | -149233.3711 | -1.8976 | OK
|  | 33 | P.Cell | 08993666 | 1 | 5072.42 | 5104.63 | 32.21 | 240000 |  | 7730400 | 7698319.3986 |  |  |  |  | 0 | 7698319.3986 | 7885674.2854 | -187354.8868 | -2.3759 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 14740800 | 14679626.7452 |  |  |  |  | 33 KV Feeders | 14679626.7452 | 15033951.8593 | -354325.1141 | -2.3568 | OK
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4240.998 | 4283.98 | 42.982 | 240000 |  | 10315680 | 10272870.6734 |  | 18922426.061 | Sarulia 33/11 kv ss |  | 33 kV Sarulia-1 Feeder | 10272870.6734 | 10360087.3052 | -87216.6318 | -0.84185 | OK
|  | 33 | P.Cell | 08993679 | 1 | 4241.94 | 4284.814 | 42.874 | 240000 |  | 10289760 | 10247058.2395 |  |  |  |  | 0 | 10247058.2395 | 10390371.5248 | -143313.2853 | -1.3793 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss |  | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6133.76 | 6174.9 | 41.14 | 240000 |  | 9873600 | 9832625.2735 |  |  |  |  | 33 kV Demra-1 Feeder | 9832625.2735 | 9517897.58 | 314727.6935 | 3.3067 | OK
|  | 33 | P.Cell | 08993676 | 1 | 5779.4 | 5820.5 | 41.1 | 240000 |  | 9864000 | 9823065.1128 |  |  |  |  | 0 | 9823065.1128 | 9533520.3917 | 289544.7211 | 3.0371 | OK
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5632.25 | 5693.6 | 61.35 | 240000 |  | 14724000 | 14662896.4639 |  | 24495521.7374 | Demra 33/11 kv ss |  | 33 kV Demra-2 Feeder | 14662896.4639 | 14137442.8196 | 525453.6444 | 3.7168 | OK
|  | 33 | P.Cell | 08993665 | 1 | 5340.51 | 5399.818 | 59.308 | 240000 |  | 14233920 | 14174850.2605 |  |  |  |  | 0 | 14174850.2605 | 14140567.3819 | 34282.8786 | 0.24244 | OK
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4526.7 | 4547.07 | 20.37 | 240000 |  | 4888800 | 4868511.8333 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 4868511.8333 | 6352475.5818 | -1483963.7485 | -23.3604 | OK
|  | 33 | P.Cell | 08993678 | 1 | 3772.326 | 3792.75 | 20.424 | 240000 |  | 4901760 | 4881418.0502 |  |  |  |  | 0 | 4881418.0502 | 6339256.2796 | -1457838.2294 | -22.997 | OK
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3959.35 | 3995.54 | 36.19 | 240000 |  | 8685600 | 8649555.3876 |  |  |  |  | 33 kV Sarulia-2 Feeder | 8649555.3876 | 8931441.2645 | -281885.8768 | -3.1561 | OK
|  | 33 | P.Cell | 08993663 | 1 | 3680.325 | 3717.421 | 37.096 | 240000 |  | 8903040 | 8866093.0273 |  |  |  |  | 0 | 8866093.0273 | 8709837.6895 | 156255.3378 | 1.794 | OK
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 361720 | 366308.8 | 4588.8 | 2000 |  | 9177600 | 9139513.6232 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 9139513.6232 | 7905743.5896 | 1233770.0335 | 15.606 | OK
[9 empty] | Total | 72105600 | 72406080 | 72105600 | -0.41499
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 14008025.4564
[5 empty] | Total = |  |  | 14008025.4564 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | IMPORT
8 | 33/11 kV Transformer-1 Incoming | 11 | New | XA587379 | 1 | 679629.3 | 686280.9 | 6651.6 | 1000 | 6651600 |  | 6812461.1218
9 | 33/11 kV Transformer-2 Incoming | 11 | New | DHKA9985 | 1 | 308134.3 | 315815.7 | 7681.4 | 1000 | 7681400 |  | 7867165.6234
[6 empty] | 0 | 0 |  | Total | 14333000 |  | 14679626.7452
| SIDDHIRGANJ 11 kV SIDE |  | EXPORT |  |  | 0 | 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 213015.1 | 215487.3 | 2472.2 | 1000 |  | 2472200 | 2486440.3485 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 2486440.3485 | 2725888.0748 | -239447.7263 | -8.7842 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16876.9 | 17004 | 127.1 | 1000 |  | 127100 | 127832.1205 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 127832.1205 | 148265.7961 | -20433.6756 | -13.7818 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 108320.7 | 109803.3 | 1482.6 | 1000 |  | 1482600 | 1491140.0618 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1491140.0618 | 1611243.3589 | -120103.2971 | -7.4541 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 169879.3 | 172372.4 | 2493.1 | 1000 |  | 2493100 | 2507460.7365 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2507460.7365 | 2663481.8388 | -156021.1022 | -5.8578 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 7001.5 | 7069.4 | 67.9 | 1000 |  | 67900 | 68291.1171 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 68291.1171 | 54248.5581 | 14042.559 | 25.8856 | OK
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 74651.5 | 76031.2 | 1379.7 | 1000 |  | 1379700 | 1387647.3379 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1387647.3379 | 1431264.5899 | -43617.252 | -3.0475 | OK
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 146439.6 | 148801 | 2361.4 | 1000 |  | 2361400 | 2375002.1192 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 2375002.1192 | 2446793.5192 | -71791.4 | -2.9341 | OK
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 79.1918 | 87.4121 | 8.2203 | 40000 |  | 328812 | 330706.0205 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 330706.0205 | 314747.6869 | 15958.3336 | 5.0702 | OK
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 14255.5 | 14944 | 688.5 | 1000 |  | 688500 | 692465.8927 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 692465.8927 | 722974.2051 | -30508.3124 | -4.2198 | OK
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 146418.5 | 149268.1 | 2849.6 | 1000 |  | 2849600 | 2866014.2453 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2866014.2453 | 2915044.2314 | -49029.9862 | -1.682 | OK
[9 empty] | Total | 14333000 | 14250912 | 14333000 | 0.57602
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 14002293.9795
[5 empty] | Matuail | at 33 KV level |  | 330706.0205
[5 empty] | Total = |  |  | 14333000 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6133.76 | 6174.9 | 41.14 | 240000 | 0 | 9873600 | 9832625.2735
0 | 0 | 33 | P.Cell | 08993676 | 1 | 5779.4 | 5820.5 | 41.1 | 240000 | 0 | 9864000 | 9823065.1128
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5632.25 | 5693.6 | 61.35 | 240000 | 0 | 14724000 | 14662896.4639
0 | 0 | 33 | P.Cell | 08993665 | 1 | 5340.51 | 5399.818 | 59.308 | 240000 | 0 | 14233920 | 14174850.2605
[9 empty] | Total | 0 | 24597600 | 24495521.7374
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 | 33 | Digital | DHK60885 | 3 | 318358.5 | 345870.6 | 27512.1 | 240 | 19808712
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
[6 empty] | 0 | 0 |  | Total | 19808712 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1011.11 | 1013.16 | 2.05 | 240000 |  | 492000 |  | Siddirgonj
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 492000
[6 empty] | 0 | 0
| DEMRA 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60886 | 1 | 733035 | 787420.6 | 54385.6 | 240 |  | 13052544
8 | 33/11 kV, 10/14 MVA T-2 (HV) | 33 | Digital | 05002303 | 1 | 0 | 0 |  | 240 |  | 0
9 | 33/11 kV, 20/28 MVA T-3 (HV) | 33 |  |  | 1 | 0 | 0 |  | 180 |  | 0
[9 empty] | Total |  | 13052544 | 0
[5 empty] | 33 KV Export-Import |  |  | KWH
[5 empty] | Total Import |  |  | 24495521.7374
[5 empty] | Siddirgonj NOCS |  |  | 492000
[5 empty] | Net Import to Demra 33/11 KV SS |  |  | 24003521.7374
11 KV SIDE of___DEMRA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.09.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK60881 | 1 | 282440.7 | 349470.8 | 67030.1 | 180 | 12065418 |  | 13484590.9002
19 | 33/11 kV, 20/28 MVA T-3 Incoming. | 11 |  | DHK60925 | 1 | 701308.6 | 753596.8 | 52288.2 | 180 | 9411876 |  | 10518930.8372
[6 empty] | 0 | 0 |  | Total | 21477294 |  | 24003521.7374
| DEMRA 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 |  | HA021101013-02 | 1 | 46067484 | 48556720 | 2489236 | 1 |  | 2489236 | 2482601.3667 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2482601.3667 | 2346002.1943 | 136599.1724 | 5.8226 | OK
12 | 11 kV DND (WASA) Feeder. | 11 |  | HA021100992-02 | 1 | 5613260 | 5963540 | 350280 | 1 |  | 350280 | 349346.3885 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 349346.3885 | 251256.153 | 98090.2355 | 39.0399 | OK
13 | 11 kV Local Feeder | 11 |  | HA021100794-02 | 1 | 9848922 | 11042260 | 1193338 | 1 |  | 1193338 | 1190157.3614 | Siddirgonj |  |  |  | 11 kV Local Feeder | 1190157.3614 | 1182388.6301 | 7768.7313 | 0.65704 | OK
14 | 11 kV Mouchak Feeder | 11 |  | DHK60888 | 1 | 893731.2 | 934490.7 | 40759.5 | 60 |  | 2445570 | 2439051.751 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2439051.751 | 2339275.7144 | 99776.0366 | 4.2653 | OK
15 | 11 kV Overhead-1 Feeder | 11 |  | HA021100829-02 | 1 | 78137143 | 78628660 | 491517 | 1 |  | 491517 | 490206.9454 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 490206.9454 | 1190489.8427 | -700282.8973 | -58.8231 | CHECK
16 | 11 kV Provati Steel Feeder | 11 |  | DHK60874 | 1 | 546973.2 | 581989.2 | 35016 | 60 |  | 2100960 | 2095360.2501 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 2095360.2501 | 124835.9443 | 1970524.3058 | 1578.4911 | FAULT
17 | 11 kV Islambagh Feeder. | 11 |  | DHKA2190 | 1 | 1048.5044 | 1099.163 | 50.6586 | 60000 |  | 3039516 | 3031414.6894 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 3031414.6894 | 2979112.0563 | 52302.6331 | 1.7556 | OK
20 | 11 kV Taj Jute Feeder. | 11 |  | DHK61062 | 1 | 613805.1 | 622580.6 | 8775.5 | 60 |  | 526530 | 525126.6242 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 525126.6242 | 1404410.5059 | -879283.8817 | -62.6088 | CHECK
21 | 11 kV Al-Aksa Steel Feeder | 11 |  | DHK61061 | 1 | 758979.9 | 787050.2 | 28070.3 | 60 |  | 1684218 | 1679729.0047 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1679729.0047 | 1595509.5853 | 84219.4194 | 5.2785 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 |  | DHKA2189 | 1 | 986.7258 | 1031.247 | 44.5212 | 60000 |  | 2671272 | 2664152.1809 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2664152.1809 | 2514049.716 | 150102.4649 | 5.9705 | OK
23 | 11 kV Over Head Feeder-2. | 11 |  | HA021100488-02 | 1 | 26957261 | 29160410 | 2203149 | 1 |  | 2203149 | 2197276.8827 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 2197276.8827 | 2204224.8423 | -6947.9595 | -0.31521 | OK
24 | 11 kV Shimrail Express Feeder. | 11 |  | HA021100511-02 | 1 | 8169444 | 8222669 | 53225 | 1 |  | 53225 | 53083.1379 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 53083.1379 | 75076.7556 | -21993.6177 | -29.2948 | OK
25 | 11 kV Sarder & Khadem Steel Feeder | 11 |  | HA021100413-02 | 1 | 80731969 | 81142180 | 410211 | 1 |  | 410211 | 409117.6527 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 409117.6527 | 331227.7744 | 77889.8783 | 23.5155 | OK
26 | 11 kV Siddhirgonj Mazar Feeder | 11 |  | HA021100393-02 | 1 | 23396.457 | 23713.14 | 316.683 | 1000 | Second Swtichgear Consumption Added | 1217452 | 1214207.0897 | Siddirgonj | Double Switchgear |  |  | 11 kV Siddhirgonj Mazar Feeder | 1214207.0897 | 1262090.4156 | -47883.3259 | -3.794 | OK
27 | 11 kV AST Beverage Feeder | 11 |  |  | 1 | 21373122 | 22265980 | 892858 | 1 |  | 892858 | 890478.2395 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 890478.2395 | 1164572.2996 | -274094.0601 | -23.536 | OK
28 | 11 kV Karim Market Feeder | 11 |  |  | 1 | 56008.912 | 58307.25 | 2298.338 | 1000 |  | 2298338 | 2292212.1727 | Matuail | OMF Corrected |  |  | 11 kV Karim Market Feeder | 2292212.1727 | 2119617.9699 | 172594.2028 | 8.1427 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 24003521.7374 | 24067670 | 24003521.7374 | -0.26653
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 7806228.2288
[5 empty] | Demra | at 33 KV level |  | 2606394.5354
[5 empty] | Siddirgonj | at 33 KV level |  | 13590898.9732
[5 empty] | Total = |  |  | 24003521.7374 | 0
| Calculation for Second Switchgear |  |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh
[6 empty] | Reading at 00.00hr 01.09.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.)
26 | 11 kV Siddhirgonj Mazar Feeder | 11 |  |  | 1 | 46789725 | 47690494 | 900769 | 1 | 900769
33 KV SIDE of___ SARULIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4240.998 | 4283.98 | 42.982 | 240000 | 0 | 10315680 | 10272870.6734
0 | 0 | 33 | P.Cell | 08993679 | 1 | 4241.94 | 4284.814 | 42.874 | 240000 | 0 | 10289760 | 10247058.2395
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3959.35 | 3995.54 | 36.19 | 240000 | 0 | 8685600 | 8649555.3876
| 0 | 33 | P.Cell | 08993663 | 1 | 3680.325 | 3717.421 | 37.096 | 240000 | 0 | 8903040 | 8866093.0273
[9 empty] | Total | 0 | 18975360 | 18896613.6271
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) | 33 |  | 30799103 | 1 | 4334.6 | 4370.29 | 35.69 | 240000 | 8565600
7 | 33 kV Siddhirgonj-1 Incoming (=L41) | 33 |  | 30799100 | 1 | 4261.05 | 4303.03 | 41.98 | 240000 | 10075200
[6 empty] | 0 | 0 |  | Total | 18640800 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| SARULIA 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33/11 kV Transformer-1 (=T31) | 33 |  | 30799099 | 1 | 4647.76 | 4695.01 | 47.25 | 180000 |  | 8505000
5 | 33/11 kV Transformer-2 (=T32) | 33 |  | 30799139 | 1 | 4020.32 | 4047.87 | 27.55 | 180000 |  | 4959000
6 | 33/11 kV Transformer-3 (=T33) | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 13464000 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 18896613.6271 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18896613.6271
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 18896613.6271 |  | 33 KV NET Receiving |  | 18640800
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 18896613.6271 |  | LOSS UNITS=> |  | 255813.6271
| IMPORT-4 |  |  |  | 132KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 1.354%
| TOTAL IMPORT |  | 18896613.6271
11 KV SIDE of___SARULIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) | 11 |  | 2007754972 | 1 | 9304.21 | 9357.31 | 53.1 | 160000 | 8496000 |  | 9106873.0359
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) | 11 |  | 30799500 | 1 | 8801.51 | 8850.1 | 48.59 | 80000 | 3887200 |  | 4166694.5463
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) | 11 |  | HA021100368-02 | 1 | 43617132 | 48862994 | 5245862 | 1 | 5245862 |  | 5623046.045
[6 empty] | 0 | 0 |  | Total | 17629062 |  | 18896613.6271
| SARULIA 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV Dayagonj Feeder (=L11) | 11 |  | 2007755114 | 1 | 5767.7 | 5809.87 | 42.17 | 60000 |  | 2530200 | 2567812.3685 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 2567812.3685 | 2674737.7934 | -106925.4249 | -3.9976 | OK
9 | 11 kV Karim Jute Feeder (=L12) | 11 |  | 30799484 | 1 | 21.3509 | 21.5916 | 0.2407 | 60000 |  | 14442 | 14656.6857 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 14656.6857 | 14157.8637 | 498.822 | 3.5233 | OK
11 | 11 kV Konapara (=L13) **** | 11 |  | DHKA2191 | 1 | 2064.619 | 2121.1009 | 56.4819 | 60000 |  | 3388914 | 3439291.4731 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 3439291.4731 | 3588042.0557 | -148750.5827 | -4.1457 | OK
12 | 11 kV Sanarpar Feeder (=L14) | 11 |  | 575926 | 1 | 51041.5 | 53570.6 | 2529.1 | 1000 |  | 2529100 | 2566696.0166 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2566696.0166 | 2627544.9143 | -60848.8977 | -2.3158 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | 11 |  | 30799450 | 1 | 1809.19 | 1814.55 | 5.36 | 60000 |  | 321600 | 326380.7042 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 326380.7042 | 261798.4288 | 64582.2754 | 24.6687 | OK
14 | 11 kV Tengra Feeder (=L16) | 11 |  | 30799145 | 1 | 5472.12 | 5519.55 | 47.43 | 60000 |  | 2845800 | 2888103.8805 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 2888103.8805 | 2785803.7935 | 102300.0869 | 3.6722 | OK
16 | 11 kV Police Line Feeder (=L17) | 11 |  | 30799480 | 1 | 3317.32 | 3337.55 | 20.23 | 60000 |  | 1213800 | 1231843.5906 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1231843.5906 | 1213792.7153 | 18050.8753 | 1.4871 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | 11 |  | 30799119 | 1 | 1639.93 | 1648.7 | 8.77 | 60000 |  | 526200 | 534022.1596 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 534022.1596 | 561432.5279 | -27410.3683 | -4.8822 | OK
18 | 11 kV Spare Feeder (=F9) | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | 11 |  | HA021100493-02 | 1 | 80604576 | 83621868 | 3017292 | 1 |  | 3017292 | 3062145.1731 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 3062145.1731 | 3047117.0714 | 15028.1018 | 0.49319 | OK
21 | 11 kV Baser Pool Feeder (=L11) | 11 |  | HA021100518-02 | 1 | 50869565 | 50869565 | 0 | 1 |  | 0 | 0 | Demra | No Reading in Grid |  |  | 11 kV Baser Pool Feeder (=L11) | 0 | 1592.7597 | -1592.7597 | -100 | CHECK
22 | 11 kV Dip-Pur Feeder (=L12) | 11 |  | HA021100697-02 | 1 | 22773043 | 25005518 | 2232475 | 1 |  | 2232475 | 2265661.5752 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 2265661.5752 | 2324189.2905 | -58527.7153 | -2.5182 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 18896613.6271 | 18619823 | 18896613.6271 | 1.4865
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Demra | at 33 KV level |  | 16329917.6105
[5 empty] | Matuail | at 33 KV level |  | 2566696.0166
[5 empty] | Total = |  |  | 18896613.6271 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 10966.771 | 20100.879 | 9134.108 | 1000 | 0 | 9134108 | 9139975.0859
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 404.5926 | 438.668 | 34.0754 | 240000 | 0 | 8178096 | 8183349.0134
| Siddhirganj 33 KV SIDE | [7 empty] | Total |  | 17312204 | 17323324.0992
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) | 33 |  | 84663042 | 1 | 411.99 | 446.09 | 34.1 | 240000 | 8184000
6 | 33 kV Shitalakhya-2 Feeder (Old) | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 8178096 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
[6 empty] | 0 | 0 |  | Total | 16362096 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
11 | 33 kV ACI Pharmacuticles Feeder | 33 |  | DHKC4791 | 1 | 900.2 | 913.82 | 13.62 | 90000 |  | 1225800 |  | N.Gonj (East)
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 1225800
[6 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  |  |  |  | 0 | 0
9 | 33/11 kV, 20/28 MVA T1 Transformer | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer | 33 |  | DHKC 9361 | 1 | 40559.36 | 40559.36 | 0 | 240 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 15136296 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 17323324.0992 |  | EXPORT TO N.Gonj (East) |  |  | 1225800 |  | 33 KV NET IMPORT |  | 16097524.0992
| SIDDIRGANJ 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 16097524.0992 |  | 33 KV TX HV SIDE |  | 15136296
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 961228.0992
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 5.971%
| TOTAL IMPORT |  | 17323324.0992
11 KV SIDE of___KHANPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. | 11 |  | DHKC 9313 | 1 | 21545963.56 | 25867132.73 | 4321169.17 | 1 | 4321169.17 |  | 4254456.9089
18 | 33/11 kV Transformer-2 Incoming. | 11 |  | DHKC 9346 | 1 | 42701376.1 | 46601349.2 | 3899973.1 | 1 | 3899973.1 |  | 3839763.4638
24 | 33/11 kV 20/28 MVA T4 Incoming | 11 |  | 06604325 | 1 | 119.84 | 141.32 | 21.48 | 240000 | 5155200 |  | 5075611.575
30 | 33/11 kV 20/28 MVA T1 Incoming | 11 |  | 06604374 | 1 | 64.94 | 77.33 | 12.39 | 240000 | 2973600 |  | 2927692.1515
[6 empty] | 0 | 0 |  | Total | 16349942.27 |  | 16097524.0992
| KHANPUR 11 KV SIDE |  |  |  |  | 0 | 0
12 | 11 kV Khanpur Feeder | 11 |  | DHKC 9348 | 1 | 47198.82 | 76101.38 | 28902.56 | 60 |  | 1734153.6 | 1753296.6737 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1753296.6737 | 1849730.4598 | -96433.786 | -5.2134 | OK
13 | 11 kV Mission Para Feeder. | 11 |  | DHKC 9347 | 1 | 32560.85 | 59807.26 | 27246.41 | 60 |  | 1634784.6 | 1652830.7535 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1652830.7535 | 1736094.2229 | -83263.4694 | -4.796 | OK
14 | 11 kV Esha Kha Feeder | 11 |  | DHKC 9311 | 1 | 79951.21 | 95916.86 | 15965.65 | 60 |  | 957939 | 968513.5517 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 968513.5517 | 939733.5453 | 28780.0064 | 3.0626 | OK
15 | 11 kV New Hazigonj Feeder | 11 |  | DHKC 9314 | 1 | 170.34 | 205.54 | 35.2 | 60000 |  | 2112000 | 2135314.0661 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 2135314.0661 | 2193735.673 | -58421.6068 | -2.6631 | OK
16 | 11 kV Spare Feeder. | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | 11 |  | 6604412 | 1 | 4.9 | 5.95 | 1.05 | 60000 |  | 63000 | 63695.448 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 63695.448 | 65004.0756 | -1308.6276 | -2.0131 | OK
20 | 11 kV Old Hajiganj Feeder. | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | 11 |  | 06604389 | 1 | 6245.25 | 27741.38 | 21496.13 | 60 |  | 1289767.8 | 1304005.3624 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 1304005.3624 | 1304824.3795 | -819.0171 | -0.062768 | OK
22 | 11 kV Spare Feeder. | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | 11 |  | 6604415 | 1 | 234.81 | 282.18 | 47.37 | 40000 |  | 1894800 | 1915716.4264 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1915716.4264 | 1976042.8964 | -60326.47 | -3.0529 | OK
26 | 11 kV Mondalpara Feeder. | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | 11 |  | 06604392 | 1 | 183.1 | 220.31 | 37.21 | 40000 |  | 1488400 | 1504830.2349 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1504830.2349 | 1509066.5776 | -4236.3427 | -0.28073 | OK
28 | 11 kV Bishaw Road Feeder. | 11 |  | 06604393 | 1 | 221.32 | 251.26 | 29.94 | 40000 |  | 1197600 | 1210820.1352 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 1210820.1352 | 1222724.6371 | -11904.5018 | -0.9736 | OK
29 | 11 kV Chasara Feeder. | 11 |  | 06604391 | 1 | 258.76 | 310.22 | 51.46 | 40000 |  | 2058400 | 2081122.3834 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 2081122.3834 | 2195963.227 | -114840.8436 | -5.2296 | OK
31 | 11 kV Pathan Tully Feeder. | 11 |  | 06604388 | 1 | 33.69 | 37.66 | 3.97 | 40000 |  | 158800 | 160552.9705 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 160552.9705 | 39690.9621 | 120862.0085 | 304.5076 | FAULT
32 | 11 kV Spare Feeder. | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | 11 |  | 6604289 | 1 | 169.17 | 202.39 | 33.22 | 40000 |  | 1328800 | 1343468.4333 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1343468.4333 | 1193968.9401 | 149499.4932 | 12.5212 | OK
34 | 11 kV Spare Feeder. | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 |  | 412109 | 1 | 9113.7 | 9145.8 | 32.1 | 10 |  | 321 | 324.5435 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 324.5435 | 42.526 | 282.0174 | 663.1643 | FAULT
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 |  | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 |  | 3000 | 3033.1166 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3033.1166 | 3037.5736 | -4.4571 | -0.14673 | OK
[9 empty] | Grand Total | 16097524.0992 | 15921766 | 16097524.0992 | 1.1039
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3996838.8098
[5 empty] | N.Gonj (East) | at 33 KV level |  | 12100685.2894
[5 empty] | Total = |  |  | 16097524.0992 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail | 132 | Impt | 8993555 | 1 | 2779.681 | 2809.435 | 29.754 | 1440000 | 0 | 42845760
|  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar | 132 | Impt |  | 1 |  |  | 0 |  | 0 | 0
|  | 132 | Expt |  | 1 |  |  | 0 |  | 0
[8 empty] | Total Import/Export |  | 0 | 42845760
[9 empty] | Net Total | 42845760
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder | 132 | Impt |  | 1 |  | 0 | 0 | 1 | 0
|  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  | 132 | Expt |  | 1 | 8832614 | 8835117 | 2503 | 1 | 2503
|  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder | 132 | Impt | HA040700237-03 | 1 | 35292309 | 35292309 | 0 | 1
|  | 132 |  | 06604364 | 1 | 6080.18 | 6094.19 | 14.01 | 960000 | 13449600
|  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 13452103 | 0
[6 empty] | 0 | 0 | Net Total |  | 13452103
| MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| MOGBAZAR 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 KV Transformer, GT-1 | 132 | DPDC | H/A040700240-03 | 1 | 118600.357 | 118600.357 | 0 | 1000 |  | 0
|  | 132 | P. Cell | 08993572 | 1 | 4948.74 | 4992.987 | 44.247 | 480000 |  | 21238560
5 | 132/33 KV Transformer, GT-2 | 132 | DPDC | H/A030700918-03 | 1 | 98510.075 | 119767.126 | 21257.051 | 1000 |  | 21257051
|  | 132 | P. Cell | 08993577 | 1 | 5010.41 | 5054.684 | 44.274 | 480000 |  | 21251520
[9 empty] | Total |  | 21257051
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 42845760 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 42845760
| 132 KV Sending From Maniknagar |  | 0 |  | 132 KV NET IMPORT |  |  | 42845760 |  | 132/33 KV GT LV Side |  | 42548828
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 296932
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.693%
| 132 KV TOTAL IMPORT |  | 42845760
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 29290.486 | 50633.758 | 21343.272 | 1000 | 21343272
|  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 50075.431 | 71280.987 | 21205.556 | 1000 | 21205556
|  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
[6 empty] | 0 | 0 |  | Total | 42548828 |  | 0
| MATUAIL 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 | 33 | DPDC | H/A060300287-03 | 1.45 | 57612.348 | 65454.666 | 7842.318 | 1000 |  | 11371361.1 | 11397537.3557 |  | 19726546.2482 | Matuail 33/11 kv ss | 0.74837 | 33/11 KV Transformer, T-3 | 11397537.3557 | 10183781.0075 | 1213756.3482 | 11.9185 | OK
|  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 | 33 | DPDC | H/A060300190-03 | 1 | 53987.849 | 62306.499 | 8318.65 | 1000 |  | 8318650 | 8337799.0806 |  |  |  |  | 33/11 KV Transformer, T-4 | 8337799.0806 | 8121899.086 | 215899.9945 | 2.6582 | OK
|  | 33 | P. Cell | 08993581 | 1 | 6204.089 | 6250.255 | 46.166 | 180000 |  | 8309880 | 8329008.8925 |  |  |  |  | 0 | 8329008.8925 | 8112839.4765 | 216169.416 | 2.6645 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 19681241.1 | 19726546.2482 |  |  |  |  | 33 KV Feeders | 19726546.2482 | 18296620.4841 | 1429925.7642 | 7.8152 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 239520 | 7526400 | 7286880 | 1 |  | 7286880 | 7303654.0021 |  | 16845408.1568 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 7303654.0021 | 6911058.2476 | 392595.7545 | 5.6807 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.257 | 0.006 | 1000 |  | 9 | 9.0207 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 9.0207 | 0 | 9.0207 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC |  | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 9099 | 9119.9454 | Matuail |  |  |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 9119.9454 | 10440.0638 | -1320.1184 | -12.6447 | OK
|  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 9.0207 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 63937.809 | 69594.69 | 5656.881 | 1000 |  | 5656881 | 5669902.8329 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 5669902.8329 | 4053093.5487 | 1616809.2842 | 39.8907 | OK
|  | 33 | P. Cell | 08993580 | 1.5 | 1345.024 | 1366.01 | 20.986 | 180000 |  | 5666220 | 5679263.3307 |  |  |  |  | 0 | 5679263.3307 | 4070022.7555 | 1609240.5752 | 39.5389 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 5669902.8329 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 | DPDC | 00000154 | 1 | 877920 | 10397760 | 9519840 | 1 |  | 9519840 | 9541754.1547 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 9541754.1547 | 9089475.6559 | 452278.4988 | 4.9758 | OK
[9 empty] | Total |  | 22472709 | 22524439.9558 |  |  |  |  | 0 | 22524439.9558 | 20064067.5159 | 2460372.4398 | 12.2626 | OK
[8 empty] | Grand Total |  | 42250986.204 | 42153950.1 | 42250986.204 | 0.23019
[5 empty] | 33 KV EXPORT |  |  | KWH
[5 empty] | EXPORT TO Matuail |  |  | 9119.9454
[5 empty] | Total Export |  |  | 9119.9454 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426631 | 1 | 7534732 | 7663124 | 128392 | 90 | 11555280 |  | 11517019.1982
11 | 33/11 kV Transformer, T-4 Incoming | 11 |  | 51426633 | 1 | 7204409 | 7295929 | 91520 | 90 | 8236800 |  | 8209527.0501
[6 empty] | 0 | 0 |  | Total | 19792080 |  | 19726546.2482
| MATUAIL 11 kV SIDE |  |  |  |  | 0 | 0
3 | 11 kV Link Road Feeder | 11 | Backup | DHK66629 | 1 | 23573.72 | 23943.96 | 370.24 | 8000 |  | 2961920 | 2984086.1691 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 2984086.1691 | 2613745.6256 | 370340.5436 | 14.169 | OK
|  | 11 |  | HA021100475-02 | 1 | 88158.496 | 91112.32 | 2953.824 | 1000 |  | 2953824 | 2975929.581 | N.Gonj (East) |  |  |  | 0 | 2975929.581 | 2607402.2302 | 368527.3507 | 14.1339 | OK
4 | 11 kV Lamapara Express Feeder | 11 |  | HA021100928-03 | 1 | 77285.778 | 78379.26 | 1093.482 | 1000 |  | 1093482 | 1101665.3091 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1101665.3091 | 726895.7131 | 374769.5961 | 51.5575 | FAULT
5 | 11 kV Kutubpur Feeder*** | 11 |  | DHK66616 | 1 | 17710.59 | 17905.31 | 194.72 | 8000 |  | 1557760 | 1569417.834 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1569417.834 | 1641482.3695 | -72064.5355 | -4.3902 | OK
|  | 11 | Backup | XA575929 | 1 | 40597.4 | 42153.8 | 1556.4 | 1000 |  | 1556400 | 1568047.6561 | N.Gonj (East) |  |  |  | 0 | 1568047.6561 | 1639602.9947 | -71555.3385 | -4.3642 | OK
6 | 11 kV Ramarbagh Feeder (F1) | 11 |  | DHK66625 | 1 | 3508.42 | 3533.8 | 25.38 | 60000 |  | 1522800 | 1534196.2033 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1534196.2033 | 1364062.3916 | 170133.8117 | 12.4726 | OK
|  | 11 | Backup |  | 1 | 8395.82 | 8395.82 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Tushardhara Feeder (F2) | 11 |  | DHK66623 | 1 | 3791.19 | 3837.99 | 46.8 | 60000 |  | 2808000 | 2829014.2755 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2829014.2755 | 2689931.0362 | 139083.2393 | 5.1705 | OK
8 | 11 kV Matuail Medical Feeder (F3) | 11 |  | DHK66627 | 1 | 3284.92 | 3301.78 | 16.86 | 60000 |  | 1011600 | 1019170.5275 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 1019170.5275 | 792368.687 | 226801.8404 | 28.6233 | OK
|  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | 11 |  | HA021101044-02 | 1 | 65554.037 | 65883.888 | 329.851 | 1000 |  | 329851 | 332319.5113 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 332319.5113 | 349545.5347 | -17226.0234 | -4.9281 | OK
12 | 11 kV Shibu Market Feeder (F7) | 11 |  | DHK66624 | 1 | 2368.99 | 2377.51 | 8.52 | 60000 |  | 511200 | 515025.6758 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 515025.6758 | 398306.2183 | 116719.4575 | 29.304 | OK
13 | 11 kV Soma-Sagar Steel (F6) | 11 |  | HA060300286-03 | 1 | 961.358 | 2257.503 | 1296.145 | 1000 | 959253 | 1486842.15 | 1497969.2549 | Fatullah | 20 days converted to 31 days |  |  | 11 kV Soma-Sagar Steel (F6) | 1497969.2549 | 1502329.9696 | -4360.7147 | -0.29026 | OK
14 | 11 kV Jhalkuri Feeder (F8) | 11 |  | DHK66626 | 1 | 4378.18 | 4421.83 | 43.65 | 60000 |  | 2619000 | 2638599.8531 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2638599.8531 | 2625668.5413 | 12931.3118 | 0.4925 | OK
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK6622 | 1 | 4189.27 | 4211.82 | 22.55 | 60000 |  | 1353000 | 1363125.4682 | Matuail |  |  |  | 0 | 1363125.4682 | 1274337.3987 | 88788.0695 | 6.9674 | OK
16 | 11 kV Rajmahal Feeder (F10) | 11 |  | DHKA2187 | 1 | 112.4599 | 116.4856 | 4.0257 | 60000 |  | 241542 | 243349.6318 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 243349.6318 | 240620.6059 | 2729.0259 | 1.1342 | OK
17 | 11 kV Bhuighor Bazar | 11 |  | HA021100861-02 | 1 | 75324.363 | 75817.099 | 492.736 | 1000 | Estimated | 1277144.82 | 1286702.6096 | Matuail | 105 |  |  | 11 kV Bhuighor Bazar | 1286702.6096 | 1290448.3093 | -3745.6997 | -0.29026 | OK
18 | 11 kV Tokkar Math Feeder | 11 |  | HA021200298-02 | 1 | 80274.518 | 81065.983 | 791.465 | 1000 |  | 791465 | 797388.0996 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 797388.0996 | 771061.022 | 26327.0775 | 3.4144 | OK
19 | 11 kV Osmani Stadium Feeder***** | 11 |  | XA575922 | 1 | 193.1 | 202.9 | 9.8 | 1000 |  | 9800 | 9873.3404 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 9873.3404 | 9194.7909 | 678.5495 | 7.3797 | OK
16 | 33/0.415 KV Transformer, AT-1 | 0.415 |  | 2001123043119 | 1 | 7351.2 | 7430.6 | 79.4 | 160 |  | 12704 | 12799.0731 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 12799.0731 | 12965.6656 | -166.5925 | -1.2849 | OK
17 | 33/0.415 KV Transformer, AT-2 | 0.415 |  | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 |  | 0 | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 19726546.2482 | 19580014.97 | 19726546.2482 | 0.74837
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 5647012.7241
[5 empty] | Shyampur | at 33 KV level |  | 256148.7049
[5 empty] | Fatullah | at 33 KV level |  | 4354452.574
[5 empty] | Matuail | at 33 KV level |  | 9468932.2452
[5 empty] | Total = |  |  | 19726546.2482 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 239520 | 7526400 | 7286880 | 1 | 0 | 7286880 | 7303654.0021
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 |  | 00000154 | 1 | 877920 | 10397760 | 9519840 | 1 | 0 | 9519840 | 9541754.1547
[9 empty] | Total | 0 | 16806720 | 16845408.1568
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder | 33 |  | 00000079 | 1 | 328295968 | 337720320 | 9424352 | 1 | 9424352
7 | 33 kV Matuail-1 Feeder | 33 |  | 00000114 | 1 | 268405376 | 275637856 | 7232480 | 1 | 7232480
[6 empty] | 0 | 0 |  | Total | 16656832 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000075 | 1 | 343010400 | 352436640 | 9426240 | 1 |  | 9426240
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000156 | 1 | 253757760 | 260989920 | 7232160 | 1 |  | 7232160
[9 empty] | Total |  | 16658400
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 16845408.1568 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 16845408.1568
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 16845408.1568 |  | 33 KV TX HV Side |  | 16658400
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 187008.1568
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.11%
| TOTAL IMPORT |  | 16845408.1568
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming | 11 |  | 00000144 | 1 | 341752352 | 351151360 | 9399008 | 1 | 9399008 |  | 9534164.1128
18 | 11 kV T-1 Incoming | 11 |  | 00000054 | 1 | 252191728 | 259399328 | 7207600 | 1 | 7207600 |  | 7311244.044
[6 empty] | 0 | 0 |  | Total | 16606608 |  | 16845408.1568
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Godnail (F16) | 11 |  | 00000109 | 1 | 24749340 | 26744174 | 1994834 | 1 |  | 1994834 | 2022169.7421 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 2022169.7421 | 1902174.2906 | 119995.4515 | 6.3083 | OK
2 | 11 kV M. Circus (F15) | 11 |  | 00000123 | 1 | 107396816 | 109200376 | 1803560 | 1 |  | 1803560 | 1828274.6635 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1828274.6635 | 1936785.1498 | -108510.4864 | -5.6026 | OK
3 | 11 kV Wapderpool (F14) | 11 |  | 00000190 | 1 | 56271624 | 57082820 | 811196 | 1 |  | 811196 | 822312.035 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 822312.035 | 474935.0147 | 347377.0203 | 73.142 | FAULT
4 | 11 kV Chowdhury Bari (F13) | 11 |  | 00000191 | 1 | 98646920 | 100811032 | 2164112 | 1 |  | 2164112 | 2193767.4037 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2193767.4037 | 2204031.0267 | -10263.623 | -0.46568 | OK
5 | 11 kV Ailpara (F12) | 1 |  | 00000192 | 1 | 51494196 | 54123108 | 2628912 | 1 |  | 2628912 | 2664936.682 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2664936.682 | 2385423.2662 | 279513.4158 | 11.7176 | OK
6 | 11 kV Spare (F11) | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | 11 |  | 00000197 | 1 | 15359563 | 16611599 | 1252036 | 1 |  | 1252036 | 1269192.9831 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1269192.9831 | 1109871.8066 | 159321.1764 | 14.3549 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 |  | 00000198 | 1 | 4078510 | 4123870 | 45360 | 1 |  | 45360 | 45981.5802 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 45981.5802 | 80821.2927 | -34839.7125 | -43.1071 | CHECK
12 | 11 kV Lucky Bazar (F5) | 11 |  | 00000199 | 1 | 88391024 | 89732904 | 1341880 | 1 |  | 1341880 | 1360268.1394 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1360268.1394 | 1265880.4844 | 94387.655 | 7.4563 | OK
13 | 11 kV Enayetnagar (F4) | 11 |  | 00000200 | 1 | 30771724 | 32415400 | 1643676 | 1 |  | 1643676 | 1666199.7304 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1666199.7304 | 1606948.7378 | 59250.9926 | 3.6872 | OK
14 | 11 kV Bhuiyapara (F3) | 11 |  | 00000201 | 1 | 64028044 | 65898400 | 1870356 | 1 |  | 1870356 | 1895985.9869 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1895985.9869 | 1703398.6781 | 192587.3088 | 11.3061 | OK
15 | 11 kV Arambagh (F2) | 11 |  | 00000202 | 1 | 7963900.5 | 9021578 | 1057677.5 | 1 |  | 1057677.5 | 1072171.1368 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 1072171.1368 | 1011302.9055 | 60868.2312 | 6.0188 | OK
16 | 11 kV Spare (F1) | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 |  | 00000204 | 1 | 1627.32 | 1668.24 | 40.92 | 100 |  | 4092 | 4148.0738 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 4148.0738 | 5028.3475 | -880.2737 | -17.5062 | OK
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 |  | 00000205 | 1 | 60.72 | 60.72 | 0 | 100 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0 | 0.99927 | -0.99927 | -100 | CHECK
[9 empty] | Grand Total | 16845408.1568 | 16617691.5 | 16845408.1568 | 1.3703
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 7798092.3106
[5 empty] | Siddirgonj | at 33 KV level |  | 9047315.8462
[5 empty] | Total = |  |  | 16845408.1568 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.257 | 0.006 | 1000 | 0 | 9 | 9.0207
0 | 0 | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side | [7 empty] | Total | 0 | 9 | 9.0207
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 685.41 | 713.83 | 28.42 | 360000 | 0 | 10231200 | 10235169.9609
0 | 0 | 33 | Backup | 041808904262 | 1 | 685.39 | 713.84 | 28.45 | 360000 | 0 | 10242000 | 10245974.1516
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 483.44 | 498.39 | 14.95 | 360000 | 0 | 5382000 | 5384088.3503
0 | 0 | 33 | Backup | 041808904258 | 1 | 483.26 | 498.58 | 15.32 | 360000 | 0 | 5515200 | 5517340.0352
[9 empty] | Total | 0 | 15613200 | 15619258.3112
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) | 33 | Digital | DHK60875 | 1 | 231451.9 | 273739.1 | 42287.2 | 240 | 10148928
9 | 33 kV New Fatulla-2 | 33 | Digital | DHK2186 | 1 | 327.6931 | 342.7352 | 15.0421 | 360000 | 5415156
[6 empty] | 0 | 0 |  | Total | 15564084 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  |  |  |  | 0 | 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60980 | 1 | 923239.5 | 951686.1 | 28446.6 | 240 |  | 6827184
13 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 | Digital | DHK60952 | 1 | 505636.6 | 519402.2 | 13765.6 | 240 |  | 10148928 |  |  | Meter Problem
[9 empty] | Total |  | 16976112 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 9.0207 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 15619267.3319
| New Fatullah 33 kv Side |  | 15619258.3112 |  | 33 KV Net Import |  |  | 15619267.3319 |  | 33 KV TX HV Side |  | 16976112
[10 empty] | LOSS UNITS=> |  | -1356844.6681
[10 empty] | LOSS % IN => |  | -8.687%
| TOTAL IMPORT |  | 15619267.3319
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 | New | DHK61060 | 1 | 108195.6 | 143716.1 | 35520.5 | 180 | 6393690 |  | 6608840.7619 | [7 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 | New | DHK61054 | 1 | 392742.5 | 411084.2 | 18341.7 | 180 | 3301506 |  | 3412603.2742 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming | 11 | New | DHK60924 | 1.1 | 465543.4 | 473074.3 | 7530.9 | 180 | 1491118.2 |  | 1541295.0489 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming | 11 | New | DHK61051 | 1 | 902378.2 | 945983.4 | 43605.2 | 90 | 3924468 |  | 4056528.2469 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[6 empty] | 0 | 0 |  | Total | 15110782.2 |  | 15619267.3319 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE |  |  |  |  | 0 | 0 | [12 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | 11 | New |  | 1 | 75456997 | 76153634 | 696637 | 1 |  | 696637 | 690626.9008 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 690626.9008 | 493276.6302 | 197350.2707 | 40.008 | FAULT
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 87945628 | 88750830 | 805202 | 1 |  | 805202 | 798255.2776 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 798255.2776 | 675313.5877 | 122941.6898 | 18.2051 | OK
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 129693.5 | 158494.1 | 28800.6 | 60 |  | 1728036 | 1713127.7082 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1713127.7082 | 1429973.3518 | 283154.3564 | 19.8014 | OK
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 308379.7 | 325173.2 | 16793.5 | 60 |  | 1007610 | 998917.0422 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 998917.0422 | 983661.4804 | 15255.5619 | 1.5509 | OK
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 976902.1 | 1003887.3 | 26985.2 | 60 |  | 1619112 | 1605143.4286 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1605143.4286 | 2269442.86 | -664299.4313 | -29.2715 | OK
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 59040.7 | 69754.4 | 10713.7 | 60 |  | 642822 | 637276.1792 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 637276.1792 | 646164.6825 | -8888.5033 | -1.3756 | OK
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 616341.5 | 631131.1 | 14789.6 | 60 |  | 887376 | 879720.3375 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 879720.3375 | 817413.76 | 62306.5775 | 7.6224 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 504567.7 | 523460.2 | 18892.5 | 60 |  | 1133550 | 1123770.5196 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1123770.5196 | 1043132.595 | 80637.9246 | 7.7304 | OK
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 864279.2 | 868890.3 | 4611.1 | 60 |  | 276666 | 274279.1183 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 274279.1183 | 230613.5281 | 43665.5902 | 18.9345 | OK
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 514317.3 | 531239.4 | 16922.1 | 60 |  | 1015326 | 1006566.474 | Fatullah |  |  |  | 11 kV Dhaka Steel | 1006566.474 | 739323.8488 | 267242.6251 | 36.1469 | OK
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 229225 | 1035040 | 805815 | 1 |  | 805815 | 798862.9891 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 798862.9891 | 731731.9387 | 67131.0503 | 9.1743 | OK
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24889601 | 25218670 | 329069 | 1 |  | 329069 | 326230.0217 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 326230.0217 | 318326.9039 | 7903.1178 | 2.4827 | OK
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 15173750 | 15526910 | 353160 | 1 |  | 353160 | 350113.1813 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 350113.1813 | 373857.3757 | -23744.1944 | -6.3511 | OK
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 13842626 | 15928564 | 2085938 | 1 |  | 2085938 | 2067941.9788 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 2067941.9788 | 1957359.7515 | 110582.2273 | 5.6496 | OK
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 4587115 | 6443078 | 1855963 | 1 |  | 1855963 | 1839951.043 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1839951.043 | 1845653.8856 | -5702.8426 | -0.30899 | OK
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15110782.2 | 15242282 | 15110782.2 | -0.86273
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 12146693.8295
[5 empty] | N.Gonj (West) | at 33 KV level |  | 1488882.1784
[5 empty] | Sytalakhya | at 33 KV level |  | 1475206.1921
[5 empty] | Total = |  |  | 15110782.2 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder | 132 | Export | 041808902770 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904227 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902770 | 1 | 187.67 | 204.38 | 16.71 | 1200000 | 20052000
|  | 132 |  | 041808904227 | 1 | 187.64 | 204.39 | 16.75 | 1200000 | 20100000
3 | 132 kV Haripur Feeder | 132 | Export | 041808902766 | 1 | 52.36 | 52.36 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904230 | 1 | 52.38 | 52.38 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902766 | 1 | 719.42 | 719.42 | 0 | 1200000 | 0
|  | 132 |  | 041808904230 | 1 | 719.67 | 719.67 | 0 | 1200000 | 0
4 | 132 kV Aggreko Feeder | 132 | Export | 041808902768 | 1 | 30.52 | 30.52 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904219 | 1 | 30.52 | 30.52 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902768 | 1 | 257.68 | 257.68 | 0 | 1200000 | 0
|  | 132 |  | 041808904219 | 1 | 257.68 | 257.68 | 0 | 1200000 | 0
6 | 132 kV Shyampur-2 Feeder | 132 | Export | 041808902793 | 1 | 120.72 | 120.72 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904278 | 1 | 120.73 | 120.73 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902793 | 1 | 179.32 | 196.13 | 16.81 | 1200000 | 20172000
|  | 132 |  | 041808904278 | 1 | 179.36 | 196.2 | 16.84 | 1200000 | 20208000
[6 empty] | 0 | 0 | Total Import/Export |  | 40224000 | 0
[6 empty] | 0 | 0 |  | Net Total | 40224000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 0 | 0
[6 empty] | 0 | 0 | Net Total |  | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| FATULLAH 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV, 80/120 MVA GT-1 | 132 | Export | 041808902767 | 1 | 575.53 | 594.51 | 18.98 | 1200000 |  | 22776000
|  | 132 | Export | 041808904228 | 1 | 575.38 | 594.37 | 18.99 | 1200000 |  | 22788000
5 | 132/33 kV, 80/120 MVA GT-2 | 132 | Export | 041808902792 | 1 | 441.17 | 455.73 | 14.56 | 1200000 |  | 17472000
|  | 132 | Export | 041808904251 | 1 | 441 | 455.54 | 14.54 | 1200000 |  | 17448000
[9 empty] | Total |  | 40248000
| 132 KV IMPORT |  | KWH | [6 empty] | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 40224000 | [6 empty] | 132 KV NET IMPORT |  | 40224000
| IMPORT-2 | [8 empty] | 132/33 KV GT LV Side |  | 40219200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 4800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.01193%
| 132 KV TOTAL IMPORT |  | 40224000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902796 | 1 | 954.68 | 986.18 | 31.5 | 720000 | 22680000
|  | 33 | Backup | 041808904255 | 1 | 954.68 | 986.18 | 31.5 | 720000 | 22680000
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902802 | 1 | 731.9 | 756.26 | 24.36 | 720000 | 17539200
|  | 33 | Backup | 041808904281 | 1 | 732.09 | 756.08 | 23.99 | 720000 | 17272800
[6 empty] | 0 | 0 |  | Total | 40219200 |  | 0
| FATULLAH 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902868 | 1 | 755.4 | 782.49 | 27.09 | 240000 |  | 6501600 | 6504122.783 |  | 12686520.7772 | New Fatullah 33/11 kv ss | 1.4646 | 33/11 kV, 28/35 MVA T-1 (=H5) | 6504122.783 | 5781367.7419 | 722755.0411 | 12.5015 | OK
|  | 33 | Backup | 041808904277 | 1 | 755.88 | 782.89 | 27.01 | 240000 |  | 6482400 | 6484915.333 |  |  |  |  | 0 | 6484915.333 | 6004188.7946 | 480726.5384 | 8.0065 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902824 | 1 | 660.38 | 686.13 | 25.75 | 240000 |  | 6180000 | 6182397.9942 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 6182397.9942 | 5958666.2139 | 223731.7803 | 3.7547 | OK
|  | 33 | Backup | 041808904267 | 1 | 660.48 | 686.03 | 25.55 | 240000 |  | 6132000 | 6134379.369 |  |  |  |  | 0 | 6134379.369 | 6006584.7199 | 127794.6491 | 2.1276 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 12681600 | 12686520.7772 |  |  |  |  | 33 KV Feeders | 12686520.7772 | 11740033.9559 | 946486.8214 | 8.062 | OK
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 746.6 | 763.86 | 17.26 | 360000 |  | 6213600 | 6216011.0318 |  | 11913420.9116 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 6216011.0318 | 6059295.0764 | 156715.9554 | 2.5864 | OK
|  | 33 | Backup | 041808904220 | 1 | 746.97 | 763.47 | 16.5 | 360000 |  | 5940000 | 5942304.8682 |  |  |  |  | 0 | 5942304.8682 | 6325242.7844 | -382937.9162 | -6.0541 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 685.41 | 713.83 | 28.42 | 360000 |  | 10231200 | 10235169.9609 |  | 15619258.3112 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 10235169.9609 | 9160820.3735 | 1074349.5874 | 11.7277 | OK
|  | 33 | Backup | 041808904262 | 1 | 685.39 | 713.84 | 28.45 | 360000 |  | 10242000 | 10245974.1516 |  |  |  |  | 0 | 10245974.1516 | 9146444.8217 | 1099529.3298 | 12.0214 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 516.32 | 532.14 | 15.82 | 360000 |  | 5695200 | 5697409.8797 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 5697409.8797 | 5042224.7878 | 655185.0919 | 12.994 | OK
|  | 33 | Backup | 041808904219 | 1 | 516.01 | 532.46 | 16.45 | 360000 |  | 5922000 | 5924297.8838 |  |  |  |  | 0 | 5924297.8838 | 4822997.6231 | 1101300.2607 | 22.8344 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 483.44 | 498.39 | 14.95 | 360000 |  | 5382000 | 5384088.3503 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 5384088.3503 | 5394425.8065 | -10337.4562 | -0.19163 | OK
|  | 33 | Backup | 041808904258 | 1 | 483.26 | 498.58 | 15.32 | 360000 |  | 5515200 | 5517340.0352 |  |  |  |  | 0 | 5517340.0352 | 5265045.8404 | 252294.1948 | 4.7919 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 27522000 | 27532679.2228 |  |  |  |  | 0 | 27532679.2228 | 25656766.0441 | 1875913.1786 | 7.3116 | OK
[8 empty] | Grand Total |  | 40219200 | 40203600 | 40219200 | 0.038802
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902832 | 1 | 723.58 | 749.07 | 25.49 | 250000 | 6372500 |  | 6459836.4885
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902765 | 1 | 632.16 | 656.73 | 24.57 | 250000 | 6142500 |  | 6226684.2888
[6 empty] | 0 | 0 |  | Total | 12515000 |  | 12686520.7772
| FATULLAH 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 887.81 | 924.36 | 36.55 | 60000 |  | 2193000 | 2225117.9731 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 2225117.9731 | 1919103.2774 | 306014.6957 | 15.9457 | OK
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 414.63 | 441.19 | 26.56 | 60000 |  | 1593600 | 1616939.3533 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1616939.3533 | 1431521.3433 | 185418.01 | 12.9525 | OK
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 530.35 | 541.83 | 11.48 | 60000 |  | 688800 | 698887.9434 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 698887.9434 | 713358.7902 | -14470.8468 | -2.0286 | OK
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1177.63 | 1209.06 | 31.43 | 60000 |  | 1885800 | 1913418.8206 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1913418.8206 | 1823628.4898 | 89790.3308 | 4.9237 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 157.05 | 176.71 | 19.66 | 60000 |  | 1179600 | 1196876.0424 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 1196876.0424 | 1264590.5826 | -67714.5402 | -5.3547 | OK
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 68.32 | 78.52 | 10.2 | 60000 |  | 612000 | 620963.1553 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 620963.1553 | 614881.6508 | 6081.5045 | 0.98905 | OK
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1090.6 | 1116.9 | 26.3 | 60000 |  | 1578000 | 1601110.8808 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1601110.8808 | 1579237.0524 | 21873.8284 | 1.3851 | OK
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1318 | 1364.21 | 46.21 | 60000 |  | 2772600 | 2813206.6084 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2813206.6084 | 2526178.8135 | 287027.7949 | 11.3621 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 12686520.7772 | 12503400 | 12686520.7772 | 1.4646
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 12686520.7772
[5 empty] | Total = |  |  | 12686520.7772 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 746.6 | 763.86 | 17.26 | 360000 | 0 | 6213600 | 6216011.0318
0 | 0 | 33 | Backup | 041808904220 | 1 | 746.97 | 763.47 | 16.5 | 360000 | 0 | 5940000 | 5942304.8682
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 516.32 | 532.14 | 15.82 | 360000 | 0 | 5695200 | 5697409.8797
0 | 0 | 33 | Backup | 041808904219 | 1 | 516.01 | 532.46 | 16.45 | 360000 | 0 | 5922000 | 5924297.8838
| DAPA 33 KV SIDE (RECEIVING) | [7 empty] | Total | 0 | 11908800 | 11913420.9116
5 | 33 kV New Fatullah Incoming Circuit-2 | 33 | Import |  | 1 | 185429248 | 191226416 | 5797168 | 1 | 5797168
6 | 33 kV Shyampur Incoming Circuit | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 | 33 | Import |  | 1 | 268448864 | 274521676 | 6072812 | 1 | 6072812
[6 empty] | 0 | 0 |  | Total | 11869980 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| DAPA 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) | 33 | Export | 00000135 | 1 | 276992640 | 282789376 | 5796736 | 1 |  | 5796736
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) | 33 | Export | 00000193 | 1 | 270130304 | 276198240 | 6067936 | 1 |  | 6067936
[9 empty] | Total |  | 11864672 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 11913420.9116 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 11913420.9116
[5 empty] | 33 KV NET IMPORT |  |  | 11913420.9116 |  | 33 KV TX HV SIDE |  | 11864672
[10 empty] | LOSS UNITS=> |  | 48748.9116
[10 empty] | LOSS % IN => |  | 0.4092%
| TOTAL IMPORT |  | 11913420.9116
11 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000035 | 1 | 68569536 | 74606336 | 6036800 | 1 | 6036800 |  | 6091207.8114
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000143 | 1 | 275792320 | 281562528 | 5770208 | 1 | 5770208 |  | 5822213.1002
[6 empty] | 0 | 0 |  | Total | 11807008 |  | 11913420.9116
| DAPA 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11 kV Katherpol Feeder | 11 |  | 00000031 | 1 | 63394284 | 65430400 | 2036116 | 1 |  | 2036116 | 2019617.347 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 2019617.347 | 1872668.2415 | 146949.1055 | 7.847 | OK
12 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | 11 |  | 00000032 | 1 | 64364204 | 65934120 | 1569916 | 1 |  | 1569916 | 1557194.9668 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1557194.9668 | 1351133.0591 | 206061.9077 | 15.251 | OK
14 | 11 kV Shiachar Feeder | 11 |  | 00000030 | 1 | 65776000 | 67793912 | 2017912 | 1 |  | 2017912 | 2001560.8541 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 2001560.8541 | 1924678.9852 | 76881.8689 | 3.9945 | OK
15 | 11 kV Sastapur Feeder | 11 |  | 00000106 | 1 | 70349912 | 70748824 | 398912 | 1 |  | 398912 | 395679.6151 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 395679.6151 | 1143053.371 | -747373.7559 | -65.384 | CHECK
17 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | 11 |  | 00000172 | 1 | 4960348 | 4961228 | 880 | 1 |  | 880 | 872.8694 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 872.8694 | 163.171 | 709.6984 | 434.9416 | FAULT
19 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | 11 |  | 00000044 | 1 | 77520128 | 78934408 | 1414280 | 1 |  | 1414280 | 1402820.0857 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 1402820.0857 | 1449235.5198 | -46415.4341 | -3.2028 | OK
23 | 11 kV Kotaler Bag Feeder | 11 |  | 00000050 | 1 | 82482440 | 85024072 | 2541632 | 1 |  | 2541632 | 2521037.1496 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 2521037.1496 | 1462297.3552 | 1058739.7944 | 72.4025 | FAULT
24 | 11 kV Idrakpur Feeder | 11 |  | 00000021 | 1 | 75647336 | 76871136 | 1223800 | 1 |  | 1223800 | 1213883.5456 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 1213883.5456 | 1042540.0593 | 171343.4863 | 16.4352 | OK
25 | 11 kV Isdair Feeder | 11 |  | 00000029 | 1 | 40064264 | 40865860 | 801596 | 1 |  | 801596 | 795100.6656 | Fatullah |  |  |  | 11 kV Isdair Feeder | 795100.6656 | 849835.155 | -54734.4893 | -6.4406 | OK
26 | 11 kV Shah Fateullah Express | 11 |  | 0000051 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKF 7522 | 1 | 3013 | 3070 | 57 | 100 |  | 5700 | 5653.8129 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 5653.8129 | 5914.9473 | -261.1344 | -4.4148 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 11913420.9116 | 12010744 | 11913420.9116 | -0.8103
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 11913420.9116
[5 empty] | Total = |  |  | 11913420.9116 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 | 132 | IMPORT | 50501730 | 1 | 2821.29 | 2864.027 | 42.737 | 480000 | 0 | 20513760
2 | Tranformer 1 | 132 |  | 80505634 | 1 | 8421.345 | 8461.981 | 40.636 | 480000 | 0 | 19505280
3 | Tranformer 2 | 132 |  | 80505637 | 1 | 8373.619 | 8414.47 | 40.851 | 480000 | 0 | 19608480
4 | MI CEMENT | 132 |  | 38992489 (New) | 1 | 278.728 | 300.247 | 21.519 | 480000 | 0 | 10329120
[8 empty] | Total Import/Export |  | 0 | 69956640
[9 empty] | Net Total | 69956640
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 278.72 | 300.227 | 21.507 | 480000 |  | 10323360
|  | 132 | DPDC | 16402670 | 1 | 1803.746 | 1825.26 | 21.514 | 480000 |  | 10326720
[9 empty] | Total |  | 10326720
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 59629920
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 69956640 |  | EXPORT TO OTHER S/S |  |  | 10326720 |  | 132 KV NET IMPORT |  | 59629920
| IMPORT-2 |  |  |  | 132 KV NET IMPORT for Sitalakhya 33/11 KV |  |  | 59629920 |  | GT (33 KV Side) |  | 59792976
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -163056
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.2734%
| 132 KV TOTAL IMPORT |  | 69956640
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A030701130-03 | 1 | 72155.148 | 91762.092 | 19606.944 | 1000 | 19606944
|  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  | 33 | DPDC | BD001913 | 1 | 1728.8978 | 1769.522 | 40.6242 | 480000 | 19499616
18 | 132/33 KV Transformer, GT-3 Incoming | 33 | DPDC | BD001915 | 1 | 2813.7368 | 2856.8335 | 43.0967 | 480000 | 20686416
[6 empty] | 0 | 0 |  | Total | 59792976 |  | 0
| SITALAKHYA 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 | 33 | DPDC | H/A030701089-03 | 1 | 70391.605 | 79915.453 | 9523.848 | 1000 |  | 9523848 | 9529965.4265 |  | 14499848.6684 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 9529965.4265 | 9115646.719 | 414318.7075 | 4.5451 | OK
|  | 33 | P. Cell | 08993597 | 1 | 5867.204 | 5906.815 | 39.611 | 240000 |  | 9506640 | 9512746.3733 |  |  |  |  | 0 | 9512746.3733 | 9102575.9317 | 410170.4416 | 4.5061 | OK
13 | 33/11 KV Transformer T-4 | 33 | DPDC | H/A030701087-03 | 1 | 71278.528 | 76245.221 | 4966.693 | 1000 |  | 4966693 | 4969883.2419 |  |  |  |  | 33/11 KV Transformer T-4 | 4969883.2419 | 4911653.8047 | 58229.4372 | 1.1855 | OK
|  | 33 | P. Cell | 08993925 | 1 | 5657.145 | 5684.712 | 27.567 | 180000 |  | 4962060 | 4965247.266 |  |  |  |  | 0 | 4965247.266 | 4909576.2491 | 55671.0169 | 1.1339 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 14490541 | 14499848.6684 |  |  |  |  | 33 KV Feeders | 14499848.6684 | 14027300.5237 | 472548.1447 | 3.3688 | OK
10 | 33 KV Char Syedpur Feeder (F1) | 33 | DPDC | H/A030701083-03 | 1 | 42622.665 | 42622.666 | 0.001 | 1000 |  | 1 | 1.0006 |  | 1.0006 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 1.0006 | 0 | 1.0006 | #DIV/0! | #DIV/0!
| 34 KV Char Syedpur Feeder (F1) | 33 | P. Cell | 08993596 | 1 | 2186.817 | 2186.817 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 18741.026 | 30073.619 | 11332.593 | 1000 |  | 11332593 | 11339872.2325 |  | 11339872.2325 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 11339872.2325 | 9960136.0654 | 1379736.1671 | 13.8526 | OK
| 33 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9728.932 | 9791.813 | 62.881 | 180000 |  | 11318580 | 11325850.2316 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 11325850.2316 | 9952272.177 | 1373578.0546 | 13.8017 | OK
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 40076.123 | 41019.721 | 943.598 | 1000 |  | 943598 | 944204.0986 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 944204.0986 | 2494536.8881 | -1550332.7894 | -62.1491 | CHECK
|  | 33 | P. Cell | 08993926 | 1 | 2298.1 | 2303.33 | 5.23 | 180000 |  | 941400 | 942004.6868 |  | 17323324.0992 | Khanpur 33/11 kv ss |  | 0 | 942004.6868 | 2489283.9547 | -1547279.2679 | -62.1576 | CHECK
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 10966.771 | 20100.879 | 9134.108 | 1000 |  | 9134108 | 9139975.0859 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 9139975.0859 | 9373947.1321 | -233972.0463 | -2.496 | OK
|  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1564.4804 | 1607.3637 | 42.8833 | 180000 |  | 7718994 | 7723952.1197 |  | 15677929.8962 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 7723952.1197 | 7622119.3784 | 101832.7413 | 1.336 | OK
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 404.5926 | 438.668 | 34.0754 | 240000 |  | 8178096 | 8183349.0134 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 8183349.0134 | 8147212.5637 | 36136.4497 | 0.44354 | OK
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1291.9433 | 1325.0636 | 33.1203 | 240000 |  | 7948872 | 7953977.7766 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 7953977.7766 | 7992728.8876 | -38751.1111 | -0.48483 | OK
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4676 | 4724.7 | 48.7 | 160 |  | 7792 | 7797.005 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 7797.005 | 4755.5609 | 3041.4441 | 63.9555 | FAULT
[9 empty] | Total |  | 45264053 | 45293127.3316 |  |  |  |  | 0 | 45293127.3316 | 45595436.4763 | -302309.1447 | -0.66303 | OK
[8 empty] | Grand Total |  | 59792976 | 59754594 | 59792976 | 0.064233
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 952001.1037
[5 empty] | Total = |  |  | 952001.1037
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming | 11 |  | DHK 9372 | 1 | 70276.2518 | 123147.3127 | 52871.0609 | 180 | 9516790.962 |  | 9542061.3539
10 | 33/11 kV Transformer, T-4 Incoming | 11 |  | DHK 9368 | 1 | 88120.1466 | 115590.4662 | 27470.3196 | 180 | 4944657.528 |  | 4957787.3145
[6 empty] | 0 | 0 |  | Total | 14461448.49 |  | 14499848.6684
| SITALAKHYA 11 kV SIDE |  |  |  |  | 0 | 0
3 | 11 kV Bholail Feeder (F-3) | 11 |  | DHK 9335 | 1 | 20042.476 | 73278.9421 | 53236.4661 | 60 |  | 3194187.966 | 3202295.2627 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 3202295.2627 | 3113891.785 | 88403.4778 | 2.839 | OK
4 | 11 kV Crony Apparels (F-2) | 11 |  | DHK 9336 | 1 | 48142.2979 | 72262.0412 | 24119.7433 | 60 |  | 1447184.598 | 1450857.7553 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1450857.7553 | 1198137.3888 | 252720.3665 | 21.0928 | OK
5 | 11 kV Baburail Feeder (F-5) | 11 |  | DHK 9322 | 1 | 82394.5117 | 116765.902 | 34371.3903 | 60 |  | 2062283.418 | 2067517.7824 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 2067517.7824 | 2058052.5984 | 9465.184 | 0.45991 | OK
6 | 11 kV Goghchar Feeder (F-1) | 11 |  | DHK 9323 | 1 | 12256.5511 | 34381.3213 | 22124.7702 | 60 |  | 1327486.212 | 1330855.5581 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1330855.5581 | 1324242.6499 | 6612.9082 | 0.49937 | OK
7 | 11 kV Norshinghopur (F-2) | 11 |  | DHK 9365 | 1 | 93513.646 | 117798.346 | 24284.7 | 60 |  | 1457082 | 1460780.2783 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1460780.2783 | 1404336.8639 | 56443.4145 | 4.0192 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 |  | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 |  | 0 | 0 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 |  | H/A030701125-03 | 1 | 73081.722 | 73316.461 | 234.739 | 1000 |  | 234739 | 235334.8005 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 235334.8005 | 246133.1449 | -10798.3444 | -4.3872 | OK
12 | 11 kV Kashipur Feeder (F-7) | 11 |  | H/A030800169-03 | 1 | 34992.83 | 36748.744 | 1755.914 | 1000 |  | 1755914 | 1760370.7558 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1760370.7558 | 1741847.8978 | 18522.858 | 1.0634 | OK
13 | 11 kV Spare Feeder (F-6) | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | 11 |  | H/A030701098-03 | 1 | 78252.992 | 79368.604 | 1115.612 | 1000 |  | 1115612 | 1118443.5796 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 1118443.5796 | 1135381.2606 | -16937.681 | -1.4918 | OK
15 | 11 kV B. K. Road Feeder (F-9) | 11 |  | H/A030800205-03 | 1 | 94550.082 | 95386.118 | 836.036 | 1000 |  | 836036 | 838157.9765 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 838157.9765 | 729788.4502 | 108369.5263 | 14.8494 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 |  | H/A030701091-03 | 1 | 53202.551 | 54235.165 | 1032.614 | 1000 |  | 1032614 | 1035234.9191 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 1035234.9191 | 1075488.4842 | -40253.5652 | -3.7428 | OK
[9 empty] | Total | 14499848.6684 | 14463139.194 | 14499848.6684 | 0.25381
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 1073492.777
[5 empty] | Sytalakhya | at 33 KV level |  | 10240394.5294
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3185961.362
[5 empty] | Total = |  |  | 14499848.6684 | 0
MI CEMENT 132/33 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 278.72 | 300.227 | 21.507 | 480000 | 10323360 |  | 10329120
|  | 132 | DPDC | 16402670 | 1 | 1803.746 | 1825.26 | 21.514 | 480000 | 10326720
2 | 132/33 kV Transformer (132 kV Side) | 132 |  | 06502030 | 1 | 3587.422 | 3630.673 | 43.251 | 240000 |  | 10380240
[6 empty] | 0 | 0 | Total Import/Export |  | 10326720 | 10380240
[6 empty] | 0 | 0 |  | Net Total
[6 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) | 33 |  | 14718815 | 1 | 7079.67 | 7165.187 | 85.517 | 120000 | 10262040
4 | 33 kV Outgoing Feeder-1 | 33 |  | 11745824 | 1 | 3669.351 | 3700.981 | 31.63 | 120000 |  | 3795600
5 | 33 kV Outgoing Feeder-2 | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 6466440
[8 empty] | Total Import/Export |  | 10262040 | 10262040
[8 empty] | Net Total |  | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 10329120
[5 empty] | Total = |  |  | 10329120
192
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1564.4804 | 1607.3637 | 42.8833 | 180000 | 0 | 7718994 | 7723952.1197
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1291.9433 | 1325.0636 | 33.1203 | 240000 | 0 | 7948872 | 7953977.7766
[9 empty] | Total | 0 | 15667866 | 15677929.8962
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder | 33 |  | 00000188 | 1 | 312969952 | 320676832 | 7706880 | 1 | 7706880
7 | 33 kV Shitalakhya-1 Feeder | 33 |  | 00000153 | 1 | 310465440 | 318432064 | 7966624 | 1 | 7966624
[6 empty] | 0 | 0 |  | Total | 15673504 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000116 | 1 | 317581696 | 325287616 | 7705920 | 1 |  | 7705920
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000194 | 1 | 305673600 | 313635840 | 7962240 | 1 |  | 7962240
[9 empty] | Total |  | 15668160
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 15677929.8962 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 15677929.8962
[5 empty] | 33 KV NET IMPORT |  |  | 15677929.8962 |  | 33 KV TX HV SIDE |  | 15668160
[10 empty] | LOSS UNITS=> |  | 9769.8962
[10 empty] | LOSS % IN => |  | 0.06232%
| TOTAL IMPORT |  | 15677929.8962
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming | 11 |  | 00000055 | 1 | 304193962 | 312124352 | 7930390 | 1 | 7930390 |  | 7974722.6449
19 | 11 kV T-2 Incoming | 11 |  | 00000017 | 1 | 315139968 | 322800352 | 7660384 | 1 | 7660384 |  | 7703207.2513
[6 empty] | 0 | 0 |  | Total | 15590774 |  | 15677929.8962
| MONDOLPARA 11 KV SIDE |  |  |  |  | 0 | 0
9 | 11 kV River View | 11 |  | 00000061 | 1 | 6387048 | 7222804 | 835756 | 1 |  | 835756 | 844731.2094 | N.Gonj (East) |  |  |  | 11 kV River View | 844731.2094 | 841728.9793 | 3002.23 | 0.35667 | OK
10 | 11 kV Railgate B.B. Road | 11 |  | 00000191 | 1 | 22810540 | 23455022 | 644482 | 1 |  | 644482 | 651403.112 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 651403.112 | 672012.4136 | -20609.3016 | -3.0668 | OK
11 | 11 kV DIT | 11 |  | 00000174 | 1 | 136605064 | 139579616 | 2974552 | 1 |  | 2974552 | 3006495.8053 | N.Gonj (West) |  |  |  | 11 kV DIT | 3006495.8053 | 3105959.8639 | -99464.0587 | -3.2024 | OK
12 | 11 kV Dalpatti | 11 |  | 00000182 | 1 | 3675991 | 4379629 | 703638 | 1 |  | 703638 | 711194.3901 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 711194.3901 | 640949.3228 | 70245.0673 | 10.9595 | OK
13 | 11 kV South Chasara | 11 |  | 00000043 | 1 | 94325328 | 96976880 | 2651552 | 1 |  | 2651552 | 2680027.0984 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2680027.0984 | 2791666.2107 | -111639.1123 | -3.999 | OK
14 | 11 kV Spare | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | 11 |  | 00000019 | 1 | 130297 | 161639 | 31342 | 1 |  | 31342 | 31678.5827 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 31678.5827 | 33494.5516 | -1815.9689 | -5.4217 | OK
17 | 11 kV Spare | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | 11 |  | 00000173 | 1 | 5319947 | 6362744 | 1042797 | 1 |  | 1042797 | 1053995.629 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1053995.629 | 1019425.3124 | 34570.3166 | 3.3912 | OK
20 | 11 kV Nitaigonj | 11 |  | 00000189 | 1 | 58092820 | 58881896 | 789076 | 1 |  | 789076 | 797549.9114 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 797549.9114 | 692971.3447 | 104578.5666 | 15.0913 | OK
21 | 11 kV Shahid Nagar | 11 |  | 00000020 | 1 | 57039820 | 58363976 | 1324156 | 1 |  | 1324156 | 1338376.1519 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1338376.1519 | 1319788.4916 | 18587.6604 | 1.4084 | OK
22 | 11 kV Bangla Bazar | 11 |  | 00000139 | 1 | 69252312 | 70904584 | 1652272 | 1 |  | 1652272 | 1670015.7997 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1670015.7997 | 1659253.7348 | 10762.0649 | 0.64861 | OK
23 | 11 kV Vogoban Gonj | 11 |  | 00000181 | 1 | 2365594 | 2840673 | 475079 | 1 |  | 475079 | 480180.888 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 480180.888 | 455263.1874 | 24917.7005 | 5.4733 | OK
24 | 11 kV Tanbazar | 11 |  | 00000138 | 1 | 48640480 | 49652160 | 1011680 | 1 |  | 1011680 | 1022544.4626 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 1022544.4626 | 983939.833 | 38604.6296 | 3.9235 | OK
25 | 11 kV SS Road | 11 |  | 00000175 | 1 | 65297040 | 66668396 | 1371356 | 1 |  | 1371356 | 1386083.0342 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1386083.0342 | 1389631.5256 | -3548.4914 | -0.25535 | OK
26 | 11 kV Spare | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 | 0.415 |  |  | 1 | 2500.38 | 2536.53 | 36.15 | 100 |  | 3615 | 3653.8216 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 3653.8216 | 8763.4945 | -5109.6729 | -58.3063 | CHECK
28 | 33/0.415 kV Auxiliary-2 | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15677929.8962 | 15511353 | 15677929.8962 | 1.0739
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1338376.1519
[5 empty] | N.Gonj (East) | at 33 KV level |  | 5593278.1851
[5 empty] | N.Gonj (West) | at 33 KV level |  | 8746275.5592
[5 empty] | Total = |  |  | 15677929.8962 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 18741.026 | 30073.619 | 11332.593 | 1000 | 0 | 11332593 | 11339872.2325
0 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9728.932 | 9791.813 | 62.881 | 180000 | 0 | 11318580 | 11325850.2316
| MATUAIL 33 KV SIDE | [7 empty] | Total |  | 11332593 | 11339872.2325
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 63937.809 | 69594.69 | 5656.881 | 1000 | 0 | 5656881 | 5669902.8329
0 | 0 | 33 | P. Cell | 08993580 | 1.5 | 1345.024 | 1366.01 | 20.986 | 180000 | 0 | 5666220 | 5679263.3307
[9 empty] | Total | 0 | 5656881 | 5669902.8329
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) | [7 empty] | Total |  | 16989474 | 17009775.0654
3 | 33 kV Matuail Feeder | 33 | Digital | ABB03910 | 1 | 81538.1627 | 82654.1714 | 1116.0087 | 4000 | 4464034.96
6 | 33 kV Shitalakhya Feeder | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  | 33 | New | DHKA2199 | 1 | 4138.69 | 4198.7525 | 60.0625 | 180000 | 10811250
[6 empty] | 0 | 0 |  | Total | 4464034.96 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 20/28 MVA Transformer-3 | 33 | Old | HA021100524-02 | 1 | 0 | 0 | 0 | 1000 |  | 0
|  | 33 | New | DHKA2200 | 1 | 4292.5688 | 4318.5088 | 25.94 | 180000 |  | 4669200
7 | 33/11 kV, 10/14 MVA Transformer-2 | 33 | Old | HA030800199-03 | 1 | 39412.298 | 44994.911 | 5582.613 | 1000 |  | 5582613
|  | 33 | New | DHKA2195 | 1 | 4476.1316 | 4533.1934 | 57.0618 | 90000 |  | 5135562
8 | 33/11 kV, 10/14 MVA Transformer-1 | 33 | Digital | ABB03909 | 1 | 425384.895 | 430788.2286 | 5403.3336 | 1000 |  | 5403333.64
[9 empty] | Total |  | 15655146.64
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 11339872.2325 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 17009775.0654
| MATUAIL 33 KV SIDE |  | 5669902.8329 |  | 33 KV NET IMPORT |  |  | 17009775.0654 |  | 33 KV TX HV SIDE |  | 15655146.64
[10 empty] | LOSS UNITS=> |  | 1354628.4254
[10 empty] | LOSS % IN => |  | 7.964%
| TOTAL IMPORT |  | 17009775.0654
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming | 11 |  | 51426632 | 1 | 3726568 | 3786782 | 60214 | 90 | 5419260 |  | 5623601.7997
16 | 33/11 kV Transformer, T-1 Incoming | 11 |  | DHKA2192 | 1 | 3844.1774 | 3904.7704 | 60.593 | 90000 | 5453370 |  | 5658997.9714
22 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426630 | 1 | 4020507 | 4081830 | 61323 | 90 | 5519070 |  | 5727175.2942
[6 empty] | 0 | 0 |  | Total | 16391700 |  | 17009775.0654
| NARAYANGONJ BSCIC 11 KV SIDE |  |  |  |  | 0 | 0
10 | 11 kV Masdair Feeder (F-8) | 11 |  | XA575914 | 1 | 212991.1 | 216058.1 | 3067 | 1000 |  | 3067000 | 3104675.7264 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 3104675.7264 | 3190609.1379 | -85933.4116 | -2.6933 | OK
11 | 11 kV Narayangonj (F-7) | 11 |  | XA575915 | 1 | 165452.9 | 166943.6 | 1490.7 | 1000 |  | 1490700 | 1509012.0982 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1509012.0982 | 1221622.7778 | 287389.3205 | 23.5252 | OK
12 | 11 kV Nearest Feeder (F-6) | 11 |  | XA575927 | 1 | 105393.1 | 106447.5 | 1054.4 | 1000 |  | 1054400 | 1067352.4897 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 1067352.4897 | 767732.4068 | 299620.0829 | 39.0266 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 |  | XA575916 | 1 | 116133.1 | 117391.8 | 1258.7 | 1000 |  | 1258700 | 1274162.1574 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1274162.1574 | 1118663.9439 | 155498.2135 | 13.9004 | OK
14 | 11 kV Abonti Color Tex. (F-4) | 11 |  | XA575912 | 1 | 54786 | 55681.1 | 895.1 | 1000 |  | 895100 | 906095.6122 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 906095.6122 | 696086.8403 | 210008.7719 | 30.1699 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 |  | DHK66615 | 1 | 194.7091 | 212.6573 | 17.9482 | 60000 |  | 1076889.78 | 1090118.5393 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 1090118.5393 | 864699.4622 | 225419.0771 | 26.0691 | OK
17 | 11 kV Shasongaon Feeder (F-2) | 11 |  | XA575920 | 1 | 231721.5 | 232617.3 | 895.8 | 1000 |  | 895800 | 906804.2112 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 906804.2112 | 982770.4437 | -75966.2325 | -7.7298 | OK
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 |  | XA575929 | 1 | 20181.2 | 21345.9 | 1164.7 | 1000 |  | 1164700 | 1179007.44 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1179007.44 | 1159908.2799 | 19099.1601 | 1.6466 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 |  | HA021100913-02 | 1 | 38961.791 | 40336.402 | 1374.611 | 1000 |  | 1374611 | 1391497.0345 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 1391497.0345 | 582908.1262 | 808588.9083 | 138.7164 | FAULT
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 |  | HA021100682-02 | 1 | 59519.019 | 61904.666 | 2385.647 | 1000 |  | 2385647 | 2414952.831 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2414952.831 | 1958482.735 | 456470.0959 | 23.3073 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 |  | HA021100455-02 | 1 | 54442.541 | 56572.368 | 2129.827 | 1000 |  | 2129827 | 2155990.2798 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 2155990.2798 | 1459919.7827 | 696070.4972 | 47.6787 | FAULT
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3813.8 | 3872.6 | 58.8 | 160 |  | 9408 | 9523.57 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 9523.57 | 9809.4637 | -285.8937 | -2.9145 | OK
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4101.4 | 4105 | 3.6 | 160 |  | 576 | 583.0757 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 583.0757 | 16.214 | 566.8617 | 3496.1274 | FAULT
[9 empty] | Grand Total | 17009775.0654 | 16803358.78 | 17009775.0654 | 1.2284
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 906804.2112
[5 empty] | N.Gonj (West) | at 33 KV level |  | 16102970.8542
[5 empty] | Total = |  |  | 17009775.0654 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  | IMPORT | 42627811 | 1 | 259.986 | 272.674 | 12.688 | 960000 | 0 | 12180480
| Madonganj to Charsyedpur-2 |  |  | 42627824 | 1 | 171.744 | 186.579 | 14.835 | 960000 | 0 | 14241600
[8 empty] | Total Import/Export |  | 0 | 26422080 | 0
[9 empty] | Net Total | 26422080
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 | 132 |  | 041808902821 | 1 | 215.46 | 225.62 | 10.16 | 1200000 | 12192000
|  | 132 |  | 041808904222 | 3 | 71.22 | 74.58 | 3.36 | 1200000 | 12096000
| 132 kV Madanganj Circuit-2 | 132 |  | 041808902865 | 1 | 137.4 | 149.27 | 11.87 | 1200000 | 14244000
|  | 132 |  | 041808904240 | 1 | 137.44 | 149.32 | 11.88 | 1200000 | 14256000
[6 empty] | 0 | 0 | Total Import/Export |  | 26436000 | 0 | 0
[6 empty] | 0 | 0 | Net Total |  | 26436000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| CHAR SYEDPUR 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV, 80/120 MVA GT-1 | 132 | EXPORT | 041808902864 | 1 | 165.82 | 175.93 | 10.11 | 1200000 | 12132000 | 12132000
|  | 132 |  | 041808904224 | 1 | 165.71 | 175.81 | 10.1 | 1200000 | 12120000 | 12120000
7 | 132/33 kV, 80/120 MVA GT-2 | 132 |  | 041808902848 | 1 | 187 | 198.92 | 11.92 | 1200000 | 14304000 | 14304000
|  | 132 |  | 041808904244 | 1 | 187.09 | 198.82 | 11.73 | 1200000 | 14076000 | 14076000
[9 empty] | Total |  | 26436000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 26422080 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 26436000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 26436000 |  | 132/33 KV LV SIDE |  | 26330400
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 105600
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3995%
| 132 KV TOTAL IMPORT |  | 26422080
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902859 | 1 | 274.58 | 291.33 | 16.75 | 720000 | 12060000 |  | 12108367.5144
|  | 33 | Backup | 041808904285 | 1 | 274.58 | 291.33 | 16.75 | 720000 | 12060000 |  | 12108367.5144
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902812 | 1 | 310.21 | 330.03 | 19.82 | 720000 | 14270400 |  | 14327632.4856
|  | 33 | Backup | 041808904276 | 1 | 310.23 | 330.05 | 19.82 | 720000 | 14270400 |  | 14327632.4856
[6 empty] | 0 | 0 |  | Total | 26330400 |  | 26436000
| CHAR SYEDPUR 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902875 | 1 | 211.11 | 221.64 | 10.53 | 240000 |  | 2527200 | 2530995.6476 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2530995.6476 | 2449181.8955 | 81813.7521 | 3.3405 | OK
|  | 33 | Backup | 041808904241 | 1 | 211.05 | 221.57 | 10.52 | 240000 |  | 2524800 | 2528592.043 |  |  |  |  | 0 | 2528592.043 | 2449181.8955 | 79410.1475 | 3.2423 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902844 | 3 | 59.77 | 63.07 | 3.3 | 240000 |  | 2376000 | 2379568.5576 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 2379568.5576 | 2213637.4149 | 165931.1427 | 7.4959 | OK
|  | 33 | Backup | 041808904259 | 3 | 59.77 | 63.07 | 3.3 | 240000 |  | 2376000 | 2379568.5576 |  |  |  |  | 0 | 2379568.5576 | 2213637.4149 | 165931.1427 | 7.4959 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 4903200 | 4910564.2051 |  |  |  |  | 33 KV Feeders | 4910564.2051 | 4662819.3103 | 247744.8948 | 5.3132 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 307.61 | 327.5 | 19.89 | 360000 |  | 7160400 | 7171154.3348 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 7171154.3348 | 6850018.059 | 321136.2758 | 4.6881 | OK
|  | 33 | Backup | 041808904221 | 1 | 307.96 | 327.65 | 19.69 | 360000 |  | 7088400 | 7099046.1967 |  |  |  |  | 0 | 7099046.1967 | 6929334.0576 | 169712.1391 | 2.4492 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 100.77 | 107.4 | 6.63 | 360000 |  | 2386800 | 2390384.7783 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2390384.7783 | 2530901.4092 | -140516.6309 | -5.552 | OK
|  | 33 | Backup | 041808904237 | 1 | 100.77 | 107.4 | 6.63 | 360000 |  | 2386800 | 2390384.7783 |  |  |  |  | 0 | 2390384.7783 | 2530901.4092 | -140516.6309 | -5.552 | OK
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 |  | 0 | 0 | Sytalakhya | Grid Has No Reading |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 400185.2656 | -400185.2656 | -100 | CHECK
|  | 33 | Backup | 041808904232 | 1 | 43.8 | 43.8 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 400185.2656 | -400185.2656 | -100 | CHECK
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 460.46 | 493.35 | 32.89 | 360000 |  | 11840400 | 11858183.3118 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 11858183.3118 | 9272761.2883 | 2585422.0235 | 27.8819 | OK
|  | 33 | Backup | 041808904242 | 1 | 460.5 | 493.4 | 32.9 | 360000 |  | 11844000 | 11861788.7187 |  |  |  |  | 0 | 11861788.7187 | 9272761.2883 | 2589027.4304 | 27.9208 | OK
| 33/0.415 kV Transformer AT-1 |  |  |  | 1 | 1595.72 | 1708.92 | 113.2 | 1 |  | 113.2 | 113.37 | [5 empty] | 113.37 | 114.6677
[9 empty] | Total |  | 21387713.2 | 21419835.7949 |  |  |  |  | 0 | 21419835.7949 | 19053980.6897 | 2365855.1052 | 12.4166 | OK
[8 empty] | Grand Total |  | 26330400 | 26290913.2 | 26330400 | 0.15019
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902756 | 1 | 201.74 | 211.8 | 10.06 | 250000 | 2515000 |  | 1881026.7113
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902778 | 1.72 | 118.79 | 128.21 | 9.42 | 250000 | 4050600 |  | 3029537.4938
[6 empty] | 0 | 0 |  | Total | 6565600 |  | 4910564.2051
| CHAR SYEDPUR 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 |  | 041808902749 | 1 | 402.78 | 425.05 | 22.27 | 60000 |  | 1336200 | 1326519.4669 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 1326519.4669 | 1258154.7044 | 68364.7625 | 5.4337 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 |  | 041808902759 | 1 | 438.15 | 457.83 | 19.68 | 60000 |  | 1180800 | 1172245.3124 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1172245.3124 | 1166152.8884 | 6092.4241 | 0.52244 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | 11 |  | 041808902786 | 1 | 275.64 | 303.34 | 27.7 | 60000 |  | 1662000 | 1649959.1034 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1649959.1034 | 1406910.8874 | 243048.216 | 17.2753 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 |  | 041808902789 | 1 | 178 | 190.79 | 12.79 | 60000 |  | 767400 | 761840.3225 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 761840.3225 | 831600.8302 | -69760.5078 | -8.3887 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907976 | 1 | 1595.72 | 1708.92 | 113.2 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4910564.2051 | 4946400 | 4910564.2051 | -0.72448
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 26330286.63
[5 empty] | Total = |  |  | 26330286.63 | 21419722.4249
33 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia | 33 | Export | SIEM0505 | 1 | 36382 | 37576 | 1194 | 6000 | 0 | 7164000 | 7166975.8566
[9 empty] | Total |  | 7164000 | 7166975.8566
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving | 33 |  |  | 1 | 1293.34 | 1332.22 | 38.88 | 180000 | 6998400
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total | 6998400 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| AMULIA 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV Transformer, T-1 | 33 |  | DHKA2194 | 1 | 353.9938 | 368.8855 | 14.8917 | 240000 |  | 3574008
4 | 33/11 kV Transformer, T-2 | 33 |  | DHKA2198 | 1 | 530.5001 | 545.5336 | 15.0335 | 240000 |  | 3608040
[9 empty] | Total |  | 7182048 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 7166975.8566 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 7166975.8566
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 7166975.8566 |  | 33 KV TX HV SIDE |  | 7182048
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -15072.1434
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.2103%
| TOTAL IMPORT |  | 7166975.8566
11 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming | 11 |  | HA021100461-02 | 1 | 16952600 | 20563188 | 3610588 | 1 | 3610588 |  | 3909294.5992
11 | 33/11 kV Transformer, T-1 Incoming | 11 |  | HA021100478-02 | 1 | 86922532 | 89931296 | 3008764 | 1 | 3008764 |  | 3257681.2573
[6 empty] | 0 | 0 |  | Total | 6619352 |  | 7166975.8566
| AMULIA 11 KV SIDE |  |  |  |  | 0 | 0
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 70057178 | 70727703 | 670525 | 1 |  | 670525 | 669679.7315 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 669679.7315 | 704760.429 | -35080.6975 | -4.9777 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 14050902 | 15370323 | 1319421 | 1 |  | 1319421 | 1317757.7287 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1317757.7287 | 1370677.2015 | -52919.4729 | -3.8608 | OK
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 878768 | 1451896 | 573128 | 1 |  | 573128 | 572405.5108 | Demra | Meter Reset |  |  | 11 kV Paity Feeder | 572405.5108 | 546070.575 | 26334.9358 | 4.8226 | OK
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 63742776 | 66196611 | 2453835 | 1 |  | 2453835 | 2450741.6785 | Demra |  |  |  | 11 kV Bamuil Feeder | 2450741.6785 | 2341533.0936 | 109208.5849 | 4.664 | OK
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 14096671 | 14737417 | 640746 | 1 |  | 640746 | 639938.2711 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 639938.2711 | 588274.3679 | 51663.9032 | 8.7823 | OK
13 | 11 kV Amulia Model Town Feeder | 11 | Demra |  | 1 | 51647116 | 51837287 | 190171 | 1 |  | 190171 | 189931.2691 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 189931.2691 | 165276.4 | 24654.8691 | 14.9174 | OK
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 10934861 | 12263057 | 1328196 | 1 |  | 1328196 | 1326521.6668 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1326521.6668 | 1251754.1184 | 74767.5484 | 5.973 | OK
15 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7166975.8566 | 7176022 | 7166975.8566 | -0.12622
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Mugdapara | at 33 KV level |  | 1309618.0026
[5 empty] | Demra | at 33 KV level |  | 5857357.8539
[5 empty] | Total = |  |  | 7166975.8566 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MOGBAZAR T&T 11 KV SIDE | [8 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder | 33 |  | 8993 841 | 1 | 39374.588 | 39440.16 | 65.572 | 36000 | 0 | 2360592 | 2360592 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 2360592 | 3210156 | -849564 | -26.4649 | OK
13 | 33 kV Mondol Para (Premire cement) Feeder | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total |  | 2360592 | 2360592 | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 2360592
[5 empty] | Total = |  |  | 2360592 | 0
Note on G480: User: Meter was faulty and New meter is installed properly in 12.07.23
Note on H480: User: Meter was faulty and New meter is installed properly in 12.07.23

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 | 132 | IMPORT | 50147584 | 1 | 3181.398 | 3226.15 | 44.752 | 1920000 | 0 | 85923840
| Maniknagar-2 | 132 |  | 50147585 | 1 | 3174.787 | 3218.346 | 43.559 | 1920000 | 0 | 83633280
[8 empty] | Total Import/Export |  | 0 | 169557120
[9 empty] | Net Total | 169557120
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 169557120
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 | 132 | EXPORT | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | From Downstream | 19670400 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 | 132 |  | 06604334 | 1 | 8884.95 | 8925.97 | 41.02 | 480000 |  | 19689600
| 132kV Motijheel Circuit-1 | 132 |  | 06604332 | 1 | 1823.15 | 1835.28 | 12.13 | 1440000 |  | 17467200
| 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1625.76 | 1633.75 | 7.99 | 1440000 |  | 11505600
| 132 kV Kazla Circuit-1 | 132 |  | ABB03905 | 1 | 747732 | 781080 | 33348 | 1000 |  | 33348000
| 132 kV Kazla Circuit-2 | 132 |  | ABB03904 | 1 | 560011 | 585377 | 25366 | 1000 |  | 25366000
[6 empty] | 0 | 0 |  | Total |  | 127046800
| MANIKNAGAR 132 KV SIDE |  |  |  |  | 0 | 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 21274000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) | 132 | Export | ABB03903 | 1 | 311836 | 333277 | 21441 | 1000 |  | 21441000 |  |  | 42715000
[9 empty] | Total |  | 42715000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 169557120 |  | EXPORT TO OTHER S/S |  |  | 127046800 |  | 132 KV NET IMPORT |  | 42510320
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 42510320 |  | 33 KV NET IMPORT |  | 42818000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -307680
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.7238%
| 132 KV TOTAL IMPORT |  | 169557120
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) | 33 | Digital | ABB03907 | 1 | 51259 | 72533 | 21274 | 1000 | 21274000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) | 33 | Digital | ABB03906 | 1 | 218841 | 240385 | 21544 | 1000 | 21544000
[6 empty] | 0 | 0 |  | Total | 42818000 |  | 0
| Maniknagar 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 11989209.5602 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK00121 | 2 | 10067.8 | 10073.3 | 5.5 | 4444 | Estimated | 4126429.8988 | 4170531.0981 |  |  |  |  | 0 | 4170531.0981 | 4161360.0577 | 9171.0404 | 0.22039 | OK | 4161360.0577
7 | 33 kV 20/28 MVA Transformer-2 | 33 | Digital | ABB03913 | 1 | 381848 | 385716 | 3868 | 2000 |  | 7736000 | 7818678.462 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 7818678.462 | 7339608.1462 | 479070.3159 | 6.5272 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 11862429.8988 | 11989209.5602 |  |  |  |  | 33 KV Feeders | 11989209.5602 | 11500968.2039 | 488241.3563 | 4.2452 | OK
2 |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 8747095.995 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder | 33 |  | DHK86054 | 1 | 2452.59 | 2468.37 | 15.78 | 270000 |  | 4260600 | 4306135.1416 |  |  |  |  | 33kV Motijheel-1 Feeder | 4306135.1416 | 7406166.835 | -3100031.6934 | -41.8574 | CHECK
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 8936192 | 9031697.5082 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 9031697.5082 | 10222414.2142 | -1190716.7061 | -11.6481 | OK
|  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 18113735.3391 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder | 33 | Digital | ABB03918 | 1 | 297786 | 302279 | 4493 | 2000 |  | 8986000 | 9082037.8309 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 9082037.8309 | 10235919.5773 | -1153881.7464 | -11.2729 | OK
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 270635 | 272335 | 1700 | 2000 |  | 3400000 | 3436337.4833 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 3436337.4833 | 7238761.6479 | -3802424.1645 | -52.5287 | CHECK
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 281410 | 283607 | 2197 | 2000 |  | 4394000 | 4440960.8534 |  | 3436337.4833 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 4440960.8534 | 7587690.532 | -3146729.6785 | -41.4715 | CHECK
12 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20947 | 21210 | 263 | 2000 |  | 526000 | 531621.6224 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 531621.6224 | 605078.9898 | -73457.3674 | -12.1401 | OK
[9 empty] | Total |  | 30502792 | 30828790.4398 |  |  |  |  | 0 | 30828790.4398 | 43296031.7961 | -12467241.3563 | -28.7953 | OK
[8 empty] | Grand Total |  | 42818000 | 42365221.8988 | 42818000 | 1.0687
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 531621.6224
[5 empty] | Total = |  |  | 531621.6224 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 | 11 | Import | 6604357 | 1 | 5424.13 | 5472.21 | 48.08 | 160000 | 7692800 |  | 11913505.0338
9 | 11kV 10/14 MVA Transformer T-1 | 11 | Import | DHK00121 | 2 | 10067.8 | 10073.3 | 5.5 | 4444 | 48884 |  | 75704.5263
[6 empty] | 0 | 0 |  | Total | 7741684 |  | 11989209.5602
| MANIKNAGAR 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Nearest Feeder | 11 |  | HA021101060-02 | 1 | 75374744 | 77039568 | 1664824 | 1 |  | 1664824 | 1666551.6834 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1666551.6834 | 1691601.9901 | -25050.3067 | -1.4809 | OK
2 | 11kV Spare | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | 11 |  | HA021100937-02 | 1 | 77211413 | 78117885 | 906472 | 1 |  | 906472 | 907412.698 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 907412.698 | 936164.8797 | -28752.1817 | -3.0713 | OK
4 | 11 kV R K Mission Road Feeder | 11 |  | HA021101035-02 | 1 | 14171862 | 15727081 | 1555219 | 1 |  | 1555219 | 1556832.94 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1556832.94 | 1647566.9154 | -90733.9755 | -5.5071 | OK
5 | 11 kV Janapath Feeder | 11 |  | HA021100864-02 | 1 | 27595235 | 29720440 | 2125205 | 1 |  | 2125205 | 2127410.4471 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 2127410.4471 | 2194112.6593 | -66702.2121 | -3.0401 | OK
6 | 11 kV Dhalpur Feeder | 11 |  | HA021100851-02 | 1 | 86139684 | 87012283 | 872599 | 1 |  | 872599 | 873504.546 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 873504.546 | 859344.4269 | 14160.1191 | 1.6478 | OK
7 | 11kV WTP | 11 |  | X0599387 | 1 | 1406.5 | 1967.9 | 561.4 | 1000 |  | 561400 | 561982.597 | Maniknagar |  |  |  | 11kV WTP | 561982.597 | 0 | 561982.597 | #DIV/0! | #DIV/0!
10 | 11kV Kamalapur Water pumping | 11 |  | HA021100474-02 | 1 | 7638435 | 7638697 | 262 | 1 | Estimated | 72979.704 | 73055.4392 | Maniknagar | 6 |  |  | 11kV Kamalapur Water pumping | 73055.4392 | 36822.7275 | 36232.7118 | 98.3977 | FAULT
11 | 11 kV Wasa Road Feeder | 11 |  | HA021001011-02 | 1 | 25380490 | 25384272 | 3782 | 1 | Estimated | 2140737.984 | 2142959.5506 | Maniknagar | 176 |  |  | 11 kV Wasa Road Feeder | 2142959.5506 | 2098895.465 | 44064.0856 | 2.0994 | OK
12 | 11kV Sutikhalpar Feeder | 11 |  | HA021101047-02 | 1 | 79907658 | 79907835 | 177 | 1 | Estimated | 2067758.28 | 2069904.1114 | Maniknagar | 170 |  |  | 11kV Sutikhalpar Feeder | 2069904.1114 | 2025250.0101 | 44654.1013 | 2.2049 | OK
13 | 11kV Spare | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 | 0.415 |  | AH14044078 | 1 | 403596.2 | 408804 | 5207.8 | 1 |  | 5207.8 | 5213.2044 | Maniknagar |  |  |  | Axuxilary -1 | 5213.2044 | 5831.4157 | -618.2112 | -10.6014 | OK
| Axuxilary -2 | 0.415 |  | AH14044072 | 1 | 374573.2 | 378951 | 4377.8 | 1 |  | 4377.8 | 4382.3431 | Maniknagar |  |  |  | Axuxilary -2 | 4382.3431 | 5377.7142 | -995.3712 | -18.5092 | OK
13 | AT-1 | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 11989209.5602 | 11976780.568 | 11989209.5602 | 0.10378
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 11989209.5602
[5 empty] | Total = |  |  | 11989209.5602 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder | 33 | 0 | DHK86054 | 1 | 2452.59 | 2468.37 | 15.78 | 270000 | 0 | 4260600 | 4306135.1416
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 281410 | 283607 | 2197 | 2000 | 0 | 4394000 | 4440960.8534
[9 empty] | Total | 0 | 8654600 | 8747095.995
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 | 33 | Import | DHK86054 | 1 | 2452.59 | 2468.37 | 15.78 | 270000 | 4260600
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) | 33 | Import | DHK68120 | 1 | 2128.45 | 2144.71 | 16.26 | 270000 | 4394000 |  |  |  | From Upstream
[6 empty] | 0 | 0 |  | Total | 8654600 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 33kV Biddyut Bhaban Circuit | 33 | Export |  | 1 | 486697 | 487353 | 656 | 600 |  | 393600
[6 empty] | 0 | 0 |  | Total |  | 393600
[6 empty] | 0 | 0 |  |  | 8261000
| Motijheel 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK86053 | 1 | 2961.62 | 2988.22 | 26.6 | 180000 |  | 4788000
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) | 33 | Export | DHK86055 | 1 | 2290.59 | 2290.59 | 0 | 180000 |  | 0
[9 empty] | Total |  | 4788000
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 8654600 |  | EXPORT TO OTHER S/S |  |  | 393600 |  | 33 KV NET IMPORT |  | 8261000
[5 empty] | 33 KV NET IMPORT |  |  | 8261000 |  | 33 KV TX HV SIDE |  | 4788000
[10 empty] | LOSS UNITS=> |  | 3473000
[10 empty] | LOSS % IN => |  | 42.04%
| TOTAL IMPORT |  | 8654600
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 | 11 | Import | DHK86059 | 1 | 3349.09 | 3379.17 | 30.08 | 160000 | 4812800 |  | 4789723.9784 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 | 11 | Import | DHK86057 | 1 | 2598.07 | 2619.87 | 21.8 | 160000 | 3488000 |  | 3471276.0216
[6 empty] | 0 | 0 |  | Total | 8300800 |  | 8261000
| MOTIJHEEL 11 KV SIDE |  |  |  |  | 0 | 0
6 | 11kV Fakirapul Panir Tank Feeder | 11 |  | DHK86058 | 1 | 1695.96 | 1714 | 18.04 | 60000 |  | 1082400 | 1083441.1947 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 1083441.1947 | 1084055.9235 | -614.7288 | -0.056706 | OK
7 | 11kV Station Road Feeder | 11 |  | DHK86075 | 1 | 2376.46 | 2378.15 | 1.69 | 60000 |  | 101400 | 101497.5399 | Motijheel |  |  |  | 11kV Station Road Feeder | 101497.5399 | 109816.6442 | -8319.1043 | -7.5754 | OK
8 | 11kV Box Culvert Road Feeder | 11 |  | DHK86071 | 1 | 3155.14 | 3187.68 | 32.54 | 60000 |  | 1952400 | 1954278.0752 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1954278.0752 | 1833753.908 | 120524.1672 | 6.5725 | OK
9 | 11kV Mohamedan Club Feeder | 11 |  | DHK86062 | 1 | 1678.4 | 1693.67 | 15.27 | 60000 |  | 916200 | 917081.3217 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 917081.3217 | 976079.7817 | -58998.46 | -6.0444 | OK
10 | 11kV Amina Ahmed Co. | 11 |  | DHK95754 | 1 | 108136 | 112104 | 3968 | 60 |  | 238080 | 238309.0167 | Motijheel |  | 178 |  | 11kV Amina Ahmed Co. | 238309.0167 | 251289.93 | -12980.9133 | -5.1657 | OK
11 | 11kV Bangabhaban -1 | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  | 71 |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | 11 |  | DHK95753 | 1 | 59617 | 68343 | 8726 | 60 |  | 523560 | 524063.6289 | Motijheel |  | 107 |  | 11kV Sonali Bank | 524063.6289 | 553807.1772 | -29743.5483 | -5.3707 | OK
15 | 11kV NCC Bank Feeder | 11 |  | DHK68123 | 1 | 320 | 324.15 | 4.15 | 60000 |  | 249000 | 249239.521 | Motijheel |  | 35.6667 |  | 11kV NCC Bank Feeder | 249239.521 | 237424.8118 | 11814.7092 | 4.9762 | OK
16 | 11kV IFIC BANK Feeder | 11 |  | DHK68116 | 1 | 397.35 | 404.96 | 7.61 | 60000 |  | 456600 | 457039.218 | Ramna |  | 106.6667 |  | 11kV IFIC BANK Feeder | 457039.218 | 500616.6574 | -43577.4394 | -8.7048 | OK
17 | 11kV Arambagh Feeder | 11 |  | DHK68117 | 1 | 3367.9 | 3391.53 | 23.63 | 60000 | Estimated | 1277144.82 | 1278373.3459 | Motijheel | 105 |  |  | 11kV Arambagh Feeder | 1278373.3459 | 1267688.622 | 10684.7239 | 0.84285 | OK
18 | 11kV Nikotborti Feeder | 11 |  | DHK68114 | 1 | 1425.76 | 1430.8 | 5.04 | 60000 |  | 302400 | 302690.8881 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 302690.8881 | 931907.7237 | -629216.8356 | -67.5192 | CHECK
19 | 11kV Agrani Bank Feeder | 11 |  | DHK95756 | 1 | 367476 | 371420 | 3944 | 60 |  | 236640 | 236867.6315 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 236867.6315 | 255891.186 | -19023.5545 | -7.4342 | OK
20 | 11kV Bangladesh Bank-2 | 11 |  | DHK95755 | 1 | 527 | 528 | 1 | 60000 | Estimated | 912246.3 | 913123.8185 | Motijheel | 75 |  |  | 11kV Bangladesh Bank-2 | 913123.8185 | 781881.091 | 131242.7275 | 16.7855 | OK
21 | 11kV PDB Design Feeder 14 | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT | 0.415 |  | ELIC5429 | 1 | 411842 | 416832 | 4990 | 1 |  | 4990 | 4994.8 | Motijheel |  |  |  | 11/0.4 kV AT | 4994.8 | 6386.5434 | -1391.7433 | -21.7918 | OK
[9 empty] | Grand Total | 8261000 | 8253061.12 | 8261000 | 0.096193
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 7803960.782
[5 empty] | Ramna | at 33 KV level |  | 457039.218
[5 empty] | Total = |  |  | 8261000 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 | 132 | 0 | 06604332 | 1 | 1823.15 | 1835.28 | 12.13 | 1440000 | 0 | 17467200
2 | 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1625.76 | 1633.75 | 7.99 | 1440000 | 0 | 11505600
[8 empty] | Total Import/Export |  | 0 | 28972800
[9 empty] | Net Total | 28972800
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 | 132 | Imp/Main | 41812909527 | 1 | 315.61 | 330.81 | 15.2 | 1200000 | 18240000
|  | 132 | Imp/Backup | 41812909575 | 1 | 315.69 | 330.89 | 15.2 | 1200000 | 18240000
5 | 132 kV Mniknagar Circuit-2 | 132 | Imp/Main | 41812909512 | 1 | 126.51 | 136.43 | 9.92 | 1200000 | 11904000
|  | 132 | Imp/Backup | 41812909591 | 1 | 126.54 | 136.46 | 9.92 | 1200000 | 11904000
[6 empty] | 0 | 0 | Total Import/Export |  | 30144000 | 0
[6 empty] | 0 | 0 | Net Total |  | 30144000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 36.32 | 37.96 | 1.64 | 1200000 |  | 1968000
|  | 132 | Exp/Backup | 41812909570 | 1 | 36.12 | 37.94 | 1.82 | 1200000 |  | 2184000
7 | 132 kV Bangabhaban Circuit-2 | 132 | Exp/Main | 41812909559 | 1 | 86.61 | 89.82 | 3.21 | 1200000 |  | 3852000
|  | 132 | Exp/Backup | 41812909569 | 1 | 86.61 | 89.82 | 3.21 | 1200000 |  | 3852000
[6 empty] | 0 | 0 |  | Total |  | 5820000
| MOTIJHEEL 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41812909509 | 1 | 207.8 | 221.36 | 13.56 | 1200000 |  | 16272000
|  | 132 | Exp/Backup | 41812909594 | 1 | 207.8 | 221.36 | 13.56 | 1200000 |  | 16272000
6 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41812909508 | 1 | 111.44 | 118.15 | 6.71 | 1200000 |  | 8052000
|  | 132 | Exp/Backup | 41812909592 | 1 | 111.41 | 118.12 | 6.71 | 1200000 |  | 8052000
[9 empty] | Total |  | 24324000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 28972800 |  | EXPORT TO OTHER S/S |  |  | 5820000 |  | 132 KV NET IMPORT |  | 23152800
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 23152800 |  | 33 KV NET IMPORT |  | 23299200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -146400
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.6323%
| 132 KV TOTAL IMPORT |  | 28972800
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41812909543 | 1 | 344.84 | 366.42 | 21.58 | 720000 | 15537600
|  | 33 | Backup | 41812909617 | 1 | 345.08 | 366.67 | 21.59 | 720000 | 15544800
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41812909468 | 1 | 183.91 | 194.69 | 10.78 | 720000 | 7761600
|  | 33 | Backup | 41812909600 | 1 | 183.88 | 194.65 | 10.77 | 720000 | 7754400
[6 empty] | 0 | 0 |  | Total | 23299200 |  | 0
| MOTIJHEEL 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) | 33 | Main | 41812909546 | 1 | 113.58 | 121.78 | 8.2 | 240000 |  | 1968000 | 1965501.871 |  | 4765143.5605 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1965501.871 | 2047621.479 | -82119.608 | -4.0105 | OK
|  | 33 | Backup | 41812909616 | 1 | 113.55 | 121.74 | 8.19 | 240000 |  | 1965600 | 1963104.9175 |  |  |  |  | 0 | 1963104.9175 | 2047621.479 | -84516.5615 | -4.1275 | OK
17 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41812909482 | 1 | 197.84 | 209.52 | 11.68 | 240000 |  | 2803200 | 2799641.6894 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2799641.6894 | 2299083.7659 | 500557.9235 | 21.7721 | OK
|  | 33 | Backup | 42003953371 | 1 | 197.89 | 209.57 | 11.68 | 240000 |  | 2803200 | 2799641.6894 |  |  |  |  | 0 | 2799641.6894 | 2301478.6448 | 498163.0446 | 21.6453 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 4771200 | 4765143.5605 |  |  |  |  | 33 KV Feeders | 4765143.5605 | 4346705.2449 | 418438.3155 | 9.6266 | OK
10 | 33 kV Spare Feeder 1 | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 420.51 | 433.64 | 13.13 | 360000 |  | 4726800 | 4720799.9207 |  | 4720799.9207 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 4720799.9207 | 5442362.3521 | -721562.4315 | -13.2583 | OK
|  | 33 | Backup | 41812909610 | 1 | 420.66 | 433.8 | 13.14 | 360000 |  | 4730400 | 4724395.3509 |  |  |  |  | 0 | 4724395.3509 | 5442362.3521 | -717967.0012 | -13.1922 | OK
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 218.11 | 242.69 | 24.58 | 360000 |  | 8848800 | 8837567.5591 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 8837567.5591 | 9666928.772 | -829361.213 | -8.5794 | OK
|  | 33 | Backup | 41812909595 | 1 | 218.2 | 242.79 | 24.59 | 360000 |  | 8852400 | 8841162.9893 |  | 13788475.0159 | Kamlapur Railway 33/11 kv ss |  | 0 | 8841162.9893 | 9674113.4088 | -832950.4195 | -8.6101 | OK
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 75.59 | 89.36 | 13.77 | 360000 |  | 4957200 | 4950907.4568 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 4950907.4568 | 3312117.5503 | 1638789.9065 | 49.4786 | FAULT
|  | 33 | Backup | 41621865733 | 1 | 75.6 | 89.37 | 13.77 | 360000 |  | 4957200 | 4950907.4568 |  |  |  |  | 0 | 4950907.4568 | 3312117.5503 | 1638789.9065 | 49.4786 | FAULT
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 136.08 | 136.08 | 0 | 360000 |  | 0 | 0 |  | No Load Due to Fdr Trip from 29/06/23 |  |  | 33 kV P & T - 2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909598 | 1 | 136.04 | 136.04 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Spare Feeder 9 | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) | 0.415 |  |  | 1 | 1130.78 | 1213.49 | 82.71 | 300 |  | 24813 | 24781.503 | [5 empty] | 24781.503 | 27086.0806
[9 empty] | Total |  | 18557613 | 18534056.4395 |  |  |  |  | 0 | 18534056.4395 | 18448494.7551 | 85561.6845 | 0.46379 | OK
[8 empty] | Grand Total |  | 23299200 | 23328813 | 23299200 | -0.12694
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) | 11 |  | 41812909493 | 1 | 108.19 | 116.01 | 7.82 | 250000 | 1955000 |  | 1964334.3512
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) | 11 |  | 41812909496 | 1 | 189.01 | 200.16 | 11.15 | 250000 | 2787500 |  | 2800809.2092
[6 empty] | 0 | 0 |  | Total | 4742500 |  | 4765143.5605
| MOTIJHEEL 11 kV SIDE |  |  |  |  | 0 | 0
2 | 11 kV Central Weman | 11 |  | 41812909492 | 1 | 146.96 | 156.68 | 9.72 | 60000 |  | 583200 | 585552.4072 | Motijheel |  |  |  | 11 kV Central Weman | 585552.4072 | 614594.3851 | -29041.978 | -4.7254 | OK
3 | 11 kV Spare Feeder 2 | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len | 11 |  | 41812909499 | 1 | 250.96 | 267.43 | 16.47 | 60000 |  | 988200 | 992186.0233 | Swamibag |  |  |  | 11 kV K. M. Das Len | 992186.0233 | 1031748.0667 | -39562.0435 | -3.8345 | OK
5 | 11 kV Gopibag | 11 |  | 41812909517 | 1 | 36.93 | 39.58 | 2.65 | 60000 |  | 159000 | 159641.3456 | Motijheel |  |  |  | 11 kV Gopibag | 159641.3456 | 169750.8488 | -10109.5032 | -5.9555 | OK
6 | 11kV SPICE TV | 11 |  | 41812909518 | 1 | 14.9 | 18.61 | 3.71 | 60000 |  | 222600 | 223497.8838 | Narinda |  |  |  | 11kV SPICE TV | 223497.8838 | 229344.2319 | -5846.3481 | -2.5492 | OK
7 | 11 kV Spare Feeder 6 | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | 11 |  | 41812909473 | 1 | 377.45 | 386.74 | 9.29 | 60000 |  | 557400 | 559648.3398 | Motijheel |  |  |  | 11 kV South Kamlapur | 559648.3398 | 571253.7429 | -11605.4031 | -2.0316 | OK
14 | 11 kV Spare Feeder 11 | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | 11 |  | 41812909514 | 1 | 179.13 | 191.59 | 12.46 | 60000 |  | 747600 | 750615.5343 | Motijheel |  |  |  | 11 kV Answer Camp | 750615.5343 | 784345.2339 | -33729.6996 | -4.3004 | OK
16 | 11 kV Shapla Chattar | 11 |  | 41812909516 | 1 | 137.07 | 156.7 | 19.63 | 60000 |  | 1177800 | 1182550.7976 | Motijheel |  |  |  | 11 kV Shapla Chattar | 1182550.7976 | 639274.4731 | 543276.3245 | 84.9833 | FAULT
17 | 11 kV Sayedabad | 11 |  | 41812909497 | 1 | 94.88 | 100.05 | 5.17 | 60000 |  | 310200 | 311451.2289 | Swamibag |  |  |  | 11 kV Sayedabad | 311451.2289 | 306394.2625 | 5056.9664 | 1.6505 | OK
22 | 33/0.4 kV Aux Transformer | 0.415 |  | 41901920686 | 1 | 1130.78 | 1213.49 | 82.71 | 1 |  |  | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4765143.5605 | 4746000 | 4765143.5605 | 0.40336
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 3238008.4245
[6 empty] | Swamibag | at 33 KV level |  | 1303637.2522
[6 empty] | Narinda | at 33 KV level |  | 223497.8838
[6 empty] | Total = |  |  | 4765143.5605 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 420.51 | 433.64 | 13.13 | 360000 | 0 | 4726800 | 4720799.9207
0 | 0 | 33 | Backup | 41812909610 | 1 | 420.66 | 433.8 | 13.14 | 360000 | 0 | 4730400 | 4724395.3509
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 136.08 | 136.08 | 0 | 360000 | 0 | 0 | 0
0 | 0 | 33 | Backup | 41812909598 | 1 | 136.04 | 136.04 | 0 | 360000 | 0 | 0 | 0
[9 empty] | Total | 0 | 4730400 | 4724395.3509
Kamalapur Railway 33 KV SIDE (Sending)
1 | 33 kV P&T Circuit | 33 | Import | 102 | 1 | 14.2 | 31.5 | 17.3 | 270000 |  | 4671000
[9 empty] | Total |  | 9395395.3509
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
5 | 33 kV Bidyut Bhaban Circuit | 33 | Import | BD017079 | 1 | 15739.3 | 15802 | 62.7 | 1000 | 62700
|  | 33 | Export | BD017079 | 1 | 0 | 0 | 0 | 1000 |  | 0
7 | 33 kV Motijheel Circuit-1 | 33 | Import | BD017081 | 1 | 132983 | 132983 | 0 | 1000 | 0
8 | 33 kV Motijheel Circuit-2 | 33 | Import | BD017082 | 1 | 21371.33 | 21371.33 | 0 | 1000 | 0
11 | 33 kV Kamlapur Circuit | 33 | Import | BD017085 | 1 | 0 | 0 | 0 | 1000 | 0
|  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
[6 empty] | 0 | 0 |  | Total | 62700 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  |  |  |  | 0 | 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | BD017080 | 1 | 43481 | 48863 | 5382 | 888.88 |  | 4783952.16
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | BD017084 | 1 | 104298 | 104298 | 0 | 888.88 |  | 0
[9 empty] | Total |  | 4783952.16
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Sending Side |  | 9395395.3509 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9395395.3509
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 9395395.3509 |  | 33 KV TX HV SIDE |  | 4783952.16
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 4611443.1909
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 49.08%
| TOTAL IMPORT |  | 9395395.3509
11 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOGBAZAR T&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 | 11 | Import | BD014056 | 1 | 77487.94 | 77487.94 | 0 | 1000 | 4783952.16 |  | 4810805.0982 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | BD014057 | 1 | 92161 | 96720 | 4559 | 1000 | 4559000 |  | 4584590.2528
[6 empty] | 0 | 0 |  | Total | 9342952.16 |  | 9395395.3509
| MOGBAZAR T&T 11 KV SIDE |  |  |  |  | 0 | 0
12 | Inner Circular Road Feeder | 11 |  | BD014042 | 1 | 40052 | 40795 | 743 | 1000 |  | 743000 | 751211.0308 | Motijheel |  |  |  | Inner Circular Road Feeder | 751211.0308 | 786225.5313 | -35014.5005 | -4.4535 | OK
13 | NSI New Building Expres Feeder | 11 |  | BD013982 | 1 | 9624 | 10028 | 404 | 1000 |  | 404000 | 408464.6789 | Ramna |  |  |  | NSI New Building Expres Feeder | 408464.6789 | 417588.6558 | -9123.9769 | -2.1849 | OK
14 | Police Hospital RMU Feeder | 11 |  | BD014044 | 1 | 3401 | 3583 | 182 | 1000 |  | 182000 | 184011.3157 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 184011.3157 | 189813.0254 | -5801.7096 | -3.0565 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | 11 |  | BD014013 | 1 | 32499 | 33977 | 1478 | 1000 |  | 1478000 | 1494333.6521 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1494333.6521 | 1501520.9321 | -7187.28 | -0.47867 | OK
17 | Nayapalton Overhead Feeder | 11 |  | BD014014 | 1 | 23646 | 24648 | 1002 | 1000 |  | 1002000 | 1013073.2878 | Ramna |  |  |  | Nayapalton Overhead Feeder | 1013073.2878 | 1003011.9866 | 10061.3012 | 1.0031 | OK
18 | Masjid Gali Over Head Feeder | 11 |  | BD014016 | 1 | 13676 | 14584 | 908 | 1000 |  | 908000 | 918034.4764 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 918034.4764 | 899114.3306 | 18920.1458 | 2.1043 | OK
19 | Spare Feeder (Feeder-8) | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) | 11 |  | BD013988 | 1 | 12.18 | 12.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | 11 |  | BD014015 | 1 | 21881 | 22853 | 972 | 1000 |  | 972000 | 982741.7522 | Ramna |  |  |  | Mid Way Over Head Feeder | 982741.7522 | 1022992.3051 | -40250.5528 | -3.9346 | OK
24 | Palton Thana Over Head Feeder | 11 |  | BD014033 | 1 | 22279 | 23625 | 1346 | 1000 |  | 1346000 | 1360874.8956 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1360874.8956 | 1387633.1169 | -26758.2213 | -1.9283 | OK
25 | Police Hospital (South) U/G Feeder 7 | 11 |  | BD014034 | 1 | 12204 | 12388 | 184 | 1000 |  | 184000 | 186033.4181 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 186033.4181 | 181820.898 | 4212.5202 | 2.3169 | OK
26 | China Town Express Feeder | 11 |  | BD013943 | 1 | 6095 | 6379 | 284 | 1000 |  | 284000 | 287138.5367 | Ramna |  |  |  | China Town Express Feeder | 287138.5367 | 264739.2196 | 22399.3171 | 8.4609 | OK
27 | Fakirapul Bazar O/H Feeder | 11 |  | BD014032 | 1 | 27825 | 29285 | 1460 | 1000 |  | 1460000 | 1476134.7307 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1476134.7307 | 1280738.4132 | 195396.3176 | 15.2565 | OK
28 | PWD Ouarter (RMU) | 11 |  | BD013937 | 1 | 2163 | 2311 | 148 | 1000 |  | 148000 | 149635.5754 | Motijheel |  |  |  | PWD Ouarter (RMU) | 149635.5754 | 151850.4203 | -2214.8448 | -1.4586 | OK
29 | Postal Quarter RMU | 11 |  | BD013945 | 1 | 2678 | 2854 | 176 | 1000 |  | 176000 | 177945.0086 | Motijheel |  |  |  | Postal Quarter RMU | 177945.0086 | 177824.8343 | 120.1744 | 0.06758 | OK
30 | 11/0.4 kV AT-1 | 0.415 |  | DHKH4409 | 1 | 1377 | 1434 | 57 | 100 |  | 5700 | 5762.9918 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 5762.9918 | 6093.9971 | -331.0054 | -5.4317 | OK
31 | 11/0.4 kV AT-2 | 0.415 |  | DHKH4411 | 1 | 508 | 508 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 0 | 5394.686 | -5394.686 | -100 | CHECK
[9 empty] | Grand Total | 9395395.3509 | 9292700 | 9395395.3509 | 1.1051
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 2554926.3456
[5 empty] | Ramna | at 33 KV level |  | 3609452.732
[5 empty] | Rajarbag | at 33 KV level |  | 3231016.2733
[5 empty] | Total = |  |  | 9395395.3509 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 218.11 | 242.69 | 24.58 | 360000 | 0 | 8848800 | 8837567.5591
0 | 0 | 33 | Backup | 41812909595 | 1 | 218.2 | 242.79 | 24.59 | 360000 | 0 | 8852400 | 8841162.9893
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 75.59 | 89.36 | 13.77 | 360000 | 0 | 4957200 | 4950907.4568
0 | 0 | 33 | Backup | 41621865733 | 1 | 75.6 | 89.37 | 13.77 | 360000 | 0 | 4957200 | 4950907.4568
[9 empty] | Total | 0 | 13809600 | 13792070.4461
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 | 33 | Import | 101 | 1 | 291 | 323.1 | 32.1 | 270000 | 8667000
6 | 33 kV Motijheel Circuit-2 | 33 | Import | 113 | 1 | 100.9 | 119 | 18.1 | 270000 | 4887000
[6 empty] | 0 | 0 |  | Total | 13554000 | 0 | 0
[6 empty] | 0 | 0
1 | 33 kV P&T Circuit | 33 | Import | 102 | 1 | 14.2 | 31.5 | 17.3 | 270000 |  | 4671000
[7 empty] | 0 |  | Total | 0 | 4671000
[6 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | 103 | 1 | 303.5 | 320.8 | 17.3 | 240000 |  | 4152000
4 | 33 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | 104 | 1 | 120.5 | 140.8 | 20.3 | 240000 |  | 4872000
[9 empty] | Total |  | 9024000
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Kamalapur Railway 33 KV SIDE (Sending) |  | 13792070.4461 |  | EXPORT TO OTHER S/S |  |  | 4671000 |  | 33 KV NET IMPORT |  | 9121070.4461
[5 empty] | 33 KV NET IMPORT |  |  | 9121070.4461 |  | 33 KV TX HV SIDE |  | 9024000
[10 empty] | LOSS UNITS=> |  | 97070.4461
[10 empty] | LOSS % IN => |  | 1.064%
| TOTAL IMPORT |  | 13792070.4461
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | 42 | 1 | 361.3 | 382 | 20.7 | 200000 | 4140000 |  | 4205036.9317
10 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | 64 | 1 | 142.5 | 166.7 | 24.2 | 200000 | 4840000 |  | 4916033.5144
[6 empty] | 0 | 0 |  | Total | 8980000 |  | 9121070.4461
| KAMALAPUR RAILWAY 11 KV SIDE |  |  |  |  | 0 | 0
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 385 | 407.2 | 22.2 | 40000 |  | 888000 | 895110.6473 | Rajarbag |  |  |  | Amtola O/H Feeder | 895110.6473 | 1426015.7648 | -530905.1175 | -37.23 | OK
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 63.9 | 69.1 | 5.2 | 40000 |  | 208000 | 209665.557 | Rajarbag |  |  |  | Police Telecom | 209665.557 | 202559.0575 | 7106.4995 | 3.5084 | OK
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 263.8 | 284.1 | 20.3 | 40000 |  | 812000 | 818502.0784 | Rajarbag |  |  |  | Railway Colony O/H | 818502.0784 | 866952.7661 | -48450.6877 | -5.5886 | OK
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 672.9 | 704.5 | 31.6 | 40000 |  | 1264000 | 1274121.462 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 1274121.462 | 2264610.2629 | -990488.8009 | -43.7377 | CHECK
5 | 11 KV Majar Feeder | 11 |  | 96 | 1 | 42.3 | 52 | 9.7 | 40000 |  | 388000 | 391106.9045 | Motijheel |  |  |  | 11 KV Majar Feeder | 391106.9045 | 417271.6585 | -26164.754 | -6.2704 | OK
7 | 11 kV Feeder-6 | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 318.7 | 330.7 | 12 | 40000 |  | 480000 | 483843.5932 | Rajarbag |  |  |  | Momenbagh O/H | 483843.5932 | 563114.1799 | -79270.5867 | -14.0772 | OK
9 | 11 kV Feeder-8 | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 207.3 | 215.5 | 8.2 | 40000 |  | 328000 | 330626.4553 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 330626.4553 | 352452.7601 | -21826.3047 | -6.1927 | OK
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 220.6 | 274.3 | 53.7 | 40000 |  | 2148000 | 2165200.0794 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 2165200.0794 | 449681.1077 | 1715518.9717 | 381.4968 | FAULT
13 | 11 kV Feeder-11 | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 59.2 | 64.4 | 5.2 | 40000 |  | 208000 | 209665.557 | Motijheel |  |  |  | Dhaka Railway | 209665.557 | 230917.3256 | -21251.7685 | -9.2032 | OK
15 | Jasimuddin Feeder-13 | 11 |  | 91 | 1 | 155 | 193.9 | 38.9 | 40000 |  | 1556000 | 1568459.6478 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1568459.6478 | 1713649.6265 | -145189.9786 | -8.4726 | OK
16 | Police Box Feeder-14 | 11 |  | 18 | 1 | 69 | 84.6 | 15.6 | 40000 |  | 624000 | 628996.6711 | Motijheel |  |  |  | Police Box Feeder-14 | 628996.6711 | 656291.3463 | -27294.6752 | -4.1589 | OK
17 | 11 kV Feeder-15 | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) | 0.415 |  | DHKF 7632 | 1 | 902.28 | 948.92 | 46.64 | 100 |  | 4664 | 4701.3469 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 4701.3469 | 8715.1034 | -4013.7565 | -46.0552 | CHECK
20 | Auxiliary -1 (AT-2 ) | 0.415 |  | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 8980000 | 8908664 | 8980000 | 0.80075
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Rajarbag | at 33 KV level |  | 6181771.2196
[5 empty] | Motijheel | at 33 KV level |  | 2798228.7804
[5 empty] | Total = |  |  | 8980000 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 36.32 | 37.96 | 1.64 | 1200000 | 0 | 1968000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 | 132 |  | 41812909559 | 1 | 86.61 | 89.82 | 3.21 | 1200000 | 0 | 3852000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
[9 empty] | Total | 0 | 5820000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
[9 empty] | Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
BANGABHABAN 33 KV SIDE
|  | 132 | NET IMPORT | [7 empty] | 0
|  | 132 | [8 empty] | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 5820000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 5820000
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 5820000 |  | 33 KV TX HV SIDE |  | 5820000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 5820000
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) | 11 | Import | 4150744 | 1 | 1516831.3 | 1520520.1 | 3688.8 | 1000 | 3688800 |  | 3881052.1178
12 | 11 kV 28/35 MVA Transformer (GT-1) | 11 | Import | 4150742 | 1 | 1439781 | 1441623.9 | 1842.9 | 1000 | 1842900 |  | 1938947.8822
[6 empty] | 0 | 0 |  | Total | 5531700 |  | 5820000
| BANGABHABAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 215236.15 | 216382 | 1145.85 | 1000 | Estimated | 875756.448 | 884099.9496 | Motijheel | 72 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 884099.9496 | 816951.1322 | 67148.8173 | 8.2194 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 24132.19 | 24203.56 | 71.37 | 1000 |  | 71370 | 72049.9558 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 72049.9558 | 82523.1488 | -10473.193 | -12.6912 | OK
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33853.02 | 33872.91 | 19.89 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 790613.46 | 798145.7878 | Motijheel | 65 | Meter Bad |  | 11 kV Modhumita via Ovisar | 798145.7878 | 731598.0289 | 66547.7589 | 9.0962 | OK
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15810 | 15886.23 | 76.23 | 1000 |  | 76230 | 76956.258 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 76956.258 | 79365.3753 | -2409.1173 | -3.0355 | OK
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 246649.65 | 247820.06 | 1170.41 | 1000 |  | 1170410 | 1181560.7231 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1181560.7231 | 1155594.7497 | 25965.9734 | 2.247 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14474.96 | 14648.55 | 173.59 | 1000 |  | 173590 | 175243.8256 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 175243.8256 | 162199.2891 | 13044.5365 | 8.0423 | OK
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 279755.532 | 282420.8172 | Motijheel | 23 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 282420.8172 | 243866.0096 | 38554.8076 | 15.8098 | OK
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163764.06 | 164126.32 | 362.26 | 1000 |  | 362260 | 365711.3213 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 365711.3213 | 363925.8833 | 1785.438 | 0.4906 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20596.96 | 20655.45 | 58.49 | 1000 | Estimated | 279755.532 | 282420.8172 | Motijheel | 23 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 282420.8172 | 243866.0096 | 38554.8076 | 15.8098 | OK
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 364898.52 | 368374.979 | Motijheel | 30 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 368374.979 | 341412.4135 | 26962.5655 | 7.8974 | OK
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122899.9 | 123222.28 | 322.38 | 1000 |  | 322380 | 325451.3768 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 325451.3768 | 302665.0764 | 22786.3004 | 7.5286 | OK
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 273094.04 | 273191.92 | 97.88 | 1000 |  | 97880 | 98812.5217 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 98812.5217 | 790606.2505 | -691793.7288 | -87.5017 | CHECK
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 80707.72 | 81231.84 | 524.12 | 1000 |  | 524120 | 529113.3929 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 529113.3929 | 587426.078 | -58312.6851 | -9.9268 | OK
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192560.77 | 192668.35 | 107.58 | 1000 | Estimated | 364898.52 | 368374.979 | Motijheel | 30 | Meter Bad |  | 11 kV BCIC Feeder | 368374.979 | 341412.4135 | 26962.5655 | 7.8974 | OK
23 | 11/0.4 kV AT-1 | 0.415 |  | 63412931 | 1 | 66825 | 72982 | 6157 | 1 |  | 6157 | 6215.6589 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 6215.6589 | 3575.8026 | 2639.8563 | 73.8256 | FAULT
24 | 11/0.4 kV AT-2 | 0.415 |  | 63403117 | 1 | 22885 | 22885 | 0 | 1 | Estimated | 5000 | 5047.636 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5047.636 | 5012.339 | 35.297 | 0.7042 | OK
[9 empty] | Grand Total | 5820000 | 5765075.012 | 5820000 | 0.95272
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 0
[5 empty] | Ramna | at 33 KV level |  | 0
[5 empty] | Swamibag | at 33 KV level |  | 0
[5 empty] | Motijheel | at 33 KV level |  | 5820000
[5 empty] | Total = |  |  | 5820000 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
1 | 132 kV Maniknagar Circuit-1 at Maniknagar | 132 | Import | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | 0 |  |  |  | Reading Corrected
2 | 132 kV Maniknagar Circui-2 at Maniknagar | 132 | Import | 06604334 | 1 | 8884.95 | 8925.97 | 41.02 | 480000 | 19689600
[8 empty] | Total Import/Export |  | 19689600 | 0
[9 empty] | Net Total | 19689600
NARINDA 132 KV SIDE (RECEIVING)
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 19689600
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 19689600
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 19689600 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 19689600
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 19689600 |  | 33 KV NET IMPORT |  | 39302400
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -19612800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -99.61%
| 132 KV TOTAL IMPORT |  | 19689600
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming | 33 | Import | 06604301 | 1 | 9251.22 | 9292.2 | 40.98 | 480000 | 19670400
7 | 132/33 kV 50/75 MVA GT-2 Incoming | 33 | Import | 06604304 | 1 | 9075.38 | 9116.28 | 40.9 | 480000 | 19632000
[6 empty] | 0 | 0 |  | Total | 39302400 |  | 0
| NARINDA 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 | 33 | Export | 06604300 | 1 | 9719.91 | 9765.71 | 45.8 | 180000 |  | 8244000 | 8261216.7571 |  | 17287227.3799 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 8261216.7571 | 8894787.493 | -633570.7359 | -7.1229 | OK
8 | 33 kV 20/28 MVA Transformer T-4 | 33 | Export | 06604303 | 1 | 9850.52 | 9900.56 | 50.04 | 180000 |  | 9007200 | 9026010.6228 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 9026010.6228 | 9193088.2931 | -167077.6703 | -1.8174 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 17251200 | 17287227.3799 |  |  |  |  | 33 KV Feeders | 17287227.3799 | 18087875.7861 | -800648.4062 | -4.4264 | OK
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1553400 | 1556644.1182 |  | 1556644.1182 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1556644.1182 | 2516574.0224 | -959929.9042 | -38.1443 | OK
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 9768408.8149 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5667.71 | 5695.91 | 28.2 | 180000 |  | 5076000 | 5086600.7107 |  |  |  |  | 33 kV Kumertully-1 Feeder | 5086600.7107 | 4432930.6774 | 653670.0333 | 14.7458 | OK
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5541.95 | 5572.58 | 30.63 | 180000 |  | 5513400 | 5524914.1762 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 5524914.1762 | 6213696.0597 | -688781.8835 | -11.0849 | OK
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 9748051 | 9768408.8149 |  | 10611514.8869 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 9768408.8149 | 9376123.4544 | 392285.3606 | 4.1839 | OK
[9 empty] | Total |  | 21890851 | 21936567.8201 |  |  |  |  | 0 | 21936567.8201 | 22539324.2139 | -602756.3938 | -2.6742 | OK
[8 empty] | Grand Total |  | 39223795.2 | 39142051 | 39223795.2 | 0.20884
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming | 11 | Import | 06604351 | 1 | 10930.46 | 10982.3 | 51.84 | 160000 | 8294400 |  | 8270301.4708
9 | 33/11 kV 20/28 MVA T-4 Incoming | 11 | Import | 06604295 | 1 | 11263.13 | 11319.65 | 56.52 | 160000 | 9043200 |  | 9016925.9091
[6 empty] | 0 | 0 |  | Total | 17337600 |  | 17287227.3799
| NARINDA 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Bonogram Feeder | 11 |  | 06604467 | 1 | 24756.85 | 24894.05 | 137.2 | 8000 |  | 1097600 | 1111412.0708 | Narinda |  |  |  | 11 kV Bonogram Feeder | 1111412.0708 | 1143423.9412 | -32011.8704 | -2.7997 | OK
2 | 11 kV Sha Saheb Len Feeder | 11 |  | 06604469 | 1 | 16724.98 | 16806.42 | 81.44 | 8000 |  | 651520 | 659718.6519 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 659718.6519 | 672430.175 | -12711.5231 | -1.8904 | OK
3 | 11 kV Sadiabad Water Treatment | 11 |  | 06604354 | 1 | 500.94 | 501.65 | 0.71 | 40000 |  | 28400 | 28757.3823 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 28757.3823 | 552771.4205 | -524014.0382 | -94.7976 | CHECK
4 | 11 kV Manashi Feeder | 11 |  | 06604353 | 1 | 5528.76 | 5557.42 | 28.66 | 40000 |  | 1146400 | 1160826.1643 | Narinda |  |  |  | 11 kV Manashi Feeder | 1160826.1643 | 1102291.2443 | 58534.92 | 5.3103 | OK
5 | 11 kV Jatrabari Feeder | 11 |  | 06604324 | 1 | 3426.03 | 3478.37 | 52.34 | 40000 |  | 2093600 | 2119945.619 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 2119945.619 | 2124511.9226 | -4566.3036 | -0.21493 | OK
6 | 11 kV Wari Feeder | 11 |  | 06604291 | 1 | 8559.74 | 8599.65 | 39.91 | 40000 |  | 1596400 | 1616488.912 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1616488.912 | 1686359.282 | -69870.37 | -4.1433 | OK
7 | 11 kV Narinda Feeder | 11 |  | 06604348 | 1 | 7302.23 | 7340.4 | 38.17 | 40000 |  | 1526800 | 1546013.0737 | Narinda |  |  |  | 11 kV Narinda Feeder | 1546013.0737 | 1594908.1278 | -48895.0541 | -3.0657 | OK
10 | 11 kV Distillary Feeder | 11 |  | 06604347 | 1 | 5997.97 | 6031.14 | 33.17 | 40000 |  | 1326800 | 1343496.2969 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1343496.2969 | 1318115.968 | 25380.3289 | 1.9255 | OK
11 | 11 kV Thatari Bazar Feeder | 11 |  | 06604296 | 1 | 5033.32 | 5059.48 | 26.16 | 40000 |  | 1046400 | 1059567.7759 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 1059567.7759 | 1097413.8494 | -37846.0735 | -3.4487 | OK
12 | 11 kV Swamibagh Feeder | 11 |  | 06604352 | 1 | 7795.93 | 7829.38 | 33.45 | 40000 |  | 1338000 | 1354837.2364 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 1354837.2364 | 1370141.5135 | -15304.2771 | -1.117 | OK
13 | 11 kV Tipu Sultan Feeder | 11 |  | 06604322 | 1 | 6375.33 | 6403.77 | 28.44 | 40000 |  | 1137600 | 1151915.4261 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 1151915.4261 | 1136839.4581 | 15075.968 | 1.3261 | OK
14 | 11 kV Spare | 11 |  | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | 11 |  | DHK00089 | 1 | 30046.6 | 33769.5 | 3722.9 | 444.44 |  | 1654605.676 | 1675427.0415 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1675427.0415 | 1798340.7365 | -122913.695 | -6.8348 | OK
16 | 11 kV Bhajohari Feeder | 11 |  | DHK27842 | 1 | 394199 | 404158 | 9959 | 80 |  | 796720 | 806745.8319 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 806745.8319 | 813305.5973 | -6559.7654 | -0.80656 | OK
17 | 11 kV Lal mohon shaha Feeder | 11 |  | DHK00086 | 1 | 34337.3 | 36773.5 | 2436.2 | 444.44 |  | 1082744.728 | 1096369.8618 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 1096369.8618 | 1097222.2328 | -852.3711 | -0.077684 | OK
18 | 11 kV Dupkhola Feeder | 11 |  | 8838024/8838029 | 1 | 36817.8 | 37366.6 | 548.8 | 1000 |  | 548800 | 555706.0354 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 555706.0354 | 579800.3171 | -24094.2817 | -4.1556 | OK
1 | 11/0.4 kV Aux Transformer-1 | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17287227.3799 | 17072390.404 | 17287227.3799 | 1.2584
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Narinda | at 33 KV level |  | 11224766.1579
[5 empty] | Maniknagar | at 33 KV level |  | 28757.3823
[5 empty] | Swamibag | at 33 KV level |  | 6033703.8397
[5 empty] | Total = |  |  | 17287227.3799 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5667.71 | 5695.91 | 28.2 | 180000 | 0 | 5076000 | 5086600.7107
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5541.95 | 5572.58 | 30.63 | 180000 | 0 | 5513400 | 5524914.1762
| MITFORD 33 KV SIDE | [9 empty] | 10589400 | 10611514.8869
1 | Kumartuly Circuit-1 | 33 | 0 | DHK-66493 | 1 | 1286272 | 1288507 | 2235 | 180 | 0 | 402300 | 402300
6 | Kumartuly Circuit-2 | 33 | 0 | DHK-60914 | 1 | 761041 | 761041 | 0 | 180 | 0 | 0 | 0
[9 empty] | Total |  | 402300 | 402300
| KUMERTULY 33 KV SIDE (RECEIVING) | [10 empty] | 11013814.8869
5 | 33 kV Mitford Circuit-1 | 33 | Import | DHK60965 | 1 | 280611.3 | 282847.4 | 2236.1 | 180 | 402498
6 | 33 kV Narinda Circuit-1 | 33 | Import | DHK60959 | 1 | 982002.8 | 991437 | 9434.2 | 540 | 5094468
9 | 33 kV Mitford Circuit-2 | 33 | Import | DHK86072 | 1 | 1762.1 | 1765.38 | 3.28 | 180000 | 590400
10 | 33 kV Narinda Circuit-2 | 33 | Import | DHK60957 | 1 | 893878.6 | 904103.9 | 10225.3 | 540 | 5521662
[6 empty] | 0 | 0 |  | Total | 11609028 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| KUMERTULY 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK60960 | 1 | 119591.5 | 147055.4 | 27463.9 | 180 |  | 4943502
8 | 33/11 kV 20/28 MVA Transformer (T-2) | 33 | Export | DHK60958 | 1 | 294551.8 | 326868.1 | 32316.3 | 180 |  | 5816934
[9 empty] | Total |  | 10760436
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 10611514.8869 |  | EXPORT TO OTHER S/S |  |  | 402300 |  | 33 KV NET IMPORT |  | 10799614.8869
| MITFORD 33 KV SIDE |  | 590400 |  | 33 KV NET IMPORT |  |  | 10799614.8869 |  | 33 KV TX HV SIDE |  | 11609028
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -809413.1131
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -7.495%
| TOTAL IMPORT |  | 11201914.8869
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming | 11 | Import | 06604403 | 1 | 7226.87 | 7257.58 | 30.71 | 160000 | 4943502 |  | 4967842.0219 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming | 11 | Import | 06604410 | 1 | 6665.81 | 6702.08 | 36.27 | 160000 | 5803200 |  | 5831772.865
[6 empty] | 0 | 0 |  | Total | 10746702 |  | 10799614.8869
| KUMERTULY 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62634.8 | 62924.7 | 289.9 | 2222.22 |  | 644221.578 | 653524.1946 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 653524.1946 | 604954.0102 | 48570.1844 | 8.0287 | OK
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4589.74 | 4623.56 | 33.82 | 40000 |  | 1352800 | 1372334.5518 | Banglabazar |  |  |  | 11kV Islampur Feeder | 1372334.5518 | 1164609.944 | 207724.6077 | 17.8364 | OK
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5143.44 | 5156.33 | 12.89 | 40000 |  | 515600 | 523045.3096 | Banglabazar |  | 125 |  | 11kV Majar O/H Feeder | 523045.3096 | 442936.2442 | 80109.0655 | 18.0859 | OK
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  | 70 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5442.14 | 5471.04 | 28.9 | 40000 |  | 1156000 | 1172692.7423 | Banglabazar |  | 55 |  | 11kV Sadarghat Feeder | 1172692.7423 | 878663.7611 | 294028.9813 | 33.4632 | OK
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal |  | 18.3333 |  | 11kV Mitford Hospital Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4079.87 | 4110.74 | 30.87 | 40000 |  | 1234800 | 1252630.6213 | Banglabazar |  | 88.3333 |  | 11kV Zindabahar Feeder | 1252630.6213 | 1111745.9438 | 140884.6775 | 12.6724 | OK
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1094695.56 | 1110503.0608 | Banglabazar | 90 |  |  | 11kV Police fari Feeder | 1110503.0608 | 1217802.7423 | -107299.6815 | -8.8109 | OK
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5901.7 | 5929.54 | 27.84 | 40000 |  | 1113600 | 1129680.4826 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 1129680.4826 | 931127.2764 | 198553.2062 | 21.324 | OK
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8198.55 | 8237.18 | 38.63 | 40000 |  | 1545200 | 1567512.8248 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1567512.8248 | 2037666.9172 | -470154.0924 | -23.0732 | OK
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3757.99 | 3769.64 | 11.65 | 40000 |  | 466000 | 472729.0813 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 472729.0813 | 450545.4563 | 22183.6249 | 4.9237 | OK
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7226.32 | 7256.13 | 29.81 | 40000 |  | 1192400 | 1209618.3616 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 1209618.3616 | 1050071.2769 | 159547.0847 | 15.1939 | OK
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3585.71 | 3592.91 | 7.2 | 40000 |  | 288000 | 292158.7455 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 292158.7455 | 264720.4859 | 27438.2596 | 10.365 | OK
27 | 11/0.4 kV AT-1 | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 | 0.415 |  | 05378636 | 1 | 168944.8 | 170919.3 | 1974.5 | 2 |  | 3949 | 4006.0239 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 4006.0239 | 7168.6788 | -3162.6549 | -44.1177 | CHECK
[9 empty] | Grand Total | 10760436 | 10607266.138 | 10760436 | 1.444
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 0
[5 empty] | Banglabazar | at 33 KV level |  | 10760436
[5 empty] | Total = |  |  | 10760436 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 9748051 | 9768408.8149
[9 empty] | Total | 0 | 9748051 | 9768408.8149
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 | 33 | Import | Mat-152447/1191738/007 | 1 | 117707400 | 120600500 | 2893100 | 1 | 2893100
5 | 33 kV Narinda Circuit-2 | 33 | Import | Mat-152447/1191738/002 | 1 | 233197900 | 242485500 | 9287600 | 1 | 9287600
[6 empty] | 0 | 0 |  | Total | 12180700 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) | 33 | Export | Mat-152447/1191738/009 | 1 | 124372000 | 127779000 | 3407000 | 1 |  | 3407000 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) | 33 | Export | Mat-152447/1191738/004 | 1 | 235669900 | 240014900 | 4345000 | 1 |  | 4345000 |  |  | #VALUE!
[9 empty] | Total |  | 7752000
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 9768408.8149 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9768408.8149
[5 empty] | 33 KV NET IMPORT |  |  | 9768408.8149 |  | 33 KV TX HV SIDE |  | 7752000
[10 empty] | LOSS UNITS=> |  | 2016408.8149
[10 empty] | LOSS % IN => |  | 20.64%
| TOTAL IMPORT |  | 9768408.8149
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 | 11 | Import | 340180016886 | 1 | 124893850 | 127805565 | 2911715 | 1 | 2911715 |  | 2917795.8212 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 | 11 | Import | 340180012685 | 1 | 236521648 | 243357984 | 6836336 | 1 | 6836336 |  | 6850612.9937
[6 empty] | 0 | 0 |  | Total | 9748051 |  | 9768408.8149
| BANGSHAL 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 38350227 | 39122615 | 772388 | 1 |  | 772388 | 773303.2759 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 773303.2759 | 760951.1172 | 12352.1587 | 1.6233 | OK
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 49714612 | 51124132 | 1409520 | 1 |  | 1409520 | 1411190.2742 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1411190.2742 | 1426877.2604 | -15686.9862 | -1.0994 | OK
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 20644794 | 21388011 | 743217 | 1 |  | 743217 | 744097.7084 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 744097.7084 | 751903.1259 | -7805.4175 | -1.0381 | OK
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 46320451 | 47954741 | 1634290 | 1 |  | 1634290 | 1636226.6255 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1636226.6255 | 1167271.1296 | 468955.4959 | 40.1754 | FAULT
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 62248027 | 63452528 | 1204501 | 1 |  | 1204501 | 1205928.3277 | Bangshal |  |  |  | 11 kV French Road Feeder | 1205928.3277 | 1183358.8995 | 22569.4281 | 1.9072 | OK
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 30418512 | 31524023 | 1105511 | 1 |  | 1105511 | 1106821.025 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 1106821.025 | 1430551.6276 | -323730.6026 | -22.6298 | OK
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 62764098 | 64344617 | 1580519 | 1 |  | 1580519 | 1582391.9071 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1582391.9071 | 1508639.2033 | 73752.7038 | 4.8887 | OK
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 50259494 | 51559395 | 1299901 | 1 |  | 1299901 | 1301441.3762 | Narinda |  |  |  | 11 kV Suritolla Feeder | 1301441.3762 | 1139549.3681 | 161892.0081 | 14.2067 | OK
13 | AT-1 | 0.415 |  | DHK-4415 | 1 | 734.14 | 734.14 | 0 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 | 0.415 |  | DHK-4410 | 1 | 684.51 | 724.82 | 40.31 | 100 |  | 7000 | 7008.295 | Bangshal |  |  |  | AT-2 | 7008.295 | 7021.7228 | -13.4278 | -0.19123 | OK
[9 empty] | Grand Total | 9768408.8149 | 9756847 | 9768408.8149 | 0.1185
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 7055777.1646
[5 empty] | Banglabazar | at 33 KV level |  | 1411190.2742
[5 empty] | Narinda | at 33 KV level |  | 1301441.3762
[5 empty] | Total = |  |  | 9768408.8149 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | 132kV Kazla Circuit-1 at Maniknagar | 132 | Import | ABB03905 | 1 | 747732 | 781080 | 33348 | 1000 | 33348000 |  |  |  | 132 kV line Loss=
2 | 132kV Kazla Circuit-2 at Maniknagar | 132 | Import | ABB03904 | 1 | 560011 | 585377 | 25366 | 1000 | 25366000 |  |  |  | 100
[6 empty] | 0 | 0 | Total Import/Export |  | 58714000 | 0
[6 empty] | 0 | 0 |  | Net Total | 58714000
| KAZLA 132 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
3 | 132kV Maniknagar Circuit-1 | 132 | Main | 41812909505 | 1 | 623.34 | 651.15 | 27.81 | 1200000 | 33372000
|  | 132 | Backup | 41812909603 | 1 | 623.32 | 651.12 | 27.8 | 1200000 | 33360000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 | 132 | Main | 41812909540 | 1 | 465.71 | 486.81 | 21.1 | 1200000 | 25320000
|  | 132 | Backup | 41812909587 | 1 | 465.72 | 486.83 | 21.11 | 1200000 | 25332000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
[6 empty] | 0 | 0 | Total Import/Export |  | 58692000 | 0
[6 empty] | 0 | 0 | Net Total |  | 58692000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| KAZLA 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Main | 41812909542 | 1 | 623.76 | 651.72 | 27.96 | 1200000 |  | 33552000 |  |  | #DIV/0!
|  | 132 | Backup | 41812909589 | 1 | 624.12 | 652.1 | 27.98 | 1200000 |  | 33576000
7 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Main | 41812909501 | 1 | 465.48 | 486.43 | 20.95 | 1200000 |  | 25140000 |  |  | 100
|  | 132 | Backup | 41812909606 | 1 | 465.42 | 486.37 | 20.95 | 1200000 |  | 25140000
[9 empty] | Total |  | 58692000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 58714000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 58714000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 58714000 |  | 33 KV NET IMPORT |  | 58492800
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 221200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3767%
| 132 KV TOTAL IMPORT |  | 58714000
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) | 33 | Main | 41812909533 | 1 | 1035.55 | 1081.97 | 46.42 | 720000 | 33422400
|  | 33 | Backup | 41812909582 | 1 | 1035.63 | 1082.06 | 46.43 | 720000 | 33429600
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) | 33 | Main | 41812909479 | 1 | 773.27 | 808.09 | 34.82 | 720000 | 25070400
|  | 33 | Backup | 41812909622 | 1 | 773.17 | 807.98 | 34.81 | 720000 | 25063200
[6 empty] | 0 | 0 |  | Total | 58492800 |  | 0
| KAZLA 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 | 33 | Main | 41812909465 | 1 | 1040.01 | 1090.98 | 50.97 | 240000 |  | 12232800 | 12249430.1142 |  | 39570922.4143 | Kazla 33/11 kv ss | 1.211 | 33/11 kV 20/28 MVA T-1 | 12249430.1142 | 11898323.8721 | 351106.2421 | 2.9509 | OK
|  | 33 | Backup | 41812909596 | 1 | 1039.74 | 1090.7 | 50.96 | 240000 |  | 12230400 | 12247026.8515 |  |  |  |  | 0 | 12247026.8515 | 11893518.4102 | 353508.4413 | 2.9723 | OK
13 | 33/11 kV 28/35 MVA T-5 | 33 | Main | 41812909536 | 1 | 115.16 | 126.37 | 11.21 | 360000 |  | 4035600 | 4041086.2737 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 4041086.2737 | 3665366.1282 | 375720.1455 | 10.2505 | OK
|  | 33 | Backup | 41812909578 | 1 | 113.55 | 121.74 | 8.19 | 360000 |  | 2948400 | 2952408.2588 |  |  |  |  | 0 | 2952408.2588 | 3081502.4972 | -129094.2383 | -4.1893 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 | Main | 41812909554 | 1 | 1039.05 | 1079.83 | 40.78 | 240000 |  | 9787200 | 9800505.3965 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 9800505.3965 | 10105886.5521 | -305381.1557 | -3.0218 | OK
|  | 33 | Backup | 41812909613 | 1 | 1038.32 | 1078.77 | 40.45 | 240000 |  | 9708000 | 9721197.7265 |  |  |  |  | 0 | 9721197.7265 | 10165954.8269 | -444757.1004 | -4.375 | OK
17 | 33/11 kV 20/28 MVA T-3 | 33 | Main | 41812909544 | 1 | 903.03 | 938.18 | 35.15 | 240000 |  | 8436000 | 8447468.4817 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 8447468.4817 | 8116425.2908 | 331043.1909 | 4.0787 | OK
|  | 33 | Backup | 41812909614 | 1 | 903.06 | 938.21 | 35.15 | 240000 |  | 8436000 | 8447468.4817 |  |  |  |  | 0 | 8447468.4817 | 8118828.0218 | 328640.4599 | 4.0479 | OK
22 | 33/11 kV 10/14 MVA T-4 | 33 | Main | 41812909506 | 1 | 470.81 | 491.75 | 20.94 | 240000 |  | 5025600 | 5032432.1482 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 5032432.1482 | 5177885.2877 | -145453.1395 | -2.8091 | OK
|  | 33 | Backup | 41812909602 | 1 | 470.94 | 491.89 | 20.95 | 240000 |  | 5028000 | 5034835.4109 |  |  |  |  | 0 | 5034835.4109 | 5175482.5567 | -140647.1458 | -2.7176 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 39517200 | 39570922.4143 |  |  |  |  | 33 KV Feeders | 39570922.4143 | 38963887.131 | 607035.2833 | 1.5579 | OK
10 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 571.22 | 592.95 | 21.73 | 360000 |  | 7822800 | 7833434.8553 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 7833434.8553 | 7323524.0635 | 509910.7918 | 6.9626 | OK
|  | 33 | Backup | 41812909580 | 1 | 571.17 | 592.9 | 21.73 | 360000 |  | 7822800 | 7833434.8553 |  |  |  |  | 0 | 7833434.8553 | 7319919.967 | 513514.8883 | 7.0153 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Spare Feeder 7 | 33 | Main | 41812909523 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909565 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 630.73 | 661.44 | 30.71 | 360000 |  | 11055600 | 11070629.7471 | Kazla |  |  |  | 33 kV Zahir Steel | 11070629.7471 | 10019388.2364 | 1051241.5107 | 10.4921 | OK
|  | 33 | Backup | 41812909563 | 1 | 630.96 | 661.68 | 30.72 | 360000 |  | 11059200 | 11074234.6412 |  |  |  |  | 0 | 11074234.6412 | 10026596.4294 | 1047638.2118 | 10.4486 | OK
| Auxiliary Transformer-3 (AT-3) | 0.415 |  |  | 1 | 2407.99 | 2519.17 | 111.18 | 160 |  | 17788.8 | 17812.9833 | [5 empty] | 17812.9833 | 18800.5691
[9 empty] | Total |  | 18896188.8 | 18921877.5857 |  |  |  |  | 0 | 18921877.5857 | 17361712.869 | 1560164.7167 | 8.9862 | OK
[8 empty] | Grand Total |  | 58492800 | 58413388.8 | 58492800 | 0.13595
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | KAZLA at 33 KV level |  |  | 18904064.6024
[6 empty] | Kazla 33/11 KV Substation |  |  | 39570922.4143
[8 empty] | Total = | 58474987.0167 | -17812.9833
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| KAZLA 11 KV SIDE | [13 empty] | 200
16 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK-61009 | 1 | 7832262 | 7899071 | 66809 | 180 | 12025620 |  | 12249430.1142 |  |  | 130
30 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK-61124 | 1 | 806735.8 | 859085.1 | 52349.3 | 180 | 9422874 |  | 9800505.3965 |  |  | 70
24 | 33/11 kV 20/28 MVA T-3 Incoming | 11 |  | DHK-61015 | 1 | 438680.6 | 489391 | 50710.4 | 180 | 9127872 |  | 8447468.4817
39 | 33/11 kV 10/14 MVA T-4 Incoming | 11 |  | 8L55984 | 1 | 27993.1 | 29233.3 | 1240.2 | 4000 | 4960800 |  | 5032432.1482 |  |  | 23.3333
42 | 33/11 kv 28/35 MVA T-5 Incomer | 11 |  | DHK00112 | 1 | 4990.3 | 9542.7 | 4552.4 | 888.8 | 4046173.12 |  | 4041086.2737 |  |  | 153.3333
[6 empty] | 0 | 0 |  | Total | 39583339.12 |  | 39570922.4143
| KAZLA 11 kV SIDE |  |  |  |  | 0 | 0
17 | 11 kV Nayanagor Feeder | 11 |  | DHK-61125 | 1 | 843800.5 | 874043.5 | 30243 | 60 |  | 1814580 | 1836553.7788 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1836553.7788 | 1866699.9643 | -30146.1855 | -1.6149 | OK
18 | 11 kV Madrasa Bazar Feeder | 11 |  | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1846586.4161 | Kazla | 150 |  |  | 11 kV Madrasa Bazar Feeder | 1846586.4161 | 1853855.1196 | -7268.7035 | -0.39209 | OK
19 | 11 kV Kazla Feeder | 11 |  | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2919188.16 | 2954538.2657 | Kazla | 240 |  |  | 11 kV Kazla Feeder | 2954538.2657 | 3027963.362 | -73425.0963 | -2.4249 | OK
20 | 11 kV Sayedabad Feeder | 11 |  | HA021101239-02 | 1 | 36963861 | 36963861 | 0 | 1000 | Estimated | 1216328.4 | 1231057.6107 | Maniknagar | 100 |  |  | 11 kV Sayedabad Feeder | 1231057.6107 | 988722.7304 | 242334.8803 | 24.5099 | OK
21 | 11 kV Zenith Feeder | 11 |  | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | 11 |  | HA-021200060 | 1 | 114727 | 116728 | 2001 | 1000 |  | 2001000 | 2025231.2443 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 2025231.2443 | 2541656.3466 | -516425.1023 | -20.3184 | OK
23 | 11 kV Matuail Feeder | 11 |  | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1946125.44 | 1969692.1771 | Kazla | 160 |  |  | 11 kV Matuail Feeder | 1969692.1771 | 1730264.7783 | 239427.3989 | 13.8376 | OK
25 | 11 kV Kutubkhali Feeder | 11 |  | DHK-61117 | 1 | 723552 | 760780.4 | 37228.4 | 60 |  | 2233704 | 2260753.1891 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2260753.1891 | 2379719.4891 | -118966.3 | -4.9992 | OK
26 | 11 kV Mridhabari Feeder | 11 |  | DHK-61118 | 1 | 624583.7 | 650400.9 | 25817.2 | 60 |  | 1549032 | 1567790.1074 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1567790.1074 | 1353302.4526 | 214487.6547 | 15.8492 | OK
27 | 11 kV Muslim Nagar Feeder | 11 |  | DHK-61011 | 1 | 25255.2 | 67793.5 | 42538.3 | 60 |  | 2552298 | 2583205.2246 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2583205.2246 | 2385633.1534 | 197572.0711 | 8.2817 | OK
28 | 11 kV Jatrabari Thana Feeder | 11 |  | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | 11 |  | DHK-61008 | 1 | 246764.7 | 281446.3 | 34681.6 | 60 |  | 2080896 | 2106094.7503 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 2106094.7503 | 2092254.4374 | 13840.3129 | 0.6615 | OK
31 | 11 kV Mukti Sharani Feeder | 11 |  | DHK-61014 | 1 | 113721.9 | 153577.1 | 39855.2 | 60 |  | 2391312 | 2420269.7538 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 2420269.7538 | 2465205.4697 | -44935.7159 | -1.8228 | OK
32 | 11 kV Kadamtali Feeder | 11 |  | DHK-61006 | 1 | 326888.5 | 373366.3 | 46477.8 | 60 |  | 2788668 | 2822437.563 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 2822437.563 | 2221373.5062 | 601064.0568 | 27.0582 | OK
33 | 11kV Rayerbagh Feeder | 11 |  | DHK-61012 | 1 | 404227.5 | 409542.6 | 5315.1 | 60 |  | 318906 | 322767.8137 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 322767.8137 | 1280357.0984 | -957589.2847 | -74.7908 | CHECK
34 | 11 kV Donia Feeder | 11 |  | DHK-61013 | 1 | 1980100 | 2013143 | 33043 | 60 |  | 1982580 | 2006588.1861 | Jurain |  |  |  | 11 kV Donia Feeder | 2006588.1861 | 2090084.0617 | -83495.8756 | -3.9949 | OK
35 | 11 kV Nimtoli Feeder | 11 |  | HA-021100855-02 | 1 | 29423230 | 30931536 | 1508306 | 1 |  | 1508306 | 1526570.9331 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1526570.9331 | 1509829.6282 | 16741.305 | 1.1088 | OK
36 | 11 kV Gobindapur Feeder | 11 |  | HA-021101057-02 | 1 | 26674761 | 27377064 | 702303 | 1 |  | 702303 | 710807.5855 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 710807.5855 | 721136.817 | -10329.2315 | -1.4324 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 |  | 9A56136 | 1 | 3271.9 | 3447.6 | 175.7 | 10000 |  | 1757000 | 1778276.5099 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1778276.5099 | 1887901.7718 | -109625.2619 | -5.8067 | OK
38 | 11 kV Samad Nagar Gate (Old) | 11 |  | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | 11 |  | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Dharmik Para | 0 | 0 | 0 | #DIV/0! | #DIV/0!
41 | 11 kV Sheikhdi Feeder | 11 |  | 9A56133 | 1 | 14288.8 | 15118.7 | 829.9 | 4000 |  | 3319600 | 3359798.9198 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 3359798.9198 | 3415699.9979 | -55901.078 | -1.6366 | OK
43 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | 11 |  | 61903661 | 1 | 20864.4 | 21474.6 | 610.2 | 1000 |  | 610200 | 617589.258 | Kazla |  |  |  | 11 kV Jenith Feeder | 617589.258 | 551840.3941 | 65748.8639 | 11.9145 | OK
45 | 11 KV Samad Nagor Gate | 11 |  | 61903675 | 1 | 17718.5 | 18394.6 | 676.1 | 2000 |  | 1352200 | 1368574.557 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1368574.557 | 1134163.594 | 234410.963 | 20.6682 | OK
46 | 11 KV Bibir Bagicha | 11 |  | 61903557 | 1 | 36323.7 | 37044.1 | 720.4 | 2000 |  | 1440800 | 1458247.4647 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 1458247.4647 | 1460126.3972 | -1878.9326 | -0.12868 | OK
47 | 33/0.4 kV AT-1 | 0.415 |  | 503043 | 1 | 96204 | 96204 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 | 0.415 |  | 503044 | 1 | 93994 | 93994 | 0 | 10 |  | 6000 | 6072.6574 | Kazla |  |  |  | 33/0.4 kV AT-2 | 6072.6574 | 6096.5612 | -23.9038 | -0.39209 | OK
23 | Auxiliary Transformer | 0.415 |  | 41901920685 | 1 | 2407.99 | 2519.17 | 111.18 | 160 |  |  | 0 | Kazla |  |  |  | Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 38779503.966 | 38315519.6 | 38779503.966 | 1.211
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 322767.8137
[5 empty] | Jurain | at 33 KV level |  | 8712842.3732
[5 empty] | Swamibag | at 33 KV level |  | 2106094.7503
[5 empty] | Maniknagar | at 33 KV level |  | 2689305.0754
[5 empty] | Shyampur | at 33 KV level |  | 2822437.563
[5 empty] | Kazla | at 33 KV level |  | 22126056.3904
[5 empty] | Total = |  |  | 38779503.966 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT | 132 |  | 8993532 | 1 | 2227.617 | 2227.617 | 0 | 960000 | 0 | 0
|  | 132 |  |  | 1 | 666.546 | 666.62 | 0.074 | 960000 | 71040 | 0
1 | Tranformer - 1 at Shyampur 230/132 | 132 |  | 38992560 | 1 | 1441.023 | 1475.868 | 34.845 | 1920000 | 0 | 66902400
|  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  | 132 |  | 38992559 | 1 | 1532.023 | 1566.65 | 34.627 | 1920000 | 0 | 66483840
| Aggrekko 100 MW (Brammhongao) | 132 |  | PN-1711A04601 | 1 | 363.871 | 363.871 | 0 | 960000 | 0 | 0
|  | 132 |  |  | 1 | 5.419 | 5.419 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Exp | 132 |  | 38992544 | 1 | 32.177 | 32.187 | 0.01 | 960000 | 0 | 9600
| Madanganj-Fatullah Imp | 132 |  | 38992544 | 1 | 18.041 | 18.041 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 71040 | 133395840
[9 empty] | Net Total | 133324800
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) | 132 | Import | 08993727 | 1 | 9070.469 | 9139.037 | 68.568 | 720000 | 49368960
|  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) | 132 | Import | 08993726 | 1 | 6822.265 | 6883.01 | 60.745 | 720000 | 43736400
|  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
[6 empty] | 0 | 0 | Total Import/Export |  | 93105360 | 0
[6 empty] | 0 | 0 | Net Total |  | 93105360
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
|  | 132 |  |  |  | 0 | 0
|  | 132 |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total |  | 40248000
| SHYAMPUR 132 KV SIDE |  |  |  |  | 0 | 0
5 | 132 kV 80/120 MVA ( GT-1) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) | 132 | Export | ABB3902 | 1 | 1883170.2 | 2196733.6 | 313563.4 | 1300 |  | 407632420
[9 empty] | Total |  | 52857360
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 133324800 |  | EXPORT TO OTHER S/S |  |  | 40248000 |  | 132 KV NET IMPORT |  | 93076800
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 93076800 |  | 33 KV NET IMPORT |  | 92938512
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 138288
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.1486%
| 132 KV TOTAL IMPORT |  | 133324800
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) | 33 | Import | BD001826 | 1 | 3379.2839 | 3424.8039 | 45.52 | 480000 | 21849600
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) | 33 | Import | BD001850 | 1 | 3436.324 | 3481.9499 | 45.6259 | 480000 | 21900432
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) | 33 | Import | BD001835 | 1 | 2926.9819 | 2977.312 | 50.3301 | 480000 | 24158448
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) | 33 | Import | BD001831 | 1 | 3807.42 | 3859.5659 | 52.1459 | 480000 | 25030032
[6 empty] | 0 | 0 |  | Total | 92938512
| SHYAMPUR 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) | 33 | Export | BD001808 | 1 | 2115.75 | 2148.642 | 32.892 | 240000 | From Downstream | 7894400 | 7895191.8306 |  | 26903818.2582 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7895191.8306 | 6833454.0489 | 1061737.7817 | 15.5374 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) | 33 | Export | BD001834 | 1 | 1928.017 | 1960.749 | 32.732 | 240000 | From Downstream | 7844800 | 7845586.8556 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7845586.8556 | 6797037.0911 | 1048549.7645 | 15.4266 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) | 33 | Export | BD001846 | 1 | 1422.083 | 1448.779 | 26.696 | 240000 |  | 6407040 | 6407682.6442 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 6407682.6442 | 5617199.691 | 790482.9532 | 14.0725 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) | 33 | Export | BD001847 | 1 | 1282.697 | 1302.509 | 19.812 | 240000 |  | 4754880 | 4755356.9279 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 4755356.9279 | 5181876.9797 | -426520.0518 | -8.231 | OK
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 26901120 | 26903818.2582 |  |  |  |  | 33 KV Feeders | 26903818.2582 | 24429567.8107 | 2474250.4475 | 10.1281 | OK
1 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 725.5189 | 736.898 | 11.3791 | 240000 |  | 2730984 | 2731257.9254 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 2731257.9254 | 2448780.2928 | 282477.6326 | 11.5354 | OK
2 | 33 kV Postogola Feeder-1. | 33 | Export | BD001804 | 1 | 1564.5419 | 1564.5419 | 0 | 240000 |  | 0 | 0 |  | 456.0457 | Postogola 33/11 kv s/s | Grid Has No Reading | 33 kV Postogola Feeder-1. | 0 | 216.1006 | -216.1006 | -100 | CHECK
5 | 33 kV Prime Textile Feeder. | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1278.1529 | 1307.8 | 29.6471 | 240000 | From Downstream | 7115304 | 7116017.6851 |  | 13193403.2028 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 7116017.6851 | 7238410.62 | -122392.9349 | -1.6909 | OK
7 | 33 kV Nondolalpur -2 feeder | 33 | Export | BD001807 | 1 | 1108.057 | 1133.3769 | 25.3199 | 240000 |  | 6076776 | 6077385.5178 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 6077385.5178 | 5427487.35 | 649898.1678 | 11.9742 | OK
8 | 33 kV Postogola Feeder-2. | 33 | Export | BD001830 | 1 | 2131.894 | 2131.8959 | 0.0019 | 240000 |  | 456 | 456.0457 |  |  |  |  | 33 kV Postogola Feeder-2. | 456.0457 | 0 | 456.0457 | #DIV/0! | #DIV/0!
11 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 637.06 | 647.0944 | 10.0344 | 240000 |  | 2408256 | 2408497.5549 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2408497.5549 | 1851141.9981 | 557355.5568 | 30.1087 | OK
12 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1143.578 | 1183.389 | 39.811 | 240000 |  | 9554640 | 9555598.3573 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 9555598.3573 | 9761265.4061 | -205667.0488 | -2.107 | OK
13 | 33 kV Fatullah Feeder-2. | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 1167285.0702 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2542.812 | 2577.923 | 35.111 | 240000 |  | 8595172.8 | 8596034.9201 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8596034.9201 | 7895073.68 | 700961.2401 | 8.8785 | OK
17 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 677.3128 | 682.176 | 4.8632 | 240000 | Prime Textile | 1167168 | 1167285.0702 | Fatullah | 18516469.8679 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 1167285.0702 | 1147950.5517 | 19334.5185 | 1.6843 | OK
18 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 135.586 | 143.0939 | 7.5079 | 240000 |  | 1801896 | 1802076.7353 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1802076.7353 | 1343089.4196 | 458987.3156 | 34.174 | OK
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 |  | 0 | 0 |  | 0 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1511.052 | 1541.9069 | 30.8549 | 240000 |  | 7405176 | 7405918.76 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 7405918.76 | 5422228.9014 | 1983689.8587 | 36.5844 | OK
23 | 33 kV Shyampur BSCIC-2. | 33 | Export | BD001827 | 1 | 2462.895 | 2504.226 | 41.331 | 240000 |  | 9919440 | 9920434.9478 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 9920434.9478 | 9538945.8814 | 381489.0664 | 3.9993 | OK
24 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2365.387 | 2403.8439 | 38.4569 | 240000 |  | 9229656 | 9230581.7605 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 9230581.7605 | 8256580.7385 | 974001.022 | 11.7967 | OK
23 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 343.416 | 345.49 | 2.074 | 2400 |  | 5102.04 | 5102.04 | Fatullah
24 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 95.379 | 102.714 | 7.335 | 2400 |  | 18044.1 | 18044.1 | Fatullah
[9 empty] | Total |  | 66028070.94 | 66034691.4202 |  |  |  |  | 0 | 66034691.4202 | 60356132.5603 | 5678558.8598 | 9.4084 | OK
[8 empty] | Grand Total |  | 92938512 | 92929190.94 | 92938509.6784 | 0.010028
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 33133931.0934
[5 empty] | Fatullah | at 33 KV level |  | 1190431.2102
[6 empty] | Export to Other SS |  | 58614147.3747
[5 empty] | Total = |  |  | 92938509.6784 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | BD001926 | 1 | 2862.73 | 2912.07 | 49.34 | 160000 | 7894400 |  | 7900544.006 |  | 7894400
16 | 11 kV 20/28 MVA Transformer-2 | 11 |  | BD001952 | 1 | 2875.42 | 2924.45 | 49.03 | 160000 | 7844800 |  | 7850905.4036
27 | 11 kV20/28 MVA Transformer-3 | 11 |  | BD001927 | 1 | 1997.67 | 2037.6981 | 40.0281 | 160000 | 6404496 |  | 6409480.4525 |  | 1665600
36 | 11 kV 20/28 MVA Transformer-4 | 11 |  | BD001927 | 1 | 1919.54 | 1949.16 | 29.62 | 160000 | 4739200 |  | 4742888.396 |  | 1665600
[6 empty] | 0 | 0 |  | Total | 26882896 |  | 26903818.2582
| SHYAMPUR 11 kV SIDE |  |  |  |  | 0 | 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur |  | 1 | 625.64 | 667.28 | 41.64 | 40000 |  | 1665600 | 1658511.8396 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1658511.8396 | 1848660.4463 | -190148.6067 | -10.2858 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | 11 |  | BD001943 | 1 | 1043.7 | 1058.93 | 15.23 | 40000 |  | 609200 | 606607.4764 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 606607.4764 | 536986.5578 | 69620.9185 | 12.9651 | OK
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1527.03 | 1547.42 | 20.39 | 40000 |  | 815600 | 812129.1164 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 812129.1164 | 684264.5087 | 127864.6077 | 18.6864 | OK
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1416.53 | 1435.24 | 18.71 | 40000 |  | 748400 | 745215.0941 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 745215.0941 | 653846.0494 | 91369.0447 | 13.9741 | OK
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1313.82 | 1338.71 | 24.89 | 40000 |  | 995600 | 991363.1049 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 991363.1049 | 1100803.9423 | -109440.8375 | -9.9419 | OK
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3283.24 | 3340.76 | 57.52 | 40000 |  | 2300800 | 2291008.6698 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2291008.6698 | 1731865.3068 | 559143.363 | 32.2856 | OK
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2133.5 | 2175.85 | 42.35 | 40000 |  | 1694000 | 1686790.98 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1686790.98 | 1265223.6985 | 421567.2815 | 33.3196 | OK
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 486.4 | 489.6 | 3.2 | 40000 |  | 128000 | 127455.2807 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 127455.2807 | 91577.1387 | 35878.142 | 39.1781 | OK
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3122.73 | 3177.03 | 54.3 | 40000 |  | 2172000 | 2162756.7937 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 2162756.7937 | 1853587.4081 | 309169.3855 | 16.6795 | OK
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1944.14 | 1979.03 | 34.89 | 40000 |  | 1395600 | 1389660.8569 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1389660.8569 | 915888.0248 | 473772.8321 | 51.7282 | FAULT
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1444.14 | 1487.49 | 43.35 | 40000 |  | 1734000 | 1726620.7552 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1726620.7552 | 1517234.7817 | 209385.9735 | 13.8005 | OK
20 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 820.21 | 839.09 | 18.88 | 40000 |  | 755200 | 751986.1559 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 751986.1559 | 501987.0295 | 249999.1264 | 49.8019 | FAULT
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1313.8 | 1332.96 | 19.16 | 40000 |  | 766400 | 763138.4929 | Shyampur |  |  |  | 11 kV Delpara Feeder | 763138.4929 | 788989.597 | -25851.1041 | -3.2765 | OK
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2984.83 | 3058.77 | 73.94 | 40000 |  | 2957600 | 2945013.5787 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2945013.5787 | 2827927.2998 | 117086.279 | 4.1404 | OK
24 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1102.63 | 1108.33 | 5.7 | 40000 |  | 228000 | 227029.7187 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 227029.7187 | 174848.8273 | 52180.8914 | 29.8434 | OK
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1946.25 | 1984.95 | 38.7 | 40000 |  | 1548000 | 1541412.3005 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1541412.3005 | 1200352.7042 | 341059.5963 | 28.4133 | OK
28 | 11 kV Spare Feeder | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1349.95 | 1370.24 | 20.29 | 40000 |  | 811600 | 808146.1389 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 808146.1389 | 598969.7492 | 209176.3897 | 34.9227 | OK
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1323.77 | 1347.53 | 23.76 | 40000 |  | 950400 | 946355.4589 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 946355.4589 | 931203.8377 | 15151.6212 | 1.6271 | OK
31 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2236.38 | 2276.03 | 39.65 | 40000 |  | 1586000 | 1579250.5869 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1579250.5869 | 1494594.8892 | 84655.6978 | 5.6641 | OK
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 172.64 | 174.71 | 2.07 | 40000 |  | 82800 | 82447.6347 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 82447.6347 | 75834.9927 | 6612.642 | 8.7198 | OK
37 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1189.74 | 1212.54 | 22.8 | 40000 |  | 912000 | 908118.8747 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 908118.8747 | 695610.598 | 212508.2766 | 30.5499 | OK
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3687.08 | 3727.77 | 40.69 | 40000 |  | 1627600 | 1620673.5531 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 1620673.5531 | 2160897.1026 | -540223.5495 | -25 | OK
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1095.43 | 1108.79 | 13.36 | 40000 |  | 534400 | 532125.7967 | Shyampur |  |  |  | 11 kV Igloo Feeder | 532125.7967 | 778413.3204 | -246287.5236 | -31.6397 | OK
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 63890 | 64345 | 455 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 |  |  | 1 | 594876 | 603513 | 8637 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 26903818.2582 | 27018800 | 26903818.2582 | -0.42556
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 1118818.3855
[5 empty] | Shyampur | at 33 KV level |  | 25784999.8727
[5 empty] | Total = |  |  | 26903818.2582 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2542.812 | 2577.923 | 35.111 | 240000 | 0 | 8595172.8 | 8596034.9201
23 | 33 kV Shyampur BSCIC-2. | 33 |  | BD001827 | 1 | 2462.895 | 2504.226 | 41.331 | 240000 | 0 | 9919440 | 9920434.9478
[9 empty] | Total | 0 | 18514612.8 | 18516469.8679
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 | 33 | Import | DHK61071 | 1 | 916104.6 | 916104.6 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-2 | 33 | Import | DHK61067 | 1 | 710976.9 | 710976.9 | 0 | 270 | 0
[6 empty] | 0 | 0 |  | Total | 0 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33 kV 20/28 MVA Transformer-1 | 33 | Export | DHK61068 | 1 | 887669.7 | 887669.7 | 0 | 180 |  | 0
3 | 33 kV 20/28 MVA Transformer-2 | 33 | Export | DHK61066 | 1 | 560787.9 | 560787.9 | 0 | 180 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 18516469.8679 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18516469.8679
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 18516469.8679 |  | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 18516469.8679
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 18516469.8679
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK61019 | 1.05 | 987931.5 | 1019950.7 | 32019.2 | 180 | 6051628.8 |  | 6992516.4701 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK61018 | 1 | 683096.1 | 738503.5 | 55407.4 | 180 | 9973332 |  | 11523953.3978
[6 empty] | 0 | 0 |  | Total | 16024960.8 |  | 18516469.8679
| SHYAMPUR BISIC 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 37882493 | 40168290 | 2285797 | 1 |  | 2285797 | 2242087.5527 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 2242087.5527 | 2142439.5507 | 99648.0019 | 4.6511 | OK
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 21288823 | 22086911 | 798088 | 1 |  | 798088 | 782826.8086 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 782826.8086 | 745206.3758 | 37620.4329 | 5.0483 | OK
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 437001.6 | 469630.5 | 32628.9 | 60 |  | 1957734 | 1920297.8361 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1920297.8361 | 1596859.747 | 323438.089 | 20.2546 | OK
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 593952.2 | 619977.8 | 26025.6 | 60 |  | 1561536 | 1531676.01 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1531676.01 | 1098969.809 | 432706.201 | 39.3738 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 615565.9 | 639408.3 | 23842.4 | 60 |  | 1430544 | 1403188.8641 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1403188.8641 | 1231235.1282 | 171953.7359 | 13.966 | OK
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 351956.3 | 371675.9 | 19719.6 | 60 |  | 1183176 | 1160551.0823 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1160551.0823 | 887582.2839 | 272968.7984 | 30.7542 | OK
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 518004.2 | 518057.4 | 53.2 | 60 |  | 3192 | 3130.962 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 3130.962 | 385792.207 | -382661.2451 | -99.1884 | CHECK
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 871854.9 | 919765.2 | 47910.3 | 60 |  | 2874618 | 2819649.0049 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2819649.0049 | 2794077.3284 | 25571.6765 | 0.91521 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 256885.3 | 282858.7 | 25973.4 | 60 |  | 1558404 | 1528603.9007 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1528603.9007 | 1237892.1591 | 290711.7416 | 23.4844 | OK
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 455733.9 | 466710.5 | 10976.6 | 60 |  | 658596 | 646002.2013 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 646002.2013 | 711159.0569 | -65156.8555 | -9.1621 | OK
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 526918.2 | 571905.4 | 44987.2 | 60 |  | 2699232 | 2647616.7695 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2647616.7695 | 2636452.1751 | 11164.5944 | 0.42347 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 856542.9 | 869895.1 | 13352.2 | 60 |  | 801132 | 785812.6007 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 785812.6007 | 661368.2767 | 124444.324 | 18.8162 | OK
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 960702.2 | 984688.2 | 23986 | 60 |  | 1439160 | 1411640.1073 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1411640.1073 | 1301431.6729 | 110208.4344 | 8.4682 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB7380 | 1 | 608485 | 612273 | 3788 | 1 |  | 3788 | 3715.5651 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3715.5651 | 3553.7906 | 161.7745 | 4.5522 | OK
[9 empty] | Grand Total | 18886799.2653 | 19254997 | 18886799.2653 | -1.9122
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 6346598.208
[5 empty] | Jurain | at 33 KV level |  | 12540201.0572
[5 empty] | Total = |  |  | 18886799.2653 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1278.1529 | 1307.8 | 29.6471 | 240000 | From Downstream | 7115304 | 7116017.6851
7 | 33 kV Nondolalpur -2 feeder | 33 |  | BD001807 | 1 | 1108.057 | 1133.3769 | 25.3199 | 240000 | 0 | 6076776 | 6077385.5178
[9 empty] | Total | 0 | 13192080 | 13193403.2028
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) | 33 | Import | 00000084 | 1 | 306721216 | 313854016 | 7132800 | 1 | 7132800
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) | 33 | Import | 00000070 | 1 | 286460160 | 292555456 | 6095296 | 1 | 6095296
[6 empty] | 0 | 0 |  | Total | 13228096 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| NANDALALPUR 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33 kV, 28/35 MVA T-1 | 33 | Export | 00000086 | 1 | 306919264 | 314048064 | 7128800 | 1 |  | 7128800
5 | 33 kV, 28/35 MVA T-2 | 33 | Export | 00000083 | 1 | 285906784 | 291998784 | 6092000 | 1 |  | 6092000
[9 empty] | Total |  | 13220800 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 13193403.2028 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 13193403.2028
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 13193403.2028 |  | 33 KV TX HV SIDE |  | 13220800
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -27396.7972
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.2077%
| TOTAL IMPORT |  | 13193403.2028
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. | 11 |  | 00000036 | 1 | 305067744 | 312165152 | 7097408 | 1 | 7097408 |  | 7113364.5704 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000033 | 1 | 284663936 | 290730336 | 6066400 | 1 | 6066400 |  | 6080038.6324
[6 empty] | 0 | 0 |  | Total | 13163808 |  | 13193403.2028
| NANDALALPUR 11 KV SIDE |  |  |  |  | 0 | 0 | [7 empty] | 75
8 | 11 kV Spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  | 50 |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | 11 |  | 00000026 | 1 | 5408547 | 6089905 | 681358 | 1 |  | 681358 | 682477.6462 | Fatullah |  | 25 |  | 11 kV Khaza Moinuddin | 682477.6462 | 727695.4191 | -45217.7729 | -6.2138 | OK
10 | 11 kV Chitashal | 11 |  | 00000027 | 1 | 33243638 | 33982516 | 738878 | 1 |  | 738878 | 740092.1663 | Shyampur |  | 8.3333 |  | 11 kV Chitashal | 740092.1663 | 801503.5058 | -61411.3394 | -7.662 | OK
11 | 11 kV Local Feeder | 11 |  | 00000157 | 1.5 | 18439474 | 18644914 | 205440 | 1 | Estimated | 668980.62 | 670079.927 | Shyampur | 55 | 58.3333 |  | 11 kV Local Feeder | 670079.927 | 673810.7719 | -3730.8449 | -0.55369 | OK
12 | 11 kV Rasel Germants | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 |  | 00000121 | 1 | 73062544 | 75768256 | 2705712 | 1 |  | 2705712 | 2710158.1798 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2710158.1798 | 2342109.1991 | 368048.9808 | 15.7144 | OK
14 | 11 kV Nandalalpur | 11 |  | 00000010 | 1 | 83856192 | 84598432 | 742240 | 1 |  | 742240 | 743459.691 | Fatullah |  |  |  | 11 kV Nandalalpur | 743459.691 | 869061.7913 | -125602.1003 | -14.4526 | OK
15 | 11 kV Sharif Bagh | 11 |  | 00000132 | 1 | 71968184 | 73572944 | 1604760 | 1 |  | 1604760 | 1607397.0329 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1607397.0329 | 1797879.9406 | -190482.9077 | -10.5949 | OK
18 | 11 kV Spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | 11 |  | 00000158 | 1 | 65089840 | 66248080 | 1158240 | 1 |  | 1158240 | 1160143.2858 | Fatullah |  |  |  | 11 KV Nayamati | 1160143.2858 | 1059913.8974 | 100229.3884 | 9.4564 | OK
20 | 11 kV Pulpar | 11 |  | 00000160 | 1 | 7628741 | 8533019 | 904278 | 1 |  | 904278 | 905763.961 | Fatullah |  |  |  | 11 kV Pulpar | 905763.961 | 653442.1412 | 252321.8198 | 38.6143 | OK
21 | 11 kV Shahi Bazar | 11 |  | 00000170 | 1 | 40882420 | 41765220 | 882800 | 1 |  | 882800 | 884250.6672 | Shyampur |  |  |  | 11 kV Shahi Bazar | 884250.6672 | 830388.5657 | 53862.1014 | 6.4864 | OK
22 | 11 kV Pagla Bazar | 11 |  | 00000060 | 1 | 50196196 | 50898636 | 702440 | 1 |  | 702440 | 703594.2894 | Fatullah |  |  |  | 11 kV Pagla Bazar | 703594.2894 | 679748.7175 | 23845.5718 | 3.508 | OK
23 | 11 kV Delpara bazar | 11 |  | 00000063 | 1 | 79142768 | 80808200 | 1665432 | 1 |  | 1665432 | 1668168.7326 | Shyampur |  |  |  | 11 kV Delpara bazar | 1668168.7326 | 1521265.0516 | 146903.6809 | 9.6567 | OK
24 | 11 kV Bhuighor (Board mill) | 11 |  | 00000146 | 1 | 43749012 | 44459652 | 710640 | 1 |  | 710640 | 711807.7641 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 711807.7641 | 702632.7597 | 9175.0043 | 1.3058 | OK
25 | 11 kV Spare | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 | 11 |  | 7803 | 1 | 2435 | 2494 | 59 | 100 |  | 5900 | 5909.6952 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 5909.6952 | 6446.2091 | -536.5139 | -8.3229 | OK
27 | 33/0.415 kV, 200 kVA AT-2 | 11 |  | 7805 | 1 | 51 | 52 | 1 | 100 | 100 | 100 | 100.1643 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 100.1643 | 0 | 100.1643 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 13193403.2028 | 13171758.62 | 13193403.2028 | 0.16433
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5575998.3855
[5 empty] | Fatullah | at 33 KV level |  | 4195438.8734
[5 empty] | Matuail | at 33 KV level |  | 3421965.9439
[5 empty] | Total = |  |  | 13193403.2028 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 | 132 | Import | 4262 7826 | 1 | 289.542 | 319.579 | 30.037 | 960000 | 0 | 28835520
[5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 | 132 |  | 4262 7815 | 1 | 133.648 | 142.531 | 8.883 | 960000 | 0 | 8527680
2 |  |  |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 37363200
[9 empty] | Net Total | 37363200
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 | 132 | Main | 41808902823 | 1 | 231.42 | 255.47 | 24.05 | 1200000 | 28860000
|  | 132 | Backup | 41808904269 | 1 | 231.42 | 255.47 | 24.05 | 1200000 | 28860000
4 | 132kV Hasnabad Circuit-2 | 132 | Imp/Main | 41808902845 | 1 | 106.82 | 113.93 | 7.11 | 1200000 | 8532000
|  | 132 | Imp/Backup | 41808904256 | 1 | 106.82 | 113.93 | 7.11 | 1200000 | 8532000
[6 empty] | 0 | 0 | Total Import/Export |  | 37392000 | 0
[6 empty] | 0 | 0 | Net Total |  | 37392000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 132 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
| POSTOGOLA 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41808902871 | 1 | 242.57 | 266.61 | 24.04 | 1200000 |  | 28848000
|  | 132 | Exp/Backup | 41808904257 | 1 | 242.57 | 266.61 | 24.04 | 1200000 |  | 28848000
5 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41808902846 | 1 | 95.54 | 102.63 | 7.09 | 1200000 |  | 8508000
|  | 132 | Exp/Backup | 41808904243 | 1 | 95.54 | 102.63 | 7.09 | 1200000 |  | 8508000
[9 empty] | Total |  | 37356000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 37363200 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 37363200
[5 empty] | 132 KV NET IMPORT |  |  | 37363200 |  | 33 KV NET IMPORT |  | 37238400
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 124800
[10 empty] | LOSS % IN => |  | 0.334%
| 132 KV TOTAL IMPORT |  | 37363200
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE | [7 empty] | Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41808902807 | 1 | 402.85 | 442.79 | 39.94 | 720000 | 28756800
|  | 33 | Backup | 41808904286 | 1 | 402.85 | 442.79 | 39.94 | 720000 | 28756800
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41808902869 | 1 | 158.14 | 169.92 | 11.78 | 720000 | 8481600
|  | 33 | Backup | 41808904268 | 1 | 158.14 | 169.92 | 11.78 | 720000 | 8481600
[6 empty] | 0 | 0 |  | Total | 37238400 |  | 0
| POSTOGOLA 33 kV SIDE |  |  |  |  | 0 | 0
| 33/11 KV Transforfers |  | EXPORT |  |  | 0 | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss |  | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  |  |  |  | 0 | 0 |  | Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 391.16 | 419.45 | 28.29 | 360000 |  | 10184400 | 10179479.5246 |  | 18667776.5195 | IG Gate 33/11 kv ss |  | 33 kV IG Gate Ckt-2 | 10179479.5246 | 9983380.2238 | 196099.3008 | 1.9643 | OK
|  | 33 | Backup | 41808904225 | 1 | 391.16 | 419.45 | 28.29 | 360000 |  | 10184400 | 10179479.5246 |  |  |  |  | 0 | 10179479.5246 | 9983380.2238 | 196099.3008 | 1.9643 | OK
8 | 33 kV Spare Feeder 2 | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 | 33 | Main | 41808902810 | 1 | 415.21 | 466.82 | 51.61 | 360000 |  | 18579600 | 18570623.4805 |  |  |  |  | 33kV Postogola circuit-1 | 18570623.4805 | 17760627.7593 | 809995.7212 | 4.5606 | OK
|  | 33 | Backup | 41808904252 | 1 | 415.21 | 466.82 | 51.61 | 360000 |  | 18579600 | 18570623.4805 |  |  |  |  | 0 | 18570623.4805 | 17760627.7593 | 809995.7212 | 4.5606 | OK
14 | 31 kV Spare Feeder 4 | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 315.79 | 339.38 | 23.59 | 360000 |  | 8492400 | 8488296.9949 |  |  |  |  | 33 kV IG Gate Ckt-1 | 8488296.9949 | 7960792.0169 | 527504.9779 | 6.6263 | OK
|  | 33 | Backup | 41812909573 | 1 | 315.79 | 339.38 | 23.59 | 360000 |  | 8492400 | 8488296.9949 |  |  |  |  | 0 | 8488296.9949 | 7960792.0169 | 527504.9779 | 6.6263 | OK
[9 empty] | Total |  | 37256400 | 37238400 |  |  |  |  | 0 | 37238400 | 35704800 | 1533600 | 4.2952 | OK
[8 empty] | Grand Total |  | 37238400 | 37256400 | 37238400 | -0.048314
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola | 33 | Import | BD001804 | 1 | 415.21 | 466.82 | 51.61 | 360000 | 18579600 |  | 18570623.4805
2 | 33 kV Postogola Circuit-2 at Shyampur | 33 | Import | BD001830 | 1 | 2131.894 | 2131.8959 | 0.0019 | 240000 | 456 |  | 456.0457
[6 empty] | 0 | 0 |  | Total | 18580056 |  | 18571079.5263
| POSTOGOLA 33 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
[6 empty] | 0 | 0 |  | Total | 0
| POSTOGOLA 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK61027 | 1 | 244625.8 | 288675.6 | 44049.8 | 180 |  | 7928964 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60870 | 1 | 671327.3 | 729592.8 | 58265.5 | 180 |  | 10487790
[6 empty] | 0 | 0 |  | Total |  | 18416754
| POSTOGOLA 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV 20/28 MVA T-1 Incoming. | 11 |  | DHK61005 | 1.165 | 837889.7 | 877082.3 | 39192.6 | 180 | 8218688.22 |  | 8205108.1928 |  | 36833508
9 | 11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK60861 | 1.165 | 889449.5 | 938963.7 | 49514.2 | 180 | 10383127.74 |  | 10365971.3334
[6 empty] | 0 | 0 |  | Total | 18601815.96 |  | 18571079.5263
| POSTOGOLA 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 62369777 | 63585293 | 1215516 | 1 |  | 1215516 | 1219095.1394 | Postogola |  |  |  | 11 kV Station Road Feeder | 1219095.1394 | 1335055.4691 | -115960.3297 | -8.6858 | OK
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 9710567 | 10944921 | 1234354 | 1 | Converted to 31 days | 1319481.8621 | 1323367.1334 | Jurain | 1234354 |  |  | 11 kV Samon & Sons Feeder. | 1323367.1334 | 1374189.6942 | -50822.5608 | -3.6984 | OK
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 24070248 | 24605728 | 535480 | 1 |  | 535480 | 537056.744 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 537056.744 | 474949.556 | 62107.188 | 13.0766 | OK
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 74369662 | 75922520 | 1552858 | 1 |  | 1552858 | 1557430.4575 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1557430.4575 | 1587221.6201 | -29791.1627 | -1.8769 | OK
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 428700.2 | 439711.4 | 11011.2 | 60 |  | 660672 | 662617.3772 | Postogola |  |  |  | 11 kV Cyca Feeder | 662617.3772 | 636891.4703 | 25725.9069 | 4.0393 | OK
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 866598.9 | 885538.7 | 18939.8 | 60 |  | 1136388 | 1139734.1436 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 1139734.1436 | 1267305.3443 | -127571.2007 | -10.0663 | OK
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 747895 | 771487.6 | 23592.6 | 60 |  | 1415556 | 1419724.1658 | Postogola |  |  |  | 11 kV Munshi Bari | 1419724.1658 | 1247409.4401 | 172314.7257 | 13.8138 | OK
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 520016 | 522254.7 | 2238.7 | 60 |  | 134322 | 134717.5169 | Postogola |  |  |  | 11 kV Cantonment Feeder | 134717.5169 | 129509.8262 | 5207.6907 | 4.0211 | OK
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 837075.6 | 859898.8 | 22823.2 | 60 |  | 1369392 | 1373424.2339 | Postogola |  |  |  | 11 kV DIT Feeder. | 1373424.2339 | 1052907.1287 | 320517.1052 | 30.4412 | OK
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 324272.2 | 364927.9 | 40655.7 | 60 |  | 2439342 | 2446524.7479 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 2446524.7479 | 2443876.2234 | 2648.5245 | 0.10837 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 38603647 | 40818183 | 2214536 | 1 |  | 2214536 | 2221056.7969 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 2221056.7969 | 2061497.5542 | 159559.2427 | 7.74 | OK
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 8284 | 10753.8 | 2469.8 | 1000 |  | 2469800 | 2477072.4328 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2477072.4328 | 2360182.711 | 116889.7218 | 4.9526 | OK
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 56071015 | 57721254 | 1650239 | 1 |  | 1650239 | 1655098.2 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1655098.2 | 1632466.5583 | 22631.6418 | 1.3863 | OK
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 53216071 | 53444745 | 228674 | 1 | Converted to 31 days | 244444.6207 | 245164.3984 | Postogola | 228674 |  |  | 11 kV Rajabari Feeder. | 245164.3984 | 245637.4316 | -473.0331 | -0.19257 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 |  | ELIB67385 | 1 | 368.64 | 426.85 | 58.21 | 80 |  | 4656.8 | 4670.5121 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 4670.5121 | 4307.9725 | 362.5397 | 8.4156 | OK
[9 empty] | Total | 18416754 | 18362684.2828 | 18416754 | 0.29445
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Postogola | at 33 KV level |  | 9411676.1449
[5 empty] | Jurain | at 33 KV level |  | 9005077.8551
[5 empty] | Total = |  |  | 18416754 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 | 0 | 0 | 0
| Postogola 33 KV SIDE | [7 empty] | Total | 0 | 0 | 0
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 391.16 | 419.45 | 28.29 | 360000 | 0 | 10184400 | 10179479.5246
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 315.79 | 339.38 | 23.59 | 360000 | 0 | 8492400 | 8488296.9949
[9 empty] | Total | 0 | 18676800 | 18667776.5195
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 | 33 | Import | DHK60973 | 1 | 264626 | 280426.9 | 15800.9 | 540 | 8532486
6 | 33 kV Postogola Incoming Feeder-2 | 33 | Import | DHK60966 | 1 | 443595.2 | 462550.7 | 18955.5 | 540 | 10235970
[6 empty] | 0 | 0 |  | Total | 18768456 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  |  | 0 | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  | 0 | 0 |  |  |  | 0
[6 empty] | 0 | 0 |  | Total |  | 0
[6 empty] | 0 | 0
| IG GATE 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK60893 | 1 | 758595.6 | 805945.3 | 47349.7 | 180 |  | 8522946
5 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60975 | 1 | 364510.9 | 421347.7 | 56836.8 | 180 |  | 10230624
[9 empty] | Total |  | 18753570
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 18667776.5195 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18667776.5195
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 18667776.5195 |  | 33 KV TX HV SIDE |  | 18753570
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -85793.4805
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.4596%
| TOTAL IMPORT |  | 18667776.5195
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month August-2023 |  |  | Name of Feeders. | Month August-2023 | Month July-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK68139 | 1 | 3699.05 | 3745.62 | 46.57 | 180000 | 8382600 |  | 8644310.9527 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK68137 | 1 | 4321.03 | 4375.03 | 54 | 180000 | 9720000 |  | 10023465.5668
[6 empty] | 0 | 0 |  | Total | 18102600 |  | 18667776.5195
| IG GATE 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Feeder-1 | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | 11 |  | DHK60970 | 1 | 223582.9 | 261150.8 | 37567.9 | 60 |  | 2254074 | 2258178.5414 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 2258178.5414 | 2013206.2605 | 244972.2809 | 12.1683 | OK
4 | 11 kV Alom Gonj | 11 |  | DHK60894 | 1 | 479815.2 | 491074.8 | 11259.6 | 60 |  | 675576 | 676806.1857 | Postogola |  |  |  | 11 kV Alom Gonj | 676806.1857 | 596654.2301 | 80151.9556 | 13.4336 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 |  | DHK60895 | 1 | 536337.9 | 567540.5 | 31202.6 | 60 |  | 1872156 | 1875565.0903 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1875565.0903 | 1850628.0181 | 24937.0722 | 1.3475 | OK
6 | 11 kV Farashgonj Feeder (F-6) | 11 |  | DHK68133 | 1 | 3589.15 | 3623.21 | 34.06 | 60000 |  | 2043600 | 2047321.2801 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 2047321.2801 | 1803939.5949 | 243381.6852 | 13.4917 | OK
7 | 11 kV Doyaganj | 11 |  | DHK68134 | 1 | 2380.418 | 2414.18 | 33.762 | 60000 | Estimated | 1642043.34 | 1645033.4081 | Swamibag | 135 |  |  | 11 kV Doyaganj | 1645033.4081 | 1687142.9696 | -42109.5615 | -2.4959 | OK
10 | 11 kV Faridabad | 11 |  | DHK68140 | 1 | 772.95 | 796.44 | 23.49 | 60000 |  | 1409400 | 1411966.4378 | Postogola |  |  |  | 11 kV Faridabad | 1411966.4378 | 1296128.1808 | 115838.257 | 8.9373 | OK
11 | 11 kV Gandaria | 11 |  | DHK60969 | 1 | 372411.9 | 407296.5 | 34884.6 | 60 |  | 2093076 | 2096887.3731 | Postogola |  |  |  | 11 kV Gandaria | 2096887.3731 | 2186472.7241 | -89585.3509 | -4.0973 | OK
12 | 11 kV Walter Road | 11 |  | DHK68136 | 1 | 973.45 | 998.43 | 24.98 | 60000 |  | 1498800 | 1501529.2301 | Banglabazar |  |  |  | 11 kV Walter Road | 1501529.2301 | 1391040.5522 | 110488.6779 | 7.9429 | OK
13 | 11 kV Murgitola Feeder (F-11) | 11 |  | DHK68138 | 1 | 3890.75 | 3930.95 | 40.2 | 60000 |  | 2412000 | 2416392.1157 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2416392.1157 | 2307519.2472 | 108872.8685 | 4.7182 | OK
14 | 11 kV Feeder-12 | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | 11 |  | DHK60899 | 1 | 667472.2 | 696216.8 | 28744.6 | 60 |  | 1724676 | 1727816.5375 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1727816.5375 | 1778252.8009 | -50436.2633 | -2.8363 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | 11 |  | DHK60967 | 1 | 166011.3 | 182818.7 | 16807.4 | 60 |  | 1008444 | 1010280.3195 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 1010280.3195 | 1031522.1618 | -21241.8422 | -2.0593 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB2774 | 1 | 279327 | 279327 | 0 | 1 |  | 0 | 0 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 1665.5005 | -1665.5005 | -100 | CHECK
[9 empty] | Grand Total | 18667776.5195 | 18633845.34 | 18667776.5195 | 0.18209
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Swamibag | at 33 KV level |  | 5789242.0614
[5 empty] | Banglabazar | at 33 KV level |  | 5807029.0516
[5 empty] | Postogola | at 33 KV level |  | 7071505.4064
[5 empty] | Total = |  |  | 18667776.5195 | 0
Note on I387: No Reading Due to PT Out
Note on K387: Reading From Higher Side
Note on I644: No Reading due to PT Open
Note on L644: Energy From Bangshal SS End
Note on L649: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Linked_11KV
SL | Feeder_Name | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | July23_Consumption | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 6440974 | 7753091 | 1312117 | 1 | 0 | 1312117 | 1314371.1616 | Paribag | Dhanmondi 33/11KV S/S | 1273734.3863 | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | 11 | 0 | HA021100463-02 | 1 | 47694141 | 49253485 | 1559344 | 1 | 0 | 1559344 | 1562022.8871 | Paribag | Dhanmondi 33/11KV S/S | 1571851.4764 | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | 11 | 0 | HA021101078-02 | 1 | 61262551 | 63457175 | 2194624 | 1 | 0 | 2194624 | 2198394.2713 | Paribag | Dhanmondi 33/11KV S/S | 2202528.7234 | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | 11 | 0 | DHK60882 | 1 | 215574 | 222720.32 | 7146.32 | 60 | 0 | 428779.2 | 429515.8245 | Paribag | Dhanmondi 33/11KV S/S | 406161.3393 | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | 11 | 0 | DHK60889 | 1 | 283084.6 | 287093.97 | 4009.37 | 60 | 0 | 240562.2 | 240975.4757 | Paribag | Dhanmondi 33/11KV S/S | 236479.8549 | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 11 | 0 | DHK60890 | 1 | 699.41 | 706.8 | 7.39 | 60000 | 0 | 443400 | 444161.7425 | Paribag | Dhanmondi 33/11KV S/S | 451511.4107 | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | 11 | 0 | DHK60880 | 1 | 552176.6 | 564493.19 | 12316.59 | 60 | 0 | 738995.4 | 740264.9629 | Ramna | Dhanmondi 33/11KV S/S | 797710.3468 | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0 | 0 | 0
9 | 11 kV TSC Feeder | 11 | 0 | DHK60873 | 1 | 928405.7 | 938763.25 | 10357.55 | 60 | 0 | 621453 | 622520.63 | Ramna | Dhanmondi 33/11KV S/S | 596411.0072 | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | 11 | 0 | DHK60883 | 1 | 28176.9 | 28300.61 | 123.71 | 60 | 0 | 7422.6 | 7435.3517 | Paribag | Dhanmondi 33/11KV S/S | 6184.9227 | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 11 | 0 | DHK60871 | 1 | 493864.3 | 513287.05 | 19422.75 | 60 | 0 | 1165365 | 1167367.0478 | Paribag | Dhanmondi 33/11KV S/S | 1168612.8044 | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | 11 | 0 | DHK60981 | 1 | 82214.7 | 100470.64 | 18255.94 | 60 | 0 | 1095356.4 | 1097238.176 | Paribag | Dhanmondi 33/11KV S/S | 1271574.285 | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | 11 | 0 | DHK61110 | 1 | 404842.1 | 430127.06 | 25284.96 | 60 | 0 | 1517097.6 | 1519703.9096 | Paribag | Dhanmondi 33/11KV S/S | 1444426.5973 | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 11 | 0 | DHK61115 | 1 | 340916.2 | 369960.07 | 29043.87 | 60 | 0 | 1742632.2 | 1745625.9685 | Paribag | Dhanmondi 33/11KV S/S | 1732224.4313 | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | 11 | 0 | DHK61107 | 1 | 547755.5 | 550080.6 | 2325.1 | 60 | 0 | 139506 | 139745.6654 | Ramna | Dhanmondi 33/11KV S/S | 147111.9421 | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 11 | 0 | DHK61112 | 1 | 342098.2 | 345525.51 | 3427.31 | 60 | 0 | 205638.6 | 205991.8784 | Paribag | Dhanmondi 33/11KV S/S | 207014.0635 | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | 11 | 0 | DHK61108 | 1 | 701416.8 | 716987.97 | 15571.17 | 60 | 0 | 934270.2 | 935875.2367 | Kakrail | Dhanmondi 33/11KV S/S | 955769.4815 | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0 | 0 | 0
19 | 11 kV DPH Sw/S-1 | 11 | 0 | DHK60978 | 1 | 782449.9 | 797585.77 | 15135.87 | 60 | 0 | 908152.2 | 909712.3671 | Kakrail | Dhanmondi 33/11KV S/S | 894673.7786 | 964542.5031 | 717844.627
20 | WASA Bhaban | 11 | 0 | 8536188 | 1.18 | 2503.3 | 271216 | 268712.7 | 1000 | 1024440 | 1024440 | 1031848.2658 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1051553.1772 | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 11 | 0 | 8536178 | 1.18 | 572139 | 576073 | 3934 | 44 | 0 | 204253.28 | 205730.3432 | Shere b.nagar | Kawranbazar 33/11KV S/S | 203697.4272 | 26163.5003 | 291323.9838
22 | Air Port Road (West) | 11 | 0 | 8536182 | 1.18 | 1503.6 | 2353.2 | 849.6 | 1000 | 0 | 1002528 | 1009777.8086 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1128128.4372 | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | 11 | 0 | 8536193 | 1.18 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0 | 0 | 0
24 | (UTC) Tower | 11 | 0 | DHK00183 | 1.18 | 15757.4 | 16418.4 | 661 | 444.44 | 0 | 346654.3112 | 349161.1513 | Shere b.nagar | Kawranbazar 33/11KV S/S | 363430.7232 | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | 11 | 0 | 8536190 | 1.18 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 109995.2784 | 110790.7123 | Kakrail | Kawranbazar 33/11KV S/S | 63163.9823 | 0 | 0
26 | Panthopath | 11 | 0 | 8536184 | 1.18 | 35309.1 | 36316 | 1006.9 | 1000 | 0 | 1188142 | 1196734.0813 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1204221.3334 | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | 11 | 0 | DHK00190 | 1.18 | 55753.9 | 56134 | 380.1 | 444.44 | 0 | 199339.3399 | 200780.8678 | Kakrail | Kawranbazar 33/11KV S/S | 155748.3677 | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 11 | 0 | DHK00021 | 1.18 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 0 | 0 | 0
29 | Aux. Transformer, AT-1 | 11 | 0 | 85-12906 | 1.18 | 68557 | 68801 | 244 | 10 | 0 | 2879.2 | 2900.021 | Shere b.nagar | Kawranbazar 33/11KV S/S | 3641.847 | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 11 | 0 | 85-12909 | 1.18 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0 | 0 | 0
31 | Police Bhaban | 11 | 0 | DHK 00005 | 1 | 73369.4 | 73629.9 | 260.5 | 444.44 | 0 | 115776.62 | 117855.6107 | Ramna | New Ramna 33/11KV S/S | 121266.9463 | 121013.0538 | 111715.2077
32 | Water Works | 11 | 0 | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Lalbag | New Ramna 33/11KV S/S | 0 | 0 | 0
33 | GPO | 11 | 0 | DHK 00060 | 1 | 98412.6 | 98961 | 548.4 | 444.44 | 0 | 243730.896 | 248107.5506 | Ramna | New Ramna 33/11KV S/S | 224260.1714 | 278965.4908 | 233730.721
34 | Culvert Road | 11 | 0 | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 85 | 1033879.14 | 1052444.418 | Ramna | New Ramna 33/11KV S/S | 990314.9211 | 787025.6832 | 769934.2629
35 | Secretariat (East) | 11 | 0 | DHK00059 | 1 | 81723.1 | 81725.2 | 2.1 | 444.44 | 0 | 933.324 | 950.0836 | Ramna | New Ramna 33/11KV S/S | 1673.5834 | 2240.1359 | 29358.1395
36 | Siddik Bazar | 11 | 0 | DHK00076 | 1 | 30335.3 | 33421.2 | 3085.9 | 444.44 | 0 | 1371497.396 | 1396125.2558 | Bangshal | New Ramna 33/11KV S/S | 499406.3237 | 894134.2296 | 765262.7858
37 | Bokshi Bazar | 11 | 0 | DHK 00206 | 1 | 86520.6 | 87765.4 | 1244.8 | 444.44 | 0 | 553238.912 | 563173.3752 | Ramna | New Ramna 33/11KV S/S | 477921.1318 | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 11 | 0 | DHK00198 | 1 | 46678.5 | 47830.6 | 1152.1 | 444.44 | 0 | 512039.324 | 521233.9697 | Ramna | New Ramna 33/11KV S/S | 36728.3702 | 1058898.5083 | 1085933.5304
39 | TNT RMU | 11 | 0 | DHK 00207 | 1 | 61321.1 | 62258.6 | 937.5 | 444.44 | 0 | 416662.5 | 424144.4724 | Ramna | New Ramna 33/11KV S/S | 438569.3066 | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 11 | 0 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 0 | 0 | 35665.375
41 | Secretariat (West) | 11 | 0 | DHK 00006 | 1 | 69075.5 | 70229.9 | 1154.4 | 444.44 | 0 | 513061.536 | 522274.5375 | Ramna | New Ramna 33/11KV S/S | 534325.4145 | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00197 | 1 | 86438.2 | 89193.3 | 2755.1 | 444.44 | 0 | 1224476.644 | 1246464.4649 | Ramna | New Ramna 33/11KV S/S | 757545.2503 | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | 11 | 0 | DHK00186 | 1 | 27519.2 | 30378.4 | 2859.2 | 444.44 | 0 | 1270742.848 | 1293561.4671 | Ramna | New Ramna 33/11KV S/S | 1334026.873 | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | 11 | 0 | DHK00030 | 1 | 54911.6 | 55416.5 | 504.9 | 444.44 | 0 | 224397.756 | 228427.247 | Ramna | New Ramna 33/11KV S/S | 210464.4166 | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | 11 | 0 | DHK 00008 | 1 | 99993.3 | 100150.4 | 157.1 | 444.44 | 0 | 69821.524 | 71075.3031 | Ramna | New Ramna 33/11KV S/S | 68978.774 | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00196 | 1 | 26040.2 | 27096.1 | 1055.9 | 444.44 | 0 | 469284.196 | 477711.0916 | Motijheel | New Ramna 33/11KV S/S | 494476.0375 | 481492.0598 | 701782.0483
47 | Jail | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 0 | 0 | 0
48 | Kosturi Bazar | 11 | 0 | HA021100713-02 | 1 | 76731766 | 76840413 | 108647 | 1 | 0 | 108647 | 110597.9648 | Ramna | New Ramna 33/11KV S/S | 782852.0054 | 108530.1819 | 101993.6695
49 | Kaptan Bazar | 11 | 0 | HA021101251-02 | 1 | 6664226 | 7099755 | 435529 | 1 | 0 | 435529 | 443349.7565 | Narinda | New Ramna 33/11KV S/S | 434935.9868 | 427872.7434 | 409490.3581
50 | G.T.V | 11 | 0 | HA-021101054-02 | 1 | 71762722 | 72361607 | 598885 | 1 | 0 | 598885 | 609639.126 | Ramna | New Ramna 33/11KV S/S | 653967.7221 | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | 11 | 0 | HA021100951-02 | 1 | 6674283 | 7041683 | 367400 | 1 | 0 | 367400 | 373997.3699 | Bangshal | New Ramna 33/11KV S/S | 641935.1027 | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 | 0 | 2436 | 1 | 67423 | 67423 | 0 | 10 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 0 | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 | 0 | 2437 | 1 | 88807 | 89174 | 367 | 10 | 0 | 3670 | 3735.9019 | Ramna | New Ramna 33/11KV S/S | 3663.8273 | 3672.2594 | 3624.4279
54 | Pioneer | 11 | 0 | 06604395 | 1 | 23854.78 | 23959.84 | 105.06 | 8000 | 0 | 840480 | 850072.0555 | Ramna | Kakrail 33/11KV S/S | 872559.2 | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | 11 | 0 | DHK-00102 | 1 | 83183.5 | 86508.9 | 3325.4 | 444.444 | 0 | 1477954.0776 | 1494821.3647 | Rajarbag | Kakrail 33/11KV S/S | 1589289.5218 | 1570646.0565 | 1456807.534
56 | Montri Para | 11 | 0 | DHK-00110 | 1 | 12700.2 | 12787.7 | 87.5 | 2222.22 | 0 | 194444.25 | 196663.3629 | Kakrail | Kakrail 33/11KV S/S | 206488.6824 | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 11 | 0 | 9119865 | 1 | 65421.2 | 67803.2 | 2382 | 1000 | 0 | 2382000 | 2409184.7946 | Kakrail | Kakrail 33/11KV S/S | 2711345 | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 0 | 0 | 0
59 | High Court | 11 | 0 | 1025651 | 1 | 29238.4 | 29559.9 | 321.5 | 1000 | 0 | 321500 | 325169.1484 | Ramna | Kakrail 33/11KV S/S | 265125 | 281963.0422 | 304725.5352
60 | Secretaiat | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 0 | 0 | 0
61 | Shanti Nagar Bazar | 11 | 0 | 06604402 | 1 | 5671.14 | 5708.48 | 37.34 | 40000 | 0 | 1493600 | 1510645.8477 | Rajarbag | Kakrail 33/11KV S/S | 1601052 | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 11 | 0 | 9119867 | 1 | 32298 | 32532.2 | 234.2 | 1000 | 0 | 234200 | 236872.8291 | Kakrail | Kakrail 33/11KV S/S | 224220 | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 11 | 0 | DHK00199 | 1 | 78681.8 | 78985.3 | 303.5 | 2222.22 | 0 | 674443.77 | 682140.9217 | Kakrail | Kakrail 33/11KV S/S | 703183.7413 | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 11 | 0 | DHK00027 | 1 | 55889.6 | 56427.3 | 537.7 | 2222.22 | 0 | 1194887.694 | 1208524.4599 | Kakrail | Kakrail 33/11KV S/S | 1467416.3104 | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | 11 | 0 | D1025656 | 1 | 66935.36 | 67951.3 | 1015.94 | 1000 | 0 | 1015940 | 1027534.5089 | Ramna | Kakrail 33/11KV S/S | 1059146.6 | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | 11 | 0 | D0086137 | 1 | 25965.1 | 26476.8 | 511.7 | 1000 | 0 | 511700 | 517539.8234 | Ramna | Kakrail 33/11KV S/S | 576508 | 916863.5723 | 907912.3538
67 | Judges Complex | 11 | 0 | 06604344 | 1 | 674.7 | 678.06 | 3.36 | 40000 | 0 | 134400 | 135933.8524 | Kakrail | Kakrail 33/11KV S/S | 151904 | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 11 | 0 | 39333 | 1 | 492441 | 492441 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 0 | 0 | 0
69 | Auxiliary Transformer, AT-2 | 11 | 0 | 39254 | 1 | 1195010 | 1220636 | 25626 | 1 | 0 | 25626 | 25918.4591 | Kakrail | Kakrail 33/11KV S/S | 0 | 0 | 0
70 | 11 kV Jamuna (F1) | 11 | 0 | BD017073 | 1 | 0.3748 | 0.3857 | 0.0109 | 2000 | 0 | 21.8 | 22.0654 | Kakrail | BSMMU 33/11KV S/S | 24.7258 | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | 11 | 0 | BD017074 | 1 | 2928.46 | 2949.81 | 21.35 | 2000 | 0 | 42700 | 43219.8277 | Kakrail | BSMMU 33/11KV S/S | 44627.1399 | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | 11 | 0 | BD017075 | 1 | 1753.43 | 1769.15 | 15.72 | 2000 | 0 | 31440 | 31822.749 | Kakrail | BSMMU 33/11KV S/S | 77353.7092 | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | 11 | 0 | BD017076 | 1 | 3017.58 | 3106.11 | 88.53 | 2000 | 0 | 177060 | 179215.5198 | Kakrail | BSMMU 33/11KV S/S | 177543.6485 | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | 11 | 0 | BD017077 | 1 | 14405.79 | 14750.36 | 344.57 | 2000 | 0 | 689140 | 697529.5567 | Kakrail | BSMMU 33/11KV S/S | 750881.7825 | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | 11 | 0 | BD017078 | 1 | 26649.82 | 26964.47 | 314.65 | 2000 | 0 | 629300 | 636961.0675 | Kakrail | BSMMU 33/11KV S/S | 681006.1346 | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | 11 | 0 | BD017079 | 1 | 31963.13 | 32752.23 | 789.1 | 2000 | 0 | 1578200 | 1597412.9298 | Paribag | BSMMU 33/11KV S/S | 1675286.7504 | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 | 0 | BD017080 | 1 | 6399.81 | 6611.65 | 211.84 | 2000 | 0 | 423680 | 428837.8596 | Paribag | BSMMU 33/11KV S/S | 457910.6397 | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | 11 | 0 | BD017083 | 1 | 2293.72 | 2364.53 | 70.81 | 2000 | 0 | 141620 | 143344.075 | Paribag | BSMMU 33/11KV S/S | 137962.1897 | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | 11 | 0 | BD017084 | 1 | 1218.74 | 1358.01 | 139.27 | 2000 | 0 | 278540 | 281930.9324 | Kakrail | BSMMU 33/11KV S/S | 302057.3893 | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 | 0 | BD017085 | 1 | 2119.1 | 2175.83 | 56.73 | 2000 | 0 | 113460 | 114841.2565 | Kakrail | BSMMU 33/11KV S/S | 122402.9977 | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | 11 | 0 | BD017086 | 1 | 2052.22 | 2138.01 | 85.79 | 2000 | 0 | 171580 | 173668.8065 | Paribag | BSMMU 33/11KV S/S | 174287.0734 | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 | 0 | BD017087 | 1 | 4149.43 | 4268.96 | 119.53 | 2000 | 0 | 239060 | 241970.3048 | Paribag | BSMMU 33/11KV S/S | 234654.3262 | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | 11 | 0 | BD017088 | 1 | 1022.96 | 1055.98 | 33.02 | 2000 | 0 | 66040 | 66843.9677 | Paribag | BSMMU 33/11KV S/S | 56065.3573 | 59004.3933 | 75292.0174
84 | Spare | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 0 | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | 11 | 0 | BD017090 | 1 | 1402.07 | 1664.04 | 261.97 | 2000 | 0 | 523940 | 530318.42 | Paribag | BSMMU 33/11KV S/S | 510819.9335 | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKD4418 | 1 | 2759.07 | 2905.71 | 146.64 | 100 | 0 | 14664 | 14842.5188 | Paribag | BSMMU 33/11KV S/S | 15407.4195 | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 1666.67 | 1671.49 | 4.82 | 100 | 0 | 482 | 487.8678 | Paribag | BSMMU 33/11KV S/S | 0 | 0 | 0
88 | Chata Mosjid | 11 | 0 | 0 | 1 | 171770.4353 | 174270.4 | 2499.9647 | 1000 | 0 | 2499964.71 | 2543835.8742 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 2199148.6226 | 2319503.7751 | 2426211.3577
89 | AC mosjid | 11 | 0 | 0 | 1 | 6488.7556 | 7869.7 | 1380.9444 | 1000 | 0 | 1380944.4 | 1405178.1975 | Lalbag | LALBAGH New 33/11 KV S/S | 1152835.6866 | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | 11 | 0 | 0 | 1 | 20836.008 | 23184.964 | 2348.956 | 1000 | 0 | 2348956 | 2390177.1556 | Lalbag | LALBAGH New 33/11 KV S/S | 2000565.9387 | 2224217.61 | 2267338.6868
91 | Nazimuddin | 11 | 0 | 0 | 1 | 4687.9236 | 5597.3048 | 909.3812 | 1000 | 0 | 909381.2 | 925339.67 | Lalbag | LALBAGH New 33/11 KV S/S | 477977.0793 | 0 | 0
92 | Kamal Bagh | 11 | 0 | 0 | 1 | 14900.122 | 16557.14 | 1657.018 | 1000 | 0 | 1657018 | 1686096.534 | Lalbag | LALBAGH New 33/11 KV S/S | 1618577.1268 | 1589844.4629 | 1583845.5588
93 | Rahamatganj | 11 | 0 | 0 | 1 | 10837.383 | 13289.972 | 2452.589 | 1000 | 0 | 2452589 | 2495628.7814 | Lalbag | LALBAGH New 33/11 KV S/S | 2157043.5386 | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 11 | 0 | 0 | 1 | 22372.9274 | 646.4972 | -21726.4302 | 1000 | Estimated | 1946125.44 | 1980277.4376 | Lalbag | LALBAGH New 33/11 KV S/S | 1747210.9883 | 1862323.276 | 1854345.8684
95 | City Colony | 11 | 0 | 0 | 1 | 24326.885 | 26507.92 | 2181.035 | 1000 | 0 | 2181035 | 2219309.3581 | Lalbag | LALBAGH New 33/11 KV S/S | 1859682.1079 | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 11 | 0 | 0 | 1 | 35515.332 | 1663.5993 | -33851.7327 | 1000 | Estimated | 2554289.64 | 2599114.1368 | Lalbag | LALBAGH New 33/11 KV S/S | 2790703.3917 | 2997202.1128 | 3092062.2371
97 | Chun Goli | 11 | 0 | 0 | 1 | 7124.165 | 8090.5632 | 966.3982 | 1000 | 0 | 966398.2 | 983357.245 | Lalbag | LALBAGH New 33/11 KV S/S | 754718.4448 | 841380.8401 | 894878.3402
98 | Alir Ghat | 11 | 0 | 0 | 1 | 121324.8 | 123425.3 | 2100.5 | 1000 | 0 | 2100500 | 2137361.0725 | Lalbag | LALBAGH New 33/11 KV S/S | 1734165.991 | 1904122.5273 | 2096766.6729
99 | Club Ghat | 11 | 0 | 0 | 1 | 16270.969 | 19197.12 | 2926.151 | 1000 | 0 | 2926151 | 2977501.1852 | Lalbag | LALBAGH New 33/11 KV S/S | 2317579.0304 | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | 11 | 0 | 0 | 1 | 29072.95 | 31744.334 | 2671.384 | 1000 | 0 | 2671384 | 2718263.3522 | Lalbag | LALBAGH New 33/11 KV S/S | 2261609.1864 | 2437761.5097 | 2619436.8857
101 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 0 | 0 | 0
102 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
103 | Sowari Ghat | 11 | 0 | 8838019 | 1 | 77211.8 | 80010.7 | 2798.9 | 1000 | 0 | 2798900 | 2802348.4469 | Lalbag | Lalbagh Old 33/11KV S/S | 2329233.6447 | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | 11 | 0 | 8838014 | 1 | 81145.3 | 81727.2 | 581.9 | 1000 | Estimated | 559511.064 | 560200.422 | Lalbag | Lalbagh Old 33/11KV S/S | 121854.324 | 118483.0867 | 132959.886
105 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
106 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
107 | Eidgah | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1429861.608 | 1431623.3008 | Lalbag | Lalbagh Old 33/11KV S/S | 1096688.9157 | 1303313.9541 | 1329598.8604
108 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
109 | Modumoti | 11 | 0 | 0 | 1 | 91067.8 | 96407.8 | 5340 | 444.44 | Estimated | 2113708.464 | 2116312.7055 | Lalbag | Lalbagh Old 33/11KV S/S | 1584106.2116 | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | 11 | 0 | 61389152 | 1 | 440978 | 441573 | 595 | 1000 | Estimated | 1243357.92 | 1244889.8267 | Lalbag | Lalbagh Old 33/11KV S/S | 1181986.9425 | 1066347.7806 | 1087853.6131
111 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
112 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
113 | Water Works 11 kV Sw/S-2 | 11 | 0 | 61389109 | 1 | 401739 | 402783 | 1044 | 1000 | 0 | 1044000 | 1045286.2834 | Lalbag | Lalbagh Old 33/11KV S/S | 874589.6653 | 951212.9635 | 980831.1601
114 | Islambagh | 11 | 0 | 61389186 | 1 | 500001 | 500941 | 940 | 1000 | 0 | 940000 | 941158.1479 | Lalbag | Lalbagh Old 33/11KV S/S | 774407.5731 | 861627.8273 | 876487.4197
115 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
116 | WASA Low Lift Pump | 11 | 0 | 61389202 | 1 | 15534 | 15590 | 56 | 1000 | 0 | 56000 | 56068.996 | Lalbag | Lalbagh Old 33/11KV S/S | 57103.7926 | 61401.0484 | 45712.4958
117 | Shahi Mosjid | 11 | 0 | 06604459 | 1 | 35827.5 | 36034.94 | 207.44 | 8000 | 0 | 1659520 | 1661564.6485 | Azimpur | Lalbagh Old 33/11KV S/S | 1773623.7611 | 1752245.002 | 1250534.8854
118 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0.415 | 0 | 5395822 | 1 | 28617 | 38472.5 | 9855.5 | 1 | 0 | 9855.5 | 9867.6427 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0 | 0
120 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0 | 0
121 | Spare | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0 | 0
122 | Chawk Bazar | 11 | 0 | DHK-60904 | 1 | 971432 | 980258.2 | 8826.2 | 60 | 0 | 529572 | 526171.1474 | Lalbag | Mitford 33/11 kV | 480516.9276 | 522405.3875 | 508276.2976
123 | Spare | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0 | 0
124 | Chatrabas | 11 | 0 | DHK-66485 | 1 | 816427 | 839123 | 22696 | 60 | 0 | 1361760 | 1353014.9285 | Bangshal | Mitford 33/11 kV | 1237900.3837 | 762976.1234 | 353557.5482
125 | Begum Bazar | 11 | 0 | DHK-66481 | 1 | 3667458 | 3708499 | 41041 | 60 | 0 | 2462460 | 2446646.3554 | Bangshal | Mitford 33/11 kV | 2397460.098 | 2421237.7604 | 2357293.0663
126 | SCC ROAD | 11 | 0 | DHK-60901 | 1 | 74915 | 103137 | 28222 | 60 | 0 | 1693320 | 1682445.687 | Bangshal | Mitford 33/11 kV | 1526989.2348 | 1650255.6547 | 1574186.7645
127 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0 | 0
128 | Armanitola | 11 | 0 | DHK-61104 | 1 | 684884 | 701514.5 | 16630.5 | 60 | 0 | 997830 | 991422.0466 | Bangshal | Mitford 33/11 kV | 974917.2355 | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 11 | 0 | DHK-61101 | 1 | 392201 | 401444.2 | 9243.2 | 60 | 0 | 554592 | 551030.4718 | Bangshal | Mitford 33/11 kV | 539101.6117 | 513839.5885 | 528540.0121
130 | Emamganj | 11 | 0 | DHK-68130 | 1 | 1450.67 | 1453.5 | 2.83 | 60000 | 0 | 169800 | 168709.5633 | Bangshal | Mitford 33/11 kV | 161982.5873 | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | 11 | 0 | DHK-68129 | 1 | 1225.4 | 1226.82 | 1.42 | 60000 | 0 | 85200 | 84652.8551 | Lalbag | Mitford 33/11 kV | 538371.2175 | 628439.5052 | 594724.3345
132 | Spare | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0 | 0
133 | Panghat | 11 | 0 | DHK-68127 | 1 | 1528.54 | 1552.36 | 23.82 | 60000 | 0 | 1429200 | 1420021.8363 | Bangshal | Mitford 33/11 kV | 1363598.8715 | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | U0004460 | 1 | 5594.68 | 5633.99 | 39.31 | 100 | 0 | 3931 | 3905.7556 | Bangshal | Mitford 33/11 kV | 3927.8323 | 4152.4762 | 4434.1352
135 | Chadni chwok | 11 | 0 | DHK60916 | 1 | 409665 | 421688 | 12023 | 60 | 0 | 721380 | 735452.5478 | Paribag | Azimpur 33/11 KV | 623153.8648 | 792142.0147 | 648152.1238
136 | BGB | 11 | 0 | DHK61090 | 1 | 676712 | 689645 | 12933 | 60 | 0 | 775980 | 791117.6745 | Jigatola | Azimpur 33/11 KV | 677536.8748 | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | 11 | 0 | DHK61091 | 1 | 780093 | 817084 | 36991 | 60 | 0 | 2219460 | 2262756.8158 | Azimpur | Azimpur 33/11 KV | 2133225.2763 | 2225341.7622 | 2144033.6462
138 | Azimpur | 11 | 0 | DHK61086 | 1 | 301821 | 320730 | 18909 | 60 | 0 | 1134540 | 1156672.3968 | Azimpur | Azimpur 33/11 KV | 1153479.4596 | 1136633.6642 | 1104066.6214
139 | Aazd | 11 | 0 | DHK61089 | 1 | 982542 | 1004577 | 22035 | 60 | 0 | 1322100 | 1347891.2826 | Azimpur | Azimpur 33/11 KV | 1333174.551 | 1318714.278 | 1257709.9294
140 | Dayra Sharif | 11 | 0 | DHK61088 | 1 | 515887 | 532893 | 17006 | 60 | 0 | 1020360 | 1040264.9944 | Azimpur | Azimpur 33/11 KV | 1036318.7466 | 1007533.0284 | 980271.2172
141 | Naya palton | 11 | 0 | DHK86065 | 1 | 1899.17 | 1928.02 | 28.85 | 60000 | 0 | 1731000 | 1764768.0283 | Azimpur | Azimpur 33/11 KV | 1711787.3638 | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | 11 | 0 | DHK66477 | 1 | 1609302 | 1633628 | 24326 | 60 | 0 | 1459560 | 1488032.8269 | Azimpur | Azimpur 33/11 KV | 1499973.4477 | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | 11 | 0 | DHK66480 | 1 | 4005845 | 4031972 | 26127 | 60 | 0 | 1567620 | 1598200.8415 | Azimpur | Azimpur 33/11 KV | 1506117.3895 | 1034936.4652 | 1287496.6695
144 | Lalbagh | 11 | 0 | DHK61093 | 1 | 726292 | 766602 | 40310 | 60 | 0 | 2418600 | 2465781.6021 | Azimpur | Azimpur 33/11 KV | 2471750.3893 | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | 11 | 0 | DHK66497 | 1 | 1239080 | 1251280 | 12200 | 60 | 0 | 732000 | 746279.7208 | Ramna | Azimpur 33/11 KV | 668533.8709 | 616760.0188 | 675859.2968
146 | Eden College | 11 | 0 | DHK60917 | 1 | 933261 | 941486 | 8225 | 60 | 0 | 493500 | 503127.1069 | Azimpur | Azimpur 33/11 KV | 450271.8574 | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | 11 | 0 | DHK60918 | 1 | 478017 | 489152 | 11135 | 60 | 0 | 668100 | 681133.1714 | Azimpur | Azimpur 33/11 KV | 683984.9722 | 653358.8311 | 648152.1238
148 | BUET | 11 | 0 | DHK66496 | 1 | 962739 | 976076 | 13337 | 60 | 0 | 800220 | 815830.544 | Ramna | Azimpur 33/11 KV | 798043.2987 | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIG2780 | 1 | 389374 | 393284 | 3910 | 1 | 0 | 3910 | 3986.2756 | Azimpur | Azimpur 33/11 KV | 4092.9197 | 4399.774 | 2203.9333
150 | Rasulpur | 11 | 0 | HA-021101042-02 | 1 | 91923561 | 93474113 | 1550552 | 1 | 0 | 1550552 | 1584215.5272 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1403442.4135 | 1475786.882 | 1248201.2259
151 | Bheribadh | 11 | 0 | HA-021101105-02 | 1 | 64458541 | 67023775 | 2565234 | 1 | 0 | 2565234 | 2620926.9562 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2327005.5404 | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | 11 | 0 | 30799521 | 1 | 2634.51 | 2640.43 | 5.92 | 60000 | 0 | 355200 | 362911.631 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 314576.4303 | 364934.8739 | 488122.7019
153 | Panna Battery Express | 11 | 0 | DHK15431 | 1 | 5278.8 | 5298.71 | 19.91 | 60000 | 0 | 1194600 | 1220535.5698 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1068349.9537 | 1060687.1709 | 1118589.0702
154 | Eidgah | 11 | 0 | 30799460 | 1 | 5369.43 | 5409.9 | 40.47 | 60000 | 0 | 2428200 | 2480917.8558 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2121576.0406 | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 0 | 0 | 0
156 | Huzur Para | 11 | 0 | HA-021101055-02 | 1 | 1275461 | 3393397 | 2117936 | 1 | 0 | 2117936 | 2163917.8156 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1832748.4977 | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | 11 | 0 | HA-021101015-02 | 1 | 21147055 | 23145473 | 1998418 | 1 | 0 | 1998418 | 2041804.9994 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1873617.2189 | 1726065.7983 | 1737567.1439
158 | Munshihati | 11 | 0 | HA-021100854-02 | 1 | 51488293 | 52835781 | 1347488 | 1 | 0 | 1347488 | 1376742.8712 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1392932.3343 | 1212171.698 | 1205376.9608
159 | Jhawchar | 11 | 0 | HA-021101028-02 | 1 | 250925 | 1779953 | 1529028 | 1 | 0 | 1529028 | 1562224.2267 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1438582.214 | 1425641.3374 | 1328999.0751
160 | RMU Express | 11 | 0 | HA-021101248-02 | 1 | 5919945 | 6564561 | 644616 | 1 | 0 | 644616 | 658611.0471 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 606779.6203 | 633839.2782 | 704501.3661
161 | Koyla Ghat | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2136683.556 | 2183072.3937 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1900877.505 | 2223108.4368 | 1816011.9444
162 | Muslimbagh | 11 | 0 | HA-021100908-02 | 1 | 26159019 | 27875253 | 1716234 | 1 | 0 | 1716234 | 1753494.5949 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1596522.772 | 1696945.1326 | 1737474.4882
163 | Noyagaon | 11 | 0 | HA-021101087-02 | 1 | 5869693 | 8700121 | 2830428 | 1 | 0 | 2830428 | 2891878.4964 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2674100.301 | 2742632.8101 | 2660587.4202
164 | Nurbagh | 11 | 0 | HA-021100982-02 | 1 | 23098305 | 25365051 | 2266746 | 1 | 0 | 2266746 | 2315958.5809 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1868573.9135 | 2159293.4513 | 2300317.433
165 | Ali Nagar | 11 | 0 | HA-021101022-02 | 1 | 22030169 | 24482441 | 2452272 | 1 | 0 | 2452272 | 2505512.4752 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2290198.0816 | 2360084.8023 | 2402380.2856
166 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
167 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
168 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
169 | Nababgonj Park | 11 | 0 | 0 | 1 | 9205025 | 10229090 | 1024065 | 1 | 0 | 1024065 | 1042273.5833 | Azimpur | BGB 33/11 KV S/S | 1021134.2367 | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | 11 | 0 | 0 | 1 | 77275264 | 80077104 | 2801840 | 1 | 0 | 2801840 | 2851658.6512 | Kamrangirchar | BGB 33/11 KV S/S | 2502740.2728 | 2762472.0542 | 2841690.4191
171 | Khalpar | 11 | 0 | 0 | 1 | 84269168 | 85938304 | 1669136 | 1 | 0 | 1669136 | 1698814.3914 | Kamrangirchar | BGB 33/11 KV S/S | 1298185.7875 | 1375644.1828 | 1437529.7992
172 | Shahidnagar | 11 | 0 | 0 | 1 | 16043430 | 17993510 | 1950080 | 1 | 0 | 1950080 | 1984753.7699 | Azimpur | BGB 33/11 KV S/S | 1856790.3941 | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | 11 | 0 | 0 | 1 | 32661410 | 34102440 | 1441030 | 1 | 0 | 1441030 | 1466652.5091 | Azimpur | BGB 33/11 KV S/S | 1458588.073 | 1375749.2129 | 1318685.5995
174 | Ganaktuli | 11 | 0 | 0 | 1 | 23467080 | 24390290 | 923210 | 1 | 0 | 923210 | 939625.3117 | Jigatola | BGB 33/11 KV S/S | 882817.4598 | 725654.1445 | 693078.4919
175 | Thana | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
176 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 32354152 | 34382472 | 2028320 | 1 | 0 | 2028320 | 2064384.9311 | Jigatola | BGB 33/11 KV S/S | 2207948.9744 | 2074198.5352 | 1909183.4664
177 | Sikder Medical | 11 | 0 | 0 | 1 | 35690888 | 36890712 | 1199824 | 1 | 0 | 1199824 | 1221157.6998 | Jigatola | BGB 33/11 KV S/S | 1181050.1989 | 1134381.9061 | 1138392.2283
178 | Gas Field | 11 | 0 | 0 | 1 | 53961540 | 56136408 | 2174868 | 1 | 0 | 2174868 | 2213538.6558 | Kamrangirchar | BGB 33/11 KV S/S | 2063276.8361 | 2061072.7993 | 1985612.1672
179 | Hazaribagh | 11 | 0 | 0 | 1 | 39936160 | 41443472 | 1507312 | 1 | 0 | 1507312 | 1534113.0489 | Jigatola | BGB 33/11 KV S/S | 1525507.7666 | 1485016.8997 | 1465699.7946
180 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
181 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 0 | 1 | 2117.04 | 2177.16 | 60.12 | 10 | 0 | 601.2 | 611.8898 | Azimpur | BGB 33/11 KV S/S | 0 | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 0 | 1 | 1699.35 | 1754.23 | 54.88 | 10 | 0 | 548.8 | 558.558 | Azimpur | BGB 33/11 KV S/S | 0 | 0 | 0
184 | Salek Garden | 11 | 0 | 2761 | 1 | 593.11 | 635.73 | 42.62 | 60000 | 0 | 2557200 | 2553649.2193 | Jigatola | Jigatola New 33/11 KV S/S | 2650896.5462 | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 11 | 0 | 2850 | 1 | 469.67 | 499.39 | 29.72 | 60000 | 0 | 1783200 | 1780723.9511 | Jigatola | Jigatola New 33/11 KV S/S | 1886527.6034 | 1807426.7227 | 1737565.9216
186 | City College | 11 | 0 | 2784 | 1 | 510.17 | 539.43 | 29.26 | 60000 | 0 | 1755600 | 1753162.2749 | Jigatola | Jigatola New 33/11 KV S/S | 1830510.0213 | 1777383.0604 | 2346194.6487
187 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0 | 0
188 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0 | 0
189 | Post Office | 11 | 0 | 2836 | 1 | 386.41 | 413.89 | 27.48 | 60000 | 0 | 1648800 | 1646510.5712 | Jigatola | Jigatola New 33/11 KV S/S | 1676311.0857 | 1671629.3692 | 1589764.671
190 | Leather Institute | 11 | 0 | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 57222.2613 | 189875.9456 | 195265.8799
191 | Mina Bazar | 11 | 0 | 2853 | 1 | 194.57 | 206.27 | 11.7 | 60000 | 0 | 702000 | 701025.2432 | Jigatola | Jigatola New 33/11 KV S/S | 763766.6032 | 746284.571 | 706562.076
192 | Road-2 | 11 | 0 | 2839 | 1 | 624.12 | 663.52 | 39.4 | 60000 | 0 | 2364000 | 2360717.4857 | Jigatola | Jigatola New 33/11 KV S/S | 2376832.0316 | 2301945.4038 | 2450136.1786
193 | SS-2 | 11 | 0 | 2838 | 1 | 291.23 | 312 | 20.77 | 60000 | 0 | 1246200 | 1244469.5984 | Jigatola | Jigatola New 33/11 KV S/S | 1139024.1692 | 1127238.2087 | 1112715.1061
194 | Spare | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0 | 0
195 | Bou Bazar | 11 | 0 | 2843 | 1 | 502.69 | 534.72 | 32.03 | 60000 | 0 | 1921800 | 1919131.4991 | Jigatola | Jigatola New 33/11 KV S/S | 1882311.2263 | 1850088.7231 | 1774816.6433
196 | BGB | 11 | 0 | 2764 | 1 | 179.28 | 186.72 | 7.44 | 60000 | 0 | 446400 | 445780.1547 | Jigatola | Jigatola New 33/11 KV S/S | 580655.3671 | 1007063.5596 | 934872.9509
197 | Dhamondi-12 | 11 | 0 | 2763 | 1 | 400.32 | 427.72 | 27.4 | 60000 | 0 | 1644000 | 1641717.2362 | Dhanmondi | Jigatola New 33/11 KV S/S | 1520907.4708 | 1213163.0828 | 1602982.669
198 | Mitali Road | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
199 | Bou Bazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
200 | Mina Bazar | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
201 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
202 | Simanto Square | 11 | 0 | DHK60946 | 1 | 1141.66 | 1157 | 15.34 | 60000 | 0 | 920400 | 922404.6994 | Jigatola | Jigatola Old 33/11KV S/S | 967800 | 852145.3731 | 901151.3428
203 | Post Office | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
204 | Hazaribagh Sw/S-2 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
205 | Green Road Via Park | 11 | 0 | DHK61070 | 1 | 3437.43 | 3458.66 | 21.23 | 60000 | 0 | 1273800 | 1276574.4307 | Jigatola | Jigatola Old 33/11KV S/S | 1342800 | 1229862.9154 | 476757.7712
206 | PWD Quarters 11 kV Saleq Grand | 11 | 0 | DHK61028 | 1 | 3630.54 | 3631.76 | 1.22 | 60000 | 0 | 73200 | 73359.435 | Jigatola | Jigatola Old 33/11KV S/S | 68400 | 74813.6195 | 63933.0345
207 | Road No.-2 | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
208 | Hzaribagh O/H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
209 | B.G.B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
210 | 11 kV City College | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
211 | Jigatala Local | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0 | 0
212 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 243284 | 1 | 84159 | 84683 | 524 | 10 | 0 | 5240 | 5251.4131 | Jigatola | Jigatola Old 33/11KV S/S | 3680 | 2585.0234 | 3440.2061
213 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 412277 | 1 | 39663 | 39664 | 1 | 10 | 0 | 10 | 10.0218 | Jigatola | Jigatola Old 33/11KV S/S | 1650 | 5393.0685 | 0
214 | Spare | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0 | 0
215 | D Block dhaka uddyan | 11 | 0 | BD014031 | 1 | 48979.01 | 49358.52 | 379.51 | 1000 | 0 | 379510 | 382937.2777 | Adabor | Dhaka Uddyan 33/11 KV S/S | 364723.8055 | 376392.0985 | 356370.9019
216 | Dill Mohammad O/H | 11 | 0 | BD014027 | 1 | 17844.24 | 19845.66 | 2001.42 | 1000 | 0 | 2001420 | 2019494.4174 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1931376.746 | 1945233.0858 | 1925614.3584
217 | Turag O/H | 11 | 0 | BD014028 | 1 | 26177.65 | 26940.95 | 763.3 | 1000 | 0 | 763300 | 770193.2072 | Adabor | Dhaka Uddyan 33/11 KV S/S | 703573.3851 | 725059.1327 | 419185.0275
218 | Nabadoy O/H | 11 | 0 | BD014025 | 1 | 35784.32 | 36623.52 | 839.2 | 1000 | 0 | 839200 | 846778.6447 | Adabor | Dhaka Uddyan 33/11 KV S/S | 874784.3247 | 873886.7957 | 1264712.0241
219 | Chandrima O/H | 11 | 0 | BD014024 | 1 | 4855.8 | 5884.34 | 1028.54 | 1000 | 0 | 1028540 | 1037828.5358 | Adabor | Dhaka Uddyan 33/11 KV S/S | 998647.327 | 974655.0029 | 879754.0777
220 | Shyamoli Housing Project-2 | 11 | 0 | BD014029 | 1 | 26451.58 | 27785.59 | 1334.01 | 1000 | 0 | 1334010 | 1346057.1733 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1686564.4606 | 1305126.5223 | 2226602.9518
221 | Spare | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0 | 0
222 | Spare | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0 | 0
223 | Spare | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0 | 0
224 | U Lab | 11 | 0 | BD013959 | 1 | 37965.55 | 39475.91 | 1510.36 | 1000 | 0 | 1510360 | 1523999.7543 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2168216.2175 | 2766170.13 | 2585824.4138
225 | Akota | 11 | 0 | BD014020 | 1 | 6085.32 | 6634.04 | 548.72 | 1000 | 0 | 548720 | 553675.3788 | Adabor | Dhaka Uddyan 33/11 KV S/S | 518552.2147 | 529306.7232 | 494561.9781
226 | Burigonga O/H | 11 | 0 | BD014019 | 1 | 4671.23 | 5080.63 | 409.4 | 1000 | 0 | 409400 | 413097.2082 | Adabor | Dhaka Uddyan 33/11 KV S/S | 391376.3535 | 420977.1349 | 372374.7602
227 | Garden City | 11 | 0 | BD014021 | 1 | 83851.34 | 86636.25 | 2784.91 | 1000 | 0 | 2784910 | 2810059.9564 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2804225.2436 | 2395190.4943 | 2278829.2831
228 | Avenue O/H | 11 | 0 | BD014017 | 1 | 12957.25 | 13982.44 | 1025.19 | 1000 | 0 | 1025190 | 1034448.2826 | Adabor | Dhaka Uddyan 33/11 KV S/S | 977183.594 | 966250.121 | 894892.5874
229 | Chand Uddyan | 11 | 0 | BD014018 | 1 | 8233.6 | 8987.27 | 753.67 | 1000 | 0 | 753670 | 760476.2406 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 759432.9748 | 732469.8888 | 645275.1572
230 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4416 | 1 | 1797.78 | 1835.21 | 37.43 | 100 | 0 | 3743 | 3776.8023 | Adabor | Dhaka Uddyan 33/11 KV S/S | 3734.949 | 3966.4616 | 1513.851
231 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0 | 2409.7413
232 | Lalmatia O/H | 11 | 0 | DHK61042 | 1 | 3147.3 | 3168.078 | 20.778 | 60000 | 0 | 1246680 | 1243685.3152 | Satmasjid | Satmasjid 33/11KV S/S | 1300189.4979 | 1240075.1783 | 1343819.1874
233 | Asad Avenue (South) | 11 | 0 | DHK 60999 | 1 | 2897.6 | 2897.6 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 99461.5008 | 201384.8525 | 143036.2105
234 | Madrasha Road | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 0 | 0 | 0
235 | Bashbari | 11 | 0 | DHK61002 | 1 | 2370.58 | 2398.83 | 28.25 | 60000 | 0 | 1695000 | 1690928.3933 | Satmasjid | Satmasjid 33/11KV S/S | 1784914.5226 | 1599091.6268 | 1533732.8114
236 | Road-27 | 11 | 0 | DHK61001 | 1 | 1438.38 | 1447.74 | 9.36 | 60000 | 0 | 561600 | 560250.965 | Satmasjid | Satmasjid 33/11KV S/S | 379271.8673 | 89903.952 | 435118.5562
237 | Boishakhi O/H | 11 | 0 | DHK61024 | 1 | 4091.98 | 4141.2 | 49.22 | 60000 | 0 | 2953200 | 2946106.036 | Dhanmondi | Satmasjid 33/11KV S/S | 2918535.965 | 3026167.0253 | 2814447.7883
238 | Katasur O/H | 11 | 0 | DHK61003 | 1 | 3605.55 | 3629.26 | 23.71 | 60000 | 0 | 1422600 | 1419182.7329 | Satmasjid | Satmasjid 33/11KV S/S | 1436799.27 | 1431270.9163 | 1334804.3002
239 | Nurjahan Road | 11 | 0 | DHK61000 | 1 | 1817.79 | 1841.57 | 23.78 | 60000 | 0 | 1426800 | 1423372.644 | Shyamoli | Satmasjid 33/11KV S/S | 1464960.0563 | 1437863.8728 | 1376873.7739
240 | polpar over head | 11 | 0 | DHK61003 | 1 | 1797.61 | 1833.4 | 35.79 | 60000 | 0 | 2147400 | 2142241.6706 | Dhanmondi | Satmasjid 33/11KV S/S | 2168380.5497 | 2135518.5405 | 2016930.7661
241 | Satmosjid Housing | 11 | 0 | DHK61043 | 1 | 2802.53 | 2825.54 | 23.01 | 60000 | 0 | 1380600 | 1377283.6223 | Satmasjid | Satmasjid 33/11KV S/S | 608153.1522 | 0 | 0
242 | Physical College | 11 | 0 | DHK61041 | 1 | 3261.37 | 3305.7 | 44.33 | 60000 | 0 | 2659800 | 2653410.8203 | Satmasjid | Satmasjid 33/11KV S/S | 2677671.3668 | 2636583.2332 | 2184607.6683
243 | Asad Avenue (North) | 11 | 0 | DHK61022 | 1 | 2725.37 | 2725.37 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 3594.994 | 0 | 0
244 | Spare Feeder | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 0 | 0 | 0
245 | Ghraphic artch college | 11 | 0 | DHK61023 | 1 | 1069.16 | 1097.82 | 28.66 | 60000 | 0 | 1719600 | 1715469.3009 | Dhanmondi | Satmasjid 33/11KV S/S | 1620743.1298 | 1570921.7218 | 1701409.7136
246 | Mohammadpur O/H | 11 | 0 | DHK61025 | 1 | 2160.67 | 2188.23 | 27.56 | 60000 | 0 | 1653600 | 1649627.8414 | Shyamoli | Satmasjid 33/11KV S/S | 1683655.5249 | 1660825.6738 | 1343218.1949
247 | Bosila Feeder | 11 | 0 | DHK60997 | 1 | 4059.26 | 4104.49 | 45.23 | 60000 | 0 | 2713800 | 2707281.1054 | Satmasjid | Satmasjid 33/11KV S/S | 2444595.9223 | 2900301.4925 | 3015179.277
248 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIB 7375 | 1 | 5698.37 | 5834.69 | 136.32 | 60 | 0 | 8179.2 | 8159.5525 | Satmasjid | Satmasjid 33/11KV S/S | 8272.6804 | 8691.9141 | 0
249 | Dhaka Uddyan | 11 | 0 | DHK86067 | 1 | 3250.6 | 3251.37 | 0.77 | 60000 | 0 | 46200 | 46170.0157 | Adabor | Japan Garden 33/11 KV | 47362.5115 | 34177.6075 | 0
250 | Shia Mosjid | 11 | 0 | DHK60950 | 1 | 3431.26 | 3469.82 | 38.56 | 60000 | 0 | 2313600 | 2312098.4465 | Shyamoli | Japan Garden 33/11 KV | 2316566.3838 | 2321079.2736 | 1677029.4105
251 | Shekhar Tek | 11 | 0 | DHK60977 | 1 | 2346.34 | 2380.53 | 34.19 | 60000 | 0 | 2051400 | 2050068.6174 | Adabor | Japan Garden 33/11 KV | 2089945.7593 | 2160384.5576 | 1966584.1503
252 | Madrasha Road | 11 | 0 | DHK61083 | 1 | 1969.45 | 1994.77 | 25.32 | 60000 | 0 | 1519200 | 1518214.0214 | Shyamoli | Japan Garden 33/11 KV | 1459844.4991 | 1147648.0831 | 1148666.6379
253 | Baitul Aman Housing | 11 | 0 | DHK668115 | 1 | 4071 | 4117.69 | 46.69 | 60000 | 0 | 2801400 | 2799581.8586 | Adabor | Japan Garden 33/11 KV | 2963454.3569 | 2980047.5303 | 2714650.3131
254 | Shyamoli Square | 11 | 0 | DHK86063 | 1 | 458.1 | 463.85 | 5.75 | 30000 | 0 | 172500 | 172388.0455 | Shyamoli | Japan Garden 33/11 KV | 167267.6038 | 170888.0374 | 163284.9924
255 | Mohammadi Housing | 11 | 0 | DHK60948 | 1 | 3785.19 | 3816.33 | 31.14 | 60000 | 0 | 1868400 | 1867187.3865 | Adabor | Japan Garden 33/11 KV | 2007211.2456 | 1954719.3056 | 1343295.1846
256 | Chand Housing | 11 | 0 | DHK60867 | 1 | 2161.88 | 2175.16 | 13.28 | 60000 | 0 | 796800 | 796282.8675 | Satmasjid | Japan Garden 33/11 KV | 850127.1046 | 960570.6526 | 891350.9825
257 | PC Culture Housing | 11 | 0 | DHK60979 | 1 | 4067.35 | 4110.13 | 42.78 | 60000 | 0 | 2566800 | 2565134.1168 | Adabor | Japan Garden 33/11 KV | 2719447.494 | 2646665.9554 | 2456140.6176
258 | Mehedibagh | 11 | 0 | DHK68121 | 1 | 2259.27 | 2309.58 | 50.31 | 60000 | 0 | 3018600 | 3016640.8933 | Adabor | Japan Garden 33/11 KV | 3040793.1415 | 3013625.5306 | 2845397.7111
259 | 33/11 kV Incoming (Spare) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 0 | 0 | 0
260 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | 0 | 1 | 647547 | 652584 | 5037 | 1 | 0 | 5037 | 5033.7309 | Adabor | Japan Garden 33/11 KV | 5179.9 | 5393.4663 | 0
261 | Mokarom Bhabon | 11 | 0 | 2761 | 1 | 50 | 53.49 | 3.49 | 60000 | 0 | 209400 | 207689.3161 | Ramna | Dhaka University 33/11 KV S/S | 186304.8566 | 168036.2342 | 191876.7922
262 | 11 kV Shaid Minar RMU | 11 | 0 | 2850 | 1 | 116.8 | 122.87 | 6.07 | 60000 | 0 | 364200 | 361224.6845 | Ramna | Dhaka University 33/11 KV S/S | 367165.7402 | 336672.5979 | 339844.4752
263 | 11 kV Shaidulla Hall | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0 | 0 | 0
264 | Spare | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
265 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
266 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
267 | MBA Bhabon | 11 | 0 | 2836 | 1 | 90.5 | 95.21 | 4.71 | 60000 | 0 | 282600 | 280291.312 | Ramna | Dhaka University 33/11 KV S/S | 263125.3657 | 250253.9631 | 301348.8178
268 | Suprime Court | 11 | 0 | 2835 | 1 | 50 | 55.93 | 5.93 | 60000 | 0 | 355800 | 352893.3079 | Ramna | Dhaka University 33/11 KV S/S | 353253.3645 | 298264.3158 | 306762.2696
269 | Karjon Hall | 11 | 0 | 2853 | 1 | 55.9 | 61.8 | 5.9 | 60000 | 0 | 354000 | 351108.0129 | Ramna | Dhaka University 33/11 KV S/S | 342970.3043 | 313267.551 | 333228.0341
270 | Spare | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
271 | Swimming Pool | 11 | 0 | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0 | 0 | 0
272 | Spare | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
273 | Police Head Quarter RMU | 11 | 0 | 2772 | 1 | 72.1 | 80.07 | 7.97 | 60000 | 0 | 478200 | 474293.3666 | Ramna | Dhaka University 33/11 KV S/S | 554680.3686 | 488505.3381 | 444504.5437
274 | Spare | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
275 | Spare | 11 | 0 | 2764 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
276 | Spare | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0 | 0
277 | Segunbagicha | 11 | 0 | DHK-C9360 | 1 | 82917.41 | 93600.91 | 10683.5 | 60 | 0 | 641010 | 652730.1844 | Ramna | Biddyut Bhaban 33/11 KV | 660791.8145 | 648570.0837 | 628132.1417
278 | Secretariat RMU | 11 | 0 | DHK-C9379 | 1 | 71809.95 | 74577.49 | 2767.54 | 60 | 0 | 166052.4 | 169088.4911 | Ramna | Biddyut Bhaban 33/11 KV | 173479.2405 | 157347.3651 | 189151.3106
279 | NBR RMU | 11 | 0 | DHK-C9319 | 1 | 51570.08 | 59233.63 | 7663.55 | 60 | 0 | 459813 | 468220.1905 | Ramna | Biddyut Bhaban 33/11 KV | 479026.3146 | 471677.0943 | 454185.7713
280 | Ramna 11 kV Sw/S-2 | 11 | 0 | DHK-C9364 | 1 | 8506.79 | 9654.36 | 1147.57 | 60 | 0 | 68854.2 | 70113.1256 | Ramna | Biddyut Bhaban 33/11 KV | 552257.97 | 1047973.9631 | 1309281.295
281 | Ramna 11 kV Sw/S-1 | 11 | 0 | DHK-C9375 | 1 | 46623.88 | 51466.11 | 4842.23 | 60 | 0 | 290533.8 | 295845.9008 | Ramna | Biddyut Bhaban 33/11 KV | 960645.5509 | 37569.2064 | 3932.094
282 | Family Planning | 11 | 0 | DHK-C9378 | 1 | 49313.12 | 57130.46 | 7817.34 | 60 | 0 | 469040.4 | 477616.3037 | Ramna | Biddyut Bhaban 33/11 KV | 472965.3149 | 459978.3897 | 450311.5022
283 | Muktijuddho Montranalaya | 11 | 0 | DHK-C9376 | 1 | 42919.82 | 58952.06 | 16032.24 | 60 | 0 | 961934.4 | 979522.345 | Ramna | Biddyut Bhaban 33/11 KV | 1003580.0431 | 989924.3443 | 925250.3935
284 | Purana Palton | 11 | 0 | DHK-C9318 | 1 | 49147.44 | 54862.84 | 5715.4 | 60 | 0 | 342924 | 349193.9997 | Ramna | Biddyut Bhaban 33/11 KV | 350733.9486 | 318744.0733 | 328976.7665
285 | Tip Top Feeder | 11 | 0 | DHK-C9318 | 1 | 89567.58 | 111275.28 | 21707.7 | 60 | 0 | 1302462 | 1326276.1291 | Kakrail | Biddyut Bhaban 33/11 KV | 1389761.4375 | 1427034.1549 | 1299449.2529
286 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 | 0 | DHKD3784 | 1 | 341182 | 345768 | 4586 | 1 | 0 | 4586 | 4669.8501 | Ramna | Biddyut Bhaban 33/11 KV | 4947.3654 | 4696.0253 | 4800.6724
287 | Nearest O/H | 11 | 0 | 00000126 | 1 | 7294622 | 7520221 | 225599 | 1 | 0 | 225599 | 227289.0317 | Ramna | DMC 33/11 KV SS | 224820.1739 | 210729.7741 | 229906.9253
288 | Jagannath Hall | 11 | 0 | 00000002 | 1 | 2654153 | 2759593 | 105440 | 1 | 0 | 105440 | 106229.8836 | Ramna | DMC 33/11 KV SS | 110593.2428 | 113276.1711 | 96242.8599
289 | Samsun Nahar Hall | 11 | 0 | 00000024 | 1 | 9370297 | 9697616 | 327319 | 1 | 0 | 327319 | 329771.0476 | Ramna | DMC 33/11 KV SS | 322680.6125 | 293593.2672 | 312413.2678
290 | Spare, 4L | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0 | 0 | 0
291 | Board Office O/H, (5L) | 11 | 0 | 00000023 | 1 | 21315228 | 21866026 | 550798 | 1 | 0 | 550798 | 554924.1978 | Lalbag | DMC 33/11 KV SS | 600144.1706 | 492983.2953 | 466712.6927
292 | OT- Complex | 11 | 0 | 00000167 | 1 | 6148345 | 6392704 | 244359 | 1 | 0 | 244359 | 246189.5687 | Ramna | DMC 33/11 KV SS | 446170.5101 | 427837.7768 | 405707.0733
293 | Alia Mdrasha O/H, (7L) | 11 | 0 | 00000148 | 1 | 9394377 | 9536497 | 142120 | 1 | 0 | 142120 | 143184.6648 | Lalbag | DMC 33/11 KV SS | 77701.5086 | 75154.3226 | 71193.4446
294 | Majed Sordar Road | 11 | 0 | 00000164 | 1 | 55060864 | 56822140 | 1761276 | 1 | 0 | 1761276 | 1774470.2621 | Bangshal | DMC 33/11 KV SS | 1602752.7729 | 1759301.3409 | 1689289.8138
295 | Chankharpool, 9L | 11 | 0 | 00000001 | 1 | 46801764 | 48003364 | 1201600 | 1 | 0 | 1201600 | 1210601.5564 | Bangshal | DMC 33/11 KV SS | 1176945.2408 | 1201456.0712 | 1157798.1959
296 | Shahidullah College O/H, (10L) | 11 | 0 | 00000003 | 1 | 12842169 | 13105088 | 262919 | 1 | 0 | 262919 | 264888.6074 | Lalbag | DMC 33/11 KV SS | 263222.0224 | 263967.4494 | 265403.8751
297 | Ananda Bazar | 11 | 0 | 00000111 | 1 | 14878044 | 15022203 | 144159 | 1 | 0 | 144159 | 145238.9396 | Ramna | DMC 33/11 KV SS | 167074.5674 | 216784.0965 | 169141.9631
298 | Hosseni Dalan O/H, (12L) | 11 | 0 | 0 | 1 | 50.74 | 54.95 | 4.21 | 60000 | Estimated | 1032221.88 | 1039954.5727 | Lalbag | DMC 33/11 KV SS | 1170127.1783 | 1629339.2554 | 1651805.4359
299 | Badrun Nessa College | 11 | 0 | 00000006 | 1 | 19521592 | 20028432 | 506840 | 1 | 0 | 506840 | 510636.8949 | Lalbag | DMC 33/11 KV SS | 522687.5196 | 511348.0734 | 487810.3149
300 | Dhaka Medical College, Unit-II | 11 | 0 | 00000125 | 1 | 11679371 | 12004431 | 325060 | 1 | 0 | 325060 | 327495.1248 | Ramna | DMC 33/11 KV SS | 332597.3491 | 314783.3957 | 318669.3545
301 | Spare, 15L | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0 | 0 | 0
302 | Sheikh Hasina National Burn Institute | 11 | 0 | 00000127 | 1 | 20301830 | 20882750 | 580920 | 1 | 0 | 580920 | 585271.851 | Ramna | DMC 33/11 KV SS | 637362.5402 | 594088.462 | 527600.9918
303 | Aux. Transformer, AT-1 | 0.415 | 0 | DHKF-7804 | 1 | 2637.73 | 2716.51 | 78.78 | 100 | 0 | 7878 | 7937.0165 | Ramna | DMC 33/11 KV SS | 8829.1604 | 8254.0596 | 7320.9952
304 | Aux. Transformer, AT-2 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 0 | 0 | 0
305 | Secratariet East | 11 | 0 | BD 013966 | 1 | 3666.02 | 3904.68 | 238.66 | 1000 | 0 | 238660 | 241216.6768 | Ramna | BB Aveneu 33/11 KV S/S | 260076.7434 | 245293.0009 | 245463.3743
306 | Taher Bag O/H | 11 | 0 | BD 014045 | 1 | 18336.98 | 19122.89 | 785.91 | 1000 | 0 | 785910 | 794329.1648 | Narinda | BB Aveneu 33/11 KV S/S | 678707.287 | 744464.9674 | 740283.3012
307 | Al Raji Complex | 11 | 0 | BD 013983 | 1 | 13753.92 | 14539.29 | 785.37 | 1000 | 0 | 785370 | 793783.38 | Ramna | BB Aveneu 33/11 KV S/S | 773675.1898 | 784809.8778 | 793405.3649
308 | Raduni | 11 | 0 | BD 013999 | 1 | 27128.05 | 28415.36 | 1287.31 | 1000 | 0 | 1287310 | 1301100.4786 | Ramna | BB Aveneu 33/11 KV S/S | 623159.8339 | 1293358.488 | 1280815.0384
309 | Sundor Bon Square O/H | 11 | 0 | BD 013954 | 1 | 12696.85 | 13211.17 | 514.32 | 1000 | 0 | 514320 | 519829.721 | Narinda | BB Aveneu 33/11 KV S/S | 434096.0289 | 473931.0551 | 515871.5523
310 | Shromo Bhobon O/H | 11 | 0 | BD 013985 | 1 | 12636.31 | 13147.42 | 511.11 | 1000 | 0 | 511110 | 516585.3335 | Ramna | BB Aveneu 33/11 KV S/S | 525134.9167 | 505142.6077 | 521299.6391
311 | Nawabpur Road | 11 | 0 | BD 013953 | 1 | 19355.25 | 20250.6 | 895.35 | 1000 | 0 | 895350 | 904941.5553 | Narinda | BB Aveneu 33/11 KV S/S | 800366.4326 | 843066.7121 | 849749.7199
312 | Spair | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0 | 0
313 | Spare | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0 | 0
314 | Ahad Police Box | 11 | 0 | BD 013984 | 1 | 10672.48 | 11126.54 | 454.06 | 1000 | 0 | 454060 | 458924.1778 | Ramna | BB Aveneu 33/11 KV S/S | 366641.2546 | 470281.7667 | 423970.1788
315 | Nearest O/H | 11 | 0 | BD 013997 | 1 | 2505.26 | 2621.4 | 116.14 | 1000 | 0 | 116140 | 117384.1651 | Ramna | BB Aveneu 33/11 KV S/S | 114763.3233 | 117912.5625 | 115595.8875
316 | Natab Bhaban | 11 | 0 | BD 014000 | 1 | 4804.84 | 4980.23 | 175.39 | 1000 | 0 | 175390 | 177268.8886 | Ramna | BB Aveneu 33/11 KV S/S | 180013.0381 | 185708.2311 | 177165.0302
317 | Spare | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0 | 0
318 | Awami League Party Office | 11 | 0 | BD 013956 | 1 | 1408.1 | 1413.62 | 5.52 | 1000 | 0 | 5520 | 5579.1337 | Ramna | BB Aveneu 33/11 KV S/S | 3568.1872 | 9417.1914 | 9250.1106
319 | Khaddar Bazar | 11 | 0 | BD 014012 | 1 | 9709.64 | 10114.75 | 405.11 | 1000 | 0 | 405110 | 409449.7945 | Ramna | BB Aveneu 33/11 KV S/S | 392931.5775 | 394275.1992 | 392631.6173
320 | Bangobondu National Stidium | 11 | 0 | BD 014008 | 1 | 6536.3 | 7820.82 | 1284.52 | 1000 | 0 | 1284520 | 1298280.5904 | Ramna | BB Aveneu 33/11 KV S/S | 390265.4601 | 288658.7112 | 290128.194
321 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4418 | 1 | 1124.63 | 1260.11 | 135.48 | 100 | 0 | 13548 | 13693.1347 | Ramna | BB Aveneu 33/11 KV S/S | 0 | 0 | 1718.8942
322 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 41.9 | 47.81 | 5.91 | 100 | 0 | 591 | 597.3312 | Ramna | BB Aveneu 33/11 KV S/S | 0 | 0 | 387.2849
323 | 11 KV Ring Road Feeder | 11 | 0 | 77816675 | 1 | 41923.11 | 42067.8 | 144.69 | 8000 | 0 | 1157520 | 1186458 | Adabor | Kallyanpur 33/11KV S/S | 1209910 | 1172682 | 1124384
324 | 11 KV Gano Bhavan RMU | 11 | 0 | DHK14997 | 1 | 995.74 | 995.77 | 0.03 | 40000 | 0 | 1200 | 1230 | Shere b.nagar | Kallyanpur 33/11KV S/S | 1230 | 1230 | 1230
325 | 11 KV Adabor O/H | 11 | 0 | DHK14957 | 1 | 4419.91 | 4471.1 | 51.19 | 40000 | 0 | 2047600 | 2098790 | Adabor | Kallyanpur 33/11KV S/S | 1976610 | 2150040 | 2995460
326 | 11 KV Goidertek (DPDC) | 11 | 0 | DHK14996 | 1 | 9369.92 | 9384.91 | 14.99 | 40000 | 0 | 599600 | 614590 | Adabor | Kallyanpur 33/11KV S/S | 586300 | 591220 | 558420
327 | 11 KV Beribandh Feeder. | 11 | 0 | DHK14960 | 1 | 9646.16 | 9652 | 5.84 | 40000 | 0 | 233600 | 239440 | Adabor | Kallyanpur 33/11KV S/S | 234930 | 301350 | 184500
328 | 11 KV Sewarage Pump | 11 | 0 | DHK14959 | 1 | 2112.81 | 2184.81 | 72 | 40000 | 0 | 2880000 | 2952000 | Adabor | Kallyanpur 33/11KV S/S | 2380460 | 2601450 | 535870
329 | 11 KV Technical School (DPDC) | 11 | 0 | DHK15019 | 1 | 8192.03 | 8249.67 | 57.64 | 40000 | 0 | 2305600 | 2363240 | Adabor | Kallyanpur 33/11KV S/S | 2400960 | 2347660 | 2184890
330 | 11 KV Mansurabad | 11 | 0 | 77816681 | 1 | 51898.42 | 52193.9 | 295.48 | 8000 | 0 | 2363840 | 2422936 | Adabor | Kallyanpur 33/11KV S/S | 2313630 | 2379804 | 2220888
331 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40464.9 | 40634.2 | 169.3 | 1000 | 0 | 169300 | 177316.5531 | Moghbazar | Moghbazar 33/11KV S/S | 65016.8533 | 1691.4448 | 1119.369
332 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 80645.6 | 80720.7 | 75.1 | 1000 | 0 | 75100 | 78656.0729 | Tejgaon | Moghbazar 33/11KV S/S | 96666.9717 | 802696.2793 | 1023306.7911
333 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 0 | 0 | 1589911.0287
334 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 119512.5 | 119910.2 | 397.7 | 1000 | 0 | 397700 | 416531.5604 | Tejgaon | Moghbazar 33/11KV S/S | 434303.9973 | 326660.2796 | 342221.6327
335 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0 | 0
336 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 119411.5 | 120973.1 | 1561.6 | 1000 | Estimated | 1921798.872 | 2012798.2977 | Kakrail | Moghbazar 33/11KV S/S | 1909092.2251 | 1919578.4326 | 1819483.4353
337 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 125254.8 | 127520.1 | 2265.3 | 1000 | 0 | 2265300 | 2372564.6062 | Moghbazar | Moghbazar 33/11KV S/S | 2579216.4264 | 2455343.5773 | 1989016.959
338 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 144229.5 | 145820.4 | 1590.9 | 1000 | 0 | 1590900 | 1666230.9769 | Tejgaon | Moghbazar 33/11KV S/S | 1593234.7726 | 1205154.4296 | 1055666.7314
339 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8577.9 | 8722.2 | 144.3 | 1000 | 0 | 144300 | 151132.7739 | Tejgaon | Moghbazar 33/11KV S/S | 165331.6353 | 136267.0228 | 122011.2214
340 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9654.6 | 9811.6 | 157 | 1000 | 0 | 157000 | 164434.1337 | Tejgaon | Moghbazar 33/11KV S/S | 177991.6827 | 170095.919 | 154167.6401
341 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 122581.3 | 124562.5 | 1981.2 | 1000 | 0 | 1981200 | 2075012.1387 | Kakrail | Moghbazar 33/11KV S/S | 2269581.709 | 2138303.3901 | 1962152.1029
342 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 84471.2 | 85985.5 | 1514.3 | 1000 | 0 | 1514300 | 1586003.8772 | Tejgaon | Moghbazar 33/11KV S/S | 1603212.6065 | 1595983.8968 | 78254.0694
343 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 173266.6 | 174312.8 | 1046.2 | 1000 | 0 | 1046200 | 1095738.7944 | Tejgaon | Moghbazar 33/11KV S/S | 1085008.9734 | 952812.0065 | 1869447.9972
344 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 123156.6 | 123510.7 | 354.1 | 1000 | 0 | 354100 | 370867.0494 | Moghbazar | Moghbazar 33/11KV S/S | 398147.7603 | 399920.9831 | 690345.3929
345 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 113333.9 | 114193.6 | 859.7 | 1000 | 0 | 859700 | 900407.8011 | Kakrail | Moghbazar 33/11KV S/S | 994564.7368 | 950591.9851 | 944645.6784
346 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43654.2 | 328.5 | 1000 | 0 | 328500 | 344054.8595 | Kakrail | Moghbazar 33/11KV S/S | 0 | 0 | 323294.1205
347 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 | 13411749.4952 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0 | 0
348 | 11 kV TCB Feeder | 11 | T-4 | 0 | 1 | 35701.5 | 36240.7 | 539.2 | 1000 | 0 | 539200 | 593608.4852 | Kakrail | Moghbazar 33/11KV S/S | 1091208.9552 | 1058026.2525 | 587067.814
349 | 11 kV Tejgaon SS-2 | 11 | T-4 | 0 | 1 | 30139.8 | 31397.9 | 1258.1 | 1000 | 0 | 1258100 | 1385049.7687 | Tejgaon | Moghbazar 33/11KV S/S | 1574127.4074 | 1532552.8114 | 1481122.0985
350 | Holy Day Inn | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 525840 | 578900.3818 | Tejgaon | Moghbazar 33/11KV S/S | 542740.3295 | 522630.1141 | 493817.3233
351 | Polly Bhabon-2 | 11 | T-4 | 0 | 1 | 18361.1 | 18383 | 21.9 | 1000 | Consumer meter damaged, 12 months average | 25557 | 28135.8532 | Kakrail | Moghbazar 33/11KV S/S | 27898.691 | 30058.9479 | 29444.1053
352 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 | 0 | 1 | 15062.1 | 16752.8 | 1690.7 | 1000 | 0 | 1690700 | 1861301.6803 | Kakrail | Moghbazar 33/11KV S/S | 1854771.9565 | 1842884.7823 | 1860061.7445
353 | 11 kV Tejturibazar | 11 | T-4 | 0 | 1 | 130665.9 | 131432.7 | 766.8 | 1000 | 0 | 766800 | 844174.6782 | Kakrail | Moghbazar 33/11KV S/S | 788742.3253 | 776669.7972 | 731592.6735
354 | Songsad | 11 | T-4 | 0 | 1 | 2920.7 | 3299.2 | 378.5 | 1000 | 0 | 378500 | 416692.9 | Shere b.nagar | Moghbazar 33/11KV S/S | 475259.7411 | 544550.7215 | 126381.9385
355 | Chennel 24 | 11 | T-4 | 0 | 1 | 7312.34 | 7319.22 | 6.88 | 1000 | 0 | 6880 | 7574.2329 | Moghbazar | Moghbazar 33/11KV S/S | 3766.4072 | 1700.7368 | 1164.858
356 | Sonargaon | 11 | T-4 | 0 | 1 | 39618 | 40252.9 | 634.9 | 1000 | 0 | 634900 | 698965.1841 | Kakrail | Moghbazar 33/11KV S/S | 733347.8124 | 844174.3497 | 839625.5215
357 | AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0 | 7215.9345
358 | AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 6414403.1644 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0 | 0
359 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 156809 | 179420 | 22611 | 60 | 0 | 1356660 | 1354639.697 | Kakrail | T&T 33/11 KV | 1410640.1386 | 1413099.3422 | 1314936.3633
360 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 423860 | 446690 | 22830 | 60 | 0 | 1369800 | 1367760.1292 | Kakrail | T&T 33/11 KV | 1475917.0544 | 1466512.1688 | 1363050.3594
361 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 944778 | 951155 | 6377 | 60 | 0 | 382620 | 382050.2122 | Moghbazar | T&T 33/11 KV | 390823.0756 | 376350.3769 | 416269.8468
362 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1943262 | 1958537 | 15275 | 60 | 0 | 916500 | 915135.1719 | Moghbazar | T&T 33/11 KV | 946635.0529 | 901476.4809 | 862940.0791
363 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 590.39 | 618.3 | 27.91 | 60000 | 0 | 1674600 | 1672106.229 | Moghbazar | T&T 33/11 KV | 1759482.372 | 1708010.1623 | 1630130.9123
364 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 885274 | 895318 | 10044 | 60 | 0 | 602640 | 601742.5641 | Kakrail | T&T 33/11 KV | 617435.7813 | 612807.1598 | 591251.5937
365 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 470250 | 488103 | 17853 | 60 | 0 | 1071180 | 1069584.8264 | Moghbazar | T&T 33/11 KV | 1086052.1721 | 1077858.8375 | 1046359.7284
366 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 697644 | 726493 | 28849 | 60 | 0 | 1730940 | 1728362.3289 | Khilgaon | T&T 33/11 KV | 1686240.4748 | 1646555.4045 | 1662984.8723
367 | 11 kv Sherebangla | 11 | 0 | DHK60915 | 1 | 694633 | 717945 | 23312 | 60 | 0 | 1398720 | 1396637.0623 | Moghbazar | T&T 33/11 KV | 1544547.6466 | 1416880.2502 | 1438632.4204
368 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 320497 | 332275 | 11778 | 60 | 0 | 706680 | 705627.6304 | Moghbazar | T&T 33/11 KV | 690498.0173 | 692746.3564 | 708065.6738
369 | Auxiliary | 0 | Export | U0004461 | 1 | 8095.99 | 8095.99 | 0 | 60 | 0 | 0 | 0 | Moghbazar | T&T 33/11 KV | 4061.5417 | 3583.4605 | 3045.4245
370 | West Malibagh | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 973062.72 | 980334.5269 | Moghbazar | Ullon local 33/11KV S/S | 1038100.3806 | 1138226.0536 | 978294.9507
371 | Ullon | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1824492.6 | 1838127.2379 | Moghbazar | Ullon local 33/11KV S/S | 1648747.6632 | 1617479.1288 | 1406298.9916
372 | Mohanagar | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1642043.34 | 1654314.5141 | Moghbazar | Ullon local 33/11KV S/S | 1770877.1198 | 1677385.7633 | 1345155.5572
373 | Bagichartek | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1094695.56 | 1102876.3427 | Moghbazar | Ullon local 33/11KV S/S | 1282359.2936 | 1317945.9568 | 1100581.8195
374 | Mirbagh | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1702859.76 | 1715585.422 | Moghbazar | Ullon local 33/11KV S/S | 1648747.6632 | 1557572.4944 | 1345155.5572
375 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1216328.4 | 1225418.1586 | Moghbazar | Ullon local 33/11KV S/S | 1282359.2936 | 1377852.5912 | 1222868.6883
376 | Jilkanon | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0 | 0
377 | AT-1 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0 | 0
378 | AT-2 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0 | 0
379 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 10.3885 | 12.208 | 1.8195 | 1000000 | 0 | 1819539 | 1839023.3133 | Mugdapara | Madarteck 33/11KV S/S | 1914129.2674 | 1830321.6533 | 1753548.1446
380 | Madertek | 11 | Mugdapara | D0086134 | 1 | 99487.1 | 101422 | 1934.9 | 1000 | 0 | 1934900 | 1955619.6426 | Mugdapara | Madarteck 33/11KV S/S | 2015001.2811 | 1947058.9925 | 1858521.5132
381 | Rajarbagh | 11 | Mugdapara | DHKD9104 | 1 | 0.9 | 1970.5 | 1969.6 | 1000 | 29 days reading Converted | 2105434.4828 | 2127980.2733 | Mugdapara | Madarteck 33/11KV S/S | 2037129.655 | 2033626.6462 | 1264456.5681
382 | Goran | 11 | 0 | X1390296 | 1 | 28663.4 | 30567.9 | 1904.5 | 1000 | 0 | 1904500 | 1924894.1079 | Bashabo | Madarteck 33/11KV S/S | 2047460.5279 | 1968306.9598 | 1851494.7743
383 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 9771.1 | 11288.809 | 1517.709 | 1000 | 0 | 1517709 | 1533961.2033 | Mugdapara | Madarteck 33/11KV S/S | 1583000.8619 | 1493157.2972 | 2039169.8043
384 | Manda | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 0 | 373198.8946 | 881499.2996
385 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 744.7806 | 984.8526 | 240.072 | 1000 | 0 | 240072 | 242642.782 | Mugdapara | Madarteck 33/11KV S/S | 236939.3158 | 229733.5056 | 209712.5124
386 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 3045.3432 | 3710.108 | 664.7648 | 1000 | 0 | 664764.8 | 671883.3535 | Mugdapara | Madarteck 33/11KV S/S | 576962.6065 | 679941.1966 | 331641.7074
387 | Mugdapara | 11 | 0 | X0854272 | 1 | 3885.1 | 4144.6 | 259.5 | 1000 | 0 | 259500 | 262278.8244 | Maniknagar | Madarteck 33/11KV S/S | 99804.6 | 280453.0279 | 256934.2344
388 | Singapur | 11 | 0 | X1390302 (N) | 1 | 33574.1 | 35882.3 | 2308.2 | 1000 | 0 | 2308200 | 2332917.0805 | Banosree | Madarteck 33/11KV S/S | 2449510.2642 | 2359732.7837 | 2200082.1244
389 | Trimohony | 11 | 0 | X1390308 | 1 | 26608.8 | 28688.1 | 2079.3 | 1000 | 0 | 2079300 | 2101565.9326 | Banosree | Madarteck 33/11KV S/S | 2104795.0854 | 2021980.735 | 1604947.893
390 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 12357.722 | 14286.038 | 1928.316 | 1000 | 0 | 1928316 | 1948965.1387 | Mugdapara | Madarteck 33/11KV S/S | 1816135.3069 | 1942171.9601 | 1839386.3794
391 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 4655.1844 | 5501.0628 | 845.8784 | 1000 | 0 | 845878.4 | 854936.3865 | Mugdapara | Madarteck 33/11KV S/S | 710891.4812 | 850151.1099 | 596386.824
392 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 720580 | 730251 | 9671 | 200 | 0 | 1934200 | 1954912.1468 | Mugdapara | Madarteck 33/11KV S/S | 1661387.6173 | 1892982.4123 | 480873.3471
393 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 754033 | 761617 | 7584 | 200 | 0 | 1516800 | 1533042.4693 | Mugdapara | Madarteck 33/11KV S/S | 1508090.9874 | 1450702.4488 | 298789.1572
394 | Nakhal Para Feeder | 11 | 0 | DHK60950 | 1 | 228050.8 | 254232.5 | 26181.7 | 60 | 0 | 1570902 | 1587033.6595 | Tejgaon | Tejgoan 33/11KV S/S | 1590100.5899 | 1545202.0376 | 1536369.5556
395 | Badda-Meghna Feeder | 11 | 0 | DHK60979 | 1 | 901418.5 | 914102.7 | 12684.2 | 60 | 0 | 761052 | 768867.2754 | Tejgaon | Tejgoan 33/11KV S/S | 797427.1133 | 711868.0468 | 842649.7133
396 | Rasulbagh Feeder | 11 | 0 | DHK60948 | 1 | 991762.3 | 1023637.7 | 31875.4 | 60 | 0 | 1912524 | 1932163.7903 | Tejgaon | Tejgoan 33/11KV S/S | 1821935.9992 | 1845073.9247 | 1902151.6741
397 | Lukas | 11 | 0 | 8A021100948-02 | 1 | 66843300 | 69201106 | 2357806 | 1 | 0 | 2357806 | 2382018.4101 | Tejgaon | Tejgoan 33/11KV S/S | 2450636.3287 | 2356930.5125 | 2345545.782
398 | PWD RMU | 11 | 0 | 0 | 1 | 654515.2 | 656351.3 | 1836.1 | 1 | 0 | 1836.1 | 1854.955 | Tejgaon | Tejgoan 33/11KV S/S | 1876.4622 | 1825.2484 | 1757.0539
399 | Civil Aviation Feeder | 11 | 0 | DHK60977 | 1 | 840529.6 | 886999.5 | 46469.9 | 60 | 0 | 2788194 | 2816826.0828 | Tejgaon | Tejgoan 33/11KV S/S | 2972868.5519 | 2843930.4649 | 2795399.6317
400 | Ahasanullah Eng. | 11 | 0 | DHK60867 | 1 | 870599.2 | 881620.2 | 11021 | 60 | 0 | 661260 | 668050.5071 | Tejgaon | Tejgoan 33/11KV S/S | 681476.0179 | 638085.1899 | 673101.4258
401 | New GMG Feeder | 11 | 0 | DHK61106 | 1 | 46250.7 | 86429.3 | 40178.6 | 60 | 0 | 2410716 | 2435471.7452 | Tejgaon | Tejgoan 33/11KV S/S | 2366892.1845 | 2233355.6797 | 2281871.6214
402 | Shikajo | 11 | 0 | HA021101036-02 | 1 | 63571582 | 64377118 | 805536 | 1 | 0 | 805536 | 813808.0835 | Tejgaon | Tejgoan 33/11KV S/S | 877169.4199 | 833321.8823 | 756034.1648
403 | Kahinur | 11 | 0 | 0 | 1 | 518848.9 | 541140.5 | 22291.6 | 60 | 0 | 1337496 | 1351230.8033 | Tejgaon | Tejgoan 33/11KV S/S | 1347009.4431 | 1251045.3402 | 1294083.2246
404 | Link road | 11 | 0 | 8A021100380-02 | 1 | 64330013 | 64751580 | 421567 | 1 | 0 | 421567 | 425896.0895 | Tejgaon | Tejgoan 33/11KV S/S | 415317.8944 | 416737.628 | 435428.3198
405 | Shanta | 11 | 0 | 0 | 1 | 310614.7 | 321223.3 | 10608.6 | 60 | 0 | 636516 | 643052.4099 | Tejgaon | Tejgoan 33/11KV S/S | 671568.0547 | 608607.1616 | 630895.3248
406 | Karnafuly Feeder | 11 | 0 | DHK61084 | 1 | 34410.6 | 35120 | 709.4 | 1000 | 0 | 709400 | 716684.8588 | Tejgaon | Tejgoan 33/11KV S/S | 722759.1976 | 686952.8872 | 738300.0364
407 | Butex | 11 | 0 | 0 | 1 | 991.5 | 1093.4 | 101.9 | 1000 | 0 | 101900 | 102946.4154 | Tejgaon | Tejgoan 33/11KV S/S | 100374.7899 | 90006.1656 | 91610.1416
408 | OriON LAB | 11 | 0 | 0 | 1 | 8102262 | 8195184 | 92922 | 1 | 0 | 92922 | 93876.22 | Tejgaon | Tejgoan 33/11KV S/S | 95833.6401 | 88588.4676 | 248723.2522
409 | Nina kabbo | 11 | 0 | 201101025-2 | 1 | 16842033 | 17125110 | 283077 | 1 | 0 | 283077 | 285983.9298 | Tejgaon | Tejgoan 33/11KV S/S | 281438.971 | 283127.915 | 99489.3009
410 | Satrong | 11 | 0 | HA021100515-2 | 1 | 91425148 | 93305530 | 1880382 | 1 | 0 | 1880382 | 1899691.7228 | Tejgaon | Tejgoan 33/11KV S/S | 1806807.9399 | 1563100.3489 | 1367977.887
411 | South East RMU | 11 | 0 | 0 | 1 | 729.2 | 858.1 | 128.9 | 1000 | 0 | 128900 | 130223.6796 | Tejgaon | Tejgoan 33/11KV S/S | 128807.568 | 139045.3993 | 149070.967
412 | Rangs Bhaban | 11 | 0 | HA021100939-2 | 1 | 432458 | 583380 | 150922 | 1 | 0 | 150922 | 152471.8244 | Tejgaon | Tejgoan 33/11KV S/S | 163396.3968 | 151255.7649 | 161670.1139
413 | Babli | 11 | 0 | 0 | 1 | 56089.7 | 58307.6 | 2217.9 | 1000 | 0 | 2217900 | 2240675.7095 | Tejgaon | Tejgoan 33/11KV S/S | 2109084.7983 | 2111815.0669 | 1541422.4274
414 | SPL | 11 | 0 | 0 | 1 | 3911.5 | 4372.4 | 460.9 | 1000 | 0 | 460900 | 465633.0017 | Tejgaon | Tejgoan 33/11KV S/S | 455733.9249 | 408962.9923 | 372268.4438
415 | DNCC Hospital | 11 | 0 | 0 | 1 | 14537.1 | 15555.1 | 1018 | 1000 | 0 | 1018000 | 1028453.8853 | Tejgaon | Tejgoan 33/11KV S/S | 1058083.8484 | 992388.6083 | 965076.0343
416 | 11/.415 kv Local transformer | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 0 | 6054.2264 | 6134.6077
417 | Gonobhaban | 11 | 0 | DHKC9332 | 1 | 72755.2 | 76114.19 | 3358.99 | 60 | 0 | 201539.4 | 203554.794 | Shere b.nagar | Asad Gate 33/11 KV S/S | 226219.392 | 216875.2359 | 216836.1836
418 | Rapa Plaza Feeder | 11 | 0 | DHKC9339 | 1 | 76499.17 | 95633.85 | 19134.68 | 60 | 0 | 1148080.8 | 1159561.608 | Dhanmondi | Asad Gate 33/11 KV S/S | 1233509.5584 | 1199461.0668 | 1170856.0696
419 | Shukrabad/ South Plaza | 11 | 0 | DHKC9324 | 1 | 15754.76 | 35056.28 | 19301.52 | 60 | 0 | 1158091.2 | 1169672.112 | Shere b.nagar | Asad Gate 33/11 KV S/S | 1195401.7152 | 1120705.5276 | 1130327.1946
420 | Wasa O/H | 11 | 0 | DHKC9333 | 1 | 442.81 | 16726.09 | 16283.28 | 60 | 0 | 976996.8 | 986766.768 | Satmasjid | Asad Gate 33/11 KV S/S | 1324483.5744 | 2118683.8855 | 1049087.4751
421 | Bangabandhu Memorial Museum | 11 | 0 | DHKC9334 | 1 | 15376.97 | 15731.68 | 354.71 | 60 | 0 | 21282.6 | 21495.426 | Dhanmondi | Asad Gate 33/11 KV S/S | 21201.264 | 20854.3329 | 20897.995
422 | Iqbal Road O/H | 11 | 0 | DHKC9330 | 1 | 72221.61 | 98671.81 | 26450.2 | 60 | 0 | 1587012 | 1602882.12 | Shyamoli | Asad Gate 33/11 KV S/S | 1776423.3984 | 1626760.4818 | 1601413.1174
423 | Town Hall | 11 | 0 | DHKC9351 | 1 | 798.64 | 35835.26 | 35036.62 | 60 | 0 | 2102197.2 | 2123219.172 | Shyamoli | Asad Gate 33/11 KV S/S | 2353752.1728 | 1991480.522 | 2338946.2013
424 | Post Office | 11 | 0 | DHKC9331 | 1 | 64790.66 | 89748.19 | 24957.53 | 60 | 0 | 1497451.8 | 1512426.318 | Shyamoli | Asad Gate 33/11 KV S/S | 1672604.0352 | 1378440.8932 | 1492441.2314
425 | Shangshad Bhaban | 11 | 0 | DHKC9370 | 1 | 11515.28 | 15559.57 | 4044.29 | 60 | 0 | 242657.4 | 245083.974 | Shere b.nagar | Asad Gate 33/11 KV S/S | 292942.1376 | 474363.1372 | 422562.5169
426 | Jakir Hossain Road | 11 | 0 | DHKC9373 | 1 | 8235.46 | 30815.6 | 22580.14 | 60 | 0 | 1354808.4 | 1368356.484 | Satmasjid | Asad Gate 33/11 KV S/S | 1603359.2736 | 1792634.4006 | 1277863.2905
427 | New Colony O/H Feeder | 11 | 0 | DHKC9369 | 1 | 86475.56 | 110299.15 | 23823.59 | 60 | 0 | 1429415.4 | 1443709.554 | Satmasjid | Asad Gate 33/11 KV S/S | 1041715.3824 | 0 | 1328527.8719
428 | Aurangzeb Feeder | 11 | 0 | DHKC9321 | 1 | 69565.32 | 95588.91 | 26023.59 | 60 | 0 | 1561415.4 | 1577029.554 | Shyamoli | Asad Gate 33/11 KV S/S | 1636123.104 | 1847282.7847 | 2012075.4293
429 | Asadgate Local Feeder | 11 | 0 | DHKC9338 | 1 | 67929.33 | 99997.41 | 32068.08 | 60 | 0 | 1924084.8 | 1943325.648 | Satmasjid | Asad Gate 33/11 KV S/S | 2129079.8592 | 2381609.9379 | 1832840.2298
430 | Sonarbangla Road | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 0 | 0 | 0
431 | Humayun Road | 11 | 0 | DHKC9366 | 1 | 78786.74 | 110191.48 | 31404.74 | 60 | 0 | 1884284.4 | 1903127.244 | Shyamoli | Asad Gate 33/11 KV S/S | 1920389.3856 | 263604.1533 | 1670349.266
432 | NHA | 11 | 0 | DHKC9374 | 1 | 57115.39 | 61032.09 | 3916.7 | 60 | 0 | 235002 | 237352.02 | Shyamoli | Asad Gate 33/11 KV S/S | 264138.5376 | 26450.7883 | 221861.5773
433 | Auxiliary transformer | 0.415 | 0 | 0 | 1 | 633994 | 651252 | 17258 | 1 | 0 | 17258 | 17430.58 | Satmasjid | Asad Gate 33/11 KV S/S | 0 | 7372.3763 | 6148.5505
434 | Angur Jora | 11 | 0 | 141 | 1 | 6021560 | 8183640 | 2162080 | 1 | 0 | 2162080 | 2196051.2126 | Banosree | Banasree 33/11 SS | 2182461.1184 | 2168323.5267 | 1879685.8324
435 | Block F-G Avenue | 11 | 0 | 68 | 1 | 8177840 | 10767760 | 2589920 | 1 | 0 | 2589920 | 2630613.5558 | Banosree | Banasree 33/11 SS | 2686465.1418 | 2772883.9436 | 2653782.5782
436 | Banasree Main Road(Monpura) | 11 | 0 | 168 | 1 | 6283880 | 8050960 | 1767080 | 1 | 0 | 1767080 | 1794844.8609 | Banosree | Banasree 33/11 SS | 1857089.8973 | 1771391.1453 | 1640446.1666
437 | Baitul Kuddus | 11 | 0 | 62 | 1 | 9606640 | 11812880 | 2206240 | 1 | 0 | 2206240 | 2240905.0671 | Banosree | Banasree 33/11 SS | 2321761.5567 | 2248090.2296 | 2090165.4312
438 | Ideal | 11 | 0 | 0 | 1 | 8292520 | 9057960 | 765440 | 1 | 0 | 765440 | 777466.8098 | Banosree | Banasree 33/11 SS | 813387.6289 | 785714.1589 | 730886.4987
439 | Central Mosque | 11 | 0 | 46 | 1 | 42320 | 2164440 | 2122120 | 1 | #REF! | 2122120 | 2155463.3498 | Banosree | Banasree 33/11 SS | 2252151.7613 | 2213991.1776 | 2027033.5767
440 | Larive | 11 | 0 | 47 | 1 | 9603880 | 10720120 | 1116240 | 1 | 0 | 1116240 | 1133778.6787 | Banosree | Banasree 33/11 SS | 1209136.6977 | 1154817.1834 | 1075325.8802
441 | Bank Colony | 11 | 0 | 0 | 1 | 4697520 | 5431800 | 734280 | 1 | 0 | 734280 | 745817.2151 | Khilgaon | Banasree 33/11 SS | 791659.8328 | 743707.201 | 684269.1356
442 | Salambagh | 11 | 0 | 0 | 1 | 3153240 | 4168440 | 1015200 | 1 | 0 | 1015200 | 1031151.1096 | Khilgaon | Banasree 33/11 SS | 794065.0493 | 937481.2326 | 1234217.735
443 | Titas Road | 11 | 0 | 0 | 1 | 2347080 | 2861160 | 514080 | 1 | 0 | 514080 | 522157.3704 | Khilgaon | Banasree 33/11 SS | 387724.9431 | 442215.7606 | 461564.0031
444 | AT-1 | 0.415 | 0 | 7734 | 1 | 3332.3 | 3405 | 72.7 | 1 | 0 | 72.7 | 73.8423 | Banosree | Banasree 33/11 SS | 76.0089 | 145.5702 | 0
445 | AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 0 | 0 | 0
446 | Meradia | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0 | 0
447 | Shipahibagh | 11 | 0 | HA-021001030-02 | 1 | 37940830 | 39395508 | 1454678 | 1 | 0 | 1454678 | 1499139.6523 | Bashabo | Goran 33/11KV S/S | 1654071.9922 | 1292900.8718 | 1411235.5236
448 | Farazi Hospital | 11 | 0 | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0 | 0
449 | West Bansree | 11 | 0 | New Meter | 1 | 93104250 | 94964796 | 1860546 | 1 | 0 | 1860546 | 1917412.8456 | Banosree | Goran 33/11KV S/S | 1975561.8751 | 1966878.4605 | 1837316.4777
450 | Model School(Nearest) | 11 | 0 | HA-030701099-03 | 1 | 17587620 | 19995869 | 2408249 | 1 | 0 | 2408249 | 2481856.1691 | Banosree | Goran 33/11KV S/S | 2525253.4223 | 2475694.1412 | 2316464.2537
451 | Bhuiyan Para | 11 | 0 | HA-021100508-02 | 1 | 55705410 | 58016858 | 2311448 | 1 | 0 | 2311448 | 2382096.4852 | Banosree | Goran 33/11KV S/S | 2607870.9453 | 2554505.4549 | 2408712.741
452 | Bonobithi (Ideal) School | 11 | 0 | HA-021100879-02 | 1 | 15718670 | 17216488 | 1497818 | 1 | 0 | 1497818 | 1543598.2091 | Banosree | Goran 33/11KV S/S | 1587554.1504 | 1568260.1835 | 1428642.8767
453 | AT-01 | 0.415 | 0 | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0 | 0
454 | AT-02 | 0.415 | 0 | 3043146 | 1 | 4782.5 | 4866.6 | 84.1 | 80 | 0 | 6728 | 6933.6386 | Banosree | Goran 33/11KV S/S | 6257.2038 | 5424.4075 | 4669.3803
455 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1459594.08 | 1473463.6679 | Dhanmondi | Lalmatia 33/11KV S/S | 1695740.7049 | 1418643.1678 | 1399733.2864
456 | Bangabobondhu museum | 11 | Export | 0 | 1 | 627449 | 627449 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0 | 0 | 0
457 | Road No-13/A | 11 | Export | 202006950 | 1 | 80492544 | 82759173 | 2266629 | 1 | 0 | 2266629 | 2288167.324 | Dhanmondi | Lalmatia 33/11KV S/S | 2330507.8061 | 2062161.6863 | 2160918.3029
458 | Jaforabad | 11 | Export | DHK00163 | 1 | 978738 | 3352637 | 2373899 | 1 | 0 | 2373899 | 2396456.6421 | Dhanmondi | Lalmatia 33/11KV S/S | 1846222.5257 | 2324395.3174 | 2181617.4346
459 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0 | 0 | 0
460 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25639.6 | 25827.6 | 188 | 3333.33 | 0 | 626666.04 | 632620.8461 | Dhanmondi | Lalmatia 33/11KV S/S | 655652.5794 | 676925.663 | 643438.6457
461 | Road No -15 | 11 | Export | DHK00162 | 1 | 69712.4 | 70131.2 | 418.8 | 3333.33 | 0 | 1395998.604 | 1409263.8848 | Dhanmondi | Lalmatia 33/11KV S/S | 1205565.6057 | 1637075.4163 | 1478674.7103
462 | Road No-27 South | 11 | Export | DHK00161 | 1 | 77687.3 | 78143.5 | 456.2 | 3333.33 | 0 | 1520665.146 | 1535115.0531 | Dhanmondi | Lalmatia 33/11KV S/S | 1547367.0274 | 1547019.5294 | 1459995.3095
463 | Road 25 | 11 | Export | 0 | 1 | 70235.1 | 70612.1 | 377 | 3333.3 | 0 | 1256654.1 | 1268595.2792 | Dhanmondi | Lalmatia 33/11KV S/S | 1429491.6026 | 1320696.1949 | 1108412.3257
464 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37836.9 | 37971.8 | 134.9 | 3333.33 | 0 | 449666.217 | 453939.1071 | Dhanmondi | Lalmatia 33/11KV S/S | 448887.9755 | 428853.4986 | 403274.921
465 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 60236116 | 61190386 | 954270 | 1 | 0 | 954270 | 963337.8167 | Dhanmondi | Lalmatia 33/11KV S/S | 1202715.5447 | 1761856.4725 | 924073.8841
466 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 69402203 | 71620534 | 2218331 | 1 | 0 | 2218331 | 2239410.379 | Dhanmondi | Lalmatia 33/11KV S/S | 2263478.6281 | 2215613.0537 | 2070071.1797
467 | Lab aid/local RMU | 11 | 0 | 3C65883 | 1 | 59173 | 64063 | 4890 | 300 | 0 | 1467000 | 1482077.1317 | Paribag | Green Road 33/11KV S/S | 1556841.7376 | 1536617.643 | 1422394.5672
468 | Green View | 11 | 0 | DHK000151 | 1 | 67239.7 | 67603.9 | 364.2 | 3333.33 | 0 | 1213998.786 | 1226475.691 | Paribag | Green Road 33/11KV S/S | 1233531.7182 | 1202336.4681 | 1154869.3417
469 | Central Road | 11 | 0 | 65943 | 1 | 21383 | 26887 | 5504 | 300 | 0 | 1651200 | 1668170.2521 | Paribag | Green Road 33/11KV S/S | 1747192.6716 | 1761466.4931 | 1692090.5953
470 | New Market | 11 | 0 | DHK000194 | 1 | 46585.3 | 46951.6 | 366.3 | 3333.33 | 0 | 1220998.779 | 1233547.6266 | Jigatola | Green Road 33/11KV S/S | 1104020.9274 | 1190965.2748 | 1011316.673
471 | DPH Feeder | 11 | 0 | HA-021100459 | 1 | 41611.3 | 41739.9 | 128.6 | 1 | 20 | 243265.68 | 245765.8495 | Paribag | Green Road 33/11KV S/S | 244229.1636 | 236205.0715 | 247670.0176
472 | Dhanmondi Rd 4(md Banglo | 11 | 0 | 6604464 | 1 | 4502.72 | 4526.74 | 24.02 | 60000 | 0 | 1441200 | 1456011.9715 | Jigatola | Green Road 33/11KV S/S | 1566178.5714 | 1573640.9477 | 1319464.1465
473 | Green Road East | 11 | 0 | HA-021101050 | 1 | 95327346 | 96835494 | 1508148 | 1 | 0 | 1508148 | 1523648.0314 | Paribag | Green Road 33/11KV S/S | 1576340.6608 | 1533242.4019 | 1471624.0188
474 | North Road | 11 | 0 | HA-021100884 | 1 | 80273857 | 81964658 | 1690801 | 1 | 0 | 1690801 | 1708178.2525 | Paribag | Green Road 33/11KV S/S | 1755468.3191 | 1721328.8161 | 1634915.8518
475 | Green road SS | 11 | 0 | DHK00135 | 1 | 18489919 | 19740764 | 1250845 | 1 | 0 | 1250845 | 1263700.5929 | Paribag | Green Road 33/11KV S/S | 1250797.3933 | 1224610.5159 | 1315498.6273
476 | Plane Moszid | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 85 | 1033879.14 | 1044504.8605 | Paribag | Green Road 33/11KV S/S | 976916.6543 | 944820.2858 | 990680.0705
477 | Malancha | 11 | 0 | HA-021100953 | 1 | 33261839 | 34719938 | 1458099 | 1 | 0 | 1458099 | 1473084.6514 | Paribag | Green Road 33/11KV S/S | 1290839.3587 | 1378192.0129 | 1148505.9825
478 | AT -1 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5051.3876 | Paribag | Green Road 33/11KV S/S | 5019.8031 | 5016.7079 | 5090.5253
479 | North Dhanmondi | 11 | 0 | BD 014039 | 1 | 22196.95 | 22423.12 | 226.17 | 2000 | 0 | 452340 | 454897.5939 | Paribag | Green Road Dormatory 33/11 SS | 484039.8994 | 504079.3978 | 452285.2955
480 | Lake circus | 11 | 0 | BD 014047 | 1 | 35647.16 | 36603.22 | 956.06 | 2000 | 0 | 1912120 | 1922931.395 | Paribag | Green Road Dormatory 33/11 SS | 2034236.8602 | 2046787.3073 | 1887308.9386
481 | Bashir Uddin | 11 | 0 | BD 014037 | 1 | 14464.14 | 14837.5 | 373.36 | 2000 | 0 | 746720 | 750942.0597 | Paribag | Green Road Dormatory 33/11 SS | 792213.6477 | 798302.5936 | 740604.9957
482 | Raza Bazar | 11 | 0 | BD 013939 | 1 | 21277.2 | 21926.2 | 649 | 2000 | 0 | 1298000 | 1305339.0743 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1333290.6732 | 1329360.3858 | 1277085.001
483 | Rasel Squar | 11 | 0 | BD 013970 | 1 | 32377.3 | 33320.15 | 942.85 | 2000 | 0 | 1885700 | 1896362.0126 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1946515.3317 | 1986224.7792 | 1860400.7233
484 | Bow Bazar | 11 | 0 | BD 013967 | 1 | 24214.38 | 24825.05 | 610.67 | 2000 | 0 | 1221340 | 1228245.6279 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1315379.6859 | 1361417.0663 | 1195690.6937
485 | BRB Hospital | 11 | 0 | BD 014003 | 1 | 12842.2 | 13270.32 | 428.12 | 2000 | 0 | 856240 | 861081.3012 | Shere b.nagar | Green Road Dormatory 33/11 SS | 841735.8151 | 735319.9448 | 733624.2823
486 | Green Road North | 11 | 0 | BD 013969 | 1 | 15378.01 | 15977.85 | 599.84 | 2000 | 0 | 1199680 | 1206463.1592 | Paribag | Green Road Dormatory 33/11 SS | 1244662.5143 | 1225136.5003 | 1163648.4072
487 | Water Bhaban | 11 | 0 | BD 014004 | 1 | 5081.77 | 5261.2 | 179.43 | 2000 | 0 | 358860 | 360889.0448 | Shere b.nagar | Green Road Dormatory 33/11 SS | 369844.7631 | 332111.9703 | 301428.8307
488 | Alamin Road | 11 | 0 | BD 014006 | 1 | 18531.9 | 18834.18 | 302.28 | 2000 | 0 | 604560 | 607978.2671 | Paribag | Green Road Dormatory 33/11 SS | 645158.196 | 644406.723 | 578607.7993
489 | Katal Bagan | 11 | 0 | 0 | 1 | 7743.31 | 8822.65 | 1079.34 | 2000 | 0 | 2158680 | 2170885.4799 | Paribag | Green Road Dormatory 33/11 SS | 2232426.2667 | 2461917.3517 | 1880307.9323
490 | Eastern Pantho chaya | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 0 | 0 | 0
491 | Kalabagan | 11 | 0 | BD 014005 | 1 | 5746.51 | 5906.28 | 159.77 | 2000 | 0 | 319540 | 321346.724 | Paribag | Green Road Dormatory 33/11 SS | 343995.7229 | 360201.2398 | 320179.3518
492 | Univer Hospital | 11 | 0 | BD 013963 | 1 | 885.22 | 1021.63 | 136.41 | 2000 | 0 | 272820 | 274362.5626 | Paribag | Green Road Dormatory 33/11 SS | 281740.4351 | 275219.2974 | 258266.1053
493 | Green Road Staff Quarter(Anowar Khan Medical) | 11 | 0 | BD 013971 | 1 | 9775.84 | 10034.2 | 258.36 | 2000 | 0 | 516720 | 519641.6074 | Paribag | Green Road Dormatory 33/11 SS | 508095.8262 | 507213.6524 | 520651.6433
494 | Matir Masjid | 11 | 0 | DHK00170 | 1 | 22583.2 | 24920.8 | 2337.6 | 888.8889 | 0 | 2077866.6667 | 2085431.7227 | Khilgaon | Taltola 33/11KV S/S | 2167154.5553 | 2177028.2382 | 2023352.6919
495 | Hajipara | 11 | 0 | DHK-00108 | 1 | 3643.3 | 4685.3 | 1042 | 2222.2222 | 0 | 2315555.5556 | 2323985.9847 | Khilgaon | Taltola 33/11KV S/S | 2257545.6108 | 2323390.6234 | 1505682.5673
496 | Nearest Feeder | 11 | 0 | DHK-00106 | 1 | 90788.1 | 91084.5 | 296.4 | 2222.222 | 0 | 658666.6008 | 661064.6612 | Bashabo | Taltola 33/11KV S/S | 0 | 0 | 102528.7436
497 | Reazbagh | 11 | 0 | DHK-00109 | 1 | 95946.5 | 96741.7 | 795.2 | 2222.222 | 0 | 1767110.9344 | 1773544.5971 | Khilgaon | Taltola 33/11KV S/S | 1831021.0001 | 1850181.9906 | 1693614.7124
498 | Chowdhury Para | 11 | 0 | DHK-00107 | 1 | 52456 | 52718.7 | 262.7 | 2222.222 | 0 | 583777.7194 | 585903.1258 | Khilgaon | Taltola 33/11KV S/S | 625509.6106 | 653692.0598 | 575139.5465
499 | Model Colleg | 11 | 0 | 9122392 | 1 | 2506.21 | 2537.32 | 31.11 | 40000 | 0 | 1244400 | 1248930.587 | Khilgaon | Taltola 33/11KV S/S | 1283320.9871 | 723685.6707 | 1038453.9207
500 | East Rampura | 11 | 0 | DHK-00181 | 1 | 98303.2 | 98770.2 | 467 | 2222.222 | 0 | 1037777.674 | 1041555.9945 | Khilgaon | Taltola 33/11KV S/S | 1373711.9053 | 1177184.4648 | 1381135.5698
501 | Adarshabagh | 11 | 0 | DHK-00090 | 1 | 49532.6 | 50492 | 959.4 | 2222.222 | 0 | 2131999.7868 | 2139761.9297 | Bashabo | Taltola 33/11KV S/S | 2323799.4344 | 2249760.2414 | 2012766.0076
502 | Khailgaon Govt Colony | 11 | 0 | DHK00167 | 1 | 75071.6 | 75784.9 | 713.3 | 2222.222 | 0 | 1585110.9526 | 1590881.9934 | Khilgaon | Taltola 33/11KV S/S | 1651220.4486 | 1644511.4325 | 1548206.2687
503 | TV Road | 11 | 0 | 6604434 | 1 | 5070.34 | 5102.73 | 32.39 | 40000 | 0 | 1295600 | 1300316.995 | Khilgaon | Taltola 33/11KV S/S | 1457589.2313 | 1435653.3713 | 1278251.1059
504 | Tilpa Para | 11 | 0 | 06604476 | 1 | 6562.81 | 6589.4 | 26.59 | 40000 | 0 | 1063600 | 1067472.334 | Bashabo | Taltola 33/11KV S/S | 544086.3384 | 925315.57 | 631719.4629
505 | Navana | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 0 | 0
506 | Shantipur | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 0 | 232625.2878
507 | AT-01 | 0.415 | 0 | 9187958 | 1 | 288.03 | 288.03 | 0 | 80 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 388.7134 | 5004.1149
508 | AT-02 | 0.415 | 0 | 9187959 | 1 | 123.08 | 123.08 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 1243.317 | 0
509 | Sher-e-Banglanagar Local | 11 | 0 | DHK 66503 | 1 | 78207 | 80683 | 2476 | 60 | 0 | 148560 | 145611.0642 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 127632.9783 | 130259.0089 | 137740.1655
510 | Mirpur Road East | 11 | 0 | DHK 60961 | 1 | 825101 | 835227 | 10126 | 60 | 0 | 607560 | 595499.8531 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 565408.7832 | 579726.769 | 591320.8565
511 | Gonobhaban school | 11 | 0 | DHK 66492 | 1 | 526229 | 529711 | 3482 | 60 | 0 | 208920 | 204772.9102 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 187053.4171 | 201293.1928 | 178100.36
512 | Babor Road | 11 | 0 | DHK 66489 | 1 | 741733 | 755796 | 14063 | 60 | 0 | 843780 | 827030.8546 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 821146.7988 | 2355047.2749 | 1531864.2685
513 | College Gate | 11 | 0 | DHK 66487 | 1 | 2623105 | 2657171 | 34066 | 60 | 0 | 2043960 | 2003387.1217 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 2118896.2632 | 2029429.4244 | 1693179.314
514 | Parade ground | 11 | 0 | DHK 66490 | 1 | 938265 | 938267 | 2 | 60 | 0 | 120 | 117.618 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 1062.133 | 1780.3054
515 | Hospital RMU | 11 | 0 | DHK 66491 | 1 | 893230 | 904485 | 11255 | 60 | 0 | 675300 | 661895.205 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 606359.9098 | 560499.4711 | 544171.0965
516 | Shamoly Square | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 0 | 0 | 0
517 | Gonobhaban RMU | 11 | 0 | DHK 60964 | 1 | 192801.1 | 194454.7 | 1653.6 | 60 | 0 | 99216 | 97246.5492 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 98796.0682 | 102753.2911 | 81921.1363
518 | Krishi University | 11 | 0 | DHK 60963 | 1 | 350091.4 | 360437.8 | 10346.4 | 60 | 0 | 620784 | 608461.3549 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 589560.5067 | 563852.3796 | 574020.0379
519 | NEC | 11 | 0 | DHK 86073 | 1 | 34.66 | 39.37 | 4.71 | 60000 | 0 | 282600 | 276990.3524 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 279104.941 | 274760.4607 | 284784.5503
520 | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 362.71 | 381.55 | 18.84 | 60000 | 0 | 463464 | 454264.1779 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 491118.4828 | 467152.1267 | 453385.8053
521 | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 362.71 | 381.55 | 18.84 | 60000 | 0 | 666936 | 653697.2316 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 706731.4752 | 672243.3043 | 652433.232
522 | Netor | 11 | 0 | DHK 60962 | 1 | 114054.4 | 124560.4 | 10506 | 60 | 0 | 630360 | 617847.27 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 628517.1836 | 620062.5542 | 596532.4766
523 | BICC | 11 | 0 | 0 | 1 | 34.66 | 39.37 | 4.71 | 60000 | 0 | 282600 | 276990.3524 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 279104.941 | 193459.8492 | 69152.9813
524 | Auxiliary | 0.415 | 0 | 0 | 1 | 5228.9 | 5279.71 | 50.81 | 60 | 0 | 3048.6 | 2988.0849 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 4296.3279 | 3895.3081 | 5642.8833
525 | City Corporation | 11 | 0 | 93 | 1 | 40386420 | 41951856 | 1565436 | 1 | 0 | 1565436 | 1583920.0344 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 672002.1574 | 951549.8845 | 660250.7383
526 | Bot tola | 11 | 0 | 0 | 1 | 53690908 | 56049584 | 2358676 | 1 | 0 | 2358676 | 2386526.2912 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 2395209.9678 | 2298336.7826 | 2240795.0697
527 | Jhilpar | 11 | 0 | 145 | 1 | 34782876 | 35789952 | 1007076 | 1 | 0 | 1007076 | 1018967.1456 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1203846.2525 | 1011093.8025 | 1160185.3486
528 | Central Bashaboo | 11 | 0 | 128 | 1 | 37782388 | 38835864 | 1053476 | 1 | 0 | 1053476 | 1065915.018 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 2018436.7723 | 1763582.1465 | 1733572.9987
529 | Kadamtala | 11 | 0 | 8 | 1.5 | 18572154 | 19006514 | 434360 | 1 | 0 | 651540 | 659233.1205 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 895857.2066 | 680353.9053 | 1958904.8441
530 | Ansar VDP | 11 | 0 | 119 | 1 | 19018394 | 19583192 | 564798 | 1 | 0 | 564798 | 571466.9061 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 611327.4182 | 1128730.4864 | 727503.1317
531 | Mugda Hospital Express-01 | 11 | 0 | 0 | 1 | 5903745 | 6214345 | 310600 | 1 | 0 | 310600 | 314267.439 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 307500.5637 | 293639.1125 | 272764.3875
532 | Boro Masjid | 11 | 0 | 7 | 1.22 | 47940324 | 49075360 | 1135036 | 1 | 0 | 1384743.92 | 1401094.4155 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1717015.7129 | 1405726.812 | 1342757.2732
533 | Anandodhara | 11 | 0 | 120 | 1 | 46909724 | 47889764 | 980040 | 1 | 0 | 980040 | 991611.9155 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 1008287.8477 | 964251.0175 | 915566.0508
534 | Culvert | 11 | 0 | 117 | 1 | 38905824 | 40800540 | 1894716 | 1 | 0 | 1894716 | 1917088.0393 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 2175998.5274 | 1824104.3237 | 1912589.1389
535 | Mugda Hospital Express-02 | 11 | 0 | 97 | 1 | 4845548 | 4845548 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0 | 0 | 0
536 | Jhor Pukur | 11 | 0 | 98 | 1 | 26401136 | 27342334 | 941198 | 1 | 0 | 941198 | 952311.2849 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1695311.8425 | 1643349.6255 | 1429146.8866
537 | T&T | 11 | 0 | 99 | 1 | 23345024 | 23934662 | 589638 | 1 | 0 | 589638 | 596600.2068 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 721459.9725 | 567104.166 | 852556.8368
538 | Haider Ali | 11 | 0 | 9 | 1 | 67435952 | 69907712 | 2471760 | 1 | 0 | 2471760 | 2500945.5412 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 2687168.9248 | 2028073.3969 | 1439434.5953
539 | 11kv Tilpapara | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 2128574.7 | 2153708.0482 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 2169910.6664 | 2181802.1625 | 2151612.2434
540 | AT-01 | 11 | 0 | 0 | 1 | 2964 | 3043 | 79 | 1 | 0 | 79 | 79.9328 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 89.8242 | 94.3756 | 0
541 | AT-02 | 11 | 0 | 0 | 1 | 17.34 | 17.34 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0.34315 | 0 | 8.4563
542 | Shantinagar s/s-1 | 11 | 0 | DHK60932 | 1 | 324830 | 343950 | 19120 | 60 | 0 | 1147200 | 1164408 | Rajarbag | Khillgaon 33/11KV S/S | 2916346.3506 | 2755360.6206 | 2616486.0095
543 | Gulbagh | 11 | 0 | DHK60934 | 1 | 122528 | 140286 | 17758 | 60 | 0 | 1065480 | 1081462.2 | Rajarbag | Khillgaon 33/11KV S/S | 329175.3109 | 325114.8574 | 314880.9114
544 | Rampura BTV | 11 | 0 | DHK60933 | 1 | 14073 | 14073 | 0 | 60 | 0 | 0 | 0 | Khilgaon | Khillgaon 33/11KV S/S | 0 | 1220.4011 | 241.3343
545 | West Shantibag | 11 | 0 | DHK60926 | 1 | 520515 | 535058 | 14543 | 60 | 0 | 872580 | 885668.7 | Rajarbag | Khillgaon 33/11KV S/S | 934072.7507 | 932020.3326 | 912726.2746
546 | East Malibagh | 11 | 0 | DHK60929 | 1 | 585478 | 605416 | 19938 | 60 | 0 | 1196280 | 1214224.2 | Rajarbag | Khillgaon 33/11KV S/S | 1558104.7013 | 1377100.6198 | 1289630.0978
547 | Police Line | 11 | 0 | DHK60930 | 1 | 565142 | 575003 | 9861 | 60 | 0 | 591660 | 600534.9 | Rajarbag | Khillgaon 33/11KV S/S | 624772.6414 | 596226.9654 | 576125.2774
548 | PWD RMU 11 KV Sajanpur Feeder. | 11 | 0 | DHK61017 | 1 | 192855 | 195323 | 2468 | 60 | 0 | 148080 | 150301.2 | Rajarbag | Khillgaon 33/11KV S/S | 152458.8445 | 149621.1769 | 146188.2445
549 | Benjir Bagan | 11 | 0 | DHK60985 | 1 | 164032 | 167244 | 3212 | 60 | 0 | 192720 | 195610.8 | Rajarbag | Khillgaon 33/11KV S/S | 195480.6318 | 194653.9781 | 180699.0476
550 | AT-1 & AT-2 | 0.415 | 0 | ELIB 7374 | 1 | 1983.75 | 2093.26 | 109.51 | 60 | 0 | 6570.6 | 6669.159 | Rajarbag | Khillgaon 33/11KV S/S | 7349.5039 | 14431.2432 | 0
551 | Spare | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 0 | 0 | 0
552 | Monipuripara west | 11 | 0 | BD013947 | 1 | 30306.07 | 31132.65 | 826.58 | 1000 | 0 | 826580 | 830035.6978 | Shere b.nagar | Monipuripara 33/11 KV S/S | 847623.509 | 861249.4503 | 873090.4062
553 | Biggan College | 11 | 0 | BD013949 | 1 | 18139.4 | 19012.35 | 872.95 | 1000 | 0 | 872950 | 876599.5577 | Kakrail | Monipuripara 33/11 KV S/S | 835521.2072 | 819870.1443 | 853994.1863
554 | Green Road South | 11 | 0 | BD013948 | 1 | 28643.32 | 29611.68 | 968.36 | 1000 | 0 | 968360 | 972408.44 | Shere b.nagar | Monipuripara 33/11 KV S/S | 975210.3173 | 1037302.1428 | 986346.7996
555 | BARC Building O/H | 11 | 0 | BD014010 | 1 | 12825.53 | 13424.05 | 598.52 | 1000 | 0 | 598520 | 601022.2433 | Shere b.nagar | Monipuripara 33/11 KV S/S | 634425.9824 | 629218.3029 | 632910.7169
556 | Green Road North | 11 | 0 | BD014036 | 1 | 57019.83 | 58901.44 | 1881.61 | 1000 | 0 | 1881610 | 1889476.4806 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1966221.9789 | 1919532.2257 | 1871294.3358
557 | Chundrima Uddan | 11 | 0 | BD014035 | 1 | 29068.98 | 30066.87 | 997.89 | 1000 | 0 | 997890 | 1002061.8966 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1070591.3324 | 1032887.2799 | 1015615.1889
558 | RMU-1 Feeder | 11 | 0 | BD013940 | 1 | 283.07 | 545 | 261.93 | 1000 | 0 | 261930 | 263025.0554 | Shere b.nagar | Monipuripara 33/11 KV S/S | 137015.3458 | 147255.7457 | 0
559 | Spare-03 | 11 | 0 | BD013946 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0 | 0
560 | kawran Bazar North | 11 | 0 | BD013964 | 1 | 40221.55 | 40298.72 | 77.17 | 1000 | 0 | 77170 | 77492.626 | Kakrail | Monipuripara 33/11 KV S/S | 79448.9981 | 30221.7434 | 0
561 | NAM Bhanan RMU | 11 | 0 | BD013950 | 1 | 15281.88 | 16243.17 | 961.29 | 1000 | 0 | 961290 | 965308.8823 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1005888.2452 | 1030950.7605 | 1013545.3917
562 | Novo Theater | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0 | 0
563 | Monipuripara Nearest | 11 | 0 | BD013962 | 1 | 37303.94 | 38123.77 | 819.83 | 1000 | 0 | 819830 | 823257.478 | Tejgaon | Monipuripara 33/11 KV S/S | 844317.6909 | 794156.578 | 733061.8614
564 | Holy Cross | 11 | 0 | BD013965 | 1 | 36115.46 | 37352.96 | 1237.5 | 1000 | 0 | 1237500 | 1242673.6384 | Tejgaon | Monipuripara 33/11 KV S/S | 1267377.9768 | 1286005.418 | 1126874.592
565 | Honda Goli | 11 | 0 | BD014011 | 1 | 13245.54 | 14300.32 | 1054.78 | 1000 | 0 | 1054780 | 1059189.7376 | Tejgaon | Monipuripara 33/11 KV S/S | 1074102.0051 | 1068926.6085 | 953126.0337
566 | Navy Quarter | 11 | 0 | BD013941 | 1 | 5132.94 | 5353.54 | 220.6 | 1000 | 0 | 220600 | 221522.2664 | Tejgaon | Monipuripara 33/11 KV S/S | 200143.5254 | 202962.2853 | 175339.91
567 | AT-01 | 0.415 | 0 | 0 | 1 | 1913.87 | 1989.96 | 76.09 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0 | 0
568 | AT-02 | 0.415 | 0 | 0 | 1 | 585.48 | 585.48 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0 | 0
569 | Doctor Goli | 11 | 0 | BD013944 | 1 | 7728.79 | 8689.39 | 960.6 | 1000 | 0 | 960600 | 963950.8063 | Moghbazar | Ispahani 33/11 KV SS | 948233.0953 | 958270.3835 | 898591.0283
570 | Ispahani | 11 | 0 | BD013947 | 1 | 8623.82 | 9707.76 | 1083.94 | 1000 | 0 | 1083940 | 1087721.0462 | Moghbazar | Ispahani 33/11 KV SS | 1055882.4039 | 1058199.8531 | 999582.0108
571 | BTCL | 11 | 0 | BD013949 | 1 | 4485.67 | 5033.71 | 548.04 | 1000 | 0 | 548040 | 549951.6967 | Kakrail | Ispahani 33/11 KV SS | 529591.2713 | 523726.617 | 532492.3633
572 | Vikarunnesa | 11 | 0 | BD013948 | 1 | 5237.35 | 6385.39 | 1148.04 | 1000 | 0 | 1148040 | 1152044.6426 | Kakrail | Ispahani 33/11 KV SS | 1148347.0254 | 1136233.5895 | 1092064.7445
573 | OASIS | 11 | 0 | 0 | 1 | 4.29 | 113.31 | 109.02 | 1000 | 0 | 109020 | 109400.2883 | Kakrail | Ispahani 33/11 KV SS | 4342.8205 | 0 | 0
574 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
575 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
576 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
577 | Wireless | 11 | 0 | 0 | 1 | 6771.63 | 7852.04 | 1080.41 | 1000 | 0 | 1080410 | 1084178.7327 | Moghbazar | Ispahani 33/11 KV SS | 1047125.901 | 1048087.1638 | 896344.5253
578 | Kazir Goli | 11 | 0 | 0 | 1 | 6092.57 | 7285.49 | 1192.92 | 1000 | 0 | 1192920 | 1197081.1949 | Kakrail | Ispahani 33/11 KV SS | 1203659.779 | 1263311.3532 | 1182067.1763
579 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
580 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
581 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
582 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
583 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
584 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
585 | AT-01 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
586 | AT-02 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0 | 0
587 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 213015.1 | 215487.3 | 2472.2 | 1000 | 0 | 2472200 | 2486440.3485 | Siddirgonj | Siddhirganj 33/11KV S/S | 2725888.0748 | 2549641.8301 | 2438789.3271
588 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16876.9 | 17004 | 127.1 | 1000 | 0 | 127100 | 127832.1205 | Siddirgonj | Siddhirganj 33/11KV S/S | 148265.7961 | 145583.9006 | 138711.8093
589 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 108320.7 | 109803.3 | 1482.6 | 1000 | 0 | 1482600 | 1491140.0618 | Siddirgonj | Siddhirganj 33/11KV S/S | 1611243.3589 | 1535819.0344 | 1523513.0022
590 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 169879.3 | 172372.4 | 2493.1 | 1000 | 0 | 2493100 | 2507460.7365 | Siddirgonj | Siddhirganj 33/11KV S/S | 2663481.8388 | 2529191.2405 | 2405949.7847
591 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 7001.5 | 7069.4 | 67.9 | 1000 | 0 | 67900 | 68291.1171 | Siddirgonj | Siddhirganj 33/11KV S/S | 54248.5581 | 41407.382 | 36566.7297
592 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 74651.5 | 76031.2 | 1379.7 | 1000 | 0 | 1379700 | 1387647.3379 | Siddirgonj | Siddhirganj 33/11KV S/S | 1431264.5899 | 1311672.4727 | 1337959.5143
593 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0 | 0
594 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0 | 0
595 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 146439.6 | 148801 | 2361.4 | 1000 | 0 | 2361400 | 2375002.1192 | Siddirgonj | Siddhirganj 33/11KV S/S | 2446793.5192 | 2328937.4468 | 2238024.8856
596 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 79.1918 | 87.4121 | 8.2203 | 40000 | 0 | 328812 | 330706.0205 | Matuail | Siddhirganj 33/11KV S/S | 314747.6869 | 291293.3394 | 424399.7103
597 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0 | 0
598 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 14255.5 | 14944 | 688.5 | 1000 | 0 | 688500 | 692465.8927 | Siddirgonj | Siddhirganj 33/11KV S/S | 722974.2051 | 681450.0937 | 758130.0486
599 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0 | 0
600 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 146418.5 | 149268.1 | 2849.6 | 1000 | 0 | 2849600 | 2866014.2453 | Siddirgonj | Siddhirganj 33/11KV S/S | 2915044.2314 | 2806489.0873 | 2820775.6603
601 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 | 0 | HA021101013-02 | 1 | 46067484 | 48556720 | 2489236 | 1 | 0 | 2489236 | 2482601.3667 | Matuail | Demra 33/11KV S/S | 2346002.1943 | 2312393.5546 | 2206583.7096
602 | 11 kV DND (WASA) Feeder. | 11 | 0 | HA021100992-02 | 1 | 5613260 | 5963540 | 350280 | 1 | 0 | 350280 | 349346.3885 | Siddirgonj | Demra 33/11KV S/S | 251256.153 | 80170.7162 | 6927.7253
603 | 11 kV Local Feeder | 11 | 0 | HA021100794-02 | 1 | 9848922 | 11042260 | 1193338 | 1 | 0 | 1193338 | 1190157.3614 | Siddirgonj | Demra 33/11KV S/S | 1182388.6301 | 2088621.9879 | 1417684.9395
604 | 11 kV Mouchak Feeder | 11 | 0 | DHK60888 | 1 | 893731.2 | 934490.7 | 40759.5 | 60 | 0 | 2445570 | 2439051.751 | Siddirgonj | Demra 33/11KV S/S | 2339275.7144 | 2308639.9015 | 2074135.4747
605 | 11 kV Overhead-1 Feeder | 11 | 0 | HA021100829-02 | 1 | 78137143 | 78628660 | 491517 | 1 | 0 | 491517 | 490206.9454 | Siddirgonj | Demra 33/11KV S/S | 1190489.8427 | 1095153.438 | 1095304.9401
606 | 11 kV Provati Steel Feeder | 11 | 0 | DHK60874 | 1 | 546973.2 | 581989.2 | 35016 | 60 | 0 | 2100960 | 2095360.2501 | Siddirgonj | Demra 33/11KV S/S | 124835.9443 | 0 | 0
607 | 11 kV Islambagh Feeder. | 11 | 0 | DHKA2190 | 1 | 1048.5044 | 1099.163 | 50.6586 | 60000 | 0 | 3039516 | 3031414.6894 | Matuail | Demra 33/11KV S/S | 2979112.0563 | 3002442.9965 | 2983539.0327
608 | 11 kV Taj Jute Feeder. | 11 | 0 | DHK61062 | 1 | 613805.1 | 622580.6 | 8775.5 | 60 | 0 | 526530 | 525126.6242 | Siddirgonj | Demra 33/11KV S/S | 1404410.5059 | 1676660.8446 | 1675376.4941
609 | 11 kV Al-Aksa Steel Feeder | 11 | 0 | DHK61061 | 1 | 758979.9 | 787050.2 | 28070.3 | 60 | 0 | 1684218 | 1679729.0047 | Siddirgonj | Demra 33/11KV S/S | 1595509.5853 | 1474597.4818 | 1597579.1906
610 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 | 0 | DHKA2189 | 1 | 986.7258 | 1031.247 | 44.5212 | 60000 | 0 | 2671272 | 2664152.1809 | Siddirgonj | Demra 33/11KV S/S | 2514049.716 | 2467512.3805 | 2370283.5934
611 | 11 kV Over Head Feeder-2. | 11 | 0 | HA021100488-02 | 1 | 26957261 | 29160410 | 2203149 | 1 | 0 | 2203149 | 2197276.8827 | Demra | Demra 33/11KV S/S | 2204224.8423 | 2131027.6013 | 2071443.4949
612 | 11 kV Shimrail Express Feeder. | 11 | 0 | HA021100511-02 | 1 | 8169444 | 8222669 | 53225 | 1 | 0 | 53225 | 53083.1379 | Siddirgonj | Demra 33/11KV S/S | 75076.7556 | 29225.6688 | 0
613 | 11 kV Sarder & Khadem Steel Feeder | 11 | 0 | HA021100413-02 | 1 | 80731969 | 81142180 | 410211 | 1 | 0 | 410211 | 409117.6527 | Demra | Demra 33/11KV S/S | 331227.7744 | 650733.1002 | 409613.9007
614 | 11 kV Siddhirgonj Mazar Feeder | 11 | 0 | HA021100393-02 | 1 | 23396.457 | 23713.14 | 316.683 | 1000 | Second Swtichgear Consumption Added | 1217452 | 1214207.0897 | Siddirgonj | Demra 33/11KV S/S | 1262090.4156 | 281800.301 | 832832.3648
615 | 11 kV AST Beverage Feeder | 11 | 0 | 0 | 1 | 21373122 | 22265980 | 892858 | 1 | 0 | 892858 | 890478.2395 | Siddirgonj | Demra 33/11KV S/S | 1164572.2996 | 1051751.2525 | 1163750.6238
616 | 11 kV Karim Market Feeder | 11 | 0 | 0 | 1 | 56008.912 | 58307.25 | 2298.338 | 1000 | 0 | 2298338 | 2292212.1727 | Matuail | Demra 33/11KV S/S | 2119617.9699 | 2072299.946 | 2089377.8867
617 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 0 | 0 | 0
618 | 11 kV Dayagonj Feeder (=L11) | 11 | 0 | 2007755114 | 1 | 5767.7 | 5809.87 | 42.17 | 60000 | 0 | 2530200 | 2567812.3685 | Demra | Sarulia 33/11KV S/S | 2674737.7934 | 2648546.8605 | 3036942.6611
619 | 11 kV Karim Jute Feeder (=L12) | 11 | 0 | 30799484 | 1 | 21.3509 | 21.5916 | 0.2407 | 60000 | 0 | 14442 | 14656.6857 | Demra | Sarulia 33/11KV S/S | 14157.8637 | 13577.9934 | 12817.0467
620 | 11 kV Konapara (=L13) **** | 11 | 0 | DHKA2191 | 1 | 2064.619 | 2121.1009 | 56.4819 | 60000 | 0 | 3388914 | 3439291.4731 | Demra | Sarulia 33/11KV S/S | 3588042.0557 | 3482255.5223 | 2467003.1131
621 | 11 kV Sanarpar Feeder (=L14) | 11 | 0 | 575926 | 1 | 51041.5 | 53570.6 | 2529.1 | 1000 | 0 | 2529100 | 2566696.0166 | Matuail | Sarulia 33/11KV S/S | 2627544.9143 | 2556143.6589 | 2386518.0767
622 | 11 kV Latif Bawani Feeder (=L15) | 11 | 0 | 30799450 | 1 | 1809.19 | 1814.55 | 5.36 | 60000 | 0 | 321600 | 326380.7042 | Demra | Sarulia 33/11KV S/S | 261798.4288 | 295524.6849 | 302404.9427
623 | 11 kV Tengra Feeder (=L16) | 11 | 0 | 30799145 | 1 | 5472.12 | 5519.55 | 47.43 | 60000 | 0 | 2845800 | 2888103.8805 | Demra | Sarulia 33/11KV S/S | 2785803.7935 | 2203397.2826 | 3315319.3041
624 | 11 kV Police Line Feeder (=L17) | 11 | 0 | 30799480 | 1 | 3317.32 | 3337.55 | 20.23 | 60000 | 0 | 1213800 | 1231843.5906 | Demra | Sarulia 33/11KV S/S | 1213792.7153 | 1297576.8726 | 1183247.2468
625 | 11 kV Demra Bazar Feeder (=L18) | 11 | 0 | 30799119 | 1 | 1639.93 | 1648.7 | 8.77 | 60000 | 0 | 526200 | 534022.1596 | Demra | Sarulia 33/11KV S/S | 561432.5279 | 558765.1604 | 495803.4526
626 | 11 kV Spare Feeder (=F9) | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0 | 0
627 | 11 kV Boxnagar Feeder (=F10) | 11 | 0 | HA021100493-02 | 1 | 80604576 | 83621868 | 3017292 | 1 | 0 | 3017292 | 3062145.1731 | Demra | Sarulia 33/11KV S/S | 3047117.0714 | 3001937.8862 | 2753359.8865
628 | 11 kV Baser Pool Feeder (=L11) | 11 | 0 | HA021100518-02 | 1 | 50869565 | 50869565 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 1592.7597 | 158210.2162 | 30254.1689
629 | 11 kV Dip-Pur Feeder (=L12) | 11 | 0 | HA021100697-02 | 1 | 22773043 | 25005518 | 2232475 | 1 | 0 | 2232475 | 2265661.5752 | Demra | Sarulia 33/11KV S/S | 2324189.2905 | 2304863.862 | 2171918.011
630 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0 | 0
631 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0 | 0
632 | 11 kV Khanpur Feeder | 11 | 0 | DHKC 9348 | 1 | 47198.82 | 76101.38 | 28902.56 | 60 | 0 | 1734153.6 | 1753296.6737 | N.Gonj (East) | Khanpur 33/11KV S/S | 1849730.4598 | 1858439.2031 | 1689432.0922
633 | 11 kV Mission Para Feeder. | 11 | 0 | DHKC 9347 | 1 | 32560.85 | 59807.26 | 27246.41 | 60 | 0 | 1634784.6 | 1652830.7535 | N.Gonj (East) | Khanpur 33/11KV S/S | 1736094.2229 | 1666330.9001 | 1591097.4109
634 | 11 kV Esha Kha Feeder | 11 | 0 | DHKC 9311 | 1 | 79951.21 | 95916.86 | 15965.65 | 60 | 0 | 957939 | 968513.5517 | N.Gonj (East) | Khanpur 33/11KV S/S | 939733.5453 | 917602.1317 | 1040108.3114
635 | 11 kV New Hazigonj Feeder | 11 | 0 | DHKC 9314 | 1 | 170.34 | 205.54 | 35.2 | 60000 | 0 | 2112000 | 2135314.0661 | N.Gonj (East) | Khanpur 33/11KV S/S | 2193735.673 | 2054393.8757 | 2135156.6373
636 | 11 kV Spare Feeder. | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
637 | 11 kV Hospital RMU Feeder. | 11 | 0 | 6604412 | 1 | 4.9 | 5.95 | 1.05 | 60000 | 0 | 63000 | 63695.448 | N.Gonj (East) | Khanpur 33/11KV S/S | 65004.0756 | 61352.3895 | 59949.0945
638 | 11 kV Old Hajiganj Feeder. | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 0 | 0 | 0
639 | 11 kV Siraj-ud-daullah Feeder. | 11 | 0 | 06604389 | 1 | 6245.25 | 27741.38 | 21496.13 | 60 | 0 | 1289767.8 | 1304005.3624 | N.Gonj (East) | Khanpur 33/11KV S/S | 1304824.3795 | 1324560.4284 | 1260578.6756
640 | 11 kV Spare Feeder. | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
641 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
642 | 11 kV B. B. Road West Feeder. | 11 | 0 | 6604415 | 1 | 234.81 | 282.18 | 47.37 | 40000 | 0 | 1894800 | 1915716.4264 | N.Gonj (West) | Khanpur 33/11KV S/S | 1976042.8964 | 1840166.7201 | 1800087.6245
643 | 11 kV Mondalpara Feeder. | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
644 | 11 kV B. B. Road East Feeder. | 11 | 0 | 06604392 | 1 | 183.1 | 220.31 | 37.21 | 40000 | 0 | 1488400 | 1504830.2349 | N.Gonj (East) | Khanpur 33/11KV S/S | 1509066.5776 | 1463548.0912 | 1396793.7162
645 | 11 kV Bishaw Road Feeder. | 11 | 0 | 06604393 | 1 | 221.32 | 251.26 | 29.94 | 40000 | 0 | 1197600 | 1210820.1352 | N.Gonj (East) | Khanpur 33/11KV S/S | 1222724.6371 | 1779421.78 | 1969640.6189
646 | 11 kV Chasara Feeder. | 11 | 0 | 06604391 | 1 | 258.76 | 310.22 | 51.46 | 40000 | 0 | 2058400 | 2081122.3834 | N.Gonj (West) | Khanpur 33/11KV S/S | 2195963.227 | 2115948.7484 | 2048765.3497
647 | 11 kV Pathan Tully Feeder. | 11 | 0 | 06604388 | 1 | 33.69 | 37.66 | 3.97 | 40000 | 0 | 158800 | 160552.9705 | N.Gonj (East) | Khanpur 33/11KV S/S | 39690.9621 | 0 | 0
648 | 11 kV Spare Feeder. | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
649 | 11 kV Nayamati Feeder. | 11 | 0 | 6604289 | 1 | 169.17 | 202.39 | 33.22 | 40000 | 0 | 1328800 | 1343468.4333 | N.Gonj (East) | Khanpur 33/11KV S/S | 1193968.9401 | 1316545.3361 | 1343505.6323
650 | 11 kV Spare Feeder. | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
651 | 11 kV Spare Feeder. | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
652 | 11 kV Spare Feeder. | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0 | 0
653 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 | 0 | 412109 | 1 | 9113.7 | 9145.8 | 32.1 | 10 | 0 | 321 | 324.5435 | N.Gonj (East) | Khanpur 33/11KV S/S | 42.526 | 0 | 0
654 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 | 0 | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 | 0 | 3000 | 3033.1166 | N.Gonj (East) | Khanpur 33/11KV S/S | 3037.5736 | 3037.247 | 3027.732
655 | 11 kV Link Road Feeder | 11 | 0 | HA021100475-02 | 1 | 88158.496 | 91112.32 | 2953.824 | 1000 | 0 | 2953824 | 2975929.581 | N.Gonj (East) | Matuail 33/11KV S/S | 2607402.2302 | 1951841.3049 | 1877540.2045
656 | 11 kV Lamapara Express Feeder | 11 | 0 | HA021100928-03 | 1 | 77285.778 | 78379.26 | 1093.482 | 1000 | 0 | 1093482 | 1101665.3091 | N.Gonj (East) | Matuail 33/11KV S/S | 726895.7131 | 1017580.9915 | 1063497.0225
657 | 11 kV Kutubpur Feeder*** | 11 | 0 | DHK66616 | 1 | 17710.59 | 17905.31 | 194.72 | 8000 | 0 | 1557760 | 1569417.834 | N.Gonj (East) | Matuail 33/11KV S/S | 1641482.3695 | 1554956.8642 | 1703285.4205
658 | 11 kV Ramarbagh Feeder (F1) | 11 | 0 | DHK66625 | 1 | 3508.42 | 3533.8 | 25.38 | 60000 | 0 | 1522800 | 1534196.2033 | Fatullah | Matuail 33/11KV S/S | 1364062.3916 | 1338941.0426 | 835792.1765
659 | 11 kV Tushardhara Feeder (F2) | 11 | 0 | DHK66623 | 1 | 3791.19 | 3837.99 | 46.8 | 60000 | 0 | 2808000 | 2829014.2755 | Matuail | Matuail 33/11KV S/S | 2689931.0362 | 2755784.1096 | 2760297.6743
660 | 11 kV Matuail Medical Feeder (F3) | 11 | 0 | DHK66627 | 1 | 3284.92 | 3301.78 | 16.86 | 60000 | 0 | 1011600 | 1019170.5275 | Matuail | Matuail 33/11KV S/S | 792368.687 | 795452.7012 | 696897.8308
661 | 11 kV Rupayan Town Feeder (F4) | 11 | 0 | HA021101044-02 | 1 | 65554.037 | 65883.888 | 329.851 | 1000 | 0 | 329851 | 332319.5113 | Matuail | Matuail 33/11KV S/S | 349545.5347 | 361905.6203 | 323912.9361
662 | 11 kV Shibu Market Feeder (F7) | 11 | 0 | DHK66624 | 1 | 2368.99 | 2377.51 | 8.52 | 60000 | 0 | 511200 | 515025.6758 | Fatullah | Matuail 33/11KV S/S | 398306.2183 | 387075.6832 | 615623.4101
663 | 11 kV Soma-Sagar Steel (F6) | 11 | 0 | HA060300286-03 | 1 | 961.358 | 2257.503 | 1296.145 | 1000 | 959253 | 1486842.15 | 1497969.2549 | Fatullah | Matuail 33/11KV S/S | 1502329.9696 | 1201993.7471 | 1110650.3388
664 | 11 kV Jhalkuri Feeder (F8) | 11 | 0 | DHK66626 | 1 | 4378.18 | 4421.83 | 43.65 | 60000 | 0 | 2619000 | 2638599.8531 | Matuail | Matuail 33/11KV S/S | 2625668.5413 | 2669361.5514 | 2690547.2387
665 | 11 kV Madani Nagar Feeder (F9) | 11 | 0 | DHK6622 | 1 | 4189.27 | 4211.82 | 22.55 | 60000 | 0 | 1353000 | 1363125.4682 | Matuail | Matuail 33/11KV S/S | 1274337.3987 | 1416234.4574 | 1374993.3702
666 | 11 kV Rajmahal Feeder (F10) | 11 | 0 | DHKA2187 | 1 | 112.4599 | 116.4856 | 4.0257 | 60000 | 0 | 241542 | 243349.6318 | Shyampur | Matuail 33/11KV S/S | 240620.6059 | 244740.1643 | 218634.2568
667 | 11 kV Bhuighor Bazar | 11 | 0 | HA021100861-02 | 1 | 75324.363 | 75817.099 | 492.736 | 1000 | Estimated | 1277144.82 | 1286702.6096 | Matuail | Matuail 33/11KV S/S | 1290448.3093 | 1462145.9342 | 1034107.8281
668 | 11 kV Tokkar Math Feeder | 11 | 0 | HA021200298-02 | 1 | 80274.518 | 81065.983 | 791.465 | 1000 | 0 | 791465 | 797388.0996 | Fatullah | Matuail 33/11KV S/S | 771061.022 | 778486.6953 | 733095.2742
669 | 11 kV Osmani Stadium Feeder***** | 11 | 0 | XA575922 | 1 | 193.1 | 202.9 | 9.8 | 1000 | 0 | 9800 | 9873.3404 | Fatullah | Matuail 33/11KV S/S | 9194.7909 | 13287.9755 | 64493.8811
670 | 33/0.415 KV Transformer, AT-1 | 0.415 | 0 | 2001123043119 | 1 | 7351.2 | 7430.6 | 79.4 | 160 | 0 | 12704 | 12799.0731 | Shyampur | Matuail 33/11KV S/S | 12965.6656 | 12496.7831 | 11807.0303
671 | 33/0.415 KV Transformer, AT-2 | 0.415 | 0 | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 0 | 0 | 129.3921
672 | 11 kV Godnail (F16) | 11 | 0 | 00000109 | 1 | 24749340 | 26744174 | 1994834 | 1 | 0 | 1994834 | 2022169.7421 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1902174.2906 | 1848814.9706 | 1869406.9017
673 | 11 kV M. Circus (F15) | 11 | 0 | 00000123 | 1 | 107396816 | 109200376 | 1803560 | 1 | 0 | 1803560 | 1828274.6635 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1936785.1498 | 1975646.3394 | 2135882.0516
674 | 11 kV Wapderpool (F14) | 11 | 0 | 00000190 | 1 | 56271624 | 57082820 | 811196 | 1 | 0 | 811196 | 822312.035 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 474935.0147 | 619875.2088 | 595303.4365
675 | 11 kV Chowdhury Bari (F13) | 11 | 0 | 00000191 | 1 | 98646920 | 100811032 | 2164112 | 1 | 0 | 2164112 | 2193767.4037 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 2204031.0267 | 2287431.9192 | 2194488.2982
676 | 11 kV Ailpara (F12) | 1 | 0 | 00000192 | 1 | 51494196 | 54123108 | 2628912 | 1 | 0 | 2628912 | 2664936.682 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 2385423.2662 | 2312455.9158 | 2506620.5244
677 | 11 kV Spare (F11) | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0 | 0
678 | 11 kV Spare (F10) | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0 | 0
679 | 11 kV Spare (F9) | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0 | 0
680 | 11 kV Spare (F8) | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0 | 0
681 | 11 kV Zulfiqur Steel | 11 | 0 | 00000197 | 1 | 15359563 | 16611599 | 1252036 | 1 | 0 | 1252036 | 1269192.9831 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1109871.8066 | 1233882.0915 | 1248729.4855
682 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 | 0 | 00000198 | 1 | 4078510 | 4123870 | 45360 | 1 | 0 | 45360 | 45981.5802 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 80821.2927 | 12574.267 | 42071.0581
683 | 11 kV Lucky Bazar (F5) | 11 | 0 | 00000199 | 1 | 88391024 | 89732904 | 1341880 | 1 | 0 | 1341880 | 1360268.1394 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1265880.4844 | 1332623.2308 | 1392661.9878
684 | 11 kV Enayetnagar (F4) | 11 | 0 | 00000200 | 1 | 30771724 | 32415400 | 1643676 | 1 | 0 | 1643676 | 1666199.7304 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1606948.7378 | 1544300.7721 | 1576051.8888
685 | 11 kV Bhuiyapara (F3) | 11 | 0 | 00000201 | 1 | 64028044 | 65898400 | 1870356 | 1 | 0 | 1870356 | 1895985.9869 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1703398.6781 | 2021560.4921 | 1949356.1666
686 | 11 kV Arambagh (F2) | 11 | 0 | 00000202 | 1 | 7963900.5 | 9021578 | 1057677.5 | 1 | 0 | 1057677.5 | 1072171.1368 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1011302.9055 | 1033739.3311 | 1073358.7436
687 | 11 kV Spare (F1) | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0 | 0
688 | 11/0.415 kV Aux. Transformer-1 | 0.415 | 0 | 00000204 | 1 | 1627.32 | 1668.24 | 40.92 | 100 | 0 | 4092 | 4148.0738 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 5028.3475 | 4509.4616 | 4713.1396
689 | 11/0.415 kV Aux. Transformer-2 | 0.415 | 0 | 00000205 | 1 | 60.72 | 60.72 | 0 | 100 | 0 | 0 | 0 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 0.99927 | 0 | 0
690 | 11 kV Minan Steel Feeder | 11 | New | 0 | 1 | 75456997 | 76153634 | 696637 | 1 | 0 | 696637 | 690626.9008 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 493276.6302 | 608736.535 | 686221.5647
691 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 87945628 | 88750830 | 805202 | 1 | 0 | 805202 | 798255.2776 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 675313.5877 | 687996.4568 | 904286.638
692 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 129693.5 | 158494.1 | 28800.6 | 60 | 0 | 1728036 | 1713127.7082 | Fatullah | Fatullah OLD 33/11KV S/S | 1429973.3518 | 1348752.6633 | 1520277.0648
693 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
694 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 308379.7 | 325173.2 | 16793.5 | 60 | 0 | 1007610 | 998917.0422 | Fatullah | Fatullah OLD 33/11KV S/S | 983661.4804 | 966418.4358 | 973413.7301
695 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 976902.1 | 1003887.3 | 26985.2 | 60 | 0 | 1619112 | 1605143.4286 | Fatullah | Fatullah OLD 33/11KV S/S | 2269442.86 | 1903765.6601 | 1898489.4903
696 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 59040.7 | 69754.4 | 10713.7 | 60 | 0 | 642822 | 637276.1792 | Fatullah | Fatullah OLD 33/11KV S/S | 646164.6825 | 667510.2274 | 661387.5474
697 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 616341.5 | 631131.1 | 14789.6 | 60 | 0 | 887376 | 879720.3375 | Fatullah | Fatullah OLD 33/11KV S/S | 817413.76 | 827156.9088 | 863427.9271
698 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 504567.7 | 523460.2 | 18892.5 | 60 | 0 | 1133550 | 1123770.5196 | Fatullah | Fatullah OLD 33/11KV S/S | 1043132.595 | 1256184.2479 | 1130265.9765
699 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 864279.2 | 868890.3 | 4611.1 | 60 | 0 | 276666 | 274279.1183 | Fatullah | Fatullah OLD 33/11KV S/S | 230613.5281 | 268951.939 | 461817.7457
700 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 514317.3 | 531239.4 | 16922.1 | 60 | 0 | 1015326 | 1006566.474 | Fatullah | Fatullah OLD 33/11KV S/S | 739323.8488 | 888156.2557 | 505747.1466
701 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 229225 | 1035040 | 805815 | 1 | 0 | 805815 | 798862.9891 | Sytalakhya | Fatullah OLD 33/11KV S/S | 731731.9387 | 686782.5544 | 645276.6941
702 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24889601 | 25218670 | 329069 | 1 | 0 | 329069 | 326230.0217 | Sytalakhya | Fatullah OLD 33/11KV S/S | 318326.9039 | 335635.5116 | 326421.8579
703 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 15173750 | 15526910 | 353160 | 1 | 0 | 353160 | 350113.1813 | Sytalakhya | Fatullah OLD 33/11KV S/S | 373857.3757 | 329133.6781 | 311868.8913
704 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
705 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 123409.7429 | 535601.4665
706 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 13842626 | 15928564 | 2085938 | 1 | 0 | 2085938 | 2067941.9788 | Fatullah | Fatullah OLD 33/11KV S/S | 1957359.7515 | 2145386.8814 | 2599917.6327
707 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
708 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
709 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 4587115 | 6443078 | 1855963 | 1 | 0 | 1855963 | 1839951.043 | Fatullah | Fatullah OLD 33/11KV S/S | 1845653.8856 | 1844325.072 | 1788794.6263
710 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
711 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0 | 0
712 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
713 | 11 kV Outgoing Feeder-2 (=F2) | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
714 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 887.81 | 924.36 | 36.55 | 60000 | 0 | 2193000 | 2225117.9731 | Sytalakhya | Fatullah New 33/11 KV SS | 1919103.2774 | 1925513.8961 | 2018573.5941
715 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 414.63 | 441.19 | 26.56 | 60000 | 0 | 1593600 | 1616939.3533 | Sytalakhya | Fatullah New 33/11 KV SS | 1431521.3433 | 1476167.1668 | 1492878.3256
716 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 530.35 | 541.83 | 11.48 | 60000 | 0 | 688800 | 698887.9434 | Sytalakhya | Fatullah New 33/11 KV SS | 713358.7902 | 702593.0118 | 691704.3007
717 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1177.63 | 1209.06 | 31.43 | 60000 | 0 | 1885800 | 1913418.8206 | Sytalakhya | Fatullah New 33/11 KV SS | 1823628.4898 | 1708359.7204 | 1811062.3039
718 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
719 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
720 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
721 | 11 kV Outgoing Feeder-10 (=F8) | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
722 | 11 kV Outgoing Feeder-11 (=F9) | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
723 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 157.05 | 176.71 | 19.66 | 60000 | 0 | 1179600 | 1196876.0424 | Sytalakhya | Fatullah New 33/11 KV SS | 1264590.5826 | 1201867.1554 | 1168078.0452
724 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 68.32 | 78.52 | 10.2 | 60000 | 0 | 612000 | 620963.1553 | Sytalakhya | Fatullah New 33/11 KV SS | 614881.6508 | 573262.9625 | 566596.0446
725 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1090.6 | 1116.9 | 26.3 | 60000 | 0 | 1578000 | 1601110.8808 | Sytalakhya | Fatullah New 33/11 KV SS | 1579237.0524 | 1146525.925 | 1680540.7098
726 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1318 | 1364.21 | 46.21 | 60000 | 0 | 2772600 | 2813206.6084 | Sytalakhya | Fatullah New 33/11 KV SS | 2526178.8135 | 2500581.4639 | 2536449.5967
727 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0 | 0
728 | 11 kV Katherpol Feeder | 11 | 0 | 00000031 | 1 | 63394284 | 65430400 | 2036116 | 1 | 0 | 2036116 | 2019617.347 | Fatullah | Dapa 33/11 kV | 1872668.2415 | 1825325.1091 | 2095256.7912
729 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
730 | 11 kV Union Parishad Feeder | 11 | 0 | 00000032 | 1 | 64364204 | 65934120 | 1569916 | 1 | 0 | 1569916 | 1557194.9668 | Fatullah | Dapa 33/11 kV | 1351133.0591 | 1174339.0851 | 1364658.7564
731 | 11 kV Shiachar Feeder | 11 | 0 | 00000030 | 1 | 65776000 | 67793912 | 2017912 | 1 | 0 | 2017912 | 2001560.8541 | Fatullah | Dapa 33/11 kV | 1924678.9852 | 1907532.8668 | 1901950.2285
732 | 11 kV Sastapur Feeder | 11 | 0 | 00000106 | 1 | 70349912 | 70748824 | 398912 | 1 | 0 | 398912 | 395679.6151 | Fatullah | Dapa 33/11 kV | 1143053.371 | 1344939.9892 | 1492863.3157
733 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
734 | 11 kV Jalal Ahmed Express | 11 | 0 | 00000172 | 1 | 4960348 | 4961228 | 880 | 1 | 0 | 880 | 872.8694 | Fatullah | Dapa 33/11 kV | 163.171 | 71453.7073 | 791901.0884
735 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
736 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
737 | 11 kV Lalpur Feeder | 11 | 0 | 00000044 | 1 | 77520128 | 78934408 | 1414280 | 1 | 0 | 1414280 | 1402820.0857 | Fatullah | Dapa 33/11 kV | 1449235.5198 | 1159780.4978 | 373576.7292
738 | 11 kV Kotaler Bag Feeder | 11 | 0 | 00000050 | 1 | 82482440 | 85024072 | 2541632 | 1 | 0 | 2541632 | 2521037.1496 | Fatullah | Dapa 33/11 kV | 1462297.3552 | 1401235.8745 | 1515181.1462
739 | 11 kV Idrakpur Feeder | 11 | 0 | 00000021 | 1 | 75647336 | 76871136 | 1223800 | 1 | 0 | 1223800 | 1213883.5456 | Fatullah | Dapa 33/11 kV | 1042540.0593 | 1114166.2721 | 1068664.5804
740 | 11 kV Isdair Feeder | 11 | 0 | 00000029 | 1 | 40064264 | 40865860 | 801596 | 1 | 0 | 801596 | 795100.6656 | Fatullah | Dapa 33/11 kV | 849835.155 | 794122.676 | 792940.801
741 | 11 kV Shah Fateullah Express | 11 | 0 | 0000051 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0 | 0 | 0
742 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
743 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0 | 0
744 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 | 0 | DHKF 7522 | 1 | 3013 | 3070 | 57 | 100 | 0 | 5700 | 5653.8129 | Fatullah | Dapa 33/11 kV | 5914.9473 | 5529.8501 | 5198.5629
745 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0 | 0 | 0
746 | 11 kV Bholail Feeder (F-3) | 11 | 0 | DHK 9335 | 1 | 20042.476 | 73278.9421 | 53236.4661 | 60 | 0 | 3194187.966 | 3202295.2627 | Sytalakhya | Sitalakhya 33/11KV S/S | 3113891.785 | 3046734.2178 | 2464743.5384
747 | 11 kV Crony Apparels (F-2) | 11 | 0 | DHK 9336 | 1 | 48142.2979 | 72262.0412 | 24119.7433 | 60 | 0 | 1447184.598 | 1450857.7553 | Sytalakhya | Sitalakhya 33/11KV S/S | 1198137.3888 | 1083589.5043 | 1409860.9795
748 | 11 kV Baburail Feeder (F-5) | 11 | 0 | DHK 9322 | 1 | 82394.5117 | 116765.902 | 34371.3903 | 60 | 0 | 2062283.418 | 2067517.7824 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 2058052.5984 | 2038840.2789 | 1960329.6227
749 | 11 kV Goghchar Feeder (F-1) | 11 | 0 | DHK 9323 | 1 | 12256.5511 | 34381.3213 | 22124.7702 | 60 | 0 | 1327486.212 | 1330855.5581 | Sytalakhya | Sitalakhya 33/11KV S/S | 1324242.6499 | 1303267.9767 | 1261095.5642
750 | 11 kV Norshinghopur (F-2) | 11 | 0 | DHK 9365 | 1 | 93513.646 | 117798.346 | 24284.7 | 60 | 0 | 1457082 | 1460780.2783 | Sytalakhya | Sitalakhya 33/11KV S/S | 1404336.8639 | 1352601.3966 | 1471201.0567
751 | 11 kV Geddar Bazar Feeder (F-4) | 11 | 0 | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 33/11KV S/S | 0 | 0 | 554462.5713
752 | 11 kV Noluyapara Feeder (F-6)*** | 11 | 0 | H/A030701125-03 | 1 | 73081.722 | 73316.461 | 234.739 | 1000 | 0 | 234739 | 235334.8005 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 246133.1449 | 234255.9876 | 224598.6372
753 | 11 kV Kashipur Feeder (F-7) | 11 | 0 | H/A030800169-03 | 1 | 34992.83 | 36748.744 | 1755.914 | 1000 | 0 | 1755914 | 1760370.7558 | Sytalakhya | Sitalakhya 33/11KV S/S | 1741847.8978 | 1664580.229 | 1652181.4751
754 | 11 kV Spare Feeder (F-6) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 0 | 0 | 0
755 | 11 kV Paikpara Feeder (F-8) | 11 | 0 | H/A030701098-03 | 1 | 78252.992 | 79368.604 | 1115.612 | 1000 | 0 | 1115612 | 1118443.5796 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 1135381.2606 | 1090515.7468 | 1082731.082
756 | 11 kV B. K. Road Feeder (F-9) | 11 | 0 | H/A030800205-03 | 1 | 94550.082 | 95386.118 | 836.036 | 1000 | 0 | 836036 | 838157.9765 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 729788.4502 | 786055.2221 | 765048.1281
757 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 | 0 | H/A030701091-03 | 1 | 53202.551 | 54235.165 | 1032.614 | 1000 | 0 | 1032614 | 1035234.9191 | Sytalakhya | Sitalakhya 33/11KV S/S | 1075488.4842 | 1015821.5301 | 958950.0681
758 | 11 kV River View | 11 | 0 | 00000061 | 1 | 6387048 | 7222804 | 835756 | 1 | 0 | 835756 | 844731.2094 | N.Gonj (East) | Mondalpara 33/11KV S/S | 841728.9793 | 838140.6773 | 803073.4017
759 | 11 kV Railgate B.B. Road | 11 | 0 | 00000191 | 1 | 22810540 | 23455022 | 644482 | 1 | 0 | 644482 | 651403.112 | N.Gonj (East) | Mondalpara 33/11KV S/S | 672012.4136 | 662899.4007 | 611819.3181
760 | 11 kV DIT | 11 | 0 | 00000174 | 1 | 136605064 | 139579616 | 2974552 | 1 | 0 | 2974552 | 3006495.8053 | N.Gonj (West) | Mondalpara 33/11KV S/S | 3105959.8639 | 3165323.9759 | 2992837.0935
761 | 11 kV Dalpatti | 11 | 0 | 00000182 | 1 | 3675991 | 4379629 | 703638 | 1 | 0 | 703638 | 711194.3901 | N.Gonj (East) | Mondalpara 33/11KV S/S | 640949.3228 | 661646.5082 | 714092.6513
762 | 11 kV South Chasara | 11 | 0 | 00000043 | 1 | 94325328 | 96976880 | 2651552 | 1 | 0 | 2651552 | 2680027.0984 | N.Gonj (West) | Mondalpara 33/11KV S/S | 2791666.2107 | 2659640.365 | 2565218.7341
763 | 11 kV Spare | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0 | 0
764 | 11 kV NCC Express | 11 | 0 | 00000019 | 1 | 130297 | 161639 | 31342 | 1 | 0 | 31342 | 31678.5827 | N.Gonj (East) | Mondalpara 33/11KV S/S | 33494.5516 | 30069.4219 | 22516.8296
765 | 11 kV Spare | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0 | 0
766 | 11 kV Masuya Bazar | 11 | 0 | 00000173 | 1 | 5319947 | 6362744 | 1042797 | 1 | 0 | 1042797 | 1053995.629 | N.Gonj (East) | Mondalpara 33/11KV S/S | 1019425.3124 | 1009868.8027 | 967617.4501
767 | 11 kV Nitaigonj | 11 | 0 | 00000189 | 1 | 58092820 | 58881896 | 789076 | 1 | 0 | 789076 | 797549.9114 | N.Gonj (East) | Mondalpara 33/11KV S/S | 692971.3447 | 773236.8002 | 671875.6098
768 | 11 kV Shahid Nagar | 11 | 0 | 00000020 | 1 | 57039820 | 58363976 | 1324156 | 1 | 0 | 1324156 | 1338376.1519 | Sytalakhya | Mondalpara 33/11KV S/S | 1319788.4916 | 1324869.236 | 1256708.9709
769 | 11 kV Bangla Bazar | 11 | 0 | 00000139 | 1 | 69252312 | 70904584 | 1652272 | 1 | 0 | 1652272 | 1670015.7997 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1659253.7348 | 1635218.8108 | 1605498.2865
770 | 11 kV Vogoban Gonj | 11 | 0 | 00000181 | 1 | 2365594 | 2840673 | 475079 | 1 | 0 | 475079 | 480180.888 | N.Gonj (East) | Mondalpara 33/11KV S/S | 455263.1874 | 451404.0608 | 442440.5963
771 | 11 kV Tanbazar | 11 | 0 | 00000138 | 1 | 48640480 | 49652160 | 1011680 | 1 | 0 | 1011680 | 1022544.4626 | N.Gonj (East) | Mondalpara 33/11KV S/S | 983939.833 | 990185.2541 | 977004.8332
772 | 11 kV SS Road | 11 | 0 | 00000175 | 1 | 65297040 | 66668396 | 1371356 | 1 | 0 | 1371356 | 1386083.0342 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1389631.5256 | 1367265.5042 | 1304240.0244
773 | 11 kV Spare | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0 | 0
774 | 33/0.415 kV Auxiliary-1 | 0.415 | 0 | 0 | 1 | 2500.38 | 2536.53 | 36.15 | 100 | 0 | 3615 | 3653.8216 | N.Gonj (West) | Mondalpara 33/11KV S/S | 8763.4945 | 8081.1571 | 8402.5235
775 | 33/0.415 kV Auxiliary-2 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 0 | 0 | 0
776 | 11 kV Masdair Feeder (F-8) | 11 | 0 | XA575914 | 1 | 212991.1 | 216058.1 | 3067 | 1000 | 0 | 3067000 | 3104675.7264 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 3190609.1379 | 3086175.0273 | 3077099.4263
777 | 11 kV Narayangonj (F-7) | 11 | 0 | XA575915 | 1 | 165452.9 | 166943.6 | 1490.7 | 1000 | 0 | 1490700 | 1509012.0982 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1221622.7778 | 1186514.4598 | 1307443.1804
778 | 11 kV Nearest Feeder (F-6) | 11 | 0 | XA575927 | 1 | 105393.1 | 106447.5 | 1054.4 | 1000 | 0 | 1054400 | 1067352.4897 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 767732.4068 | 814473.5094 | 997748.2737
779 | 11 kV BSCIC-2 Feeder (F-5) | 11 | 0 | XA575916 | 1 | 116133.1 | 117391.8 | 1258.7 | 1000 | 0 | 1258700 | 1274162.1574 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1118663.9439 | 1197874.4889 | 1341268.5888
780 | 11 kV Abonti Color Tex. (F-4) | 11 | 0 | XA575912 | 1 | 54786 | 55681.1 | 895.1 | 1000 | 0 | 895100 | 906095.6122 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 696086.8403 | 614760.142 | 701320.2188
781 | 11 kV BSCIC-1 Feeder (F-3) | 11 | 0 | DHK66615 | 1 | 194.7091 | 212.6573 | 17.9482 | 60000 | 0 | 1076889.78 | 1090118.5393 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 864699.4622 | 933339.9033 | 1045632.3523
782 | 11 kV Shasongaon Feeder (F-2) | 11 | 0 | XA575920 | 1 | 231721.5 | 232617.3 | 895.8 | 1000 | 0 | 895800 | 906804.2112 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 982770.4437 | 813154.9346 | 1189560.6195
783 | 11 kV Fakir Apparels Feeder (F-1) | 11 | 0 | XA575929 | 1 | 20181.2 | 21345.9 | 1164.7 | 1000 | 0 | 1164700 | 1179007.44 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1159908.2799 | 1225868.8461 | 1274022.8667
784 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 | 0 | HA021100913-02 | 1 | 38961.791 | 40336.402 | 1374.611 | 1000 | 0 | 1374611 | 1391497.0345 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 582908.1262 | 649651.6597 | 916096.371
785 | 11 kV BSCIC-4 Feeder (F-11) | 11 | 0 | HA021100682-02 | 1 | 59519.019 | 61904.666 | 2385.647 | 1000 | 0 | 2385647 | 2414952.831 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1958482.735 | 2197501.257 | 2366722.3025
786 | 11 kV BSCIC-3 Feeder (F-10) | 11 | 0 | HA021100455-02 | 1 | 54442.541 | 56572.368 | 2129.827 | 1000 | 0 | 2129827 | 2155990.2798 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1459919.7827 | 1675803.0813 | 1827353.8856
787 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3813.8 | 3872.6 | 58.8 | 160 | 0 | 9408 | 9523.57 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 9809.4637 | 10077.9686 | 6902.8139
788 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4101.4 | 4105 | 3.6 | 160 | 0 | 576 | 583.0757 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 16.214 | 519.3156 | 421.2985
789 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
790 | 11 kV Char-Syedpur Feeder(=F2) | 11 | 0 | 041808902749 | 1 | 402.78 | 425.05 | 22.27 | 60000 | 0 | 1336200 | 1326519.4669 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1258154.7044 | 1256317.0074 | 1308593.1901
791 | 11 kV UltraTech Cement Feeder (=F3) | 11 | 0 | 041808902759 | 1 | 438.15 | 457.83 | 19.68 | 60000 | 0 | 1180800 | 1172245.3124 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1166152.8884 | 1226848.5855 | 1401162.4833
792 | 11 kV Outgoing Feeder-4 (=F4) | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
793 | 11 kV Outgoing Feeder-5 (=F5) | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
794 | 11 kV Outgoing Feeder-6 (=F6) | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
795 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
796 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
797 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
798 | 11 kV Mokterpur Feeder (=F8) | 11 | 0 | 041808902786 | 1 | 275.64 | 303.34 | 27.7 | 60000 | 0 | 1662000 | 1649959.1034 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1406910.8874 | 1384414.4332 | 1059738.0772
799 | 11 kV Dhaleshwary Feeder (=F9) | 11 | 0 | 041808902789 | 1 | 178 | 190.79 | 12.79 | 60000 | 0 | 767400 | 761840.3225 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 831600.8302 | 763171.9877 | 845746.7241
800 | 11 kV Outgoing Feeder-12 (=F10) | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
801 | 11 kV Outgoing Feeder-13 (=F11) | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
802 | 11 kV Outgoing Feeder-14 (=F12) | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
803 | 11 kV Outgoing Feeder-15 (=F13) | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
804 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
805 | 33/0.415 kV Transformer AT-1 | 0.415 | 0 | 041811907976 | 1 | 1595.72 | 1708.92 | 113.2 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
806 | 33/0.415 kV Transformer AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0 | 0
807 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 70057178 | 70727703 | 670525 | 1 | 0 | 670525 | 669679.7315 | Mugdapara | Amulia 33/11 kv | 704760.429 | 655997.4572 | 731782.37
808 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0 | 0
809 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 14050902 | 15370323 | 1319421 | 1 | 0 | 1319421 | 1317757.7287 | Demra | Amulia 33/11 kv | 1370677.2015 | 1292488.6152 | 1242034.7233
810 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 878768 | 1451896 | 573128 | 1 | 0 | 573128 | 572405.5108 | Demra | Amulia 33/11 kv | 546070.575 | 498813.9667 | 550647.0061
811 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 63742776 | 66196611 | 2453835 | 1 | 0 | 2453835 | 2450741.6785 | Demra | Amulia 33/11 kv | 2341533.0936 | 2143176.0462 | 2258006.7634
812 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 14096671 | 14737417 | 640746 | 1 | 0 | 640746 | 639938.2711 | Mugdapara | Amulia 33/11 kv | 588274.3679 | 552448.5186 | 1045691.8176
813 | 11 kV Amulia Model Town Feeder | 11 | Demra | 0 | 1 | 51647116 | 51837287 | 190171 | 1 | 0 | 190171 | 189931.2691 | Demra | Amulia 33/11 kv | 165276.4 | 158821.9675 | 145542.9861
814 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 10934861 | 12263057 | 1328196 | 1 | 0 | 1328196 | 1326521.6668 | Demra | Amulia 33/11 kv | 1251754.1184 | 1263380.0786 | 1242709.7581
815 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0 | 0
816 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0 | 0
817 | 33/0.415 kV Transformer, AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0 | 0
818 | 11 kV Nearest Feeder | 11 | 0 | HA021101060-02 | 1 | 75374744 | 77039568 | 1664824 | 1 | 0 | 1664824 | 1666551.6834 | Maniknagar | Maniknagar 33/11 KV SS | 1691601.9901 | 1589546.8433 | 1558145.6337
819 | 11kV Spare | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 0 | 0
820 | 11 kV City Palli Feeder | 11 | 0 | HA021100937-02 | 1 | 77211413 | 78117885 | 906472 | 1 | 0 | 906472 | 907412.698 | Maniknagar | Maniknagar 33/11 KV SS | 936164.8797 | 876024.4652 | 849393.0553
821 | 11 kV R K Mission Road Feeder | 11 | 0 | HA021101035-02 | 1 | 14171862 | 15727081 | 1555219 | 1 | 0 | 1555219 | 1556832.94 | Maniknagar | Maniknagar 33/11 KV SS | 1647566.9154 | 1564049.4804 | 1502639.6704
822 | 11 kV Janapath Feeder | 11 | 0 | HA021100864-02 | 1 | 27595235 | 29720440 | 2125205 | 1 | 0 | 2125205 | 2127410.4471 | Maniknagar | Maniknagar 33/11 KV SS | 2194112.6593 | 2093083.5306 | 2005205.5254
823 | 11 kV Dhalpur Feeder | 11 | 0 | HA021100851-02 | 1 | 86139684 | 87012283 | 872599 | 1 | 0 | 872599 | 873504.546 | Maniknagar | Maniknagar 33/11 KV SS | 859344.4269 | 844664.2379 | 860069.6023
824 | 11kV WTP | 11 | 0 | X0599387 | 1 | 1406.5 | 1967.9 | 561.4 | 1000 | 0 | 561400 | 561982.597 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 0 | 145877.5724
825 | 11kV Kamalapur Water pumping | 11 | 0 | HA021100474-02 | 1 | 7638435 | 7638697 | 262 | 1 | Estimated | 72979.704 | 73055.4392 | Maniknagar | Maniknagar 33/11 KV SS | 36822.7275 | 20221.1849 | 24456.8935
826 | 11 kV Wasa Road Feeder | 11 | 0 | HA021001011-02 | 1 | 25380490 | 25384272 | 3782 | 1 | Estimated | 2140737.984 | 2142959.5506 | Maniknagar | Maniknagar 33/11 KV SS | 2098895.465 | 1863737.1947 | 2040994.3579
827 | 11kV Sutikhalpar Feeder | 11 | 0 | HA021101047-02 | 1 | 79907658 | 79907835 | 177 | 1 | Estimated | 2067758.28 | 2069904.1114 | Maniknagar | Maniknagar 33/11 KV SS | 2025250.0101 | 1882771.0147 | 2076315.0532
828 | 11kV Spare | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0 | 0
829 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0 | 0
830 | 11kV Spare | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0 | 0
831 | 11kV Spare | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0 | 0
832 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0 | 0
833 | AT-1 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 0 | 0
834 | 11kV Fakirapul Panir Tank Feeder | 11 | 0 | DHK86058 | 1 | 1695.96 | 1714 | 18.04 | 60000 | 0 | 1082400 | 1083441.1947 | Motijheel | Motijheel old 33/11 kV | 1084055.9235 | 997541.2473 | 913140.3988
835 | 11kV Station Road Feeder | 11 | 0 | DHK86075 | 1 | 2376.46 | 2378.15 | 1.69 | 60000 | 0 | 101400 | 101497.5399 | Motijheel | Motijheel old 33/11 kV | 109816.6442 | 95033.1244 | 121832.4707
836 | 11kV Box Culvert Road Feeder | 11 | 0 | DHK86071 | 1 | 3155.14 | 3187.68 | 32.54 | 60000 | 0 | 1952400 | 1954278.0752 | Motijheel | Motijheel old 33/11 kV | 1833753.908 | 1479451.1554 | 1996966.8828
837 | 11kV Mohamedan Club Feeder | 11 | 0 | DHK86062 | 1 | 1678.4 | 1693.67 | 15.27 | 60000 | 0 | 916200 | 917081.3217 | Motijheel | Motijheel old 33/11 kV | 976079.7817 | 1139171.2585 | 731597.9549
838 | 11kV Amina Ahmed Co. | 11 | 0 | DHK95754 | 1 | 108136 | 112104 | 3968 | 60 | 0 | 238080 | 238309.0167 | Motijheel | Motijheel old 33/11 kV | 251289.93 | 373020.341 | 139323.2709
839 | 11kV Bangabhaban -1 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0 | 0
840 | 11kV Sonali Bank | 11 | 0 | DHK95753 | 1 | 59617 | 68343 | 8726 | 60 | 0 | 523560 | 524063.6289 | Motijheel | Motijheel old 33/11 kV | 553807.1772 | 446839.6196 | 345775.0268
841 | 11kV NCC Bank Feeder | 11 | 0 | DHK68123 | 1 | 320 | 324.15 | 4.15 | 60000 | 0 | 249000 | 249239.521 | Motijheel | Motijheel old 33/11 kV | 237424.8118 | 404044.0578 | 147163.9744
842 | 11kV IFIC BANK Feeder | 11 | 0 | DHK68116 | 1 | 397.35 | 404.96 | 7.61 | 60000 | 0 | 456600 | 457039.218 | Ramna | Motijheel old 33/11 kV | 500616.6574 | 354381.5863 | 554880.5594
843 | 11kV Arambagh Feeder | 11 | 0 | DHK68117 | 1 | 3367.9 | 3391.53 | 23.63 | 60000 | Estimated | 1277144.82 | 1278373.3459 | Motijheel | Motijheel old 33/11 kV | 1267688.622 | 59250.2714 | 488536.1447
844 | 11kV Nikotborti Feeder | 11 | 0 | DHK68114 | 1 | 1425.76 | 1430.8 | 5.04 | 60000 | 0 | 302400 | 302690.8881 | Motijheel | Motijheel old 33/11 kV | 931907.7237 | 862042.4055 | 655000.3125
845 | 11kV Agrani Bank Feeder | 11 | 0 | DHK95756 | 1 | 367476 | 371420 | 3944 | 60 | 0 | 236640 | 236867.6315 | Motijheel | Motijheel old 33/11 kV | 255891.186 | 369219.0161 | 144691.1372
846 | 11kV Bangladesh Bank-2 | 11 | 0 | DHK95755 | 1 | 527 | 528 | 1 | 60000 | Estimated | 912246.3 | 913123.8185 | Motijheel | Motijheel old 33/11 kV | 781881.091 | 669891.5592 | 180939.3128
847 | 11kV PDB Design Feeder 14 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0 | 0
848 | 11kV Bangabhaban-2 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0 | 0
849 | 11/0.4 kV AT | 0.415 | 0 | ELIC5429 | 1 | 411842 | 416832 | 4990 | 1 | 0 | 4990 | 4994.8 | Motijheel | Motijheel old 33/11 kV | 6386.5434 | 8270.9474 | 3518.2644
850 | 11 kV Central Weman | 11 | 0 | 41812909492 | 1 | 146.96 | 156.68 | 9.72 | 60000 | 0 | 583200 | 585552.4072 | Motijheel | Motijheel 33/11 KV SS (new) | 614594.3851 | 602582.0913 | 559727.7485
851 | 11 kV Spare Feeder 2 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
852 | 11 kV K. M. Das Len | 11 | 0 | 41812909499 | 1 | 250.96 | 267.43 | 16.47 | 60000 | 0 | 988200 | 992186.0233 | Swamibag | Motijheel 33/11 KV SS (new) | 1031748.0667 | 1006914.6746 | 933883.7569
853 | 11 kV Gopibag | 11 | 0 | 41812909517 | 1 | 36.93 | 39.58 | 2.65 | 60000 | 0 | 159000 | 159641.3456 | Motijheel | Motijheel 33/11 KV SS (new) | 169750.8488 | 161492.0005 | 148216.3898
854 | 11kV SPICE TV | 11 | 0 | 41812909518 | 1 | 14.9 | 18.61 | 3.71 | 60000 | 0 | 222600 | 223497.8838 | Narinda | Motijheel 33/11 KV SS (new) | 229344.2319 | 216326.9708 | 196416.8418
855 | 11 kV Spare Feeder 6 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
856 | 11 kV Spare Feeder 7 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
857 | 11 kV BPT-1 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
858 | 11 kV BPT-2 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
859 | 10 kV Spare Feeder 8 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
860 | 11 kV Spare Feeder 9 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
861 | 11 kV South Kamlapur | 11 | 0 | 41812909473 | 1 | 377.45 | 386.74 | 9.29 | 60000 | 0 | 557400 | 559648.3398 | Motijheel | Motijheel 33/11 KV SS (new) | 571253.7429 | 550760.0315 | 1048359.8303
862 | 11 kV Spare Feeder 11 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
863 | 11 kV Answer Camp | 11 | 0 | 41812909514 | 1 | 179.13 | 191.59 | 12.46 | 60000 | 0 | 747600 | 750615.5343 | Motijheel | Motijheel 33/11 KV SS (new) | 784345.2339 | 758048.2709 | 729031.836
864 | 11 kV Shapla Chattar | 11 | 0 | 41812909516 | 1 | 137.07 | 156.7 | 19.63 | 60000 | 0 | 1177800 | 1182550.7976 | Motijheel | Motijheel 33/11 KV SS (new) | 639274.4731 | 598966.5988 | 591058.0422
865 | 11 kV Sayedabad | 11 | 0 | 41812909497 | 1 | 94.88 | 100.05 | 5.17 | 60000 | 0 | 310200 | 311451.2289 | Swamibag | Motijheel 33/11 KV SS (new) | 306394.2625 | 315753.0159 | 300047.8135
866 | 33/0.4 kV Aux Transformer | 0.415 | 0 | 41901920686 | 1 | 1130.78 | 1213.49 | 82.71 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new) | 0 | 0 | 0
867 | Inner Circular Road Feeder | 11 | 0 | BD014042 | 1 | 40052 | 40795 | 743 | 1000 | 0 | 743000 | 751211.0308 | Motijheel | P & T 33/11 KV SS | 786225.5313 | 2044037.2926 | 2028898.6132
868 | NSI New Building Expres Feeder | 11 | 0 | BD013982 | 1 | 9624 | 10028 | 404 | 1000 | 0 | 404000 | 408464.6789 | Ramna | P & T 33/11 KV SS | 417588.6558 | 429529.4901 | 413128.6457
869 | Police Hospital RMU Feeder | 11 | 0 | BD014044 | 1 | 3401 | 3583 | 182 | 1000 | 0 | 182000 | 184011.3157 | Rajarbag | P & T 33/11 KV SS | 189813.0254 | 182072.2195 | 167833.5123
870 | Jonaki O/H Feeder | 11 | 0 | BD014013 | 1 | 32499 | 33977 | 1478 | 1000 | 0 | 1478000 | 1494333.6521 | Rajarbag | P & T 33/11 KV SS | 1501520.9321 | 1581312.3149 | 1420129.7195
871 | Nayapalton Overhead Feeder | 11 | 0 | BD014014 | 1 | 23646 | 24648 | 1002 | 1000 | 0 | 1002000 | 1013073.2878 | Ramna | P & T 33/11 KV SS | 1003011.9866 | 1008941.636 | 976215.0449
872 | Masjid Gali Over Head Feeder | 11 | 0 | BD014016 | 1 | 13676 | 14584 | 908 | 1000 | 0 | 908000 | 918034.4764 | Ramna | P & T 33/11 KV SS | 899114.3306 | 924444.0314 | 878891.4697
873 | Spare Feeder (Feeder-8) | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 0 | 0 | 0
874 | Mid Way Over Head Feeder | 11 | 0 | BD014015 | 1 | 21881 | 22853 | 972 | 1000 | 0 | 972000 | 982741.7522 | Ramna | P & T 33/11 KV SS | 1022992.3051 | 1000894.2451 | 972242.6541
875 | Palton Thana Over Head Feeder | 11 | 0 | BD014033 | 1 | 22279 | 23625 | 1346 | 1000 | 0 | 1346000 | 1360874.8956 | Rajarbag | P & T 33/11 KV SS | 1387633.1169 | 1346932.0545 | 1294006.3108
876 | Police Hospital (South) U/G Feeder 7 | 11 | 0 | BD014034 | 1 | 12204 | 12388 | 184 | 1000 | 0 | 184000 | 186033.4181 | Rajarbag | P & T 33/11 KV SS | 181820.898 | 172012.9808 | 167833.5123
877 | China Town Express Feeder | 11 | 0 | BD013943 | 1 | 6095 | 6379 | 284 | 1000 | 0 | 284000 | 287138.5367 | Ramna | P & T 33/11 KV SS | 264739.2196 | 295741.6161 | 284025.9439
878 | Fakirapul Bazar O/H Feeder | 11 | 0 | BD014032 | 1 | 27825 | 29285 | 1460 | 1000 | 0 | 1460000 | 1476134.7307 | Motijheel | P & T 33/11 KV SS | 1280738.4132 | 1354979.4454 | 1402253.9607
879 | PWD Ouarter (RMU) | 11 | 0 | BD013937 | 1 | 2163 | 2311 | 148 | 1000 | 0 | 148000 | 149635.5754 | Motijheel | P & T 33/11 KV SS | 151850.4203 | 150888.5797 | 145985.3628
880 | Postal Quarter RMU | 11 | 0 | BD013945 | 1 | 2678 | 2854 | 176 | 1000 | 0 | 176000 | 177945.0086 | Motijheel | P & T 33/11 KV SS | 177824.8343 | 174024.8285 | 164854.2192
881 | 11/0.4 kV AT-1 | 0.415 | 0 | DHKH4409 | 1 | 1377 | 1434 | 57 | 100 | 0 | 5700 | 5762.9918 | Rajarbag | P & T 33/11 KV SS | 6093.9971 | 301.7772 | 0
882 | 11/0.4 kV AT-2 | 0.415 | 0 | DHKH4411 | 1 | 508 | 508 | 0 | 100 | 0 | 0 | 0 | Rajarbag | P & T 33/11 KV SS | 5394.686 | 0 | 5362.7276
883 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 385 | 407.2 | 22.2 | 40000 | 0 | 888000 | 895110.6473 | Rajarbag | Kamalapur Railway 33/11 KV SS | 1426015.7648 | 1381038.2208 | 1302977.567
884 | Police Telecom | 11 | Rajarbag | 130 | 1 | 63.9 | 69.1 | 5.2 | 40000 | 0 | 208000 | 209665.557 | Rajarbag | Kamalapur Railway 33/11 KV SS | 202559.0575 | 214648.1692 | 201076.785
885 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 263.8 | 284.1 | 20.3 | 40000 | 0 | 812000 | 818502.0784 | Rajarbag | Kamalapur Railway 33/11 KV SS | 866952.7661 | 866692.6078 | 735941.0332
886 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 672.9 | 704.5 | 31.6 | 40000 | 0 | 1264000 | 1274121.462 | Rajarbag | Kamalapur Railway 33/11 KV SS | 2264610.2629 | 2211281.1394 | 2079133.9572
887 | 11 KV Majar Feeder | 11 | 0 | 96 | 1 | 42.3 | 52 | 9.7 | 40000 | 0 | 388000 | 391106.9045 | Motijheel | Kamalapur Railway 33/11 KV SS | 417271.6585 | 400946.5802 | 382045.8916
888 | 11 kV Feeder-6 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
889 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 318.7 | 330.7 | 12 | 40000 | 0 | 480000 | 483843.5932 | Rajarbag | Kamalapur Railway 33/11 KV SS | 563114.1799 | 1081340.777 | 1001362.3894
890 | 11 kV Feeder-8 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
891 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 207.3 | 215.5 | 8.2 | 40000 | 0 | 328000 | 330626.4553 | Rajarbag | Kamalapur Railway 33/11 KV SS | 352452.7601 | 340197.0984 | 337808.9988
892 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 220.6 | 274.3 | 53.7 | 40000 | 0 | 2148000 | 2165200.0794 | Rajarbag | Kamalapur Railway 33/11 KV SS | 449681.1077 | 437396.2693 | 402153.5701
893 | 11 kV Feeder-11 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
894 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 59.2 | 64.4 | 5.2 | 40000 | 0 | 208000 | 209665.557 | Motijheel | Kamalapur Railway 33/11 KV SS | 230917.3256 | 222748.1001 | 217162.9278
895 | Jasimuddin Feeder-13 | 11 | 0 | 91 | 1 | 155 | 193.9 | 38.9 | 40000 | 0 | 1556000 | 1568459.6478 | Motijheel | Kamalapur Railway 33/11 KV SS | 1713649.6265 | 1656435.8718 | 1097879.2463
896 | Police Box Feeder-14 | 11 | 0 | 18 | 1 | 69 | 84.6 | 15.6 | 40000 | 0 | 624000 | 628996.6711 | Motijheel | Kamalapur Railway 33/11 KV SS | 656291.3463 | 664194.3349 | 643445.7121
897 | 11 kV Feeder-15 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
898 | 11 kV Feeder-16 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
899 | Auxiliary -1 (AT-1 ) | 0.415 | 0 | DHKF 7632 | 1 | 902.28 | 948.92 | 46.64 | 100 | 0 | 4664 | 4701.3469 | Rajarbag | Kamalapur Railway 33/11 KV SS | 8715.1034 | 2871.4255 | 5128.4634
900 | Auxiliary -1 (AT-2 ) | 0.415 | 0 | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS | 0 | 0 | 0
901 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 215236.15 | 216382 | 1145.85 | 1000 | Estimated | 875756.448 | 884099.9496 | Motijheel | Bangabhaban 132/11KV S/S | 816951.1322 | 793502.3098 | 860468.6016
902 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 24132.19 | 24203.56 | 71.37 | 1000 | 0 | 71370 | 72049.9558 | Motijheel | Bangabhaban 132/11KV S/S | 82523.1488 | 83389.7606 | 79020.0597
903 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 0 | 0 | 0
904 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0 | 240728.715
905 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0 | 0
906 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33853.02 | 33872.91 | 19.89 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 0 | 0 | 20212.3186
907 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 790613.46 | 798145.7878 | Motijheel | Bangabhaban 132/11KV S/S | 731598.0289 | 710599.0834 | 737544.5157
908 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15810 | 15886.23 | 76.23 | 1000 | 0 | 76230 | 76956.258 | Motijheel | Bangabhaban 132/11KV S/S | 79365.3753 | 70158.8804 | 76837.1293
909 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0 | 0
910 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 246649.65 | 247820.06 | 1170.41 | 1000 | 0 | 1170410 | 1181560.7231 | Motijheel | Bangabhaban 132/11KV S/S | 1155594.7497 | 1181422.0182 | 1217478.907
911 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14474.96 | 14648.55 | 173.59 | 1000 | 0 | 173590 | 175243.8256 | Motijheel | Bangabhaban 132/11KV S/S | 162199.2891 | 174416.2041 | 171420.6744
912 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0 | 0
913 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 279755.532 | 282420.8172 | Motijheel | Bangabhaban 132/11KV S/S | 243866.0096 | 236866.3611 | 245848.1719
914 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163764.06 | 164126.32 | 362.26 | 1000 | 0 | 362260 | 365711.3213 | Motijheel | Bangabhaban 132/11KV S/S | 363925.8833 | 326878.2024 | 270087.1078
915 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20596.96 | 20655.45 | 58.49 | 1000 | Estimated | 279755.532 | 282420.8172 | Motijheel | Bangabhaban 132/11KV S/S | 243866.0096 | 236866.3611 | 245848.1719
916 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 364898.52 | 368374.979 | Motijheel | Bangabhaban 132/11KV S/S | 341412.4135 | 331612.9056 | 368772.2578
917 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122899.9 | 123222.28 | 322.38 | 1000 | 0 | 322380 | 325451.3768 | Motijheel | Bangabhaban 132/11KV S/S | 302665.0764 | 348419.8864 | 313139.3465
918 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 273094.04 | 273191.92 | 97.88 | 1000 | 0 | 97880 | 98812.5217 | Motijheel | Bangabhaban 132/11KV S/S | 790606.2505 | 819439.2218 | 796304.7174
919 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 80707.72 | 81231.84 | 524.12 | 1000 | 0 | 524120 | 529113.3929 | Motijheel | Bangabhaban 132/11KV S/S | 587426.078 | 481785.1466 | 474463.9677
920 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192560.77 | 192668.35 | 107.58 | 1000 | Estimated | 364898.52 | 368374.979 | Motijheel | Bangabhaban 132/11KV S/S | 341412.4135 | 331612.9056 | 368772.2578
921 | 11/0.4 kV AT-1 | 0.415 | 0 | 63412931 | 1 | 66825 | 72982 | 6157 | 1 | 0 | 6157 | 6215.6589 | Motijheel | Bangabhaban 132/11KV S/S | 3575.8026 | 0 | 0
922 | 11/0.4 kV AT-2 | 0.415 | 0 | 63403117 | 1 | 22885 | 22885 | 0 | 1 | Estimated | 5000 | 5047.636 | Motijheel | Bangabhaban 132/11KV S/S | 5012.339 | 5030.7529 | 5053.0797
923 | 11 kV Bonogram Feeder | 11 | 0 | 06604467 | 1 | 24756.85 | 24894.05 | 137.2 | 8000 | 0 | 1097600 | 1111412.0708 | Narinda | Narinda 33/11KV S/S | 1143423.9412 | 1139801.4532 | 1096395.2732
924 | 11 kV Sha Saheb Len Feeder | 11 | 0 | 06604469 | 1 | 16724.98 | 16806.42 | 81.44 | 8000 | 0 | 651520 | 659718.6519 | Swamibag | Narinda 33/11KV S/S | 672430.175 | 685656.1379 | 629657.0471
925 | 11 kV Sadiabad Water Treatment | 11 | 0 | 06604354 | 1 | 500.94 | 501.65 | 0.71 | 40000 | 0 | 28400 | 28757.3823 | Maniknagar | Narinda 33/11KV S/S | 552771.4205 | 653217.1868 | 492385.8425
926 | 11 kV Manashi Feeder | 11 | 0 | 06604353 | 1 | 5528.76 | 5557.42 | 28.66 | 40000 | 0 | 1146400 | 1160826.1643 | Narinda | Narinda 33/11KV S/S | 1102291.2443 | 1122855.7324 | 1066634.3599
927 | 11 kV Jatrabari Feeder | 11 | 0 | 06604324 | 1 | 3426.03 | 3478.37 | 52.34 | 40000 |  | 2093600 | 2119945.619 | Swamibag | Narinda 33/11KV S/S | 2124511.9226 | 2030258.73 | 1913892.8816
928 | 11 kV Wari Feeder | 11 | 0 | 06604291 | 1 | 8559.74 | 8599.65 | 39.91 | 40000 | 0 | 1596400 | 1616488.912 | Narinda | Narinda 33/11KV S/S | 1686359.282 | 1652611.2397 | 1532808.0158
929 | 11 kV Narinda Feeder | 11 | 0 | 06604348 | 1 | 7302.23 | 7340.4 | 38.17 | 40000 | 0 | 1526800 | 1546013.0737 | Narinda | Narinda 33/11KV S/S | 1594908.1278 | 1590073.4608 | 1585232.3889
930 | 11 kV Distillary Feeder | 11 | 0 | 06604347 | 1 | 5997.97 | 6031.14 | 33.17 | 40000 | 0 | 1326800 | 1343496.2969 | Swamibag | Narinda 33/11KV S/S | 1318115.968 | 1326607.8506 | 1271895.9437
931 | 11 kV Thatari Bazar Feeder | 11 | 0 | 06604296 | 1 | 5033.32 | 5059.48 | 26.16 | 40000 | 0 | 1046400 | 1059567.7759 | Narinda | Narinda 33/11KV S/S | 1097413.8494 | 1083315.7174 | 1015016.5156
932 | 11 kV Swamibagh Feeder | 11 | 0 | 06604352 | 1 | 7795.93 | 7829.38 | 33.45 | 40000 | 0 | 1338000 | 1354837.2364 | Swamibag | Narinda 33/11KV S/S | 1370141.5135 | 1100261.4381 | 886375.1694
933 | 11 kV Tipu Sultan Feeder | 11 | 0 | 06604322 | 1 | 6375.33 | 6403.77 | 28.44 | 40000 | 0 | 1137600 | 1151915.4261 | Narinda | Narinda 33/11KV S/S | 1136839.4581 | 1115189.8112 | 1101315.099
934 | 11 kV Spare | 11 | 0 | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0 | 0
935 | 11 kV Folder Street Feeder | 11 | 0 | DHK00089 | 1 | 30046.6 | 33769.5 | 3722.9 | 444.44 | 0 | 1654605.676 | 1675427.0415 | Narinda | Narinda 33/11KV S/S | 1798340.7365 | 1748933.3106 | 1624153.5662
936 | 11 kV Bhajohari Feeder | 11 | 0 | DHK27842 | 1 | 394199 | 404158 | 9959 | 80 | 0 | 796720 | 806745.8319 | Narinda | Narinda 33/11KV S/S | 813305.5973 | 819688.7194 | 775800.0686
937 | 11 kV Lal mohon shaha Feeder | 11 | 0 | DHK00086 | 1 | 34337.3 | 36773.5 | 2436.2 | 444.44 | 0 | 1082744.728 | 1096369.8618 | Narinda | Narinda 33/11KV S/S | 1097222.2328 | 1092539.7614 | 1048880.237
938 | 11 kV Dupkhola Feeder | 11 | 0 | 8838024/8838029 | 1 | 36817.8 | 37366.6 | 548.8 | 1000 | 0 | 548800 | 555706.0354 | Swamibag | Narinda 33/11KV S/S | 579800.3171 | 568589.4506 | 537047.3757
939 | 11/0.4 kV Aux Transformer-1 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0 | 0
940 | 11/0.4 kV Aux Transformer-2 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0 | 0
941 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62634.8 | 62924.7 | 289.9 | 2222.22 | 0 | 644221.578 | 653524.1946 | Banglabazar | Kumertuly 33/11KV S/S | 604954.0102 | 476949.7245 | 555416.4351
942 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4589.74 | 4623.56 | 33.82 | 40000 | 0 | 1352800 | 1372334.5518 | Banglabazar | Kumertuly 33/11KV S/S | 1164609.944 | 1430849.1736 | 1481110.4937
943 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 0 | 0 | 0
944 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5143.44 | 5156.33 | 12.89 | 40000 | 0 | 515600 | 523045.3096 | Banglabazar | Kumertuly 33/11KV S/S | 442936.2442 | 536568.4401 | 493703.4979
945 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 0 | 0 | 0
946 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5442.14 | 5471.04 | 28.9 | 40000 | 0 | 1156000 | 1172692.7423 | Banglabazar | Kumertuly 33/11KV S/S | 878663.7611 | 1216221.7976 | 1419397.5564
947 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 0 | 40077.0255 | 0
948 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4079.87 | 4110.74 | 30.87 | 40000 | 0 | 1234800 | 1252630.6213 | Banglabazar | Kumertuly 33/11KV S/S | 1111745.9438 | 834662.018 | 740555.2468
949 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1094695.56 | 1110503.0608 | Banglabazar | Kumertuly 33/11KV S/S | 1217802.7423 | 1144679.3389 | 925694.0585
950 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5901.7 | 5929.54 | 27.84 | 40000 | 0 | 1113600 | 1129680.4826 | Banglabazar | Kumertuly 33/11KV S/S | 931127.2764 | 1021492.1651 | 1019206.2302
951 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8198.55 | 8237.18 | 38.63 | 40000 | 0 | 1545200 | 1567512.8248 | Banglabazar | Kumertuly 33/11KV S/S | 2037666.9172 | 1989498.8221 | 1947085.7372
952 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3757.99 | 3769.64 | 11.65 | 40000 | 0 | 466000 | 472729.0813 | Banglabazar | Kumertuly 33/11KV S/S | 450545.4563 | 410865.9482 | 427409.0643
953 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7226.32 | 7256.13 | 29.81 | 40000 | 0 | 1192400 | 1209618.3616 | Banglabazar | Kumertuly 33/11KV S/S | 1050071.2769 | 1251993.0269 | 1073805.1079
954 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3585.71 | 3592.91 | 7.2 | 40000 | 0 | 288000 | 292158.7455 | Banglabazar | Kumertuly 33/11KV S/S | 264720.4859 | 275126.2119 | 281286.3072
955 | 11/0.4 kV AT-1 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 0 | 0 | 0
956 | 11/0.4 kV AT-2 | 0.415 | 0 | 05378636 | 1 | 168944.8 | 170919.3 | 1974.5 | 2 | 0 | 3949 | 4006.0239 | Banglabazar | Kumertuly 33/11KV S/S | 7168.6788 | 4775.6076 | 4915.4072
957 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 38350227 | 39122615 | 772388 | 1 | 0 | 772388 | 773303.2759 | Bangshal | Banshal 33/11KV S/S | 760951.1172 | 778854.3109 | 716311.3918
958 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0 | 0
959 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0 | 0
960 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 49714612 | 51124132 | 1409520 | 1 | 0 | 1409520 | 1411190.2742 | Banglabazar | Banshal 33/11KV S/S | 1426877.2604 | 1429747.5487 | 1353751.6158
961 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 20644794 | 21388011 | 743217 | 1 | 0 | 743217 | 744097.7084 | Bangshal | Banshal 33/11KV S/S | 751903.1259 | 737930.5287 | 715455.6721
962 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 46320451 | 47954741 | 1634290 | 1 | 0 | 1634290 | 1636226.6255 | Bangshal | Banshal 33/11KV S/S | 1167271.1296 | 1660584.0104 | 1409457.3709
963 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 62248027 | 63452528 | 1204501 | 1 | 0 | 1204501 | 1205928.3277 | Bangshal | Banshal 33/11KV S/S | 1183358.8995 | 1169829.7548 | 1127796.6211
964 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 30418512 | 31524023 | 1105511 | 1 | 0 | 1105511 | 1106821.025 | Bangshal | Banshal 33/11KV S/S | 1430551.6276 | 1633419.2244 | 1486833.0286
965 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 62764098 | 64344617 | 1580519 | 1 | 0 | 1580519 | 1582391.9071 | Bangshal | Banshal 33/11KV S/S | 1508639.2033 | 1596892.4609 | 1498407.2378
966 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 50259494 | 51559395 | 1299901 | 1 | 0 | 1299901 | 1301441.3762 | Narinda | Banshal 33/11KV S/S | 1139549.3681 | 1267199.3373 | 1145519.8164
967 | AT-1 | 0.415 | 0 | DHK-4415 | 1 | 734.14 | 734.14 | 0 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0 | 0
968 | AT-2 | 0.415 | 0 | DHK-4410 | 1 | 684.51 | 724.82 | 40.31 | 100 | 0 | 7000 | 7008.295 | Bangshal | Banshal 33/11KV S/S | 7021.7228 | 7023.9917 | 6997.7081
969 | 11 kV Nayanagor Feeder | 11 | 0 | DHK-61125 | 1 | 843800.5 | 874043.5 | 30243 | 60 | 0 | 1814580 | 1836553.7788 | Kazla | Kazla 33/11KV S/S | 1866699.9643 | 1792344.292 | 1710856.4639
970 | 11 kV Madrasa Bazar Feeder | 11 | 0 | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1846586.4161 | Kazla | Kazla 33/11KV S/S | 1853855.1196 | 1913492.0332 | 1855425.2355
971 | 11 kV Kazla Feeder | 11 | 0 | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2919188.16 | 2954538.2657 | Kazla | Kazla 33/11KV S/S | 3027963.362 | 3049627.928 | 2968680.3768
972 | 11 kV Sayedabad Feeder | 11 | 0 | HA021101239-02 | 1 | 36963861 | 36963861 | 0 | 1000 | Estimated | 1216328.4 | 1231057.6107 | Maniknagar | Kazla 33/11KV S/S | 988722.7304 | 1076339.2687 | 556627.5706
973 | 11 kV Zenith Feeder | 11 | 0 | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 0
974 | 11 kV Paterbagh Feeder | 11 | 0 | HA-021200060 | 1 | 114727 | 116728 | 2001 | 1000 | 0 | 2001000 | 2025231.2443 | Jurain | Kazla 33/11KV S/S | 2541656.3466 | 2207984.2138 | 2092993.2394
975 | 11 kV Matuail Feeder | 11 | 0 | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1946125.44 | 1969692.1771 | Kazla | Kazla 33/11KV S/S | 1730264.7783 | 1734102.1551 | 1855425.2355
976 | 11 kV Kutubkhali Feeder | 11 | 0 | DHK-61117 | 1 | 723552 | 760780.4 | 37228.4 | 60 | 0 | 2233704 | 2260753.1891 | Jurain | Kazla 33/11KV S/S | 2379719.4891 | 2279252.9698 | 2232712.5636
977 | 11 kV Mridhabari Feeder | 11 | 0 | DHK-61118 | 1 | 624583.7 | 650400.9 | 25817.2 | 60 | 0 | 1549032 | 1567790.1074 | Kazla | Kazla 33/11KV S/S | 1353302.4526 | 1381440.9902 | 1371332.0993
978 | 11 kV Muslim Nagar Feeder | 11 | 0 | DHK-61011 | 1 | 25255.2 | 67793.5 | 42538.3 | 60 | 0 | 2552298 | 2583205.2246 | Kazla | Kazla 33/11KV S/S | 2385633.1534 | 2345596.1288 | 2459477.0573
979 | 11 kV Jatrabari Thana Feeder | 11 | 0 | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 0
980 | 11 kV Mirhazirbag Feeder | 11 | 0 | DHK-61008 | 1 | 246764.7 | 281446.3 | 34681.6 | 60 | 0 | 2080896 | 2106094.7503 | Swamibag | Kazla 33/11KV S/S | 2092254.4374 | 2069592.0061 | 1962979.7252
981 | 11 kV Mukti Sharani Feeder | 11 | 0 | DHK-61014 | 1 | 113721.9 | 153577.1 | 39855.2 | 60 | 0 | 2391312 | 2420269.7538 | Jurain | Kazla 33/11KV S/S | 2465205.4697 | 2452063.3964 | 2370251.5382
982 | 11 kV Kadamtali Feeder | 11 | 0 | DHK-61006 | 1 | 326888.5 | 373366.3 | 46477.8 | 60 | 0 | 2788668 | 2822437.563 | Shyampur | Kazla 33/11KV S/S | 2221373.5062 | 2471771.8805 | 3092469.9692
983 | 11kV Rayerbagh Feeder | 11 | 0 | DHK-61012 | 1 | 404227.5 | 409542.6 | 5315.1 | 60 | 0 | 318906 | 322767.8137 | Matuail | Kazla 33/11KV S/S | 1280357.0984 | 1277473.0974 | 837095.6004
984 | 11 kV Donia Feeder | 11 | 0 | DHK-61013 | 1 | 1980100 | 2013143 | 33043 | 60 | 0 | 1982580 | 2006588.1861 | Jurain | Kazla 33/11KV S/S | 2090084.0617 | 2017361.1702 | 1952856.964
985 | 11 kV Nimtoli Feeder | 11 | 0 | HA-021100855-02 | 1 | 29423230 | 30931536 | 1508306 | 1 | 0 | 1508306 | 1526570.9331 | Kazla | Kazla 33/11KV S/S | 1509829.6282 | 1633862.5979 | 1591423.3402
986 | 11 kV Gobindapur Feeder | 11 | 0 | HA-021101057-02 | 1 | 26674761 | 27377064 | 702303 | 1 | 0 | 702303 | 710807.5855 | Kazla | Kazla 33/11KV S/S | 721136.817 | 697773.6086 | 686441.9856
987 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | 0 | 9A56136 | 1 | 3271.9 | 3447.6 | 175.7 | 10000 | 0 | 1757000 | 1778276.5099 | Kazla | Kazla 33/11KV S/S | 1887901.7718 | 1946667.4736 | 1703398.1226
988 | 11 kV Samad Nagar Gate (Old) | 11 | 0 | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 0
989 | 11 kV Dharmik Para | 11 | 0 | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 23977.7413 | 1140208.9403
990 | 11 kV Sheikhdi Feeder | 11 | 0 | 9A56133 | 1 | 14288.8 | 15118.7 | 829.9 | 4000 | 0 | 3319600 | 3359798.9198 | Kazla | Kazla 33/11KV S/S | 3415699.9979 | 3248780.7482 | 3103743.9224
991 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 0
992 | 11 kV Jenith Feeder | 11 | 0 | 61903661 | 1 | 20864.4 | 21474.6 | 610.2 | 1000 | 0 | 610200 | 617589.258 | Kazla | Kazla 33/11KV S/S | 551840.3941 | 574043.3834 | 0
993 | 11 KV Samad Nagor Gate | 11 | 0 | 61903675 | 1 | 17718.5 | 18394.6 | 676.1 | 2000 | 0 | 1352200 | 1368574.557 | Kazla | Kazla 33/11KV S/S | 1134163.594 | 1293375.6231 | 1288887.6302
994 | 11 KV Bibir Bagicha | 11 | 0 | 61903557 | 1 | 36323.7 | 37044.1 | 720.4 | 2000 | 0 | 1440800 | 1458247.4647 | Maniknagar | Kazla 33/11KV S/S | 1460126.3972 | 1445370.1189 | 1356006.601
995 | 33/0.4 kV AT-1 | 0.415 | 0 | 503043 | 1 | 96204 | 96204 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 244.069
996 | 33/0.4 kV AT-2 | 0.415 | 0 | 503044 | 1 | 93994 | 93994 | 0 | 10 | 0 | 6000 | 6072.6574 | Kazla | Kazla 33/11KV S/S | 6096.5612 | 6096.0359 | 6101.7246
997 | Auxiliary Transformer | 0.415 | 0 | 41901920685 | 1 | 2407.99 | 2519.17 | 111.18 | 160 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0 | 0
998 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur | 0 | 1 | 625.64 | 667.28 | 41.64 | 40000 | 0 | 1665600 | 1658511.8396 | Shyampur | Shyampur 33/11KV S/S | 1848660.4463 | 1329002.2614 | 1796570.0888
999 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1000 | 11 kV Road No.-21 Feeder | 11 | 0 | BD001943 | 1 | 1043.7 | 1058.93 | 15.23 | 40000 | 0 | 609200 | 606607.4764 | Shyampur | Shyampur 33/11KV S/S | 536986.5578 | 689153.8135 | 726162.1684
1001 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1527.03 | 1547.42 | 20.39 | 40000 | 0 | 815600 | 812129.1164 | Shyampur | Shyampur 33/11KV S/S | 684264.5087 | 768373.9842 | 842780.9272
1002 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1416.53 | 1435.24 | 18.71 | 40000 | 0 | 748400 | 745215.0941 | Shyampur | Shyampur 33/11KV S/S | 653846.0494 | 678120.977 | 664045.6474
1003 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1313.82 | 1338.71 | 24.89 | 40000 | 0 | 995600 | 991363.1049 | Fatullah | Shyampur 33/11KV S/S | 1100803.9423 | 1060453.8119 | 1011898.1651
1004 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3283.24 | 3340.76 | 57.52 | 40000 | 0 | 2300800 | 2291008.6698 | Shyampur | Shyampur 33/11KV S/S | 1731865.3068 | 2347543.3088 | 2415731.5404
1005 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1006 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2133.5 | 2175.85 | 42.35 | 40000 | 0 | 1694000 | 1686790.98 | Shyampur | Shyampur 33/11KV S/S | 1265223.6985 | 1510257.147 | 1400226.6095
1007 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 486.4 | 489.6 | 3.2 | 40000 | 0 | 128000 | 127455.2807 | Fatullah | Shyampur 33/11KV S/S | 91577.1387 | 112254.6055 | 96981.9232
1008 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3122.73 | 3177.03 | 54.3 | 40000 | 0 | 2172000 | 2162756.7937 | Shyampur | Shyampur 33/11KV S/S | 1853587.4081 | 1927999.1795 | 1824622.7112
1009 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1944.14 | 1979.03 | 34.89 | 40000 | 0 | 1395600 | 1389660.8569 | Shyampur | Shyampur 33/11KV S/S | 915888.0248 | 1677475.7016 | 1601003.2355
1010 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1444.14 | 1487.49 | 43.35 | 40000 | 0 | 1734000 | 1726620.7552 | Shyampur | Shyampur 33/11KV S/S | 1517234.7817 | 1359049.2203 | 1887540.7358
1011 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1012 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 820.21 | 839.09 | 18.88 | 40000 | 0 | 755200 | 751986.1559 | Shyampur | Shyampur 33/11KV S/S | 501987.0295 | 565017.3838 | 552636.6613
1013 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1313.8 | 1332.96 | 19.16 | 40000 | 0 | 766400 | 763138.4929 | Shyampur | Shyampur 33/11KV S/S | 788989.597 | 774228.7961 | 1030332.7456
1014 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2984.83 | 3058.77 | 73.94 | 40000 | 0 | 2957600 | 2945013.5787 | Shyampur | Shyampur 33/11KV S/S | 2827927.2998 | 2567335.031 | 2104748.1835
1015 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1016 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1102.63 | 1108.33 | 5.7 | 40000 | 0 | 228000 | 227029.7187 | Shyampur | Shyampur 33/11KV S/S | 174848.8273 | 295251.5179 | 251271.3464
1017 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1946.25 | 1984.95 | 38.7 | 40000 | 0 | 1548000 | 1541412.3005 | Shyampur | Shyampur 33/11KV S/S | 1200352.7042 | 1365805.0805 | 1428279.2319
1018 | 11 kV Spare Feeder | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1019 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1349.95 | 1370.24 | 20.29 | 40000 | 0 | 811600 | 808146.1389 | Shyampur | Shyampur 33/11KV S/S | 598969.7492 | 543740.6288 | 732574.1964
1020 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1323.77 | 1347.53 | 23.76 | 40000 | 0 | 950400 | 946355.4589 | Shyampur | Shyampur 33/11KV S/S | 931203.8377 | 1080348.9594 | 971021.4868
1021 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1022 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1023 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1024 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2236.38 | 2276.03 | 39.65 | 40000 | 0 | 1586000 | 1579250.5869 | Shyampur | Shyampur 33/11KV S/S | 1494594.8892 | 1526560.1151 | 1250345.4555
1025 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 172.64 | 174.71 | 2.07 | 40000 | 0 | 82800 | 82447.6347 | Shyampur | Shyampur 33/11KV S/S | 75834.9927 | 95891.5675 | 84558.6189
1026 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1027 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1189.74 | 1212.54 | 22.8 | 40000 | 0 | 912000 | 908118.8747 | Shyampur | Shyampur 33/11KV S/S | 695610.598 | 869607.7672 | 875642.5706
1028 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3687.08 | 3727.77 | 40.69 | 40000 | 0 | 1627600 | 1620673.5531 | Shyampur | Shyampur 33/11KV S/S | 2160897.1026 | 1905144.5888 | 2092324.8793
1029 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1095.43 | 1108.79 | 13.36 | 40000 | 0 | 534400 | 532125.7967 | Shyampur | Shyampur 33/11KV S/S | 778413.3204 | 463585.7706 | 590307.3256
1030 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1031 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 63890 | 64345 | 455 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1032 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 | 0 | 0 | 1 | 594876 | 603513 | 8637 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1033 | 11/0.4 kV Aux Transformer, T-2 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0 | 0
1034 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 37882493 | 40168290 | 2285797 | 1 | 0 | 2285797 | 2242087.5527 | Shyampur | Shyampur BISIC 33/11KV S/S | 2142439.5507 | 2098065.1104 | 2051822.5774
1035 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 21288823 | 22086911 | 798088 | 1 | 0 | 798088 | 782826.8086 | Jurain | Shyampur BISIC 33/11KV S/S | 745206.3758 | 738065.3088 | 731764.9753
1036 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 0 | 0 | 0
1037 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 0 | 0 | 0
1038 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 437001.6 | 469630.5 | 32628.9 | 60 | 0 | 1957734 | 1920297.8361 | Jurain | Shyampur BISIC 33/11KV S/S | 1596859.747 | 1920766.0882 | 1940683.7189
1039 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 593952.2 | 619977.8 | 26025.6 | 60 | 0 | 1561536 | 1531676.01 | Jurain | Shyampur BISIC 33/11KV S/S | 1098969.809 | 1475476.6819 | 1381608.0185
1040 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 615565.9 | 639408.3 | 23842.4 | 60 | 0 | 1430544 | 1403188.8641 | Jurain | Shyampur BISIC 33/11KV S/S | 1231235.1282 | 1429313.0963 | 1378277.4296
1041 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 351956.3 | 371675.9 | 19719.6 | 60 | 0 | 1183176 | 1160551.0823 | Shyampur | Shyampur BISIC 33/11KV S/S | 887582.2839 | 954363.7317 | 1019394.7492
1042 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 518004.2 | 518057.4 | 53.2 | 60 | 0 | 3192 | 3130.962 | Jurain | Shyampur BISIC 33/11KV S/S | 385792.207 | 8184.8678 | 8596.203
1043 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 871854.9 | 919765.2 | 47910.3 | 60 | 0 | 2874618 | 2819649.0049 | Jurain | Shyampur BISIC 33/11KV S/S | 2794077.3284 | 2700808.4363 | 2561826.8196
1044 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 256885.3 | 282858.7 | 25973.4 | 60 | 0 | 1558404 | 1528603.9007 | Shyampur | Shyampur BISIC 33/11KV S/S | 1237892.1591 | 1229098.1908 | 1284557.7074
1045 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 455733.9 | 466710.5 | 10976.6 | 60 | 0 | 658596 | 646002.2013 | Jurain | Shyampur BISIC 33/11KV S/S | 711159.0569 | 480060.5409 | 1215195.8482
1046 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 526918.2 | 571905.4 | 44987.2 | 60 | 0 | 2699232 | 2647616.7695 | Jurain | Shyampur BISIC 33/11KV S/S | 2636452.1751 | 2526376.4464 | 2465450.8355
1047 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 856542.9 | 869895.1 | 13352.2 | 60 | 0 | 801132 | 785812.6007 | Jurain | Shyampur BISIC 33/11KV S/S | 661368.2767 | 689554.7346 | 725640.3272
1048 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 960702.2 | 984688.2 | 23986 | 60 | 0 | 1439160 | 1411640.1073 | Shyampur | Shyampur BISIC 33/11KV S/S | 1301431.6729 | 1235612.3209 | 1199610.0995
1049 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB7380 | 1 | 608485 | 612273 | 3788 | 1 | 0 | 3788 | 3715.5651 | Shyampur | Shyampur BISIC 33/11KV S/S | 3553.7906 | 3904.2091 | 3633.5474
1050 | 11 kV Spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0 | 0
1051 | 11 kV Khaza Moinuddin | 11 | 0 | 00000026 | 1 | 5408547 | 6089905 | 681358 | 1 | 0 | 681358 | 682477.6462 | Fatullah | Nandalalpur 33/11 kV | 727695.4191 | 676115.2751 | 672821.6526
1052 | 11 kV Chitashal | 11 | 0 | 00000027 | 1 | 33243638 | 33982516 | 738878 | 1 | 0 | 738878 | 740092.1663 | Shyampur | Nandalalpur 33/11 kV | 801503.5058 | 725908.576 | 676035.0889
1053 | 11 kV Local Feeder | 11 | 0 | 00000157 | 1.5 | 18439474 | 18644914 | 205440 | 1 | Estimated | 668980.62 | 670079.927 | Shyampur | Nandalalpur 33/11 kV | 673810.7719 | 652026.96 | 610908.7086
1054 | 11 kV Rasel Germants | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 0 | 0 | 0
1055 | 11 kV Matuail Medical (Adorsho nagar) | 11 | 0 | 00000121 | 1 | 73062544 | 75768256 | 2705712 | 1 | 0 | 2705712 | 2710158.1798 | Matuail | Nandalalpur 33/11 kV | 2342109.1991 | 2438091.1118 | 2521439.5722
1056 | 11 kV Nandalalpur | 11 | 0 | 00000010 | 1 | 83856192 | 84598432 | 742240 | 1 | 0 | 742240 | 743459.691 | Fatullah | Nandalalpur 33/11 kV | 869061.7913 | 928548.3765 | 892208.2473
1057 | 11 kV Sharif Bagh | 11 | 0 | 00000132 | 1 | 71968184 | 73572944 | 1604760 | 1 | 0 | 1604760 | 1607397.0329 | Shyampur | Nandalalpur 33/11 kV | 1797879.9406 | 1716982.5939 | 1682233.437
1058 | 11 kV Spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0 | 0
1059 | 11 KV Nayamati | 11 | 0 | 00000158 | 1 | 65089840 | 66248080 | 1158240 | 1 | 0 | 1158240 | 1160143.2858 | Fatullah | Nandalalpur 33/11 kV | 1059913.8974 | 1145403.0364 | 1037983.1413
1060 | 11 kV Pulpar | 11 | 0 | 00000160 | 1 | 7628741 | 8533019 | 904278 | 1 | 0 | 904278 | 905763.961 | Fatullah | Nandalalpur 33/11 kV | 653442.1412 | 808373.695 | 916555.6279
1061 | 11 kV Shahi Bazar | 11 | 0 | 00000170 | 1 | 40882420 | 41765220 | 882800 | 1 | 0 | 882800 | 884250.6672 | Shyampur | Nandalalpur 33/11 kV | 830388.5657 | 784445.919 | 785444.6114
1062 | 11 kV Pagla Bazar | 11 | 0 | 00000060 | 1 | 50196196 | 50898636 | 702440 | 1 | 0 | 702440 | 703594.2894 | Fatullah | Nandalalpur 33/11 kV | 679748.7175 | 834561.5067 | 783154.3223
1063 | 11 kV Delpara bazar | 11 | 0 | 00000063 | 1 | 79142768 | 80808200 | 1665432 | 1 | 0 | 1665432 | 1668168.7326 | Shyampur | Nandalalpur 33/11 kV | 1521265.0516 | 1508132.7308 | 1527622.8486
1064 | 11 kV Bhuighor (Board mill) | 11 | 0 | 00000146 | 1 | 43749012 | 44459652 | 710640 | 1 | 0 | 710640 | 711807.7641 | Matuail | Nandalalpur 33/11 kV | 702632.7597 | 668462.9794 | 1074021.0416
1065 | 11 kV Spare | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0 | 0
1066 | 33/0.415 kV, 200 kVA AT-1 | 11 | 0 | 7803 | 1 | 2435 | 2494 | 59 | 100 | 0 | 5900 | 5909.6952 | Shyampur | Nandalalpur 33/11 kV | 6446.2091 | 6244.3055 | 5725.7228
1067 | 33/0.415 kV, 200 kVA AT-2 | 11 | 0 | 7805 | 1 | 51 | 52 | 1 | 100 | 100 | 100 | 100.1643 | Shyampur | Nandalalpur 33/11 kV | 0 | 0 | 0
1068 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 62369777 | 63585293 | 1215516 | 1 | 0 | 1215516 | 1219095.1394 | Postogola | Postogola 33/11KV S/S | 1335055.4691 | 1307497.2614 | 1269812.3426
1069 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 9710567 | 10944921 | 1234354 | 1 | Converted to 31 days | 1319481.8621 | 1323367.1334 | Jurain | Postogola 33/11KV S/S | 1374189.6942 | 1360936.1962 | 1367079.5822
1070 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 24070248 | 24605728 | 535480 | 1 | 0 | 535480 | 537056.744 | Jurain | Postogola 33/11KV S/S | 474949.556 | 542387.1952 | 435813.5436
1071 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 74369662 | 75922520 | 1552858 | 1 | 0 | 1552858 | 1557430.4575 | Postogola | Postogola 33/11KV S/S | 1587221.6201 | 1546887.4107 | 1509702.7057
1072 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 428700.2 | 439711.4 | 11011.2 | 60 | 0 | 660672 | 662617.3772 | Postogola | Postogola 33/11KV S/S | 636891.4703 | 664686.4068 | 678488.3278
1073 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 866598.9 | 885538.7 | 18939.8 | 60 | 0 | 1136388 | 1139734.1436 | Postogola | Postogola 33/11KV S/S | 1267305.3443 | 1258808.5211 | 1186933.4512
1074 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 747895 | 771487.6 | 23592.6 | 60 | 0 | 1415556 | 1419724.1658 | Postogola | Postogola 33/11KV S/S | 1247409.4401 | 1227619.0196 | 1164704.2052
1075 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 520016 | 522254.7 | 2238.7 | 60 | 0 | 134322 | 134717.5169 | Postogola | Postogola 33/11KV S/S | 129509.8262 | 124992.5587 | 126222.4118
1076 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 837075.6 | 859898.8 | 22823.2 | 60 | 0 | 1369392 | 1373424.2339 | Postogola | Postogola 33/11KV S/S | 1052907.1287 | 1323292.4846 | 1331811.5849
1077 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 324272.2 | 364927.9 | 40655.7 | 60 | 0 | 2439342 | 2446524.7479 | Jurain | Postogola 33/11KV S/S | 2443876.2234 | 2429557.5202 | 2393972.4885
1078 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 38603647 | 40818183 | 2214536 | 1 | 0 | 2214536 | 2221056.7969 | Jurain | Postogola 33/11KV S/S | 2061497.5542 | 2071894.6482 | 1933992.5359
1079 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 8284 | 10753.8 | 2469.8 | 1000 | 0 | 2469800 | 2477072.4328 | Jurain | Postogola 33/11KV S/S | 2360182.711 | 2388027.6504 | 2351667.7366
1080 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 56071015 | 57721254 | 1650239 | 1 | 0 | 1650239 | 1655098.2 | Postogola | Postogola 33/11KV S/S | 1632466.5583 | 1639249.0712 | 1571920.5306
1081 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 53216071 | 53444745 | 228674 | 1 | Converted to 31 days | 244444.6207 | 245164.3984 | Postogola | Postogola 33/11KV S/S | 245637.4316 | 262708.1006 | 303872.8913
1082 | 11/0.415 kV, 200 kVA AT-1+2 | 11 | 0 | ELIB67385 | 1 | 368.64 | 426.85 | 58.21 | 80 | 0 | 4656.8 | 4670.5121 | Postogola | Postogola 33/11KV S/S | 4307.9725 | 5751.9551 | 4375.6621
1083 | 11 kV Feeder-1 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0 | 0
1084 | 11 kV Feeder-2 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0 | 0
1085 | 11 kV Dholaikal RMU | 11 | 0 | DHK60970 | 1 | 223582.9 | 261150.8 | 37567.9 | 60 | 0 | 2254074 | 2258178.5414 | Banglabazar | IG Gate GIS 33/11 kV | 2013206.2605 | 1942348.072 | 1890634.7965
1086 | 11 kV Alom Gonj | 11 | 0 | DHK60894 | 1 | 479815.2 | 491074.8 | 11259.6 | 60 | 0 | 675576 | 676806.1857 | Postogola | IG Gate GIS 33/11 kV | 596654.2301 | 589855.3321 | 589628.102
1087 | 11 kV Dhalka Nagar Feeder (F-5) | 11 | 0 | DHK60895 | 1 | 536337.9 | 567540.5 | 31202.6 | 60 | 0 | 1872156 | 1875565.0903 | Postogola | IG Gate GIS 33/11 kV | 1850628.0181 | 1792355.2732 | 1711977.4089
1088 | 11 kV Farashgonj Feeder (F-6) | 11 | 0 | DHK68133 | 1 | 3589.15 | 3623.21 | 34.06 | 60000 | 0 | 2043600 | 2047321.2801 | Banglabazar | IG Gate GIS 33/11 kV | 1803939.5949 | 1748762.5817 | 1815572.1775
1089 | 11 kV Doyaganj | 11 | 0 | DHK68134 | 1 | 2380.418 | 2414.18 | 33.762 | 60000 | Estimated | 1642043.34 | 1645033.4081 | Swamibag | IG Gate GIS 33/11 kV | 1687142.9696 | 1819772.2117 | 1955417.8504
1090 | 11 kV Faridabad | 11 | 0 | DHK68140 | 1 | 772.95 | 796.44 | 23.49 | 60000 | 0 | 1409400 | 1411966.4378 | Postogola | IG Gate GIS 33/11 kV | 1296128.1808 | 1292615.9757 | 1233789.9626
1091 | 11 kV Gandaria | 11 | 0 | DHK60969 | 1 | 372411.9 | 407296.5 | 34884.6 | 60 | 0 | 2093076 | 2096887.3731 | Postogola | IG Gate GIS 33/11 kV | 2186472.7241 | 2176408.4497 | 2008723.2675
1092 | 11 kV Walter Road | 11 | 0 | DHK68136 | 1 | 973.45 | 998.43 | 24.98 | 60000 | 0 | 1498800 | 1501529.2301 | Banglabazar | IG Gate GIS 33/11 kV | 1391040.5522 | 1437042.3417 | 1402694.4766
1093 | 11 kV Murgitola Feeder (F-11) | 11 | 0 | DHK68138 | 1 | 3890.75 | 3930.95 | 40.2 | 60000 | 0 | 2412000 | 2416392.1157 | Swamibag | IG Gate GIS 33/11 kV | 2307519.2472 | 2337901.7997 | 2438521.0841
1094 | 11 kV Feeder-12 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0 | 0
1095 | 11 kV Begumgonj Feeder (F-13) | 11 | 0 | DHK60899 | 1 | 667472.2 | 696216.8 | 28744.6 | 60 | 0 | 1724676 | 1727816.5375 | Swamibag | IG Gate GIS 33/11 kV | 1778252.8009 | 1741101.9665 | 1809148.9629
1096 | 11 kV Lohar Pool Feeder (F-14) | 11 | 0 | DHK60967 | 1 | 166011.3 | 182818.7 | 16807.4 | 60 | 0 | 1008444 | 1010280.3195 | Postogola | IG Gate GIS 33/11 kV | 1031522.1618 | 1006862.3928 | 984580.1304
1097 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB2774 | 1 | 279327 | 279327 | 0 | 1 | 0 | 0 | 0 | Postogola | IG Gate GIS 33/11 kV | 1665.5005 | 1667.9239 | 1718.3058
1098 | Nizambag | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1155511.98 | 1158100.6579 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1095738.2283 | 1008260.1492 | 972380.6635
1099 | Merry Stopes | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 328408.668 | 329144.3975 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 365246.0761 | 355856.5232 | 364642.7488
1100 | Mujibur Ghat | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1340958.6566 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1217486.9203 | 1304807.2519 | 1337023.4124
1101 | Madrasa | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1459594.08 | 1462863.989 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1424459.6968 | 1542044.934 | 1701666.1612
1102 | Thana | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1219053.3241 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1217486.9203 | 1423426.093 | 1337023.4124
1103 | Al-Hera | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0 | 0 | 0
1104 | Waz Uddin School | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 973062.72 | 975242.6593 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 730492.1522 | 830331.8876 | 972380.6635
1105 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0 | 0 | 0
1106 | Bashundhara City | 33 | 0 | 660434 | 1 | 765.8 | 778.29 | 12.49 | 180000 | 0 | 2248200 | 2253160.9458 | Shere b.nagar | Moghbazar 132/33/11KV S/S | 2286948.2926 | 2480389.347 | 2161081.9864
1107 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4526.7 | 4547.07 | 20.37 | 240000 | 0 | 4888800 | 4868511.8333 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 6352475.5818 | 7317548.4229 | 5615154.9463
1108 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 361720 | 366308.8 | 4588.8 | 2000 | 0 | 9177600 | 9139513.6232 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 7905743.5896 | 8068621.1441 | 8850787.3005
1109 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1011.11 | 1013.16 | 2.05 | 240000 | 0 | 492000 | 492000 | Siddirgonj | Demra 33/11KV S/S | 571200 | 446400 | 0
1110 | 33 kV ACI Pharmacuticles Feeder | 33 | 0 | DHKC4791 | 1 | 900.2 | 913.82 | 13.62 | 90000 | 0 | 1225800 | 1225800 | N.Gonj (East) | Khanpur 33/11KV S/S | 1291500 | 1045800 | 0
1111 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC | 0 | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 9099 | 9119.9454 | Matuail | Matuail 132/33 KV S/S | 10440.0638 | 10260.3419 | 10991.7418
1112 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 40076.123 | 41019.721 | 943.598 | 1000 | 0 | 943598 | 944204.0986 | Sytalakhya | Sitalakhya 132/33KV S/S | 2494536.8881 | 923421.8011 | 1229303.7954
1113 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S | 0 | 0 | 0
1114 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4676 | 4724.7 | 48.7 | 160 | 0 | 7792 | 7797.005 | Sytalakhya | Sitalakhya 132/33KV S/S | 4755.5609 | 4035.644 | 2848.7249
1115 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 307.61 | 327.5 | 19.89 | 360000 | 0 | 7160400 | 7171154.3348 | Sytalakhya | Char Syedpur 132/33KV S/S | 6850018.059 | 6815752.3123 | 6616060.3155
1116 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 100.77 | 107.4 | 6.63 | 360000 | 0 | 2386800 | 2390384.7783 | Sytalakhya | Char Syedpur 132/33KV S/S | 2530901.4092 | 2430058.343 | 2458012.5886
1117 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0 | 0
1118 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0 | 0
1119 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 400185.2656 | 1006790.1928 | 1108090.8439
1120 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0 | 0
1121 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0 | 0
1122 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 460.46 | 493.35 | 32.89 | 360000 | 0 | 11840400 | 11858183.3118 | Sytalakhya | Char Syedpur 132/33KV S/S | 9272761.2883 | 10712537.375 | 10817421.0397
1123 | 11 KV Shahidbagh Feeder | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 588674 | 597504.11 | Rajarbag | Santinagar Switching S/S | 524779.3911 | 36416.7693 | -3994.0825
1124 | 11 Fortune(MogBazar)-new | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 105886 | 107474.29 | Moghbazar | Santinagar Switching S/S | 138756.0658 | 127666.1608 | 126229.899
1125 | Centerpoint-Kakrail | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 43200 | 43848 | Kakrail | Santinagar Switching S/S | 71600.1051 | 81766.8748 | 80846.9863
1126 | 11 KV Shyamoli O/H | 11 | 0 | DHK-15026 | 1 | 9179.18 | 9192.48 | 13.3 | 40000 | 0 | 532000 | 545300 | Shere b.nagar | Agargaon 33/11 KV S/S | 584660 | 530950
1127 | 11 KV Nearest RMU | 11 | 0 | DHK-15027 | 1 | 3863.97 | 3867.99 | 4.02 | 40000 | 0 | 160800 | 164820 | Shere b.nagar | Agargaon 33/11 KV S/S | 182450 | 165230
1128 | 11 KV Sher-e-bangla Nagar | 11 | 0 | DHK-15025 | 1 | 3977.36 | 3978.44 | 1.08 | 40000 | 0 | 43200 | 44280 | Shere b.nagar | Agargaon 33/11 KV S/S | 49610 | 45920
1129 | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S | 0 | -13837.5
1130 | 33/0.4 kV, 500 kVA AT-1 | 0.4 | 0 | 84.2659 | 1 | 316189 | 318696 | 2507 | 10 | 0 | 25070 | 25078.0786 | Paribag | Dhanmondi 33/11KV S/S | 24914.239 | 24707.6715
1131 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 | 0 | 84.2673 | 1 | 478688 | 478689 | 1 | 10 | 0 | 10 | 10.0032 | Paribag | Dhanmondi 33/11KV S/S | 0 | 0
1132 | 33 KV Japan Genden City | 33 | 0 | DHK15681 | 1 | 442.67 | 523.32 | 80.65 | 18000 | 0 | 1451700 | 1451700 | Adabor | Japan Garden 33/11 KV | 1519200 | 1531620
1133 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKE6223 | 1 | 43047.09 | 43238.07 | 190.98 | 120 | 0 | 22917.6 | 23415.1565 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 24412.3409 | 25361.4506
1134 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 0 | 0
1135 | AT-1 | 0.415 | 0 | 0 | 1 | 502.11 | 657.61 | 155.5 | 80 | 0 | 12440 | 12573.2122 | Mugdapara | Madarteck 33/11KV S/S | 11708.7885 | 9611.7345
1136 | AT-2 | 0.415 | 0 | 63394003 | 1 | 233.54 | 303.41 | 69.87 | 80 | 0 | 5589.6 | 5649.4556 | Mugdapara | Madarteck 33/11KV S/S | 6156.9427 | 5477.3433
1137 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 571.22 | 592.95 | 21.73 | 360000 | 0 | 7822800 | 7833434.8553 | Kazla | Kazla 132/133 KV SS | 7323524.0635 | 7145780.8426
1138 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 630.73 | 661.44 | 30.71 | 360000 | 0 | 11055600 | 11070629.7471 | Kazla | Kazla 132/133 KV SS | 10019388.2364 | 9121125.0936
1139 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20947 | 21210 | 263 | 2000 | 0 | 526000 | 531621.6224 | Maniknagar | Maniknagar 132/33 KV SS | 605078.9898 | 1062218.4705
1140 | Axuxilary -1 | 0.415 | 0 | AH14044078 | 1 | 403596.2 | 408804 | 5207.8 | 1 | 0 | 5207.8 | 5213.2044 | Maniknagar | Maniknagar 132/33/11KV S/S | 5831.4157 | 6475.0369
1141 | Axuxilary -2 | 0.415 | 0 | AH14044072 | 1 | 374573.2 | 378951 | 4377.8 | 1 | 0 | 4377.8 | 4382.3431 | Maniknagar | Maniknagar 132/33/11KV S/S | 5377.7142 | 4841.9103
1142 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 725.5189 | 736.898 | 11.3791 | 240000 | 0 | 2730984 | 2731257.9254 | Shyampur | Shyampur 132/33KV S/S | 2448780.2928 | 2460914.9302
1143 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 637.06 | 647.0944 | 10.0344 | 240000 | 0 | 2408256 | 2408497.5549 | Shyampur | Shyampur 132/33KV S/S | 1851141.9981 | 2281164.2763
1144 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1143.578 | 1183.389 | 39.811 | 240000 | 0 | 9554640 | 9555598.3573 | Shyampur | Shyampur 132/33KV S/S | 9761265.4061 | 10754060.1599
1145 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 135.586 | 143.0939 | 7.5079 | 240000 | 0 | 1801896 | 1802076.7353 | Shyampur | Shyampur 132/33KV S/S | 1343089.4196 | 1442423.9509
1146 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1511.052 | 1541.9069 | 30.8549 | 240000 | 0 | 7405176 | 7405918.76 | Shyampur | Shyampur 132/33KV S/S | 5422228.9014 | 6501978.5941
1147 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2365.387 | 2403.8439 | 38.4569 | 240000 | 0 | 9229656 | 9230581.7605 | Shyampur | Shyampur 132/33KV S/S | 8256580.7385 | 8640663.1605
1148 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 677.3128 | 682.176 | 4.8632 | 240000 | Prime Textile | 1167168 | 1167285.0702 | Fatullah | Shyampur 132/33KV S/S | 1147950.5517 | 674551.2513
1149 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 343.416 | 345.49 | 2.074 | 2400 | 0 | 5102.04 | 5102.04 | Fatullah | Shyampur 132/33KV S/S | 5527.62 | 10071.24
1150 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 95.379 | 102.714 | 7.335 | 2400 | 0 | 18044.1 | 18044.1 | Fatullah | Shyampur 132/33KV S/S | 19434 | 11042.94
1151 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 278.72 | 300.227 | 21.507 | 480000 |  | 10329120 | 10329120 | Sytalakhya | MI CEMENT 132/33 kV | 10749120 | 9239520
1152 | 33 kV Shah Cement Feeder | 33 | 0 | 8993 841 | 1 | 39374.588 | 39440.16 | 65.572 | 36000 | 0 | 2360592 | 2360592 | Sytalakhya | Madonganj 132/33 KV SS | 3210156 | 3227092
1153 | 33 kV Mondol Para (Premire cement) Feeder | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS | 0 | 0
1154 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 0 | 0 | Dhanmondi | Jigatola Switching | 679467.069
1155 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1581226.92 | 1579031.3193 | Jigatola | Jigatola Switching | 1587392.6308
1156 | 11 kV Mitali | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1506373.08 | 1504281.4171 | Jigatola | Jigatola Switching | 1520651.6572

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month August-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month August-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.09.2023 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 9358458.9781 | 19826152.6597 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 7122678.34 |  | North | 309239220.1308 | Tejgaon | 61119170.0927 | Tejgaon | 34065933.7505 | 34031890.1848 | 34043.5657 | 0.10003 | North | 309239220.1308 | 303699254.015 | 1.7915 | Tejgaon | 61119170.0927 | 59346933 | 2.8996 | Tejgaon | 34065933.7505 | 31468806 | 7.6238 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 416692.9 | [5 empty] | Kakrail | 27053236.3422 | 28375284.9016 | -1322048.5594 | -4.6592 | [8 empty] | Kakrail | 27053236.3422 | 27878127 | -3.0491 | 2 | Tejgaon | 31468806 | 196426 | 31665232 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | -1039625.1815
|  |  |  | Maghbazar | 2928322.4416 |  |  |  | Moghbazar | 37378950.5815 | Moghbazar | 20829444.6511 | 21329436.2056 | -499991.5545 | -2.3441 |  |  |  |  | Moghbazar | 37378950.5815 | 36894933 | 1.2949 | Moghbazar | 20829444.6511 | 20573106 | 1.2307 | 3 | Kakrail | 27878127 | 134050 | 28012177 | A1 | Motijheel | 22865869 | 164088 | 23029957
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 14330216.2987 |  |  |  |  | Khilgaon | 16549505.9304 | 16918091.0673 | -368585.1369 | -2.1786 | [8 empty] | Khilgaon | 16549505.9304 | 16321827 | 1.3757 | 4 | Moghbazar | 20573106 | 63535 | 20636641 | A2 | Khilgaon | 16321827 | 59703 | 16381530
|  |  |  | Jigatola | 2689559.5981 |  |  |  | Satmasjid | 48268477.3057 | Satmosjid | 23310707.9778 | 23421031.5433 | -110323.5656 | -0.47104 |  |  |  |  | Satmasjid | 48268477.3057 | 46167247 | 4.3532 | Satmosjid | 23310707.9778 | 22160943 | 4.9323 | 5 | Khilgaon | 16321827 | 59703 | 16381530 | A3 | Lalbag | 32204138 | 464799 | 32668937
|  |  |  | Paribagh | 11640656.7006 | [5 empty] | Sherebanglanagar | 24957769.3279 | 25550090.7434 | -592321.4155 | -2.3183 | [8 empty] | Sherebangla nagar | 24957769.3279 | 24006304 | 3.8123 | 6 | Satmosjid | 22160943 | 83495 | 22244438 | A4 | Kazla | 38390804 | 86446 | 38477250
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 14660370 |  |  | Dhanmondi | 53293002.276 | Dhanmondi | 24286961.2779 | 24788375.0068 | -501413.7289 | -2.0228 |  |  |  |  | Dhanmondi | 53293002.276 | 53818759.15 | -0.98654 | Dhanmondi | 24286961.2779 | 24555384 | -1.1052 | 7 | Sherebanglanagar | 24006304 | 57477 | 24063781 | A5 | Postogola | 15925283 | 139839 | 16065122
[11 empty] | Jhigatala | 29006040.9982 | 29481491.9766 | -475450.9784 | -1.6127 | [8 empty] | Jhigatala | 29006040.9982 | 29263375.15 | -0.88717 | 8 | Dhanmondi | 24555384 | 124825 | 24680209 | A6 | Banglabazar | 16227586 | 65470 | 16293056
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 56230206.9247 | Azimpur | 20469030.3009 | 20094312.838 | 374717.4629 | 1.8648 |  |  |  |  | Azimpur | 56230206.9247 | 54252662.865 | 3.5169 | Azimpur | 20469030.3009 | 19587741 | 4.3055 | 9 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274 | A7 | N.Gonj (West) | 28707452 | 196212 | 28903664
|  |  |  | Dhanmondi | 14660370 | [5 empty] | Paribagh | 35761176.6239 | 36086512.9374 | -325336.3136 | -0.90155 | [8 empty] | Paribagh | 35761176.6239 | 34664921.865 | 3.0655 | 10 | Azimpur | 19587741 | 236081 | 19823822 | A8 | Siddirgonj | 49639472 | 532212 | 50171684
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 22942915.0586 | 22942915.0586 |  |  | Shamoly | 52949412.9502 | Shyamoli | 18862155.4031 | 19659362.7576 | -797207.3544 | -4.0551 |  |  |  |  | Shamoly | 52949412.9502 | 53218719 | -0.50861 | Shyamoli | 18862155.4031 | 19516523 | -3.4692 | 11 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448 | A9 | Bashabo | 14583022 | 53363 | 14636385
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 15306010.6385 |  |  |  |  | Adabor | 34087257.547 | 33945911.5689 | 141345.9781 | 0.41639 | [8 empty] | Adabor | 34087257.547 | 33702196 | 1.1296 | 12 | Shyamoli | 19516523 | 64518 | 19581041 | B1 | Narinda | 13978240 | 38770 | 14017010
|  |  |  | RAMNA | 1502531.2583 |  | Central | 281759077.7173 | Lalbagh | 81389124.2923 | Lalbagh | 37849772.8377 | 32545410.1246 | 5304362.7131 | 16.2983 | Central | 281759077.7173 | 262953550.91 | 6.6743 | Lalbagh | 81389124.2923 | 70781931 | 13.0327 | Lalbagh | 37849772.8377 | 32204138 | 14.9159 | 13 | Adabor | 33702196 | 255452 | 33957648 | B2 | Maniknagar | 20970662 | 109760 | 21080422
|  |  |  | Kakrail | 1845587.6038 | [5 empty] | Kamrangirchar | 43539351.4546 | 38848556.6907 | 4690794.7639 | 12.0746 | [8 empty] | Kamrangirchar | 43539351.4546 | 38577793 | 11.3956 | 14 | Lalbagh | 32204138 | 464799 | 32668937 | B3 | Jurain | 27684985 | 453096 | 28138081
|  |  |  | Paribagh | 11957891.7764 |  |  |  | Ramna | 47983558.4152 | Ramna | 29668920.4409 | 29132056.3783 | 536864.0626 | 1.8429 |  |  |  |  | Ramna | 47983558.4152 | 47932700 | 0.10599 | Ramna | 29668920.4409 | 28702610 | 3.257 | 15 | Kamrangirchar | 38577793 | 101944 | 38679737 | B4 | Shyampur | 66519316 | 426920 | 66946236
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 4107723.2513 |  |  |  |  | Rajarbagh | 18314637.9743 | 19839259.3057 | -1524621.3314 | -7.6849 | [8 empty] | Rajarbagh | 18314637.9743 | 19230090 | -4.9985 | 16 | Ramna | 28702610 | 211333 | 28913943 | B5 | Swamibag | 13880852 | 46920 | 13927772
|  |  |  | Kakrail | 311571.5801 |  |  |  | Bashabo | 40660852.8477 | Bashabo | 14965275.1098 | 15301078.259 | -335803.1492 | -2.1946 |  |  |  |  | Bashabo | 40660852.8477 | 39590401.91 | 2.6326 | Bashabo | 14965275.1098 | 14583022 | 2.5543 | 17 | Rajarbagh | 19230090 | 88052 | 19318142 | B6 | Bangshal | 19038085 | 79495 | 19117580
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 25695577.7378 | 26579332.7573 | -883755.0195 | -3.325 | [8 empty] | Bonossri | 25695577.7378 | 25007379.91 | 2.6783 | 18 | Bashabo | 14583022 | 53363 | 14636385 | B7 | N.Gonj (East) | 30757520 | 509964 | 31267484
|  |  |  | Shere Bangla Nagar | 3796151.6712 |  |  |  | Motijheel | 42673885.064 | Motijheel | 22692835.4241 | 22930447.2198 | -237611.7957 | -1.0362 |  |  |  |  | Motijheel | 42673885.064 | 41523755 | 2.6952 | Motijheel | 22692835.4241 | 22865869 | -0.7625 | 19 | Bnossri | 25007379.91 | 102145 | 25109524.91 | B8 | Fateullah | 32245904 | 463782 | 32709686
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1770122.6257 | 9704868.9662 |  |  |  |  | Mughdapara | 19981049.6399 | 20216338.7843 | -235289.1444 | -1.1639 | [8 empty] | Mughdapara | 19981049.6399 | 18657886 | 6.6221 | 20 | Motijheel | 22865869 | 164088 | 23029957 | B9 | Mugdapara | 18657886 | 36172 | 18694058
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 38406823.579 | Banglabazar | 17978655.3258 | 16484479.4051 | 1494175.9207 | 9.0641 |  |  |  |  | Banglabazar | 38406823.579 | 35265671 | 8.1786 | Banglabazar | 17978655.3258 | 16227586 | 9.7397 | 21 | Mughdapara | 18657886 | 36172 | 18694058 | C1 | Tejgaon | 31468806 | 196426 | 31665232
|  |  |  | Narinda | 443349.7565 | [5 empty] | Bongshal | 20428168.2532 | 19249211.1209 | 1178957.1323 | 6.1247 | [8 empty] | Bongshal | 20428168.2532 | 19038085 | 6.8047 | 22 | Banglabazar | 16227586 | 65470 | 16293056 | C2 | Satmasjid | 22160943 | 83495 | 22244438
|  |  |  | Motijheel | 477711.0916 |  |  |  | Narinda | 30644833.5191 | Narinda | 15412155.6155 | 15837103.8048 | -424948.1893 | -2.6832 |  |  |  |  | Narinda | 30644833.5191 | 27859092 | 9.0904 | Narinda | 15412155.6155 | 13978240 | 9.3038 | 23 | Bongshal | 19038085 | 79495 | 19117580 | C3 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448
|  |  |  | RAMNA | 7013685.4924 | [5 empty] | Swamibagh | 15232677.9036 | 15168311.6806 | 64366.223 | 0.42435 | [8 empty] | Swamibagh | 15232677.9036 | 13880852 | 8.8745 | 24 | Narinda | 13978240 | 38770 | 14017010 | C6 | Kakrail | 27878127 | 134050 | 28012177
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 451430261.7686 | Kazla | 62410377.2053 | Kazla | 41030120.9927 | 38787299.8942 | 2242821.0986 | 5.7824 | South | 451430261.7686 | 418742139 | 7.241 | Kazla | 62410377.2053 | 59361466 | 4.8853 | Kazla | 41030120.9927 | 38390804 | 6.4326 | 25 | Swamibagh | 13880852 | 46920 | 13927772 | D1 | Moghbazar | 20573106 | 63535 | 20636641
|  | Khillgaon 33/11KV S/S |  | Kakrail | 43848 | 6047705.559 |  |  |  |  | Maniknagar | 21380256.2125 | 21298139.082 | 82117.1305 | 0.38556 | [8 empty] | Maniknagar | 21380256.2125 | 20970662 | 1.9158 | 26 | Kazla | 38390804 | 86446 | 38477250 | D2 | Dhanmondi | 24555384 | 124825 | 24680209
|  |  |  | Khilgaon | 0 |  |  |  | Shyampur | 97846530.0418 | Shyampur | 73920113.8277 | 66549426.7658 | 7370687.0618 | 11.0755 |  |  |  |  | Shyampur | 97846530.0418 | 88513636 | 9.5383 | Shyampur | 73920113.8277 | 66519316 | 10.0119 | 27 | Maniknagar | 20970662 | 109760 | 21080422 | D3 | Ramna | 28702610 | 211333 | 28913943
| 9 |  |  | Maghbazaar | 107474.29 | [5 empty] | Matuail | 23926416.2142 | 23544863.4499 | 381552.7642 | 1.6205 | [8 empty] | Matuail | 23926416.2142 | 21994320 | 8.0752 | 28 | Shyampur | 66519316 | 426920 | 66946236 | D4 | Shyamoli | 19516523 | 64518 | 19581041
|  |  |  | Rajarbagh | 5896383.269 |  |  |  | Postogola | 46741302.8369 | Postogola | 16483181.5514 | 16101783.0766 | 381398.4748 | 2.3687 |  |  |  |  | Postogola | 46741302.8369 | 43610268 | 6.6986 | Postogola | 16483181.5514 | 15925283 | 3.3847 | 29 | Matuail | 21994320 | 179400 | 22173720 | D5 | Shere b.nagar | 24006304 | 57477 | 24063781
| 10 | Goran 33/11KV S/S |  | Bashabo | 1499139.6523 | 9831037 |  |  |  |  | Jurain | 30258121.2855 | 29452481.21 | 805640.0755 | 2.7354 | [8 empty] | Jurain | 30258121.2855 | 27684985 | 8.504 | 30 | Postogola | 15925283 | 139839 | 16065122 | D6 | Rajarbag | 19230090 | 88052 | 19318142
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 66959290.0498 | Narayangonj-West | 33520928.7636 | 30519764.2002 | 3001164.5634 | 9.8335 |  |  |  |  | Narayangonj | 66959290.0498 | 59464972 | 11.1923 | Narayangonj- West | 33520928.7636 | 28707452 | 14.3596 | 31 | Jurain | 27684985 | 453096 | 28138081 | D8 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274
|  |  |  | Banosree | 8331897.3477 | [5 empty] | Narayangonj-East | 33438361.2862 | 31800817.8855 | 1637543.4007 | 5.1494 | [8 empty] | Narayangonj- East | 33438361.2862 | 30757520 | 8.0173 | 32 | Narayangonj-West | 28707452 | 196212 | 28903664 | D9 | Azimpur | 19587741 | 236081 | 19823822
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 11950551.0003 | 15818849.9251 |  |  | Demra | 75934204.2552 | Demra | 24793669.9998 | 24683428.3053 | 110241.6946 | 0.44662 |  |  |  |  | Demra | 75934204.2552 | 71702210 | 5.5732 | Demra | 24793669.9998 | 22062738 | 11.0146 | 33 | Narayangonj-East | 30757520 | 509964 | 31267484 | E1 | Demra | 22062738 | 533151 | 22595889
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 51140534.2553 | 51179003.4461 | -38469.1908 | -0.075166 | [8 empty] | Siddhirgonj | 51140534.2553 | 49639472 | 2.9352 | 34 | Damra | 22062738 | 533151 | 22595889 | E2 | Matuail | 21994320 | 179400 | 22173720
|  |  |  | Bashabo | 3868298.9248 |  |  |  | Fatullah | 101538557.3797 | Fatulla | 34919255.7842 | 33464369.2197 | 1454886.5645 | 4.3476 |  |  |  |  | Fatullah | 101538557.3797 | 96089587 | 5.3664 | Fatulla | 34919255.7842 | 32245904 | 7.6558 | 35 | Siddhirgonj | 49639472 | 532212 | 50171684 | E3 | Sytalakha | 63843683 | 329125 | 64172808
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 21537000 |  |  |  |  | Shitalakha | 66619301.5955 | 65632174.0045 | 987127.591 | 1.504 | [8 empty] | Sytalakhya | 66619301.5955 | 63843683 | 4.1664 | 36 | Fatulla | 32245904 | 463782 | 32709686 | F1 | Kamrangirchar | 38577793 | 101944 | 38679737
|  |  |  | Shyamoli | 3073000.4854 |  | TOTAL=> | 1042428559.6168 | TOTAL=> | 1042428559.6168 | TOTAL=> | 1042428559.6168 | 1018826927.8022 | 23601631.8146 | 2.3165 |  | 1042428559.6168 | 985394943.925 |  | TOTAL=> | 1042428559.6168 | 985394943.925 |  | Total=> | 1042428559.6168 | 985394943.925 | 5.4712 | 37 | Shitalokko | 63843683 | 329125 | 64172808 | F2 | Banosree | 25007379.91 | 102145 | 25109524.91
|  |  |  | Shere Bangla Nagar | 0 | [23 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823 | G1 | Adabor | 33702196 | 255452 | 33957648
|  |  |  | Satmosjid | 11660182.507 | [14 empty] | 132KV Import => |  |  |  |  | 1047706516.48 | [8 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823
|  |  |  | Dhanmondi NOCS | 6803817.0076 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 1047706516.48 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 1042428559.6168
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 1042428559.6168 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.50376
| 13 | Japan garden Building |  | Adabor | 1451700 | 1451700 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.50376 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 985394943.925
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 5277956.8632 | [8 empty] | System loss at 132kv level => |  |  |  |  | 5.9474
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 2277600 | 2277600
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 11877454 | 12633084
| 16 |  |  | Shere Bangla Nagar | 755630
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 27746140.1976 | 27746140.1976
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1661564.6485 | 11869320.4204
|  |  |  | Lalbagh | 10207755.7719
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 8516656.2021
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 8516656.2021
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 2720315.5362 | 10621021.4283
|  |  |  | Rajarbaghl | 3005467.2124
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 4895238.6797 | 4895238.6797
|  | Banshal 33/11 KV S/S |  | Bangshal | 7055777.1646 | 9768408.8149
|  |  |  | Banglabazar | 1411190.2742
|  |  |  | Narinda | 1301441.3762
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 12349816.6191 | 17148800
|  |  |  | Shamoly | 4002700.5134
|  |  |  | Satmosjit | 796282.8675
|  | Azimpur 33/11 KV |  | jigatola | 791117.6745 | 17401295.8295
|  |  |  | Azimpur | 14312615.3423
|  |  |  | RAMNA | 1562110.2648
|  |  |  | Paribagh | 735452.5478
|  | T&T 33/11 KV |  | Kakrail | 3324142.3903 | 11193645.8514
|  |  |  | Mogbazar | 6141141.1322
|  |  |  | Khilgaon | 1728362.3289
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 3942567.1741 | 7426800
|  |  |  | Shamoly | 2830417.9764
|  |  |  | Tejgaon | 653697.2316
|  |  |  | Satmosjit | 117.618
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 24517604.1258 | 27061440
|  |  |  | Kamrangirchar | 2543835.8742
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 3467000.3909 | 4793276.52
|  |  |  | Kakrail | 1326276.1291
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1181057.034
|  |  |  | Shere Bangla Nagar | 1618310.88
|  |  |  | Shamoly | 8956036.428
|  |  |  | Satmosjit | 5759589.034
|  | Banasree 33/11SS |  | Khilgaon | 2299125.6951
|  |  |  | Bansree | 12929197.377 | 12929197.377
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 571466.9061 | 18113735.3391
|  |  |  | Bashabo | 7672942.4249
|  |  |  | Mugdapara | 3990242.2602
|  |  |  | Maniknagor | 5879083.7479
|  | DMC |  | Bangshal | 2985071.8185
|  |  |  | RAMNA | 1975422.4635 | 4489011.401
|  |  |  | Lalbagh | 2513588.9375
|  | Green Road Dormatory |  | Paribagh | 8229448.8489
|  |  |  | Shere Bangla Nagar | 5651917.0608
|  | BSMMU 33/11KV S/S |  | Kakrail | 1985542.975
|  |  |  | Paribagh | 3197726.7501
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 8408286.9279
|  |  |  | Satmasjid | 5094535.9513
|  | Dhaka University 33/11 KV SS |  | RAMNA | 2027500
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 6523338.696
|  |  |  | Kakrail | 954092.1837
|  |  |  | Tejgaon | 3346643.1203
|  | BGB 33/11 KV SS |  | Kamrangirchar | 6764011.6984
|  |  |  | Jigatola | 5759280.9915
|  |  |  | Azimpur | 4494850.3101
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2253160.9458
|  | BB Avenue 33/11 KV SS |  | Narinda | 2219100.4411
|  |  |  | Ramna | 5333863.0848
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 17488482.734
|  |  |  | Dhanmondi | 1641717.2362
|  | Ispahani 33/11 KV SS |  | Moghbazar | 3135850.5852
|  |  |  | Kakrail | 3008477.8225
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 6485363.6844
|  |  |  | Total=> | 486356365.6761 | 324124000.781
NORTH ZONE TOTAL=>
|  | NOCS |  | 486356365.6761 |  | 200857461
|  | diff |  |  | -486356365.6761
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 5820000
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 5820000
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 28757.3823 | 17287227.3799
|  |  |  | Swamibagh | 6033703.8397
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 11224766.1579
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 10760436
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 10760436
| 4 | Maderteck 33/11KV S/S |  | Banosree | 4434483.0131 | 21302845.3224
|  |  |  | Bashabo | 1924894.1079
|  |  |  | Maniknagar | 262278.8244
|  |  |  | Mugdapara | 14681189.377
| 5 | Kazla 33/11KV S/S |  | Matual | 322767.8137 | 38779503.966
|  |  |  | Jurain | 8712842.3732
|  |  |  | Swamibagh | 2106094.7503
|  |  |  | Maniknagar | 2689305.0754
|  |  |  | Shyampur | 2822437.563
|  |  |  | Kazla | 22126056.3904
|  | Shyampur 132/11KV S/S |  | Shyampur | 33133931.0934 | 34324362.3037
|  |  |  | Fatullah. | 1190431.2102
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 26903818.2582
|  |  |  | Fatullah | 1118818.3855
|  |  |  | Shyampur | 25784999.8727
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 6346598.208 | 18886799.2653
|  |  |  | Jurain | 12540201.0572
| 8 | Postogola 33/11KV S/S |  | Jurain | 9005077.8551 | 18416754
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 9411676.1449
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 12146693.8295 | 13621900.0216
|  |  |  | Narayanganj (West) | 1488882.1784
|  |  |  | Shitalakhy | 1475206.1921
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 1073492.777 | 15451849.772
|  |  |  | Shitalakhy | 10240394.5294
|  |  |  | Narayanganj (West) | 3185961.362
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 952001.1037
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 906804.2112
| 11 |  |  | Narayanganj (West) | 16102970.8542 | 17009775.0654
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 14008025.4564 | 14008025.4564
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 14002293.9795 | 14002293.9795
|  |  |  | Matuail | 330706.0205
| 14 | Sarulia 33/11KV S/S |  | Demra | 16329917.6105 | 18896613.6271
|  |  |  | Matuail | 2566696.0166
|  | Demra 33/11KV S/S |  | Matuail | 7806228.2288 | 24495521.7374
| 15 |  |  | Demra | 2606394.5354
|  |  |  | Siddhirganj | 14082898.9732
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1338376.1519
| 16 |  |  | Narayanganj (East) | 5593278.1851 | 14339553.7443
|  |  |  | Narayanganj (West) | 8746275.5592
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 3996838.8098 | 17323324.0992
|  |  |  | Narayanganj (East) | 13326485.2894
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 5647012.7241 | 19735666.1936
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 256148.7049
|  |  |  | Fatullah | 4354452.574
|  |  |  | Matuail | 9478052.1906
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 2360592 | 2360592
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 531621.6224
|  |  |  | Maniknagar | 11989209.5602 | 11989209.5602
|  | IG Gate 33/11 kv |  | Swamibagh | 5789242.0614 | 18667776.5195
|  |  |  | Banglabazr | 5807029.0516
|  |  |  | Postogola | 7071505.4064
|  | Motijil 33/11kv |  | kamlapur | 7803960.782 | 8261000
|  |  |  | RAMNA | 457039.218
|  | Mitford 33/11kv |  | Banshal | 8617196.6445 | 9228020.647
|  |  |  | Lalbagh | 610824.0025
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 5575998.3855 | 13193403.2028
|  |  |  | Fatullah | 4195438.8734
|  |  |  | Matuail | 3421965.9439
|  | MI CEMENT |  | Shitalakhy | 10329120 | 10329120
|  | Dapa 33/11 kV |  | Fatullah | 11913420.9116 | 11913420.9116
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7798092.3106 | 16845408.1568
|  |  |  | Siddhirganj | 9047315.8462
|  | Amulia 33/11 KV SS |  | Mugdapara | 1309618.0026 | 7166975.8566
|  |  |  | Demra | 5857357.8539
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 12686520.7772
|  | P&T 33/11 KV SS |  | Motijeel | 2554926.3456
|  |  |  | RAMNA | 3609452.732
|  |  |  | Rajarbagh | 3231016.2733
|  | Kazla 132/33 KV SS |  | Kazla | 18904064.6024
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 6181771.2196
|  |  |  | Motijeel | 2798228.7804
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 26330286.63
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 3238008.4245
|  |  |  | Swamibagh | 1303637.2522
|  |  |  | Narinda | 223497.8838
|  |  |  | Total=> | 556072193.9407 | 435395392.1215
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 556072193.9407
| Diff zone&Nocs |  |  |  | -43472951.6156
|  |  |  | Diff= | 0

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 33326427.9121 | 34065933.7505 | 739505.8384 | 2.1708 | 34031890.1848 | 34043.5657
Kakrail | 26542949.8477 | 27053236.3422 | 510286.4945 | 1.8862 | 28375284.9016 | -1322048.5594
Moghbazar | 20914248.216 | 20829444.6511 | -84803.5649 | -0.40713 | 21329436.2056 | -499991.5545
Khilgaon | 16885238.3373 | 16549505.9304 | -335732.4069 | -2.0287 | 16918091.0673 | -368585.1369
Satmosjid | 23263785.2371 | 23310707.9778 | 46922.7407 | 0.20129 | 23421031.5433 | -110323.5656
Sherebanglanagar | 25060986.3423 | 24957769.3279 | -103217.0144 | -0.41357 | 25550090.7434 | -592321.4155
Dhanmondi | 24559325.7701 | 24286961.2779 | -272364.4922 | -1.1214 | 24788375.0068 | -501413.7289
Jhigatala | 28755390.4901 | 29006040.9982 | 250650.5081 | 0.86413 | 29481491.9766 | -475450.9784
Azimpur | 19894403.1357 | 20469030.3009 | 574627.1651 | 2.8073 | 20094312.838 | 374717.4629
Paribagh | 36106922.2961 | 35761176.6239 | -345745.6722 | -0.96682 | 36086512.9374 | -325336.3136
Shyamoli | 18256801.2634 | 18862155.4031 | 605354.1397 | 3.2094 | 19659362.7576 | -797207.3544
Adabor | 33991693.0318 | 34087257.547 | 95564.5152 | 0.28035 | 33945911.5689 | 141345.9781
Lalbagh | 35248383.1173 | 37849772.8377 | 2601389.7204 | 6.8729 | 32545410.1246 | 5304362.7131
Kamrangirchar | 40610208.52 | 43539351.4546 | 2929142.9347 | 6.7276 | 38848556.6907 | 4690794.7639
Ramna | 28248495.4309 | 29668920.4409 | 1420425.01 | 4.7876 | 29132056.3783 | 536864.0626
Rajarbagh | 19358621.1692 | 18314637.9743 | -1043983.1949 | -5.7003 | 19542983.0087 | -1228345.0344
Bashabo | 14802303.8161 | 14965275.1098 | 162971.2938 | 1.089 | 15301078.259 | -335803.1492
Bonoseeri | 26067833.1015 | 25695577.7378 | -372255.3636 | -1.4487 | 26579332.7573 | -883755.0195
Motijheel | 23157371.0896 | 22692835.4241 | -464535.6655 | -2.0471 | 22930447.2198 | -237611.7957
Mughdapara | 19531394.45 | 19981049.6399 | 449655.1899 | 2.2504 | 20216338.7843 | -235289.1444
Banglabazar | 17151582.8188 | 17978655.3258 | 827072.507 | 4.6003 | 16797076.4051 | 1181578.9207
Bongshal | 20320381.2069 | 20428168.2532 | 107787.0464 | 0.52764 | 18936614.1209 | 1491554.1323
Narinda | 14687870.9921 | 15412155.6155 | 724284.6234 | 4.6994 | 15837103.8048 | -424948.1893
Swamibagh | 15102409.2817 | 15232677.9036 | 130268.6219 | 0.85519 | 15168311.6806 | 64366.223
Kazla | 37908086.6755 | 41030120.9927 | 3122034.3173 | 7.6091 | 38787299.8942 | 2242821.0986
Maniknagar | 20926873.0633 | 21380256.2125 | 453383.1492 | 2.1206 | 21298139.082 | 82117.1305
Shyampur | 70614491.3479 | 73920113.8277 | 3305622.4798 | 4.4719 | 65449426.7658 | 8470687.0618
Matuail | 23789745.4001 | 23926416.2142 | 136670.8141 | 0.57121 | 24044863.4499 | -118447.2358
Postogola | 16221258.1373 | 16483181.5514 | 261923.4141 | 1.589 | 16101783.0766 | 381398.4748
Jurain | 29718071.1615 | 30258121.2855 | 540050.124 | 1.7848 | 30052481.21 | 205640.0755
Narayangonj-West | 30810293.9579 | 33520928.7636 | 2710634.8057 | 8.0864 | 30519764.2002 | 3001164.5634
Narayangonj-East | 31744596.4334 | 33438361.2862 | 1693764.8528 | 5.0653 | 31800817.8855 | 1637543.4007
Damra | 24103097.7168 | 24793669.9998 | 690572.283 | 2.7853 | 24683428.3053 | 110241.6946
Siddhirgonj | 51252886.2733 | 51140534.2553 | -112352.018 | -0.21969 | 51179003.4461 | -38469.1908
Fatulla | 33019604.8442 | 34919255.7842 | 1899650.94 | 5.4401 | 33464369.2197 | 1454886.5645
Shitalakha | 63181001.7532 | 66619301.5955 | 3438299.8423 | 5.1611 | 65632174.0045 | 987127.591
TOTAL=> | 1015135033.6381 | 1042428559.6168 | 27293525.9787 | 2.6183 | 1018530651.5052 | 23897908.1116

## Sheet2 (hidden)
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.09.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2234.48 | 2259.85 | 25.37 | 720000 | 18266400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2203.57 | 2228.85 | 25.28 | 720000 | 18201600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1933.1 | 1967.67 | 34.57 | 720000 | 24890400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1802.6 | 1838.52 | 35.92 | 480000 | 17241600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2082.67 | 2113.89 | 31.22 | 240000 | 0 | 7492800 | 7495214.4889 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2383.66 | 2416.09 | 32.43 | 240000 | 0 | 7783200 | 7785708.0678 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1460.93 | 1476.87 | 15.94 | 240000 | 0 | 3825600 | 3826832.766 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 826.76 | 848.87 | 22.11 | 240000 | 0 | 5306400 | 5308109.9408 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1843.63 | 1860.74 | 17.11 | 240000 | 0 | 4106400 | 4107723.2513 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1192.37 | 1210.37 | 18 | 240000 | 0 | 4320000 | 4321392.082 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 405.5 | 420.58 | 15.08 | 240000 | 0 | 3619200 | 3620366.2554 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2087.7 | 2116.15 | 28.45 | 240000 | 0 | 6828000 | 6830200.263 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1612.37 | 1634.5 | 22.13 | 240000 | 0 | 5311200 | 5312911.4875 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 710.95 | 725.99 | 15.04 | 240000 | 0 | 3609600 | 3610763.1619 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1978.52 | 2016.45 | 37.93 | 240000 | 0 | 9103200 | 9106133.4262 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1809.7 | 1843.76 | 34.06 | 240000 | 0 | 8174400 | 8177034.1286 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 151.65 | 158.2 | 6.55 | 240000 | 0 | 1572000 | 1572506.5632 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1411.09 | 1442.33 | 31.24 | 240000 | 0 | 7497600 | 7500016.0357 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.09.2023 | Reading at 00.00hr 01.09.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2234.48 | 2259.85 | 25.37 | 720000 | 18266400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2203.57 | 2228.85 | 25.28 | 720000 | 18201600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1933.1 | 1967.67 | 34.57 | 720000 | 24890400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1802.6 | 1838.52 | 35.92 | 480000 | 17241600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2082.67 | 2113.89 | 31.22 | 240000 | 0 | 7492800 | 7495214.4889 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2383.66 | 2416.09 | 32.43 | 240000 | 0 | 7783200 | 7785708.0678 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1460.93 | 1476.87 | 15.94 | 240000 | 0 | 3825600 | 3826832.766 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 826.76 | 848.87 | 22.11 | 240000 | 0 | 5306400 | 5308109.9408 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1843.63 | 1860.74 | 17.11 | 240000 | 0 | 4106400 | 4107723.2513 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1192.37 | 1210.37 | 18 | 240000 | 0 | 4320000 | 4321392.082 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 405.5 | 420.58 | 15.08 | 240000 | 0 | 3619200 | 3620366.2554 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2087.7 | 2116.15 | 28.45 | 240000 | 0 | 6828000 | 6830200.263 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1612.37 | 1634.5 | 22.13 | 240000 | 0 | 5311200 | 5312911.4875 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 710.95 | 725.99 | 15.04 | 240000 | 0 | 3609600 | 3610763.1619 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1978.52 | 2016.45 | 37.93 | 240000 | 0 | 9103200 | 9106133.4262 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1809.7 | 1843.76 | 34.06 | 240000 | 0 | 8174400 | 8177034.1286 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 151.65 | 158.2 | 6.55 | 240000 | 0 | 1572000 | 1572506.5632 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1411.09 | 1442.33 | 31.24 | 240000 | 0 | 7497600 | 7500016.0357 | 0 | Dhanmondi 132/33/11KV S/S