## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month November-2023 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 766 | 1 | 960000 | 2229.915 | 2234.461 | 4.546 |  | 4364160 | 1950.526 | 1951.095 | 0.569 |  | 546240 | 4010880 | -178560 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 667.19 | 667.558 | 0.368 | 353280 |  | 378.836 | 379.591 | 0.755 | 724800 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 378.796 | 402.926 | 24.13 |  | 23164800 | 169.543 | 181.302 | 11.759 |  | 11288640 | 23164800 | 11288640 | 0.9 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 159.248 | 165.737 | 6.489 |  | 6229440 | 53.833 | 55.775 | 1.942 |  | 1864320 | 6229440 | 1864320 | 0.96 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | HASNABAD –FATULLAH (New) |  | 132 | Exp | 5972 3848 | 1 | 960000 | 0 | 6.982 | 6.982 |  | 6702720 | 0 | 6.834 | 6.834 |  | 6560640 | 6470400 | 6424320 |  |  | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0.242 | 0.242 | 232320 |  | 0 | 0.142 | 0.142 | 136320 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 585600 | 40461120 |  |  | Total=> | 861120 | 20259840 | 39875520 | 19398720 | 0.9 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 8993 624 | 1 | 960000 | 4864.387 | 4885.436 | 21.049 |  | 20207040 | 2401.046 | 2405.774 | 4.728 |  | 4538880 | 20207040 | 4538880 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 11.083 | 11.083 | 0 | 0 |  | 7.816 | 7.816 | 0 | 0 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 20207040 |  |  | Total=> | 0 | 4538880 | 20207040 | 4538880 | 0.98 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 8993 518 | 1 | 960000 | 1173.431 | 1188.499 | 15.068 |  | 14465280 | 781.529 | 786.614 | 5.085 |  | 4881600 | 14465280 | 4881600 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 70.101 | 70.101 | 0 | 0 |  | 141.182 | 141.182 | 0 | 0 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 350.838 | 366.009 | 15.171 |  | 14564160 | 136.132 | 141.385 | 5.253 |  | 5042880 | 14564160 | 5042880 | 0.94 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.408 | 4.408 | 0 | 0 |  | 30.499 | 30.499 | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 0 | 29029440 |  |  | Total=> | 0 | 9924480 | 29029440 | 9924480 | 0.95
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 2948.743 | 2986.08 | 37.337 |  | 17921760 | 1197.064 | 1210.475 | 13.411 |  | 6437280 | 17921760 | 6437280 | 0.94 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8541.707 | 8576.821 | 35.114 |  | 16854720 | 4996.746 | 5014.301 | 17.555 |  | 8426400 | 16854720 | 8426400 | 0.89 | 0.005 | 84273.6
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8494.043 | 8529.331 | 35.288 |  | 16938240 | 4956.296 | 4973.939 | 17.643 |  | 8468640 | 16938240 | 8468640 | 0.89 | 0.005 | 84691.2
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 350.233 | 375.942 | 25.709 |  | 12340320 | 66.568 | 71.576 | 5.008 |  | 2403840 | 12340320 | 2403840 | 0.98 | 0 | 0
[10 empty] | Total=> | 0 | 64055040 |  |  | Total=> | 0 | 25736160 | 64055040 | 25736160 | 0.93
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 8993 683 | 1 | 960000 | 8449.443 | 8481.316 | 31.873 |  | 30598080 | 4698.185 | 4712.021 | 13.836 |  | 13282560 | 30598080 | 13282560 | 0.92 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 8993 682 | 1 | 960000 | 8439.078 | 8470.688 | 31.61 |  | 30345600 | 4692.679 | 4706.454 | 13.775 |  | 13224000 | 30345600 | 13224000 | 0.92 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 8993 681 | 1 | 1440000 | 2714.49 | 2732.15 | 17.66 |  | 25430400 | 1387.291 | 1389.481 | 2.19 |  | 3153600 | 25430400 | 3153600 | 0.99 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 9.184 | 9.184 | 0 | 0 |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 8993 680 | 1 | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 22.279 | 22.279 | 0 | 0 |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 8993 555 | 1 | 1440000 | 2867.349 | 2894.06 | 26.711 |  | 38463840 | 1333.673 | 1345.175 | 11.502 |  | 16562880 | 38463840 | 16562880 | 0.92 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 771.699 | 771.699 | 0 | 0 |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 0 | 124837920 |  |  | Total=> | 0 | 46223040 | 124837920 | 46223040 | 0.94 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993 631 | 1 | 960000 | 5922.51 | 5948.831 | 26.321 |  | 25268160 | 3017.843 | 3028.686 | 10.843 |  | 10409280 | 25268160 | 10409280 | 0.92 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993 659 | 1 | 960000 | 5042.863 | 5064.126 | 21.263 |  | 20412480 | 2558.736 | 2567.33 | 8.594 |  | 8250240 | 20412480 | 8250240 | 0.93 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4438.485 | 4448.367 | 9.882 |  | 9486720 | 1773.32 | 1774.761 | 1.441 |  | 1383360 | 9486720 | 1383360 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.561 | 1.561 | 0 | 0 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993 660 | 1 | 960000 | 4121.721 | 4130.91 | 9.189 |  | 8821440 | 1637.224 | 1638.966 | 1.742 |  | 1672320 | 8821440 | 1672320 | 0.98 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.33 | 1.33 | 0 | 0 |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 5014 6667 | 1 | 960000 | 1867.274 | 1886.879 | 19.605 |  | 18820800 | 686.153 | 693.714 | 7.561 |  | 7258560 | 18820800 | 7258560 | 0.93 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 5014 6668 | AMR | 960000 | 1661.144 | 1680.527 | 19.383 |  | 18607680 | 711.371 | 718.856 | 7.485 |  | 7185600 | 18607680 | 7185600 | 0.93 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 4262 7810 | 1 | 960000 | 201.909 | 214.859 | 12.95 |  | 12432000 | 3.49 | 3.91 | 0.42 |  | 403200 | 12432000 | 403200 | 1 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 67.85 | 70.933 | 3.083 | 2959680 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 4262 7812 | 1 | 960000 | 203.94 | 217.013 | 13.073 |  | 12550080 | 2.463 | 2.775 | 0.312 |  | 299520 | 12550080 | 299520 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 72.042 | 75.351 | 3.309 | 3176640
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 0 | 126399360 |  |  | Total=> | 6136320 | 36862080 | 126399360 | 30725760 | 0.97 |  | 0
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3318.886 | 3356.292 | 37.406 |  | 71819520 | 1665.595 | 1679.108 | 13.513 |  | 25944960 | 71819520 | 25944960 | 0.94 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3311.084 | 3347.682 | 36.598 |  | 70268160 | 1662.662 | 1675.926 | 13.264 |  | 25466880 | 70268160 | 25466880 | 0.94 | 0 | 0
[10 empty] | Total=> |  | 142087680 |  |  | Total=> | 0 | 51411840 | 142087680 | 51411840 | 0.94
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1553.392 | 1593.217 | 39.825 |  | 76464000 | 755.156 | 772.967 | 17.811 |  | 34197120 | 76464000 | 34197120 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
|  |  | Calculated Unit for 230/132kV T-1 due to R-phase PT Missing | [8 empty] | 161432 |  |  |  |  | 72197
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1643.73 | 1683.807 | 40.077 |  | 76947840 | 795.209 | 813.34 | 18.131 |  | 34811520 | 76947840 | 34811520 | 0.94 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 153573272 |  |  | Total=> | 0 | 69080837 | 153573272 | 69080837 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 991.183 | 1025.378 | 34.195 |  | 49240800 | 209.048 | 216.288 | 7.24 |  | 10425600 | 49240800 | 10425600 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.021 | 0 | 0 |  | 0.894 | 0.894 | 0 | 0
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 718.358 | 752.493 | 34.135 |  | 49154400 | 304.05 | 320.715 | 16.665 |  | 23997600 | 49154400 | 23996160 | 0.9 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.837 | 0.838 | 0.001 | 1440 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 0 | 98395200 |  |  | Total=> | 1440 | 34423200 | 98395200 | 34421760 | 0.94
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 296.146 | 306.632 | 10.486 |  | 10066560 | 75.817 | 78.091 | 2.274 |  | 2183040 | 10066560 | 2183040 | 0.98 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 220.999 | 237.944 | 16.945 |  | 16267200 | 50.718 | 54.336 | 3.618 |  | 3473280 | 16267200 | 3473280 | 0.98 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 33.497 | 33.859 | 0.362 |  | 347520 | 16.216 | 16.247 | 0.031 |  | 29760 | 347520 | 29760 | 1
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 66.461 | 105.155 | 38.694 | 37146240 |  | 57.754 | 88.645 | 30.891 | 29655360
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[10 empty] | Total=> | 37146240 | 26681280 |  |  | Total=> | 29655360 | 5686080 | -10464960 | -23969280 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 37731840 | 825727352 |  |  |  | 36654240 | 304146437
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 787995512 |  |  |  |  | 267492197 | 787995512 | 267492197 | 0.95 |  | 168964.8 |  | 0.94693
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 787995512 |  | 267492197 |  | 0.95 | 168964.8
[8 empty] | PDB Unit |  | 788164476.8 |  | KWH
[8 empty] | PGCB Unit |  | 787995512 |  | KWH
33 KV LEVEL | [10 empty] | Month November-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Exp | 8993 841 | 1 | 18000 | 29344.892 | 29344.892
4 | Shah Cement |  | 33 | Exp | 8993 841 | 1 | 36000 | 39516.99 | 39602.522 | 85.532 |  | 3079152 | 10433.048 | 10453.354 | 20.306 |  | 731016 | 3079152 | 731016 | 0.97296 | 0 | 0 | 9656
| Shah Cement (new) |  | 33 | Exp | 5050 1238 | 1 | 36000 | 0 | 17.275 | 17.275 |  | 621900 | 0 | 3.716 | 3.716 |  | 133776 | 621900 | 133776 | 0.97764 | 0 | 0 | 1950
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 3701052 |  |  | Total=> | 0 | 864792 | 3701052 | 864792 | 0.97377 |  | 0 | 11606
6 | Jigatala (JP garden) | Kallyanpur
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.405 | 1.459 | 0.054 |  | 9720 | 0.104 | 0.104 | 0 |  | 0 | 9720 | 0 | 0 | 0 | 0 | 6
7 | Shere Bangla |  | 33 | Exp | 8993 833 | 1 | 180000 | 317.734 | 317.735 | 0.001 |  | 180 | 244.376 | 244.376 | 0 |  | 0 | 180 | 0 | 0 | 0 | 0 | 0
| Shere Bangla (new ) |  | 33 | Exp | 59723 485 | 1 | 180000 | 0 | 0.107 | 0.107 |  | 19260 | 0 | 0.003 | 0.003 |  | 540 | 19260 | 540 | 0.99961 | 0 | 0 | 11
8 | Satmosjid-1 |  | 33 | Exp | 8993 638E | 1 | 180000 | 4216.182 | 4218.892 | 2.71 |  | 487800 | 2258.095 | 2258.434 | 0.339 |  | 61020 | 487800 | 61020 | 0.99227 | 0 | 0 | 277
| Satmosjid-1 (new ) |  | 33 | Exp | 59723 483 | 1 | 180000 | 0 | 3.32 | 3.32 |  | 597600 | 0 | 0.44 | 0.44 |  | 79200 | 597600 | 79200 | 0.99133 | 0 | 0 | 340
9 | Satmosjid -2 |  | 33 | Exp | 8993 669E | 1 | 180000 | 5941.853 | 5957.121 | 15.268 |  | 2748240 | 2692.955 | 2699.191 | 6.236 |  | 1122480 | 2748240 | 1122480 | 0.92576 | 0 | 0 | 1563
| Satmosjid-2 (new ) |  | 33 | Exp | 59723 851 | 1 | 180000 | 0 | 12.822 | 12.822 |  | 2307960 | 0 | 4.877 | 4.877 |  | 877860 | 2307960 | 877860 | 0.93467 | 0 | 0 | 1313
10 | Kallayanpur T3 |  | 33 | Exp | 8993 831 | 1 | 180000 | 6605.491 | 6618.376 | 12.885 |  | 2319300 | 3218.73 | 3224.358 | 5.628 |  | 1013040 | 2319300 | 1013040 | 0.9164 | 0 | 0 | 1319
| Kallayanpur T3 (New) |  | 33 | Exp | 59723 486 | 1 | 180000 | 0 | 19.616 | 19.616 |  | 3530880 | 0 | 8.668 | 8.668 |  | 1560240 | 3530880 | 1560240 | 0.91468 | 0 | 0 | 2008
11 | Kallayanpur T4 |  | 33 | Exp | 8993 839 | 1 | 180000 | 8813.321 | 8827.525 | 14.204 |  | 2556720 | 4100.067 | 4106.273 | 6.206 |  | 1117080 | 2556720 | 1117080 | 0.91635 | 0 | 0 | 1454
| Kallayanpur T4 (New) |  | 33 | Exp | 59723 875 | 1 | 180000 | 0 | 18.01 | 18.01 |  | 3241800 | 0 | 7.905 | 7.905 |  | 1422900 | 3241800 | 1422900 | 0.91568 | 0 | 0 | 1844
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 182.172 | 184.069 | 1.897 |  | 341460 | 51.275 | 52.275 | 1 |  | 180000 | 341460 | 180000 | 0.88461 | 0.01 |  | 193 | T-5 has been used by DESCO
| Exp to Desco at 11 KV |  | 33 | Exp |  | 1 |  |  |  |  | 3303780 |  |  |  |  | 1282480 |  | -3303780 | -1282480 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Exp | 8993 836E | 1 | 180000 | 5452.879 | 5453.99 | 1.111 |  | 199980 | 2686.623 | 2687.213 | 0.59 |  | 106200 | 199980 | 106200 | 0.88319 | 0.01 | 1999.8 | 114
| Lalmatia (New) |  | 33 | Exp | 59723 850 | 1 | 180000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  | 0
[10 empty] | Total=> | 3303780 | 18360900 |  |  | Total=> | 1282480 | 7540560 | 15057120 | 6258080 | 0.92342 |  | 1999.8 | 10442
SATMOSJID 132/33KV SS
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3275.612 | 3308.169 | 32.557 |  | 24417750 | 1630.967 | 1646.116 | 15.149 |  | 11361750 | 24417750 | 11361750 | 0.90665 | 0 | 0 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 2917.773 | 2950.394 | 32.621 |  | 24465750 | 1428 | 1443.211 | 15.211 |  | 11408250 | 24465750 | 11408250 | 0.90631 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 48883500 |  |  | Total=> | 0 | 22770000 | 48883500 | 22770000 | 0.90648 | 0 | 0 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1 | 180000 | 1983.503 | 1999.239 | 15.736 |  | 2832480 | 658.662 | 660.982 | 2.32 |  | 417600 | 2832480 | 417600 | 0.98931 | 0 | 0 | 3465.1
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1 | 180000 | 708.985 | 720.775 | 11.79 |  | 2122200 | 50.302 | 50.696 | 0.394 |  | 70920 | 2122200 | 70920 | 0.99944 | 0 | 0 | 2596.19
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1 | 180000 | 108.018 | 110.267 | 2.249 |  | 404820 | 4.16 | 4.16 | 0 |  | 0 | 404820 | 0 | 0 | 0 | 0 | 495.24
19 | Monipuripara-1 |  |  |  |  | 1 | 180000 | 1168.374 | 1182.108 | 13.734 |  | 2472120 | 482.334 | 487.279 | 4.945 |  | 890100 | 2472120 | 890100 | 0.94087 | 0 | 0 | 3024.26
20 | Monipuripara-2 |  |  |  |  | 1 | 180000 | 838.951 | 869.027 | 30.076 |  | 5413680 | 299.53 | 309.804 | 10.274 |  | 1849320 | 5413680 | 1849320 | 0.94631 | 0 | 0 | 6622.81
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 13245300 |  |  | Total=> | 0 | 3227940 | 13245300 | 3227940 | 0.97156 |  | 0 | 16203.6
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 420573.6 | 424443.4 | 3869.8 |  | 3966.545 | 269629.8 | 272257.6 | 2627.8 |  | 2693.495 | 3966.545 | 2693.495 | 0.82729 | 0.06 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 388432.8 | 392725.7 | 4292.9 |  | 4400.2225 | 136479.6 | 137792.8 | 1313.2 |  | 1346.03 | 4400.2225 | 1346.03 | 0.95626 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 8366.7675 |  |  | Total=> | 0 | 4039.525 | 8366.7675 | 4039.525 | 0.90053 |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 349.667 | 351.425 | 1.758 |  | 4324.68 | 223.421 | 255.48 | 32.059 |  | 78865.14 | 4324.68 | 78865.14 | 0.054754 | 0 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 117.946 | 124.447 | 6.501 |  | 15992.46 | 63.748 | 67.846 | 4.098 |  | 10081.08 | 15992.46 | 10081.08 | 0.84595 | 0.04 | 0 | 0
[10 empty] | Total=> | 0 | 20317.14 |  |  | Total=> | 0 | 88946.22 | 20317.14 | 88946.22 | 0.22268 |  | 0 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 3303780 | 84219435.9075 |  |  |  | 1282480 | 34496277.745 | [5 empty] | 38251.6 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 80915655.9075 |  |  |  |  | 33213797.745 | 80915655.9075 | 33213797.745 | 0.9251 |  | 1999.8 |  | Total PFC Unit
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 615820 |  |  | 81531475.9075 |  |  | 84219435.9075 | 34496277.745
33 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 80915655.9075 |  | 33213797.745 |  | 0.9251 | 1999.8
[8 empty] | PDB Unit |  | 80917655.7075 |  | KWH
[8 empty] | PGCB Unit |  | 80915655.9075 |  | KWH
11 KV LEVEL | [10 empty] | Month November-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [9 empty] | Total=> |  | 0 |  |  |  |  | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 1502 6 | 1 | 40000 | 9219.86 | 9229.09 | 9.23 |  | 369200 | 3474.29 | 3477.86 | 3.57 |  | 142800 | 378430 | 146370 | 0.93267 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 1502 7 | 1 | 40000 | 3875.73 | 3878 | 2.27 |  | 90800 | 1263.65 | 1263.75 | 0.1 |  | 4000 | 93070 | 4100 | 0.99903 | 1 |  | 4000 | RMU Feeder KVARH Back Calculation as per KWH Percentage
3a | PD Betar |  | 11 | Imp | 2612 100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612 100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 1502 5 | 1 | 40000 | 3980.52 | 3984.04 | 3.52 |  | 140800 | 1890.52 | 1894.36 | 3.84 |  | 153600 | 144320 | 157440 | 0.67572 | 1.3319
5 | BICC - U/G |  | 11 | Exp | 1502 4 | 1 | 40000 | 1038.9 | 1038.9 | 0 |  | 0 | 297.34 | 297.34 | 0 |  | 0 | 0 | 0 | 0 | 1
6 | NEC |  | 11 | Exp | 1502 3 | 1 | 40000 | 431.67 | 431.67 | 0 |  | 0 | 56.31 | 56.31 | 0 |  | 0 | 0 | 0 | 0 | 1
7 | Manikmia Avenue |  | 11 | Exp | 7602 6327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 600800 |  |  |  | 0 | 300400 | 615820 | 307910 | 0.89443
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 600800 |  |  |  | 0 | 300400
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 600800 |  |  |  |  | 300400
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 615820 |  |  |  |  | 307910 | 615820 | 307910 | 0.89443 |  | 0 |  | 0.89443
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 615820 |  | 307910 |  | 0.89443 | 0
[8 empty] | PDB Unit |  | 615820 |  | KWH
[8 empty] | PGCB Unit |  | 615820 |  | KWH

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month November-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 787995512 | 8.1335 | 6409161497 |  |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 787995512 | 787995512 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 6409161497 | 6409161497 | 0
2a | 33kv | 80915655.9075 | 8.22 | 665126692 |  |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 80915655.9075 | 80915655.9075 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 665126692 | 665126692 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 615820 | 8.22 | 5062040 |  |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 615820 | 615820 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 5062040 | 5062040 | 0
2c | Bus Loss Units (33kv) | 38250.81 | 8.22 | 314422 |  |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 38250.81 | 38250.81 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 314422 | 314422 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 81569726.7175 |  | 670503154 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 81569726.7175 | 81569726.7175 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 670503154 | 670503154 | 0
4 | TOTAL 132kv & 33kv (1+3) | 869565238.7175 |  | 7079664651 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 869565238.7175 | 869565238.7175 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 7079664651 | 7079664651 | 0
5 | 132KV P.F.C | 168964.8 | 8.1335 | 1374275 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 168964.8 | 168964.8 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 1374275 | 1374275 | 0
6 | 33KV P.F.C | 0 | 8.22 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 168964.8 |  | 1374275 |  |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 168964.8 | 168964.8 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 1374275 | 1374275 | 0
8 | TOTAL Billed Amount => (4+7) | 869734203.5175 |  | 7081038926 |  | 7081038926 |  | 10 | সর্বমোট (৬+৯) | 869734203.5175 | 869734203.5175 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 7081038926 | 7081038926 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 424862336 | Source Tax | [10 empty] | 11 | উৎস কর (মোট বিলের উপর ৬%) | 424862336 | 424862336 | -
10 | NET BILL TOTAL => (8-9) |  |  | 6656176590 |  | 7755732645 | , কমা চেইঞ্জার | [8 empty] | 12 | কর পরবর্তী মোট পরিশোধ যোগ্য বিল (১০-১১) | 6656176590 | 6656176590 | -
11*** | 24th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  |  | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 6656176590
"In word: Taka Seven Hundred Seventy Five Crore Fifty Seven Lac Thirty Two Thousand Six Hundred and Forty Five Only"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | 31683869.1762 | 2021-10-01
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid | 30306309.6468 | 2021-11-01
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid | 28928750.1174 | 2021-12-01
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid | 27551190.588 | 2022-01-01
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid | 26173631.0586 | 2022-02-01
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid | 24796071.5292 | 2022-03-01
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid | 23418511.9998 | 2022-04-01
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid | 22040952.4704 | 2022-05-01
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid | 20663392.941 | 2022-06-01
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid | 19285833.4116 | 2022-07-01
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid | 17908273.8822 | 2022-08-01
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid | 16530714.3528 | 2022-09-01
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid | 15153154.8234 | 2022-10-01
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid | 13775595.294 | 2022-11-01
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid | 12398035.7646 | 2022-12-01
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid | 11020476.2352 | 2023-01-01
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid | 9642916.7058 | 2023-02-01
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid | 8265357.1764 | 2023-03-01
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid | 6887797.647 | 2023-04-01 |  | 366430834.8204
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid | 5510238.1176 | 2023-05-01 |  | 20971130269.73
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid | 4132678.5882 | 2023-06-01
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Paid | 2755119.0588 | 2023-07-01
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94 | Paid | 1377559.5294 | 2023-08-01 |  | 20604699434.9096
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0 | Certified For Payment | 380206430.1144
| Total | 3306142870.56
20984905865.024
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month November-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [9 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[12 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month November-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 787995512 | 0.2886 | 227415504.7632 |  | 293050922 | , কমা চেইঞ্জার | 1 | 132 †Kwf (GbvwR©) | 787995512 | 787995512 | 787995512 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 6409161497 | 227415504.7632 | 227415504.7632 | 0
2a | 33kv Level | 80915655.9075 | 0.2944 | 23821569.0992 |  |  |  | 2 | 33 †Kwf (GbvwR©) | 80915655.9075 | 80915655.9075 | 80915655.9075 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 665126692 | 23821569.0992 | 23821569.0992 | 0 |  | 33KV Amount (2+3+4) => | 24014127.8856
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 615820 | 0.2944 | 181297.408 |  |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 615820 | 615820 | 615820 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 5062040 | 181297.408 | 181297.408 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 38250.81 | 0.2944 | 11261.3785 |  |  |  | 4 | 33 ‡Kwf evm jm | 38250.81 | 38250.81 | 38250.81 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 314422 | 11261.3785 | 11261.3785 | 0 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 81569726.7175 | 0.2944 | 24014127.8856 |  |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 81569726.7175 | 81569726.7175 | 81569726.7175 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 670503154 | 24014127.8856 | 24014127.8856 | 0
4 | TOTAL=> (1+3) | 869565238.7175 |  | 251429632.6488 |  |  |  | 6 | me©‡gvU (1+5) | 869565238.7175 | 869565238.7175 | 869565238.7175 | 0 |  |  | 6 | me©‡gvU (1+5) | 7079664651 | 251429632.6488 | 251429632.6488 | 0
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000 | [12 empty] | 298330160 | , কমা চেইঞ্জার
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 13th Installment ) |  |  | 25993419.79 |  |  |  | ‡gvU (GbvwR©) |  | 869526987.9075 | 869526987.9075 | 869526987.9075 | 0 |  |  | ‡gvU (GbvwR©) |  | 7079350229 | 251418371.2704 | 24014127.8856 | 227404243.3847
7 | Grand TOTAL=> (4-5+6) |  |  | 275923052.4388
| CERTIFIED UNITS |  |  | 869565238.7175 |  | 317544342 | , কমা চেইঞ্জার
| CERTIFIED TAKA |  |  | 251429632.6488
| CERTIFIED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 13th Installment of Wheeling Charge Due) |  |  | 275923052.4388
evsjv
In word: Taka Thirty One Crore Seventy Five Lac Forty Four Thousand Three Hundred and Forty Two
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Paid
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Paid
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06 | Paid
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27 | Paid
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48 | Paid
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69 | Certified For Payment
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check
[6 empty] | Month November-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 127114717.14 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 126751632 | Fatullah Grid | 37303200 | 363085.14 | 0.2856%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 4364160 |  |  |  | Shyampur Grid | 89448432
|  |  | 132 | Import |  | 353280 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 23164800 | 29394240 | Postogola 132/33 KV Grid | 29394240 | Postogola Grid | 29394240 | 0 | 0%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 6229440
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 6702720 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 232320 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 585600 | 40461120
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 20207040 | 88927680 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 88119020.2 | Ullon Grid | 23332608 | 808659.8 | 0.9093%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 54051385
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 20207040 |  |  |  | DU Grid | 10735027.2
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 14465280 | 127424640 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 124655916 | Lalbagh Grid | 48775116 | 2768724 | 2.173%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 27590400
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 14564160 |  |  |  | Jigatola Grid | 48290400
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 29029440
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 17921760 | 51714720 | Sitalakhya 132/33 KV Grid | 51603503.841 | Sitalakhya Grid | 51603503.841 | 111216.159 | 0.2151%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 16854720
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 16938240
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 12340320 | 12340320 | Sitalakhya NOCS | 12340320 | Sitalakhya NOCS | 12340320 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 64055040
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 30598080 | 60943680 | Siddirganj 132/33 KV Grid | 60943680 | Siddirganj Grid | 60943680 | 0 | 0%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 30345600
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 25430400 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 38463840 | 38463840 | Matuail 132/33 KV Grid | 38369025.636 | Matuail Grid | 38369025.636 | 94814.364 | 0.2465%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 124837920
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 25268160 | 45680640 | Moghbazar 132/33 KV Grid | 45384134.4 | Moghbazar Gird | 45384134.4 | 296505.6 | 0.6491%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 20412480
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 9486720 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 8821440
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 18820800 | 37428480 | Madartek 132/33 KV Grid | 37428480 | Madartek Grid | 37428480 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 18607680
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 12432000 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 12550080
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 126399360
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 71819520 | 142087680 | Maniknagar 132/33 KV Grid | 140566668.48 | Kazla Grid | 50457283.2 | 1521011.52 | 1.07%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 70268160 |  |  |  | Motijheel Grid | 18943200
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 142087680 |  |  |  | Narinda Grid | 31210865.28
[11 empty] | Bangabhaban Grid | 4428000
[11 empty] | Maniknagar Grid | 34311000
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 76464000 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid |  | Metro Rail | 1216320
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 76947840
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 153573272
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 49240800 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 49154400
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 98395200
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 10066560 | 26333760 | Charsyedpur 132/33 KV Grid | 26280000 | Charsyedpur Grid | 26280000 | 53760 | 0.2041%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 16267200
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 347520 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 37146240 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 37146240 | 26681280 | 787854397.14 |  | 781836620.557 |  | 781836620.557 | 6017776.583 | 0.7638%
[9 empty] | 33 KV Transmission Loss |  | 70575758.7675 | 80473811.7623 | -9898052.9948 | -14.02%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 615820 | 617050 | -1230 | -0.1997%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 859045975.9075 | 862927482.3193 | -3881506.4118 | -0.4518%
[9 empty] | From Summary Sheet |  |  |  | 4539416.3441 | 0.522%
[9 empty] | Mismatch in KWH |  |  |  | -8420922.7559
| 33 KV LEVEL |  |  |  |  | Month November-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 3079152 | 3079152 | Sitalakhya NOCS | 3079152 | Sitalakhya NOCS | 3079152 | 0 | 0%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 3701052
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 9720 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 9720 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 9720
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 180
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 487800 | 52319520 | Shatmasjid 132/33 KV Grid | 55741651.0844 | Asadgate SS | 11909161.0844 | -3422131.0844 | -6.541%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 2748240 |  |  |  | Lalmatia SS | 10503000
[11 empty] | Japan Garden SS | 12168000
[11 empty] | Jigatola Old SS | 1622400
[11 empty] | Shatmasjid SS | 16847460
[11 empty] | BGB SS | 2691630
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 2319300 | 1913700 | Adabor NOCS | 8788678 | Adabor NOCS | 8788678 | -6874978 | -359.3%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 2556720
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 341460
| Export to Desco at 11 KV |  |  |  |  | 3303780 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 199980 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 3303780 | 18360900
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 24417750 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 24465750
AGARGAON 132/33KV SS | [5 empty] | 0 | 48883500
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 2832480 | 5359500 | Sherebanglanagar 33/11 KV SS | 4960741.29 | Sherebanglanagar SS | 4960741.29 | 398758.71 | 7.44%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 2122200
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 404820
19 | Monipuripara-1 |  |  |  |  | 0 | 2472120 | 7885800 | Monipuripara 33/11 KV SS | 7895447.07 | Monipuripara SS | 7895447.07 | -9647.07 | -0.1223%
20 | Monipuripara-2 |  |  |  |  | 0 | 5413680
| Maniknagar 230/132 kv |  |  |  |  | 0 | 13245300
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 3966.545 | 8366.7675 | Maniknagar 33/11 KV SS | 8142.3179 | Maniknagar 33/11 KV SS | 8142.3179 | 224.4496 | 2.683%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 4400.2225
Shyampur 230/132 kv | [5 empty] | 0 | 8366.7675
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 4324.68 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 15992.46
[6 empty] | 0 | 20317.14
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 3303780 | 84219435.9075 | 70575758.7675 |  | 80473811.7623 |  | 80473811.7623 | -9898052.9948 | -14.02%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 369200 | 615820 | Sherebanglanagar NOCS | 617050 | Sherebanglanagar NOCS | 617050 | -1230 | -0.1997%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 90800
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 140800
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 0
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 600800
TOTAL => | [5 empty] | 0 | 600800 | 615820 |  | 617050 |  | 617050 | -1230 | -0.1997%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 182.172 | 170.633 |  | 11.539 | 180000 | 2077020 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8813.321 | 8772.538 |  | 40.783 | 180000 | 7340940 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.9 | #REF!
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6605.491 | 6570.523 |  | 34.968 | 180000 | 6294240 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9673.06 | #REF!
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4620.87 | #REF!
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 4419.5 | 4382.3 |  | 38.13 | 8000 | 305040 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 52970.34 | #REF!
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 42456.21 | #REF!
03 |  | 11 KV Bashir Uddin |  | 74819925 | 934.477 | 934.477 |  | 0 | 16000 | 0 | 0 | #DIV/0! | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 2350.06 | #REF!
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8401.63 | #REF!
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1131.24 | 1131.24 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9431.09 | #REF!
05 |  | 11 KV Lalkuthy |  | DHK15018 | 1031.06 | 1001.83 |  | 29.9607 | 40000 | 1198430 | 0 | 1 |  |  |  |  | 0 |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9794.39 | 9750.48 |  | 45.0077 | 40000 | 1800310 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [5 empty] | #REF!
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 52970.34 | 52769.06 |  | 206.312 | 8000 | 1650496 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  | #REF!
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8401.63 | 8361.96 |  | 40.6618 | 40000 | 1626470 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  | #REF!
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2350.06 | 2296.25 |  | 55.1552 | 40000 | 2206210 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  | #REF!
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  | #REF!
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.705 | 3273.705 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  | #REF!
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9673.06 | 9667.45 |  | 5.7502 | 40000 | 230010 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  | #REF!
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9431.09 | 9414.91 |  | 16.5845 | 40000 | 663380 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  | #REF!
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4620.87 | 4583.3 |  | 38.5092 | 40000 | 1540370 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  | #REF!
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.9 | 995.87 |  | 0.03075 | 40000 | 1230 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 42456.21 | 42349.9 |  | 108.9677 | 8000 | 871742 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 3303780 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 12408420 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48 | 48 | 48 | 48 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41 | 41 | 41 | 41 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [137 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | 89 | 89 | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [177 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[140 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.15752 | 0.36993 | 0.1982 | 0.22066 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.8235 | 3.3831 | 4.7675 | 6.4099 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.8104 | 1.4562 | 0.087826 | 1.0278 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 1.7413 | 0.57703 | 0.73688 | 0.95024 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 0.58489 | 1.028 | 0.51858 | 1.0269 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.0112 | -1.6675 | -0.51228 | -0.14892 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.11776 | 0.40506 | 0.59878 | 0.032224 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | -0.0059747 | 0.78672 | 0.71164 | 0.1718 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | -0.22661 | 0.090354 | 1.8004 | 0.72315 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | -0.34635 | 1.7093 | 1.2924 | 1.7957 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.078999 | 0.012837 | 0.076849 | 0.070408 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.71194 | 0.42244 | 0.67755 | 0.74731 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 0.39893 | -0.035562 | 1.3133 | 1.1413 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.23283 | 0.31121 | 1.418 | 1.5 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 1.6403 | 0.39586 | 0.22128 | 3.0565 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 1.1177 | 0.22363 | -0.15783 | 0.36408 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.75805 | 0.86271 | -0.5535 | -0.24021 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | -0.36418 | 0.10052 | -0.025203 | 0.21781 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.086911 | -0.2611 | 0.97617 | -0.13914 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.8667 | 1.1968 | 2.1342 | 2.1711 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.31895 | 0.16255 | -0.50074 | 0.12321 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.11321 | 0.07333 | 0.10551 | 0.1185 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.53789 | -0.043971 | -0.075665 | -0.064901 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.8226 | 1.1357 | 2.0237 | 1.9508 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.93812 | 0.5119 | 0.40513 | -1.985 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.21759 | 0.14868 | 0.41233 | 0.10871 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | -0.06039 | 1.5455 | 1.2197 | 1.7549 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 0.85 | 0.85 | 1 | 1 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -2.4815 | 2.0082 | -2.831 | -2.6717 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.3444 | 1.2163 | 0.86585 | 1.5712 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | -0.32329 | 1.3885 | 1.3864 | 1.1808 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | -0.09904 | 0.15826 | 0.3214 | 0.74913 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | -0.86776 | 1.3314 | 0.41255 | 0.56541 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.6468 | -0.78277 | 1.757 | 1.2174 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.39969 | 1.2104 | 0.54824 | 0.90308 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.30898 | 0.026513 | 0.047491 | -0.25931 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | -0.15046 | 0.063822 | 1.034 | -0.81695 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.54646 | 1.0407 | 0.334 | 0.41807 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.27825 | 0.23578 | 1.0938 | 1.7781 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | -0.40364 | 0.31408 | 0.18399 | 1.0713 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.26271 | -0.092639 | -0.05005 | 0.074283 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.62337 | 0.24412 | 0.051628 | -0.13885 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.92584 | 1.2666 | 0.69212 | 0.34882 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.26743 | 0.070914 | 0.3138 | 0.22403 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | November-2023 % of Loss | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.65358 | 0.15556 | 0.20112 | 0.95272 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.22332 | 0.15665 | 0.20537 | 0.20884 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.0652 | 1.1157 | 1.2591 | 1.2584 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.53762 | 0.77964 | 0.65402 | 1.444 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | -0.32773 | 0.17832 | 0.31771 | 1.0687 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | -0.2497 | 0.24297 | 0.17031 | 0.10378 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.0012825 | 0.10878 | -0.085961 | 0.041539 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.71204 | 0.43536 | 0.43971 | 1.0708 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | 0.14942 | -0.13156 | -0.4174 | 0.13595 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.1659 | 1.3565 | 2.1519 | 1.211 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.014741 | -0.031653 | -0.01844 | 0.010028 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.22189 | 0.79245 | 0.12531 | -0.42556 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.8 | -0.48244 | 0 | -1.9122 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -0.24353 | -1.0495e-13 | -0.04852 | -0.048314 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.3882 | 1.8683 | 1.573 | 0.29445 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 1.1022 | 0.43069 | 0.068963 | -0.86273 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | -0.02899 | -0.023304 | 0.076622 | 0.064233 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.23889 | 0.18888 | 0.15171 | 0.25381 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 0.12376 | 1.5174 | 2.7774 | 1.2284 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.078372 | -0.48766 | 0.66641 | -0.41499 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.57715 | 0.64916 | 0.88184 | 0.57602 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.2689 | 0.32352 | 0.80196 | -0.26653 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.56141 | 0.25534 | 0.44829 | 1.0739 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 0.9012 | 1.0829 | 1.112 | 1.1039 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.21493 | 0.33276 | 0.71435 | 0.23019 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 0.79088 | 1.0512 | 1.0599 | 0.74837 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.095 | 1.1333 | 1.4904 | 1.4865 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 0 | 1.4383 | 2.0408 | 0.18209 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.1359 | 1.4766 | 0.10496 | 0.096193 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | 0.3109 | 1.2474 | -0.24532 | -0.64219 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.49417 | 0.28876 | -0.62244 | 1.8284 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.22815 | 0.24367 | 0.46773 | 0.16433 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | 2.1521 | 0.66653 | 0.56513 | -0.8103 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.347 | 1.4676 | 1.9489 | 1.3703 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | 0.45149 | 1.3208 | 0.33477 | -0.12622 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.073934 | -0.057847 | -0.086839 | 0.038802 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.23243 | 0.22785 | 0.18163 | 1.4646 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | 1.7361 | 1.179 | 0.4914 | 1.1051 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.025332 | -0.044529 | -0.040721 | -0.12694 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.5041 | -2.2501 | 3.468 | 0.40336 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.35988 | 1.5164 | 1.7985 | 0.80075 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.096563 | 0.12007 | 0.27405 | 0.15019 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.40379 | -0.18029 | -0.41785 | -0.72448 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 0 | 0 | 0 | 0 | 0.033974

## ALL SS Loss History (hidden)
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68
|  | DPDC TOTAL SS | 89 | 89
NORTH
[7 empty] | HV Side |  |  |  | LV Side |  |  | % LOSS
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export / Import | XFR-Sending | XFR-Receiving | Feeder Total | Corrected Feeder Total | S_FT | R_FT | XS_FT | XR_FT
[7 empty] | S | R | EI | XS | XR | FT | CFT | %S | %R | %XS | %XR
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.15752 | 132 | 33 | 45680640 | 45921600 | 0 | 45921600 | 45566400 | 45312758.4 | 45384134.4 | 0.81187 | 1.3436 | 1.3436 | 0.55976
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 2.8235 | 33 | 11 |  |  |  | 16335190.4879 | 16212300 | 15886635.6 | 16335190.4879 | -100 | -100 | 2.8235 | 2.0499
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.8104 | 33 | 11 | 10841551.7853 | 0 | 0 | 0 | 11454900 | 10584878.192 | 10776502.4746 | 2.4249 | -100 | -100 | 8.2195
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 1.7413 | 33 | 11 | 10242362.8329 | 0 | 0 | 0 | 10503000 | 10323241.627 | 10503000 | -0.78346 | -100 | -100 | 1.7413
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 0.58489 | 33 | 11 | 16441858.2452 | 0 | 0 | 13358291 | 9630698 | 16346250.8 | 16441858.2452 | 0.58489 | -100 | -18.2792 | -41.0831
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | 1.0112 | 33 | 11 | 8358914.6524 | 2304000 | 0 | 2401200 | 23055480 | 8275237.2 | 8358914.6524 | 1.0112 | -72.1579 | -70.9833 | 178.6081
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.11776 | 132 | 33 | 0 | 54345000 | 14070000 | 54323000 | 54007200 | 53987810 | 54051385 | -100 | 0.66161 | 0.62086 | 0.035916
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | -0.0059747 | 33 | 11 |  |  |  | 10466710.8991 | 4966237.8 | 10467336.2901 | 10466710.8991 | -100 | -100 | -0.0059747 | -52.5549
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | -0.22661 | 33 | 11 | 3335122.7566 | 3361500 | 0 | 3454200 | 3357000 | 3342697.6213 | 3335122.7566 | -0.22661 | 0.56249 | 3.3357 | 0.42787
N-1 | 10 | New Ramna 33/11KV S/S | 10 | -0.34635 | 33 | 11 | 7161607.7459 | 0 | 0 | 0 | 7125200 | 7149963.684 | 7125200 | 0.16285 | -100 | -100 | -0.34635
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.078999 | 132 | 33 | 63945600 | 0 | 40275000 | 23670600 | 23332608 | 23314190 | 23332608 | 174.2776 | -100 | 1.5287 | 0.078999
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.71194 | 33 | 11 |  |  |  | 6259292.8817 | 6254352 | 6215045.76 | 6259292.8817 | -100 | -100 | 0.71194 | 0.63244
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 0.39893 | 33 | 11 | 7210881.4068 | 5986800 | 0 | 0 | 7152000.894 | 7182229.2386 | 7210881.4068 | 0.39893 | -16.6443 | -100 | -0.42088
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.23283 | 33 | 11 | 5712719.908 | 2015280 | 0 | 5818860 | 5718420 | 5805343.2 | 5818860 | -1.5955 | -65.2858 | 0.23283 | -1.4973
N-2 | 15 | Goran 33/11KV S/S | 15 | 1.6403 | 33 | 11 | 10018128.4771 | 0 | 0 | 10018000 | 9994040 | 9832754.4 | 9994040 | 1.8853 | -100 | 1.884 | 1.6403
N-2 | 16 | Taltola 33/11KV S/S | 16 | 1.1177 | 33 | 11 | 12736053.4253 | 0 | 0 | 0 | 12622400 | 12595278.7976 | 12736053.4253 | 1.1177 | -100 | -100 | 0.21533
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.75805 | 33 | 11 |  |  |  | 16429381.9035 | 16847460 | 16976148 | 16847460 | -100 | -100 | -3.2208 | -0.75805
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | -0.36418 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.086911 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.8667 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.31895 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.11321 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.53789 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.8226 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.93812 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.21759 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | -0.06039 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 0.85 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -2.4815 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 31 | Banasree 33/11 SS | 31 | 1.3444 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 32 | Mugdhapara Hospital | 32 | -0.32329 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 33 | DMC | 33 | -0.09904 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | -0.86776 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.6468 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 0.39969 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.30898 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | -0.15046 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.54646 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.27825 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | -0.40364 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.26271 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.62337 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 0.92584 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.26743 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
|  | SOUTH |  |  |  |  | S: HV Side; XR: LV Side
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export | XFR-Sending | XFR-Receiving | Feeder Total | Feeder Total
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.65358 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.22332 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.0652 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.53762 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | -0.32773 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | -0.2497 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.0012825 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.71204 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 9 | Kazla 132/133 KV SS | 39 | 0.14942 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.1659 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.014741 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.22189 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.8 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -0.24353 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.3882 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 1.1022 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | -0.02899 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.23889 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 0.12376 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.078372 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.57715 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.2689 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.56141 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 0.9012 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.21493 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 26 | Matuail 33/11KV S/S | 23 | 0.79088 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.095 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 0 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.1359 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Mitford 33/11 kV | 29 | 0.3109 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.49417 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.22815 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 33 | Dapa 33/11 kV | 32 | 2.1521 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.347 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 35 | Amulia 33/11 kv | 34 | 0.45149 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.073934 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.23243 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 38 | P & T 33/11 KV SS | 37 | 1.7361 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.025332 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.5041 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.35988 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.096563 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.40379 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Feeder Code | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) |  | 3: 132; 4: IMPORT; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000
| 132 KV DHANMONDI-3 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 10: Net Total | 54345000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 |  | 132 |  | SIEM0480 | 1 | 1632768 | 1632768 | 0 | 1000 | 0
| 132 kV Dhaka University |  | 132 |  | SIEM0480 | 1 | 119880 | 133950 | 14070 | 1000 | 14070000
3 | 132 kV Dhaka University |  | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 |  | 132 |  | SIEM0481 | 1 | 2212585 | 2235495 | 22910 | 1000 | 22910000
8 | 132 kV Ullon Circuit-3 |  | 132 |  | SIEM0484 | 1 | 2974112 | 2991477 | 17365 | 1000 | 17365000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 54345000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 54345000
| DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhaka University (Export) |  | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) |  | 132 |  |  | 1 | 119880 | 133950 | 14070 | 1000 |  | 14070000
|  |  | 7: 0; 8: 0; 10: Total |  | 14070000
| DHANMONDI 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) |  | 132 | NET IMPORT | SIEM0487 | 1 | 909704 | 921073 | 11369 | 1000 |  | 11369000
5 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | SIEM0496 | 1 | 1489700 | 1496532 | 6832 | 2000 |  | 13664000
9 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | SIEM0493 | 1 | 1359750 | 1366335 | 6585 | 2000 |  | 13170000
10 | 132/33kV, 80/120 MVA GT-3 (HV) |  | 132 |  | SIEM0497 | 1 | 1331375 | 1339435 | 8060 | 2000 |  | 16120000
|  |  | 10: Total |  | 54323000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 4: 54323000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 54323000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 54323000 | 132/33 kv GT LV Side |  | 54007200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 315800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.5813%
| 132 KV TOTAL IMPORT |  | 4: 54323000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming |  | 33 | IMPORT | BD001860 | 1 | 2305.89 | 2324.72 | 18.83 | 720000 | 13557600
12 | 132/33 kV GT-2 Incoming |  | 33 |  | BD001818 | 1 | 2274.38 | 2292.58 | 18.2 | 720000 | 13104000
17 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001863 | 1 | 2024.16 | 2046.44 | 22.28 | 720000 | 16041600
24 | 132/33 kV GT-4 Incoming |  | 33 |  | BD001916 | 1 | 1886.38 | 1909.93 | 23.55 | 480000 | 11304000
|  |  | 7: 0; 8: 0; 10: Total | 54007200 |  | 0
| DHANMONDI 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 |  |  |  |  | 10466710.8991 | Dhanmondi 33/11 kv ss | -0.0059747 |  | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 |  | 33 |  | BD001861 | 1 | 2170.41 | 2191.32 | 20.91 | 240000 |  | 5018400 | 5024309.5707 | [5 empty] | 33/11 kV 20/28 MVA T-1 | 5024309.5707 | 6385761.8419 | -1361452.2712 | -21.3201 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 |  | BD001892 | 1 | 2475.1 | 2497.75 | 22.65 | 240000 |  | 5436000 | 5442401.3284 | [5 empty] | 33/11 kV 20/28 MVA T-2 | 5442401.3284 | 6706254.7947 | -1263853.4664 | -18.8459 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 10454400 | 10466710.8991 | [5 empty] | 33 KV Feeders | 10466710.8991 | 13092016.6366 | -2625305.7376 | -20.0527 | OK
5 | New Ramna Circuit-1 |  | 33 |  | BD001919 | 1 | 1512.88 | 1527.47 | 14.59 | 240000 |  | 3501600 | 3505723.4164 |  | 6035899.3982 | New Ramna 33/11 kv ss | -0.34635 |  | New Ramna Circuit-1 | 3505723.4164 | 4392922.2029 | -887198.7866 | -20.1961 | OK
8 | Kakrail Circuit-1 |  | 33 |  | BD001825 | 1 | 890.27 | 900.82 | 10.55 | 240000 |  | 2532000 | 2534981.6342 | [5 empty] | Kakrail Circuit-1 | 2534981.6342 | 4855588.7213 | -2320607.0871 | -47.7925 | CHECK
9 | Kawran Bazar Circuit-1 |  | 33 |  | BD001820 | 1 | 1890.5 | 1904.37 | 13.87 | 240000 |  | 3328800 | 3332719.9304 |  | 7210881.4068 | Kakrail 33/11 kv ss | 0.39893 |  | Kawran Bazar Circuit-1 | 3332719.9304 | 3949533.4562 | -616813.5257 | -15.6174 | OK
10 | New Ramna Circuit-2 |  | 33 |  | BD001816 | 1 | 1236.03 | 1246.56 | 10.53 | 240000 |  | 2527200 | 2530175.9818 | [5 empty] | New Ramna Circuit-2 | 2530175.9818 | 3115769.8346 | -585593.8528 | -18.7945 | OK
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.43 | 462.44 | 0.01 | 240000 |  | 2400 | 2402.8262 |  | 3335122.7566 | Kawran Bazar 33/11 kv ss | -0.22661 |  | Kawran BazarCircuit-2 | 2402.8262 | 0 | 2402.8262 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder |  | 33 |  | BD001840 | 1 | 446.7 | 464.63 | 17.93 | 240000 |  | 4303200 | 4308267.365 | [5 empty] | DMC Hospital Feeder | 4308267.365 | 3197700.3639 | 1110567.0012 | 34.7302 | OK
15 | Green Road Circuit-2 (U/G) |  | 33 |  | BD001918 | 1 | 2172.52 | 2193.69 | 21.17 | 240000 |  | 5080800 | 5086783.0517 |  | 4308267.365 | DMC Hospital 33/11 kv ss | -0.09904 |  | Green Road Circuit-2 (U/G) | 5086783.0517 | 6561671.5077 | -1474888.456 | -22.4773 | OK
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1676.76 | 1696.22 | 19.46 | 240000 |  | 4670400 | 4675899.7726 | [5 empty] | Kakrail Circuit-2 | 4675899.7726 | 4812213.7352 | -136313.9626 | -2.8327 | OK
18 | BSMMU Hospital Circuit-1 |  | 33 |  | BD001920 | 1 | 755.4 | 766.57 | 11.17 | 240000 |  | 2680800 | 2683956.8582 |  | 10841551.7853 | Green Road 33/11 kv ss | 1.8104 |  | BSMMU Hospital Circuit-1 | 2683956.8582 | 3484457.2164 | -800500.3582 | -22.9735 | OK
19 | Azimpur Circuit-1 |  | 33 |  | BD001822 | 1 | 2057.42 | 2072.37 | 14.95 | 240000 |  | 3588000 | 3592225.1593 | [5 empty] | Azimpur Circuit-1 | 3592225.1593 | 8120761.2858 | -4528536.1264 | -55.7649 | CHECK
20 | Azimpur Circuit-2 |  | 33 |  | BD001857 | 1 | 1867.53 | 1885.43 | 17.9 | 240000 |  | 4296000 | 4301058.8864 |  | 3940634.9574 | BSMMU 33/11 kv ss | 0.6468 |  | Azimpur Circuit-2 | 4301058.8864 | 544597.0477 | 3756461.8388 | 689.769 | FAULT
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 170.67 | 175.9 | 5.23 | 240000 |  | 1255200 | 1256678.0992 | [5 empty] | BSMMU Hospital Circuit-2 | 1256678.0992 | 1424145.3768 | -167467.2776 | -11.7591 | OK
23 | Green Road Circuit-1 |  | 33 |  | BD001865 | 1 | 1502.1 | 1526.05 | 23.95 | 240000 |  | 5748000 | 5754768.7335 |  | 7893284.0458 | Azimpur 33/11 kv ss | 1.8226 |  | Green Road Circuit-1 | 5754768.7335 | 6860476.9675 | -1105708.234 | -16.1171 | OK
26 | 33/0.4 kV, 500 kVA AT-1 |  | 0.4 |  | 84.2659 | 1 | 323466 | 325367 | 1901 | 10 |  | 19010 | 19032.3858 | Paribag |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 19032.3858 | 23956.6474 | -4924.2616 | -20.5549 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 |  | 0.4 |  | 84.2673 | 1 | 478776 | 478776 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 43533410 | 43584674.1009 | [6 empty] | 43584674.1009 | 51343794.3634 | -7759120.2624 | -15.1121 | OK
|  |  | 9=8-7: Grand Total | 54051385 | 53987810 | 54051385 | 0.11776
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming |  | 11 | IMPORT | DHK60884 | 1 | 975119.32 | 975119.32 | 0 | 180 | 0 |  | 0
16 | 33/11 kV Transformer-1 Incoming |  | 11 |  | DHK60976 | 1 | 611778.42 | 639368.63 | 27590.21 | 180 | 4966237.8 |  | 10466710.8991
|  |  | 7: 0; 8: 0; 10: Total | 4966237.8 |  | 10466710.8991
| DHANMONDI 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 10517508 | 11634850 | 1117342 | 1 |  | 1117342 | 1117275.2423 | Paribag |  |  |  |  | 11 kV Balaka Feeder | 1117275.2423 | 1327224.0724 | -209948.8301 | -15.8186 | OK
5 | 11 kV Mogbazar O/H | C301M | 11 |  | HA021100463-02 | 1 | 52334628 | 53414203 | 1079575 | 1 |  | 1079575 | 1079510.4987 | Paribag |  |  |  |  | 11 kV Mogbazar O/H | 1079510.4987 | 1506112.4428 | -426601.9441 | -28.3247 | OK
6 | 11 kV Panthopath Feeder | C3011 | 11 |  | HA021101078-02 | 1 | 66739049 | 67706878 | 967829 | 1 |  | 967829 | 967771.1752 | Paribag |  |  |  |  | 11 kV Panthopath Feeder | 967771.1752 | 1200141.0854 | -232369.9102 | -19.3619 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 |  | DHK60882 | 1 | 236770.81 | 242194.26 | 5423.45 | 60 |  | 325407 | 325387.5579 | Paribag |  |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 325387.5579 | 424694.4888 | -99306.9308 | -23.3831 | OK
8 | 11 kV P G Hospital Feeder | C301P | 11 |  | DHK60889 | 1 | 294533.1518 | 296567.58 | 2034.4282 | 60 |  | 122065.6901 | 122058.3971 | Paribag |  |  |  |  | 11 kV P G Hospital Feeder | 122058.3971 | 224979.6606 | -102921.2636 | -45.7469 | CHECK
9 | 11 kV Abdul Monem Ltd |  | 11 |  | DHK60890 | 1 | 720.79 | 726.52 | 5.73 | 60000 |  | 343800 | 343779.459 | Paribag |  |  |  |  | 11 kV Abdul Monem Ltd | 343779.459 | 423304.2367 | -79524.7777 | -18.7867 | OK
10 | 11 kV Surjasen Hall Feeder | D301H | 11 |  | DHK60880 | 1 | 576270.3 | 581064.2 | 4793.9 | 60 |  | 287634 | 287616.8148 | Ramna |  |  |  |  | 11 kV Surjasen Hall Feeder | 287616.8148 | 330665.314 | -43048.4992 | -13.0188 | OK
11 | 11 kV Azimpur-1 Feeder |  | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | D301U | 11 |  | DHK60873 | 1 | 956639.98 | 963916.78 | 7276.8 | 60 |  | 436608 | 436581.914 | Ramna |  |  |  |  | 11 kV TSC Feeder | 436581.914 | 552858.9173 | -116277.0032 | -21.0319 | OK
13 | 11 kV SCADA Bhaban | C301S | 11 |  | DHK60883 | 1 | 28791.31 | 28971.13 | 179.82 | 60 |  | 10789.2 | 10788.5554 | Paribag |  |  |  |  | 11 kV SCADA Bhaban | 10788.5554 | 14763.0376 | -3974.4822 | -26.9218 | OK
14 | 11 kV DPH Sw/S-2 |  | 11 |  | DHK60871 | 1 | 549657.1 | 563612.73 | 13955.63 | 60 |  | 837337.8 | 837287.7716 | Paribag |  |  |  |  | 11 kV DPH Sw/S-2 | 837287.7716 | 1020090.0393 | -182802.2677 | -17.9202 | OK
17 | 11 kV New Elephant Road Feeder | C301E | 11 |  | DHK60981 | 1 | 131190.1 | 143677.95 | 12487.85 | 60 |  | 749271 | 749226.2334 | Paribag |  |  |  |  | 11 kV New Elephant Road Feeder | 749226.2334 | 894951.6314 | -145725.3981 | -16.283 | OK
18 | 11 kV Dhanmondi O/H Feeder | C301D | 11 |  | DHK61110 | 1 | 480431.1 | 501237.66 | 20806.56 | 60 |  | 1248393.6 | 1248319.0123 | Paribag |  |  |  |  | 11 kV Dhanmondi O/H Feeder | 1248319.0123 | 1468536.7336 | -220217.7212 | -14.9957 | OK
19 | 11 kV Sonargaon Feeder |  | 11 |  | DHK61115 | 1 | 426855.1 | 449664.26 | 22809.16 | 60 |  | 1368549.6 | 1368467.8334 | Paribag |  |  |  |  | 11 kV Sonargaon Feeder | 1368467.8334 | 1667970.4775 | -299502.6441 | -17.9561 | OK
20 | 11 kV Museum Feeder | D301M | 11 |  | DHK61107 | 1 | 554305.25 | 556021.54 | 1716.29 | 60 |  | 102977.4 | 102971.2474 | Ramna |  |  |  |  | 11 kV Museum Feeder | 102971.2474 | 132172.5149 | -29201.2675 | -22.0933 | OK
21 | 11 kV Shanta property |  | 11 |  | DHK61112 | 1 | 352032.55 | 354429.92 | 2397.37 | 60 |  | 143842.2 | 143833.6059 | Paribag |  |  |  |  | 11 kV Shanta property | 143833.6059 | 183722.5048 | -39888.899 | -21.7115 | OK
22 | 11 kV BIRDEM RMU Feeder | C601R | 11 |  | DHK61108 | 1 | 746291.96 | 756877.47 | 10585.51 | 60 |  | 635130.6 | 635092.6529 | Kakrail |  |  |  |  | 11 kV BIRDEM RMU Feeder | 635092.6529 | 850234.9813 | -215142.3284 | -25.3039 | OK
23 | 11 kV Azimpur-2 Feeder |  | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 |  | 11 |  | DHK60978 | 1 | 826536.1 | 838049.17 | 11513.07 | 60 |  | 690784.2 | 690742.9278 | Kakrail |  |  |  |  | 11 kV DPH Sw/S-1 | 690742.9278 | 869594.4982 | -178851.5704 | -20.5672 | OK
|  |  | 10: Total | 10466710.8991 | 10467336.2901 | 10466710.8991 | -0.0059747
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Paribag at 33 KV level |  |  | 8332737.728
[7 empty] | Azimpur at 33 KV level |  |  | 0
[7 empty] | Ramna at 33 KV level |  |  | 827169.9762
[7 empty] | Kakrail at 33 KV level |  |  | 1325835.5807
|  |  | 7: Total =; 10: 10485743.2849 | -1.3752e-09
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 |  | 33 | 0 | BD001820 | 1 | 1890.5 | 1904.37 | 13.87 | 240000 | 0 | 3328800 | 3332719.9304
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.43 | 462.44 | 0.01 | 240000 | 0 | 2400 | 2402.8262
|  |  | 10: Total | 0 | 3331200 | 3335122.7566
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar |  | 33 | 0 | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAWRANBAZAR 33 KV SIDE (RECEIVING) | [10 empty] | 3331200 | 3335122.7566
1 | 33 kV Dhanmondi Circuit-1 |  | 33 |  | DHK61036 | 1 | 3462.35 | 3474.8 | 12.45 | 270000 | 3361500
5 | 33 kV Dhanmondi Circuit-2 |  | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar |  | 33 |  | DHK 61038 | 1 | 1061.95 | 1061.95 | 0 | 270000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 3361500 | 0 | 3335122.7566
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | DHK61039 | 1 | 5201.11 | 5220.3 | 19.19 | 180000 |  | 3454200
3 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 3454200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4: 3335122.7566; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3335122.7566
| MOGBAZAR 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 3335122.7566 | 33 KV TX HV SIDE |  | 3454200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -119077.2434
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -3.57%
| TOTAL IMPORT |  | 4: 3335122.7566
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK00182 | 1 | 15223.2 | 15558.9 | 335.7 | 10000 | 3357000 |  | 3335122.7566
15 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 3357000 |  | 3335122.7566
| KAWRANBAZAR 11 KV SIDE |  | 7: 0; 8: 0
6 | WASA Bhaban | C605M | 11 |  | 8536188 | 1.18 | 271216 | 271216 | 0 | 1000 | 935160 | 935160 | 933040.8402 | Shere b.nagar | From Customer End | 80 |  |  | WASA Bhaban | 933040.8402 | 1122893.6635 | -189852.8233 | -16.9075 | OK
7 | Sangsad Bhaban |  | 11 |  | 8536178 | 1.18 | 581779 | 586004 | 4225 | 44 |  | 219362 | 218864.9052 | Shere b.nagar |  | 20 |  |  | Sangsad Bhaban | 218864.9052 | 224818.1088 | -5953.2035 | -2.648 | OK
8 | Air Port Road (West) | D505A | 11 |  | 8536182 | 1.18 | 4157.6 | 4761.7 | 604.1 | 1000 |  | 712838 | 711222.6426 | Shere b.nagar |  | 60 |  |  | Air Port Road (West) | 711222.6426 | 1042454.0487 | -331231.4061 | -31.7742 | OK
9 | ICC (PM Office) | C172C | 11 |  | 8536193 | 1.18 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  | 20 |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | D505U | 11 |  | DHK00183 | 1.18 | 17563.9 | 18092.4 | 528.5 | 444.44 |  | 277166.1172 | 276538.0329 | Shere b.nagar |  | 40 |  |  | (UTC) Tower | 276538.0329 | 285253.3218 | -8715.2889 | -3.0553 | OK
11 | Sonargaon Hotel | C605O | 11 |  | 8536190 | 1.18 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 47083.68 | 46976.984 | Kakrail | Estimated |  |  |  | Sonargaon Hotel | 46976.984 | 0 | 46976.984 | #DIV/0! | #DIV/0!
12 | Panthopath | D505P | 11 |  | 8536184 | 1.18 | 38266.9 | 39056.5 | 789.6 | 1000 |  | 931728 | 929616.6174 | Shere b.nagar |  |  |  |  | Panthopath | 929616.6174 | 1035454.7302 | -105838.1128 | -10.2214 | OK
13 | Titas Bhaban | C605N | 11 |  | DHK00190 | 1.18 | 57079.4 | 57494.3 | 414.9 | 444.44 |  | 217589.8241 | 217096.7452 | Kakrail |  |  |  |  | Titas Bhaban | 217096.7452 | 236270.9269 | -19174.1817 | -8.1153 | OK
16 | Green Road Dormatory s/s |  | 11 |  | DHK00021 | 1.18 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | [5 empty] | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 |  | 11 |  | 85-12906 | 1.18 | 69276 | 69426 | 150 | 10 |  | 1770 | 1765.989 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-1 | 1765.989 | 2388.6563 | -622.6673 | -26.0677 | OK
27 | Aux. Transformer, AT-2 |  | 11 |  | 85-12909 | 1.18 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3335122.7566 | 3342697.6213 | 3335122.7566 | -0.22661
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail at 33 KV level |  |  | 264073.7292
[6 empty] | Shere b.nagar at 33 KV level |  |  | 3071049.0274
[6 empty] | Total = |  |  | 3335122.7566 | 0
|  |  | 9=8-7: Customer Name; 10: Customer Number | Feeder name | Consumption | OMF
|  |  | 9=8-7: Square Hospital; 10: 27529489 | Wasa Bhaban | 935160 | 6000
|  |  | 9=8-7: NOCS Name; 10: Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
|  |  | 9=8-7: ShereBangla Nagar; 10: 2874.54 | 2984.58 | 1130.35 | 1176.17
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 |  | 33 | 0 | BD001919 | 1 | 1512.88 | 1527.47 | 14.59 | 240000 | 0 | 3501600 | 3505723.4164
10 | New Ramna Circuit-2 |  | 33 | 0 | BD001816 | 1 | 1236.03 | 1246.56 | 10.53 | 240000 | 0 | 2527200 | 2530175.9818
|  |  | 10: Total | 0 | 6028800 | 6035899.3982
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1123200 | 1125708.3477
|  |  | 10: Total | 0 | 1123200 | 1125708.3477
| NEW RAMNA 33 KV SIDE (RECEIVING) | [10 empty] | 7152000 | 7161607.7459
|  |  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 10: Total |  | 0 | 7161607.7459
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 9=8-7: 0 |  | 0
| Feeder No.2 |  | 3: 33; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.3. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 7161607.7459 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 6035899.3982; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7161607.7459
| NARINDA 33 KV SIDE |  | 4: 1125708.3477; 6: 33 KV NET IMPORT; 9=8-7: 7161607.7459 | 33 KV TX HV SIDE |  | 7161607.7459
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 7161607.7459
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK 00002 | 1 | 26395 | 26743.5 | 348.5 | 10000 | 3485000 |  | 3502807.359
15 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK 00007 | 1 | 14584.3 | 14836 | 251.7 | 10000 | 2517000 |  | 2529861.1543
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming |  | 11 |  | DHKA2182 | 1 | 623.07 | 629.31 | 6.24 | 180000 | 1123200 |  | 1128939.2326
|  |  | 7: 0; 8: 0; 10: Total | 7125200 |  | 7161607.7459
| NEW RAMNA 11 KV SIDE |  | 7: 0; 8: 0
4 | Police Bhaban | D315I | 11 |  | DHK 00005 | 1 | 74130.7 | 74352.7 | 222 | 444.44 |  | 98665.68 | 98323.9544 | Ramna |  |  |  |  | Police Bhaban | 98323.9544 | 113280.4639 | -14956.5095 | -13.2031 | OK
5 | Water Works |  | 11 |  | DHK 00010 | 1 | 0 | 681.6 | 681.6 | 444.44 |  | 302930.304 | 301881.114 | Lalbag |  |  |  |  | Water Works | 301881.114 | 0 | 301881.114 | #DIV/0! | #DIV/0!
6 | GPO | D3157 | 11 |  | DHK 00060 | 1 | 84.7 | 681.6 | 596.9 | 444.44 |  | 265286.236 | 264367.4251 | Ramna |  |  |  |  | GPO | 264367.4251 | 254768.0345 | 9599.3906 | 3.7679 | OK
7 | Culvert Road | D315C | 11 |  | 8536184 | 1 | 40096.9 | 40342.5 | 245.6 | 444.44 | 50 | 588546 | 586507.5886 | Ramna | Estimated |  |  |  | Culvert Road | 586507.5886 | 1175263.5465 | -588755.9578 | -50.0957 | CHECK
8 | Secretariat (East) | D315E | 11 |  | DHK00059 | 1 | 81730.6 | 81748.6 | 18 | 444.44 |  | 7999.92 | 7972.2125 | Ramna |  |  |  |  | Secretariat (East) | 7972.2125 | 1672.5368 | 6299.6757 | 376.6539 | FAULT
9 | Siddik Bazar | B615S | 11 |  | DHK00076 | 1 | 41750.6 | 45245.7 | 3495.1 | 444.44 |  | 1553362.244 | 1547982.2206 | Bangshal |  |  |  |  | Siddik Bazar | 1547982.2206 | 1854662.4712 | -306680.2506 | -16.5356 | OK
10 | Bokshi Bazar | D315X | 11 |  | DHK 00206 | 1 | 90253.3 | 91450.6 | 1197.3 | 444.44 |  | 532128.012 | 530285.0026 | Ramna |  |  |  |  | Bokshi Bazar | 530285.0026 | 560480.6352 | -30195.6325 | -5.3875 | OK
11 | Ramna 11 kV Sw/S Circuit-1 |  | 11 |  | DHK00198 | 1 | 50244.2 | 51162 | 917.8 | 444.44 |  | 407907.032 | 406494.2583 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 406494.2583 | 588235.7049 | -181741.4467 | -30.896 | OK
12 | TNT RMU | D315Z | 11 |  | DHK 00207 | 1 | 64037.1 | 64922.1 | 885 | 444.44 |  | 393329.4 | 391967.1155 | Ramna |  |  |  |  | TNT RMU | 391967.1155 | 395125.5127 | -3158.3973 | -0.79934 | OK
13 | DIT 11 kV Sw/S Circuit-1 |  | 11 |  | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | D315W | 11 |  | DHK 00006 | 1 | 72394.3 | 73143.7 | 749.4 | 444.44 |  | 333063.336 | 331909.7812 | Ramna |  |  |  |  | Secretariat (West) | 331909.7812 | 504156.8291 | -172247.048 | -34.1654 | OK
17 | Ramna 11 kV Sw/S Circuit-2 |  | 11 |  | DHK00197 | 1 | 89224 | 89232.8 | 8.8 | 444.44 |  | 3911.072 | 3897.5261 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 3897.5261 | 12747.4425 | -8849.9163 | -69.425 | CHECK
18 | Sayed Nazrul Islam Road | D315A | 11 |  | DHK00186 | 1 | 36023.9 | 38231 | 2207.1 | 444.44 |  | 980923.524 | 977526.1249 | Ramna |  |  |  |  | Sayed Nazrul Islam Road | 977526.1249 | 1189218.8524 | -211692.7275 | -17.801 | OK
19 | Gulistan Complex | D3153 | 11 |  | DHK00030 | 1 | 56404.5 | 56794.4 | 389.9 | 444.44 |  | 173287.156 | 172686.9812 | Ramna |  |  |  |  | Gulistan Complex | 172686.9812 | 222492.5951 | -49805.6139 | -22.3853 | OK
20 | Mohanagor Nattomanso | D3152 | 11 |  | DHK 00008 | 1 | 443.7 | 564 | 120.3 | 444.44 |  | 53466.132 | 53280.9537 | Ramna |  |  |  |  | Mohanagor Nattomanso | 53280.9537 | 61024.9905 | -7744.0369 | -12.6899 | OK
21 | DIT 11 kV Sw/S Circuit-2 |  | 11 |  | DHK00196 | 1 | 29086.7 | 29843.6 | 756.9 | 444.44 |  | 336396.636 | 335231.5364 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-2 | 335231.5364 | 454930.0034 | -119698.467 | -26.3114 | OK
22 | Jail | B678Z | 11 |  | DHK00009 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | D315K | 11 |  | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 |  | 0 | 0 | Ramna | Check |  |  |  | Kosturi Bazar | 0 | 254911.0541 | -254911.0541 | -100 | CHECK
24 | Kaptan Bazar | B124K | 11 |  | HA021101251-02 | 1 | 7930785 | 8299757 | 368972 | 1 |  | 368972 | 367694.0766 | Narinda |  |  |  |  | Kaptan Bazar | 367694.0766 | 419318.091 | -51624.0144 | -12.3114 | OK
25 | G.T.V | D315G | 11 |  | HA-021101054-02 | 1 | 73543399 | 73968193 | 424794 | 1 |  | 424794 | 423322.7388 | Ramna |  |  |  |  | G.T.V | 423322.7388 | 579351.6265 | -156028.8877 | -26.9316 | OK
26 | Kazi Alauddin Road | B615K | 11 |  | HA021100951-02 | 1 | 7837719 | 8159834 | 322115 | 1 |  | 322115 | 320999.3644 | Bangshal |  |  |  |  | Kazi Alauddin Road | 320999.3644 | 441368.6747 | -120369.3103 | -27.2718 | OK
28 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.4 |  | 2436 | 1 | 67703 | 67991 | 288 | 10 |  | 2880 | 2870.0252 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 2870.0252 | 2847.8614 | 22.1638 | 0.77826 | OK
29 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.4 |  | 2437 | 1 | 90000 | 90000 | 0 | 10 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 4943.0737 | -4943.0737 | -100 | CHECK
|  |  | 10: Grand Total | 7125200 | 7149963.684 | 7125200 | -0.34635
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 4251411.688
[6 empty] | Lalbag | at 33 KV level |  | 301881.114
[6 empty] | Bangshal | at 33 KV level |  | 1868981.585
[6 empty] | Motijheel | at 33 KV level |  | 335231.5364
[6 empty] | Narinda | at 33 KV level |  | 367694.0766
[6 empty] | Total = |  |  | 7125200 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 |  | 33 | 0 | BD001825 | 1 | 890.27 | 900.82 | 10.55 | 240000 | 0 | 2532000 | 2534981.6342
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1676.76 | 1696.22 | 19.46 | 240000 | 0 | 4670400 | 4675899.7726
|  |  | 10: Total | 0 | 7202400 | 7210881.4068
ULLON 33 KV SIDE
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder.(import) |  | 33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAKRAIL 33 KV SIDE (RECEIVING) | [10 empty] | 7202400 | 7210881.4068
5 | 33 kV Dhanmondi-2 |  | 33 |  | 06604376 | 1 | 5370.95 | 5396.96 | 26.01 | 180000 | 4681800
2 | 33 kV Dhanmondi-1 |  | 33 |  | 06604375 | 1 | 2115.36 | 2122.61 | 7.25 | 180000 | 1305000
| 33 KV Kakrail From ULLON |  | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola |  | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
|  |  | 10: Total | 5986800
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 4: 7210881.4068; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KAKRAIL 33 KV NET IMPORT |  | 7210881.4068
| ULLON 33 KV SIDE |  | 4: 0; 6: KAKRAIL 33 KV NET IMPORT; 9=8-7: 7210881.4068 | KAKRAIL KV NET IMPORT |  | 7152000.894
| Taltola 33 KV SIDE |  | 4: 0 | LOSS UNITS=> |  | 58880.5128
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.8166%
| TOTAL IMPORT |  | 4: 7210881.4068
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK00017 | 1 | 20700.9 | 20985.2 | 284.3 | 8888.89 | 2527111.427 |  | 2547916.4603
15 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK00018 | 1 | 7413 | 7933.3 | 520.3 | 8888.89 | 4624889.467 |  | 4662964.9465
|  |  | 7: 0; 8: 0; 10: Total | 7152000.894 |  | 7210881.4068
| KAKRAIL 11 KV SIDE |  | 7: 0; 8: 0
7 | Pioneer | D304P | 11 |  | 06604395 | 1 | 24160.1 | 24231.18 | 71.08 | 8000 |  | 568640 | 570908.4836 | Ramna |  |  |  |  | Pioneer | 570908.4836 | 784360.9682 | -213452.4847 | -27.2136 | OK
8 | Pir Saheber Goli | D604L | 11 |  | DHK-00102 | 1 | 92942.8 | 95296.1 | 2353.3 | 444.444 |  | 1045910.0652 | 1050082.5289 | Rajarbag |  |  |  |  | Pir Saheber Goli | 1050082.5289 | 1392792.0181 | -342709.4891 | -24.6059 | OK
9 | Montri Para | C604B | 11 |  | DHK-00110 | 1 | 12950.5 | 12973.5 | 23 | 2222.22 |  | 51111.06 | 51314.9581 | Kakrail |  |  |  |  | Montri Para | 51314.9581 | 167051.5164 | -115736.5583 | -69.282 | CHECK
10 | Baily Road 11 kV Sw/S-2 |  | 11 |  | 9119865 | 1 | 72383.6 | 73065.6 | 682 | 1000 |  | 682000 | 684720.7122 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-2 | 684720.7122 | 2230006.6883 | -1545285.9761 | -69.2951 | CHECK
11 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | D3046 | 11 |  | 1025651 | 1 | 30010.8 | 30191.9 | 181.1 | 1000 |  | 181100 | 181822.4648 | Ramna |  |  |  |  | High Court | 181822.4648 | 251110.6689 | -69288.2041 | -27.5927 | OK
13 | Secretaiat |  | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | D604N | 11 |  | 06604402 | 1.1 | 5783.83 | 5809.98 | 26.15 | 40000 |  | 1150600 | 1155190.1048 | Rajarbag | CF 1.1 due to PT missing from 10-11-2023 to 12-11-2023 |  |  |  | Shanti Nagar Bazar | 1155190.1048 | 1443886.346 | -288696.2412 | -19.9944 | OK
17 | Tottho Bhovon |  | 11 |  | 9119867 | 1.1 | 32987.8 | 33058.1 | 70.3 | 1000 |  | 77330 | 77638.4937 | Kakrail |  |  |  |  | Tottho Bhovon | 77638.4937 | 216622.9377 | -138984.444 | -64.1596 | CHECK
18 | Central Police Hospital/ PNT (Circuit House) |  | 11 |  | DHK00199 | 1.1 | 79591.4 | 79666.3 | 74.9 | 2222.22 |  | 183088.7058 | 183819.1042 | Kakrail |  |  |  |  | Central Police Hospital/ PNT (Circuit House) | 183819.1042 | 639993.908 | -456174.8038 | -71.278 | CHECK
19 | Baily Road 11 kV Sw/S-1 |  | 11 |  | DHK00027 | 1.1 | 57453.2 | 58241 | 787.8 | 2222.22 |  | 1925731.4076 | 1933413.755 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-1 | 1933413.755 | 1067396.9898 | 866016.7652 | 81.1335 | FAULT
20 | Bijoy Nagar | D304B | 11 |  | D1025656 | 1.1 | 69884.3 | 70601.3 | 717 | 1000 |  | 788700 | 791846.372 | Ramna |  |  |  |  | Bijoy Nagar | 791846.372 | 917673.5431 | -125827.1711 | -13.7115 | OK
21 | Shilpakala Academy | D304F | 11 |  | D0086137 | 1.1 | 27376 | 27773.3 | 397.3 | 1000 |  | 437030 | 438773.4499 | Ramna |  |  |  |  | Shilpakala Academy | 438773.4499 | 432945.982 | 5827.4679 | 1.346 | OK
22 | Judges Complex | C604JC | 11 |  | 06604344 | 1.1 | 684.38 | 686.38 | 2 | 40000 |  | 88000 | 88351.0596 | Kakrail |  |  |  |  | Judges Complex | 88351.0596 | 118357.8949 | -30006.8352 | -25.3526 | OK
23 | Auxiliary Transformer, AT-1 |  | 11 |  | 39333 | 1 | 496195 | 499183 | 2988 | 1 |  | 2988 | 2999.9201 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-1 | 2999.9201 | 3752.665 | -752.7449 | -20.0589 | OK
24 | Auxiliary Transformer, AT-2 |  | 11 |  | 39254 | 1 | 1228762 | 1228762 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-2 | 0 | 1874.3332 | -1874.3332 | -100 | CHECK
|  |  | 10: Grand Total | 7210881.4068 | 7182229.2386 | 7210881.4068 | 0.39893
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1983350.7703
[6 empty] | Rajarbag | at 33 KV level |  | 2205272.6337
[6 empty] | Kakrail | at 33 KV level |  | 3022258.0028
[6 empty] | Total = |  |  | 7210881.4068 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 |  | 33 | 0 | BD001920 | 1 | 755.4 | 766.57 | 11.17 | 240000 | 0 | 2680800 | 2683956.8582
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 170.67 | 175.9 | 5.23 | 240000 | 0 | 1255200 | 1256678.0992
|  |  | 10: Total |  | 3936000 | 3940634.9574 | 0.11776
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 |  | 33 |  | BD017073 | 1 | 78529.65 | 81207.61 | 2677.96 | 1000 | 2677960
4 | 33 kV Dhanmondi Incoming Circuit-2 |  | 33 |  | BD017074 | 1 | 40908.72 | 42162.3 | 1253.58 | 1000 | 1253580
| 33 KV Ullon-1 Feeder |  | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 3931540 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0 |  | Total
[7 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017072 | 1 | 104707.64 | 104707.64 | 0 | 888.89 |  | 0
6 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017076 | 1 | 38893.33 | 40308.75 | 1415.42 | 888.89 |  | 1258152.6838
|  |  | 10: Total |  | 1258152.6838
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 3940634.9574; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3940634.9574
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 3940634.9574 | 33/11 KV XF HV SIDE |  | 1258152.6838
[11 empty] | LOSS UNITS=> |  | 2682482.2736
[11 empty] | LOSS % IN => |  | 68.07%
| TOTAL IMPORT |  | 4: 3940634.9574
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD017081 | 1 | 84305.1 | 86969.48 | 2664.38 | 1000 | 2664380 |  | 2688700.603
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD017082 | 1 | 33653.56 | 34894.17 | 1240.61 | 1000 | 1240610 |  | 1251934.3544
|  |  | 7: 0; 8: 0; 10: Total | 3904990 |  | 3940634.9574
| BSMMU HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Jamuna (F1) | C6101JG | 11 |  | BD017073 | 1 | 0.4073 | 0.4177 | 0.0104 | 2000 |  | 20.8 | 20.9345 | Kakrail |  |  |  |  | 11 kV Jamuna (F1) | 20.9345 | 34.3292 | -13.3946 | -39.0182 | OK
9 | 11 kV Pukur Par (F2) | C6101PP | 11 |  | BD017074 | 1 | 2992.52 | 3012.43 | 19.91 | 2000 |  | 39820 | 40077.555 | Kakrail |  |  |  |  | 11 kV Pukur Par (F2) | 40077.555 | 42742.7844 | -2665.2294 | -6.2355 | OK
10 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 |  | BD017075 | 1 | 1854.6 | 1878.4 | 23.8 | 2000 |  | 47600 | 47907.8759 | Kakrail |  |  |  |  | 11 kV BSMMU Convention center (F3) | 47907.8759 | 87211.9487 | -39304.0728 | -45.0673 | CHECK
11 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 |  | BD017076 | 1 | 3278.62 | 3350.25 | 71.63 | 2000 |  | 143260 | 144186.603 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 144186.603 | 174503.2711 | -30316.6681 | -17.3731 | OK
12 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 |  | BD017077 | 1 | 15411.85 | 15660.41 | 248.56 | 2000 |  | 497120 | 500335.3629 | Kakrail |  |  |  |  | 11 kV Holi Family Feeder (F5) | 500335.3629 | 627271.1967 | -126935.8338 | -20.2362 | OK
13 | 11 kV Navy House Feeder (F6) | C6101NH | 11 |  | BD017078 | 1 | 27649.1 | 27893.89 | 244.79 | 2000 |  | 489580 | 492746.5943 | Kakrail |  |  |  |  | 11 kV Navy House Feeder (F6) | 492746.5943 | 733453.4805 | -240706.8862 | -32.8183 | OK
14 | 11 kV Paribagh Feeder (F7) | C31016 | 11 |  | BD017079 | 1 | 34271.31 | 34847.13 | 575.82 | 2000 |  | 1151640 | 1159088.7861 | Paribag |  |  |  |  | 11 kV Paribagh Feeder (F7) | 1159088.7861 | 1451369.5422 | -292280.7561 | -20.1383 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 |  | BD017080 | 1 | 7006.17 | 7150.9 | 144.73 | 2000 |  | 289460 | 291332.2219 | Paribag |  |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 291332.2219 | 378930.46 | -87598.2382 | -23.1172 | OK
18 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 |  | BD017083 | 1 | 2501.72 | 2558.44 | 56.72 | 2000 |  | 113440 | 114173.7278 | Paribag |  |  |  |  | 11 kV Oncology Bhaban (F9) | 114173.7278 | 135094.1858 | -20920.458 | -15.4858 | OK
19 | Rupayan Trade Center | C6101RT | 11 |  | BD017084 | 1 | 1616.91 | 1722.15 | 105.24 | 2000 |  | 210480 | 211841.3807 | Kakrail |  |  |  |  | Rupayan Trade Center | 211841.3807 | 253083.3205 | -41241.9397 | -16.2958 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 |  | BD017085 | 1 | 2282.95 | 2325.72 | 42.77 | 2000 |  | 85540 | 86093.2711 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 86093.2711 | 101598.4476 | -15505.1765 | -15.2612 | OK
21 | 11 kV BSMMU RMU (F12) | C3101RM | 11 |  | BD017086 | 1 | 2299.99 | 2390.79 | 90.8 | 2000 |  | 181600 | 182774.5854 | Paribag |  |  |  |  | 11 kV BSMMU RMU (F12) | 182774.5854 | 159898.4943 | 22876.0911 | 14.3066 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 |  | BD017087 | 1 | 4503.32 | 4595.64 | 92.32 | 2000 |  | 184640 | 185834.2481 | Paribag |  |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 185834.2481 | 231553.1807 | -45718.9326 | -19.7445 | OK
23 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 |  | BD017088 | 1 | 1117.1 | 1140.23 | 23.13 | 2000 |  | 46260 | 46559.2088 | Paribag |  |  |  |  | 11 kV BCS Academy RMU (F14) | 46559.2088 | 60542.3562 | -13983.1474 | -23.0965 | OK
24 | Spare |  | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | C310113 | 11 |  | BD017090 | 1 | 2155.2 | 2367.14 | 211.94 | 2000 |  | 423880 | 426621.648 | Paribag |  |  |  |  | BSMMU Super Specialist Hospital RMU | 426621.648 | 459157.5154 | -32535.8675 | -7.086 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKD4418 | 1 | 2965 | 3035.81 | 70.81 | 100 |  | 7081 | 7126.7998 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 7126.7998 | 0 | 7126.7998 | #DIV/0! | #DIV/0!
27 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 1877.04 | 1915.93 | 38.89 | 100 |  | 3889 | 3914.154 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 3914.154 | 12158.0799 | -8243.9259 | -67.8062 | CHECK
|  |  | 10: Grand Total | 3940634.9574 | 3915310.8 | 3940634.9574 | 0.6468
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 1523209.5776
[6 empty] | Paribag | at 33 KV level |  | 2417425.3798
[6 empty] | Total = |  |  | 3940634.9574 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 |  | 132 |  | 8993518 | 1 | 1173.431 | 1188.499 | 15.068 | 960000 | 0 | 14465280
|  |  | 132 |  |  | 1 | 70.101 | 70.101 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 |  | 132 |  | 5014660 | 1 | 350.838 | 366.009 | 15.171 | 960000 | 0 | 14564160
|  |  | 132 |  |  | 1 | 4.408 | 4.408 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 |  | 132 |  | 38992597 | 1 | 718.358 | 752.493 | 34.135 | 1440000 | 0 | 49154400
|  |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 78183840
|  |  | 10: Net Total | 78183840
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 |  | 132 | RECEIVE | 6604452 | 1 | 326613 | 340574 | 13961 | 1000 | 13961000
|  |  | 132 |  |  | 1 | 6797 | 6797 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) |  | 132 |  |  | 1 | 4535442 | 4584458 | 49016 | 1000 | 49016000
|  |  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar |  | 132 |  |  | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  |  | 1 | 617805 | 645542 | 27737 | 1000 |  | 27737000
| Kallyanpur-2 |  | 132 |  | 6604428 | 1 | 424205 | 437971 | 13766 | 1000 | 13766000
|  |  | 132 |  |  | 1 | 7153 | 7153 | 0 | 1000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 76743000 | 27737000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 49006000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
6 | Kamrangirchar |  | 132 |  | SIEM491 | 1 | 7584 | 7584 | 0 | 1000 | 0
|  |  | 132 |  | SIEM491 | 1 | 617805 | 645542 | 27737 | 1000 |  | 27737000
|  |  | 7: 0; 8: 0; 10: Total |  | 27737000
| LALBAGH 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 | NET IMPORT | SIEM494 | 1 | 2275159 | 2299916 | 24757 | 1000 |  | 24757000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | SIEM499 | 1 | 2386769 | 2411035 | 24266 | 1000 |  | 24266000
|  |  | 10: Total |  | 49023000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 78183840; 6: EXPORT TO OTHER S/S; 9=8-7: 27737000 | 132 KV NET IMPORT |  | 50446840
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 50446840 | 132/33 KV GT LV SIDE |  | 48971000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1475840
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.926%
| 132 KV TOTAL IMPORT |  | 4: 78183840
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | SIEM0517 | 1 | 2274394 | 2299099 | 24705 | 1000 | 24705000
16 | 132/33 kV GT-2 Incoming (LV) |  | 33 |  | SIEM0518 | 1 | 2360827 | 2385093 | 24266 | 1000 | 24266000
|  |  | 7: 0; 8: 0; 10: Total | 48971000 |  | 0
| LALBAGH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SIEM0502 | 1 | 856934 | 863359 | 6425 | 2000 |  | 12850000 | 12877960.4874 |  | 25769951.4376 | Lalbagh New 33/11 kv ss | -0.06039 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 12877960.4874 | 13325783.2033 | -447822.716 | -3.3606 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SIEM0501 | 1 | 850759 | 857191 | 6432 | 2000 |  | 12864000 | 12891990.9502 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 12891990.9502 | 13610205.4512 | -718214.501 | -5.277 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 25714000 | 25769951.4376 | [5 empty] | 33 KV Feeders | 25769951.4376 | 26935988.6545 | -1166037.217 | -4.3289 | OK
9 | Spare |  | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 6195451.4967 | Mitford 33/11 kv ss | 0.3109 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 |  | 33 |  | SIEM0513 | 1 | 327222 | 328991 | 1769 | 2000 |  | 3538000 | 3545698.3817 | [5 empty] | Mitford Circuit-1 | 3545698.3817 | 4498678.6524 | -952980.2708 | -21.1836 | OK
12 | Azimpur Circuit-1 |  | 33 |  | SIEM0503 | 1 | 74595 | 76611 | 2016 | 2000 |  | 4032000 | 4040773.2829 |  | 5920855.2965 | Azimpur 33/11 kv ss | 1.8226 |  | Azimpur Circuit-1 | 4040773.2829 | 420624.451 | 3620148.8319 | 860.6606 | FAULT
15 | Azimpur Circuit-2 |  | 33 |  | SIEM0507 | 1 | 90074 | 91012 | 938 | 2000 |  | 1876000 | 1880082.0136 | [5 empty] | Azimpur Circuit-2 | 1880082.0136 | 6952321.2835 | -5072239.2699 | -72.9575 | CHECK
17 | Lalbagh old |  | 33 |  | SIEM0509 | 1 | 239469 | 244897 | 5428 | 2000 |  | 10856000 | 10879621.716 |  | 10879621.716 | Lalbagh old 33/11 kv ss | 0.31895 |  | Lalbagh old | 10879621.716 | 10892170.3081 | -12548.5921 | -0.11521 | OK
18 | Mitford Circuit-2 |  | 33 |  | SIEM0511 | 1 | 363079 | 364401 | 1322 | 2000 |  | 2644000 | 2649753.1151 | [5 empty] | Mitford Circuit-2 | 2649753.1151 | 3589328.6488 | -939575.5337 | -26.1769 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKC7982 | 1 | 7561.41 | 7621.11 | 59.7 | 120 |  | 7164 | 7179.5882 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-1 | 7179.5882 | 11048.0017 | -3868.4134 | -35.0146 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHU02670 | 1 | 27089.5 | 27106.6 | 17.1 | 120 |  | 2052 | 2056.465 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-2 | 2056.465 | 0 | 2056.465 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 22955216 | 23005164.5624 | [5 empty] | 0 | 23005164.5624 | 26364171.3455 | -3359006.783 | -12.7408 | OK
|  |  | 9=8-7: Grand Total | 48775116 | 48669216 | 48775116 | 0.21759
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK98833 | 1 | 608591 | 615022.5 | 6431.5 | 2000 | 12863000 |  | 12883022.6834
11 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK98832 | 1 | 605422.8 | 611856.25 | 6433.45 | 2000 | 12866900 |  | 12886928.7542
|  |  | 7: 0; 8: 0; 10: Total | 25729900 |  | 25769951.4376
| LALBAGH 11 kV SIDE |  | 7: 0; 8: 0
3 | Chata Mosjid |  | 11 |  |  | 1 | 178961 | 182187.1 | 3226.1 | 1000 |  | 3226100 | 3224151.7427 | Kamrangirchar |  | 275 |  |  | Chata Mosjid | 3224151.7427 | 2448059.1892 | 776092.5534 | 31.7024 | OK
4 | AC mosjid | A3109X | 11 |  |  | 1 | 10394.041 | 11622.59 | 1228.549 | 1000 |  | 1228549 | 1227807.0733 | Lalbag |  | 200 |  |  | AC mosjid | 1227807.0733 | 1300312.4106 | -72505.3373 | -5.576 | OK
5 | Kazi Reaz Uddin Road | A3109K | 11 |  |  | 1 | 27738.754 | 29890.208 | 2151.454 | 1000 |  | 2151454 | 2150154.7266 | Lalbag |  | 75 |  |  | Kazi Reaz Uddin Road | 2150154.7266 | 2361420.5589 | -211265.8323 | -8.9466 | OK
6 | Nazimuddin | A3109M | 11 |  |  | 1 | 7287.9168 | 7907.4712 | 619.5544 | 1000 |  | 619554.4 | 619180.2481 | Lalbag |  | 25 |  |  | Nazimuddin | 619180.2481 | 762703.8683 | -143523.6201 | -18.8177 | OK
7 | Kamal Bagh | A3109U | 11 |  |  | 1 | 20174.008 | 21734.92 | 1560.912 | 1000 |  | 1560912 | 1559969.3577 | Lalbag |  | 225 |  |  | Kamal Bagh | 1559969.3577 | 2099983.5161 | -540014.1584 | -25.7152 | OK
8 | Rahamatganj | A3109B | 11 |  |  | 1 | 18036.49 | 20350.666 | 2314.176 | 1000 |  | 2314176 | 2312778.458 | Lalbag |  |  |  |  | Rahamatganj | 2312778.458 | 2488587.0183 | -175808.5603 | -7.0646 | OK
9 | Water Works 11kV Sw/S-1 |  | 11 |  |  | 1 | 4448.2884 | 6144.4552 | 1696.1668 | 1000 |  | 1696166.8 | 1695142.4767 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-1 | 1695142.4767 | 1852690.3414 | -157547.8647 | -8.5037 | OK
12 | City Colony | A3109J | 11 |  |  | 1 | 1465.432 | 3450.24 | 1984.808 | 1000 |  | 1984808 | 1983609.3649 | Lalbag |  | 29263.742 |  |  | City Colony | 1983609.3649 | 2200330.7905 | -216721.4256 | -9.8495 | OK
13 | Water Works 11kV Sw/S-2 |  | 11 |  |  | 1 | 7701.988 | 10455.924 | 2753.936 | 1000 |  | 2753936 | 2752272.8848 | Lalbag |  |  |  |  | Water Works 11kV Sw/S-2 | 2752272.8848 | 2717279.1674 | 34993.7173 | 1.2878 | OK
14 | Chun Goli | A3109H | 11 |  |  | 1 | 1678.5962 | 2584.3304 | 905.7342 | 1000 |  | 905734.2 | 905187.2228 | Lalbag |  |  |  |  | Chun Goli | 905187.2228 | 976536.6596 | -71349.4369 | -7.3064 | OK
15 | Alir Ghat | A3109L | 11 |  |  | 1 | 127347 | 129316.3 | 1969.3 | 1000 |  | 1969300 | 1968110.7302 | Lalbag |  |  |  |  | Alir Ghat | 1968110.7302 | 2047969.8743 | -79859.144 | -3.8994 | OK
16 | Club Ghat | A3109C | 11 |  |  | 1 | 24630.07 | 27337.512 | 2707.442 | 1000 |  | 2707442 | 2705806.9627 | Lalbag |  |  |  |  | Club Ghat | 2705806.9627 | 2856757.5327 | -150950.57 | -5.284 | OK
17 | Debidas Ghat | A3109V | 11 |  |  | 1 | 1744.5846 | 4371.9 | 2627.3154 | 1000 |  | 2627315.4 | 2625728.7516 | Lalbag |  | 35045.236 |  |  | Debidas Ghat | 2625728.7516 | 2710169.0726 | -84440.321 | -3.1157 | OK
18 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 25729900 | 25745447.8 | 25729900 | -0.06039
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 3224151.7427
[6 empty] | Lalbag | at 33 KV level |  | 22505748.2573
[6 empty] | Total = |  |  | 25729900 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old |  | 33 | 0 | SIEM0509 | 1 | 239469 | 244897 | 5428 | 2000 | 0 | 10856000 | 10879621.716
|  |  | 10: Total |  | 10856000 | 10879621.716 | 0.21759
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 |  | 33 | 0 | 30799098 | 1 | 1760.66 | 1760.74 | 0.08 | 240000 | 0 | 19200 | 19183.3131
|  |  | 10: Total |  | 19200 | 19183.3131
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming |  | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0 | 10898805.0291
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 4: 10879621.716; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALBAGH OLD 33 KV NET IMPORT |  | 10898805.0291
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 19183.3131; 6: LALBAGH OLD 33 KV NET IMPORT; 9=8-7: 10898805.0291 | 33 KV TX HV SIDE |  | 10898805.0291
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 10898805.0291
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) |  | 11 |  | 8838010 | 1 | 88171.7 | 88171.7 | 0 | 1000 | 0 |  | 0
27 | 33/11 kV T1 Incoming (LV) |  | 11 |  | 06604426 | 1 | 36285.09 | 36460.24 | 175.15 | 16000 | 2802400 |  | 6869110.1146
28 | 33/11 kV T2 Incoming (LV) |  | 11 |  |  | 1 | 609117 | 610761 | 1644 | 1000 | 1644000 |  | 4029694.9145
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 4446400 |  | 10898805.0291
| LALBAGH OLD 11 KV SIDE |  | 7: 0; 8: 0
15 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | A319R | 11 |  | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2827636.56 | 2836655.3487 | Lalbag | 235 |  |  |  | Sowari Ghat | 2836655.3487 | 2802102.8851 | 34552.4636 | 1.2331 | OK
17 | Novo Kumar (Kara Odidoptor) | A3202 | 11 |  | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 541462.32 | 543189.3221 | Lalbag | 45 |  |  |  | Novo Kumar (Kara Odidoptor) | 543189.3221 | 622689.53 | -79500.2079 | -12.7672 | OK
19 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | A320A | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1203249.6 | 1207087.3824 | Lalbag | 100 |  |  |  | Eidgah | 1207087.3824 | 1369916.966 | -162829.5836 | -11.8861 | OK
23 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | A3201 | 11 |  |  | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 2045524.32 | 2052048.5501 | Lalbag | 170 |  |  |  | Modumoti | 2052048.5501 | 2241682.3081 | -189633.7579 | -8.4594 | OK
25 | Lalbagh O/H | A320Y | 11 |  | 61389152 | 1 | 442711 | 443210 | 499 | 1000 | Estimated | 962599.68 | 965669.9059 | Lalbag | 80 |  |  |  | Lalbagh O/H | 965669.9059 | 1120841.154 | -155171.2481 | -13.8442 | OK
26 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | A320G | 11 |  | 61389109 | 1 | 404617 | 405569 | 952 | 1000 |  | 952000 | 955036.4181 | Lalbag |  |  |  |  | Water Works 11 kV Sw/S-2 | 955036.4181 | 858393.0961 | 96643.3221 | 11.2586 | OK
31 | Islambagh | A320D | 11 |  | 61389186 | 1 | 502493 | 503360 | 867 | 1000 |  | 867000 | 869765.3094 | Lalbag |  |  |  |  | Islambagh | 869765.3094 | 693124.8804 | 176640.429 | 25.4846 | OK
32 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | A320F | 11 |  | 61389202 | 1 | 15689 | 15746 | 57 | 1000 |  | 57000 | 57181.8023 | Lalbag |  |  |  |  | WASA Low Lift Pump | 57181.8023 | 43069.8986 | 14111.9037 | 32.7651 | OK
34 | Shahi Mosjid | D920M | 11 |  | 06604459 | 1 | 36418.54 | 36593.61 | 175.07 | 8000 |  | 1400560 | 1405027.1069 | Azimpur |  |  |  |  | Shahi Mosjid | 1405027.1069 | 1328075.3488 | 76951.7581 | 5.7942 | OK
35 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer |  | 0.415 |  | 5395822 | 1 | 60635.8 | 67756.97 | 7121.17 | 1 |  | 7121.17 | 7143.8831 | Lalbag |  |  |  |  | 33/0.4 kV Auxiliary Transformer | 7143.8831 | 13347.8624 | -6203.9793 | -46.4792 | CHECK
|  |  | 10: Grand Total | 10898805.0291 | 10864153.65 | 10898805.0291 | 0.31895
33/0.4 kV Auxiliary Transformer meter change at 30 April 2023
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Lalbag | at 33 KV level |  | 9493777.9222
[6 empty] | Azimpur | at 33 KV level |  | 1405027.1069
[6 empty] | Total = |  |  | 10898805.0291 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 |  | 33 | 0 | SIEM0513 | 1 | 327222 | 328991 | 1769 | 2000 | 0 | 3538000 | 3545698.3817
18 | Mitford Circuit-2 |  | 33 | 0 | SIEM0511 | 1 | 363079 | 364401 | 1322 | 2000 | 0 | 2644000 | 2649753.1151
|  |  | 10: Total | 0 | 6182000 | 6195451.4967
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 1260.55 | 1267.61 | 7.06 | 540000 |  | 3812400
| Lalbagh Circuit-2 |  | 33 |  | DHK68131 | 1 | 1307.9 | 1310.98 | 3.08 | 540000 |  | 1663200
|  |  | 7: 0; 8: 0; 10: Total |  | 5475600
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
1 | Kumartuly Circuit-1 |  | 33 |  | DHK-66493 | 1 | 1291902 | 1304145 | 12243 | 180 |  | 2343942 |  |  | From Kumertully End
6 | Kumartuly Circuit-2 |  | 33 |  | DHK-60914 | 1.1 | 776528.4 | 786422.9 | 9894.5 | 180 |  | 1954260 |  |  | From Kumertully End
|  |  | 7: 0; 8: 0; 10: Total |  | 4298202
[7 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-66494 | 1 | 2992345 | 3027889 | 35544 | 180 | From Downstream | 3975161.4
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHKA-2193 | 1 | 636.7265 | 655.1572 | 18.4307 | 180000 |  | 3317531.4
|  |  | 10: Total |  | 7292692.8
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 4: 6195451.4967; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7292692.8
| IMPORT-2 |  | 4: 4298202; 6: 33 KV NET IMPORT; 9=8-7: 7292692.8 | 33 KV TX HV SIDE |  | 7292692.8
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 10493653.4967
11 KV SIDE of___MIDFORT 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK-66484 | 1 | 2838299 | 2859740 | 21441 | 180 | 3859380 |  | 3920926.4607
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK-66476 | 1 | 2119739 | 2138177 | 18438 | 180 | 3318840 |  | 3371766.3393
|  |  | 7: 0; 8: 0; 10: Total | 7178220 |  | 7292692.8
| MIDFORT 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | A319Z | 11 |  | DHK-60904 | 1 | 997275.1 | 1004599.4 | 7324.3 | 60 |  | 439458 | 440824.2804 | Lalbag |  |  |  |  | Chawk Bazar | 440824.2804 | 524398.7147 | -83574.4343 | -15.9372 | OK
10 | Spare |  | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | B688D | 11 |  | DHK-66485 | 1 | 863260 | 867960 | 4700 | 60 |  | 282000 | 282876.7415 | Bangshal |  |  |  |  | Chatrabas | 282876.7415 | 339280.009 | -56403.2675 | -16.6244 | OK
12 | Begum Bazar | B678G | 11 |  | DHK-66481 | 1 | 3787572 | 3818719 | 31147 | 60 |  | 1868820 | 1874630.1846 | Bangshal |  |  |  |  | Begum Bazar | 1874630.1846 | 2344342.8516 | -469712.6671 | -20.036 | OK
13 | SCC ROAD | B688R | 11 |  | DHK-60901 | 1 | 157171.5 | 179474.4 | 22302.9 | 60 |  | 1338174 | 1342334.3996 | Bangshal |  |  |  |  | SCC ROAD | 1342334.3996 | 1631812.3089 | -289477.9093 | -17.7397 | OK
16 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | B619A | 11 |  | DHK-61104 | 1 | 733048.2 | 745406.5 | 12358.3 | 60 |  | 741498 | 743803.3265 | Bangshal |  |  |  |  | Armanitola | 743803.3265 | 925763.6241 | -181960.2976 | -19.6552 | OK
18 | Mitford Hospital (RMU) |  | 11 |  | DHK-61101 | 1 | 418515.6 | 425420.5 | 6904.9 | 60 |  | 414294 | 415582.0452 | Bangshal |  |  |  |  | Mitford Hospital (RMU) | 415582.0452 | 494194.5928 | -78612.5477 | -15.9072 | OK
19 | Emamganj | B688I | 11 |  | DHK-68130 | 1 | 1478.28 | 1494.26 | 15.98 | 60000 |  | 958800 | 961780.9211 | Bangshal |  |  |  |  | Emamganj | 961780.9211 | 1149360.3885 | -187579.4674 | -16.3203 | OK
20 | Kamal Dho Road | A319T | 11 |  | DHK-68129 | 1 | 1226.82 | 1226.83 | 0.01 | 60000 |  | 600 | 601.8654 | Lalbag |  |  |  |  | Kamal Dho Road | 601.8654 | 0 | 601.8654 | #DIV/0! | #DIV/0!
21 | Spare |  | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | B688P | 11 |  | DHK-68127 | 1 | 1597.26 | 1617.63 | 20.37 | 60000 |  | 1222200 | 1225999.835 | Bangshal |  |  |  |  | Panghat | 1225999.835 | 1414831.0491 | -188831.2141 | -13.3466 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | U0004460 | 1 | 5717.83 | 5760.29 | 42.46 | 100 |  | 4246 | 4259.2009 | Bangshal |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4259.2009 | 4363.7626 | -104.5617 | -2.3961 | OK
|  |  | 10: Grand Total | 7292692.8 | 7270090 | 7292692.8 | 0.3109
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 6851266.6542
[6 empty] | Lalbag | at 33 KV level |  | 441426.1458
[6 empty] | Total = |  |  | 7292692.8 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 |  | 33 | 0 | SIEM0503 | 1 | 74595 | 76611 | 2016 | 2000 | 0 | 4032000 | 4040773.2829
15 | Azimpur Circuit-2 |  | 33 | 0 | SIEM0507 | 1 | 90074 | 91012 | 938 | 2000 | 0 | 1876000 | 1880082.0136
|  |  | 10: Total | 0 | 5908000 | 5920855.2965
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 |  | 33 | 0 | BD001822 | 1 | 2057.42 | 2072.37 | 14.95 | 240000 | 0 | 3588000 | 3592225.1593
20 | Azimpur Circuit-2 |  | 33 | 0 | BD001857 | 1 | 1867.53 | 1885.43 | 17.9 | 240000 | 0 | 4296000 | 4301058.8864
|  |  | 10: Total | 0 | 7884000 | 7893284.0458
|  |  | 10: GRAND TOTAL |  | 13792000 | 13814139.3422
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 828004 | 850372 | 22368 | 180 |  | 4026240
| Dhanmondi Circuit-1 |  | 33 |  | DHK68131 | 1 | 1220950 | 1227584 | 6634 | 540 |  | 3582360
| Dhanmondi Circuit-2 |  | 33 |  |  | 1 | 161289 | 169233 | 7944 | 540 |  | 4289760
| Lalbagh Circuit-2 |  | 33 |  | DHK68132 | 1 | 999490 | 1009914 | 10424 | 180 |  | 1876320
|  |  | 7: 0; 8: 0; 10: Total |  | 13774680 | #REF!
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 |  | 3: 33; 6: 1; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK61094 | 1 | 437555 | 479842 | 42287 | 180 |  | 7611660
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK60919 | 1 | 543166 | 577452 | 34286 | 180 |  | 6171480
|  |  | 10: Total |  | 13783140 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 4: 5920855.2965; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | AZIMPUR 33 KV NET IMPORT |  | 13814139.3422
| DHANMONDI 33 kV SIDE |  | 4: 7893284.0458; 6: AZIMPUR 33 KV NET IMPORT; 9=8-7: 13814139.3422 | 33 KV TX HV SIDE |  | 13783140
[11 empty] | LOSS UNITS=> |  | 30999.3422
[11 empty] | LOSS % IN => |  | 0.2244%
| TOTAL IMPORT |  | 4: 13814139.3422
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) |  | 11 |  | DHK60909 | 1 | 440607 | 482949 | 42342 | 180 | 7621560 |  | 7621383.0903
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK60902 | 1 | 559018 | 593423 | 34405 | 180 | 6192900 |  | 6192756.252
|  |  | 7: 0; 8: 0; 10: Total | 13814460 |  | 13814139.3422
| AZIMPUR 11 KV SIDE |  | 7: 0; 8: 0
7 | Chadni chwok |  | 11 |  | DHK60916 | 1 | 444571 | 454152 | 9581 | 60 |  | 574860 | 585337.5096 | Paribag |  |  |  |  | Chadni chwok | 585337.5096 | 659849.4891 | -74511.9795 | -11.2923 | OK
8 | BGB |  | 11 |  | DHK61090 | 1 | 714040 | 716307 | 2267 | 60 |  | 136020 | 138499.1268 | Jigatola |  |  |  |  | BGB | 138499.1268 | 715312.2841 | -576813.1572 | -80.6379 | CHECK
9 | Pari Bibi Mazar | D920P | 11 |  | DHK61091 | 1 | 888592 | 919902 | 31310 | 60 |  | 1878600 | 1912839.727 | Azimpur |  |  |  |  | Pari Bibi Mazar | 1912839.727 | 2177491.1776 | -264651.4506 | -12.154 | OK
10 | Azimpur | D901P | 11 |  | DHK61086 | 1 | 356695 | 383398 | 26703 | 60 |  | 1602180 | 1631381.6426 | Azimpur |  |  |  |  | Azimpur | 1631381.6426 | 1038683.4379 | 592698.2047 | 57.0624 | FAULT
11 | Aazd | D901Z | 11 |  | DHK61089 | 1 | 47477 | 64260 | 16783 | 60 |  | 1006980 | 1025333.4123 | Azimpur |  |  |  |  | Aazd | 1025333.4123 | 1260231.211 | -234897.7988 | -18.6393 | OK
12 | Dayra Sharif | D966D | 11 |  | DHK61088 | 1 | 566604 | 579254 | 12650 | 60 |  | 759000 | 772833.6808 | Azimpur |  |  |  |  | Dayra Sharif | 772833.6808 | 1018901.3032 | -246067.6224 | -24.1503 | OK
13 | Naya palton | D966U | 11 |  | DHK86065 | 1 | 1983.32 | 2006.64 | 23.32 | 60000 |  | 1399200 | 1424702.0899 | Azimpur |  |  |  |  | Naya palton | 1424702.0899 | 1594707.0602 | -170004.9703 | -10.6606 | OK
16 | Viqarunnisa Noon School | D966V | 11 |  | DHK66477 | 1 | 1680319 | 1696824 | 16505 | 60 |  | 990300 | 1008349.3994 | Azimpur |  |  |  |  | Viqarunnisa Noon School | 1008349.3994 | 1357200.0802 | -348850.6809 | -25.7037 | OK
17 | Subal Das Lane | D966W | 11 |  | DHK66480 | 1 | 4079743 | 4107768 | 28025 | 60 |  | 1681500 | 1712147.3443 | Azimpur |  |  |  |  | Subal Das Lane | 1712147.3443 | 1414604.6799 | 297542.6644 | 21.0336 | OK
18 | Lalbagh | D920L | 11 |  | DHK61093 | 1 | 844380 | 874634 | 30254 | 60 |  | 1815240 | 1848324.9154 | Azimpur |  |  |  |  | Lalbagh | 1848324.9154 | 2271183.2515 | -422858.3361 | -18.6184 | OK
19 | Zahrul Haque Hall | D366J | 11 |  | DHK66497 | 1 | 1273675 | 1281591 | 7916 | 60 |  | 474960 | 483616.7128 | Ramna |  |  |  |  | Zahrul Haque Hall | 483616.7128 | 594434.9453 | -110818.2324 | -18.6426 | OK
20 | Eden College | D966E | 11 |  | DHK60917 | 1 | 957512 | 962562 | 5050 | 60 |  | 303000 | 308522.5366 | Azimpur |  |  |  |  | Eden College | 308522.5366 | 489031.3622 | -180508.8256 | -36.9115 | OK
21 | Nilkhet/ PWD-01 | D902N | 11 |  | DHK60918 | 1 | 510949 | 519580 | 8631 | 60 |  | 517860 | 527298.6165 | Azimpur |  |  |  |  | Nilkhet/ PWD-01 | 527298.6165 | 634848.7543 | -107550.1378 | -16.9411 | OK
22 | BUET | D366BU | 11 |  | DHK66496 | 1 | 1008669 | 1015739 | 7070 | 60 |  | 424200 | 431931.5513 | Ramna |  |  |  |  | BUET | 431931.5513 | 807548.0045 | -375616.4532 | -46.5132 | CHECK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIG2780 | 1 | 401869 | 404836 | 2967 | 1 |  | 2967 | 3021.0771 | Azimpur |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 3021.0771 | 4277.027 | -1255.9499 | -29.365 | OK
|  |  | 10: Grand Total | 13814139.3422 | 13566867 | 13814139.3422 | 1.8226
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 585337.5096
[6 empty] | Jigatola | at 33 KV level |  | 138499.1268
[6 empty] | Azimpur | at 33 KV level |  | 12174754.4418
[6 empty] | Ramna | at 33 KV level |  | 915548.2641
[6 empty] | Total = |  |  | 13814139.3422 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar |  | 132 |  | 38992596 | 1 | 991.183 | 1025.378 | 34.195 | 1440000 | 0 | 49240800
|  |  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 49240800
|  |  | 10: Net Total | 49240800
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj |  | 132 | RECEIVE |  | 1 | 5848.3 | 5899.76 | 51.46 | 960000 | 49401600
|  |  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh |  | 132 |  |  | 1 | 3152.31 | 3181.25 | 28.94 | 960000 | 27782400
|  |  | 132 |  |  | 1 | 7.84 | 7.84 | 0 | 960000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 77184000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 77184000
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
5 | 132 kV Jigatola-1 |  | 132 |  | 42003953362 | 1 | 261 | 278.28 | 17.28 | 1440000 |  | 24883200
6 | 132 kV Jigatola-2 |  | 132 |  | 42003953364 | 1 | 255.14 | 271.97 | 16.83 | 1440000 |  | 24235200
|  |  | 7: 0; 8: 0; 10: Total |  | 49118400
| KAMRANGIRCHAR 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | 30799138 | 1 | 3419.21 | 3428.7 | 9.49 | 960000 |  | 9110400
2 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 |  | 30799148 | 1 | 3396.81 | 3406.36 | 9.55 | 960000 |  | 9168000
7 | 132/33 kV, 50/75 MVA GT-3 (HV) |  | 132 |  | BD001910 | 1 | 1199.08 | 1208.83 | 9.75 | 960000 |  | 9360000
|  |  | 10: Total |  | 27638400 | 76756800
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 4: 49240800; 6: EXPORT TO OTHER S/S; 9=8-7: 49118400 | 132 KV NET IMPORT |  | 27904800
| FROM LALBAGH 132/33 KV GRID |  | 4: 27782400; 6: 132 KV NET IMPORT; 9=8-7: 27904800 | 33 KV NET IMPORT |  | 27590400
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 314400
[11 empty] | LOSS % IN => |  | 1.127%
| 132 KV TOTAL IMPORT |  | 4: 77023200
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001914 | 1 | 2412.91 | 2432.43 | 19.52 | 480000 | 9369600 |  | 9476369.1023
14 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | 30799094 | 1 | 6938.61 | 6957.76 | 19.15 | 480000 | 9192000 |  | 9296745.3027
19 | 132/33 kV GT-2 Incoming |  | 33 |  | 30799150 | 1 | 6838.19 | 6857 | 18.81 | 480000 | 9028800 |  | 9131685.595
|  |  | 7: 0; 8: 0; 10: Total | 27590400 |  | 27904800
| KAMRANGIRCHAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) |  | 33 |  | 30799129 | 1 | 6951.01 | 6986.34 | 35.33 | 240000 |  | 8479200 | 8471830.6275 |  | 26252363.9145 | Kamrangir Char 33/11 kv ss | 1.8667 |  | 33/11 kV, 20/28 MVA T31 (HV) | 8471830.6275 | 8820908.2726 | -349077.6451 | -3.9574 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) |  | 33 |  | 30799110 | 1 | 6846.9 | 6881.97 | 35.07 | 240000 |  | 8416800 | 8409484.8601 | [5 empty] | 33/11 kV, 20/28 MVA T32 (HV) | 8409484.8601 | 8667709.323 | -258224.4629 | -2.9792 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) |  | 33 |  | 30799137 | 1 | 3989.84 | 4028.92 | 39.08 | 240000 |  | 9379200 | 9371048.4269 | [5 empty] | 33/11 kV, 20/28 MVA T-33 (HV) | 9371048.4269 | 8220081.142 | 1150967.2849 | 14.0019 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 26275200 | 26252363.9145 | [5 empty] | 33 KV Feeders | 26252363.9145 | 25708698.7376 | 543665.1768 | 2.1147 | OK
8 | Dhaka Uddyan 2 |  | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 2397.9141 | Dhaka Uddan 33/11 kv ss | 0.39969 |  | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 |  | 33 |  | BD001912 | 1 | 428.23 | 428.24 | 0.01 | 240000 |  | 2400 | 2397.9141 | [5 empty] | Dhaka Uddyan 1 | 2397.9141 | 0 | 2397.9141 | #DIV/0! | #DIV/0!
10 | Spare Feeder -2 |  | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) |  | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 |  | 33 |  | 30799098 | 1 | 1760.66 | 1760.74 | 0.08 | 240000 |  | 19200 | 19183.3131 |  | 1335638.1714 | Kamrangir Char-2 33/11 kv ss | 0.26743 |  | Lalbagh Circuit-1 | 19183.3131 | 201073.6214 | -181890.3084 | -90.4596 | CHECK
16 | Zigatola Circuit-1 (BGB-1) |  | 33 |  | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 |  | 0 | 0 | [5 empty] | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 |  | 33 |  | 30799147 | 1 | 1597.96 | 1603.45 | 5.49 | 240000 |  | 1317600 | 1316454.8583 |  | 0 | BGB 33/11 kv ss | 0.27825 |  | Kamrangir Char-2 | 1316454.8583 | 6250038.3989 | -4933583.5405 | -78.9369 | CHECK
22 | Zigatola Circuit-2 (BGB-2) |  | 33 |  | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Grid Has No Reading | Zigatola Circuit-2 (BGB-2) | 0 | 19389.2421 | -19389.2421 | -100 | CHECK
|  |  | 10: Total |  | 1339200 | 1338036.0855 | [5 empty] | 0 | 1338036.0855 | 6470501.2624 | -5132465.1768 | -79.321 | CHECK
|  |  | 9=8-7: Grand Total | 27590400 | 27614400 | 27590400 | -0.086911
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 8449200 |  | 8495770.0755
11 | 33/11 kV T-32 Incoming |  | 11 |  | 6604433 | 1 | 7720.18 | 7767.12 | 46.94 | 180000 | 8449200 |  | 8495770.0755
22 | 33/11 kV T-33 Incoming |  | 11 |  | DHK 95817 | 1 | 4696130 | 4747297 | 51167 | 180 | 9210060 |  | 9260823.7634
|  |  | 7: 0; 8: 0; 10: Total | 26108460 |  | 26252363.9145
| KAMRANGIRCHAR 11 kV SIDE |  | 7: 0; 8: 0
4 | Rasulpur | F120R | 11 |  | HA-021101042-02 | 1 | 96619539 | 97733809 | 1114270 | 1 |  | 1114270 | 1135070.1317 | Kamrangirchar |  | 224 |  |  | Rasulpur | 1135070.1317 | 1665082.8173 | -530012.6857 | -31.831 | OK
5 | Bheribadh | F120B | 11 |  | HA-021101105-02 | 1 | 71909539 | 74035356 | 2125817 | 1 |  | 2125817 | 2165499.7281 | Kamrangirchar |  | 120 |  |  | Bheribadh | 2165499.7281 | 2508479.0993 | -342979.3712 | -13.6728 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 |  | 30799521 | 1 | 2651.27 | 2655.72 | 4.45 | 60000 |  | 267000 | 271984.1018 | Kamrangirchar |  | 104 |  |  | Panna Tower 11 KV Faridpur Tower Express | 271984.1018 | 253194.3598 | 18789.742 | 7.4211 | OK
8 | Panna Battery Express | F140E | 11 |  | DHK15431 | 1 | 5329.54 | 5345.3 | 15.76 | 60000 |  | 945600 | 963251.5607 | Kamrangirchar |  | 34.6667 |  |  | Panna Battery Express | 963251.5607 | 788120.5732 | 175130.9874 | 22.2213 | OK
9 | Eidgah | F140I | 11 |  | 30799460 | 1 | 5487.62 | 5523.86 | 36.24 | 60000 |  | 2174400 | 2214989.6293 | Kamrangirchar |  | 154.6667 |  |  | Eidgah | 2214989.6293 | 2418400.8037 | -203411.1744 | -8.411 | OK
10 | Bot Tola Mazar | D840L | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | F140H | 11 |  | HA-021101055-02 | 1 | 7396376 | 9989092 | 2592716 | 1 |  | 2592716 | 2641114.3542 | Kamrangirchar |  |  |  |  | Huzur Para | 2641114.3542 | 2153483.8082 | 487630.546 | 22.6438 | OK
13 | Kamrangirchar | F103K | 11 |  | HA-021101015-02 | 1 | 27010939 | 29348087 | 2337148 | 1 |  | 2337148 | 2380775.6541 | Kamrangirchar |  |  |  |  | Kamrangirchar | 2380775.6541 | 2064906.2609 | 315869.3931 | 15.297 | OK
14 | Munshihati | F140T | 11 |  | HA-021100854-02 | 1 | 55432498 | 56404546 | 972048 | 1 |  | 972048 | 990193.2667 | Kamrangirchar |  |  |  |  | Munshihati | 990193.2667 | 1294711.6864 | -304518.4197 | -23.5202 | OK
15 | Jhawchar | F140J | 11 |  | HA-021101028-02 | 1 | 4801619 | 6004029 | 1202410 | 1 |  | 1202410 | 1224855.4453 | Kamrangirchar |  |  |  |  | Jhawchar | 1224855.4453 | 1505628.0528 | -280772.6075 | -18.6482 | OK
16 | RMU Express | F140D | 11 |  | HA-021101248-02 | 1 | 7971838 | 8590513 | 618675 | 1 |  | 618675 | 630223.836 | Kamrangirchar |  |  |  |  | RMU Express | 630223.836 | 713470.7397 | -83246.9038 | -11.6679 | OK
17 | Koyla Ghat | F140C | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2067758.28 | 2106357.2232 | Kamrangirchar | 170 |  |  |  | Koyla Ghat | 2106357.2232 | 1907872.1438 | 198485.0794 | 10.4035 | OK
18 | Muslimbagh | F140M | 11 |  | HA-021100908-02 | 1 | 31186206 | 34050945 | 2864739 | 1 |  | 2864739 | 2918215.2206 | Kamrangirchar |  |  |  |  | Muslimbagh | 2918215.2206 | 1684632.0125 | 1233583.2081 | 73.2257 | FAULT
19 | Noyagaon | F140Y | 11 |  | HA-021101087-02 | 1 | 13945688 | 16193892 | 2248204 | 1 |  | 2248204 | 2290171.3321 | Kamrangirchar |  |  |  |  | Noyagaon | 2290171.3321 | 2533643.7042 | -243472.372 | -9.6096 | OK
20 | Nurbagh | F140N | 11 |  | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2250207.54 | 2292212.2723 | Kamrangirchar | 185 |  |  |  | Nurbagh | 2292212.2723 | 2098659.3582 | 193552.9141 | 9.2227 | OK
21 | Ali Nagar | F140A | 11 |  | HA-021101022-02 | 1 | 29006769 | 30998173 | 1991404 | 1 |  | 1991404 | 2028577.6342 | Kamrangirchar |  |  |  |  | Ali Nagar | 2028577.6342 | 2162413.4126 | -133835.7784 | -6.1892 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKE6223 | 1 | 43619.2 | 43796.79 | 177.59 | 120 |  | 21310.8 | 21708.6097 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 21708.6097 | 23301.1673 | -1592.5575 | -6.8347 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 26275200 | 25793707.62 | 26275200 | 1.8667
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 26275200
[6 empty] | Jigatola | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 26275200 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: TOTAL |  | 0 | 0
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old |  | 33 | 0 | 43998033 | 1 | 277.88 | 287.849 | 9.969 | 270000 |  | 2691630 | 2624835.8633
|  |  | 10: TOTAL |  | 2691630 | 2691630
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 |  | 33 | 0 | 0 | 1 | 79.33 | 79.33 | 0 | 360000 | 0 | 0 | 0
11 | BGB-2 |  | 33 | 0 | 0 | 1 | 299.67 | 326.06 | 26.39 | 360000 | 0 | 9500400 | 9475441.0826
|  |  | 10: Total | 0 | 9500400 | 9475441.0826
|  |  | 10: GRAND TOTAL |  | 12192030 | 12167071.0826
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 |  | 33 |  | 43998032 | 1 | 1047.72 | 1047.72 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old |  | 33 |  | 43998033 | 1 | 277.88 | 287.849 | 9.969 | 270000 | 2691630
| 33 kV Zigatola-1 |  | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 |  | 33 |  | 43998027 | 1 | 781.12 | 781.12 | 0 | 270000 | 0
| 33 kV Zigatola-2 |  | 33 |  | 43998031 | 1 | 398.008 | 433.992 | 35.984 | 270000 | 9715680
|  |  | 7: 0; 8: 0; 10: Total | 12407310 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BGB 33 KV SIDE |  | 7: 0; 8: 0
6 | 33/11 kV T1 |  | 33 |  | 43998028 | 1 | 857.502 | 867.256 | 9.754 | 270000 |  | 2633580
9 | 33/11 kV T2 |  | 33 |  | 43998029 | 1 | 846.088 | 882.002 | 35.914 | 270000 |  | 9696780
11 | 33/11 kV T3 |  | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 12330360
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 4: 12167071.0826; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BGB 33 KV NET IMPORT |  | 12167071.0826
|  |  | 6: BGB 33 KV NET IMPORT; 9=8-7: 12167071.0826 | 33 KV TX HV SIDE |  | 12330360
[11 empty] | LOSS UNITS=> |  | -163288.9174
[11 empty] | LOSS % IN => |  | -1.342%
| TOTAL IMPORT |  | 4: 12167071.0826
11 KV SIDE of___BGB 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming |  | 11 |  |  | 1 | 29743100 | 32273270 | 2530170 | 1 | 2530170 |  | 2581490.5435
29 | 33/11 kV T-2 Incoming |  | 11 |  |  | 1 | 26455760 | 36010820 | 9555060 | 1 | 9555060 |  | 9748869.4565
30 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 12085230 |  | 12330360
| BGB 11 KV SIDE |  | 7: 0; 8: 0
12 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | D920K | 11 |  |  | 1 | 12267110 | 12523740 | 256630 | 1 |  | 256630 | 257344.0613 | Azimpur |  |  |  |  | Nababgonj Park | 257344.0613 | 1028840.1279 | -771496.0666 | -74.987 | CHECK
16 | Kholamura Ghat | F1104O | 11 |  |  | 1 | 85905840 | 88803750 | 2897910 | 1 |  | 2897910 | 2905973.3033 | Kamrangirchar |  |  |  |  | Kholamura Ghat | 2905973.3033 | 3092402.2195 | -186428.9163 | -6.0286 | OK
17 | Khalpar | F1104L | 11 |  |  | 1 | 89399920 | 91426620 | 2026700 | 1 |  | 2026700 | 2032339.2009 | Kamrangirchar |  |  |  |  | Khalpar | 2032339.2009 | 1943499.6703 | 88839.5307 | 4.5711 | OK
18 | Shahidnagar | D920S | 11 |  |  | 1 | 21734350 | 23321150 | 1586800 | 1 |  | 1586800 | 1591215.1991 | Azimpur |  |  |  |  | Shahidnagar | 1591215.1991 | 1859313.6405 | -268098.4414 | -14.4192 | OK
19 | BGB 1 No Gate | D9104G | 11 |  |  | 1 | 36808688 | 37153410 | 344722 | 1 |  | 344722 | 345681.1733 | Azimpur |  |  |  |  | BGB 1 No Gate | 345681.1733 | 1312194.6593 | -966513.4859 | -73.6563 | CHECK
21 | Ganaktuli | D8104J | 11 |  |  | 1 | 26164070 | 26868220 | 704150 | 1 |  | 704150 | 706109.2655 | Jigatola |  |  |  |  | Ganaktuli | 706109.2655 | 871530.0895 | -165420.824 | -18.9805 | OK
22 | Thana |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | D8104L | 11 |  |  | 1 | 38561747 | 39081811 | 520064 | 1 |  | 520064 | 521511.0545 | Jigatola |  |  |  |  | Bot Tola Mazar | 521511.0545 | 2086773.692 | -1565262.6375 | -75.0087 | CHECK
24 | Sikder Medical | D8104K | 11 |  |  | 1 | 39247632 | 40142320 | 894688 | 1 |  | 894688 | 897177.4288 | Jigatola |  |  |  |  | Sikder Medical | 897177.4288 | 1152362.6885 | -255185.2597 | -22.1445 | OK
25 | Gas Field | F1104G | 11 |  |  | 1 | 60444680 | 62157430 | 1712750 | 1 |  | 1712750 | 1717515.6493 | Kamrangirchar |  |  |  |  | Gas Field | 1717515.6493 | 2221738.1672 | -504222.518 | -22.695 | OK
26 | Hazaribagh | D8104H | 11 |  |  | 1 | 44324280 | 45430730 | 1106450 | 1 |  | 1106450 | 1109528.647 | Jigatola |  |  |  |  | Hazaribagh | 1109528.647 | 1387872.6757 | -278344.0288 | -20.0554 | OK
27 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  |  | 1 | 2295.89 | 2337.12 | 41.23 | 10 |  | 412.3 | 413.4472 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-1 | 413.4472 | 551.1966 | -137.7494 | -24.991 | OK
32 | 11/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  |  | 1 | 1866.97 | 1909.01 | 42.04 | 10 |  | 420.4 | 421.5697 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-2 | 421.5697 | 541.173 | -119.6033 | -22.1007 | OK
|  |  | 10: Grand Total | 12085230 | 12051696.7 | 12085230 | 0.27825
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Azimpur | at 33 KV level |  | 2195075.4507
[6 empty] | Kamrangirchar | at 33 KV level |  | 6655828.1535
[6 empty] | Jigatola | at 33 KV level |  | 3234326.3958
[6 empty] | Total = |  |  | 12085230 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 |  | 132 | 0 | 42003953362 | 1 | 261 | 278.28 | 17.28 | 1440000 | 0 | 24883200 | 0
6 | 132 kV Jigatola-2 |  | 132 | 0 |  | 1 | 255.14 | 271.97 | 16.83 | 1440000 | 0 | 24235200 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 49118400
|  |  | 10: Net Total | 49118400
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 |  | 132 | RECEIVE | 6604452 | 1 | 313.35 | 333.89 | 20.54 | 1200000 | 24648000
| 132 kV Kamrangirchar 2 |  | 132 |  |  | 1 | 306.5 | 326.11 | 19.61 | 1200000 | 23532000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 48180000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 48180000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| JIGATOLA 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  |  | 1 | 257.76 | 278.04 | 20.28 | 1200000 |  | 24336000
3 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  |  | 1 | 361.92 | 382.22 | 20.3 | 1200000 |  | 24360000
|  |  | 10: Total |  | 48696000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 49118400; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 49118400
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 49118400 | 33 KV NET IMPORT |  | 48290400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 828000
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.686%
| 132 KV TOTAL IMPORT |  | 4: 49118400
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  |  | 1 | 427.26 | 461.23 | 33.97 | 720000 | 24458400
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  |  | 1 | 600.91 | 634.01 | 33.1 | 720000 | 23832000
|  |  | 7: 0; 8: 0; 10: Total | 48290400 |  | 0
| JIGATOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  |  | 1 | 626.43 | 653.96 | 27.53 | 240000 |  | 6607200 | 6589841.9352 |  | 16377660.1963 | JIGATOLA NEW 3/11 KV SS | 0.62337 |  | 33/11 kV 28/35 MVA T-1 | 6589841.9352 | 5749868.4529 | 839973.4822 | 14.6086 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  |  | 1 | 505.05 | 525.07 | 20.02 | 240000 |  | 4804800 | 4792177.0992 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 4792177.0992 | 7562587.6149 | -2770410.5157 | -36.6331 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  |  | 1 | 411.33 | 432.2 | 20.87 | 240000 |  | 5008800 | 4995641.1619 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 4995641.1619 | 5066502.1022 | -70860.9403 | -1.3986 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 16420800 | 16377660.1963 | [5 empty] | 33 KV Feeders | 16377660.1963 | 18378958.17 | -2001297.9737 | -10.8891 | OK
2 | BGB-1 |  | 33 |  |  | 1 | 79.33 | 79.33 | 0 | 360000 |  | 0 | 0 |  | 9475441.0826 | BGB 33/11 kv ss | 0.27825 |  | BGB-1 | 0 | 7193.33 | -7193.33 | -100 | CHECK
2 | Spair |  | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 |  | 33 |  |  | 1 | 243.8 | 257.91 | 14.11 | 360000 |  | 5079600 | 5066255.1601 | [5 empty] | Dhaka Uddyan-1 | 5066255.1601 | 6168280.4817 | -1102025.3216 | -17.866 | OK
4 | Green Road -1 |  | 33 |  |  | 1 | 33.92 | 54 | 20.08 | 360000 |  | 7228800 | 7209808.9025 |  | 9468259.998 | Dhaka Uddan 33/11 kv ss | 0.39969 |  | Green Road -1 | 7209808.9025 | 3654211.644 | 3555597.2586 | 97.3013 | FAULT
9 | Green Road -2 |  | 33 |  |  | 1 | 77.32 | 88.88 | 11.56 | 360000 |  | 4161600 | 4150666.8782 | [5 empty] | Green Road -2 | 4150666.8782 | 4708034.4901 | -557367.612 | -11.8386 | OK
10 | Dhaka Uddyan-2 |  | 33 |  |  | 1 | 261.02 | 273.28 | 12.26 | 360000 |  | 4413600 | 4402004.8379 | [5 empty] | Dhaka Uddyan-2 | 4402004.8379 | 7775989.7385 | -3373984.9006 | -43.3898 | CHECK
11 | BGB-2 |  | 33 |  |  | 1 | 299.67 | 326.06 | 26.39 | 360000 |  | 9500400 | 9475441.0826 |  | 1608562.9424 | Jigatla Old 33/11 kv ss | -0.36418 |  | BGB-2 | 9475441.0826 | 7822746.3835 | 1652694.6991 | 21.1268 | OK
12 | Jigatola Old |  | 33 |  |  | 1 | 34.46 | 38.94 | 4.48 | 360000 |  | 1612800 | 1608562.9424 | [5 empty] | Jigatola Old | 1608562.9424 | 1956585.7621 | -348022.8197 | -17.7873 | OK
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 31996800 | 31912739.8037 | [5 empty] | 0 | 31912739.8037 | 32093041.83 | -180302.0263 | -0.56181 | OK
|  |  | 9=8-7: Grand Total | 48290400 | 48417600 | 48290400 | -0.26271
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 195.3 | 221.38 | 26.08 | 250000 | 6520000 |  | 6579318.8219
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 226.24 | 245.15 | 18.91 | 250000 | 4727500 |  | 4770510.6949
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 161.95 | 181.88 | 19.93 | 250000 | 4982500 |  | 5027830.6795
|  |  | 7: 0; 8: 0; 10: Total | 16230000 |  | 16377660.1963
| JIGATOLA 11 kV SIDE |  | 7: 0; 8: 0
| Salek Garden |  | 11 |  | 2761 | 1 | 718.18 | 749.07 | 30.89 | 60000 |  | 1853400 | 1864953.454 | Jigatola |  |  |  |  | Salek Garden | 1864953.454 | 2402250.1859 | -537296.7319 | -22.3664 | OK
4 | Jigatola Local |  | 11 |  | 2850 | 1 | 557.19 | 578.8 | 21.61 | 60000 |  | 1296600 | 1304682.5555 | Jigatola |  |  |  |  | Jigatola Local | 1304682.5555 | 1679891.0289 | -375208.4733 | -22.3353 | OK
5 | Modina Rayer Bazar |  | 11 |  | 2851 | 1 | 628.51 | 662.99 | 34.48 | 60000 |  | 2068800 | 2081696.183 | Switching | Grid has No Reading |  |  |  | Modina Rayer Bazar | 2081696.183 | 0 | 2081696.183 | #DIV/0! | #DIV/0!
6 | City College |  | 11 |  | 2784 | 1 | 596.23 | 617.99 | 21.76 | 60000 |  | 1305600 | 1313738.6584 | Jigatola |  |  |  |  | City College | 1313738.6584 | 1670267.593 | -356528.9345 | -21.3456 | OK
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office |  | 11 |  | 2836 | 1 | 467.42 | 488.7 | 21.28 | 60000 |  | 1276800 | 1284759.1292 | Jigatola |  |  |  |  | Post Office | 1284759.1292 | 1558395.1507 | -273636.0215 | -17.5588 | OK
11 | Leather Institute |  | 11 |  | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 |  | 0 | 0 | Jigatola | Grid has No Reading |  |  |  | Leather Institute | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Mina Bazar |  | 11 |  | 2853 | 1 | 229 | 237.44 | 8.44 | 60000 |  | 506400 | 509556.7223 | Jigatola |  |  |  |  | Mina Bazar | 509556.7223 | 661611.218 | -152054.4957 | -22.9825 | OK
13 | Mitali |  | 11 |  | 2852 | 1 | 519.49 | 536.6 | 17.11 | 60000 |  | 1026600 | 1032999.469 | Switching |  |  |  |  | Mitali | 1032999.469 | 2938155.2725 | -1905155.8035 | -64.8419 | CHECK
14 | Road-2 |  | 11 |  | 2839 | 1 | 742.81 | 774.77 | 31.96 | 60000 |  | 1917600 | 1929553.6546 | Jigatola |  |  |  |  | Road-2 | 1929553.6546 | 2419692.6635 | -490139.0089 | -20.2563 | OK
15 | SS-2 |  | 11 |  | 2838 | 1 | 352.5 | 387.95 | 35.45 | 60000 |  | 2127000 | 2140258.9817 | Jigatola |  |  |  |  | SS-2 | 2140258.9817 | 1225183.6827 | 915075.299 | 74.6888 | FAULT
16 | Spare |  | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar |  | 11 |  | 2843 | 1 | 596.66 | 620.73 | 24.07 | 60000 |  | 1444200 | 1453202.6428 | Jigatola |  |  |  |  | Bou Bazar | 1453202.6428 | 1833866.0032 | -380663.3604 | -20.7574 | OK
18 | BGB |  | 11 |  | 2764 | 1 | 201.95 | 214.64 | 12.69 | 60000 |  | 761400 | 766146.304 | Jigatola |  |  |  |  | BGB | 766146.304 | 453504.4167 | 312641.8873 | 68.9391 | FAULT
19 | Dhamondi-12 |  | 11 |  | 2763 | 1 | 487.48 | 499.01 | 11.53 | 60000 |  | 691800 | 696112.4417 | Dhanmondi |  |  |  |  | Dhamondi-12 | 696112.4417 | 1536140.9551 | -840028.5134 | -54.6843 | CHECK
|  |  | 10: Total | 16377660.1963 | 16276200 | 16377660.1963 | 0.62337
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Jigatola | at 33 KV level |  | 14891928.0319 | Including Switching
[6 empty] | Dhanmondi | at 33 KV level |  | 1485732.1644
[6 empty] | Total = |  |  | 16377660.1963 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [14 empty] | Month November-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | 4: CF; 5: Number; 7: 2023-04-01; 8: 2023-04-01 | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar |  | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 34.48 | 60000 | 0 | 2068800 | 2081696.183 |  | 0
13 | Mitali |  | 11 | 0 | 2852 | 1 | 519.49 | 536.6 | 17.11 | 60000 | 0 | 1026600 | 1032999.469 |  | 100
|  |  | 10: Total |  | 3095400 | 3114695.652
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 784728 | 789619.7227 | Dhanmondi
3 | 11 kV Madina Masjid Feeder |  | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1216328.4 | 1223910.5702 | Jigatola
3 | 11 kV Mitali |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1094343.6 | 1101165.3592 | Jigatola | Switching Total - Madina - Rayer Bazar
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.96 | 1884.96 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit |  | 33 | 0 | 214393/37-2711 | 1 | 35.6193 | 38.183 | 2.5637 | 1000 | Estimated | 1644300 | 1603495.878
|  |  | 10: Total |  | 1644300 | 1603495.878
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  |  | 3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 | NET IMPORT | DHK61073 | 1 | 4042.01 | 4048.77 | 6.76 | 240000 |  | 1622400
2 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
|  |  | 10: Total |  | 1622400
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 1603495.878
| Satmasjid 33 KV SIDE |  | 4: 1603495.878; 6: 33 KV NET IMPORT; 9=8-7: 1603495.878 | ZIGATOLA OLD 11 KV NET IMPORT |  | 1622400
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -18904.122
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.179%
| TOTAL IMPORT |  | 4: 1603495.878
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0
16 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0
17 | 33/11 kV T-1 Incoming |  | 11 |  | DHK61028 | 1.32 | 1873.29 | 1879.77 | 6.48 | 180000 | 1539648
|  |  | 7: 0; 8: 0; 10: Total | 1539648 |  | 1622400
| ZIGATOLA OLD 11 KV SIDE |  | 7: 0; 8: 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | D803D | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | D803E | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | D803I | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | D803R | 11 |  | DHK60946 | 1 | 1187.02 | 1199.27 | 12.25 | 60000 |  | 735000 | 732323.3006 | Jigatola |  |  |  |  | Simanto Square | 732323.3006 | 891294.9856 | -158971.6851 | -17.836 | OK
12 | Post Office | D803P | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | D803S | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | D803G | 11 |  | DHK61070 | 1 | 3493.18 | 3506.97 | 13.79 | 60000 |  | 827400 | 824386.8012 | Jigatola |  |  |  |  | Green Road Via Park | 824386.8012 | 963367.3565 | -138980.5553 | -14.4265 | OK
15 | PWD Quarters 11 kV Saleq Grand | D803A | 11 |  | DHK61028 | 1 | 3634.3 | 3635.35 | 1.05 | 60000 |  | 63000 | 62770.5686 | Jigatola |  |  |  |  | PWD Quarters 11 kV Saleq Grand | 62770.5686 | 73874.1801 | -11103.6115 | -15.0304 | OK
18 | Road No.-2 | D803T | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | D803H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | D803B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | D803C | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | D803M | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | D803Z | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  | 243284 | 1 | 85276 | 85569 | 293 | 10 |  | 2930 | 2919.3296 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 2919.3296 | 1971.9801 | 947.3495 | 48.0405 | FAULT
25 | 33/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  | 412277 | 1 | 39890 | 39890 | 0 | 10 |  | 0 | 0 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 0 | 1491.4977 | -1491.4977 | -100 | CHECK
|  |  | 10: Grand Total | 1622400 | 1628330 | 1622400 | -0.36418
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Jigatola | at 33 KV level |  | 1622400
[6 empty] | Total = |  |  | 1622400 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) |  | 33 | 0 | BD001912 | 1 | 428.23 | 428.24 | 0.01 | 240000 | 0 | 2400 | 2397.9141
|  |  | 10: Total | 0 | 2400 | 2397.9141
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 |  | 33 | 0 | 0 | 1 | 243.8 | 257.91 | 14.11 | 360000 | 0 | 5079600 | 5066255.1601
10 | Dhaka Uddyan-2 |  | 33 | 0 | 0 | 1 | 261.02 | 273.28 | 12.26 | 360000 | 0 | 4413600 | 4402004.8379
|  |  | 10: Total | 0 | 9493200 | 9468259.998
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | RECEIVE | BD017107 | 1 | 90469.03 | 90469.3 | 0.27 | 1125 |  | 303.75
| 33 kV Jigatala Incoming Circuit-1 |  | 33 |  | BD017098 | 1 | 77583.6 | 82191.3 | 4607.7 | 1125 |  | 5183662.5
| 33 kV Jigatala Incoming Circuit-2 |  | 33 |  | BD017097 | 1 | 83159.4 | 87149.2 | 3989.8 | 1125 |  | 4488525
| 33 kV Kamrangirchar Circuit-2 (O/H) |  | 33 |  | BD017108 | 1 | 73739.05 | 73739.05 | 0 | 1125 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 9672491.25 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017100 | 1 | 89836.5 | 95037.2 | 5200.7 | 1000 |  | 5200700
3 | 33/11 kV, 28/35 MVA T-3 (Future) |  | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017109 | 1 | 77076.6 | 81579.7 | 4503.1 | 1000 |  | 4503100
|  |  | 10: Total |  | 9703800 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 2397.9141; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9703800
| JIGATOLA 33 KV SIDE |  | 4: 9468259.998; 6: 33 KV NET IMPORT; 9=8-7: 9703800 | 33 KV TX HV |  | 9703800
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9470657.9121
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD014060 | 1 | 88750.1 | 93929.02 | 5178.92 | 1000 | 5178920 |  | 5198753.2452
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD014061 | 1 | 76362.2 | 80850.06 | 4487.86 | 1000 | 4487860 |  | 4505046.7548
|  |  | 7: 0; 8: 0; 10: Total | 9666780 |  | 9703800
| DHAKA UDDYAN 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | G1103L | 11 |  | BD014031 | 1 | 50107.2 | 50391.3 | 284.1 | 1000 |  | 284100 | 285235.5277 | Adabor |  |  |  |  | D Block dhaka uddyan | 285235.5277 | 367241.8104 | -82006.2827 | -22.3303 | OK
8 | Dill Mohammad O/H | G1103DM | 11 |  | BD014027 | 1 | 23726.2 | 25238.4 | 1512.2 | 1000 |  | 1512200 | 1518244.1569 | Adabor |  |  |  |  | Dill Mohammad O/H | 1518244.1569 | 1927925.8849 | -409681.728 | -21.2499 | OK
9 | Turag O/H | G1103U | 11 |  | BD014028 | 1 | 28276.4 | 28864.7 | 588.3 | 1000 |  | 588300 | 590651.3937 | Adabor |  |  |  |  | Turag O/H | 590651.3937 | 705567.8194 | -114916.4257 | -16.2871 | OK
10 | Nabadoy O/H | G1103N | 11 |  | BD014025 | 1 | 38453.6 | 39575.1 | 1121.5 | 1000 |  | 1121500 | 1125982.5565 | Adabor |  |  |  |  | Nabadoy O/H | 1125982.5565 | 997660.9336 | 128321.623 | 12.8622 | OK
11 | Chandrima O/H | G1103CH | 11 |  | BD014024 | 1 | 7893.5 | 8643.05 | 749.55 | 1000 |  | 749550 | 752545.8986 | Adabor |  |  |  |  | Chandrima O/H | 752545.8986 | 970880.6709 | -218334.7723 | -22.4883 | OK
12 | Shyamoli Housing Project-2 | G1103SH | 11 |  | BD014029 | 1 | 31072.7 | 31988.5 | 915.8 | 1000 |  | 915800 | 919460.3881 | Adabor |  |  |  |  | Shyamoli Housing Project-2 | 919460.3881 | 1164941.4253 | -245481.0372 | -21.0724 | OK
13 | Spare |  | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare |  | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare |  | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | C2103U | 11 |  | BD013959 | 1 | 44808.9 | 45500.4 | 691.5 | 1000 |  | 691500 | 694263.8768 | Satmasjid |  |  |  |  | U Lab | 694263.8768 | 2706800.3719 | -2012536.4951 | -74.3511 | CHECK
19 | Akota | G1103AK | 11 |  | BD014020 | 1 | 7699.4 | 8078.5 | 379.1 | 1000 |  | 379100 | 380615.236 | Adabor |  |  |  |  | Akota | 380615.236 | 526131.9628 | -145516.7268 | -27.6578 | OK
20 | Burigonga O/H | G1103BU | 11 |  | BD014019 | 1 | 5871.8 | 6149.5 | 277.7 | 1000 |  | 277700 | 278809.9473 | Adabor |  |  |  |  | Burigonga O/H | 278809.9473 | 387230.8575 | -108420.9102 | -27.999 | OK
21 | Garden City | C2103G | 11 |  | BD014021 | 1 | 92171 | 94056.2 | 1885.2 | 1000 |  | 1885200 | 1892735.0117 | Satmasjid |  |  |  |  | Garden City | 1892735.0117 | 2553547.6368 | -660812.6251 | -25.8782 | OK
22 | Avenue O/H | G1103AV | 11 |  | BD014017 | 1 | 15936.5 | 16683.5 | 747 | 1000 |  | 747000 | 749985.7064 | Adabor |  |  |  |  | Avenue O/H | 749985.7064 | 943169.2729 | -193183.5665 | -20.4824 | OK
23 | Chand Uddyan | C2103D | 11 |  | BD014018 | 1 | 10428.5 | 10938.7 | 510.2 | 1000 |  | 510200 | 512239.2335 | Satmasjid |  |  |  |  | Chand Uddyan | 512239.2335 | 689384.282 | -177145.0485 | -25.6961 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4416 | 1 | 1888.5 | 1917.01 | 28.51 | 100 |  | 2851 | 2862.3952 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 2862.3952 | 3787.2919 | -924.8966 | -24.4211 | OK
25 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4412 | 1 | 283.05 | 284.73 | 1.68 | 100 |  | 168 | 168.6715 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 168.6715 | 0 | 168.6715 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 9703800 | 9665169 | 9703800 | 0.39969
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 6604561.878
[6 empty] | Satmasjid | at 33 KV level |  | 3099238.122
[6 empty] | Total = |  |  | 9703800 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 |  | 33 | IMPORT | 8993 638E | 1 | 4216.182 | 4218.892 | 2.71 | 180000 | 0 | 487800
9 | Satmosjid -2 |  | 33 |  | 8993 669E | 1 | 5941.853 | 5957.121 | 15.268 | 180000 | 0 | 2748240
13 | Lalmatia |  | 33 |  |  | 1 | 5452.879 | 5453.99 | 1.111 | 180000 | 0 | 199980
14 | Transformer-1 |  | 33 |  | 50147586E | 1 | 3275.612 | 3308.169 | 32.557 | 750000 | 0 | 24417750
15 | Transformer-2 |  | 33 |  | 50148569E | 1 | 2917.773 | 2950.394 | 32.621 | 750000 | 0 | 24465750
|  |  | 9=8-7: Total Import/Export | 0 | 52319520
|  |  | 10: Net Total | 52319520
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | 4: RECEIVE; 6: 1; 9=8-7: 0
| 33 KV GT-2 Incomming |  | 6: 1; 9=8-7: 0
| 33 KV Satmosjid-1 Incomming |  | 6: 1; 9=8-7: 0
Total Import/Export
|  |  | 9=8-7: Net Total | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 4: EXPORT |  | 0
| Feeder No.2 | [10 empty] | 0
|  |  | 10: Total |  | 0
SATMOSJID 132 KV SIDE
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 4: 52319520; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 52319520
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 52319520 | 33 KV NET IMPORT |  | 52319520
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 52319520
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming |  | 33 |  | 50147586 | 1 | 3232.217 | 3232.217 | 0 | 750000 | 0
10 | 132/33 kV, 80/120 MVA GT-2 Incoming |  | 33 |  | 50148569 | 1 | 2873.592 | 2873.592 | 0 | 750000 | 0
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 52319520
| SATMOSJID 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SICAM | 1 | 4214 | 4214 | 0 | 1000 | From Downstream | 8322660 | 8116129.0541 |  | -0.75805 | Satmasjid 3/11 kv ss | 16429381.9035 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 8116129.0541 | 9397407.3121 | -1281278.2581 | -13.6344 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SICAM | 1 | 4298 | 4298 | 0 | 1000 | From Downstream | 8524800 | 8313252.8495 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 8313252.8495 | 9626925.8573 | -1313673.0078 | -13.6458 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 16847460 | 16429381.9035 | [5 empty] | 33 KV Feeders | 16429381.9035 | 19024333.1694 | -2594951.2659 | -13.6402 | OK
6 | BGB |  | 33 |  | 214393/40-2711 | 1 | 5807.1386 | 8456.954 | 2649.8154 | 1000 | From Downstream | 2691630 | 2624835.8633 |  | 0.27825 | BGB 33/11 KV SS | 2624835.8633 |  | BGB | 2624835.8633 | 9347831.3064 | -6722995.4431 | -71.9204 | CHECK
| Asad Gate Circuit-1 |  | 33 |  | 214393/44-2711 | 1 | 89.5259 | 4308.85 | 4219.3241 | 1000 | Estimated | 6556024.8 | 6393333.7849 |  | 0.85 | ASADGATE 33/11 KV SS | 11693411.6282 |  | Asad Gate Circuit-1 | 6393333.7849 | 5408599.0077 | 984734.7772 | 18.2068 | OK
8 | Lalmatia Circuit-2 |  | 33 |  | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 10503000 | 10242362.8329 |  | 1.7413 | LALMATIA 33/11 KV SS | 10242362.8329 |  | Lalmatia Circuit-2 | 10242362.8329 | 14054705.8227 | -3812342.9898 | -27.125 | OK
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 5434948.8 | 5300077.8433 |  | -0.36418 | JIGATOLA OLD 33/11 KV SS | 1603495.878 |  | Asad Gate Circuit-2 | 5300077.8433 | 8023320.1777 | -2723242.3344 | -33.9416 | OK
13 | Jigatola U/G Circuit |  | 33 |  | 214393/37-2711 | 1 | 35.6193 | 38.183 | 2.5637 | 1000 | Estimated | 1644300 | 1603495.878 |  | -0.53789 | JAPAN GARDEN 33/11 KV SS | 9726031.8942 |  | Jigatola U/G Circuit | 1603495.878 | 1597449.0742 | 6046.8038 | 0.37853 | OK
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 9973530 | 9726031.8942 | [5 empty] | Japan Garden City-2 | 9726031.8942 | 17542561.442 | -7816529.5478 | -44.5575 | CHECK
|  |  | 10: Total |  | 36803433.6 | 35890138.0965 | [5 empty] | 0 | 35890138.0965 | 55974466.8306 | -20084328.7341 | -35.8812 | OK
|  |  | 9=8-7: Grand Total | 52319520 | 53650893.6 | 52319520 | -2.4815
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming |  | 11 |  | DHK60998 | 1 | 4966.87 | 5013.107 | 46.237 | 180000 | 8322660 |  | 8116129.0541
24 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61044 | 1 | 5058.43 | 5105.79 | 47.36 | 180000 | 8524800 |  | 8313252.8495
|  |  | 7: 0; 8: 0; 10: Total | 16847460 |  | 16429381.9035
| SATMOSJID 11 kV SIDE |  | 7: 0; 8: 0
16 | Lalmatia O/H | C209M | 11 |  | DHK61042 | 1 | 3204.12 | 3220.42 | 16.3 | 60000 |  | 978000 | 970586.2531 | Satmasjid |  |  |  |  | Lalmatia O/H | 970586.2531 | 911395.4616 | 59190.7916 | 6.4945 | OK
16 | Asad Avenue (South) | C209C | 11 |  | DHK 60999 | 1 | 2936 | 2949.71 | 13.71 | 60000 |  | 822600 | 816364.2657 | Satmasjid |  |  |  |  | Asad Avenue (South) | 816364.2657 | 854508.8922 | -38144.6266 | -4.4639 | OK
17 | Madrasha Road |  | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | C209H | 11 |  | DHK61002 | 1 | 2441.86 | 2461.86 | 20 | 60000 |  | 1200000 | 1190903.3781 | Satmasjid |  |  |  |  | Bashbari | 1190903.3781 | 1245452.7622 | -54549.3841 | -4.3799 | OK
19 | Road-27 | C209A | 11 |  | DHK61001 | 1 | 1474.17 | 1479.65 | 5.48 | 60000 |  | 328800 | 326307.5256 | Satmasjid |  |  |  |  | Road-27 | 326307.5256 | 422413.036 | -96105.5104 | -22.7515 | OK
20 | Boishakhi O/H | D209O | 11 |  | DHK61024 | 1 | 4226.72 | 4253.99 | 27.27 | 60000 |  | 1636200 | 1623796.756 | Dhanmondi |  |  |  |  | Boishakhi O/H | 1623796.756 | 2461251.8872 | -837455.1312 | -34.0256 | OK
21 | Katasur O/H | C209K | 11 |  | DHK61003 | 1 | 3674.52 | 3692.06 | 17.54 | 60000 |  | 1052400 | 1044422.2626 | Satmasjid |  |  |  |  | Katasur O/H | 1044422.2626 | 1288420.2773 | -243998.0148 | -18.9378 | OK
22 | Nurjahan Road | D409I | 11 |  | DHK61000 | 1 | 1885.68 | 1912.62 | 26.94 | 60000 |  | 1616400 | 1604146.8503 | Shyamoli |  |  |  |  | Nurjahan Road | 1604146.8503 | 1215193.9487 | 388952.9015 | 32.0075 | OK
25 | polpar over head | D209W | 11 |  | DHK61003 | 1 | 1902.19 | 1928.75 | 26.56 | 60000 |  | 1593600 | 1581519.6861 | Dhanmondi |  |  |  |  | polpar over head | 1581519.6861 | 1999502.3937 | -417982.7077 | -20.9043 | OK
26 | Satmosjid Housing | C209S | 11 |  | DHK61043 | 1 | 2828.71 | 2852.16 | 23.45 | 60000 |  | 1407000 | 1396334.2108 | Satmasjid | Check |  |  |  | Satmosjid Housing | 1396334.2108 | 0 | 1396334.2108 | #DIV/0! | #DIV/0!
27 | Physical College | C209P | 11 |  | DHK61041 | 1 | 3391.12 | 3423.91 | 32.79 | 60000 |  | 1967400 | 1952486.0884 | Satmasjid |  |  |  |  | Physical College | 1952486.0884 | 2469119.1787 | -516633.0904 | -20.9238 | OK
28 | Asad Avenue (North) | D409V | 11 |  | DHK61022 | 1 | 2730.21 | 2730.21 | 0 | 60000 |  | 0 | 0 | Shyamoli | Check |  |  |  | Asad Avenue (North) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare Feeder |  | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | D209Z | 11 |  | DHK61023 | 1 | 1148.21 | 1170.56 | 22.35 | 60000 |  | 1341000 | 1330834.525 | Dhanmondi |  |  |  |  | Ghraphic artch college | 1330834.525 | 1448791.9887 | -117957.4637 | -8.1418 | OK
31 | Mohammadpur O/H | D409W | 11 |  | DHK61025 | 1 | 2241.73 | 2252.68 | 10.95 | 60000 |  | 657000 | 652019.5995 | Shyamoli |  |  |  |  | Mohammadpur O/H | 652019.5995 | 1590403.2357 | -938383.6362 | -59.0029 | CHECK
32 | Bosila Feeder | C209V | 11 |  | DHK60997 | 1 | 4192.28 | 4231.8 | 39.52 | 60000 |  | 2371200 | 2353225.0751 | Satmasjid |  |  |  |  | Bosila Feeder | 2353225.0751 | 2736001.9135 | -382776.8384 | -13.9904 | OK
33 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIB 7375 | 1 | 6093.1 | 6168.9 | 75.8 | 60 |  | 4548 | 4513.5238 | Satmasjid |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4513.5238 | 7345.0244 | -2831.5006 | -38.5499 | OK
|  |  | 10: Total | 16847460 | 16976148 | 16847460 | -0.75805
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Satmasjid | at 33 KV level |  | 10055142.5831
[6 empty] | Shyamoli | at 33 KV level |  | 2256166.4498
[6 empty] | Dhanmondi | at 33 KV level |  | 4536150.9671
[6 empty] | Total = |  |  | 16847460 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 |  | 33 |  | 38992490 (new) | 1 | 1.405 | 1.459 | 0.054 | 180000 | 0 | 9720 | 9720
| Kallyanpur to Japangarden-2 |  | 33 |  | 8993669E | 1 | 5941.853 | 5957.121 | 15.268 | 180000 | 0 | 2748240 | 2748240
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 9973530 | 9726031.8942
|  |  | 10: Total | 0 | 12731490 | 12483991.8942
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G |  | 33 | RECEIVE | DHK86051 | 1 | 3050.92 | 3076.8 | 25.88 | 270000 |  | 6987600
| kallyanpur U/G-2 |  | 33 |  | DHK61100 | 1 | 2932.12 | 2950.85 | 18.73 | 270000 |  | 5057100
|  |  | 8: 0; 10: Total |  | 12044700
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| 33 KV Japan Genden City |  | 33 |  | DHK15681 | 1 | 687.9 | 750.68 | 62.78 | 18000 |  | 1130040 | 1130040 | Adabor | Customer Number:-27111298
[7 empty] | 0 | 0
|  |  | 8: 0; 10: Total |  | 1130040
0
| JAPAN GERDEN CITY 33 KV SIDE |  | 8: 0
| 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61080 | 1 | 4370.75 | 4399.31 | 28.56 | 180000 |  | 5140800
3 | 33/11 kV 20/28 MVA T-1 (HV) |  | 33 |  | 86052 | 1 | 5196.91 | 5196.91 | 0 | 180000 |  | 7027200 |  |  | Check Meter
|  |  | 10: Total |  | 12168000 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 4: 13298040; 6: Adabor NOCS; 9=8-7: 1130040 | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 12168000
| IMPORT-2 |  | 6: JAPAN GERDEN CITY 33 KV NET IMPORT; 9=8-7: 12168000 | 33 KV TX HV SIDE |  | 12168000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 13298040
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK61079 | 1 | 5796.91 | 5841.01 | 44.1 | 160000 | 7056000 |  | 7022756.1837
10 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK61082 | 1 | 4865.43 | 4897.74 | 32.31 | 160000 | 5169600 |  | 5145243.8163
|  |  | 7: 0; 8: 0; 10: Total | 12225600 |  | 12168000
| JAPAN GERDEN CITY 11 KV SIDE |  | 7: 0; 8: 0
5 | Dhaka Uddyan | G186D | 11 |  | DHK86067 | 1 | 3252.83 | 3254.34 | 1.51 | 60000 |  | 90600 | 90112.6747 | Adabor |  |  |  |  | Dhaka Uddyan | 90112.6747 | 43181.0046 | 46931.6701 | 108.6859 | FAULT
| Shia Mosjid | D409H | 11 |  | DHK60950 | 1 | 3541.94 | 3569.61 | 27.67 | 60000 |  | 1660200 | 1651270.0056 | Shyamoli |  |  |  |  | Shia Mosjid | 1651270.0056 | 1965935.1818 | -314665.1761 | -16.0059 | OK
6 | Shekhar Tek | G186S | 11 |  | DHK60977 | 1 | 2443.6 | 2464.44 | 20.84 | 60000 |  | 1250400 | 1243674.2652 | Adabor |  |  |  |  | Shekhar Tek | 1243674.2652 | 1739834.6438 | -496160.3786 | -28.5177 | OK
7 | Madrasha Road | D434D | 11 |  | DHK61083 | 1 | 2064.99 | 2092.58 | 27.59 | 60000 |  | 1655400 | 1646495.8242 | Shyamoli |  |  |  |  | Madrasha Road | 1646495.8242 | 1898764.7302 | -252268.906 | -13.2859 | OK
8 | Baitul Aman Housing | G186B | 11 |  | DHK668115 | 1 | 4208.5 | 4242.38 | 33.88 | 60000 |  | 2032800 | 2021865.8399 | Adabor |  |  |  |  | Baitul Aman Housing | 2021865.8399 | 2579465.2888 | -557599.4489 | -21.6169 | OK
11 | Shyamoli Square | D486G | 11 |  | DHK86063 | 1 | 475.86 | 480.53 | 4.67 | 30000 |  | 140100 | 139346.4208 | Shyamoli |  |  |  |  | Shyamoli Square | 139346.4208 | 179920.8525 | -40574.4317 | -22.5513 | OK
12 | Mohammadi Housing | G186E | 11 |  | DHK60948 | 1 | 3873.73 | 3887.07 | 13.34 | 60000 |  | 800400 | 796094.7552 | Adabor |  |  |  |  | Mohammadi Housing | 796094.7552 | 1504138.327 | -708043.5718 | -47.073 | CHECK
13 | Chand Housing | C286H | 11 |  | DHK60867 | 1 | 2213.38 | 2223.07 | 9.69 | 60000 |  | 581400 | 578272.7269 | Satmasjid |  |  |  |  | Chand Housing | 578272.7269 | 1066930.6554 | -488657.9284 | -45.8003 | CHECK
14 | PC Culture Housing |  | 11 |  | DHK60979 | 1 | 4192.75 | 4222.72 | 29.97 | 60000 |  | 1798200 | 1788527.722 | Adabor |  |  |  |  | PC Culture Housing | 1788527.722 | 2352165.2785 | -563637.5564 | -23.9625 | OK
15 | Mehedibagh | G186H | 11 |  | DHK68121 | 1 | 2408.52 | 2445.54 | 37.02 | 60000 |  | 2221200 | 2209252.4615 | Adabor |  |  |  |  | Mehedibagh | 2209252.4615 | 2861941.0273 | -652688.5658 | -22.8058 | OK
16 | 33/11 kV Incoming (Spare) |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 |  | 0 | 0 | Adabor |  |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer |  | 11 |  |  | 1 | 661926 | 665030 | 3104 | 1 |  | 3104 | 3087.304 | Adabor |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 3087.304 | 4523.0103 | -1435.7063 | -31.7423 | OK
|  |  | 10: Grand Total | 12168000 | 12233804 | 12168000 | -0.53789
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Adabor | at 33 KV level |  | 8152615.0224
[6 empty] | Shyamoli | at 33 KV level |  | 3437112.2506
[6 empty] | Satmasjid | at 33 KV level |  | 578272.7269
[6 empty] | Total = |  |  | 12168000 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) |  | 132 |  | 42627810 | 1 | 201.909 | 214.859 | 12.95 | 960000 | 0 | 12432000
2 | Dhaka University-1 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) |  | 132 |  | 42627812 | 1 | 203.94 | 217.013 | 13.073 | 960000 | 0 | 12550080
3 | Dhaka University-2 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 24982080
|  |  | 10: Net Total | 24982080
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 |  | 132 |  | 2877 | 1 | 161.6 | 171.97 | 10.37 | 1200000 |  | 12444000
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 |  | 132 |  | 2811 | 1 | 163.14 | 173.6 | 10.46 | 1200000 |  | 12552000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 24996000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 24996000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhanmondi |  | 132 | 0 | SIEM0480 | 1 | 119880 | 133950 | 14070 | 1000 |  | 14070000
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 14070000
| DHAKA UNIVERSITY 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | 2752 | 1 | 220.25 | 224.83 | 4.58 | 1200000 |  | 5496000
4 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | 2867 | 1 | 238.28 | 242.82 | 4.54 | 1200000 |  | 5448000
|  |  | 10: Total |  | 10944000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 24982080; 6: EXPORT TO OTHER S/S; 9=8-7: 14070000 | 132 KV NET IMPORT |  | 10944000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 10944000 | 33 KV NET IMPORT |  | 10821600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 122400
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.118%
| 132 KV TOTAL IMPORT |  | 4: 24982080
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  | 2769 | 1 | 364.32 | 371.83 | 7.51 | 720000 | 5407200
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  | 2830 | 1 | 393.63 | 401.15 | 7.52 | 720000 | 5414400
|  |  | 7: 0; 8: 0; 10: Total | 10821600 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  | 2751 | 1 | 38.87 | 39.91 | 1.04 | 240000 |  | 249600 | 250371.2207 |  | -0.15046 | DHAKA UNIVERSITY 33/11 KV SS | 1374634.2983 |  | 33/11 kV 28/35 MVA T-1 | 250371.2207 | 540143.1709 | -289771.9501 | -53.6472 | CHECK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  | 4253 | 1 | 62.84 | 65.91 | 3.07 | 240000 |  | 736800 | 739076.5842 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 739076.5842 | 936248.1628 | -197171.5786 | -21.0598 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  | 2808 | 1 | 24.72 | 26.32 | 1.6 | 240000 |  | 384000 | 385186.4934 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 385186.4934 | 542543.8072 | -157357.3138 | -29.0036 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 1370400 | 1374634.2983 | [5 empty] | 33 KV Feeders | 1374634.2983 | 2018935.1408 | -644300.8425 | -31.9129 | OK
2 | Spare |  | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 |  | 33 |  | 2804 | 1.5 | 174.5 | 181.85 | 7.35 | 360000 |  | 3969000 | 3981263.5215 |  | -0.40364 | BB AVENUE 33/11 KV SS | 6072103.956 |  | BB Avenue-1 | 3981263.5215 | 4623625.5425 | -642362.021 | -13.893 | OK
3 | DMC Circuit-1 |  | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 | [5 empty] | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 |  | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | -0.09904 | DMC 33/11 KV SS | 1453838.271 |  | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 |  | 33 |  | 2753 | 1 | 426.46 | 431.54 | 5.08 | 360000 |  | 1828800 | 1834450.6748 | [5 empty] | Biddyut Bhaban Circuit-2 | 1834450.6748 | 1897703.0069 | -63252.3322 | -3.3331 | OK
10 | DMC Circuit-2 |  | 33 |  | 2803 | 1.1 | 329.75 | 333.41 | 3.66 | 360000 |  | 1449360 | 1453838.271 |  | 0.49417 | BIDDYUT BHABAN 33/11 KV SS | 1834450.6748 |  | DMC Circuit-2 | 1453838.271 | 3486084.0247 | -2032245.7537 | -58.2959 | CHECK
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 205.04 | 210.83 | 5.79 | 360000 |  | 2084400 | 2090840.4344 | [5 empty] | BB Avenue-2 | 2090840.4344 | 2524269.0851 | -433428.6507 | -17.1705 | OK
12 | Spare |  | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 9331560 | 9360392.9017 | [5 empty] | 0 | 9360392.9017 | 12531681.6592 | -3171288.7575 | -25.3062 | OK
|  |  | 9=8-7: Grand Total | 10735027.2 | 10701960 | 10735027.2 | 0.30898
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 49.17 | 50.61 | 1.44 | 250000 | 360000 |  | 338950.9229
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 58.77 | 61.67 | 2.9 | 250000 | 725000 |  | 682609.4974
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 22.8 | 24.3 | 1.5 | 250000 | 375000 |  | 353073.878
|  |  | 7: 0; 8: 0; 10: Total | 1460000 |  | 1374634.2983
| DHAKA UNIVERSITY 11 kV SIDE |  | 7: 0; 8: 0
| Mokarom Bhabon | D3108MB | 11 |  | 2761 | 1 | 60.6 | 63.51 | 2.91 | 60000 |  | 174600 | 174337.3 | Ramna |  |  |  |  | Mokarom Bhabon | 174337.3 | 202329.0481 | -27991.7482 | -13.8348 | OK
4 | 11 kV Shaid Minar RMU | D3108SM | 11 |  | 2850 | 1 | 143.49 | 146.61 | 3.12 | 60000 |  | 187200 | 186918.3422 | Ramna |  |  |  |  | 11 kV Shaid Minar RMU | 186918.3422 | 606987.1444 | -420068.8022 | -69.2056 | CHECK
5 | 11 kV Shaidulla Hall | D3108SH | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | D3108MA | 11 |  | 2836 | 1 | 103.68 | 106.63 | 2.95 | 60000 |  | 177000 | 176733.689 | Ramna |  |  |  |  | MBA Bhabon | 176733.689 | 232348.1947 | -55614.5058 | -23.9358 | OK
11 | Suprime Court |  | 11 |  | 2835 | 1 | 66 | 70.7 | 4.7 | 60000 |  | 282000 | 281575.7078 | Ramna |  |  |  |  | Suprime Court | 281575.7078 | 323006.0175 | -41430.3097 | -12.8265 | OK
12 | Karjon Hall | D3108KH | 11 |  | 2853 | 1 | 72.86 | 76.92 | 4.06 | 60000 |  | 243600 | 243233.4838 | Ramna |  |  |  |  | Karjon Hall | 243233.4838 | 317602.5711 | -74369.0873 | -23.4158 | OK
13 | Spare |  | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | D3108SP | 11 |  | 2839 | 1 | 2.33 | 2.73 | 0.4 | 60000 |  | 24000 | 23963.89 | Ramna |  |  |  |  | Swimming Pool | 23963.89 | 46229.4858 | -22265.5957 | -48.1632 | CHECK
15 | Spare |  | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU |  | 11 |  | 2772 | 1 | 93.56 | 98.89 | 5.33 | 60000 |  | 319800 | 319318.8346 | Ramna |  |  |  |  | Police Head Quarter RMU | 319318.8346 | 399254.6499 | -79935.8153 | -20.0213 | OK
17 | Spare |  | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare |  | 11 |  | 2764 | 1 | 1.48 | 2.38 | 0.9 | 60000 | Cheek Nocs & Feeder | 54000 | 53918.7526 | [5 empty] | Spare | 53918.7526 | 67242.8884 | -13324.1358 | -19.8149 | OK
19 | Spare |  | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 1460000 | 1462200 | 1460000 | -0.15046
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1460000
[6 empty] | Total = |  |  | 1460000 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 |  | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 |  | 33 | 0 | 2753 | 1 | 426.46 | 431.54 | 5.08 | 360000 | 0 | 1828800 | 1834450.6748
| Motijheel Old 33 KV Side (Sending) |  | 10: Total | 0 | 1828800 | 1834450.6748
| Motijheel Incoming |  | 33 | 0 | DHK-C9344 | 1 | 69353.02 | 73648.71 | 4295.69 | 270 | 0 | 1159836.3 |  | 0
P&T 33 KV Side (Sending)
| P&T Incoming |  | 33 | Export | BD017079 | 1 | 144 | 1533 | 1389 | 1000 | 0 | 1389000
|  |  | 10: Total |  | 4383286.9748
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 69353.02 | 73648.71 | 4295.69 | 270 | 0 | 1159836.3
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 21216.28 | 21216.28 | 0 | 270 |  | 0
| Dhaka University Incoming-1 |  | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 | From P&T END | 1389000
| Dhaka University Incoming-2 |  | 33 |  | DHK-C9343 | 1 | 69597.58 | 76502.64 | 6905.06 | 270 |  | 1864366.2
|  |  | 7: 0; 8: 0; 10: Total |  | 4413202.5 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 |  | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-C9342 | 1 | 99167.93 | 105607.26 | 6439.33 | 270 |  | 1738619.1
3 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK-C9308 | 1 | 58019.02 | 68327.02 | 10308 | 270 |  | 2783160
|  |  | 10: Total |  | 4521779.1 | 4521779.1
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 4: 4413202.5; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4521779.1
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4521779.1 | 33 KV TX HV SIDE |  | 4521779.1
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 4413202.5
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK-C9316 | 1 | 82092.02 | 89297.15 | 7205.13 | 240 | 1729231.2 |  | 4521779.1
10 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK-C9377 | 1 | 113467.84 | 113467.84 | 0 | 240 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 1729231.2 |  | 4521779.1
| BIDDYUT BHABAN 11 KV SIDE |  | 7: 0; 8: 0
6 | Segunbagicha | D394S | 11 |  | DHK-C9360 | 1 | 13326.33 | 20686.9 | 7360.57 | 60 |  | 441634.2 | 443816.6143 | Ramna |  |  |  |  | Segunbagicha | 443816.6143 | 585591.0985 | -141774.4841 | -24.2105 | OK
| Secretariat RMU | D394FB | 11 |  | DHK-C9379 | 1 | 79602.83 | 81663.25 | 2060.42 | 60 |  | 123625.2 | 124236.116 | Ramna |  |  |  |  | Secretariat RMU | 124236.116 | 153919.5822 | -29683.4662 | -19.285 | OK
7 | NBR RMU | D394NR | 11 |  | DHK-C9319 | 1 | 73234.86 | 78532.8 | 5297.94 | 60 |  | 317876.4 | 319447.2431 | Ramna |  |  |  |  | NBR RMU | 319447.2431 | 425924.9701 | -106477.7271 | -24.9992 | OK
8 | Ramna 11 kV Sw/S-2 |  | 11 |  | DHK-C9364 | 1 | 50263.55 | 64314.76 | 14051.21 | 60 |  | 843072.6 | 847238.794 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-2 | 847238.794 | 1202930.2093 | -355691.4153 | -29.5687 | OK
11 | Ramna 11 kV Sw/S-1 |  | 11 |  | DHK-C9375 | 1 | 55956.29 | 57677.67 | 1721.38 | 60 |  | 103282.8 | 103793.1904 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-1 | 103793.1904 | 54867.1796 | 48926.0108 | 89.1717 | FAULT
12 | Family Planning | D394FP | 11 |  | DHK-C9378 | 1 | 71774.93 | 77750.21 | 5975.28 | 60 |  | 358516.8 | 360288.4749 | Ramna |  |  |  |  | Family Planning | 360288.4749 | 436247.6925 | -75959.2176 | -17.4119 | OK
13 | Muktijuddho Montranalaya | D394MJ | 11 |  | DHK-C9376 | 1 | 88559.61 | 99696.86 | 11137.25 | 60 |  | 668235 | 671537.2027 | Ramna |  |  |  |  | Muktijuddho Montranalaya | 671537.2027 | 860939.7125 | -189402.5098 | -21.9995 | OK
14 | Purana Palton | D394R | 11 |  | DHK-C9318 | 1 | 65821.54 | 70819.4 | 4997.86 | 60 |  | 299871.6 | 301353.4691 | Ramna |  |  |  |  | Purana Palton | 301353.4691 | 347167.2021 | -45813.733 | -13.1964 | OK
15 | Tip Top Feeder |  | 11 |  | DHK-C9318 | 1 | 70239.61 | 92552.33 | 22312.72 | 60 |  | 1338763.2 | 1345378.9377 | Kakrail |  |  |  |  | Tip Top Feeder | 1345378.9377 | 2213157.3667 | -867778.429 | -39.21 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT |  | 0.415 |  | DHKD3784 | 1 | 355193 | 359859 | 4666 | 1 |  | 4666 | 4689.0579 | Ramna |  |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 4689.0579 | 5100.6865 | -411.6286 | -8.0701 | OK
|  |  | 10: Grand Total | 4521779.1 | 4499543.8 | 4521779.1 | 0.49417
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 3176400.1623
[6 empty] | Kakrail | at 33 KV level |  | 1345378.9377
[6 empty] | Total = |  |  | 4521779.1 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 |  | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 |  | 33 | 0 | 2803 | 1.1 | 329.75 | 333.41 | 3.66 | 360000 | 0 | 1449360 | 1453838.271
|  |  | 10: Total | 0 | 1449360 | 1453838.271
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder |  | 33 | 0 | BD001840 | 1 | 446.7 | 464.63 | 17.93 | 240000 | 0 | 4303200 | 4308267.365
|  |  | 10: Total |  | 4303200 | 4308267.365
| DMCH 33 KV SIDE (RECEIVING) | [11 empty] | 5762105.636
| 33 kV DU Incoming Circuit-1 |  | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming |  | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 |  | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0 | 0
| DMCH 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DMCH 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | 00000069 | 1 | 135049440 | 138244800 | 3195360 | 1 |  | 3195360
2 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 10: Total |  | 3195360
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 4: 1453838.271; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5762105.636
| DHANMONDI 33 kV SIDE |  | 4: 4308267.365; 6: 33 KV NET IMPORT; 9=8-7: 5762105.636 | 33 KV TX HV SIDE |  | 5762105.636
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 5762105.636
11 KV SIDE of___DMCH 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000056 | 1 | 133739664 | 136910672 | 3171008 | 1 | 3171008 |  | 3270968.6239
14 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000034 | 1 | 163047472 | 165462480 | 2415008 | 1 | 2415008 |  | 2491137.0121
|  |  | 7: 0; 8: 0; 10: Total | 5586016 |  | 5762105.636
| DMCH 11 KV SIDE |  | 7: 0; 8: 0
6 | Nearest O/H | D398NE | 11 |  | 00000126 | 1 | 7943260.5 | 8118980 | 175719.5 | 1 |  | 175719.5 | 175545.4669 | Ramna |  |  |  |  | Nearest O/H | 175545.4669 | 200195.8311 | -24650.3642 | -12.3131 | OK
| Jagannath Hall | D398JA | 11 |  | 00000002 | 1 | 2968112.8 | 3050232 | 82119.2 | 1 |  | 82119.2 | 82037.8689 | Ramna |  |  |  |  | Jagannath Hall | 82037.8689 | 101039.4533 | -19001.5844 | -18.8061 | OK
7 | Samsun Nahar Hall | D398SN | 11 |  | 00000024 | 1 | 10295055 | 10524494 | 229439 | 1 |  | 229439 | 229211.7629 | Ramna |  |  |  |  | Samsun Nahar Hall | 229211.7629 | 277277.1279 | -48065.365 | -17.3348 | OK
8 | Spare, 4L |  | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | A3983 | 11 |  | 00000023 | 1 | 22742504 | 23025144 | 282640 | 1 |  | 282640 | 282360.0725 | Lalbag |  |  |  |  | Board Office O/H, (5L) | 282360.0725 | 404116.548 | -121756.4755 | -30.129 | OK
10 | OT- Complex | D398OT | 11 |  | 00000167 | 1 | 6834903.5 | 7175302 | 340398.5 | 1 |  | 340398.5 | 340061.3683 | Ramna |  |  |  |  | OT- Complex | 340061.3683 | 106528.8271 | 233532.5412 | 219.22 | FAULT
11 | Alia Mdrasha O/H, (7L) | A3984 | 11 |  | 00000148 | 1 | 9674696 | 9776616 | 101920 | 1 |  | 101920 | 101819.0581 | Lalbag |  |  |  |  | Alia Mdrasha O/H, (7L) | 101819.0581 | 64901.5515 | 36917.5066 | 56.8823 | FAULT
12 | Majed Sordar Road | B698J | 11 |  | 00000164 | 1 | 60280212 | 62242088 | 1961876 | 1 |  | 1961876 | 1959932.9522 | Bangshal |  |  |  |  | Majed Sordar Road | 1959932.9522 | 1719312.7006 | 240620.2516 | 13.9951 | OK
15 | Chankharpool, 9L | B698Q | 11 |  | 00000001 | 1 | 50333796 | 50750956 | 417160 | 1 |  | 417160 | 416746.8435 | Bangshal |  |  |  |  | Chankharpool, 9L | 416746.8435 | 1136431.6854 | -719684.8419 | -63.3285 | CHECK
16 | Shahidullah College O/H, (10L) | A3986 | 11 |  | 00000003 | 1 | 13594687 | 13802806 | 208119 | 1 |  | 208119 | 207912.8783 | Lalbag |  |  |  |  | Shahidullah College O/H, (10L) | 207912.8783 | 235452.0398 | -27539.1614 | -11.6963 | OK
17 | Ananda Bazar | D398AB | 11 |  | 00000111 | 1 | 15255803 | 15359723 | 103920 | 1 |  | 103920 | 103817.0773 | Ramna |  |  |  |  | Ananda Bazar | 103817.0773 | 119468.7736 | -15651.6963 | -13.1011 | OK
18 | Hosseni Dalan O/H, (12L) | A3985 | 11 |  |  | 1 | 62.84 | 65.91 | 3.07 | 60000 | Estimated | 860184.9 | 859332.9703 | Lalbag | Estimated from Grid SAS Data |  |  |  | Hosseni Dalan O/H, (12L) | 859332.9703 | 999393.6344 | -140060.664 | -14.0146 | OK
19 | Badrun Nessa College | A398W | 11 |  | 00000006 | 1 | 20999788 | 21354548 | 354760 | 1 |  | 354760 | 354408.6447 | Lalbag |  |  |  |  | Badrun Nessa College | 354408.6447 | 469459.7974 | -115051.1528 | -24.5071 | OK
20 | Dhaka Medical College, Unit-II | D398DM | 11 |  | 00000125 | 1 | 12612529 | 12836569 | 224040 | 1 |  | 224040 | 223818.1101 | Ramna |  |  |  |  | Dhaka Medical College, Unit-II | 223818.1101 | 299392.072 | -75573.9618 | -25.2425 | OK
21 | Spare, 15L |  | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | D398SH | 11 |  | 00000127 | 1 | 21974666 | 22395106 | 420440 | 1 |  | 420440 | 420023.595 | Ramna |  |  |  |  | Sheikh Hasina National Burn Institute | 420023.595 | 543136.2141 | -123112.6192 | -22.667 | OK
23 | Aux. Transformer, AT-1 |  | 0.415 |  | DHKF-7804 | 1 | 2872.86 | 2923.68 | 50.82 | 100 |  | 5082 | 5076.9668 | Ramna |  |  |  |  | Aux. Transformer, AT-1 | 5076.9668 | 7678.1323 | -2601.1655 | -33.8776 | OK
24 | Aux. Transformer, AT-2 |  | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5762105.636 | 5767818.1 | 5762105.636 | -0.09904
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1579592.2163
[6 empty] | Lalbag | at 33 KV level |  | 1805833.624
[6 empty] | Bangshal | at 33 KV level |  | 2376679.7958
[6 empty] | Total = |  |  | 5762105.636 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 |  | 33 | 0 | 2804 | 1.5 | 174.5 | 181.85 | 7.35 | 360000 | 0 | 3969000 | 3981263.5215
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 205.04 | 210.83 | 5.79 | 360000 | 0 | 2084400 | 2090840.4344
|  |  | 10: Total | 0 | 6053400 | 6072103.956
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 |  | 33 |  | BD 017078 | 1 | 0 | 0 | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 |  | 33 |  | BD 017090 | 1 | 73665.36 | 75816.77 | 2151.41 | 1125 |  | 2420336.25
|  |  | 7: 0; 8: 0; 10: Total | 0 | 2420336.25 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD 017093 | 1 | 106526.14 | 106526.14 | 0 | 1000 |  | 0
3 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD 017094 | 1 | 59075.6 | 61232.28 | 2156.68 | 1000 |  | 2156680
|  |  | 10: Total |  | 2156680
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 6072103.956; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BB AVENEU 33 KV NET IMPORT |  | 6072103.956
|  |  | 6: BB AVENEU 33 KV NET IMPORT; 9=8-7: 6072103.956 | 33 KV TX HV SIDE |  | 2156680
[11 empty] | LOSS UNITS=> |  | 3915423.956
[11 empty] | LOSS % IN => |  | 64.48%
| TOTAL IMPORT |  | 4: 6072103.956
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD 014052 | 1 | 106679.74 | 106679.74 | 0 | 1000 | 0 |  | 0
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD 014055 | 1 | 58511.9 | 60655.42 | 2143.52 | 1000 | 2143520 |  | 6072103.956
|  |  | 7: 0; 8: 0; 10: Total | 2143520 |  | 6072103.956
| BB AVENEU 11 KV SIDE |  | 7: 0; 8: 0
6 | Secratariet East | D363BS | 11 |  | BD 013966 | 1 | 4367.4 | 4544.19 | 176.79 | 1000 |  | 176790 | 176076.397 | Ramna |  |  |  |  | Secratariet East | 176076.397 | 242760.0671 | -66683.6702 | -27.469 | OK
| Taher Bag O/H | B163G | 11 |  | BD 014045 | 1 | 20674.71 | 21284.07 | 609.36 | 1000 |  | 609360 | 606900.3521 | Narinda |  |  |  |  | Taher Bag O/H | 606900.3521 | 725752.2867 | -118851.9346 | -16.3764 | OK
7 | Al Raji Complex | D363AR | 11 |  | BD 013983 | 1 | 16069.61 | 16656.82 | 587.21 | 1000 |  | 587210 | 584839.7594 | Ramna |  |  |  |  | Al Raji Complex | 584839.7594 | 756317.9861 | -171478.2267 | -22.6728 | OK
8 | Raduni | D363RI | 11 |  | BD 013999 | 1 | 30757.71 | 31732.57 | 974.86 | 1000 |  | 974860 | 970925.0317 | Ramna |  |  |  |  | Raduni | 970925.0317 | 1082729.9623 | -111804.9307 | -10.3262 | OK
9 | Sundor Bon Square O/H | B163D | 11 |  | BD 013954 | 1 | 14187.74 | 14602.66 | 414.92 | 1000 |  | 414920 | 413245.1984 | Narinda |  |  |  |  | Sundor Bon Square O/H | 413245.1984 | 496614.8713 | -83369.6728 | -16.7876 | OK
10 | Shromo Bhobon O/H | D363SB | 11 |  | BD 013985 | 1 | 14129.96 | 14602.66 | 472.7 | 1000 |  | 472700 | 470791.9727 | Ramna |  |  |  |  | Shromo Bhobon O/H | 470791.9727 | 489342.1006 | -18550.128 | -3.7908 | OK
11 | Nawabpur Road | B163P | 11 |  | BD 013953 | 1 | 21924.28 | 22640.38 | 716.1 | 1000 |  | 716100 | 713209.502 | Narinda |  |  |  |  | Nawabpur Road | 713209.502 | 834593.0606 | -121383.5586 | -14.544 | OK
12 | Spair |  | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare |  | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | D363AP | 11 |  | BD 013984 | 1 | 12043.51 | 12534.21 | 490.7 | 1000 |  | 490700 | 488719.3167 | Ramna |  |  |  |  | Ahad Police Box | 488719.3167 | 481256.786 | 7462.5306 | 1.5506 | OK
17 | Nearest O/H | D363NE | 11 |  | BD 013997 | 1 | 2866.83 | 2970.68 | 103.85 | 1000 |  | 103850 | 103430.8152 | Ramna |  |  |  |  | Nearest O/H | 103430.8152 | 124640.2411 | -21209.4259 | -17.0165 | OK
18 | Natab Bhaban | D363NB | 11 |  | BD 014000 | 1 | 5346.21 | 5488.09 | 141.88 | 1000 |  | 141880 | 141307.3092 | Ramna |  |  |  |  | Natab Bhaban | 141307.3092 | 179461.8844 | -38154.5751 | -21.2605 | OK
19 | Spare |  | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | D363AO | 11 |  | BD 013956 | 1 | 1434.02 | 1452.23 | 18.21 | 1000 |  | 18210 | 18136.4963 | Ramna |  |  |  |  | Awami League Party Office | 18136.4963 | 10332.35 | 7804.1464 | 75.5312 | FAULT
21 | Khaddar Bazar | D363KB | 11 |  | BD 014012 | 1 | 10910.83 | 11244.73 | 333.9 | 1000 |  | 333900 | 332552.2312 | Ramna |  |  |  |  | Khaddar Bazar | 332552.2312 | 396371.0138 | -63818.7826 | -16.1008 | OK
22 | Bangobondu National Stidium | D363NS | 11 |  | BD 014008 | 1 | 10449.23 | 11498.09 | 1048.86 | 1000 |  | 1048860 | 1044626.3348 | Ramna |  |  |  |  | Bangobondu National Stidium | 1044626.3348 | 1319581.5303 | -274955.1955 | -20.8365 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4418 | 1 | 1407.54 | 1481.27 | 73.73 | 100 |  | 7373 | 7343.2393 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 7343.2393 | 8140.4874 | -797.2481 | -9.7936 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 48.11 | 48.11 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6072103.956 | 6096713 | 6072103.956 | -0.40364
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 4338748.9033
[6 empty] | Narinda | at 33 KV level |  | 1733355.0526
[6 empty] | Total = |  |  | 6072103.956 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 |  | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
|  |  | 10: Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 |  | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 |  | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 |  | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 0
|  |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 0 | KALLYANPUR 11 KV NET IMPORT |  | 0
|  |  | 6: TOTAL EXPORT; 9=8-7: 0 | LOSS UNITS=> |  | 0
|  |  | 6: 132KV NET LOSS =>; 9=8-7: #DIV/0! | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 4: 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming |  | 11 |  | 74819926 | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  | 7: 0; 8: 0
A | From Kallyanpur S/S. |  | 7: 0; 8: 0
| 11 KV Gano Bhavan RMU | D534T | 11 |  | DHK14997 | 1 | 995.87 | 995.9 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar |  |  |  |  | 11 KV Gano Bhavan RMU | 1230 | 2050 | -820 | -40 | OK
| 11 KV Beribandh Feeder. | G134K | 11 |  | DHK14960 | 1 | 9667.45 | 9673.06 | 5.61 | 40000 |  | 224400 | 230010 | Adabor |  |  |  |  | 11 KV Beribandh Feeder. | 230010 | 285360 | -55350 | -19.3966 | OK
| 11 KV Adabor O/H | D434A | 11 |  | DHK14957 | 1 | 4583.3 | 4620.87 | 37.57 | 40000 |  | 1502800 | 1540370 | Adabor |  |  |  |  | 11 KV Adabor O/H | 1540370 | 2118880 | -578510 | -27.3026 | OK
| 11 KV Mansurabad | G134M | 11 |  | 77816681 | 1 | 52769.06 | 52970.34 | 201.28 | 8000 |  | 1610240 | 1650496 | Adabor |  |  |  |  | 11 KV Mansurabad | 1650496 | 2258116 | -607620 | -26.9083 | OK
| 11 KV Ring Road Feeder | G134R | 11 |  | 77816675 | 1 | 42349.9 | 42456.21 | 106.31 | 8000 |  | 850480 | 871742 | Adabor |  |  |  |  | 11 KV Ring Road Feeder | 871742 | 1122088 | -250346 | -22.3107 | OK
| 11 KV Sewarage Pump | G134P | 11 |  | DHK14959 | 1 | 2296.25 | 2350.06 | 53.81 | 40000 |  | 2152400 | 2206210 | Adabor |  |  |  |  | 11 KV Sewarage Pump | 2206210 | 2792510 | -586300 | -20.9954 | OK
| 11 KV Technical School (DPDC) | G134T | 11 |  | DHK15019 | 1 | 8361.96 | 8401.63 | 39.67 | 40000 |  | 1586800 | 1626470 | Adabor |  |  |  |  | 11 KV Technical School (DPDC) | 1626470 | 2204980 | -578510 | -26.2365 | OK
| 11 KV Goidertek (DPDC) | G134G | 11 |  | DHK14996 | 1 | 9414.91 | 9431.09 | 16.18 | 40000 |  | 647200 | 663380 | Adabor |  |  |  |  | 11 KV Goidertek (DPDC) | 663380 | 612540 | 50840 | 8.2999 | OK
B | From Agargaon S/S. |  | 3: 11 |  |  | 0
| 11 KV P.C Culture Housing | G186C | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H |  | 11 |  | DHK-15026 | 1 | 9219.86 | 9229.09 | 9.23 | 40000 |  | 369200 | 378430 | Shere b.nagar
| 11 KV Nearest RMU |  | 11 |  | DHK-15027 | 1 | 3875.73 | 3878 | 2.27 | 40000 |  | 90800 | 93070 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar |  | 11 |  | DHK-15025 | 1 | 3980.52 | 3984.04 | 3.52 | 40000 |  | 140800 | 144320 | Shere b.nagar
| 11 KV BICC Feeder. |  | 11 |  | DHK-15024 | 1 | 1038.9 | 1038.9 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV NEC Feeder. |  | 11 |  | DHK-15023 | 1 | 431.67 | 431.67 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV Manik Mia Feeder. |  | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
|  |  | 7: Export To Desco; 9=8-7: 0; 10: Grand Total |  | 9176320 | 9405728 | 2.5
DESCO | 11 kV Tolarbugh |  | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil |  | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy |  | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari |  | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H |  | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur |  | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S |  | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 0 | 0 | #DIV/0!
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 8788678
[6 empty] | Shere b.nagar | at 33 KV level |  | 617050
[6 empty] | Satmasjid | at 33 KV level
[6 empty] | DESCO | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 9405728 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 |  | 33 | 0 | 30799147 | 1 | 1597.96 | 1603.45 | 5.49 | 240000 | 0 | 1317600 | 1335638.1714
|  |  | 10: Total | 0 |  | 1335638.1714
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
|  |  | 10: Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming |  | 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
| Lalbagh Incoming |  | 3: 33; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 |  | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 |  | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 1335638.1714; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 1335638.1714
| IMPORT-2 |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 1335638.1714 | KALLYANPUR 11 KV NET IMPORT |  | 1335638.1714
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 1335638.1714
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month November-2023 |  |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 320
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 100
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 220
|  |  | 10: Total | 0 |  | 1335638.1714 |  |  | 73.3333
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 173.3333
1 | Nizambag | F1114Z | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 233456.58 | 234080.9166 | Kamrangirchar | 85 |  |  |  | Nizambag | 234080.9166 | 1217190.9472 | -983110.0306 | -80.7688 | CHECK
2 | Merry Stopes | F1114P | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 54930.96 | 55077.8627 | Kamrangirchar | 20 |  |  |  | Merry Stopes | 55077.8627 | 304297.7368 | -249219.8741 | -81.9 | CHECK
3 | Mujibur Ghat | F1114V | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 274654.8 | 275389.3137 | Kamrangirchar | 100 |  |  |  | Mujibur Ghat | 275389.3137 | 1278050.4946 | -1002661.1809 | -78.4524 | CHECK
4 | Madrasa | F1114U | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 329585.76 | 330467.1764 | Kamrangirchar | 120 |  |  |  | Madrasa | 330467.1764 | 1582348.2314 | -1251881.055 | -79.1154 | CHECK
5 | Thana | F1114Q | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 247189.32 | 247850.3823 | Kamrangirchar | 90 |  |  |  | Thana | 247850.3823 | 1217190.9472 | -969340.5649 | -79.6375 | CHECK
6 | Al-Hera |  | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | F1114W | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 192258.36 | 192772.5196 | Kamrangirchar | 70 |  |  |  | Waz Uddin School | 192772.5196 | 852033.6631 | -659261.1435 | -77.375 | CHECK
8 | 11/0.4 kV Auxiliary Transformer |  | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off |  | 10: Grand Total | 1335638.1714 | 1332075.78 | 1335638.1714 | 0.26743
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 1335638.1714
[6 empty] | Total = |  |  | 1335638.1714 | 0
Note on G935: User: Grid CF=1.5

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) |  | 132 | IMPORT | 8993631 | 1 | 5922.51 | 5948.831 | 26.321 | 960000 | 0 | 25268160
| 132 KV Mogbazar-2 CKT(EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) |  | 132 |  | 8993659 | 1 | 5042.863 | 5064.126 | 21.263 | 960000 | 0 | 20412480
| 132 KV Mogbazar-1 CKT(EXP) |  | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 45680640
|  |  | 10: Net Total | 45680640
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE | 6604452 | 1 | 9469.87 | 9505.05 | 35.18 | 720000 | 25329600
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  | 6604428 | 1 | 5705.45 | 5734.05 | 28.6 | 720000 | 20592000
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
|  |  | 9=8-7: Total Import/Export | 45921600 | 0
|  |  | 9=8-7: Net Total | 45921600 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0 |  |  | future Scope
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0 |  |  | No meter
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 45921600
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 45680640; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 45680640
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 45680640 | MOGBAZAR 33 KV NET IMPORT |  | 45566400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 114240
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2501%
| 132 KV TOTAL IMPORT |  | 4: 45680640
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming |  | 33 | IMPORT | 76026303 | 1 | 10062.5 | 10094.56 | 32.06 | 480000 | 15388800 |  | 15427381.4221
| 132/33 KV GT-2 Incomming |  | 33 |  | 76026307 | 1 | 10057.53 | 10089.58 | 32.05 | 480000 | 15384000 |  | 15422569.388
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 8261.3 | 8292.12 | 30.82 | 480000 | 14793600 |  | 14830689.1899
|  |  | 7: 0; 8: 0; 10: Total | 45566400 |  | 45680640
| MOGBAZAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. |  | 33 |  | 6604465 | 1 | 7025.58 | 7038.34 | 12.76 | 180000 |  | 2296800 | 2300417.8861 |  | 16335190.4879 | MOGBAZAR 33/11 KV SS | 2.8235 | 33/11 KV Transformer No.1. | 2300417.8861 | 2990020.124 | -689602.238 | -23.0635 | OK
| 33/11 KV Transformer No.2. |  | 33 |  | 202006985 | 1 | 35663032846 | 35669075293 | 6042447 | 3 | T2 Incomer side | 4470300 | 4477341.5517 |  |  |  |  | 33/11 KV Transformer No.2. | 4477341.5517 | 5386051.0203 | -908709.4686 | -16.8715 | OK
| 33/11 KV Transformer No.3. |  | 33 |  | 6604338 | 1 | 7139.46 | 7166.66 | 27.2 | 180000 |  | 4896000 | 4903712.1082 |  |  |  |  | 33/11 KV Transformer No.3. | 4903712.1082 | 5907773.9006 | -1004061.7924 | -16.9956 | OK
| 33/11 KV Transformer No.4 |  | 33 |  |  | 1 | 1134977 | 1161118 | 26141 | 180000 | T4 Incomer side | 4646400 | 4653718.9419 |  |  |  |  | 33/11 KV Transformer No.4 | 4653718.9419 | 5868027.4096 | -1214308.4677 | -20.6936 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 16309500 | 16335190.4879 |  |  |  |  | 33 KV Feeders | 16335190.4879 | 20151872.4546 | -3816681.9667 | -18.9396 | OK
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 |  | 76026300 | 1 | 6785.52 | 6802.73 | 17.21 | 360000 |  | 6195600 | 6205359.2193 |  | 16441858.2452 | Tejgoan 33/11 kv ss | 0.58489 | 33 kV Tejgaon U/G Feeder-1 | 6205359.2193 | 7786698.9333 | -1581339.714 | -20.3082 | OK
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 |  | 06604453 | 1 | 6628.97 | 6657.36 | 28.39 | 360000 |  | 10220400 | 10236499.0259 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 10236499.0259 | 13076595.5636 | -2840096.5377 | -21.7189 | OK
10 | Bashundhara City |  | 33 |  | 660434 | 1 | 803.19 | 814.02 | 10.83 | 180000 |  | 1949400 | 1952470.6666 | Shere b.nagar | 4600835.7721 | Ispahani 33/11 kv ss | 0.92584 | Bashundhara City | 1952470.6666 | 2191476.9852 | -239006.3186 | -10.9062 | OK
11 | Ispahani-1 |  | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Ispahani-2 |  | 33 |  |  | 1 | 3957.05 | 3982.57 | 25.52 | 180000 |  | 4593600 | 4600835.7721 |  | 0 | Green Road Dormatory 33/11 kv ss | -0.86776 | Ispahani-2 | 4600835.7721 | 5774081.1579 | -1173245.3858 | -20.3192 | OK
13 | 33 kV Green Road Dormitory |  | 33 |  | 76026305 | 1 | 8111.66 | 8111.66 | 0 | 180000 | Reading From G. Dormitory Side | 0 | 0 |  |  |  |  | 33 kV Green Road Dormitory | 0 | 5689057.7928 | -5689057.7928 | -100 | CHECK
14 | 33 KV T&T-1 |  | 33 |  | 6604337 | 1 | 4653.65 | 4673.82 | 20.17 | 180000 |  | 3630600 | 3636318.8685 |  | 6041301.2039 | T&T 33/11 kv ss | 1.0112 | 33 KV T&T-1 | 3636318.8685 | 4233001.2995 | -596682.431 | -14.096 | OK
13 | 33 KV T&T-2 |  | 33 |  | 6604336 | 1 | 5745.52 | 5758.86 | 13.34 | 180000 |  | 2401200 | 2404982.3354 |  |  |  |  | 33 KV T&T-2 | 2404982.3354 | 5136330.6421 | -2731348.3066 | -53.177 | CHECK
14 | 33KV Karwan Bazar |  | 33 |  | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | -0.22661 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | AT-1 |  | 33 |  | 6603338 | 1 | 2569.26 | 2724.99 | 155.73 | 80 |  | 12458.4 | 12478.0243 |  |  |  |  | AT-1 | 12478.0243 | 16597.1711 | -4119.1468 | -24.8184 | OK
20 | AT-2 |  | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 29003258.4 | 29048943.9121 |  |  |  |  | 0 | 29048943.9121 | 43903839.5454 | -14854895.6333 | -33.8351 | OK
|  |  | 9=8-7: Grand Total | 45384134.4 | 45312758.4 | 45384134.4 | 0.15752
-0.3377
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 1952470.6666
|  |  | 9=8-7: Total =; 10: 1952470.6666 | 0 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 |  | 11 | Import | 6604457 | 1 | 544213.6 | 546486.3 | 2272.7 | 1000 | 2272700 |  | 2289927.2418
2 | 33/11 kV Transformer-2 |  | 11 | Import | 30/11009-1101 | 1 | 596523.4 | 600993.7 | 4470.3 | 1000 | 4470300 |  | 4504185.2197
3 | 33/11 kV Transformer-3 |  | 11 | Import | 6604454 | 1 | 592450.3 | 597273.2 | 4822.9 | 1000 | 4822900 |  | 4859457.955
4 | 33/11 kV Transformer-4 |  | 11 | Import |  | 1 | 1124.16 | 1153.2 | 29.04 | 160000 | 4646400 |  | 4681620.0714
|  |  | 7: 0; 8: 0; 10: Total | 16212300 |  | 16335190.4879
| MOGBAZAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 40966.6 | 41105.9 | 139.3 | 1000 |  | 139300 | 140940.5878 | Kakrail |  |  |  | 11 kV Doctor's Lane | 140940.5878 | 170232.3057 | -29291.7179 | -17.2069 | OK
2 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 80957.2 | 81024 | 66.8 | 1000 |  | 66800 | 67586.7284 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 67586.7284 | 136288.0862 | -68701.3578 | -50.4089 | CHECK
3 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 |  | 11 | T-1 | 30/11004-1101 | 1 | 120741.7 | 121092.2 | 350.5 | 1000 |  | 350500 | 354627.9687 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 354627.9687 | 467141.9849 | -112514.0162 | -24.0856 | OK
7 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 132139.2 | 133873.6 | 1734.4 | 1000 |  | 1734400 | 1754826.6729 | Moghbazar |  |  |  | 11KV Ambagan | 1754826.6729 | 2252689.725 | -497863.0521 | -22.1008 | OK
[7 empty] | 0 | 0
5 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 148899.1 | 150222.7 | 1323.6 | 1000 |  | 1323600 | 1339188.5287 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1339188.5287 | 1537918.5242 | -198729.9955 | -12.922 | OK
3 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10125.5 | 10241.6 | 116.1 | 1000 |  | 116100 | 117467.3528 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 117467.3528 | 150704.1553 | -33236.8025 | -22.0543 | OK
4 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 128558 | 130036 | 1478 | 1000 |  | 1478000 | 1495406.9549 | Kakrail |  |  |  | 11 kV Bangla Motor | 1495406.9549 | 1911100.4557 | -415693.5008 | -21.7515 | OK
1 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 178896.5 | 180854.9 | 1958.4 | 1000 |  | 1958400 | 1981464.8041 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1981464.8041 | 2346752.0201 | -365287.216 | -15.5657 | OK
[7 empty] | 0 | 0
6 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 123990 | 125174.5 | 1184.5 | 1000 | Estimated | 1530219.6 | 1548241.5645 | Kakrail | 130 |  |  | 11 kV Iskaton | 1548241.5645 | 1803211.1873 | -254969.6228 | -14.1398 | OK
5 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 89088.7 | 90371.6 | 1282.9 | 1000 |  | 1282900 | 1298009.1897 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1298009.1897 | 1555095.1172 | -257085.9275 | -16.5318 | OK
2 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124248.6 | 124552.3 | 303.7 | 1000 |  | 303700 | 307276.7877 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 307276.7877 | 363366.7355 | -56089.9478 | -15.4362 | OK
3 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 116054.5 | 116794.1 | 739.6 | 1000 |  | 739600 | 748310.5439 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 748310.5439 | 931830.1708 | -183519.627 | -19.6945 | OK
4 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 44614.9 | 45007.6 | 392.7 | 1000 |  | 392700 | 397324.9737 | Kakrail |  |  |  | 11 kV BSRS Feeder | 397324.9737 | 478388.5637 | -81063.5899 | -16.9451 | OK
2 | 11 kV Vumi Bhaban |  | 11 | T-3 | 21101039 | 1 | 8997.2 | 9098.9 | 101.7 | 1000 |  | 101700 | 102897.7587 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 102897.7587 | 143547.2416 | -40649.4829 | -28.3178 | OK
5 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | check | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0 | 11653570.4165 | 11517919.6 | 11653570.4165 | 1.1777 |  |  |  |  | 11653570.4165 | 14248266.2732
1 | 11 kV TCB Feeder | C608P | 11 | T-4 |  | 1 | 36868.9 | 37126.3 | 257.4 | 1000 |  | 257400 | 275835.9679 | Kakrail |  |  |  | 11 kV TCB Feeder | 275835.9679 | 327449.4305 | -51613.4626 | -15.7623 | OK
2 | 11 kV Tejgaon SS-2 |  | 11 | T-4 |  | 1 | 34285.7 | 35724.6 | 1438.9 | 1000 |  | 1438900 | 1541959.4958 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1541959.4958 | 1519526.851 | 22432.6448 | 1.4763 | OK
3 | Holy Day Inn | C108HY | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 306390 | 328334.8182 | Tejgaon |  |  |  | Holy Day Inn | 328334.8182 | 421689.4191 | -93354.6009 | -22.1382 | OK
4 | Polly Bhabon-2 | C608PB | 11 | T-4 |  | 1 | 18384.8 | 18385 | 0.2 | 1000 | According to AMR meter reading | 16146 | 17302.438 | Kakrail |  |  |  | Polly Bhabon-2 | 17302.438 | 23296.5077 | -5994.0697 | -25.7295 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 |  | 1 | 20174.3 | 21533.5 | 1359.2 | 1000 |  | 1359200 | 1456551.0784 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1456551.0784 | 1783228.8258 | -326677.7474 | -18.3195 | OK
6 | 11 kV Tejturibazar | C608X | 11 | T-4 |  | 1 | 132923.9 | 133302 | 378.1 | 1000 |  | 378100 | 405180.9614 | Kakrail |  |  |  | 11 kV Tejturibazar | 405180.9614 | 781650.0519 | -376469.0905 | -48.1634 | CHECK
7 | Songsad |  | 11 | T-4 |  | 1 | 3864.8 | 3864.8 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Songsad | 0 | 154587.5799 | -154587.5799 | -100 | CHECK
| Chennel 24 |  | 11 | T-4 |  | 1 | 7327.44 | 7329.92 | 2.48 | 1000 |  | 2480 | 2657.627 | Moghbazar |  |  |  | Chennel 24 | 2657.627 | 3644.2295 | -986.6025 | -27.073 | OK
8 | Sonargaon | C608K | 11 | T-4 |  | 1 | 41957.9 | 42568 | 610.1 | 1000 |  | 610100 | 653797.6846 | Kakrail |  |  |  | Sonargaon | 653797.6846 | 888533.2859 | -234735.6013 | -26.4183 | OK
| AT -1 |  | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 |  | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[11 empty] | 4681620.0714 | 4368716 | 4681620.0714 | 7.1624
|  |  | 10: Total | 16335190.4879 | 15886635.6 | 16335190.4879 | 2.8235
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH | [13 empty] | AMR Meter Information
|  |  | 6: Moghbazar; 7: at 33 KV level; 9=8-7: 2064761.0876 | [13 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
|  |  | 6: Tejgaon; 7: at 33 KV level; 9=8-7: 7131536.6451 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 69210 | 3000
|  |  | 6: Kakrail; 7: at 33 KV level; 9=8-7: 7138892.7551 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 237180 | 3000
|  |  | 6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 0 | [13 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 16146 | 300
[6 empty] | Total = |  |  | 16335190.4879 | 0
AMR Meter Information
[24 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[24 empty] | Shah Garments | 832.6 | 850.51 | 229.22 | 234.38
[24 empty] | Habib Hotel | 2794.53 | 2852.4 | 925.49 | 946.68
[24 empty] | The Joint Director BRDB | 1367.9 | 1415.14 | 262.9 | 269.48
[26 empty] | 832.6 | 229.22
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [24 empty] | 2794.53 | 925.49
[26 empty] | 1367.9 | 262.9
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 |  | 33 | 0 | 6604337 | 1 | 4653.65 | 4673.82 | 20.17 | 180000 | 0 | 3630600 | 3636318.8685
13 | 33 KV T&T-2 |  | 33 | 0 | 6604336 | 1 | 5745.52 | 5758.86 | 13.34 | 180000 | 0 | 2401200 | 2404982.3354
0 | Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 333.6908 | 343.3399 | 9.6491 | 240000 | 0 | 2315784 | 2317613.4485
|  |  | 10: Total | 0 | 8347584 | 8358914.6524
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder |  | 33 | Import | DHK60891 | 1 | 1006947 | 1006947 | 0 | 360 | 0
2 | 33 kV Moghbazar-2 Feeder |  | 33 | Import | DHK68131 | 1 | 898200 | 898200 | 0 | 360 | 0
| 33 kV Ullon Feeder |  | 33 | Import | DHK68132 | 1 | 349.9 | 362.7 | 12.8 | 180000 | 2304000
|  |  | 7: 0; 8: 0; 10: Total | 2304000 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 1031989 | 1031989 | 0 | 180 |  | 0
4 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 900418 | 917708 | 17290 | 180 |  | 2401200 |  |  | Meter Problem
|  |  | 10: Total |  | 2401200 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 8358914.6524; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8358914.6524
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 8358914.6524 | 33/11 KV XF LV SIDE |  | 23055480
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -14696565.3476
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -175.8%
| TOTAL IMPORT |  | 4: 8358914.6524
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 136043 | 155985 | 19942 | 180 | 3589560 |  | 1301418.3908 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 1021744 | 1021744 | 108144 | 180 | 19465920 |  | 7057496.2616 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 23055480 |  | 8358914.6524 | -63.7443 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 208557 | 225815 | 17258 | 60 |  | 1035480 | 1045950.5553 | Kakrail |  |  |  | 11 kV post office | 1045950.5553 | 350929.0306 | 695021.5246 | 198.0519 | FAULT
2 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 491607 | 508205 | 16598 | 60 |  | 995880 | 1005950.1284 | Kakrail |  |  |  | 11 kV anarkoli | 1005950.1284 | 1232617.5702 | -226667.4418 | -18.3891 | OK
3 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 963754 | 968143 | 4389 | 60 |  | 263340 | 266002.8385 | Moghbazar |  |  |  | 11 kV sonalibagh | 266002.8385 | 363967.9203 | -97965.0818 | -26.9159 | OK
4 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1987746 | 1999157 | 11411 | 60 |  | 684660 | 691583.1374 | Moghbazar |  |  |  | 11 Kv desh tv | 691583.1374 | 808883.1556 | -117300.0182 | -14.5015 | OK
5 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 670.9 | 690.8 | 19.9 | 60000 |  | 1194000 | 1206073.4761 | Moghbazar |  |  |  | 11 Kv Btcl | 1206073.4761 | 1469087.5693 | -263014.0933 | -17.9032 | OK
1 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 916060 | 923585 | 7525 | 60 |  | 451500 | 456065.4727 | Kakrail |  |  |  | 11 kV century | 456065.4727 | 614479.8006 | -158414.3279 | -25.7802 | OK
2 | 11 kV cinema hall |  | 11 | Mogbazar | DHK60979 | 1 | 522676 | 535968 | 13292 | 60 |  | 797520 | 805584.354 | Moghbazar |  |  |  | 11 kV cinema hall | 805584.354 | 981161.6979 | -175577.344 | -17.8948 | OK
3 | 11 kV malibagh bazar |  | 11 | Khailgaon | DHK61106 | 1 | 782487 | 803461 | 20974 | 60 |  | 1258440 | 1271165.0797 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1271165.0797 | 1621719.2778 | -350554.1981 | -21.6162 | OK
4 | 11 kv Sherebangla | D1105G | 11 |  | DHK60915 | 1 | 765116 | 782199 | 17083 | 60 |  | 1024980 | 1035344.3815 | Moghbazar |  |  |  | 11 kv Sherebangla | 1035344.3815 | 1275392.2083 | -240047.8268 | -18.8215 | OK
5 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 355079 | 364525 | 9446 | 60 |  | 566760 | 572490.9575 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 572490.9575 | 647224.5235 | -74733.566 | -11.5468 | OK
6 | Auxiliary |  |  | Export | U0004461 | 1 | 8288.88 | 8333.5 | 44.62 | 60 |  | 2677.2 | 2704.2713 | Moghbazar |  |  |  | Auxiliary | 2704.2713 | 3869.1873 | -1164.916 | -30.1075 | OK
|  |  | 10: Grand Total | 8358914.6524 | 8275237.2 | 8358914.6524 | 1.0112
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 2507966.1564
[6 empty] | Moghbazar | at 33 KV level |  | 4579783.4163
[6 empty] | Khilgaon | at 33 KV level |  | 1271165.0797
[6 empty] | Total = |  |  | 8358914.6524 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 |  | 132 | IMPORT | 8993681 | 1 | 2714.49 | 2732.15 | 17.66 | 1440000 | 0 | 25430400
| Ullon-1 |  | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 25430400
|  |  | 9=8-7: Net Total | 25430400
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) |  | 132 |  | 8993624 | 1 | 4864.387 | 4885.436 | 21.049 | 960000 | 0 | 20207040
| Maniknager-2 (new line to ullon) |  | 132 |  |  | 1 | 11.083 | 11.083 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 20207040
|  |  | 9=8-7: Net Total | 20207040
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 |  | 132 |  | 8993659 | 1 | 4438.485 | 4448.367 | 9.882 | 960000 | 0 | 9486720
| Ullon U/G-1 |  | 132 |  |  | 1 | 1.561 | 1.561 | 0 | 960000 | 0 | 0
| Ullon U/G-2 |  | 132 |  | 8993660 | 1 | 4121.721 | 4130.91 | 9.189 | 960000 | 0 | 8821440
| Ullon U/G-2 |  | 132 |  |  | 1 | 1.33 | 1.33 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 18308160
|  |  | 9=8-7: Net Total | 18308160
| ULLON 132 KV SIDE (RECEIVING) | [9 empty] | 63945600
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) |  | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
| EXPORT TO OTHERS 132/33 KV SS | [13 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 |  | 132 |  |  | 1 | 1632768 | 1632768 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 |  | 132 |  |  | 1 | 2212585 | 2235495 | 22910 | 1000 |  | 22910000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 |  | 132 |  |  | 1 | 2974112 | 2991477 | 17365 | 1000 |  | 17365000 |  |  | 132 kV Ullon CKT-3 | 31978000
|  |  | 10: Total |  | 40275000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 23670600
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 4: 25430400; 6: EXPORT TO OTHER S/S; 9=8-7: 40275000 | 132 KV NET IMPORT |  | 23670600
| HORIPUR 132 SIDE (TARIFF POINT) |  | 4: 20207040; 6: 132 KV Net EXPORT; 9=8-7: 23670600 | 132/33 KV GT LV Side |  | 23332608
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 18308160 | LOSS UNITS=>(132 HV-33 LV) |  | 337992
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.428%
| 132 KV TOTAL IMPORT |  | 4: 63945600
33 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | BD001812 | 1 | 2234.826 | 2257.2727 | 22.4467 | 480000 | 10774416 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming |  | 33 | Import | BD001858 | 1 | 2155.0415 | 2177.0059 | 21.9644 | 480000 | 10542912 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming |  | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 2015280 |  |  |  | Estimated | [5 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 23332608 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1666.769 | 1690.629 | 23.86 | 240000 |  | 5726400 | 5730923.8044 |  | 12736053.4253 | Taltola 33/11 kv ss | 1.1177 | Taltala-1 | 5730923.8044 | 9041864.5151 | -3310940.7107 | -36.6179 | OK
| Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 333.6908 | 343.3399 | 9.6491 | 240000 |  | 2315784 | 2317613.4485 |  |  |  |  | Mgbazar T&T | 2317613.4485 | 0 | 2317613.4485 | #DIV/0! | #DIV/0!
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9124 | 1163.9124 | 0 | 240000 |  | 0 | 0 |  | 2317613.4485 | Mgbazar T&T 33/11 kv ss | 1.0112 | Kakrail | 0 | 24.0031 | -24.0031 | -100 | CHECK
2 | Taltala-2 |  | 33 | Export | BD001837 | 1 | 2610.6135 | 2639.7785 | 29.165 | 240000 |  | 6999600 | 7005129.6209 |  |  |  |  | Taltala-2 | 7005129.6209 | 3325434.8165 | 3679694.8044 | 110.653 | FAULT
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 0 | Kakrail 33/11 kv ss | 0.39893 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 1.6403 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3194 | 79.3331 | 0.0137 | 240000 | From Downstream | 2015280 | 2016872.053 |  | 0 | Tejgoan 33/11 kv ss | 0.58489 | Khailgaon | 2016872.053 | 922198.3633 | 1094673.6897 | 118.7026 | FAULT
4 | AT at GIS Building |  | 415 | Export | DHKE4577 | 1 | 155214 | 157988 | 2774 | 1 |  | 2774 | 2776.1914 |  | 2016872.053 | Khilgoan 33/11 kv ss | 0.23283 | AT at GIS Building | 2776.1914 | 3515.4512 | -739.2598 | -21.0289 | OK
|  |  | 7: 0; 8: 0; 10: TOTAL= |  | 17059838 | 17073315.1183 |  |  |  |  | 0 | 17073315.1183 | 13293037.1493 | 3780277.969 | 28.438 | OK
| 33 KV Local Feeder -1 |  | 33 | NET IMPORT |  | 1 | 1187.637 | 1200.8375 | 13.2005 | 240000 |  | 3168120 | 3170622.7862 |  | 6259292.8817 | Ullon 33/11 kv ss | 0.71194 | 33 KV Local Feeder -1 | 3170622.7862 | 4153181.057 | -982558.2708 | -23.658 | OK
| 33KV Local Feeder- 2 |  | 33 |  |  | 1 | 914.402 | 927.2613 | 12.8593 | 240000 |  | 3086232 | 3088670.0955 |  |  |  |  | 33KV Local Feeder- 2 | 3088670.0955 | 4030645.3297 | -941975.2342 | -23.3703 | OK
|  |  | 10: TOTAL= |  | 6254352 | 6259292.8817 |  |  |  |  | 0 | 6259292.8817 | 8183826.3867 | -1924533.505 | -23.5163 | OK
|  |  | 10: Grand Total | 23332608 | 23314190 | 23332608 | 0.078999
11 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 186 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 100 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 6254352 |  | 6259292.8817 |  |  | 86 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [14 empty] | 28.6667 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 706255.2 | 711283.282 | Moghbazar | 60 | 128.6667 |  | West Malibagh | 711283.282 | 977173.2999 | -265890.0179 | -27.2101 | OK
2 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1294801.2 | 1304019.3504 | Moghbazar | 110 |  |  | Ullon | 1304019.3504 | 1832199.9373 | -528180.587 | -28.8277 | OK
3 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1235946.6 | 1244745.7435 | Moghbazar | 105 |  |  | Mohanagar | 1244745.7435 | 1526833.2811 | -282087.5376 | -18.4753 | OK
4 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 918131.76 | 924668.2666 | Moghbazar | 78 |  |  | Bagichartek | 924668.2666 | 1038246.6311 | -113578.3645 | -10.9394 | OK
1 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1177092 | 1185472.1367 | Moghbazar | 100 |  |  | Mirbagh | 1185472.1367 | 1710053.2748 | -524581.1381 | -30.6763 | OK
2 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 882819 | 889104.1025 | Moghbazar | 75 |  |  | West Rampura | 889104.1025 | 1099319.9624 | -210215.8599 | -19.1224 | OK
3 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 |  | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 |  | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6259292.8817 | 6215045.76 | 6259292.8817 | 0.71194
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 6259292.8817
[6 empty] | Total = |  |  | 6259292.8817 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 |  | 132 | Export | 50146667 | 1 | 1867.274 | 1886.879 | 19.605 | 960000 | 0 | 18820800
2 | Rampura to Madartek-2 |  | 132 | Export | 50146668 | 1 | 1661.144 | 1680.527 | 19.383 | 960000 | 0 | 18607680
|  |  | 9=8-7: Total Import/Export | 0 | 37428480
|  |  | 9=8-7: Net Total | 37428480
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 |  | 132 | Import | SIEM0492 | 1 | 1650013 | 1668805 | 18792 | 1000 | 18792000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 |  | 132 | Import | SIEM0489 | 1 | 1599552 | 1618218 | 18666 | 1000 | 18666000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 37458000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 37458000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| MADERTEK 132 KV SIDE |  | 7: 0; 8: 0
3 | 133 kV GT-1 |  | 132 | Export |  | 1 | 1486557 | 1505378 | 18821 | 1000 |  | 18821000
4 | 133 kV GT-2 |  | 132 | Export |  | 1 | 1474412 | 1493107 | 18695 | 1000 |  | 18695000
|  |  | 10: Total |  | 37516000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 37428480; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 37428480
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 37428480 | 33 KV NET IMPORT |  | 37609000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -180520
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.4823%
| 132 KV TOTAL IMPORT |  | 4: 37428480
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0516 | 1 | 1635234 | 1654069 | 18835 | 1000 | 18835000 |  | 18744593.6026
2 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0515 | 3 | 543077 | 549335 | 6258 | 1000 | 18774000 |  | 18683886.3974
|  |  | 7: 0; 8: 0; 10: Total | 37609000 |  | 37428480
| MADERTEK 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kv Transforfers |  | 7: 0; 8: 0
1 | 33 kV T-1 |  | 33 | Import | SIEM0512 | 1 | 420830 | 423836 | 3006 | 2000 |  | 6012000 | 6012077.1016 |  | 14666188.0859 | Madartek 33/11 kv ss
2 | 33 kV T-3 |  | 33 | Export |  | 1 | 81155 | 82436 | 1281 | 2000 |  | 2562000 | 2562032.8567
2 | 33 kV T-2 |  | 33 | Export | SIEM0505 | 1 | 423956 | 427002 | 3046 | 2000 |  | 6092000 | 6092078.1276
| 33 kv Feeders |  | 7: 0; 8: 0; 10: Total |  | 14666000 | 14666188.0859 |  | 8412107.8807 | Banasree 33/11 kv ss
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 116881 | 118449 | 1568 | 2000 |  | 3136000 | 3136040.218
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 365258 | 370267 | 5009 | 2000 |  | 10018000 | 10018128.4771 |  | 10018128.4771 | Goran 33/11 kv ss
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 38986 | 39708 | 722 | 6000 |  | 4332000 | 4332055.5563
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 100415 | 103053 | 2638 | 2000 |  | 5276000 | 5276067.6627 |  | 4332055.5563 | Amulia 33/11 kv ss
|  |  | 10: Total |  | 22762000 | 22762291.9141
|  |  | 9=8-7: Grand Total | 37428480 | 37428000 | 37428480 | 0.0012825
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | GJU 71154 | 1 | 393620.5 | 396603.8 | 2983.3 | 2000 | 5966600 |  | 6009124.7208 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | GJU 71155 | 1 | 396916.7 | 399942.9 | 3026.2 | 2000 | 6052400 |  | 6095536.2283 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming |  | 11 | Import | 6604399 | 1 | 4745.57 | 4759.7 | 14.13 | 180000 | 2543400 |  | 2561527.1369 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 14562400 |  | 14666188.0859 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 15.7858 | 17.0895 | 1.3037 | 1000000 |  | 1303698 | 1312980.8765 | Mugdapara |  |  |  | Sobujbagh | 1312980.8765 | 1733090.4653 | -420109.5888 | -24.2405 | OK
2 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 105215.6 | 106484.9 | 1269.3 | 1000 |  | 1269300 | 1278337.9483 | Mugdapara |  |  |  | Madertek | 1278337.9483 | 1814364.7668 | -536026.8185 | -29.5435 | OK
3 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 6227.8 | 7446.5 | 1218.7 | 1000 |  | 1218700 | 1227377.6551 | Mugdapara |  |  |  | Rajarbagh | 1227377.6551 | 2135456.6106 | -908078.9555 | -42.5239 | CHECK
| Goran | A921G | 11 |  | X1390296 | 1 | 34326.4 | 35532.5 | 1206.1 | 1000 |  | 1206100 | 1214687.9378 | Bashabo |  |  |  | Goran | 1214687.9378 | 1825010.9149 | -610322.9771 | -33.4422 | OK
5 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 14225.436 | 15256.78 | 1031.344 | 1000 |  | 1031344 | 1038687.6018 | Mugdapara |  |  |  | Dhakhingaon | 1038687.6018 | 1446701.0468 | -408013.445 | -28.203 | OK
6 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | Manda | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1479.3345 | 1661.0999 | 181.7654 | 1000 |  | 181765.4 | 183059.6459 | Mugdapara |  |  |  | Green Model Town | 183059.6459 | 244346.2732 | -61286.6273 | -25.0819 | OK
1 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 4970.5368 | 5343.364 | 372.8272 | 1000 |  | 372827.2 | 375481.886 | Mugdapara |  |  |  | Biswa Road | 375481.886 | 578366.2569 | -202884.3709 | -35.0789 | OK
2 | Mugdapara | B921P | 11 |  | X0854272 | 1 | 4681.7 | 4957.2 | 275.5 | 1000 |  | 275500 | 277461.6755 | Maniknagar |  |  |  | Mugdapara | 277461.6755 | 259324.0979 | 18137.5777 | 6.9942 | OK
| Singapur | F221S | 11 |  | X1390302 (N) | 1 | 40431.5 | 41999.2 | 1567.7 | 1000 |  | 1567700 | 1578862.6815 | Banosree |  |  |  | Singapur | 1578862.6815 | 2168600.2792 | -589737.5978 | -27.1944 | OK
| Trimohony | F221T | 11 |  | X1390308 | 1 | 32844.1 | 34398.2 | 1554.1 | 1000 |  | 1554100 | 1565165.8438 | Banosree |  |  |  | Trimohony | 1565165.8438 | 2029899.048 | -464733.2042 | -22.8944 | OK
5 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 17776.286 | 19281.996 | 1505.71 | 1000 |  | 1505710 | 1516431.2867 | Mugdapara |  |  |  | Mayakanon | 1516431.2867 | 1620835.8728 | -104404.5862 | -6.4414 | OK
6 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 7166.0944 | 7716.29 | 550.1956 | 1000 |  | 550195.6 | 554113.2234 | Mugdapara |  |  |  | Ahmedbagh | 554113.2234 | 808655.6976 | -254542.4742 | -31.4772 | OK
1 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 748752 | 755370 | 6618 | 200 |  | 1323600 | 1333024.5871 | Mugdapara |  |  |  | Wasa Road | 1333024.5871 | 1795382.4839 | -462357.8968 | -25.7526 | OK
2 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 777256 | 783208 | 5952 | 200 |  | 1190400 | 1198876.1472 | Mugdapara |  |  |  | Nandipara | 1198876.1472 | 1488652.8964 | -289776.7491 | -19.4657 | OK
| AT-1 |  | 0.415 |  |  | 1 | 950.84 | 1021.24 | 70.4 | 80 |  | 5632 | 5672.1022 | Mugdapara |  |  |  | AT-1 | 5672.1022 | 12954.5544 | -7282.4522 | -56.2154 | CHECK
3 | AT-2 |  | 0.415 |  | 63394003 | 1 | 475.19 | 549.25 | 74.06 | 80 |  | 5924.8 | 5966.9871 | Mugdapara |  |  |  | AT-2 | 5966.9871 | 6056.6539 | -89.6668 | -1.4805 | OK
|  |  | 10: Total | 14666188.0859 | 14562497 | 14666188.0859 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 14666188.0859 | 14562497 | 14666188.0859 | 0.71204
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 3144028.5252
[6 empty] | Bashabo | at 33 KV level |  | 1214687.9378
[6 empty] | Maniknagar | at 33 KV level |  | 277461.6755
[6 empty] | Mugdapara | at 33 KV level |  | 10030009.9473
[6 empty] | Total = |  |  | 14666188.0859 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 | 0 | 76026300 | 1 | 6785.52 | 6802.73 | 17.21 | 360000 | 0 | 6195600 | 6205359.2193
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 | 0 | 06604453 | 1 | 6628.97 | 6657.36 | 28.39 | 360000 | 0 | 10220400 | 10236499.0259
0 | Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 16416000 | 16441858.2452
TEJGOAN 33 KV SIDE (RECEIVING)
|  |  | 7: 0; 8: 0; 10: Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 760200.3 | 783323.2 | 23122.9 | 270 |  | 6243183
2 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 639645 | 677710.6 | 38065.6 | 180 |  | 6851808
3 | 33/11 kV Transfomer-3 (T3) |  | 33 | Export | BD001872 | 1 | 235387.6 | 235650.9 | 263.3 | 180000 |  | 263300
|  |  | 10: Total |  | 13358291 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 16441858.2452; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TEJGOAN 33 KV NET IMPORT |  | 16441858.2452
| IMPORT-2 |  | 6: TEJGOAN 33 KV NET IMPORT; 9=8-7: 16441858.2452 | 33 KV TX HV Side |  | 13358291
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 3083567.2452
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 18.75%
| TOTAL IMPORT |  | 4: 16441858.2452
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 960009.4 | 991694.1 | 31684.7 | 180 | 5703246 |  | 9736777.3623 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 872676.3 | 893032.7 | 20356.4 | 180 | 3664152 |  | 6255566.0839 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming |  | 11 | Import | BD001875 | 1 | 235387.6 | 235650.9 | 263.3 | 1000 | 263300 |  | 449514.799 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 9630698 |  | 16441858.2452 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | C110U | 11 |  | DHK60950 | 1 | 305498.9 | 324180.3 | 18681.4 | 60 |  | 1120884 | 1127439.9287 | Tejgaon |  |  |  | Nakhal Para Feeder | 1127439.9287 | 1500089.328 | -372649.3993 | -24.8418 | OK
2 | Badda-Meghna Feeder | C110N | 11 |  | DHK60979 | 1 | 940674.7 | 952442.1 | 11767.4 | 60 |  | 706044 | 710173.5747 | Tejgaon |  |  |  | Badda-Meghna Feeder | 710173.5747 | 794267.6303 | -84094.0557 | -10.5876 | OK
3 | Rasulbagh Feeder | C110K | 11 |  | DHK60948 | 1 | 82062.5 | 107045.9 | 24983.4 | 60 |  | 1499004 | 1507771.5116 | Tejgaon |  |  |  | Rasulbagh Feeder | 1507771.5116 | 1806034.3017 | -298262.7901 | -16.5148 | OK
4 | Lukas | C171V | 11 |  | 8A021100948-02 | 1 | 73546915 | 75134351 | 1587436 | 1 |  | 1587436 | 1596720.7407 | Tejgaon |  |  |  | Lukas | 1596720.7407 | 2026298.4778 | -429577.7371 | -21.2001 | OK
5 | PWD RMU |  | 11 |  |  | 1 | 660047.1 | 661501.9 | 1454.8 | 1 |  | 1454.8 | 1463.309 | Tejgaon |  |  |  | PWD RMU | 1463.309 | 1806.986 | -343.677 | -19.0194 | OK
1 | Civil Aviation Feeder |  | 11 |  | DHK60977 | 1 | 984210.7 | 1019068.7 | 34858 | 60 |  | 2091480 | 2103712.8393 | Tejgaon |  |  |  | Civil Aviation Feeder | 2103712.8393 | 2870937.6357 | -767224.7964 | -26.7238 | OK
2 | Ahasanullah Eng. | C171L | 11 |  | DHK60867 | 1 | 900589.8 | 908328.2 | 7738.4 | 60 |  | 464304 | 467019.6637 | Tejgaon |  |  |  | Ahasanullah Eng. | 467019.6637 | 571155.4762 | -104135.8125 | -18.2325 | OK
3 | New GMG Feeder | C110M | 11 |  | DHK61106 | 1 | 151809.7 | 180726.9 | 28917.2 | 60 |  | 1735032 | 1745180.0137 | Tejgaon |  |  |  | New GMG Feeder | 1745180.0137 | 1868942.3881 | -123762.3744 | -6.6221 | OK
4 | Shikajo | C171Z | 11 |  | HA021101036-02 | 1 | 66059038 | 66732385 | 673347 | 1 |  | 673347 | 677285.3335 | Tejgaon |  |  |  | Shikajo | 677285.3335 | 862880.7653 | -185595.4318 | -21.5088 | OK
5 | Kahinur |  | 11 |  |  | 1 | 584798.7 | 602529.6 | 17730.9 | 60 |  | 1063854 | 1070076.3665 | Tejgaon |  |  |  | Kahinur | 1070076.3665 | 1309013.1381 | -238936.7716 | -18.2532 | OK
6 | Link road | C171X | 11 |  | 8A021100380-02 | 1 | 66112857 | 66526725 | 413868 | 1 |  | 413868 | 416288.669 | Tejgaon |  |  |  | Link road | 416288.669 | 724119.8808 | -307831.2118 | -42.5111 | CHECK
7 | Shanta | C110E | 11 |  |  | 1 | 341520.5 | 350241.3 | 8720.8 | 60 |  | 523248 | 526308.4207 | Tejgaon |  |  |  | Shanta | 526308.4207 | 628311.0309 | -102002.6102 | -16.2344 | OK
1 | Karnafuly Feeder | C110Y | 11 |  | DHK61084 | 1 | 36682 | 37300.6 | 618.6 | 1000 |  | 618600 | 622218.1242 | Tejgaon |  |  |  | Karnafuly Feeder | 622218.1242 | 807314.3803 | -185096.2561 | -22.9274 | OK
2 | Butex | C110BT | 11 |  |  | 1 | 1299 | 1403 | 104 | 1000 |  | 104000 | 104608.2847 | Tejgaon |  |  |  | Butex | 104608.2847 | 106281.4076 | -1673.1229 | -1.5742 | OK
3 | OriON LAB | C171A | 11 |  |  | 1 | 8377954 | 8454240 | 76286 | 1 |  | 76286 | 76732.1885 | Tejgaon |  |  |  | OriON LAB | 76732.1885 | 90864.5418 | -14132.3533 | -15.5532 | OK
4 | Nina kabbo | C171Y | 11 |  | 201101025-2 | 1 | 17647767 | 17854558 | 206791 | 1 |  | 206791 | 208000.4981 | Tejgaon |  |  |  | Nina kabbo | 208000.4981 | 261868.4978 | -53867.9998 | -20.5706 | OK
5 | Satrong | C171S | 11 |  | HA021100515-2 | 1 | 97172731 | 98397161 | 1224430 | 1 |  | 1224430 | 1231591.5581 | Tejgaon |  |  |  | Satrong | 1231591.5581 | 1888984.3136 | -657392.7555 | -34.8014 | OK
6 | South East RMU |  | 11 |  |  | 1 | 1108.7 | 1176.1 | 67.4 | 1000 |  | 67400 | 67794.2153 | Tejgaon |  |  |  | South East RMU | 67794.2153 | 115171.8675 | -47377.6523 | -41.1365 | CHECK
7 | Rangs Bhaban |  | 11 |  | HA021100939-2 | 1 | 881462 | 1006950 | 125488 | 1 |  | 125488 | 126221.9657 | Tejgaon |  |  |  | Rangs Bhaban | 126221.9657 | 151848.0457 | -25626.08 | -16.8761 | OK
8 | Babli | C171R | 11 |  |  | 1 | 60405.4 | 61327 | 921.6 | 1000 |  | 921600 | 926990.3383 | Tejgaon |  |  |  | Babli | 926990.3383 | 1047558.8549 | -120568.5166 | -11.5095 | OK
| SPL |  | 11 |  |  | 1 | 5307 | 5708.6 | 401.6 | 1000 |  | 401600 | 403948.9148 | Tejgaon |  |  |  | SPL | 403948.9148 | 470689.2376 | -66740.3228 | -14.1793 | OK
9 | DNCC Hospital |  | 11 |  |  | 1 | 17538 | 18258.1 | 720.1 | 1000 |  | 720100 | 724311.7867 | Tejgaon |  |  |  | DNCC Hospital | 724311.7867 | 958856.3113 | -234544.5246 | -24.4609 | OK
| 11/.415 kv Local transformer |  | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
|  |  | 10: Grand Total | 16441858.2452 | 16346250.8 | 16441858.2452 | 0.58489
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Tejgaon | at 33 KV level |  | 16441858.2452
[6 empty] | Total = |  |  | 16441858.2452 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 |  | 33 | 0 | 214393/44-2711 | 1 | 89.5259 | 4308.85 | 4219.3241 | 1000 | Estimated | 6556024.8 | 6393333.7849
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 5434948.8 | 5300077.8433
|  |  | 10: Total |  | 11990973.6 | 11693411.6282
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 33 | Import | DHKC9350 | 1 | 6431.12 | 30700.57 | 24269.45 | 270 | 6552751.5
2 | Shatmasjid-2 |  | 33 | Import | DHKC9354 | 1 | 35333.77 | 55611.4 | 20277.63 | 270 | 5474960.1
|  |  | 7: 0; 8: 0; 10: Total | 12027711.6
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  | 7: 0; 8: 0
1 | Transfomer-1 (T1) |  | 33 | Export | DHKC9353 | 1 | 80735.16 | 117157.52 | 36422.36 | 180 |  | 6556024.8
2 | Transfomer-2 (T2) |  | 33 | Export | DHKC9305 | 1 | 66005.32 | 96496.48 | 30491.16 | 180 |  | 5488408.8
|  |  | 10: Total |  | 12044433.6 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 4: 11693411.6282; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | ASADGATE 33 KV NET IMPORT |  | 11693411.6282
| IMPORT-2 |  | 6: ASADGATE 33 KV NET IMPORT; 9=8-7: 11693411.6282 | ASADGATE 11 KV NET IMPORT |  | 11909161.0844
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -215749.4562
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.845%
| TOTAL IMPORT |  | 4: 11693411.6282
11 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHKC9371 | 1 | 35405.06 | 59690.95 | 24285.89 | 180 | 6556024.8 |  |  |  | From Upstream | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHKC9337 | 1 | 66006.83 | 96200.99 | 30194.16 | 180 | 5434948.8 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 11990973.6 |  | 11693411.6282 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | D570T | 11 |  | DHKC9332 | 1 | 82497.17 | 84785.44 | 2288.27 | 60 |  | 137296.2 | 138463.2177 | Shere b.nagar |  |  |  | Gonobhaban | 138463.2177 | 186647.9358 | -48184.7181 | -25.8158 | OK
2 | Rapa Plaza Feeder | D270R | 11 |  | DHKC9339 | 1 | 31044.61 | 46040.31 | 14995.7 | 60 |  | 899742 | 907389.807 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 907389.807 | 1054413.3744 | -147023.5674 | -13.9436 | OK
3 | Shukrabad/ South Plaza | D570S | 11 |  | DHKC9324 | 1 | 71432.99 | 85995.04 | 14562.05 | 60 |  | 873723 | 881149.6455 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 881149.6455 | 1103197.1415 | -222047.496 | -20.1276 | OK
4 | Wasa O/H | C270W | 11 |  | DHKC9333 | 1 | 58765.81 | 70721.35 | 11955.54 | 60 |  | 717332.4 | 723429.7254 | Satmasjid |  |  |  | Wasa O/H | 723429.7254 | 739783.158 | -16353.4326 | -2.2106 | OK
5 | Bangabandhu Memorial Museum |  | 11 |  | DHKC9334 | 1 | 16332.37 | 16545.05 | 212.68 | 60 |  | 12760.8 | 12869.2668 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 12869.2668 | 18497.907 | -5628.6402 | -30.4285 | OK
6 | Iqbal Road O/H | D470Q | 11 |  | DHKC9330 | 1 | 48276.24 | 66650.02 | 18373.78 | 60 |  | 1102426.8 | 1111797.4278 | Shyamoli |  |  |  | Iqbal Road O/H | 1111797.4278 | 1464338.9745 | -352541.5467 | -24.0751 | OK
7 | Town Hall | D470W | 11 |  | DHKC9351 | 1 | 3102.61 | 29529.34 | 26426.73 | 60 |  | 1585603.8 | 1599081.4323 | Shyamoli |  |  |  | Town Hall | 1599081.4323 | 1961962.9278 | -362881.4955 | -18.4958 | OK
8 | Post Office | D470P | 11 |  | DHKC9331 | 1 | 33036.5 | 50889.76 | 17853.26 | 60 |  | 1071195.6 | 1080300.7626 | Shyamoli |  |  |  | Post Office | 1080300.7626 | 1412012.952 | -331712.1894 | -23.4921 | OK
9 | Shangshad Bhaban |  | 11 |  | DHKC9370 | 1 | 24023.67 | 24023.68 | 0.01 | 60 |  | 0.6 | 0.6051 | Shere b.nagar |  |  |  | Shangshad Bhaban | 0.6051 | 94824.6159 | -94824.0108 | -99.9994 | CHECK
10 | Jakir Hossain Road | C270J | 11 |  | DHKC9373 | 1 | 67793.29 | 83237.19 | 15443.9 | 60 |  | 926634 | 934510.389 | Satmasjid |  |  |  | Jakir Hossain Road | 934510.389 | 1496705.7735 | -562195.3845 | -37.5622 | OK
11 | New Colony O/H Feeder | C270N | 11 |  | DHKC9369 | 1 | 31606.58 | 48198.28 | 16591.7 | 60 |  | 995502 | 1003963.767 | Satmasjid |  |  |  | New Colony O/H Feeder | 1003963.767 | 1053637.6362 | -49673.8692 | -4.7145 | OK
12 | Aurangzeb Feeder | D470M | 11 |  | DHKC9321 | 1 | 34889.71 | 54002.53 | 19112.82 | 60 |  | 1146769.2 | 1156516.7382 | Shyamoli |  |  |  | Aurangzeb Feeder | 1156516.7382 | 1667662.8612 | -511146.123 | -30.6504 | OK
13 | Asadgate Local Feeder | C270E | 11 |  | DHKC9338 | 1 | 42257.12 | 52468.4 | 10211.28 | 60 |  | 612676.8 | 617884.5528 | Satmasjid |  |  |  | Asadgate Local Feeder | 617884.5528 | 1521583.8549 | -903699.3021 | -59.392 | CHECK
14 | Sonarbangla Road | D470R | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | D470H | 11 |  | DHKC9366 | 1 | 57194.89 | 83086.82 | 25891.93 | 60 |  | 1553515.8 | 1566720.6843 | Shyamoli |  |  |  | Humayun Road | 1566720.6843 | 1813580.3058 | -246859.6215 | -13.6117 | OK
16 | NHA | D470B | 11 |  | DHKC9374 | 1 | 65850.12 | 68657.31 | 2807.19 | 60 |  | 168431.4 | 169863.0669 | Shyamoli |  |  |  | NHA | 169863.0669 | 219431.6487 | -49568.5818 | -22.5895 | OK
17 | Auxiliary transformer |  | 0.415 |  |  | 1 | 667095 | 672271 | 5176 | 1 |  | 5176 | 5219.996 | Satmasjid |  |  |  | Auxiliary transformer | 5219.996 | 7644.43 | -2424.434 | -31.715 | OK
|  |  | 10: Grand Total | 11909161.0844 | 11808786.4 | 11909161.0844 | 0.85
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 1019613.4683
[6 empty] | Dhanmondi | at 33 KV level |  | 920259.0738
[6 empty] | Satmasjid | at 33 KV level |  | 3285008.4302
[6 empty] | Shyamoli | at 33 KV level |  | 6684280.1121
at 33 KV level
[6 empty] | Total = |  |  | 11909161.0844 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 116881 | 118449 | 1568 | 2000 | 0 | 3136000 | 3136040.218
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 100415 | 103053 | 2638 | 2000 | 0 | 5276000 | 5276067.6627
|  |  | 10: Total |  | 8412000 | 8412107.8807 | 0.0012825
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import |  | 1 | 2325280 | 5435140 | 3109860 | 1 | 3109860
2 | Madertek Circuit-02 |  | 33 | Import |  | 1 | 19510 | 5261020 | 5241510 | 1 | 5241510
3 | Ullon O/H |  | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
|  |  | 10: Total | 8351370 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 |  | 33 | Export | 14 | 1 | 8361040 | 11472400 | 3111360 | 1 |  | 3111360
2 | Transformer-02 |  | 33 | Export | 74 | 1 | 6889120 | 12130960 | 5241840 | 1 |  | 5241840 |  |  | Meter Problem
|  |  | 10: Total |  | 8353200
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 4: 8412107.8807; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 8412107.8807
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 8412107.8807 | 33 KV TX HV SIDE |  | 8353200
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 58907.8807
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.7003%
| TOTAL IMPORT |  | 4: 8412107.8807
11 KV SIDE of___BANASREE 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 3111360 |  | 3133301.7258 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | 198 | 1 | 0 | 0 | 0 | 1 | 5241840 |  | 5278806.155 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 8353200 |  | 8412107.8807 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | F292A | 11 |  | 141 | 1 | 2417760 | 3821920 | 1404160 | 1 |  | 1404160 | 1423037.4494 | Banosree |  |  |  | Angur Jora | 1423037.4494 | 2051370.0659 | -628332.6166 | -30.6299 | OK
2 | Block F-G Avenue | F299G | 11 |  | 68 | 1 | 5525600 | 6117160 | 591560 | 1 |  | 591560 | 599512.8999 | Banosree |  |  |  | Block F-G Avenue | 599512.8999 | 2148314.9942 | -1548802.0942 | -72.0938 | CHECK
3 | Banasree Main Road(Monpura) | F292P | 11 |  | 168 | 1 | 276520 | 766400 | 489880 | 1 |  | 489880 | 496465.9196 | Banosree |  |  |  | Banasree Main Road(Monpura) | 496465.9196 | 1014510.7585 | -518044.8389 | -51.0635 | CHECK
4 | Baitul Kuddus | F292Q | 11 |  | 62 | 1 | 6205400 | 7869640 | 1664240 | 1 |  | 1664240 | 1686613.9505 | Banosree |  |  |  | Baitul Kuddus | 1686613.9505 | 2119711.2807 | -433097.3302 | -20.4319 | OK
5 | Ideal | F214I | 11 |  |  | 1 | 538960 | 1080480 | 541520 | 1 |  | 541520 | 548800.1649 | Banosree |  |  |  | Ideal | 548800.1649 | 698230.2076 | -149430.0426 | -21.4013 | OK
6 | Central Mosque | F292C | 11 |  | 46 | 1 | 6352040 | 7883600 | 1531560 | 1 |  | 1531560 | 1552150.2079 | Banosree |  |  |  | Central Mosque | 1552150.2079 | 2014405.8899 | -462255.682 | -22.9475 | OK
7 | Larive | F299L | 11 |  | 47 | 1 | 3120560 | 3914200 | 793640 | 1 |  | 793640 | 804309.6523 | Banosree |  |  |  | Larive | 804309.6523 | 1248158.3596 | -443848.7073 | -35.5603 | OK
8 | Bank Colony | A299K | 11 |  |  | 1 | 8053280 | 8610600 | 557320 | 1 |  | 557320 | 564812.5793 | Khilgaon |  |  |  | Bank Colony | 564812.5793 | 1882703.3 | -1317890.7208 | -69.9999 | CHECK
9 | Salambagh | A299G | 11 |  |  | 1 | 6381080 | 6829880 | 448800 | 1 |  | 448800 | 454833.6424 | Khilgaon |  |  |  | Salambagh | 454833.6424 | 1308766.6526 | -853933.0102 | -65.2472 | CHECK
10 | Titas Road | A299T | 11 |  |  | 1 | 4635200 | 4913000 | 277800 | 1 |  | 277800 | 281534.7278 | Khilgaon |  |  |  | Titas Road | 281534.7278 | 1393019.0625 | -1111484.3347 | -79.7896 | CHECK
11 | AT-1 |  | 0.415 |  | 7734 | 1 | 3534.86 | 3571.06 | 36.2 | 1 |  | 36.2 | 36.6867 | Banosree |  |  |  | AT-1 | 36.6867 | 64.6367 | -27.95 | -43.2417 | CHECK
12 | AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 8412107.8807 | 8300516.2 | 8412107.8807 | 1.3444
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 7110926.9313
[6 empty] | Khilgaon | at 33 KV level |  | 1301180.9495
[6 empty] | Total = |  |  | 8412107.8807 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 365258 | 370267 | 5009 | 2000 | 0 | 10018000 | 10018128.4771
ULLON 33 KV SIDE | bar: 4
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 10018000 | 10018128.4771
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import | HA-030701133-03 | 1 | 108926360 | 108926360 | 0 | 1 | 0
2 | Ullon O/H |  | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GORAN 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | HA-030800176-03 | 1 | 23372460 | 27106240 | 3733780 | 1 |  | 3733780
2 | Transformer-02 |  | 33 | Export | HA-030701133-03 | 1 | 91501130 | 94701270 | 3200140 | 1 |  | 3200140
3 | Transformer-03 |  | 33 | Export | DHK-57075 | 1 | 12285.5 | 12413.92 | 128.42 | 120000 |  | 3084080 |  |  | Problem
|  |  | 10: Total |  | 10018000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 4: 10018128.4771; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10018128.4771
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 10018128.4771 | 33 KV TX HV SIDE |  | 10018000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 128.4771
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.001282%
| TOTAL IMPORT |  | 4: 10018128.4771
11 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming |  | 11 | IMPORT |  | 1 | 63953260 | 67679970 | 3726710 | 1 | 3726710 |  | 3735692.4304
| 33/11 kV Transfomer-2 Incoming |  | 11 |  |  | 1 | 99003240 | 102196020 | 3192780 | 1 | 3192780 |  | 3200475.5073
| 33/11 kV Transfomer-3 Incoming |  | 11 |  |  | 1 | 84043760 | 87118310 | 3074550 | 1 | 3074550 |  | 3081960.5394
|  |  | 7: 0; 8: 0; 10: Total | 9994040 |  | 10018128.4771
| GORAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Meradia | F214M | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 170 | 2001056.4 | 2033879.5103 | Banosree | Estimated |  |  | Meradia | 2033879.5103 | 378160.5224 | 1655718.9879 | 437.835 | FAULT
2 | Shipahibagh | A914S | 11 |  | HA-021001030-02 | 1 | 42070870 | 43252680 | 1181810 | 1 |  | 1181810 | 1201195.1008 | Bashabo |  |  |  | Shipahibagh | 1201195.1008 | 1194417.5741 | 6777.5267 | 0.56743 | OK
3 | Farazi Hospital | F214F | 11 |  | HA-030701081-03 | 1 | 51724280 | 52545470 | 821190 | 1 |  | 821190 | 834659.8902 | Banosree |  |  |  | Farazi Hospital | 834659.8902 | 663014.2572 | 171645.6329 | 25.8887 | OK
4 | West Bansree | F214W | 11 |  | New Meter | 1 | 98404140 | 99726960 | 1322820 | 1 |  | 1322820 | 1344518.0725 | Banosree |  |  |  | West Bansree | 1344518.0725 | 1500984.3633 | -156466.2908 | -10.4242 | OK
5 | Model School(Nearest) | F214D | 11 |  | HA-030701099-03 | 1 | 24729160 | 26588810 | 1859650 | 1 |  | 1859650 | 1890153.6365 | Banosree |  |  |  | Model School(Nearest) | 1890153.6365 | 2273552.5905 | -383398.954 | -16.8634 | OK
6 | Bhuiyan Para | F214V | 11 |  | HA-021100508-02 | 1 | 63138610 | 64706638 | 1568028 | 1 |  | 1568028 | 1593748.1926 | Banosree |  |  |  | Bhuiyan Para | 1593748.1926 | 2480699.3677 | -886951.1751 | -35.7541 | OK
7 | Bonobithi (Ideal) School | F214B | 11 |  | HA-021100879-02 | 1 | 20164310 | 21242510 | 1078200 | 1 |  | 1078200 | 1095885.5972 | Banosree |  |  |  | Bonobithi (Ideal) School | 1095885.5972 | 1387260.9532 | -291375.356 | -21.0036 | OK
8 | AT-01 |  | 0.415 |  | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 562.2168 | -562.2168 | -100 | CHECK
9 | AT-02 |  | 0.415 |  | 3043146 | 1 | 5084.2 | 5084.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-02 | 0 | 11959.1548 | -11959.1548 | -100 | CHECK
|  |  | 10: Grand Total | 9994040 | 9832754.4 | 9994040 | 1.6403
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 8792844.8992
[6 empty] | Bashabo | at 33 KV level |  | 1201195.1008
[6 empty] | Total = |  |  | 9994040 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 |  | 33 | 0 | SICAM | 1 | 4612 | 4612 | 0 | 1000 | Estimated | 10503000 | 10242362.8329
|  |  | 10: Total |  | 10503000 | 10242362.8329
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
2 | Shatmasjid-2 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
3 | Kallayanpur |  | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
|  |  | 10: Total | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 |  | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 |  | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 4: 10242362.8329; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALMATIA 33 KV NET IMPORT |  | 10242362.8329
| IMPORT-2 |  | 6: LALMATIA 33 KV NET IMPORT; 9=8-7: 10242362.8329 | LALMATIA 11 KV NET IMPORT |  | 10503000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -260637.1671
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -2.545%
| TOTAL IMPORT |  | 4: 10242362.8329
11 KV SIDE of___LALMATIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | DHK000180 | 1 | 3002013 | 3046616 | 44603 | 90 | 4014270 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | DHK000177 | 1 | 3053906 | 3126003 | 72097 | 90 | 6488730 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 10503000 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1412510.4 | 1437106.4117 | Dhanmondi | Estimated | 160 |  | Shankor O/H | 1437106.4117 | 1468016.3082 | -30909.8965 | -2.1056 | OK
2 | Bangabobondhu museum | D207B | 11 | Export |  | 1 | 629342 | 629342 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 100 |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 86479670 | 87980510 | 1500840 | 1 |  | 1500840 | 1526974.093 | Dhanmondi |  | 60 |  | Road No-13/A | 1526974.093 | 1886658.0381 | -359683.9451 | -19.0646 | OK
4 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 7608679 | 8383244 | 774565 | 1 |  | 774565 | 788052.4828 | Dhanmondi |  | 20 |  | Jaforabad | 788052.4828 | 2056165.5278 | -1268113.045 | -61.6737 | CHECK
5 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 120 |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26183.9 | 26317.7 | 133.8 | 3333.33 |  | 445999.554 | 453765.7341 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 453765.7341 | 575970.5227 | -122204.7885 | -21.2172 | OK
1 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71012.2 | 71326.8 | 314.6 | 3333.33 |  | 1048665.618 | 1066926.0087 | Dhanmondi |  |  |  | Road No -15 | 1066926.0087 | 1423833.9987 | -356907.99 | -25.0667 | OK
2 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79007.3 | 79310 | 302.7 | 3333.33 |  | 1008998.991 | 1026568.6676 | Dhanmondi |  |  |  | Road No-27 South | 1026568.6676 | 1364158.3566 | -337589.689 | -24.7471 | OK
| Road 25 | D207C | 11 | Export |  | 1 | 71389.6 | 71667.3 | 277.7 | 3333.3 |  | 925657.41 | 941775.8615 | Dhanmondi |  |  |  | Road 25 | 941775.8615 | 1290390.3315 | -348614.4699 | -27.0162 | OK
3 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38220.6 | 38312.4 | 91.8 | 3333.33 |  | 305999.694 | 311328.0598 | Dhanmondi |  |  |  | Ibne Sina | 311328.0598 | 402642.9556 | -91314.8958 | -22.6789 | OK
4 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 63193708 | 64469326 | 1275618 | 1 |  | 1275618 | 1297830.3074 | Dhanmondi |  |  |  | Road No-31 (PARI) | 1297830.3074 | 1076949.6203 | 220880.6871 | 20.5098 | OK
5 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | 138 | 1624386.96 | 1652672.3734 | Dhanmondi | Estimated |  |  | Satmoszid Road West | 1652672.3734 | 2233224.3406 | -580551.9672 | -25.9961 | OK
|  |  | 10: Grand Total | 10503000 | 10323241.627 | 10503000 | 1.7413
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Dhanmondi | at 33 KV level |  | 10503000
[6 empty] | Total = |  |  | 10503000 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) |  | 33 | 0 | BD001918 | 1 | 2172.52 | 2193.69 | 21.17 | 240000 | 0 | 5080800 | 5086783.0517
23 | Green Road Circuit-1 |  | 33 | 0 | BD001865 | 1 | 1502.1 | 1526.05 | 23.95 | 240000 | 0 | 5748000 | 5754768.7335
|  |  | 10: Total | 0 | 10828800 | 10841551.7853
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory |  | 3: 33; 4: EXPORT |  | 0
| Green Road Dormatory |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0
| 33/11 KV Transformer No.2. |  | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 4: 10841551.7853; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | Green Road 33 KV NET IMPORT |  | 10841551.7853
| IMPORT-2 |  | 6: Green Road 33 KV NET IMPORT; 9=8-7: 10841551.7853 | Green Road 11 KV NET IMPORT |  | 10776502.4746
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 10841551.7853 | LOSS UNITS=> |  | 65049.3107
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0.6%
| TOTAL IMPORT |  | 4: 10841551.7853
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 00138 | 1 | 3265238 | 3328979 | 63741 | 100 | 6374100
2 | Transfomer-2 Incoming |  | 11 | Import | HA-021101496 | 1 | 5650.806 | 6214.5824 | 563.7764 | 10000 | 5080800
|  |  | 7: 0; 8: 0; 10: Total | 11454900 |  | 10841551.7853
| Green Road 11 KV SIDE |  | 7: 0; 8: 0
1 | Lab aid/local RMU | C302L | 11 |  | 3C65883 | 1 | 73195 | 76794 | 3599 | 300 |  | 1079700 | 1099246.4449 | Paribag |  |  |  | Lab aid/local RMU | 1099246.4449 | 1368745.9116 | -269499.4668 | -19.6895 | OK
2 | Green View | C302V | 11 |  | DHK000151 | 1 | 68313.2 | 68593.9 | 280.7 | 3333.33 |  | 935665.731 | 952604.6387 | Paribag |  |  |  | Green View | 952604.6387 | 1155247.0433 | -202642.4047 | -17.541 | OK
3 | Central Road | C302C | 11 |  | 65943 | 1 | 37616 | 41167 | 3551 | 300 |  | 1065300 | 1084585.7532 | Paribag |  |  |  | Central Road | 1084585.7532 | 1542540.4225 | -457954.6694 | -29.6883 | OK
4 | New Market | D802N | 11 |  | DHK000194 | 1 | 47697.9 | 48019.6 | 321.7 | 3333.33 |  | 1072332.261 | 1091745.3233 | Jigatola |  |  |  | New Market | 1091745.3233 | 1265157.8423 | -173412.5189 | -13.7068 | OK
5 | DPH Feeder |  | 11 |  | HA-021100459 | 1 | 41984 | 42140.3 | 156.3 | 1 | 25 | 294273 | 299600.3974 | Paribag | Estimated |  |  | DPH Feeder | 299600.3974 | 308510.2151 | -8909.8177 | -2.888 | OK
6 | Dhanmondi Rd 4(md Banglo | D802F | 11 |  | 6604464 | 1 | 4573.53 | 4589.51 | 15.98 | 60000 |  | 958800 | 976157.721 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 976157.721 | 1290523.1633 | -314365.4423 | -24.3595 | OK
1 | Green Road East | C302X | 11 |  | HA-021101050 | 1 | 99752905 | 100777480 | 1024575 | 1 |  | 1024575 | 1043123.4845 | Paribag |  |  |  | Green Road East | 1043123.4845 | 1394173.8849 | -351050.4004 | -25.1798 | OK
2 | North Road | C302Z | 11 |  | HA-021100884 | 1 | 85256362 | 86548201 | 1291839 | 1 |  | 1291839 | 1315225.9221 | Paribag |  |  |  | North Road | 1315225.9221 | 1610609.432 | -295383.5099 | -18.3399 | OK
3 | Green road SS | C302W | 11 |  | DHK00135 | 1 | 22261302 | 23172245 | 910943 | 1 |  | 910943 | 927434.3375 | Paribag |  |  |  | Green road SS | 927434.3375 | 1235249.8127 | -307815.4752 | -24.9193 | OK
4 | Plane Moszid | C302A | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 706255.2 | 719040.9537 | Paribag | Estimated |  |  | Plane Moszid | 719040.9537 | 740424.5162 | -21383.5625 | -2.888 | OK
5 | Malancha | C302H | 11 |  | HA-021100953 | 1 | 37784204 | 39024399 | 1240195 | 1 |  | 1240195 | 1262646.9803 | Paribag |  |  |  | Malancha | 1262646.9803 | 1505893.42 | -243246.4397 | -16.153 | OK
| AT -1 |  | 7: 22891; 8: 22891; 10: 1 |  | 5000 | 5090.5179 | Paribag |  |  |  | AT -1 | 5090.5179 | 5072.8112 | 17.7068 | 0.34905 | OK
|  |  | 10: Grand Total | 10776502.4746 | 10584878.192 | 10776502.4746 | 1.8104
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 8708599.4302
[6 empty] | Jigatola | at 33 KV level |  | 2067903.0443
[6 empty] | Total = |  |  | 10776502.4746 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory |  | 33 | 0 | 76026305 | 1 | 8111.66 | 8111.66 | 0 | 180000 | Reading From G. Dormitory Side | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 |  | 33 | 0 | 0 | 1 | 33.92 | 54 | 20.08 | 360000 | 0 | 7228800 | 7209808.9025
9 | Green Road -2 |  | 33 | 0 | 0 | 1 | 77.32 | 88.88 | 11.56 | 360000 | 0 | 4161600 | 4150666.8782
|  |  | 10: Total | 0 | 11390400 | 11360475.7807
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [10 empty] | 11390400 | 11360475.7807
1 | Mogbazar Grid |  | 33 | Import | BD 017064 | 1 | 57264.79 | 57264.79 | 0 | 1000 | 0
2 | Green Road SS |  | 33 | Import | BD 017070 | 1 | 32923.13 | 32923.13 | 0 | 1000 | 0
3 | Jigatola Ckt-1 |  | 33 | Import |  | 1 | 12056.02 | 19368 | 7311.98 | 1000 | 7311980
NEW | Jigatola Ckt-2 |  | 33 |  |  | 1 | 27752.82 | 31940.13 | 4187.31 | 1000 | 4187310 |  |  |  | NEW FOUND
|  |  | 7: 0; 8: 0; 10: Total | 11499290 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | BD 017065 | 1 | 108288.53 | 108288.53 | 0 | 888.89 |  | 0
2 | Transformer-02 |  | 33 | Export | BD 017069 | 1 | 105577.05 | 105577.05 | 0 | 888.89 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 11360475.7807; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 11360475.7807
|  |  | 6: GREEN ROAD DORMITORY 33 KV NET IMPORT; 9=8-7: 11360475.7807 | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 11360475.7807
|  |  | 6: TOTAL EXPORT; 9=8-7: 11360475.7807 | LOSS UNITS=> |  | 0
|  |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 11360475.7807
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD 014050 | 1 | 100124.44 | 100124.44 | 0 | 1000 | 0
2 | Transformer-02 Incoming |  | 11 | Import | BD 014059 | 1 | 90985.34 | 95155.39 | 4170.05 | 1000 | 4170050
|  |  | 7: 0; 8: 0; 10: Total | 4170050 |  | 11360475.7807
| GREEN ROAD DORMITORY 11 KV SIDE |  | 7: 0; 8: 0
1 | North Dhanmondi | C31002 | 11 |  | BD 014039 | 1 | 23293.96 | 23783.66 | 489.7 | 2000 |  | 979400 | 970901.1912 | Paribag |  |  |  | North Dhanmondi | 970901.1912 | 1220415.3715 | -249514.1802 | -20.445 | OK
2 | Lake circus | C31004 | 11 |  | BD 014047 | 1 | 38490.6 | 39176.51 | 685.91 | 2000 |  | 1371820 | 1359915.9406 | Paribag |  |  |  | Lake circus | 1359915.9406 | 1817014.2474 | -457098.3068 | -25.1566 | OK
3 | Bashir Uddin | C31003 | 11 |  | BD 014037 | 1 | 15568.84 | 15830.71 | 261.87 | 2000 |  | 523740 | 519195.2113 | Paribag |  |  |  | Bashir Uddin | 519195.2113 | 699693.4639 | -180498.2526 | -25.7968 | OK
4 | Raza Bazar | D5100R | 11 |  | BD 013939 | 1 | 23208.95 | 23815.99 | 607.04 | 2000 |  | 1214080 | 1203544.7399 | Shere b.nagar |  |  |  | Raza Bazar | 1203544.7399 | 1251949.7098 | -48404.9699 | -3.8664 | OK
5 | Rasel Squar | D5100RS | 11 |  | BD 013970 | 1 | 35203.1 | 35887.97 | 684.87 | 2000 |  | 1369740 | 1357853.9899 | Shere b.nagar |  |  |  | Rasel Squar | 1357853.9899 | 1818453.1535 | -460599.1636 | -25.3292 | OK
6 | Bow Bazar | D5100O | 11 |  | BD 013967 | 1 | 26056.32 | 26716.98 | 660.66 | 2000 |  | 1321320 | 1309854.1577 | Shere b.nagar |  |  |  | Bow Bazar | 1309854.1577 | 1211822.467 | 98031.6907 | 8.0896 | OK
7 | BRB Hospital | D5100S | 11 |  | BD 014003 | 1 | 14075.99 | 14382.67 | 306.68 | 2000 |  | 613360 | 608037.5277 | Shere b.nagar |  |  |  | BRB Hospital | 608037.5277 | 807753.2915 | -199715.7638 | -24.7248 | OK
8 | Green Road North | C31008 | 11 |  | BD 013969 | 1 | 17173.89 | 17616.03 | 442.14 | 2000 |  | 884280 | 876606.6014 | Paribag |  |  |  | Green Road North | 876606.6014 | 1205661.5166 | -329054.9152 | -27.2925 | OK
1 | Water Bhaban | D5100PB | 11 |  | BD 014004 | 1 | 5589.6 | 5723.95 | 134.35 | 2000 |  | 268700 | 266368.3378 | Shere b.nagar |  |  |  | Water Bhaban | 266368.3378 | 341567.9548 | -75199.617 | -22.016 | OK
2 | Alamin Road | C31007 | 11 |  | BD 014006 | 1 | 19439.5 | 19724.04 | 284.54 | 2000 |  | 569080 | 564141.7704 | Paribag |  |  |  | Alamin Road | 564141.7704 | 583425.7911 | -19284.0207 | -3.3053 | OK
3 | Katal Bagan | C3100K | 11 |  |  | 1 | 10936.14 | 11681.91 | 745.77 | 2000 |  | 1491540 | 1478597.0623 | Paribag |  |  |  | Katal Bagan | 1478597.0623 | 2049711.7232 | -571114.6609 | -27.8632 | OK
4 | Eastern Pantho chaya | C310010 | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan |  | 11 |  | BD 014005 | 1 | 6224.11 | 6367.44 | 143.33 | 2000 |  | 286660 | 284172.4888 | Paribag |  |  |  | Kalabagan | 284172.4888 | 308027.2544 | -23854.7656 | -7.7444 | OK
6 | Univer Hospital | C310012 | 11 |  | BD 013963 | 1 | 1281.57 | 1392.56 | 110.99 | 2000 |  | 221980 | 220053.7538 | Paribag |  |  |  | Univer Hospital | 220053.7538 | 258516.7219 | -38462.9682 | -14.8783 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 |  | BD 013971 | 1 | 10529.2 | 10701.31 | 172.11 | 2000 |  | 344220 | 341233.008 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 341233.008 | 477291.2605 | -136058.2524 | -28.5063 | OK
|  |  | 10: Grand Total | 11360475.7807 | 11459920 | 11360475.7807 | -0.86776
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 6614817.0276
[6 empty] | Shere b.nagar | at 33 KV level |  | 4745658.7531
[6 empty] | Total = |  |  | 11360475.7807 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1666.769 | 1690.629 | 23.86 | 240000 | 0 | 5726400 | 5730923.8044
2 | Taltala-2 |  | 33 |  | BD001837 | 1 | 2610.6135 | 2639.7785 | 29.165 | 240000 | 0 | 6999600 | 7005129.6209
|  |  | 10: Total | 0 | 12726000 | 12736053.4253
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming |  | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 |  | 0
| 33 KV Ullon-ckt-2 incoming |  | 3: 33; 6: 1; 9=8-7: 0; 10: 1000 |  | 0
|  |  | 10: Total |  | 0 | 12736053.4253
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) |  | 3: 33; 4: EXPORT |  | 0
| 33 KV Khilgaon Feeder(Import) |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
|  |  | 10: Total |  | 0 | 12736053.4253 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 4: 12736053.4253; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TALTOLA 33 KV NET IMPORT |  | 12736053.4253
| IMPORT-2 |  | 6: TALTOLA 33 KV NET IMPORT; 9=8-7: 12736053.4253 | TALTOLA 11 KV NET IMPORT |  | 12736053.4253
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 12736053.4253 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 12736053.4253
11 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming |  | 11 | Import | 06604431 | 1 | 8689.58 | 8728.02 | 38.44 | 160000 | 6150400
2 | Transformer-02 Incoming |  | 11 | Import | 06604341 | 1 | 9410.47 | 9450.92 | 40.45 | 160000 | 6472000
3 | Transformer-03 Incoming |  | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 12622400 |  | 12736053.4253
| TALTOLA 11 KV SIDE |  | 7: 0; 8: 0
1 | Matir Masjid | A229S | 11 |  | DHK00170 | 1 | 29471.9 | 31256.8 | 1784.9 | 888.8889 |  | 1586577.7778 | 1604310.6045 | Khilgaon |  |  |  | Matir Masjid | 1604310.6045 | 1914137.6974 | -309827.093 | -16.1862 | OK
2 | Hajipara | A229P | 11 |  | DHK-00108 | 1 | 6219.3 | 7020.3 | 801 | 2222.2222 |  | 1780000 | 1799894.6638 | Khilgaon |  |  |  | Hajipara | 1799894.6638 | 1077292.6606 | 722602.0032 | 67.0757 | FAULT
3 | Nearest Feeder | A929N | 11 |  | DHK-00106 | 1 | 91617.7 | 92041.4 | 423.7 | 2222.222 |  | 941555.4614 | 952079.0172 | Bashabo |  |  |  | Nearest Feeder | 952079.0172 | 736977.684 | 215101.3332 | 29.187 | OK
4 | Reazbagh | A229C | 11 |  | DHK-00109 | 1 | 98320.2 | 98929.8 | 609.6 | 2222.222 |  | 1354666.5312 | 1369807.3375 | Khilgaon |  |  |  | Reazbagh | 1369807.3375 | 1677297.9566 | -307490.6191 | -18.3325 | OK
5 | Chowdhury Para | A229F | 11 |  | DHK-00107 | 1 | 53269.4 | 53518 | 248.6 | 2222.222 |  | 552444.3892 | 558618.9372 | Khilgaon |  |  |  | Chowdhury Para | 558618.9372 | 561029.5515 | -2410.6144 | -0.42968 | OK
6 | Model Colleg | A229D | 11 |  | 9122392 | 1 | 2584.74 | 2601.93 | 17.19 | 40000 |  | 687600 | 695285.1522 | Khilgaon |  |  |  | Model Colleg | 695285.1522 | 561252.3268 | 134032.8253 | 23.881 | OK
1 | East Rampura | A229B | 11 |  | DHK-00181 | 1 | 99587.6 | 100070 | 482.4 | 2222.222 |  | 1071999.8928 | 1083981.397 | Khilgaon |  |  |  | East Rampura | 1083981.397 | 632299.6811 | 451681.7159 | 71.4348 | FAULT
2 | Adarshabagh | A929A | 11 |  | DHK-00090 | 1 | 52389.5 | 53089.4 | 699.9 | 2222.222 |  | 1555333.1778 | 1572716.7906 | Bashabo |  |  |  | Adarshabagh | 1572716.7906 | 2035653.077 | -462936.2865 | -22.7414 | OK
3 | Khailgaon Govt Colony | A229K | 11 |  | DHK00167 | 1 | 77198.2 | 77744.9 | 546.7 | 2222.222 |  | 1214888.7674 | 1228467.3088 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1228467.3088 | 1508476.8371 | -280009.5283 | -18.5624 | OK
4 | TV Road | A214T | 11 |  | 6604434 | 1 | 5147.41 | 5174.98 | 27.57 | 40000 |  | 1102800 | 1115125.7501 | Khilgaon |  |  |  | TV Road | 1115125.7501 | 339156.7632 | 775968.9869 | 228.7936 | FAULT
5 | Post Office |  | 11 |  | 06604476 | 1 | 6635.86 | 6654.54 | 18.68 | 40000 |  | 747200 | 755551.2881 | Bashabo |  |  |  | Post Office | 755551.2881 | 1009051.5047 | -253500.2166 | -25.1226 | OK
1 | Navana | A929V | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | A929P | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 |  | 0.415 |  | 9187958 | 1 | 787.71 | 790.37 | 2.66 | 80 |  | 212.8 | 215.1784 | Bashabo |  |  |  | AT-01 | 215.1784 | 17609.6926 | -17394.5142 | -98.7781 | CHECK
3 | AT-02 |  | 0.415 |  | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 164.5672 | -164.5672 | -100 | CHECK
|  |  | 10: Grand Total | 12736053.4253 | 12595278.7976 | 12736053.4253 | 1.1177
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Khilgaon | at 33 KV level |  | 9455491.151
[6 empty] | Bashabo | at 33 KV level |  | 3280562.2743
[6 empty] | Total = |  |  | 12736053.4253 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 |  | 33 | Import | 35786569 | 1 | 1983.503 | 1999.239 | 15.736 | 180000 | 0 | 2832480 | 3465.1
2 | Sher-e-Banglanagar Ckt-02 |  | 33 | Import | 35786575 | 1 | 708.985 | 720.775 | 11.79 | 180000 | 0 | 2122200 | 2596.19
|  |  | 10: Total | 0 | 4954680 | 6061.29
|  |  | 10: Net Total | 4960741.29
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 |  | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
|  |  | 10: Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 |  | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 |  | 33 | Export | DHK 66500 | 1 | 775578 | 787774 | 12196 | 180 |  | 2195280
|  |  | 10: Total |  | 2195280 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 4: 4960741.29; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 4960741.29
| IMPORT-2 |  | 6: SHER-E-BANGLANAGAR 33 KV NET IMPORT; 9=8-7: 4960741.29 | 33 KV TX HV SIDE |  | 4960741.29
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 4960741.29
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 66503 | 1 | 2256757 | 2273078 | 16321 | 180 | 2937780 |  | 2833890.7453
2 | Transfomer-2 Incoming |  | 11 | Import | DHK 66495 | 1 | 758156 | 770405 | 12249 | 180 | 2204820 |  | 2126850.5447
|  |  | 7: 0; 8: 0; 10: Total | 5142600 |  | 4960741.29
| SHER-E-BANGLANAGAR 11 KV SIDE |  | 7: 0; 8: 0
1 | Sher-e-Banglanagar Local |  | 11 |  | DHK 66503 | 1.28 | 84325 | 85742 | 1417 | 60 | 11 kv bus-1 R Phase PT missing | 108825.6 | 109846.5171 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 109846.5171 | 124871.9678 | -15025.4507 | -12.0327 | OK
2 | Mirpur Road East | D550F | 11 |  | DHK 60961 | 1.28 | 849497 | 854603 | 5106 | 60 |  | 392140.8 | 395819.5598 | Shere b.nagar |  |  |  | Mirpur Road East | 395819.5598 | 504909.4833 | -109089.9235 | -21.6058 | OK
3 | Gonobhaban school | D550E | 11 |  | DHK 66492 | 1.28 | 534506 | 536080 | 1574 | 60 |  | 120883.2 | 122017.2321 | Shere b.nagar |  |  |  | Gonobhaban school | 122017.2321 | 162123.6893 | -40106.4572 | -24.7382 | OK
4 | Babor Road | D450B | 11 |  | DHK 66489 | 1.28 | 791315 | 798679 | 7364 | 60 |  | 565555.2 | 570860.7987 | Shyamoli |  |  |  | Babor Road | 570860.7987 | 723610.3177 | -152749.519 | -21.1094 | OK
5 | College Gate | D450K | 11 |  | DHK 66487 | 1.28 | 2705027 | 2718507 | 13480 | 60 |  | 1035264 | 1044976.0411 | Shyamoli |  |  |  | College Gate | 1044976.0411 | 1347445.4847 | -302469.4435 | -22.4476 | OK
6 | Parade ground |  | 11 |  | DHK 66490 | 1.28 | 938426 | 938469 | 43 | 60 |  | 3302.4 | 3333.3805 | Satmasjid |  |  |  | Parade ground | 3333.3805 | 6820.7377 | -3487.3572 | -51.1287 | CHECK
7 | Hospital RMU | D550H | 11 |  | DHK 66491 | 1.28 | 921595 | 927197 | 5602 | 60 |  | 430233.6 | 434269.7168 | Shere b.nagar |  |  |  | Hospital RMU | 434269.7168 | 581861.3963 | -147591.6795 | -25.3654 | OK
1 | Shamoly Square |  | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | D550D | 11 |  | DHK 60964 | 1 | 197469.2 | 198714.3 | 1245.1 | 60 |  | 74706 | 75406.8335 | Shere b.nagar |  |  |  | Gonobhaban RMU | 75406.8335 | 93681.1141 | -18274.2805 | -19.5069 | OK
3 | Krishi University | D550V | 11 |  | DHK 60963 | 1 | 378971.9 | 386593 | 7621.1 | 60 |  | 457266 | 461555.7137 | Shere b.nagar |  |  |  | Krishi University | 461555.7137 | 534152.4164 | -72596.7026 | -13.591 | OK
4 | NEC | D550X | 11 |  | DHK 86073 | 1 | 47.94 | 51.31 | 3.37 | 60000 |  | 202200 | 204096.883 | Shere b.nagar |  |  |  | NEC | 204096.883 | 264748.3525 | -60651.4695 | -22.9091 | OK
5 | Novo Theater/Army Musium | D550A | 11 |  | DHK 86074 | 1 | 417.87 | 432.4 | 14.53 | 60000 |  | 871800 | 879978.5491 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 879978.5491 | 1116285.1948 | -236306.6457 | -21.169 | OK
6 | Netor |  | 11 |  | DHK 60962 | 1 | 143367.9 | 150829.4 | 7461.5 | 60 |  | 447690 | 451889.8792 | Shere b.nagar |  |  |  | Netor | 451889.8792 | 546388.7354 | -94498.8563 | -17.2952 | OK
7 | BICC | D550VV | 11 |  |  | 1 | 47.94 | 51.31 | 3.37 | 60000 |  | 202200 | 204096.883 | Shere b.nagar |  |  |  | BICC | 204096.883 | 264748.3525 | -60651.4695 | -22.9091 | OK
8 | Auxiliary |  | 0.415 |  |  | 1 | 5396.67 | 5439.49 | 42.82 | 60 |  | 2569.2 | 2593.3022 | Shere b.nagar |  |  |  | Auxiliary | 2593.3022 | 3246.9365 | -653.6343 | -20.1308 | OK
|  |  | 10: Grand Total | 4960741.29 | 4914636 | 4960741.29 | 0.93812
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 2822383.7256 | Including 41% of Novo Theatre
[6 empty] | Shyamoli | at 33 KV level |  | 1615836.8399
[6 empty] | Satmasjid | at 33 KV level |  | 3333.3805
[6 empty] | Tejgaon | at 33 KV level |  | 519187.344 | 59% of Novo Theatre
[6 empty] | Total = |  |  | 4960741.29 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 7118816 | 7095485.6643
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 |  | ABB03918 | 1 | 311588 | 314865 | 3277 | 2000 | 0 | 6554000 | 6532520.7231
|  |  | 10: Total | 0 | 13672816 | 13628006.3873
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 |  | 33 | Import | 38 | 1 | 318124256 | 325243072 | 7118816 | 1 | 7118816
2 | Maniknagor Incoming-02 |  | 33 | Import | 15 | 1 | 233208176 | 239893376 | 6685200 | 1 | 6685200
|  |  | 7: 0; 8: 0; 10: Total | 13804016 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | 16 | 1 | 306727680 | 313843456 | 7115776 | 1 |  | 7115776
4 | Transformer-02 |  | 33 | Export | 196 | 1 | 244464960 | 251151120 | 6686160 | 1 |  | 6686160
|  |  | 10: Total |  | 13801936 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 4: 13628006.3873; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 13804016
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 13804016 | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 13801936
[11 empty] | LOSS UNITS=> |  | 2080
[11 empty] | LOSS % IN => |  | 0.01507%
| TOTAL IMPORT |  | 4: 13628006.3873
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | 192 | 1 | 304537952 | 311617152 | 7079200 | 1 | 7079200 |  | 7114668.1568
2 | Transformer-02 Incoming |  | 11 | Import | 118 | 1 | 242838320 | 249494320 | 6656000 | 1 | 6656000 |  | 6689347.8432
|  |  | 7: 0; 8: 0; 10: Total | 13735200 |  | 13804016
| MUGDAPARA HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
1 | City Corporation | A997Y | 11 |  | 93 | 1 | 44005332 | 44783932 | 778600 | 1 |  | 778600 | 776082.8806 | Bashabo |  |  |  | City Corporation | 776082.8806 | 996604.0058 | -220521.1251 | -22.1273 | OK
2 | Bot tola | B297L | 11 |  |  | 1 | 60692692 | 62504888 | 1812196 | 1 |  | 1812196 | 1806337.3901 | Maniknagar |  |  |  | Bot tola | 1806337.3901 | 2300581.3394 | -494243.9492 | -21.4834 | OK
3 | Jhilpar | B997J | 11 |  | 145 | 1 | 37775588 | 38598064 | 822476 | 1 |  | 822476 | 819817.0349 | Mugdapara |  |  |  | Jhilpar | 819817.0349 | 964321.9183 | -144504.8835 | -14.9851 | OK
4 | Central Bashaboo | A997C | 11 |  | 128 | 1 | 42422256 | 43766652 | 1344396 | 1 |  | 1344396 | 1340049.7308 | Bashabo |  |  |  | Central Bashaboo | 1340049.7308 | 1729561.5012 | -389511.7704 | -22.5208 | OK
5 | Kadamtala | B997L | 11 |  | 8 | 1.5 | 20022992 | 20429350 | 406358 | 1 |  | 609537 | 607566.4408 | Mugdapara |  |  |  | Kadamtala | 607566.4408 | 808410.7915 | -200844.3507 | -24.8443 | OK
6 | Ansar VDP | A297A | 11 |  | 119 | 1 | 21280468 | 21940426 | 659958 | 1 |  | 659958 | 657824.4358 | Khilgaon |  |  |  | Ansar VDP | 657824.4358 | 1198004.0816 | -540179.6457 | -45.09 | CHECK
7 | Mugda Hospital Express-01 | B997H | 11 |  |  | 1 | 6811903 | 7018583 | 206680 | 1 |  | 206680 | 206011.8286 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 206011.8286 | 296418.3041 | -90406.4755 | -30.4996 | OK
8 | Boro Masjid | B997Z | 11 |  | 7 | 1.22 | 51357956 | 52337832 | 979876 | 1 |  | 1195448.72 | 1191583.9793 | Mugdapara |  |  |  | Boro Masjid | 1191583.9793 | 1366718.9494 | -175134.9701 | -12.8143 | OK
1 | Anandodhara | B297B | 11 |  | 120 | 1 | 49877200 | 50564636 | 687436 | 1 |  | 687436 | 685213.6028 | Maniknagar |  |  |  | Anandodhara | 685213.6028 | 1028241.2626 | -343027.6598 | -33.3606 | OK
2 | Culvert | A997L | 11 |  | 117 | 1 | 44077932 | 45451008 | 1373076 | 1 |  | 1373076 | 1368637.0118 | Bashabo |  |  |  | Culvert | 1368637.0118 | 1587860.9817 | -219223.9698 | -13.8062 | OK
3 | Mugda Hospital Express-02 |  | 11 |  | 97 | 1 | 4845548 | 4870948 | 25400 | 1 |  | 25400 | 25317.8849 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 25317.8849 | 0 | 25317.8849 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | A997J | 11 |  | 98 | 1 | 29356208 | 29587808 | 231600 | 1 |  | 231600 | 230851.2653 | Bashabo |  | 218 |  | Jhor Pukur | 230851.2653 | 807820.7106 | -576969.4453 | -71.423 | CHECK
5 | T&T | B997T | 11 |  | 99 | 1 | 25139698 | 25731818 | 592120 | 1 |  | 592120 | 590205.7479 | Mugdapara |  | 130 |  | T&T | 590205.7479 | 628322.5712 | -38116.8233 | -6.0664 | OK
6 | Haider Ali | B297H | 11 |  | 9 | 1 | 74741936 | 76603816 | 1861880 | 1 |  | 1861880 | 1855860.7678 | Maniknagar |  | 159.3333 |  | Haider Ali | 1855860.7678 | 2415267.9161 | -559407.1483 | -23.1613 | OK
| 11kv Tilpapara | A929T | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 1647928.8 | 1642601.2461 | Bashabo | 140 |  |  | 11kv Tilpapara | 1642601.2461 | 2219790.0622 | -577188.8162 | -26.002
7 | AT-01 |  | 11 |  |  | 1 | 3207.07 | 3262 | 54.93 | 1 |  | 54.93 | 54.7524 | Mugdapara |  |  |  | AT-01 | 54.7524 | 80.2692 | -25.5168 | -31.789 | OK
8 | AT-02 |  | 11 |  |  | 1 | 17.34 | 17.34 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 13804016 | 13848787.45 | 13804016 | -0.32329
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bashabo | at 33 KV level |  | 5358222.1347
[6 empty] | Maniknagar | at 33 KV level |  | 4347411.7607
[6 empty] | Mugdapara | at 33 KV level |  | 3440557.6688
[6 empty] | Khilgaon | at 33 KV level |  | 657824.4358
[6 empty] | Total = |  |  | 13804016 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 79.3194 | 79.3331 | 0.0137 | 240000 | From Downstream | 2015280 | 2016872.053
MANKNAGAR 33 KV SIDE | bar: 4
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 278536 | 280390 | 1854 | 2000 | 0 | 3708000 | 3695847.8549
|  |  | 10: Total | 0 | 5723280 | 5712719.908
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming |  | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming |  | 33 |  |  | 1 | 71914 | 79378 | 7464 | 270 |  | 2015280
| 33 kV Maniknagor Incoming |  | 33 |  |  | 1.08 | 1007578 | 1007578 | 0 | 180 |  | 0
|  |  | 8: 0; 10: Total |  | 2015280
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| KHILGOAN 33 KV SIDE |  | 8: 0
3 | Transformer -01 |  | 33 | Export | DHK60982 | 1 | 829685 | 840895 | 11210 | 180 |  | 2017800
4 | Transformer -02 |  | 33 | Export | DHK60947 | 1 | 844340 | 865457 | 21117 | 180 |  | 3801060
|  |  | 10: Total |  | 5818860 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 4: 5712719.908; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5712719.908
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5712719.908 | 33 KV TX HV SIDE |  | 5818860
[11 empty] | LOSS UNITS=> |  | -106140.092
[11 empty] | LOSS % IN => |  | -1.858%
| TOTAL IMPORT |  | 4: 5712719.908
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | DHK60927 | 1 | 829484 | 840290 | 10806 | 180 | 1945080 |  | 1943141.1541
2 | Transformer-02 Incoming |  | 11 | Import | DHK60928 | 1 | 2727 | 23690 | 20963 | 180 | 3773340 |  | 3769578.7538
|  |  | 7: 0; 8: 0; 10: Total | 5718420 |  | 5712719.908
| KHILGOAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Shantinagar s/s-1 |  | 11 |  | DHK60932 | 1 | 397140 | 430321 | 33181 | 60 |  | 1990860 | 1995495.3946 | Rajarbag |  |  |  | Shantinagar s/s-1 | 1995495.3946 | 1888358.4836 | 107136.911 | 5.6735 | OK
2 | Gulbagh | D606G | 11 |  | DHK60934 | 1 | 175960 | 189715 | 13755 | 60 |  | 825300 | 827221.5772 | Rajarbag |  |  |  | Gulbagh | 827221.5772 | 1048994.4227 | -221772.8455 | -21.1415 | OK
3 | Rampura BTV | A206H | 11 |  | DHK60933 | 1 | 14073 | 14076 | 3 | 60 |  | 180 | 180.4191 | Khilgaon |  |  |  | Rampura BTV | 180.4191 | 0 | 180.4191 | #DIV/0! | #DIV/0!
4 | West Shantibag | D606W | 11 |  | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 706255.2 | 707899.6007 | Rajarbag | 60 |  |  | West Shantibag | 707899.6007 | 1098102.3361 | -390202.7354 | -35.5343 | OK
1 | East Malibagh | D606E | 11 |  | DHK60929 | 1 | 648732 | 665295 | 16563 | 60 |  | 993780 | 996093.8555 | Rajarbag |  |  |  | East Malibagh | 996093.8555 | 1225702.646 | -229608.7905 | -18.7328 | OK
2 | Police Line | D606S | 11 |  | DHK60930 | 1 | 594185 | 601907 | 7722 | 60 |  | 463320 | 464398.7655 | Rajarbag |  |  |  | Police Line | 464398.7655 | 567380.2526 | -102981.4871 | -18.1503 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 |  | DHK61017 | 1 | 199938 | 201786 | 1848 | 60 |  | 110880 | 111138.1661 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 111138.1661 | 133734.902 | -22596.7359 | -16.8967 | OK
4 | Benjir Bagan | D662R | 11 |  | DHK60985 | 1 | 173708 | 175954 | 2246 | 60 |  | 134760 | 135073.7668 | Rajarbag |  |  |  | Benjir Bagan | 135073.7668 | 193500.3195 | -58426.5527 | -30.1946 | OK
5 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 883323 | 892895 | 9572 | 60 |  | 574320 | 575657.211 | Switching |  |  |  | Shantinagar s/s-2 | 575657.211 | 675595.9834 | -99938.7724 | -14.7927 | OK
6 | AT-1 & AT-2 |  | 0.415 |  | ELIB 7374 | 1 | 2332.2 | 2427 | 94.8 | 60 |  | 5688 | 5701.2436 | Rajarbag |  |  |  | AT-1 & AT-2 | 5701.2436 | 7360.8364 | -1659.5928 | -22.5463 | OK
|  |  | 10: Grand Total | 5818860 | 5805343.2 | 5818860 | 0.23283
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Rajarbag | at 33 KV level |  | 5650071.9172 | Including Switching
[6 empty] | Khilgaon | at 33 KV level |  | 180.4191
[6 empty] | Moghbazar | at 33 KV level |  | 104859.5814
[6 empty] | Kakrail | at 33 KV level |  | 63748.0823
[6 empty] | Total = |  |  | 5818860 | 0
11 KV SIDE of___Santinagar Switching S/S | [14 empty] | Month November-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 883323 | 892895 | 9572 | 60 |  | 574320 | 575657.211 | 0.23283
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder |  | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 406104 | 407049.5473 | Rajarbag
2 | 11 Fortune(MogBazar)-new |  | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 104616 | 104859.5814 | Moghbazar
3 | Centerpoint-Kakrail |  | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 63600 | 63748.0823 | Kakrail
[12 empty] | 574320 | 575657.211 | 0.23283
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 |  | 33 | Import |  | 1 | 1168.374 | 1182.108 | 13.734 | 180000 | 0 | 2472120 | 3024.26
2 | Sherebangla to Monipuripara-2 |  | 33 | Import |  | 1 | 838.951 | 869.027 | 30.076 | 180000 | 0 | 5413680 | 6622.81
|  |  | 10: Total | 0 | 7885800 | 9647.07
|  |  | 10: Net Total | 7895447.07
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | BD017103 | 1 | 47130.77 | 49332.2 | 2201.43 | 1000 | 2201430
2 | Agargaon Ckt-02 |  | 33 | Import | BD017104 | 1 | 34130.21 | 38934.14 | 4803.93 | 1000 | 4803930
|  |  | 8: 0; 10: Total | 7005360 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
0
| MONIPURIPARA 33 KV SIDE |  | 8: 0
3 | Transformer-01 |  | 33 | Export | BD017102 | 1 | 47130.77 | 49332.2 | 2201.43 | 1000 |  | 2201430 |  |  | OMF Corrected by Grid
4 | Transformer-02 |  | 33 | Export | BD017105 | 1 | 51463.55 | 56887.35 | 5423.8 | 1000 |  | 5423800 |  |  | OMF Corrected by Grid
|  |  | 10: Total |  | 7625230 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 4: 7895447.07; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7895447.07
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 7895447.07 | 33 KV TX HV SIDE |  | 7625230
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 270217.07
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 3.422%
| TOTAL IMPORT |  | 4: 7895447.07
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD014058 | 1 | 3951.91 | 12724.35 | 8772.44 | 1000 | 8772440 |  | 4891017.5738
2 | Transformer -02 Incoming |  | 11 | Import | BD014062 | 1 | 50491.18 | 55879.87 | 5388.69 | 1000 | 5388690 |  | 3004429.4962
|  |  | 7: 0; 8: 0; 10: Total | 14161130 | 0 | 7895447.07
| MONIPURIPARA 11 KV SIDE |  | 7: 0; 8: 0
1 | Spare |  | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | D572W | 11 |  | BD013947 | 1 | 32779.66 | 33710.12 | 930.46 | 1000 |  | 930460 | 935544.6228 | Shere b.nagar |  |  |  | Monipuripara west | 935544.6228 | 814448.4485 | 121096.1743 | 14.8685 | OK
3 | Biggan College | C672BC | 11 |  | BD013949 | 1 | 20808.54 | 21787.07 | 978.53 | 1000 |  | 978530 | 983877.3078 | Kakrail |  |  |  | Biggan College | 983877.3078 | 910214.7983 | 73662.5094 | 8.0929 | OK
4 | Green Road South | D572G | 11 |  | BD013948 | 1 | 31642.23 | 32252.24 | 610.01 | 1000 |  | 610010 | 613343.481 | Shere b.nagar |  |  |  | Green Road South | 613343.481 | 1046963.2451 | -433619.7641 | -41.4169 | CHECK
5 | BARC Building O/H | D572B | 11 |  | BD014010 | 1 | 14574.54 | 14613.61 | 39.07 | 1000 |  | 39070 | 39283.5032 | Shere b.nagar |  |  |  | BARC Building O/H | 39283.5032 | 553036.0194 | -513752.5162 | -92.8968 | CHECK
6 | Indira Road (Green Road North) | D572NN | 11 |  | BD014036 | 1 | 62546.1 | 63504.96 | 958.86 | 1000 |  | 958860 | 964099.8184 | Shere b.nagar |  |  |  | Indira Road (Green Road North) | 964099.8184 | 1738404.7784 | -774304.9599 | -44.5411 | CHECK
7 | Chundrima Uddan | D572C | 11 |  | BD014035 | 1 | 32013.76 | 32488.76 | 475 | 1000 |  | 475000 | 477595.7009 | Shere b.nagar |  |  |  | Chundrima Uddan | 477595.7009 | 964413.0153 | -486817.3144 | -50.4781 | CHECK
8 | RMU-1 Feeder |  | 11 |  | BD013940 | 1 | 1047.79 | 1367.45 | 319.66 | 1000 |  | 319660 | 321406.8247 | Shere b.nagar |  |  |  | RMU-1 Feeder | 321406.8247 | 250904.1991 | 70502.6256 | 28.0994 | OK
1 | Farmgate foot over bridge RMU |  | 11 |  | BD013946 | 1 | 63.59 | 239.33 | 175.74 | 1000 |  | 175740 | 176700.3547 | Tejgaon |  |  |  | Farmgate foot over bridge RMU | 176700.3547 | 0 | 176700.3547 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | C672K | 11 |  | BD013964 | 1 | 40456.52 | 40517.44 | 60.92 | 1000 |  | 60920 | 61252.9055 | Kakrail |  |  |  | kawran Bazar North | 61252.9055 | 77104.1375 | -15851.2321 | -20.5582 | OK
3 | NAM Bhanan RMU | D572NM | 11 |  | BD013950 | 1 | 18200.87 | 18967.08 | 766.21 | 1000 |  | 766210 | 770397.0568 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 770397.0568 | 959936.9135 | -189539.8567 | -19.745 | OK
4 | Novo Theater |  | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | C172I | 11 |  | BD013962 | 1 | 39654.38 | 40098.87 | 444.49 | 1000 |  | 444490 | 446918.9749 | Tejgaon |  |  |  | Monipuripara Nearest | 446918.9749 | 732201.3407 | -285282.3658 | -38.9623 | OK
6 | Holy Cross | C172HC | 11 |  | BD013965 | 1 | 39906.37 | 40933.65 | 1027.28 | 1000 |  | 1027280 | 1032893.7086 | Tejgaon |  |  |  | Holy Cross | 1032893.7086 | 1312589.0703 | -279695.3616 | -21.3087 | OK
7 | Honda Goli | C172HG | 11 |  | BD014011 | 1 | 16352.73 | 17161.03 | 808.3 | 1000 |  | 808300 | 812717.0632 | Tejgaon |  |  |  | Honda Goli | 812717.0632 | 996766.2388 | -184049.1756 | -18.4646 | OK
8 | Navy Quarter | C172NQ | 11 |  | BD013941 | 1 | 5723.59 | 5981.54 | 257.95 | 1000 |  | 257950 | 259359.6022 | Tejgaon |  |  |  | Navy Quarter | 259359.6022 | 175972.436 | 83387.1662 | 47.3865 | FAULT
9 | AT-01 |  | 0.415 |  |  | 1 | 2141.19 | 2170.58 | 29.39 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 585.48 | 641.32 | 55.84 | 1 |  | 55.84 | 56.1451 | Shere b.nagar |  |  |  | AT-02 | 56.1451 | 0 | 56.1451 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 7895447.07 | 7852535.84 | 7895447.07 | 0.54646
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 4121727.1531
[6 empty] | Kakrail | at 33 KV level |  | 1045130.2132
[6 empty] | Tejgaon | at 33 KV level |  | 2728589.7037
[6 empty] | Total = |  |  | 7895447.07 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 |  | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 |  | 33 | 0 | 0 | 1 | 3957.05 | 3982.57 | 25.52 | 180000 | 0 | 4593600 | 4600835.7721
|  |  | 10: Total | 0 | 4593600 | 4600835.7721
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 |  | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 |  | 33 | Import |  | 1 | 44123.44 | 48712.32 | 4588.88 | 1000 | 4588880
|  |  | 10: Total | 4588880 | 0 | 0
Ispahani 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 0
Ispahani 33 KV SIDE
3 | Transformer-01 |  | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 |  | 33 | Export |  | 1 | 43978.86 | 49141.45 | 5162.59 | 888.8889 |  | 4588968.9463
|  |  | 10: Total |  | 4588968.9463 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 4: 4600835.7721; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4600835.7721
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4600835.7721 | 33 KV TX HV SIDE |  | 4588968.9463
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 11866.8259
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2579%
| TOTAL IMPORT |  | 4: 4600835.7721
11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import |  | 1 | 12740.85 | 14251.82 | 1510.97 | 1000 | 4588968.9463 |  | 4600835.7721 |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 4588968.9463 | 0 | 4600835.7721
| Ispahani 11 KV SIDE |  | 7: 0; 8: 0
1 | Doctor Goli | D1113D | 11 |  | BD013944 | 1 | 10546.84 | 11220.97 | 674.13 | 1000 |  | 674130 | 680371.3877 | Moghbazar |  |  |  | Doctor Goli | 680371.3877 | 917384.4784 | -237013.0907 | -25.8357 | OK
2 | Ispahani | D1113S | 11 |  | BD013947 | 1 | 11780.12 | 12560.14 | 780.02 | 1000 |  | 780020 | 787241.7632 | Moghbazar |  |  |  | Ispahani | 787241.7632 | 1000362.3505 | -213120.5873 | -21.3043 | OK
3 | BTCL | C6113BT | 11 |  | BD013949 | 1 | 6098.75 | 6628.46 | 529.71 | 1000 |  | 529710 | 534614.2847 | Kakrail |  |  |  | BTCL | 534614.2847 | 552136.017 | -17521.7322 | -3.1734 | OK
4 | Vikarunnesa | C6113VQ | 11 |  | BD013948 | 1 | 8561.61 | 9308.85 | 747.24 | 1000 |  | 747240 | 754158.2718 | Kakrail |  |  |  | Vikarunnesa | 754158.2718 | 1059198.2594 | -305039.9876 | -28.7991 | OK
5 | OASIS |  | 11 |  |  | 1 | 310.99 | 424 | 113.01 | 1000 |  | 113010 | 114056.2956 | Kakrail |  |  |  | OASIS | 114056.2956 | 109560.3611 | 4495.9345 | 4.1036 | OK
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | D1113W | 11 |  |  | 1 | 9982.44 | 10751.41 | 768.97 | 1000 |  | 768970 | 776089.4575 | Moghbazar |  |  |  | Wireless | 776089.4575 | 1063107.1511 | -287017.6936 | -26.998 | OK
2 | Kazir Goli | C6113KG | 11 |  |  | 1 | 9531.61 | 10477.16 | 945.55 | 1000 |  | 945550 | 954304.3117 | Kakrail |  |  |  | Kazir Goli | 954304.3117 | 1072332.5406 | -118028.2289 | -11.0067 | OK
3 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 4600835.7721 | 4558630 | 4600835.7721 | 0.92584
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 2243702.6084
[6 empty] | Kakrail | at 33 KV level |  | 2357133.1637
[6 empty] | Total = |  |  | 4600835.7721 | 0

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 |  | 132 | IMPORT | 8993683 | 1 | 8449.443 | 8481.316 | 31.873 | 960000 | 0 | 30598080
| XFR- T2 |  | 132 |  | 8993682 | 1 | 8439.078 | 8470.688 | 31.61 | 960000 | 0 | 30345600
|  |  | 10: Total | 0 | 60943680
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** |  | 132 | P. Cell | 08993685 | 1 | 8449.443 | 8481.208 | 31.765 | 960000 | 30494400
| 132/33 kV Transformer-2(HV) ** |  | 132 | P. Cell | 08993684 | 1 | 8439.078 | 8470.673 | 31.595 | 960000 | 30331200
|  |  | 10: Total | 60825600
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 4: 60943680; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 60943680
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 60943680 | 33 KV NET IMPORT |  | 60906720
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 60943680 | LOSS UNITS=>(132 HV-33 LV) |  | 36960
| IMPORT-4 |  | 6: Loss Units=> (132 IMP-132 EXP); 9=8-7: 0 | LOSS % IN => |  | 0.06065%
| 132 KV TOTAL IMPORT |  | 4: 60943680; 6: 132 KV NET LOSS =>; 9=8-7: 0%
| 33 KV GT INCOMING-NOCS |  | 4: 60906720
| Loss Units=> (132 IMP-33 IMP) |  | 4: 36960
| LOSS % IN => |  | 4: 0.06065%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | 4: IMPORT
3 | 132/33 kV Transformer, T-1 (LV) |  | 33 | PGCB | J2002016494 | 1 | 22609.343 | 22821.391 | 212.048 | 144000 | 30534912
4 | 132/33 kV Transformer, T-2 (LV) |  | 33 | PGCB | J2002016859 | 1 | 32581.943 | 32792.205 | 210.262 | 144000 | 30277728
| DPDC |  | 7: 0; 8: 0; 10: Total | 60812640
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | DPDC | 07389553 | 1 | 1828.88 | 1892.64 | 63.76 | 480000 | 30604800
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | DPDC | 07389485 | 1.038 | 1204.02 | 1256.79 | 52.77 | 480000 | 26292124.8
| P.Cell |  | 7: 0; 8: 0; 10: Total | 56896924.8
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | P.Cell | 08993674 | 1 | 11093.974 | 11157.639 | 63.665 | 480000 | 30559200
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | P.Cell | 8993667 | 1 | 11002.294 | 11065.518 | 63.224 | 480000 | 30347520
|  |  | 7: 0; 8: 0; 10: Total | 60906720
| SIDDHIRGANJ 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) |  | 33 | DPDC | 07389555 | 1 | 5723.1 | 5746.05 | 22.95 | 240000 |  | 5508000 | 5503683.2922 |  | 11678839.9272 | Siddhirganj 33/11 kv ss | 0.57715 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 5503683.2922 | 6761266.2239 | -1257582.9317 | -18.5998 | OK
|  |  | 33 | P.Cell | 08993675 | 1 | 5022.34 | 5022.34 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) |  | 33 | DPDC | 07389487 | 1 | 5902.59 | 5928.34 | 25.75 | 240000 |  | 6180000 | 6175156.635 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 6175156.635 | 7370281.7262 | -1195125.0912 | -16.2155 | OK
|  |  | 33 | P.Cell | 08993666 | 1 | 5166.841 | 5192.564 | 25.723 | 240000 |  | 6173520 | 6168681.7135 |  |  |  |  | 0 | 6168681.7135 | 7373864.1703 | -1205182.4568 | -16.344 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 11688000 | 11678839.9272 |  |  |  |  | 33 KV Feeders | 11678839.9272 | 14131547.95 | -2452708.0229 | -17.3563 | OK
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4367.621 | 4401.053 | 33.432 | 240000 |  | 8023680 | 8017391.7134 |  | 14871216.0485 | Sarulia 33/11 kv ss | 1.095 | 33 kV Sarulia-1 Feeder | 8017391.7134 | 9880858.5734 | -1863466.86 | -18.8594 | OK
|  |  | 33 | P.Cell | 08993679 | 1 | 4368.442 | 4401.846 | 33.404 | 240000 |  | 8016960 | 8010676.98 |  |  |  |  | 0 | 8010676.98 | 9881097.403 | -1870420.423 | -18.9293 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) |  | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss | 0.9012 | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6258.43 | 6293.38 | 34.95 | 240000 |  | 8388000 | 8381426.19 |  |  |  |  | 33 kV Demra-1 Feeder | 8381426.19 | 9849333.0651 | -1467906.875 | -14.9036 | OK
|  |  | 33 | P.Cell | 08993676 | 1 | 5904.017 | 5938.92 | 34.903 | 240000 |  | 8376720 | 8370155.0303 |  |  |  |  | 0 | 8370155.0303 | 9850288.3835 | -1480133.3532 | -15.0263 | OK
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5809.89 | 5855.99 | 46.1 | 240000 |  | 11064000 | 11055328.9659 |  | 19436755.156 | Demra 33/11 kv ss | 0.2689 | 33 kV Demra-2 Feeder | 11055328.9659 | 13735090.7995 | -2679761.8336 | -19.5103 | OK
|  |  | 33 | P.Cell | 08993665 | 1 | 5518.105 | 5564.146 | 46.041 | 240000 |  | 11049840 | 11041180.0634 |  |  |  |  | 0 | 11041180.0634 | 13735329.6291 | -2694149.5658 | -19.6147 | OK
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder |  | 33 | DPDC | 7389486 | 1 | 4592.74 | 4616.75 | 24.01 | 240000 |  | 5762400 | 5757883.9148 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 5757883.9148 | 5345006.6439 | 412877.2709 | 7.7245 | OK
|  |  | 33 | P.Cell | 08993678 | 1 | 3838.41 | 3862.384 | 23.974 | 240000 |  | 5753760 | 5749250.6861 |  |  |  |  | 0 | 5749250.6861 | 5344767.8143 | 404482.8718 | 7.5678 | OK
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4066.02 | 4094.6 | 28.58 | 240000 |  | 6859200 | 6853824.3351 |  |  |  |  | 33 kV Sarulia-2 Feeder | 6853824.3351 | 8277834.2395 | -1424009.9044 | -17.2027 | OK
|  |  | 33 | P.Cell | 08993663 | 1 | 3787.867 | 3816.402 | 28.535 | 240000 |  | 6848400 | 6843032.7992 |  |  |  |  | 0 | 6843032.7992 | 8273774.1361 | -1430741.3369 | -17.2925 | OK
17 | 33 kV Adamjee EPZ Feeder |  | 33 | DPDC | ABB03919 | 1 | 375764.6 | 380367.7 | 4603.1 | 2000 |  | 9206200 | 9198984.9536 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 9198984.9536 | 9835003.2885 | -636018.335 | -6.4669 | OK
|  |  | 10: Total | 60943680 | 60991480 | 60943680 | -0.078372
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 14956868.8684
[6 empty] | Total = |  |  | 14956868.8684 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | 4: IMPORT
8 | 33/11 kV Transformer-1 Incoming |  | 11 | New | XA587379 | 1 | 698853 | 703843.3 | 4990.3 | 1000 | 4990300 |  | 5224223.4951
9 | 33/11 kV Transformer-2 Incoming |  | 11 | New | DHKA9985 | 1 | 330703.8 | 336869.4 | 6165.6 | 1000 | 6165600 |  | 6454616.4321
|  |  | 7: 0; 8: 0; 10: Total | 11155900 |  | 11678839.9272
| SIDDHIRGANJ 11 kV SIDE |  | 4: EXPORT; 7: 0; 8: 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1.1 | 220112.5 | 221836.7 | 1724.2 | 1000 |  | 1896620 | 1907566.3908 | Siddirgonj | CF due to PT Low Voltage in Y Phase |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 1907566.3908 | 2264304.2356 | -356737.8449 | -15.7549 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1.1 | 17238.9 | 17327.3 | 88.4 | 1000 |  | 97240 | 97801.2231 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 97801.2231 | 114438.0991 | -16636.876 | -14.5379 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1.1 | 112545.1 | 113678.5 | 1133.4 | 1000 |  | 1246740 | 1253935.5917 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1253935.5917 | 1366513.6955 | -112578.1037 | -8.2383 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1.1 | 177164.8 | 179110.6 | 1945.8 | 1000 |  | 2140380 | 2152733.2578 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2152733.2578 | 2379446.8789 | -226713.6211 | -9.528 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1.1 | 7210.5 | 7300.2 | 89.7 | 1000 |  | 98670 | 99239.4764 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 99239.4764 | 85853.7366 | 13385.7398 | 15.5913 | OK
10 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 78690 | 79934 | 1244 | 1000 |  | 1244000 | 1251179.7778 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1251179.7778 | 1359166.3065 | -107986.5288 | -7.9451 | OK
11 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) |  | 11 | T2 |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 153390.8 | 155175.3 | 1784.5 | 1000 |  | 1784500 | 1794799.2873 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 1794799.2873 | 2274671.0995 | -479871.8122 | -21.0963 | OK
14 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 101.8282 | 111.26 | 9.4318 | 40000 |  | 377272 | 379449.435 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 379449.435 | 283444.1488 | 96005.2862 | 33.871 | OK
15 | 11 kV Madrasha Road Feeder (F-11) |  | 11 | T2 | XA575919 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 16306.6 | 16870.9 | 564.3 | 1000 |  | 564300 | 567556.8719 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 567556.8719 | 709475.9549 | -141919.083 | -20.0034 | OK
17 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 154796.1 | 156958.2 | 2162.1 | 1000 |  | 2162100 | 2174578.6154 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2174578.6154 | 2726585.8445 | -552007.2291 | -20.2454 | OK
|  |  | 10: Total | 11678839.9272 | 11611822 | 11678839.9272 | 0.57715
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 11299390.4922
[6 empty] | Matuail | at 33 KV level |  | 379449.435
[6 empty] | Total = |  |  | 11678839.9272 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6258.43 | 6293.38 | 34.95 | 240000 | 0 | 8388000 | 8381426.19
0 | 0 |  | 33 | P.Cell | 08993676 | 1 | 5904.017 | 5938.92 | 34.903 | 240000 | 0 | 8376720 | 8370155.0303
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5809.89 | 5855.99 | 46.1 | 240000 | 0 | 11064000 | 11055328.9659
0 | 0 |  | 33 | P.Cell | 08993665 | 1 | 5518.105 | 5564.146 | 46.041 | 240000 | 0 | 11049840 | 11041180.0634
|  |  | 10: Total | 0 | 19452000 | 19436755.156
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 |  | 33 | Digital | DHK60885 | 3 | 405772.8 | 425220.6 | 19447.8 | 240 | 14002416
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) |  | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
|  |  | 8: 0; 10: Total | 14002416 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
10 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1019.06 | 1022.36 | 3.3 | 240000 |  | 792000 |  | Siddirgonj
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 792000
0
| DEMRA 33 KV SIDE |  | 8: 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60886 | 1 | 870056.3 | 905180.8 | 35124.5 | 240 |  | 8429880
8 | 33/11 kV, 10/14 MVA T-2 (HV) |  | 33 | Digital | 05002303 | 1 | 52.29 | 61.99 | 9.7 | 240000 |  | 2328000
9 | 33/11 kV, 20/28 MVA T-3 (HV) |  | 33 |  |  | 1 |  | 0 | 0 | 180 |  | 0
|  |  | 10: Total |  | 10757880 | 0
[6 empty] | 33 KV Export-Import |  |  | KWH
[6 empty] | Total Import |  |  | 19436755.156
[6 empty] | Siddirgonj NOCS |  |  | 792000
[6 empty] | Net Import to Demra 33/11 KV SS |  |  | 18644755.156
11 KV SIDE of___DEMRA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK60881 | 1 | 464775.3 | 499660.4 | 34885.1 | 180 | 6279318 |  | 7066410.558
19 | 33/11 kV, 20/28 MVA T-3 Incoming. |  | 11 |  | DHK60925 | 1 | 856253.7 | 898930.8 | 42677.1 | 180 | 7681878 |  | 8644776.9972
| 33/11 kV, 10/14 MVA T-2 Incoming. |  | 11 |  |  | 1 | 15708.168 | 18314.98 | 2606.812 | 1000 | 2606812 |  | 2933567.6007
|  |  | 7: 0; 8: 0; 10: Total | 16568008 |  | 18644755.156
| DEMRA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 |  | HA021101013-02 | 1 | 54945696 | 57648360 | 2702664 | 1 |  | 2702664 | 2709931.5892 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2709931.5892 | 3182659.205 | -472727.6158 | -14.8532 | OK
12 | 11 kV DND (WASA) Feeder. | A816B | 11 |  | HA021100992-02 | 1 | 6447792 | 6452560 | 4768 | 1 |  | 4768 | 4780.8214 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 4780.8214 | 190285.6191 | -185504.7977 | -97.4876 | CHECK
13 | 11 kV Local Feeder | A816D | 11 |  | HA021100794-02 | 1 | 13337258 | 14233810 | 896552 | 1 |  | 896552 | 898962.87 | Siddirgonj |  |  |  | 11 kV Local Feeder | 898962.87 | 1098339.8454 | -199376.9754 | -18.1526 | OK
14 | 11 kV Mouchak Feeder | A816A | 11 |  | DHK60888 | 1 | 1013189.5 | 1047240.6 | 34051.1 | 60 |  | 2043066 | 2048559.8995 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2048559.8995 | 2345108.3326 | -296548.4331 | -12.6454 | OK
15 | 11 kV Overhead-1 Feeder | A816C | 11 |  | HA021100829-02 | 1 | 79563317 | 79937310 | 373993 | 1 |  | 373993 | 374998.6846 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 374998.6846 | 432331.1497 | -57332.4651 | -13.2612 | OK
16 | 11 kV Provati Steel Feeder | A816Z | 11 |  | DHK60874 | 1 | 601475.9 | 609350.3 | 7874.4 | 60 |  | 472464 | 473734.4777 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 473734.4777 | 572313.5546 | -98579.0769 | -17.2247 | OK
17 | 11 kV Islambagh Feeder. | E116I | 11 |  | DHKA2190 | 1 | 1179.7411 | 1212.637 | 32.8959 | 60000 |  | 1973754 | 1979061.5163 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 1979061.5163 | 2382248.0982 | -403186.5819 | -16.9246 | OK
20 | 11 kV Taj Jute Feeder. | A816E | 11 |  | DHK61062 | 1 | 679906.6 | 702990.4 | 23083.8 | 60 |  | 1385028 | 1388752.4047 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1388752.4047 | 1608771.849 | -220019.4442 | -13.6762 | OK
21 | 11 kV Al-Aksa Steel Feeder | A816S | 11 |  | DHK61061 | 1 | 848208.6 | 877240.8 | 29032.2 | 60 |  | 1741932 | 1746616.1362 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1746616.1362 | 1742517.141 | 4098.9952 | 0.23523 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 |  | DHKA2189 | 1 | 1116.5269 | 1151.187 | 34.6601 | 60000 |  | 2079606 | 2085198.1573 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2085198.1573 | 2525197.0695 | -439998.9123 | -17.4243 | OK
23 | 11 kV Over Head Feeder-2. | E116V | 11 |  | HA021100488-02 | 1 | 33418808 | 35111950 | 1693142 | 1 |  | 1693142 | 1697694.9376 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 1697694.9376 | 2095936.8227 | -398241.8851 | -19.0007 | OK
24 | 11 kV Shimrail Express Feeder. | A8164 | 11 |  | HA021100511-02 | 1 | 8254376 | 8254917 | 541 | 1 |  | 541 | 542.4548 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 542.4548 | 30546.5041 | -30004.0493 | -98.2242 | CHECK
25 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 |  | HA021100413-02 | 1 | 82154657 | 82521598 | 366941 | 1 |  | 366941 | 367927.7214 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 367927.7214 | 330954.2369 | 36973.4846 | 11.1718 | OK
26 | 11 kV Siddhirgonj Mazar Feeder |  | 11 |  | HA021100393-02 | 1 | 26069.366 | 26893.78 | 824.414 | 1000 |  | 824414 | 826630.8876 | Siddirgonj |  |  |  | 11 kV Siddhirgonj Mazar Feeder | 826630.8876 | 1127913.2115 | -301282.3239 | -26.7115 | OK
27 | 11 kV AST Beverage Feeder | A816J | 11 |  |  | 1 | 23064522 | 23358696 | 294174 | 1 |  | 294174 | 294965.0476 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 294965.0476 | 533291.7199 | -238326.6723 | -44.6897 | CHECK
28 | 11 kV Karim Market Feeder | E216K | 11 |  |  | 1 | 62687.216 | 64428.93 | 1741.714 | 1000 |  | 1741714 | 1746397.55 | Matuail |  |  |  | 11 kV Karim Market Feeder | 1746397.55 | 2153249.6409 | -406852.0909 | -18.8948 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 |  | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 18644755.156 | 18594753 | 18644755.156 | 0.2689
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 6435390.6556
[6 empty] | Demra | at 33 KV level |  | 2065622.659
[6 empty] | Siddirgonj | at 33 KV level |  | 10143741.8414
[6 empty] | Total = |  |  | 18644755.156 | 0
33 KV SIDE of___ SARULIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4367.621 | 4401.053 | 33.432 | 240000 | 0 | 8023680 | 8017391.7134
0 | 0 |  | 33 | P.Cell | 08993679 | 1 | 4368.442 | 4401.846 | 33.404 | 240000 | 0 | 8016960 | 8010676.98
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4066.02 | 4094.6 | 28.58 | 240000 | 0 | 6859200 | 6853824.3351
| 0 |  | 33 | P.Cell | 08993663 | 1 | 3787.867 | 3816.402 | 28.535 | 240000 | 0 | 6848400 | 6843032.7992
|  |  | 10: Total | 0 | 14882880 | 14871216.0485
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) |  | 33 |  | 30799103 | 1 | 4440.54 | 4468.94 | 28.4 | 240000 | 6816000
7 | 33 kV Siddhirgonj-1 Incoming (=L41) |  | 33 |  | 30799100 | 1 | 4385.63 | 4418.41 | 32.78 | 240000 | 7867200
|  |  | 7: 0; 8: 0; 10: Total | 14683200 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SARULIA 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV Transformer-1 (=T31) |  | 33 |  | 30799099 | 1 | 4788.57 | 4826.03 | 37.46 | 180000 |  | 6742800
5 | 33/11 kV Transformer-2 (=T32) |  | 33 |  | 30799139 | 1 | 4102.02 | 4124.15 | 22.13 | 180000 |  | 3983400
6 | 33/11 kV Transformer-3 (=T33) |  | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
|  |  | 10: Total |  | 10726200 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 4: 14871216.0485; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 14871216.0485
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 14871216.0485 | 33 KV NET Receiving |  | 14683200
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 14871216.0485 | LOSS UNITS=> |  | 188016.0485
| IMPORT-4 |  | 6: 132KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 1.264%
| TOTAL IMPORT |  | 4: 14871216.0485
11 KV SIDE of___SARULIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) |  | 11 |  | 2007754972 | 1 | 9462.068 | 9504.86 | 42.792 | 160000 | 6846720 |  | 6865221.3659
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) |  | 11 |  | 30799500 | 1 | 8932.09 | 8981.71 | 49.62 | 80000 | 3969600 |  | 3980326.7454
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) |  | 11 |  | HA021100368-02 | 1 | 59061733 | 63076552 | 4014819 | 1 | 4014819 |  | 4025667.9372
|  |  | 7: 0; 8: 0; 10: Total | 14831139 |  | 14871216.0485
| SARULIA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 |  | 2007755114 | 1 | 5918.8 | 5962.59 | 43.79 | 60000 |  | 2627400 | 2656170.9356 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 2656170.9356 | 3219680.3589 | -563509.4233 | -17.502 | OK
9 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 |  | 30799484 | 1 | 22.0742 | 22.3065 | 0.2323 | 60000 |  | 13938 | 14090.6259 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 14090.6259 | 14581.402 | -490.7761 | -3.3658 | OK
11 | 11 kV Konapara (=L13) **** | E183KL | 11 |  | DHKA2191 | 1 | 2208.3613 | 2242.8601 | 34.4988 | 60000 |  | 2069928 | 2092594.4251 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 2092594.4251 | 2580974.9024 | -488380.4773 | -18.9223 | OK
12 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 |  | 575926 | 1 | 58574.2 | 60597 | 2022.8 | 1000 |  | 2022800 | 2044950.3572 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2044950.3572 | 2502341.7238 | -457391.3666 | -18.2785 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 |  | 30799450 | 1 | 1825.25 | 1829.83 | 4.58 | 60000 |  | 274800 | 277809.1547 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 277809.1547 | 324637.9555 | -46828.8008 | -14.4249 | OK
14 | 11 kV Tengra Feeder (=L16) | E183T | 11 |  | 30799145 | 1 | 5610.1 | 5648.31 | 38.21 | 60000 |  | 2292600 | 2317704.7602 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 2317704.7602 | 2700866.43 | -383161.6698 | -14.1866 | OK
16 | 11 kV Police Line Feeder (=L17) | E183PL | 11 |  | 30799480 | 1 | 3379.8 | 3396.71 | 16.91 | 60000 |  | 1014600 | 1025710.2197 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1025710.2197 | 1276100.2252 | -250390.0055 | -19.6215 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 |  | 30799119 | 1 | 1664.08 | 1670.44 | 6.36 | 60000 |  | 381600 | 385778.6515 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 385778.6515 | 493328.3324 | -107549.6809 | -21.8008 | OK
18 | 11 kV Spare Feeder (=F9) |  | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 |  | HA021100493-02 | 1 | 89482972 | 91722476 | 2239504 | 1 |  | 2239504 | 2264027.3407 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 2264027.3407 | 2874690.3342 | -610662.9935 | -21.2427 | OK
21 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 |  | HA021100518-02 | 1 | 50895377 | 50895377 | 0 | 1 |  | 0 | 0 | Demra | No Reading in Grid |  |  | 11 kV Baser Pool Feeder (=L11) | 0 | 26104.5324 | -26104.5324 | -100 | CHECK
22 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 |  | HA021100697-02 | 1 | 29322895 | 31095860 | 1772965 | 1 |  | 1772965 | 1792379.5779 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 1792379.5779 | 2145386.6161 | -353007.0382 | -16.4542 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) |  | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) |  | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 14871216.0485 | 14710135 | 14871216.0485 | 1.095
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Demra | at 33 KV level |  | 12826265.6913
[6 empty] | Matuail | at 33 KV level |  | 2044950.3572
[6 empty] | Total = |  |  | 14871216.0485 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 38383.46 | 46039.096 | 7655.636 | 1000 | 0 | 7655636 | 7653416.6363
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 508.7791 | 537.5595 | 28.7804 | 240000 | 0 | 6907296 | 6905293.5796
| Siddhirganj 33 KV SIDE |  | 10: Total |  | 14562932 | 14558710.2159
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) |  | 33 |  | 84663042 | 1 | 516.19 | 544.98 | 28.79 | 240000 | 6909600
6 | 33 kV Shitalakhya-2 Feeder (Old) |  | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 7655636 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 |  | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 |  | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 14565236 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
11 | 33 kV ACI Pharmacuticles Feeder |  | 33 |  | DHKC4791 | 1 | 943.24 | 960.83 | 17.59 | 90000 |  | 1583100 |  | N.Gonj (East)
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 1583100
[7 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  | 7: 0; 8: 0
9 | 33/11 kV, 20/28 MVA T1 Transformer |  | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer |  | 33 |  | DHKC 9361 | 1 | 40559.36 | 50295.81 | 9736.45 | 240 |  | 2336748 |  |  | Meter Problem
|  |  | 10: Total |  | 12982136 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 14558710.2159; 6: EXPORT TO N.Gonj (East); 9=8-7: 1583100 | 33 KV NET IMPORT |  | 12975610.2159
| SIDDIRGANJ 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 12975610.2159 | 33 KV TX HV SIDE |  | 12982136
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -6525.7841
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.05029%
| TOTAL IMPORT |  | 4: 14558710.2159
11 KV SIDE of___KHANPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. |  | 11 |  | DHKC 9313 | 1 | 34465175.91 | 37858588.1 | 3393412.19 | 1 | 3393412.19 |  | 2167761.6636
18 | 33/11 kV Transformer-2 Incoming. |  | 11 |  | DHKC 9346 | 1 | 52103145.32 | 62167341.88 | 10064196.56 | 1 | 10064196.56 |  | 6429156.9241
24 | 33/11 kV 20/28 MVA T4 Incoming |  | 11 |  | 06604325 | 1 | 183.27 | 199.96 | 16.69 | 240000 | 4005600 |  | 2558836.2491
30 | 33/11 kV 20/28 MVA T1 Incoming |  | 11 |  | 06604374 | 1 | 104.74 | 116.61 | 11.87 | 240000 | 2848800 |  | 1819855.379
|  |  | 7: 0; 8: 0; 10: Total | 20312008.75 |  | 12975610.2159
| KHANPUR 11 KV SIDE |  | 7: 0; 8: 0
12 | 11 kV Khanpur Feeder | B723B | 11 |  | DHKC 9348 | 1 | 32799.1 | 55005.6 | 22206.5 | 60 |  | 1332390 | 1344397.4603 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1344397.4603 | 1671397.6523 | -327000.192 | -19.5645 | OK
13 | 11 kV Mission Para Feeder. | B723T | 11 |  | DHKC 9347 | 1 | 12889.86 | 33948.22 | 21058.36 | 60 |  | 1263501.6 | 1274888.2401 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1274888.2401 | 1557478.0335 | -282589.7935 | -18.1441 | OK
14 | 11 kV Esha Kha Feeder | B723M | 11 |  | DHKC 9311 | 1 | 29602.88 | 42944.3 | 13341.42 | 60 |  | 800485.2 | 807699.1496 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 807699.1496 | 1039293.9368 | -231594.7872 | -22.2839 | OK
15 | 11 kV New Hazigonj Feeder | B723F | 11 |  | DHKC 9314 | 1 | 275.24 | 302.18 | 26.94 | 60000 |  | 1616400 | 1630966.9503 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 1630966.9503 | 2057845.6627 | -426878.7125 | -20.744 | OK
16 | 11 kV Spare Feeder. |  | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | B723H | 11 |  | 6604412 | 1 | 8.03 | 8.79 | 0.76 | 60000 |  | 45600 | 46010.9459 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 46010.9459 | 61862.7343 | -15851.7884 | -25.6241 | OK
20 | 11 kV Old Hajiganj Feeder. | B723E | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 |  | 06604389 | 1 | 70259.15 | 85919.8 | 15660.65 | 60 |  | 939639 | 948106.9996 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 948106.9996 | 1250130.6264 | -302023.6268 | -24.1594 | OK
22 | 11 kV Spare Feeder. |  | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming |  | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | A723A | 11 |  | 6604415 | 1 | 375.72 | 413.32 | 37.6 | 40000 |  | 1504000 | 1517554.0047 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1517554.0047 | 1864372.9936 | -346818.9889 | -18.6024 | OK
26 | 11 kV Mondalpara Feeder. |  | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | B723C | 11 |  | 06604392 | 1 | 293.14 | 323.08 | 29.94 | 40000 |  | 1197600 | 1208392.7367 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1208392.7367 | 1428099.2005 | -219706.4637 | -15.3845 | OK
28 | 11 kV Bishaw Road Feeder. | B723A | 11 |  | 06604393 | 1 | 308.98 | 332.61 | 23.63 | 40000 |  | 945200 | 953718.1152 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 953718.1152 | 1117572.534 | -163854.4188 | -14.6616 | OK
29 | 11 kV Chasara Feeder. | A723B | 11 |  | 06604391 | 1 | 410.64 | 449.6 | 38.96 | 40000 |  | 1558400 | 1572444.256 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 1572444.256 | 1942004.6602 | -369560.4043 | -19.0298 | OK
31 | 11 kV Pathan Tully Feeder. | B723G | 11 |  | 06604388 | 1 | 65.03 | 78.12 | 13.09 | 40000 |  | 523600 | 528318.6681 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 528318.6681 | 576981.1889 | -48662.5207 | -8.434 | OK
32 | 11 kV Spare Feeder. |  | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | B722J | 11 |  | 6604289 | 1 | 266.66 | 294.9 | 28.24 | 40000 |  | 1129600 | 1139779.9227 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1139779.9227 | 1329442.2908 | -189662.3681 | -14.2663 | OK
34 | 11 kV Spare Feeder. |  | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. |  | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. |  | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 |  | 0.415 |  | 412109 | 1 | 9204 | 9234.3 | 30.3 | 10 |  | 303 | 305.7306 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 305.7306 | 270.9022 | 34.8285 | 12.8565 | OK
38 | 33/0.415 kV Auxiliary Transformer-2 |  | 0.415 |  | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 |  | 3000 | 3027.0359 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3027.0359 | 3032.487 | -5.4511 | -0.17976 | OK
|  |  | 10: Grand Total | 12975610.2159 | 12859718.8 | 12975610.2159 | 0.9012
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (West) | at 33 KV level |  | 3089998.2607
[6 empty] | N.Gonj (East) | at 33 KV level |  | 9885611.9552
[6 empty] | Total = |  |  | 12975610.2159 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail |  | 132 | Impt | 8993555 | 1 | 2867.349 | 2894.06 | 26.711 | 1440000 | 0 | 38463840
|  |  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar |  | 3: 132; 4: Impt; 6: 1; 9=8-7: 0 | 0 | 0
|  |  | 3: 132; 4: Expt; 6: 1; 9=8-7: 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 38463840
|  |  | 10: Net Total | 38463840
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder |  | 132 | Impt |  | 1 | 0 | 0 | 0 | 1 | 0
|  |  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  |  | 132 | Expt |  | 1 | 8845764 | 9004370 | 158606 | 1 | 158606
|  |  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder |  | 132 | Impt | HA040700237-03 | 1 | 35292309 | 45393605 | 10101296 | 1
|  |  | 132 |  | 06604364 | 1 | 6104.46 | 6108.75 | 4.29 | 960000 | 4118400
|  |  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
|  |  | 8: 0; 9=8-7: Total Import/Export | 4277006 | 0
|  |  | 8: 0; 9=8-7: Net Total | 4277006
| MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
| MOGBAZAR 132 KV SIDE |  | 8: 0
4 | 132/33 KV Transformer, GT-1 |  | 132 | DPDC | H/A040700240-03 | 1 | 100656.262 | 100656.262 | 0 | 1000 |  | 0
|  |  | 132 | P. Cell | 08993572 | 1 | 5035.178 | 5051.982 | 16.804 | 480000 |  | 8065920
5 | 132/33 KV Transformer, GT-2 |  | 132 | DPDC | H/A030700918-03 | 1 | 61470.348 | 80918.411 | 19448.063 | 1000 |  | 19448063
|  |  | 132 | P. Cell | 08993577 | 1 | 5141.562 | 5182.088 | 40.526 | 480000 |  | 19452480
|  |  | 10: Total |  | 19448063
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 4: 38463840; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 38622446
| 132 KV Sending From Maniknagar |  | 4: 158606; 6: 132 KV NET IMPORT; 9=8-7: 38622446 | 132/33 KV GT LV Side |  | 38620056
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 2390
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.006188%
| 132 KV TOTAL IMPORT |  | 4: 38622446
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | 4: IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 92536.341 | 111744.258 | 19207.917 | 1000 | 19207917
|  |  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 12913.01 | 32325.149 | 19412.139 | 1000 | 19412139
|  |  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 38620056 |  | 0
| MATUAIL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 |  | 33 | DPDC | H/A060300287-03 | 1.45 | 80475.35 | 87559.704 | 7084.354 | 1000 |  | 10272313.3 | 10294391.7589 |  | 17428512.3607 | Matuail 33/11 kv ss | 0.79088 | 33/11 KV Transformer, T-3 | 10294391.7589 | 11274886.4179 | -980494.659 | -8.6963 | OK
|  |  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 |  | 33 | DPDC | H/A060300190-03 | 1 | 79030.852 | 86159.232 | 7128.38 | 1000 |  | 7128380 | 7143701.1492 |  |  |  |  | 33/11 KV Transformer, T-4 | 7143701.1492 | 8483806.9272 | -1340105.778 | -15.796 | OK
|  |  | 33 | P. Cell | 08993581 | 1 | 6342.966 | 6382.515 | 39.549 | 180000 |  | 7118820 | 7134120.6018 |  |  |  |  | 0 | 7134120.6018 | 8456546.5169 | -1322425.9151 | -15.6379 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 17391133.3 | 17428512.3607 |  |  |  |  | 33 KV Feeders | 17428512.3607 | 19731432.9348 | -2302920.5741 | -11.6713 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 1280320 | 7233760 | 5953440 | 1 |  | 5953440 | 5966235.8306 |  | 14673871.1611 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 5966235.8306 | 7128361.5316 | -1162125.7011 | -16.3028 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.26 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 0 | 3.01 | -3.01 | -100 | CHECK
|  |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC |  | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 7200 | 7215.4751 | Matuail | Customer Number 35568341 | From AMR Reading |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 7215.4751 | 8160.0632 | -944.5881 | -11.5757 | OK
|  |  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 0 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 82417.915 | 88663.917 | 6246.002 | 1000 |  | 6246002 | 6259426.6391 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 6259426.6391 | 6831251.1517 | -571824.5126 | -8.3707 | OK
|  |  | 33 | P. Cell | 08993580 | 1.5 | 1413.422 | 1436.51 | 23.088 | 180000 |  | 6233760 | 6247158.3271 |  |  |  |  | 0 | 6247158.3271 | 6813366.8376 | -566208.5104 | -8.3103 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 6259426.6391 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 | DPDC | 00000154 | 1 | 8103040 | 16792000 | 8688960 | 1 |  | 8688960 | 8707635.3306 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 8707635.3306 | 9013333.1247 | -305697.7941 | -3.3916 | OK
|  |  | 10: Total |  | 20895602 | 20940513.2753 |  |  |  |  | 0 | 20940513.2753 | 22981108.8812 | -2040595.6059 | -8.8794 | OK
|  |  | 9=8-7: Grand Total | 38369025.636 | 38286735.3 | 38369025.636 | 0.21493
[6 empty] | 33 KV EXPORT |  |  | KWH
[6 empty] | EXPORT TO Matuail |  |  | 7215.4751
[6 empty] | Total Export |  |  | 7215.4751 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426631 | 1 | 7846895 | 7933529 | 86634 | 90 | 7797060 |  | 9137849.7413
11 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | 51426633 | 1 | 7479675 | 7558277 | 78602 | 90 | 7074180 |  | 8290662.6194
|  |  | 7: 0; 8: 0; 10: Total | 14871240 |  | 17428512.3607
| MATUAIL 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Link Road Feeder | B741N | 11 | Backup | DHK66629 | 1 | 24693.58 | 25054.42 | 360.84 | 8000 |  | 2886720 | 2909550.3778 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 2909550.3778 | 3118278.6369 | -208728.2591 | -6.6937 | OK
|  |  | 11 |  | HA021100475-02 | 1 | 97092.756 | 99970.287 | 2877.531 | 1000 |  | 2877531 | 2900288.7042 | N.Gonj (East) |  |  |  | 0 | 2900288.7042 | 3109326.5102 | -209037.8061 | -6.7229 | OK
4 | 11 kV Lamapara Express Feeder | B723L | 11 |  | HA021100928-03 | 1 | 80182.444 | 81154.775 | 972.331 | 1000 |  | 972331 | 980020.9332 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 980020.9332 | 1044271.2809 | -64250.3477 | -6.1526 | OK
5 | 11 kV Kutubpur Feeder*** | B741Q | 11 |  | DHK66616 | 1 | 18290.01 | 18505.85 | 215.84 | 8000 |  | 1726720 | 1740376.2153 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1740376.2153 | 1768072.7988 | -27696.5835 | -1.5665 | OK
|  |  | 11 | Backup | XA575929 | 1 | 45228.5 | 46952.4 | 1723.9 | 1000 |  | 1723900 | 1737533.9126 | N.Gonj (East) |  |  |  | 0 | 1737533.9126 | 1765667.78 | -28133.8674 | -1.5934 | OK
6 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 |  | DHK66625 | 1 | 3580.6 | 3598.24 | 17.64 | 60000 |  | 1058400 | 1066770.6323 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1066770.6323 | 1419365.2857 | -352594.6534 | -24.8417 | OK
|  |  | 11 | Backup |  | 1 | 8395.82 | 8395.82 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Tushardhara Feeder (F2) | E241T | 11 |  | DHK66623 | 1 | 3931.53 | 3975.1 | 43.57 | 60000 |  | 2614200 | 2634875.0823 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2634875.0823 | 2672602.3834 | -37727.3011 | -1.4116 | OK
8 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 |  | DHK66627 | 1 | 3332.15 | 3345.82 | 13.67 | 60000 |  | 820200 | 826686.7655 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 826686.7655 | 937957.3247 | -111270.5591 | -11.8631 | OK
|  |  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 |  | HA021101044-02 | 1 | 66528.706 | 66770.571 | 241.865 | 1000 |  | 241865 | 243777.8524 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 243777.8524 | 299669.3822 | -55891.5298 | -18.6511 | OK
12 | 11 kV Shibu Market Feeder (F7) | B841B | 11 |  | DHK66624 | 1 | 2390.92 | 2396.07 | 5.15 | 60000 |  | 309000 | 311443.8071 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 311443.8071 | 425021.3863 | -113577.5792 | -26.7228 | OK
13 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 |  | HA060300286-03 | 1 | 5075.064 | 6365.598 | 1290.534 | 1000 |  | 1290534 | 1300740.5246 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 1300740.5246 | 1507092.8931 | -206352.3685 | -13.6921 | OK
14 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 |  | DHK66626 | 1 | 4509.48 | 4543.46 | 33.98 | 60000 |  | 2038800 | 2054924.3814 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2054924.3814 | 2632586.1045 | -577661.7232 | -21.9427 | OK
15 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK6622 | 1 | 4256.29 | 4277.24 | 20.95 | 60000 |  | 1257000 | 1266941.3122 | Matuail |  |  |  | 0 | 1266941.3122 | 1346002.1078 | -79060.7956 | -5.8737 | OK
16 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 |  | DHKA2187 | 1 | 126.118 | 131.7799 | 5.6619 | 60000 |  | 339714 | 342400.7167 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 342400.7167 | 335087.831 | 7312.8857 | 2.1824 | OK
17 | 11 kV Bhuighor Bazar |  | 11 |  | HA021100861-02 | 1 | 2266.614 | 3332.199 | 1065.585 | 1000 |  | 1065585 | 1074012.4568 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 1074012.4568 | 1411612.637 | -337600.1802 | -23.9159 | OK
18 | 11 kV Tokkar Math Feeder | B8416 | 11 |  | HA021200298-02 | 1 | 82630.261 | 83283.485 | 653.224 | 1000 |  | 653224 | 658390.1923 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 658390.1923 | 791536.1434 | -133145.9511 | -16.8212 | OK
19 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 |  | XA575922 | 1 | 232.8 | 249.9 | 17.1 | 1000 |  | 17100 | 17235.2398 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 17235.2398 | 19603.9346 | -2368.6948 | -12.0828 | OK
16 | 33/0.415 KV Transformer, AT-1 |  | 0.415 |  | 2001123043119 | 1 | 7578.2 | 7626.4 | 48.2 | 160 |  | 7712 | 7772.9924 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 7772.9924 | 11624.9311 | -3851.9388 | -33.1352 | OK
17 | 33/0.415 KV Transformer, AT-2 |  | 0.415 |  | 2001123043157 | 1 | 4715.3 | 4726.8 | 11.5 | 160 |  | 1840 | 1854.5521 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 1854.5521 | 0 | 1854.5521 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 17428512.3607 | 17291756 | 17428512.3607 | 0.79088
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 5620685.8527
[6 empty] | Shyampur | at 33 KV level |  | 352028.2612
[6 empty] | Fatullah | at 33 KV level |  | 3354580.3961
[6 empty] | Matuail | at 33 KV level |  | 8101217.8506
[6 empty] | Total = |  |  | 17428512.3607 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 1280320 | 7233760 | 5953440 | 1 | 0 | 5953440 | 5966235.8306
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 |  | 00000154 | 1 | 8103040 | 16792000 | 8688960 | 1 | 0 | 8688960 | 8707635.3306
|  |  | 10: Total | 0 | 14642400 | 14673871.1611
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder |  | 33 |  | 00000079 | 1 | 355244928 | 363851200 | 8606272 | 1 | 8606272
7 | 33 kV Matuail-1 Feeder |  | 33 |  | 00000114 | 1 | 289280960 | 295190176 | 5909216 | 1 | 5909216
|  |  | 7: 0; 8: 0; 10: Total | 14515488 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000075 | 1 | 369965504 | 378491040 | 8525536 | 1 |  | 8525536
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000156 | 1 | 274632704 | 280624576 | 5991872 | 1 |  | 5991872
|  |  | 10: Total |  | 14517408
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 14673871.1611; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 14673871.1611
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 14673871.1611 | 33 KV TX HV Side |  | 14517408
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 156463.1611
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.066%
| TOTAL IMPORT |  | 4: 14673871.1611
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming |  | 11 |  | 00000144 | 1 | 368629376 | 377131200 | 8501824 | 1 | 8501824 |  | 8620531.036
18 | 11 kV T-1 Incoming |  | 11 |  | 00000054 | 1 | 272994144 | 278964128 | 5969984 | 1 | 5969984 |  | 6053340.1252
|  |  | 7: 0; 8: 0; 10: Total | 14471808 |  | 14673871.1611
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Godnail (F16) | A8963 | 11 |  | 00000109 | 1 | 30618406 | 32205162 | 1586756 | 1 |  | 1586756 | 1608130.1776 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1608130.1776 | 1902311.4075 | -294181.2299 | -15.4644 | OK
2 | 11 kV M. Circus (F15) | B796C | 11 |  | 00000123 | 1 | 112349288 | 114200200 | 1850912 | 1 |  | 1850912 | 1875844.4545 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1875844.4545 | 1681278.3417 | 194566.1129 | 11.5725 | OK
3 | 11 kV Wapderpool (F14) | B723W | 11 |  | 00000190 | 1 | 58342616 | 59257536 | 914920 | 1 |  | 914920 | 927244.3035 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 927244.3035 | 798221.6352 | 129022.6683 | 16.1638 | OK
4 | 11 kV Chowdhury Bari (F13) | A896C | 11 |  | 00000191 | 1 | 105146864 | 107236336 | 2089472 | 1 |  | 2089472 | 2117617.9441 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2117617.9441 | 2183088.6246 | -65470.6805 | -2.999 | OK
5 | 11 kV Ailpara (F12) | B7966 | 1 |  | 00000192 | 1 | 58996976 | 61060412 | 2063436 | 1 |  | 2063436 | 2091231.2297 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2091231.2297 | 2449465.553 | -358234.3233 | -14.625 | OK
6 | 11 kV Spare (F11) |  | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) |  | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) |  | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) |  | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | A8962H | 11 |  | 00000197 | 1 | 18664354 | 19720952 | 1056598 | 1 |  | 1056598 | 1070830.7575 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1070830.7575 | 1205147.4911 | -134316.7336 | -11.1453 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 |  | 00000198 | 1 | 4241549 | 4290309 | 48760 | 1 |  | 48760 | 49416.8148 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 49416.8148 | 38314.1839 | 11102.6309 | 28.9779 | OK
12 | 11 kV Lucky Bazar (F5) | B796Z | 11 |  | 00000199 | 1 | 92459576 | 93619848 | 1160272 | 1 |  | 1160272 | 1175901.2838 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1175901.2838 | 1409832.0895 | -233930.8057 | -16.5928 | OK
13 | 11 kV Enayetnagar (F4) | A896Y | 11 |  | 00000200 | 1 | 35538712 | 36816152 | 1277440 | 1 |  | 1277440 | 1294647.5791 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1294647.5791 | 1539178.9886 | -244531.4094 | -15.8871 | OK
14 | 11 kV Bhuiyapara (F3) | A896V | 11 |  | 00000201 | 1 | 69299712 | 70774584 | 1474872 | 1 |  | 1474872 | 1494739.0596 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1494739.0596 | 1820491.9548 | -325752.8952 | -17.8937 | OK
15 | 11 kV Arambagh (F2) | B796D | 11 |  | 00000202 | 1 | 11191773 | 12144210 | 952437 | 1 |  | 952437 | 965266.6711 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 965266.6711 | 1110256.976 | -144990.3049 | -13.0592 | OK
16 | 11 kV Spare (F1) |  | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 |  | 0.415 |  | 00000204 | 1 | 1753.31 | 1782.91 | 29.6 | 100 |  | 2960 | 2999.8723 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 2999.8723 | 4062.7646 | -1062.8924 | -26.1618 | OK
18 | 11/0.415 kV Aux. Transformer-2 |  | 0.415 |  | 00000205 | 1 | 61.16 | 61.17 | 0.01 | 100 |  | 1 | 1.0135 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 1.0135 | 44.6458 | -43.6323 | -97.73 | CHECK
|  |  | 10: Grand Total | 14673871.1611 | 14478836 | 14673871.1611 | 1.347
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 7087905.6432
[6 empty] | Siddirgonj | at 33 KV level |  | 7585965.5179
[6 empty] | Total = |  |  | 14673871.1611 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.26 | 39497.26 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side |  | 10: Total | 0 | 0 | 0
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 763.72 | 785.87 | 22.15 | 360000 | 0 | 7974000 | 7968104.5357
0 | 0 |  | 33 | Backup | 041808904262 | 1 | 763.74 | 785.88 | 22.14 | 360000 | 0 | 7970400 | 7964507.1973
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 521.27 | 530.58 | 9.31 | 360000 | 0 | 3351600 | 3349122.0419
0 | 0 |  | 33 | Backup | 041808904258 | 1 | 521.47 | 530.78 | 9.31 | 360000 | 0 | 3351600 | 3349122.0419
|  |  | 10: Total | 0 | 11325600 | 11317226.5775
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) |  | 33 | Digital | DHK60875 | 1 | 348151.5 | 381161.7 | 33010.2 | 240 | 7922448
9 | 33 kV New Fatulla-2 |  | 33 | Digital | DHK2186 | 1 | 365.6807 | 375.0002 | 9.3195 | 360000 | 3355020
|  |  | 7: 0; 8: 0; 10: Total | 11277468 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  | 7: 0; 8: 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60980 | 1 | 5390.6 | 29151.7 | 23761.1 | 240 |  | 5702664
13 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 | Digital | DHK60952 | 1 | 539976.3 | 549175.1 | 9198.8 | 240 |  | 7922448 |  |  | Meter Problem
|  |  | 10: Total |  | 13625112 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 11317226.5775
| New Fatullah 33 kv Side |  | 4: 11317226.5775; 6: 33 KV Net Import; 9=8-7: 11317226.5775 | 33 KV TX HV Side |  | 13625112
[11 empty] | LOSS UNITS=> |  | -2307885.4225
[11 empty] | LOSS % IN => |  | -20.39%
| TOTAL IMPORT |  | 4: 11317226.5775
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 | New | DHK61060 | 1 | 210760.5 | 240545.7 | 29785.2 | 180 | 5361336 |  | 5566999.9805 | [7 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 | New | DHK61054 | 1 | 438470.1 | 450703.8 | 12233.7 | 180 | 2202066 |  | 2286538.538 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming |  | 11 | New | DHK60924 | 1.1 | 487046.8 | 493401 | 6354.2 | 180 | 1258131.6 |  | 1306394.263 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming |  | 11 | New | DHK61051 | 1 | 6319.9 | 29404.3 | 23084.4 | 90 | 2077596 |  | 2157293.7961 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 10899129.6 |  | 11317226.5775 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | A717R | 11 | New |  | 1 | 77458900 | 78084808 | 625908 | 1 |  | 625908 | 632806.8774 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 632806.8774 | 639787.7036 | -6980.8262 | -1.0911 | OK
15 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 90382612 | 91204625 | 822013 | 1 |  | 822013 | 831073.3841 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 831073.3841 | 837776.7717 | -6703.3876 | -0.80014 | OK
16 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 205819 | 228288.5 | 22469.5 | 60 |  | 1348170 | 1363029.7869 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1363029.7869 | 1190995.536 | 172034.2509 | 14.4446 | OK
17 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 358618.1 | 370704.6 | 12086.5 | 60 |  | 725190 | 733183.1825 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 733183.1825 | 994384.377 | -261201.1945 | -26.2676 | OK
19 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 67878.2 | 94344.4 | 26466.2 | 60 |  | 1587972 | 1605474.9303 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1605474.9303 | 1916663.5337 | -311188.6035 | -16.236 | OK
20 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 91772.6 | 102086.1 | 10313.5 | 60 |  | 618810 | 625630.6419 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 625630.6419 | 700600.4968 | -74969.8549 | -10.7008 | OK
23 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 661621.5 | 676359 | 14737.5 | 60 |  | 884250 | 893996.3722 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 893996.3722 | 935867.4295 | -41871.0573 | -4.474 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 559147.2 | 576544.9 | 17397.7 | 60 |  | 1043862 | 1055367.6461 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1055367.6461 | 1081150.4699 | -25782.8238 | -2.3848 | OK
25 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 877493.5 | 882166.7 | 4673.2 | 60 |  | 280392 | 283482.5341 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 283482.5341 | 300394.2285 | -16911.6943 | -5.6298 | OK
26 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Dhaka Steel | 0 | 3404.6005 | -3404.6005 | -100 | CHECK
27 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 2534578 | 3152340 | 617762 | 1 |  | 617762 | 624571.0906 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 624571.0906 | 739019.2541 | -114448.1635 | -15.4865 | OK
28 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 25882355 | 26146252 | 263897 | 1 |  | 263897 | 266805.7231 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 266805.7231 | 329009.9458 | -62204.2227 | -18.9065 | OK
29 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 16128427 | 16501720 | 373293 | 1 |  | 373293 | 377407.5066 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 377407.5066 | 371813.5071 | 5593.9995 | 1.5045 | OK
30 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 17649412 | 18251948 | 602536 | 1 |  | 602536 | 609177.2667 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 609177.2667 | 739088.5512 | -129911.2845 | -17.5772 | OK
35 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 179956 | 1166208 | 986252 | 1 |  | 986252 | 997122.6577 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 997122.6577 | 1798366.2205 | -801243.5629 | -44.554 | CHECK
37 | 11 kV Spare Feeder |  | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 |  | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 10899129.6 | 10780307 | 10899129.6 | 1.1022
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 8166465.0182
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1463880.2614
[6 empty] | Sytalakhya | at 33 KV level |  | 1268784.3203
[6 empty] | Total = |  |  | 10899129.6 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder |  | 132 | Export | 041808902770 | 1 | 126.96 | 126.99 | 0.03 | 1200000 |  | 36000
|  |  | 132 |  | 041808904227 | 1 | 126.96 | 126.99 | 0.03 | 1200000 |  | 36000
|  |  | 132 | Import | 041808902770 | 1 | 256.46 | 282.88 | 26.42 | 1200000 | 31704000
|  |  | 132 |  | 041808904227 | 1 | 256.42 | 282.84 | 26.42 | 1200000 | 31704000
3 | 132 kV Haripur Feeder |  | 132 | Export | 041808902766 | 1 | 91.34 | 122.48 | 31.14 | 1200000 |  | 37368000
|  |  | 132 |  | 041808904230 | 1 | 91.38 | 122.53 | 31.15 | 1200000 |  | 37380000
|  |  | 132 | Import | 041808902766 | 1 | 720.47 | 720.75 | 0.28 | 1200000 | 336000
|  |  | 132 |  | 041808904230 | 1 | 720.72 | 721 | 0.28 | 1200000 | 336000
4 | 132 kV Aggreko Feeder |  | 132 | Export | 041808902768 | 1 | 30.88 | 31.37 | 0.49 | 1200000 |  | 588000
|  |  | 132 |  | 041808904219 | 1 | 30.88 | 31.37 | 0.49 | 1200000 |  | 588000
|  |  | 132 | Import | 041808902768 | 1 | 259.55 | 268.85 | 9.3 | 1200000 | 11160000
|  |  | 132 |  | 041808904219 | 1 | 259.55 | 268.85 | 9.3 | 1200000 | 11160000
6 | 132 kV Shyampur-2 Feeder |  | 132 | Export | 041808902793 | 1 | 120.73 | 120.76 | 0.03 | 1200000 |  | 36000
|  |  | 132 |  | 041808904278 | 1 | 120.74 | 120.78 | 0.04 | 1200000 |  | 48000
|  |  | 132 | Import | 041808902793 | 1 | 248.72 | 275.62 | 26.9 | 1200000 | 32280000
|  |  | 132 |  | 041808904278 | 1 | 248.76 | 275.68 | 26.92 | 1200000 | 32304000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 75480000 | 38028000
|  |  | 7: 0; 8: 0; 10: Net Total | 37452000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| FATULLAH 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | Export | 041808902767 | 1 | 631.52 | 648.14 | 16.62 | 1200000 |  | 19944000
|  |  | 132 | Export | 041808904228 | 1 | 631.35 | 647.97 | 16.62 | 1200000 |  | 19944000
5 | 132/33 kV, 80/120 MVA GT-2 |  | 132 | Export | 041808902792 | 1 | 486.92 | 501.51 | 14.59 | 1200000 |  | 17508000
|  |  | 132 | Export | 041808904251 | 1 | 486.73 | 501.32 | 14.59 | 1200000 |  | 17508000
|  |  | 10: Total |  | 37452000
| 132 KV IMPORT |  | 4: KWH | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 4: 37452000 | 132 KV NET IMPORT |  | 37452000
| IMPORT-2 | [9 empty] | 132/33 KV GT LV Side |  | 37303200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 148800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3973%
| 132 KV TOTAL IMPORT |  | 4: 37452000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902796 | 1 | 1047.58 | 1075.17 | 27.59 | 720000 | 19864800
|  |  | 33 | Backup | 041808904255 | 1 | 1047.58 | 1075.17 | 27.59 | 720000 | 19864800
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902802 | 1 | 808.06 | 832.28 | 24.22 | 720000 | 17438400
|  |  | 33 | Backup | 041808904281 | 1 | 807.86 | 832.07 | 24.21 | 720000 | 17431200
|  |  | 7: 0; 8: 0; 10: Total | 37303200 |  | 0
| FATULLAH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902868 | 1 | 835.73 | 857.74 | 22.01 | 240000 |  | 5282400 | 5278494.5321 |  | 11377182.2174 | New Fatullah 33/11 kv ss | 0.23243 | 33/11 kV, 28/35 MVA T-1 (=H5) | 5278494.5321 | 6358719.5465 | -1080225.0144 | -16.9881 | OK
|  |  | 33 | Backup | 041808904277 | 1 | 835.19 | 857.19 | 22 | 240000 |  | 5280000 | 5276096.3065 |  |  |  |  | 0 | 5276096.3065 | 6353922.3231 | -1077826.0166 | -16.9632 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902824 | 1 | 737.7 | 763.13 | 25.43 | 240000 |  | 6103200 | 6098687.6852 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 6098687.6852 | 6473852.9068 | -375165.2216 | -5.7951 | OK
|  |  | 33 | Backup | 041808904267 | 1 | 737.58 | 763 | 25.42 | 240000 |  | 6100800 | 6096289.4596 |  |  |  |  | 0 | 6096289.4596 | 6471454.2951 | -375164.8355 | -5.7972 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 11385600 | 11377182.2174 |  |  |  |  | 33 KV Feeders | 11377182.2174 | 12832572.4533 | -1455390.2359 | -11.3414 | OK
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 801.89 | 820.3 | 18.41 | 360000 |  | 6627600 | 6622699.9775 |  | 14608791.2051 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 6622699.9775 | 7221020.4431 | -598320.4656 | -8.2858 | OK
|  |  | 33 | Backup | 041808904220 | 1 | 801.49 | 819.89 | 18.4 | 360000 |  | 6624000 | 6619102.6391 |  |  |  |  | 0 | 6619102.6391 | 7203030.8556 | -583928.2164 | -8.1067 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) |  | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 763.72 | 785.87 | 22.15 | 360000 |  | 7974000 | 7968104.5357 |  | 11317226.5775 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 7968104.5357 | 8606218.6846 | -638114.1489 | -7.4146 | OK
|  |  | 33 | Backup | 041808904262 | 1 | 763.74 | 785.88 | 22.14 | 360000 |  | 7970400 | 7964507.1973 |  |  |  |  | 0 | 7964507.1973 | 8609816.6021 | -645309.4048 | -7.495 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 578.03 | 600.23 | 22.2 | 360000 |  | 7992000 | 7986091.2276 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 7986091.2276 | 8832887.4877 | -846796.2601 | -9.5869 | OK
|  |  | 33 | Backup | 041808904219 | 1 | 578.38 | 600.6 | 22.22 | 360000 |  | 7999200 | 7993285.9044 |  |  |  |  | 0 | 7993285.9044 | 8840083.3227 | -846797.4183 | -9.5791 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 521.27 | 530.58 | 9.31 | 360000 |  | 3351600 | 3349122.0419 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 3349122.0419 | 3972100.9313 | -622978.8895 | -15.6839 | OK
|  |  | 33 | Backup | 041808904258 | 1 | 521.47 | 530.78 | 9.31 | 360000 |  | 3351600 | 3349122.0419 |  |  |  |  | 0 | 3349122.0419 | 3975698.8488 | -626576.807 | -15.7602 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) |  | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 25945200 | 25926017.7826 |  |  |  |  | 0 | 25926017.7826 | 28632227.5467 | -2706209.7641 | -9.4516 | OK
|  |  | 9=8-7: Grand Total | 37303200 | 37330800 | 37303200 | -0.073934
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902832 | 1 | 800.08 | 821.16 | 21.08 | 250000 | 5270000 |  | 5282621.1705
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902765 | 1 | 706.13 | 730.45 | 24.32 | 250000 | 6080000 |  | 6094561.0468
|  |  | 7: 0; 8: 0; 10: Total | 11350000 |  | 11377182.2174
| FATULLAH 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) |  | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 999.44 | 1032.15 | 32.71 | 60000 |  | 1962600 | 1967161.5939 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 1967161.5939 | 2374197.2935 | -407035.6996 | -17.1441 | OK
7 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 497.96 | 519.22 | 21.26 | 60000 |  | 1275600 | 1278564.8268 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1278564.8268 | 1599035.1072 | -320470.2804 | -20.0415 | OK
8 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 563.73 | 572.34 | 8.61 | 60000 |  | 516600 | 517800.713 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 517800.713 | 643462.7923 | -125662.0793 | -19.529 | OK
9 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1267.53 | 1292.66 | 25.13 | 60000 |  | 1507800 | 1511304.5202 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1511304.5202 | 1737349.5392 | -226045.0191 | -13.0109 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) |  | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) |  | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 213.78 | 227.78 | 14 | 60000 |  | 840000 | 841952.3789 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 841952.3789 | 1083663.5063 | -241711.1274 | -22.305 | OK
16 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 98.21 | 105.2 | 6.99 | 60000 |  | 419400 | 420374.7949 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 420374.7949 | 572501.475 | -152126.6801 | -26.5723 | OK
17 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1178.03 | 1220.63 | 42.6 | 60000 |  | 2556000 | 2561940.8101 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 2561940.8101 | 2204010.4054 | 357930.4047 | 16.24 | OK
18 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1452.18 | 1490.06 | 37.88 | 60000 |  | 2272800 | 2278082.5795 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2278082.5795 | 2618352.3343 | -340269.7548 | -12.9956 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 11377182.2174 | 11350800 | 11377182.2174 | 0.23243
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 11377182.2174
[6 empty] | Total = |  |  | 11377182.2174 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 801.89 | 820.3 | 18.41 | 360000 | 0 | 6627600 | 6622699.9775
0 | 0 |  | 33 | Backup | 041808904220 | 1 | 801.49 | 819.89 | 18.4 | 360000 | 0 | 6624000 | 6619102.6391
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 578.03 | 600.23 | 22.2 | 360000 | 0 | 7992000 | 7986091.2276
0 | 0 |  | 33 | Backup | 041808904219 | 1 | 578.38 | 600.6 | 22.22 | 360000 | 0 | 7999200 | 7993285.9044
| DAPA 33 KV SIDE (RECEIVING) |  | 10: Total | 0 | 14619600 | 14608791.2051
5 | 33 kV New Fatullah Incoming Circuit-2 |  | 33 | Import |  | 1 | 207699664 | 215665744 | 7966080 | 1 | 7966080
6 | 33 kV Shyampur Incoming Circuit |  | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder |  | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  |  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 |  | 33 | Import |  | 1 | 288178816 | 294787360 | 6608544 | 1 | 6608544
|  |  | 7: 0; 8: 0; 10: Total | 14574624 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DAPA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) |  | 33 | Export | 00000135 | 1 | 299261760 | 307227584 | 7965824 | 1 |  | 7965824
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) |  | 33 | Export | 00000193 | 1 | 289843904 | 296447040 | 6603136 | 1 |  | 6603136
|  |  | 10: Total |  | 14568960 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 4: 14608791.2051; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 14568960
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 14568960 | 33 KV TX HV SIDE |  | 14568960
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 14608791.2051
11 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000035 | 1 | 81020736 | 81020736 | 0 | 1 | 0 |  | 0
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000143 | 1 | 297978560 | 305916544 | 7937984 | 1 | 7937984 |  | 14568960
|  |  | 7: 0; 8: 0; 10: Total | 7937984 |  | 14568960
| DAPA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV Katherpol Feeder | B8919 | 11 |  | 00000031 | 1 | 69331312 | 71074344 | 1743032 | 1 |  | 1743032 | 1780543.7815 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 1780543.7815 | 2017920.9065 | -237377.125 | -11.7635 | OK
12 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | B8918 | 11 |  | 00000032 | 1 | 69825752 | 71909144 | 2083392 | 1 |  | 2083392 | 2128228.6671 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 2128228.6671 | 2252272.5782 | -124043.9111 | -5.5075 | OK
14 | 11 kV Shiachar Feeder | B891G | 11 |  | 00000030 | 1 | 71832544 | 73433864 | 1601320 | 1 |  | 1601320 | 1635781.9984 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 1635781.9984 | 2031118.288 | -395336.2896 | -19.464 | OK
15 | 11 kV Sastapur Feeder | B8913 | 11 |  | 00000106 | 1 | 71818424 | 72296704 | 478280 | 1 |  | 478280 | 488573.0611 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 488573.0611 | 516338.7434 | -27765.6823 | -5.3774 | OK
17 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | B891JA | 11 |  | 00000172 | 1 | 5637386 | 5879505 | 242119 | 1 |  | 242119 | 247329.6416 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 247329.6416 | 398396.8352 | -151067.1936 | -37.9188 | OK
19 | 11 kV Hajibari Feeder |  | 11 |  | 00000105 | 1 | 80 | 164959 | 164879 | 1 |  | 164879 | 168427.36 | Fatullah |  |  |  | 11 kV Hajibari Feeder | 168427.36 | 0 | 168427.36 | #DIV/0! | #DIV/0!
21 | 11 kV Railine Feeder |  | 11 |  |  | 1 | 0 | 195799 | 195799 | 1 |  | 195799 | 200012.7891 | Fatullah |  |  |  | 11 kV Railine Feeder | 200012.7891 | 0 | 200012.7891 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | B8911 | 11 |  | 00000044 | 1 | 84092032 | 86381512 | 2289480 | 1 |  | 2289480 | 2338751.8857 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 2338751.8857 | 2709693.2174 | -370941.3317 | -13.6894 | OK
23 | 11 kV Kotaler Bag Feeder | B8912 | 11 |  | 00000050 | 1 | 89610784 | 91574936 | 1964152 | 1 |  | 1964152 | 2006422.5038 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 2006422.5038 | 2309410.8982 | -302988.3944 | -13.1197 | OK
24 | 11 kV Idrakpur Feeder | B8915 | 11 |  | 00000021 | 1 | 79058888 | 80022008 | 963120 | 1 |  | 963120 | 983847.2999 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 983847.2999 | 1146390.3941 | -162543.0942 | -14.1787 | OK
25 | 11 kV Isdair Feeder | B8914 | 11 |  | 00000029 | 1 | 42475456 | 43086456 | 611000 | 1 |  | 611000 | 624149.3274 | Fatullah |  |  |  | 11 kV Isdair Feeder | 624149.3274 | 790469.7993 | -166320.4719 | -21.0407 | OK
26 | 11 kV Shah Fateullah Express |  | 11 |  | 0000051 | 1 | 2873073 | 4770108 | 1897035 | 1 |  | 1897035 | 1937861.0792 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 1937861.0792 | 1875856.2789 | 62004.8003 | 3.3054 | OK
27 | 11 kV Boubazar Feeder |  | 11 |  | 00000151 | 1 | 0 | 23719 | 23719 | 1 |  | 23719 | 24229.4565 | Fatullah |  |  |  | 11 kV Boubazar Feeder | 24229.4565 | 0 | 24229.4565 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKF 7522 | 1 | 3192 | 3239 | 47 | 100 |  | 4700 | 4801.1487 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 4801.1487 | 6039.9915 | -1238.8429 | -20.5107 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 14568960 | 14262027 | 14568960 | 2.1521
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 14568960
[6 empty] | Total = |  |  | 14568960 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 |  | 132 | IMPORT | 50501730 | 1 | 2948.743 | 2986.08 | 37.337 | 480000 | 0 | 17921760
2 | Tranformer 1 |  | 132 |  | 80505634 | 1 | 8541.707 | 8576.821 | 35.114 | 480000 | 0 | 16854720
3 | Tranformer 2 |  | 132 |  | 80505637 | 1 | 8494.043 | 8529.331 | 35.288 | 480000 | 0 | 16938240
4 | MI CEMENT |  | 132 |  | 38992489 (New) | 1 | 350.233 | 375.942 | 25.709 | 480000 | 0 | 12340320
|  |  | 9=8-7: Total Import/Export | 0 | 64055040
|  |  | 10: Net Total | 64055040
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 350.233 | 375.928 | 25.695 | 480000 |  | 12333600
|  |  | 132 | DPDC | 16402670 | 1 | 1875.206 | 1900.898 | 25.692 | 480000 |  | 12332160
|  |  | 10: Total |  | 12332160
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 51722880
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 64055040; 6: EXPORT TO OTHER S/S; 9=8-7: 12332160 | 132 KV NET IMPORT |  | 51722880
| IMPORT-2 |  | 6: 132 KV NET IMPORT for Sitalakhya 33/11 KV; 9=8-7: 51722880 | GT (33 KV Side) |  | 51655159
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 67721
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1309%
| 132 KV TOTAL IMPORT |  | 4: 64055040
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A030701130-03 | 1 | 30217.589 | 47153.34 | 16935.751 | 1000 | 16935751
|  |  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  |  | 33 | DPDC | BD001913 | 1 | 1848.6479 | 1883.7495 | 35.1016 | 480000 | 16848768
18 | 132/33 KV Transformer, GT-3 Incoming |  | 33 | DPDC | BD001915 | 1 | 2941.3245 | 2978.555 | 37.2305 | 480000 | 17870640
|  |  | 7: 0; 8: 0; 10: Total | 51655159 |  | 0
| SITALAKHYA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 |  | 33 | DPDC | H/A030701089-03 | 1 | 98625.747 | 107336.072 | 8710.325 | 1000 |  | 8710325 | 8707799.8827 |  | 12643176.6888 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 8707799.8827 | 9301117.9185 | -593318.0358 | -6.379 | OK
|  |  | 33 | P. Cell | 08993597 | 1 | 5984.717 | 6020.945 | 36.228 | 240000 |  | 8694720 | 8692199.4065 |  |  |  |  | 0 | 8692199.4065 | 9287515.0893 | -595315.6828 | -6.4098 | OK
13 | 33/11 KV Transformer T-4 |  | 33 | DPDC | H/A030701087-03 | 1 | 85925.898 | 89862.416 | 3936.518 | 1000 |  | 3936518 | 3935376.8061 |  |  |  |  | 33/11 KV Transformer T-4 | 3935376.8061 | 4759677.5238 | -824300.7177 | -17.3184 | OK
|  |  | 33 | P. Cell | 08993925 | 1 | 5738.492 | 5760.334 | 21.842 | 180000 |  | 3931560 | 3930420.2434 |  |  |  |  | 0 | 3930420.2434 | 4757191.1034 | -826770.86 | -17.3794 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 12646843 | 12643176.6888 |  |  |  |  | 33 KV Feeders | 12643176.6888 | 14060795.4423 | -1417618.7536 | -10.0821 | OK
10 | 33 KV Char Syedpur Feeder (F1) |  | 33 | DPDC | H/A030701083-03 | 1 | 42622.667 | 42622.667 | 0 | 1000 |  | 0 | 0 |  | 179.9478 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 34 KV Char Syedpur Feeder (F1) |  | 33 | P. Cell | 08993596 | 1 | 2186.831 | 2186.832 | 0.001 | 180000 |  | 180 | 179.9478 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 179.9478 | 2519.4127 | -2339.4649 | -92.8575 | CHECK
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 52115.953 | 63140.766 | 11024.813 | 1000 |  | 11024813 | 11021616.9142 |  | 11021616.9142 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 11021616.9142 | 11933830.2359 | -912213.3217 | -7.6439 | OK
| 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9914.297 | 9975.444 | 61.147 | 180000 |  | 11006460 | 11003269.2347 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 11003269.2347 | 11933918.2153 | -930648.9807 | -7.7984 | OK
14 | 33 KV Shah Cement Feeder (F2) |  | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 0 | 108.9746 | -108.9746 | -100 | CHECK
|  |  | 33 | P. Cell | 08993926 | 1 | 2303.686 | 2303.686 | 0 | 180000 |  | 0 | 0 |  | 14558710.2159 | Khanpur 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 38383.46 | 46039.096 | 7655.636 | 1000 |  | 7655636 | 7653416.6363 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 7653416.6363 | 9044378.7642 | -1390962.1279 | -15.3793 | OK
|  |  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1692.0883 | 1729.3965 | 37.3082 | 180000 |  | 6715476 | 6713529.188 |  | 13376109.1505 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 6713529.188 | 7589982.7824 | -876453.5944 | -11.5475 | OK
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 508.7791 | 537.5595 | 28.7804 | 240000 |  | 6907296 | 6905293.5796 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 6905293.5796 | 8296306.1392 | -1391012.5596 | -16.7666 | OK
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1391.8606 | 1419.6294 | 27.7688 | 240000 |  | 6664512 | 6662579.9625 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 6662579.9625 | 8007605.435 | -1345025.4725 | -16.7968 | OK
21 | 33/0.415 KV Transformer AT-1 |  | 0.415 | DPDC | 2001123043108 | 1 | 6559.9 | 6583.1 | 23.2 | 160 |  | 3712 | 3710.9239 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 3710.9239 | 639.8509 | 3071.073 | 479.967 | FAULT
22 | 33/0.415 KV Transformer AT-2 |  | 0.415 | DPDC | 2001123043171 | 1 | 4786.1 | 4786.1 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 0 | 3647.1499 | -3647.1499 | -100 | CHECK
|  |  | 10: Total |  | 38971625 | 38960327.1522 |  |  |  |  | 0 | 38960327.1522 | 44879018.7447 | -5918691.5924 | -13.1881 | OK
|  |  | 9=8-7: Grand Total | 51603503.841 | 51618468 | 51603503.841 | -0.02899
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 3710.9239
[6 empty] | Total = |  |  | 3710.9239
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | DHK 9372 | 1 | 26942.4609 | 74991.6605 | 48049.1996 | 180 | 8648855.928 |  | 8701056.5654 |  |  |  |  | 33/11 kV Transformer, T-3 Incoming | 8701056.5654 | 9303322.5104 | -602265.945 | -6.4737 | OK
10 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | DHK 9368 | 1 | 69190.5714 | 90959.8491 | 21769.2777 | 180 | 3918469.986 |  | 3942120.1234 |  |  |  |  | 33/11 kV Transformer, T-4 Incoming | 3942120.1234 | 4757472.932 | -815352.8086 | -17.1384 | OK
|  |  | 7: 0; 8: 0; 10: Total | 12567325.914 |  | 12643176.6888
| SITALAKHYA 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Bholail Feeder (F-3) | E330V | 11 |  | DHK 9335 | 1 | 70399.8787 | 115853.9958 | 45454.1171 | 60 |  | 2727247.026 | 2733762.095 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 2733762.095 | 2632122.2753 | 101639.8196 | 3.8615 | OK
4 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 |  | DHK 9336 | 1 | 17372.339 | 34520.8952 | 17148.5562 | 60 |  | 1028913.372 | 1031371.3237 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1031371.3237 | 1296469.7835 | -265098.4598 | -20.4477 | OK
5 | 11 kV Baburail Feeder (F-5) | A730R | 11 |  | DHK 9322 | 1 | 84762.3796 | 111014.0086 | 26251.629 | 60 |  | 1575097.74 | 1578860.4613 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 1578860.4613 | 1983304.4857 | -404444.0244 | -20.3924 | OK
6 | 11 kV Goghchar Feeder (F-1) | E330G | 11 |  | DHK 9323 | 1 | 76884.4867 | 93927.0295 | 17042.5428 | 60 |  | 1022552.568 | 1024995.3245 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1024995.3245 | 1237157.8572 | -212162.5327 | -17.1492 | OK
7 | 11 kV Norshinghopur (F-2) | E330N | 11 |  | DHK 9365 | 1 | 66325.1503 | 92611.445 | 26286.2947 | 60 |  | 1577177.682 | 1580945.372 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1580945.372 | 1560990.7311 | 19954.6409 | 1.2783 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 |  | DHK 9367 | 1 | 15212.6093 | 27485.0632 | 12272.4539 | 60 |  | 736347.234 | 738106.28 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 738106.28 | 517148.8821 | 220957.3979 | 42.7261 | FAULT
11 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 |  | H/A030701125-03 | 1 | 73783.826 | 73961.68 | 177.854 | 1000 |  | 177854 | 178278.8721 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 178278.8721 | 227804.4627 | -49525.5907 | -21.7404 | OK
12 | 11 kV Kashipur Feeder (F-7) | E317K | 11 |  | H/A030800169-03 | 1 | 40041.956 | 41289.934 | 1247.978 | 1000 |  | 1247978 | 1250959.2711 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1250959.2711 | 1588658.98 | -337699.7089 | -21.2569 | OK
13 | 11 kV Spare Feeder (F-6) |  | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | A730D | 11 |  | H/A030701098-03 | 1 | 81538.063 | 82381 | 842.937 | 1000 |  | 842937 | 844950.6763 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 844950.6763 | 1070234.6333 | -225283.957 | -21.05 | OK
15 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 |  | H/A030800205-03 | 1 | 97166.397 | 98073.528 | 907.131 | 1000 |  | 907131 | 909298.0281 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 909298.0281 | 937852.0624 | -28554.0342 | -3.0446 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 |  | H/A030701091-03 | 1 | 56283.66 | 57053.47 | 769.81 | 1000 |  | 769810 | 771648.9846 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 771648.9846 | 1009051.2889 | -237402.3044 | -23.5273 | OK
|  |  | 10: Total | 12643176.6888 | 12613045.622 | 12643176.6888 | 0.23889
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 1087576.9002
[6 empty] | Sytalakhya | at 33 KV level |  | 9131788.651
[6 empty] | N.Gonj (West) | at 33 KV level |  | 2423811.1376
[6 empty] | Total = |  |  | 12643176.6888 | 0
MI CEMENT 132/33 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 350.233 | 375.928 | 25.695 | 480000 | 12333600 |  | 12340320
|  |  | 132 | DPDC | 16402670 | 1 | 1875.206 | 1900.898 | 25.692 | 480000 | 12332160
2 | 132/33 kV Transformer (132 kV Side) |  | 132 |  | 06502030 | 1 | 3731.122 | 3782.742 | 51.62 | 240000 |  | 12388800
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 12332160 | 12388800
[7 empty] | 0 | 0 |  | Net Total
[7 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) |  | 33 |  | 14718815 | 1 | 7363.831 | 7465.912 | 102.081 | 120000 | 12249720
4 | 33 kV Outgoing Feeder-1 |  | 33 |  | 11745824 | 1 | 3776.316 | 3816.137 | 39.821 | 120000 |  | 4778520
5 | 33 kV Outgoing Feeder-2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 7471200
|  |  | 9=8-7: Total Import/Export | 12249720 | 12249720
|  |  | 9=8-7: Net Total | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 12340320
[6 empty] | Total = |  |  | 12340320
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1692.0883 | 1729.3965 | 37.3082 | 180000 | 0 | 6715476 | 6713529.188
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1391.8606 | 1419.6294 | 27.7688 | 240000 | 0 | 6664512 | 6662579.9625
|  |  | 10: Total | 0 | 13379988 | 13376109.1505
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder |  | 33 |  | 00000188 | 1 | 335898624 | 342601120 | 6702496 | 1 | 6702496
7 | 33 kV Shitalakhya-1 Feeder |  | 33 |  | 00000153 | 1 | 334500032 | 341183872 | 6683840 | 1 | 6683840
|  |  | 7: 0; 8: 0; 10: Total | 13386336 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000116 | 1 | 340581376 | 347282176 | 6700800 | 1 |  | 6700800
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000194 | 1 | 329620544 | 336301184 | 6680640 | 1 |  | 6680640
|  |  | 10: Total |  | 13381440
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 13376109.1505; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 13376109.1505
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 13376109.1505 | 33 KV TX HV SIDE |  | 13381440
[11 empty] | LOSS UNITS=> |  | -5330.8495
[11 empty] | LOSS % IN => |  | -0.03985%
| TOTAL IMPORT |  | 4: 13376109.1505
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming |  | 11 |  | 00000055 | 1 | 328043776 | 334699168 | 6655392 | 1 | 6655392 |  | 6700538.6904
19 | 11 kV T-2 Incoming |  | 11 |  | 00000017 | 1 | 338026176 | 344656768 | 6630592 | 1 | 6630592 |  | 6675570.4602
|  |  | 7: 0; 8: 0; 10: Total | 13285984 |  | 13376109.1505
| MONDOLPARA 11 KV SIDE |  | 7: 0; 8: 0
9 | 11 kV River View | B793U | 11 |  | 00000061 | 1 | 8849520 | 9679440 | 829920 | 1 |  | 829920 | 834579.227 | N.Gonj (East) |  |  |  | 11 kV River View | 834579.227 | 838291.0284 | -3711.8013 | -0.44278 | OK
10 | 11 kV Railgate B.B. Road | B793F | 11 |  | 00000191 | 1 | 24783300 | 25321458 | 538158 | 1 |  | 538158 | 541179.2554 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 541179.2554 | 698256.3766 | -157077.1212 | -22.4956 | OK
11 | 11 kV DIT | A722D | 11 |  | 00000174 | 1 | 145783200 | 148263920 | 2480720 | 1 |  | 2480720 | 2494646.9299 | N.Gonj (West) |  |  |  | 11 kV DIT | 2494646.9299 | 3067765.2362 | -573118.3063 | -18.6819 | OK
12 | 11 kV Dalpatti | B7227 | 11 |  | 00000182 | 1 | 5882705 | 6596464 | 713759 | 1 |  | 713759 | 717766.0913 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 717766.0913 | 789288.224 | -71522.1327 | -9.0616 | OK
13 | 11 kV South Chasara | A793S | 11 |  | 00000043 | 1 | 102195272 | 104270584 | 2075312 | 1 |  | 2075312 | 2086962.942 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2086962.942 | 2534727.6524 | -447764.7104 | -17.6652 | OK
14 | 11 kV Spare |  | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | B7225 | 11 |  | 00000019 | 1 | 213639 | 237799 | 24160 | 1 |  | 24160 | 24295.6359 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 24295.6359 | 23419.6471 | 875.9888 | 3.7404 | OK
17 | 11 kV Spare |  | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | B7229 | 11 |  | 00000173 | 1 | 8565979 | 9690976 | 1124997 | 1 |  | 1124997 | 1131312.8093 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1131312.8093 | 1152492.2619 | -21179.4526 | -1.8377 | OK
20 | 11 kV Nitaigonj | B722G | 11 |  | 00000189 | 1 | 60384252 | 61101972 | 717720 | 1 |  | 717720 | 721749.3286 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 721749.3286 | 797467.0545 | -75717.7259 | -9.4948 | OK
21 | 11 kV Shahid Nagar | E323T | 11 |  | 00000020 | 1 | 60968412 | 62024488 | 1056076 | 1 |  | 1056076 | 1062004.8821 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1062004.8821 | 1271995.6228 | -209990.7407 | -16.5088 | OK
22 | 11 kV Bangla Bazar | A793Z | 11 |  | 00000139 | 1 | 74210456 | 75510416 | 1299960 | 1 |  | 1299960 | 1307258.0634 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1307258.0634 | 1631386.9501 | -324128.8867 | -19.8683 | OK
23 | 11 kV Vogoban Gonj | B7228 | 11 |  | 00000181 | 1 | 3768630 | 4220269 | 451639 | 1 |  | 451639 | 454174.5319 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 454174.5319 | 474606.7675 | -20432.2356 | -4.3051 | OK
24 | 11 kV Tanbazar | B722I | 11 |  | 00000138 | 1 | 51622392 | 52421992 | 799600 | 1 |  | 799600 | 804089.0085 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 804089.0085 | 976523.0891 | -172434.0806 | -17.658 | OK
25 | 11 kV SS Road | A793O | 11 |  | 00000175 | 1 | 69392152 | 70578344 | 1186192 | 1 |  | 1186192 | 1192851.3622 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1192851.3622 | 1337205.7052 | -144354.3431 | -10.7952 | OK
26 | 11 kV Spare |  | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 |  | 0.415 |  |  | 1 | 2640.91 | 2673.12 | 32.21 | 100 |  | 3221 | 3239.0829 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 3239.0829 | 4162.6017 | -923.5187 | -22.1861 | OK
28 | 33/0.415 kV Auxiliary-2 |  | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 13376109.1505 | 13301434 | 13376109.1505 | 0.56141
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 1062004.8821
[6 empty] | N.Gonj (East) | at 33 KV level |  | 5229145.888
[6 empty] | N.Gonj (West) | at 33 KV level |  | 7084958.3804
[6 empty] | Total = |  |  | 13376109.1505 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 52115.953 | 63140.766 | 11024.813 | 1000 | 0 | 11024813 | 11021616.9142
0 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9914.297 | 9975.444 | 61.147 | 180000 | 0 | 11006460 | 11003269.2347
| MATUAIL 33 KV SIDE |  | 10: Total |  | 11024813 | 11021616.9142
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 82417.915 | 88663.917 | 6246.002 | 1000 | 0 | 6246002 | 6259426.6391
0 | 0 |  | 33 | P. Cell | 08993580 | 1.5 | 1413.422 | 1436.51 | 23.088 | 180000 | 0 | 6233760 | 6247158.3271
|  |  | 10: Total | 0 | 6246002 | 6259426.6391
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) |  | 10: Total |  | 17270815 | 17281043.5532
3 | 33 kV Matuail Feeder |  | 33 | Digital | ABB03910 | 1 | 85490.813 | 86520.8375 | 1030.0245 | 4000 | 4120097.84
6 | 33 kV Shitalakhya Feeder |  | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  |  | 33 | New | DHKA2199 | 1 | 4318.7162 | 4377.8099 | 59.0937 | 180000 | 10636866
|  |  | 7: 0; 8: 0; 10: Total | 14756963.84 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 20/28 MVA Transformer-3 |  | 33 | Old | HA021100524-02 | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 33 | New | DHKA2200 | 1 | 4379.5301 | 4411.5177 | 31.9876 | 180000 |  | 5757768
7 | 33/11 kV, 10/14 MVA Transformer-2 |  | 33 | Old | HA030800199-03 | 1 | 55897.14 | 61346.715 | 5449.575 | 1000 |  | 5449575
|  |  | 33 | New | DHKA2195 | 1 | 4648.3212 | 4704.6652 | 56.344 | 90000 |  | 5070960
8 | 33/11 kV, 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03909 | 1 | 441660.8969 | 447034.8626 | 5373.9657 | 1000 |  | 5373965.73
|  |  | 10: Total |  | 16581308.73
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 11021616.9142; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 17281043.5532
| MATUAIL 33 KV SIDE |  | 4: 6259426.6391; 6: 33 KV NET IMPORT; 9=8-7: 17281043.5532 | 33 KV TX HV SIDE |  | 16581308.73
[11 empty] | LOSS UNITS=> |  | 699734.8232
[11 empty] | LOSS % IN => |  | 4.049%
| TOTAL IMPORT |  | 4: 17281043.5532
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | 51426632 | 1 | 3910814 | 3970994 | 60180 | 90 | 5416200 |  | 5445590.0896
16 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | DHKA2192 | 1 | 4029.6985 | 4090.3268 | 60.6283 | 90000 | 5456547 |  | 5486156.0257
22 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426630 | 1 | 4218029 | 4288196 | 70167 | 90 | 6315030 |  | 6349297.4379
|  |  | 7: 0; 8: 0; 10: Total | 17187777 |  | 17281043.5532
| NARAYANGONJ BSCIC 11 KV SIDE |  | 7: 0; 8: 0
10 | 11 kV Masdair Feeder (F-8) | A727M | 11 |  | XA575914 | 1 | 222435 | 225307.3 | 2872.3 | 1000 |  | 2872300 | 2875854.6768 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 2875854.6768 | 3291294.4584 | -415439.7816 | -12.6224 | OK
11 | 11 kV Narayangonj (F-7) | A727N | 11 |  | XA575915 | 1 | 169847.6 | 171294.6 | 1447 | 1000 |  | 1447000 | 1448790.766 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1448790.766 | 1519105.835 | -70315.0689 | -4.6287 | OK
12 | 11 kV Nearest Feeder (F-6) | A727B | 11 |  | XA575927 | 1 | 108569.7 | 109777.2 | 1207.5 | 1000 |  | 1207500 | 1208994.3676 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 1208994.3676 | 1130497.3656 | 78497.0021 | 6.9436 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 |  | XA575916 | 1 | 120037.9 | 121288 | 1250.1 | 1000 |  | 1250100 | 1251647.0882 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1251647.0882 | 1407639.7693 | -155992.6811 | -11.0819 | OK
14 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 |  | XA575912 | 1 | 57538.4 | 58701.7 | 1163.3 | 1000 |  | 1163300 | 1164739.667 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 1164739.667 | 905839.439 | 258900.228 | 28.5812 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 |  | DHK66615 | 1 | 246.1468 | 262.4459 | 16.2991 | 60000 |  | 977948.46 | 979158.7412 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 979158.7412 | 1098396.235 | -119237.4938 | -10.8556 | OK
17 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 |  | XA575920 | 1 | 234533.8 | 235307.8 | 774 | 1000 |  | 774000 | 774957.8804 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 774957.8804 | 1276885.4045 | -501927.5241 | -39.3087 | OK
18 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 |  | XA575929 | 1 | 23731.9 | 24939.8 | 1207.9 | 1000 |  | 1207900 | 1209394.8627 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1209394.8627 | 1314142.277 | -104747.4144 | -7.9708 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 |  | HA021100913-02 | 1 | 44435.628 | 46643.437 | 2207.809 | 1000 |  | 2207809 | 2210541.3216 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 2210541.3216 | 2452393.5389 | -241852.2173 | -9.8619 | OK
20 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 |  | HA021100682-02 | 1 | 66687.61 | 69020.842 | 2333.232 | 1000 |  | 2333232 | 2336119.5415 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2336119.5415 | 2520803.045 | -184683.5034 | -7.3264 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 |  | HA021100455-02 | 1 | 59670.325 | 61478.231 | 1807.906 | 1000 |  | 1807906 | 1810143.413 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1810143.413 | 1837185.1157 | -27041.7027 | -1.4719 | OK
23 | 11/0.415 KV Transformer,AT-1 |  | 0.415 | Analog | 2001123043161 | 1 | 3995.5 | 4048.1 | 52.6 | 160 |  | 8416 | 8426.4154 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 8426.4154 | 10606.5342 | -2180.1188 | -20.5545 | OK
24 | 11/0.415 KV Transformer,AT-2 |  | 0.415 | Analog | 2001123043118 | 1 | 4108.1 | 4122.3 | 14.2 | 160 |  | 2272 | 2274.8118 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 2274.8118 | 292.37 | 1982.4418 | 678.0592 | FAULT
|  |  | 10: Grand Total | 17281043.5532 | 17259683.46 | 17281043.5532 | 0.12376
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 774957.8804
[6 empty] | N.Gonj (West) | at 33 KV level |  | 16506085.6729
[6 empty] | Total = |  |  | 17281043.5532 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) |  | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  |  | IMPORT | 42627811 | 1 | 296.146 | 306.632 | 10.486 | 960000 | 0 | 10066560
| Madonganj to Charsyedpur-2 |  |  |  | 42627824 | 1 | 220.999 | 237.944 | 16.945 | 960000 | 0 | 16267200
|  |  | 9=8-7: Total Import/Export | 0 | 26333760 | 0
|  |  | 10: Net Total | 26333760
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 |  | 132 |  | 041808902821 | 1 | 244.39 | 252.73 | 8.34 | 1200000 | 10008000
|  |  | 132 |  | 041808904222 | 3 | 80.89 | 83.66 | 2.77 | 1200000 | 9972000
| 132 kV Madanganj Circuit-2 |  | 132 |  | 041808902865 | 1 | 176.79 | 190.32 | 13.53 | 1200000 | 16236000
|  |  | 132 |  | 041808904240 | 1 | 176.85 | 190.39 | 13.54 | 1200000 | 16248000
|  |  | 9=8-7: Total Import/Export | 26244000 | 0 | 0
|  |  | 9=8-7: Net Total | 26244000
CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Shah Cement |  | 132 | EXPORT | 042003953369 | 1 | 21.5 | 33.07 | 11.57 | 1200000 |  | 13884000 |  | Sytalakhya | Main Meter
| 133 kV Shah Cement |  | 132 |  | 042003953379 | 1 | 21.52 | 33.1 | 11.58 | 1200000 |  | 13896000 |  |  | Check Meter
|  |  | 10: Total |  | 13884000
CHAR SYEDPUR 132 KV SIDE
4 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | EXPORT | 041808902864 | 1 | 194.68 | 203.03 | 8.35 | 1200000 | 10020000 | 10020000
|  |  | 132 |  | 041808904224 | 1 | 194.55 | 202.89 | 8.34 | 1200000 | 10008000 | 10008000
7 | 132/33 kV, 80/120 MVA GT-2 |  | 132 |  | 041808902848 | 1 | 204.95 | 206.93 | 1.98 | 1200000 | 2376000 | 2376000
|  |  | 132 |  | 041808904244 | 1 | 205.05 | 207.03 | 1.98 | 1200000 | 2376000 | 2376000
|  |  | 10: Total |  | 12396000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 26333760; 6: Sytalakhya NOCS; 9=8-7: 13884000 | 132 KV NET IMPORT |  | 12396000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 12396000 | 132/33 KV LV SIDE |  | 12268800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 127200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.026%
| 132 KV TOTAL IMPORT |  | 4: 26333760
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902859 | 1 | 322.37 | 336.17 | 13.8 | 720000 | 9936000 |  | 10039014.0845
|  |  | 33 | Backup | 041808904285 | 1 | 322.37 | 336.17 | 13.8 | 720000 | 9936000 |  | 10039014.0845
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902812 | 1 | 339.93 | 343.17 | 3.24 | 720000 | 2332800 |  | 2356985.9155
|  |  | 33 | Backup | 041808904276 | 1 | 339.96 | 343.19 | 3.23 | 720000 | 2325600 |  | 2349711.2676
|  |  | 7: 0; 8: 0; 10: Total | 12268800 |  | 12396000
| CHAR SYEDPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902875 | 1 | 241.33 | 250.91 | 9.58 | 240000 |  | 2299200 | 2301420.1682 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2301420.1682 | 2390867.2743 | -89447.1061 | -3.7412 | OK
|  |  | 33 | Backup | 041808904241 | 1 | 241.25 | 250.83 | 9.58 | 240000 |  | 2299200 | 2301420.1682 |  |  |  |  | 0 | 2301420.1682 | 2388464.3926 | -87044.2244 | -3.6444 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902844 | 3 | 69.51 | 72.62 | 3.11 | 240000 |  | 2239200 | 2241362.2306 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 2241362.2306 | 2400478.801 | -159116.5704 | -6.6285 | OK
|  |  | 33 | Backup | 041808904259 | 3 | 69.51 | 72.62 | 3.11 | 240000 |  | 2239200 | 2241362.2306 |  |  |  |  | 0 | 2241362.2306 | 2400478.801 | -159116.5704 | -6.6285 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 4538400 | 4542782.3988 |  |  |  |  | 33 KV Feeders | 4542782.3988 | 4791346.0753 | -248563.6765 | -5.1878 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) |  | 33 | Main | 041808902866 | 1 | 361.28 | 375.17 | 13.89 | 360000 |  | 5000400 | 5005228.5182 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 5005228.5182 | 6404881.1253 | -1399652.6071 | -21.8529 | OK
|  |  | 33 | Backup | 041808904221 | 1 | 361.46 | 375.35 | 13.89 | 360000 |  | 5000400 | 5005228.5182 |  |  |  |  | 0 | 5005228.5182 | 6412089.7703 | -1406861.2521 | -21.9408 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) |  | 33 | Main | 041808902876 | 1 | 122.98 | 130.36 | 7.38 | 360000 |  | 2656800 | 2659365.4762 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2659365.4762 | 2937522.8571 | -278157.3809 | -9.4691 | OK
|  |  | 33 | Backup | 041808904237 | 1 | 122.98 | 130.36 | 7.38 | 360000 |  | 2656800 | 2659365.4762 |  |  |  |  | 0 | 2659365.4762 | 2937522.8571 | -278157.3809 | -9.4691 | OK
11 | 33 kV Outgoing Feeder-3 (=H3) |  | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) |  | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 |  | 0 | 0 | Sytalakhya | Grid Has No Reading |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904232 | 1 | 43.8 | 43.8 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Outgoing Feeder-6 (=H12) |  | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) |  | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904242 | 1 | 499.7 | 499.7 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/0.415 kV Transformer AT-1 |  |  |  |  | 1 | 1916.44 | 1995.97 | 79.53 | 1 |  | 79.53 | 79.6068 | [5 empty] | 79.6068 | 101.9423
|  |  | 10: Total |  | 7657279.53 | 7664673.6012 |  |  |  |  | 0 | 7664673.6012 | 9342505.9247 | -1677832.3235 | -17.9591 | OK
|  |  | 9=8-7: Grand Total | 12207456 | 12195679.53 | 12207456 | 0.096563
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902756 | 1 | 230.6 | 239.75 | 9.15 | 250000 | 2287500 |  | 1677094.7899
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902778 | 1.72 | 146.48 | 155.57 | 9.09 | 250000 | 3908700 |  | 2865687.6089
|  |  | 7: 0; 8: 0; 10: Total | 6196200 |  | 4542782.3988
| CHAR SYEDPUR 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 |  | 041808902749 | 1 | 468.54 | 484.37 | 15.83 | 60000 |  | 949800 | 945964.8168 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 945964.8168 | 1302048.296 | -356083.4792 | -27.3479 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) |  | 11 |  | 041808902759 | 1 | 492.75 | 515.1 | 22.35 | 60000 |  | 1341000 | 1335585.1962 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1335585.1962 | 1070865.8478 | 264719.3483 | 24.7201 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) |  | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) |  | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) |  | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 |  | 041808902786 | 1 | 356.76 | 379.9 | 23.14 | 60000 |  | 1388400 | 1382793.8004 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1382793.8004 | 1588331.224 | -205537.4235 | -12.9405 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 |  | 041808902789 | 1 | 215.77 | 230.47 | 14.7 | 60000 |  | 882000 | 878438.5854 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 878438.5854 | 830100.7076 | 48337.8779 | 5.8231 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) |  | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) |  | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) |  | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) |  | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907976 | 1 | 1916.44 | 1995.97 | 79.53 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 4542782.3988 | 4561200 | 4542782.3988 | -0.40379
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 12207376.3932
[6 empty] | Total = |  |  | 12207376.3932 | 7664593.9944
33 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 38986 | 39708 | 722 | 6000 | 0 | 4332000 | 4332055.5563
FROM Kazla 33 KV SIDE
| 33 kV Amulia Feeder | 0 | 33 | Main | 41812909523 | 1 | 17.72 | 23.56 | 5.84 | 360000 | 0 | 2102400 | 2105541.5069
|  |  | 10: Total |  | 6434400 | 6437597.0631
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving |  | 33 |  |  | 1 | 1379.37 | 1403.57 | 24.2 | 180000 | 4356000
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 4356000 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AMULIA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transformer, T-1 |  | 33 |  | DHKA2194 | 1 | 398.8151 | 412.1093 | 13.2942 | 240000 |  | 3190608
4 | 33/11 kV Transformer, T-2 |  | 33 |  | DHKA2198 | 1 | 576.0084 | 589.4324 | 13.424 | 240000 |  | 3221760
|  |  | 10: Total |  | 6412368 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 4: 6437597.0631; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6437597.0631
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 6437597.0631 | 33 KV TX HV SIDE |  | 6412368
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 25229.0631
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3919%
| TOTAL IMPORT |  | 4: 6437597.0631
11 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | HA021100461-02 | 1 | 27840165 | 31065070 | 3224905 | 1 | 3224905 |  | 3235529.975
11 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | HA021100478-02 | 1 | 96259150 | 99450702 | 3191552 | 1 | 3191552 |  | 3202067.0881
|  |  | 7: 0; 8: 0; 10: Total | 6416457 |  | 6437597.0631
| AMULIA 11 KV SIDE |  | 7: 0; 8: 0
5 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 72083645 | 73017725 | 934080 | 1 |  | 934080 | 938316.3983 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 938316.3983 | 618877.1744 | 319439.2239 | 51.6159 | FAULT
6 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 18045139 | 19053674 | 1008535 | 1 |  | 1008535 | 1013109.0793 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1013109.0793 | 1328671.185 | -315562.1057 | -23.7502 | OK
8 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 2394570 | 2915432 | 520862 | 1 |  | 520862 | 523224.3018 | Demra |  |  |  | 11 kV Paity Feeder | 523224.3018 | 581908.8947 | -58684.5929 | -10.0848 | OK
9 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 71254185 | 73339160 | 2084975 | 1 |  | 2084975 | 2094431.1329 | Demra |  |  |  | 11 kV Bamuil Feeder | 2094431.1329 | 2508124.4895 | -413693.3566 | -16.4941 | OK
12 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 16052331 | 16625684 | 573353 | 1 |  | 573353 | 575953.3679 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 575953.3679 | 671288.426 | -95335.0581 | -14.2018 | OK
13 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra |  | 1 | 52158655 | 52278896 | 120241 | 1 |  | 120241 | 120786.3374 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 120786.3374 | 168139.8027 | -47353.4652 | -28.1632 | OK
14 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 15044850 | 16211336 | 1166486 | 1 |  | 1166486 | 1171776.4455 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1171776.4455 | 1342546.4505 | -170770.005 | -12.7199 | OK
15 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6437597.0631 | 6408532 | 6437597.0631 | 0.45149
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Mugdapara | at 33 KV level |  | 1514269.7663
[6 empty] | Demra | at 33 KV level |  | 4923327.2969
[6 empty] | Total = |  |  | 6437597.0631 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MOGBAZAR T&T 11 KV SIDE | [9 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder |  | 33 |  | 8993 841 | 1 | 39516.99 | 39602.522 | 85.532 | 36000 | 0 | 3079152 | 3079152 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 3079152 | 1948464 | 1130688 | 58.0297 | FAULT
13 | 33 kV Mondol Para (Premire cement) Feeder |  | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 3079152 | 3079152 | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 3079152
[6 empty] | Total = |  |  | 3079152 | 0
Note on H481: User: Meter was faulty and New meter is installed properly in 12.07.23
Note on I481: User: Meter was faulty and New meter is installed properly in 12.07.23

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 |  | 132 | IMPORT | 50147584 | 1 | 3318.886 | 3356.292 | 37.406 | 1920000 | 0 | 71819520
| Maniknagar-2 |  | 132 |  | 50147585 | 1 | 3311.084 | 3347.682 | 36.598 | 1920000 | 0 | 70268160
|  |  | 9=8-7: Total Import/Export | 0 | 142087680
|  |  | 10: Net Total | 142087680
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 142087680
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 |  | 132 | EXPORT | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | From Downstream | 15729600 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 |  | 132 |  | 06604334 | 1 | 9009.55 | 9042.13 | 32.58 | 480000 |  | 15638400
| 132kV Motijheel Circuit-1 |  | 132 |  | 06604332 | 1 | 1855.74 | 1864.13 | 8.39 | 1440000 |  | 12081600
| 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1 | 1651.74 | 1659.62 | 7.88 | 1440000 |  | 11347200
| 132 kV Kazla Circuit-1 |  | 132 |  | ABB03905 | 1 | 844535 | 870310 | 25775 | 1000 |  | 25775000
| 132 kV Kazla Circuit-2 |  | 132 |  | ABB03904 | 1.3 | 640950 | 660390 | 19440 | 1000 |  | 25272000 |  |  | R Phase PT Missing
| 132 KV Metro Rail -1 |  | 132 |  | 42627805 | 1 | 0.006 | 0.239 | 0.233 | 480000 |  | 111840 |  | Motijheel | KVARH Reading Shown Seperately
| 132 KV Metro Rail -2 |  | 132 |  | 42627793 | 1 | 0.002 | 2.303 | 2.301 | 480000 |  | 1104480 |  | Motijheel
|  |  | 7: 0; 8: 0; 10: Total |  | 107060120
| MANIKNAGAR 132 KV SIDE |  | 7: 0; 8: 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 16964000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) |  | 132 | Export | ABB03903 | 1 | 383445 | 401094 | 17649 | 1000 |  | 17649000 |  |  | 34613000
|  |  | 10: Total |  | 34613000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 4: 142087680; 6: EXPORT TO OTHER S/S; 9=8-7: 105843800 | 132 KV NET IMPORT |  | 35027560
| IMPORT-2 |  | 6: Motijheel NOCS; 9=8-7: 1216320 | 33 KV NET IMPORT |  | 34311000
| IMPORT-3 |  | 6: 132 KV NET IMPORT; 9=8-7: 35027560 | LOSS UNITS=>(132 HV-33 LV) |  | 716560
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.046%
| 132 KV TOTAL IMPORT |  | 4: 142087680
KVARH For Metro Rail
|  | Previous | 3: Present; 4: Total KVARH; 5: Remark
| 132 KV Metro Rail -1 | 0 | 3: 3.517; 4: 1688160; 5: Leading PF
| 132 KV Metro Rail -2 | 0 | 3: 6.57; 4: 3153600; 5: Leading PF
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) |  | 33 | Digital | ABB03907 | 1 | 122312 | 139276 | 16964 | 1000 | 16964000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) |  | 33 | Digital | ABB03906 | 1 | 290989 | 308336 | 17347 | 1000 | 17347000
|  |  | 7: 0; 8: 0; 10: Total | 34311000
| Maniknagar 33 kV SIDE |  | 7: 0; 8: 0 |  |  |  |  | 4126429.8988
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 9213804.9175 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK00121 | 1 | 10495.1 | 11269.2 | 774.1 | 4444 | From Downstream | 3440100.4 | 3428826.2363 |  |  |  |  | 0 | 3428826.2363 | 3968474.087 | -539647.8508 | -13.5984 | OK | 4161360.0577
7 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Digital | ABB03913 | 1 | 392918 | 395820 | 2902 | 2000 |  | 5804000 | 5784978.6812 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 5784978.6812 | 6918315.0595 | -1133336.3783 | -16.3817 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 9244100.4 | 9213804.9175 |  |  |  |  | 33 KV Feeders | 9213804.9175 | 10886789.1465 | -1672984.2291 | -15.3671 | OK
2 |  |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 7304881.1607 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder |  | 33 |  | DHK86054 | 1 | 2516.03 | 2529.5 | 13.47 | 270000 |  | 3636900 | 3624980.8693 |  |  |  |  | 33kV Motijheel-1 Feeder | 3624980.8693 | 6348200.2173 | -2723219.348 | -42.8975 | CHECK
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 7118816 | 7095485.6643 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 7095485.6643 | 9089523.9553 | -1994038.2911 | -21.9378 | OK
|  |  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 13628006.3873 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 | Digital | ABB03918 | 1 | 311588 | 314865 | 3277 | 2000 |  | 6554000 | 6532520.7231 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 6532520.7231 | 9258480.7096 | -2725959.9865 | -29.4428 | OK
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 278536 | 280390 | 1854 | 2000 |  | 3708000 | 3695847.8549 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 3695847.8549 | 5916531.8189 | -2220683.964 | -37.5335 | OK
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 290204 | 292050 | 1846 | 2000 |  | 3692000 | 3679900.2914 |  | 3695847.8549 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 3679900.2914 | 6469516.1677 | -2789615.8764 | -43.1194 | CHECK
12 | 33kV Water Treatment Plant |  | 33 | Digital | 80379618 | 1 | 21815 | 22050 | 235 | 2000 |  | 470000 | 468459.6796 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 468459.6796 | 526937.9846 | -58478.305 | -11.0978 | OK
|  |  | 10: Total |  | 25179716 | 25097195.0825 |  |  |  |  | 0 | 25097195.0825 | 37609190.8535 | -12511995.7709 | -33.2685 | OK
|  |  | 9=8-7: Grand Total | 34311000 | 34423816.4 | 34311000 | -0.32773
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 468459.6796
[6 empty] | Total = |  |  | 468459.6796 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 |  | 11 | Import | 6604357 | 1 | 5561.26 | 5597.97 | 36.71 | 160000 | 5873600 |  | 5810601.8273
9 | 11kV 10/14 MVA Transformer T-1 |  | 11 | Import | DHK00121 | 1 | 10495.1 | 11269.2 | 774.1 | 4444 | 3440100.4 |  | 3403203.0902
|  |  | 7: 0; 8: 0; 10: Total | 9313700.4 |  | 9213804.9175
| MANIKNAGAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nearest Feeder | B2110N | 11 |  | HA021101060-02 | 1 | 80316933 | 81633988 | 1317055 | 1 |  | 1317055 | 1313766.3455 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1313766.3455 | 1615577.819 | -301811.4735 | -18.6813 | OK
2 | 11kV Spare |  | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | B2110C | 11 |  | HA021100937-02 | 1 | 79831670 | 80522134 | 690464 | 1 |  | 690464 | 688739.9281 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 688739.9281 | 831311.9243 | -142571.9962 | -17.1502 | OK
4 | 11 kV R K Mission Road Feeder | B2110R | 11 |  | HA021101035-02 | 1 | 18813697 | 20022438 | 1208741 | 1 |  | 1208741 | 1205722.8029 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1205722.8029 | 1505793.7255 | -300070.9226 | -19.9278 | OK
5 | 11 kV Janapath Feeder | B2110J | 11 |  | HA021100864-02 | 1 | 33876168 | 35472819 | 1596651 | 1 |  | 1596651 | 1592664.201 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 1592664.201 | 2018970.5577 | -426306.3566 | -21.115 | OK
6 | 11 kV Dhalpur Feeder | B2110D | 11 |  | HA021100851-02 | 1 | 88732684 | 89539002 | 806318 | 1 |  | 806318 | 804304.6434 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 804304.6434 | 844139.0145 | -39834.371 | -4.7189 | OK
7 | 11kV WTP | B2110O | 11 |  | X0599387 | 1 | 2253.4 | 2506.6 | 253.2 | 1000 |  | 253200 | 252567.7657 | Maniknagar |  |  |  | 11kV WTP | 252567.7657 | 0 | 252567.7657 | #DIV/0! | #DIV/0!
10 | 11kV Kamalapur Water pumping | B2110F | 11 |  | HA021100474-02 | 1 | 7657094 | 7681209 | 24115 | 1 |  | 24115 | 24054.7854 | Maniknagar | 8 |  |  | 11kV Kamalapur Water pumping | 24054.7854 | 97542.6949 | -73487.9094 | -75.3392 | CHECK
11 | 11 kV Wasa Road Feeder | B2110A | 11 |  | HA021001011-02 | 1 | 26301986 | 28031254 | 1729268 | 1 |  | 1729268 | 1724950.0596 | Maniknagar | 170 |  |  | 11 kV Wasa Road Feeder | 1724950.0596 | 2072782.2659 | -347832.2063 | -16.7809 | OK
12 | 11kV Sutikhalpar Feeder | B2110K | 11 |  | HA021101047-02 | 1 | 80885566 | 82588606 | 1703040 | 1 |  | 1703040 | 1698787.5503 | Maniknagar | 155 |  |  | 11kV Sutikhalpar Feeder | 1698787.5503 | 1889889.713 | -191102.1627 | -10.1118 | OK
13 | 11kV Spare |  | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare |  | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare |  | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 |  | 0.415 |  | AH14044078 | 1 | 420573.6 | 424443.4 | 3869.8 | 1 |  | 3869.8 | 3860.1372 | Maniknagar |  |  |  | Axuxilary -1 | 3860.1372 | 5837.95 | -1977.8128 | -33.8785 | OK
| Axuxilary -2 |  | 0.415 |  | AH14044072 | 1 | 388432.8 | 392725.7 | 4292.9 | 1 |  | 4292.9 | 4282.1807 | Maniknagar |  |  |  | Axuxilary -2 | 4282.1807 | 4943.482 | -661.3012 | -13.3772 | OK
13 | AT-1 |  | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 9313700.4 | 9337014.7 | 9313700.4 | -0.2497
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 9313700.4
[6 empty] | Total = |  |  | 9313700.4 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder |  | 33 | 0 | DHK86054 | 1 | 2516.03 | 2529.5 | 13.47 | 270000 | 0 | 3636900 | 3624980.8693
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 290204 | 292050 | 1846 | 2000 | 0 | 3692000 | 3679900.2914
|  |  | 10: Total | 0 | 7328900 | 7304881.1607
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 |  | 33 | Import | DHK86054 | 1 | 2516.03 | 2529.5 | 13.47 | 270000 | 3636900
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) |  | 33 | Import | DHK68120 | 1 | 2193.32 | 2207.29 | 13.97 | 270000 | 3771900 |  |  |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 7408800 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33kV Biddyut Bhaban Circuit |  | 33 | Export |  | 1 | 503691 | 503691 | 0 | 600 | Estimated | 1159836.3 |  |  | From remote end
|  |  | 7: 0; 8: 0; 10: Total |  | 1159836.3
[7 empty] | 0 | 0
| Motijheel 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK86053 | 1 | 3039.65 | 3060.96 | 21.31 | 180000 |  | 3835800
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) |  | 33 | Export | DHK86055 | 1 | 2374.62 | 2388.21 | 13.59 | 180000 |  | 2446200
|  |  | 10: Total |  | 6282000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 4: 7408800; 6: EXPORT TO OTHER S/S; 9=8-7: 1159836.3 | 33 KV NET IMPORT |  | 6248963.7
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 6248963.7 | 33 KV TX HV SIDE |  | 6282000
[11 empty] | LOSS UNITS=> |  | -33036.3
[11 empty] | LOSS % IN => |  | -0.5287%
| TOTAL IMPORT |  | 4: 7408800
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 |  | 11 | Import | DHK86059 | 1 | 3437.35 | 3461.47 | 24.12 | 160000 | 3859200 |  | 3821627.9017 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 |  | 11 | Import | DHK86057 | 1 | 2663.32 | 2678.64 | 15.32 | 160000 | 2451200 |  | 2427335.7983
|  |  | 7: 0; 8: 0; 10: Total | 6310400 |  | 6248963.7
| MOTIJHEEL 11 KV SIDE |  | 7: 0; 8: 0
6 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 |  | DHK86058 | 1 | 1749.51 | 1763.67 | 14.16 | 60000 |  | 849600 | 859250.5994 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 859250.5994 | 1078290.2684 | -219039.6689 | -20.3136 | OK
7 | 11kV Station Road Feeder | A175H | 11 |  | DHK86075 | 1 | 2381.38 | 2382.7 | 1.32 | 60000 |  | 79200 | 80099.6322 | Motijheel |  |  |  | 11kV Station Road Feeder | 80099.6322 | 97417.5285 | -17317.8963 | -17.777 | OK
8 | 11kV Box Culvert Road Feeder | A175F | 11 |  | DHK86071 | 1 | 3251.61 | 3279.86 | 28.25 | 60000 |  | 1695000 | 1714253.4911 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1714253.4911 | 1945915.1314 | -231661.6403 | -11.905 | OK
9 | 11kV Mohamedan Club Feeder | A174V | 11 |  | DHK86062 | 1 | 1722.37 | 1734.42 | 12.05 | 60000 |  | 723000 | 731212.5511 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 731212.5511 | 895632.4025 | -164419.8514 | -18.358 | OK
10 | 11kV Amina Ahmed Co. |  | 11 |  | DHK95754 | 1 | 119456 | 122809 | 3353 | 60 |  | 201180 | 203465.202 | Motijheel |  | 267 |  | 11kV Amina Ahmed Co. | 203465.202 | 231731.9459 | -28266.7439 | -12.198 | OK
11 | 11kV Bangabhaban -1 |  | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  | 16 |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | A175SB | 11 |  | DHK95753 | 1 | 84919 | 89291 | 4372 | 60 |  | 262320 | 265299.6907 | Motijheel |  | 251 |  | 11kV Sonali Bank | 265299.6907 | 525993.7678 | -260694.0771 | -49.5622 | CHECK
15 | 11kV NCC Bank Feeder | A133S | 11 |  | DHK68123 | 1 | 331.8 | 335.29 | 3.49 | 60000 |  | 209400 | 211778.5729 | Motijheel |  | 83.6667 |  | 11kV NCC Bank Feeder | 211778.5729 | 238064.0852 | -26285.5123 | -11.0414 | OK
16 | 11kV IFIC BANK Feeder |  | 11 |  | DHK68116 | 1 | 419.59 | 426.1 | 6.51 | 60000 |  | 390600 | 395036.8222 | Ramna |  | 99.6667 |  | 11kV IFIC BANK Feeder | 395036.8222 | 459080.103 | -64043.2808 | -13.9503 | OK
17 | 11kV Arambagh Feeder | A174X | 11 |  | DHK68117 | 1 | 3437.26 | 3445.31 | 8.05 | 60000 |  | 483000 | 488486.393 | Motijheel |  |  |  | 11kV Arambagh Feeder | 488486.393 | 1367498.5561 | -879012.163 | -64.2788 | CHECK
18 | 11kV Nikotborti Feeder | A175K | 11 |  | DHK68114 | 1 | 1439.72 | 1443.26 | 3.54 | 60000 |  | 212400 | 214812.6499 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 214812.6499 | 275204.518 | -60391.8681 | -21.9444 | OK
19 | 11kV Agrani Bank Feeder | A174O | 11 |  | DHK95756 | 1 | 378789 | 381960 | 3171 | 60 |  | 190260 | 192421.1618 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 192421.1618 | 232340.8054 | -39919.6436 | -17.1815 | OK
20 | 11kV Bangladesh Bank-2 | A133D | 11 |  | DHK95755 | 1 | 546 | 552 | 6 | 60000 | Estimated | 882819 | 892846.9338 | Motijheel | 75 |  |  | 11kV Bangladesh Bank-2 | 892846.9338 | 987430.8879 | -94583.9541 | -9.5788 | OK
21 | 11kV PDB Design Feeder 14 |  | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 |  | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT |  | 0.415 |  | ELIC5429 | 1 | 422280 | 422280 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6248963.7 | 6178779 | 6248963.7 | 1.1359
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 5853926.8778
[6 empty] | Ramna | at 33 KV level |  | 395036.8222
[6 empty] | Total = |  |  | 6248963.7 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 |  | 132 | 0 | 06604332 | 1 | 1855.74 | 1864.13 | 8.39 | 1440000 | 0 | 12081600
2 | 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1 | 1651.74 | 1659.62 | 7.88 | 1440000 | 0 | 11347200
|  |  | 9=8-7: Total Import/Export | 0 | 23428800
|  |  | 10: Net Total | 23428800
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 |  | 132 | Imp/Main | 41812909527 | 1 | 355.33 | 365.39 | 10.06 | 1200000 | 12072000
|  |  | 132 | Imp/Backup | 41812909575 | 1 | 355.42 | 365.48 | 10.06 | 1200000 | 12072000
5 | 132 kV Mniknagar Circuit-2 |  | 132 | Imp/Main | 41812909512 | 1 | 158.04 | 167.5 | 9.46 | 1200000 | 11352000
|  |  | 132 | Imp/Backup | 41812909591 | 1 | 158.07 | 167.54 | 9.47 | 1200000 | 11364000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 23424000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 23424000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1 | 40.51 | 41.84 | 1.33 | 1200000 |  | 1596000
|  |  | 132 | Exp/Backup | 41812909570 | 1 | 40.51 | 41.84 | 1.33 | 1200000 |  | 1596000
7 | 132 kV Bangabhaban Circuit-2 |  | 132 | Exp/Main | 41812909559 | 1 | 95.51 | 97.87 | 2.36 | 1200000 |  | 2832000
|  |  | 132 | Exp/Backup | 41812909569 | 1 | 95.51 | 97.87 | 2.36 | 1200000 |  | 2832000
|  |  | 7: 0; 8: 0; 10: Total |  | 4428000
| MOTIJHEEL 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41812909509 | 1 | 243.3 | 251.99 | 8.69 | 1200000 |  | 10428000
|  |  | 132 | Exp/Backup | 41812909594 | 1 | 243.3 | 251.99 | 8.69 | 1200000 |  | 10428000
6 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41812909508 | 1 | 134.07 | 141.26 | 7.19 | 1200000 |  | 8628000
|  |  | 132 | Exp/Backup | 41812909592 | 1 | 134.03 | 141.22 | 7.19 | 1200000 |  | 8628000
|  |  | 10: Total |  | 19056000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 4: 23428800; 6: EXPORT TO OTHER S/S; 9=8-7: 4428000 | 132 KV NET IMPORT |  | 19000800
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 19000800 | 33 KV NET IMPORT |  | 18943200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 57600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3031%
| 132 KV TOTAL IMPORT |  | 4: 23428800
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41812909543 | 1 | 402.78 | 417.18 | 14.4 | 720000 | 10368000
|  |  | 33 | Backup | 41812909617 | 1 | 403.06 | 417.46 | 14.4 | 720000 | 10368000
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41812909468 | 1 | 220.99 | 232.9 | 11.91 | 720000 | 8575200
|  |  | 33 | Backup | 41812909600 | 1 | 220.94 | 232.86 | 11.92 | 720000 | 8582400
|  |  | 7: 0; 8: 0; 10: Total | 18943200 |  | 0
| MOTIJHEEL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) |  | 33 | Main | 41812909546 | 1 | 138.19 | 144.64 | 6.45 | 240000 |  | 1548000 | 1547607.8531 |  | 3970993.7935 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1547607.8531 | 2007905.5104 | -460297.6573 | -22.9243 | OK
|  |  | 33 | Backup | 41812909616 | 1 | 138.24 | 144.59 | 6.35 | 240000 |  | 1524000 | 1523613.9329 |  |  |  |  | 0 | 1523613.9329 | 2029495.8922 | -505881.9594 | -24.9265 | OK
17 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41812909482 | 1 | 232.67 | 242.77 | 10.1 | 240000 |  | 2424000 | 2423385.9405 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2423385.9405 | 2780361.3937 | -356975.4533 | -12.8392 | OK
|  |  | 33 | Backup | 42003953371 | 1 | 232.72 | 242.83 | 10.11 | 240000 |  | 2426400 | 2425785.3325 |  |  |  |  | 0 | 2425785.3325 | 2780361.3937 | -354576.0613 | -12.7529 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 3972000 | 3970993.7935 |  |  |  |  | 33 KV Feeders | 3970993.7935 | 4788266.9042 | -817273.1106 | -17.0682 | OK
10 | 33 kV Spare Feeder 1 |  | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 |  | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 459.45 | 475.22 | 15.77 | 360000 |  | 5677200 | 5675761.8239 |  | 9152480.8613 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 5675761.8239 | 4523184.9939 | 1152576.8301 | 25.4815 | OK
|  |  | 33 | Backup | 41812909610 | 1 | 459.63 | 475.4 | 15.77 | 360000 |  | 5677200 | 5675761.8239 |  |  |  |  | 0 | 5675761.8239 | 4526783.3908 | 1148978.4331 | 25.3818 | OK
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 278.65 | 287.38 | 8.73 | 360000 |  | 3142800 | 3142003.8505 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 3142003.8505 | 3897063.9207 | -755060.0702 | -19.3751 | OK
|  |  | 33 | Backup | 41812909595 | 1 | 278.66 | 287.5 | 8.84 | 360000 |  | 3182400 | 3181593.8189 |  | 5819725.3452 | Kamlapur Railway 33/11 kv ss |  | 0 | 3181593.8189 | 3861079.951 | -679486.1321 | -17.5983 | OK
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 113.56 | 121 | 7.44 | 360000 |  | 2678400 | 2677721.4946 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 2677721.4946 | 3907859.1117 | -1230137.617 | -31.4786 | OK
|  |  | 33 | Backup | 41621865733 | 1 | 113.58 | 121.02 | 7.44 | 360000 |  | 2678400 | 2677721.4946 |  |  |  |  | 0 | 2677721.4946 | 3907859.1117 | -1230137.617 | -31.4786 | OK
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 149.11 | 158.77 | 9.66 | 360000 |  | 3477600 | 3476719.0374 |  |  |  |  | 33 kV P & T - 2 Feeder | 3476719.0374 | 4433225.0696 | -956506.0322 | -21.5759 | OK
|  |  | 33 | Backup | 41812909598 | 1 | 149.07 | 158.73 | 9.66 | 360000 |  | 3477600 | 3476719.0374 |  |  |  |  | 0 | 3476719.0374 | 4433225.0696 | -956506.0322 | -21.5759 | OK
20 | 33 kV Spare Feeder 9 |  | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 |  | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) |  | 0.415 |  |  | 1 | 1382.5 | 1459.01 | 76.51 | 300 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 14976000 | 14972206.2065 |  |  |  |  | 0 | 14972206.2065 | 16761333.0958 | -1789126.8894 | -10.6741 | OK
|  |  | 9=8-7: Grand Total | 18943200 | 18948000 | 18943200 | -0.025332
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) |  | 11 |  | 41812909493 | 1 | 131.66 | 137.81 | 6.15 | 250000 | 1537500 |  | 1544693.9804
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) |  | 11 |  | 41812909496 | 1 | 222.3 | 231.96 | 9.66 | 250000 | 2415000 |  | 2426299.8131
|  |  | 7: 0; 8: 0; 10: Total | 3952500 |  | 3970993.7935
| MOTIJHEEL 11 kV SIDE |  | 7: 0; 8: 0
2 | 11 kV Central Weman | A1111CW | 11 |  | 41812909492 | 1 | 179.49 | 188.77 | 9.28 | 60000 |  | 556800 | 559606.8157 | Motijheel |  |  |  | 11 kV Central Weman | 559606.8157 | 780631.0755 | -221024.2598 | -28.3135 | OK
3 | 11 kV Spare Feeder 2 |  | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len |  | 11 |  | 41812909499 | 1 | 297.27 | 308.53 | 11.26 | 60000 |  | 675600 | 679005.6837 | Swamibag |  |  |  | 11 kV K. M. Das Len | 679005.6837 | 845732.5401 | -166726.8565 | -19.7139 | OK
5 | 11 kV Gopibag | A1111GP | 11 |  | 41812909517 | 1 | 44.79 | 46.6 | 1.81 | 60000 |  | 108600 | 109147.45 | Motijheel |  |  |  | 11 kV Gopibag | 109147.45 | 151903.4174 | -42755.9674 | -28.1468 | OK
6 | 11kV SPICE TV | B1111E | 11 |  | 41812909518 | 1 | 26.14 | 29.4 | 3.26 | 60000 |  | 195600 | 196586.015 | Narinda |  |  |  | 11kV SPICE TV | 196586.015 | 229907.875 | -33321.86 | -14.4936 | OK
7 | 11 kV Spare Feeder 6 |  | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 |  | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 |  | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 |  | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 |  | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 |  | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | A1111SK | 11 |  | 41812909473 | 1 | 406.2 | 413.52 | 7.32 | 60000 |  | 439200 | 441413.9968 | Motijheel |  |  |  | 11 kV South Kamlapur | 441413.9968 | 616997.6645 | -175583.6677 | -28.4578 | OK
14 | 11 kV Spare Feeder 11 |  | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | A1111AC | 11 |  | 41812909514 | 1 | 215.83 | 225.49 | 9.66 | 60000 |  | 579600 | 582521.7499 | Motijheel |  |  |  | 11 kV Answer Camp | 582521.7499 | 703799.6173 | -121277.8674 | -17.2319 | OK
16 | 11 kV Shapla Chattar | A1111SC | 11 |  | 41812909516 | 1 | 194.83 | 210.07 | 15.24 | 60000 |  | 914400 | 919009.4688 | Motijheel |  |  |  | 11 kV Shapla Chattar | 919009.4688 | 1155990.8714 | -236981.4026 | -20.5003 | OK
17 | 11 kV Sayedabad |  | 11 |  | 41812909497 | 1 | 110.21 | 118.23 | 8.02 | 60000 |  | 481200 | 483625.7179 | Swamibag |  |  |  | 11 kV Sayedabad | 483625.7179 | 303220.3351 | 180405.3827 | 59.4965 | FAULT
22 | 33/0.4 kV Aux Transformer |  | 0.415 |  | 41901920686 | 1 | 1382.5 | 1459.01 | 76.51 | 1 |  | 76.51 | 76.8957 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 76.8957 | 83.5078 | -6.6121 | -7.9179 | OK
|  |  | 10: Total | 3970993.7935 | 3951076.51 | 3970993.7935 | 0.5041
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Motijheel | at 33 KV level |  | 2611776.377
[7 empty] | Swamibag | at 33 KV level |  | 1162631.4015
[7 empty] | Narinda | at 33 KV level |  | 196586.015
|  |  | 7: Total =; 10: 3970993.7935 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 459.45 | 475.22 | 15.77 | 360000 | 0 | 5677200 | 5675761.8239
0 | 0 |  | 33 | Backup | 41812909610 | 1 | 459.63 | 475.4 | 15.77 | 360000 | 0 | 5677200 | 5675761.8239
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 149.11 | 158.77 | 9.66 | 360000 | 0 | 3477600 | 3476719.0374
0 | 0 |  | 33 | Backup | 41812909598 | 1 | 149.07 | 158.73 | 9.66 | 360000 | 0 | 3477600 | 3476719.0374
|  |  | 10: Total | 0 | 9154800 | 9152480.8613
P&T 33 KV SIDE (Sending) | bar: 4
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 9152480.8613
P&T 33 KV SIDE (Receiving)
5 | 33 kV Bidyut Bhaban Circuit |  | 33 | Import | BD017079 | 1 | 15811 | 15811 | 0 | 1000 | 0
|  |  | 33 | Export | BD017079 | 1 | 144 | 1533 | 1389 | 1000 |  | 1389000
7 | 33 kV Motijheel Circuit-1 |  | 33 | Import | BD017081 | 1 | 64921 | 70579 | 5658 | 1000 | 5658000
8 | 33 kV Motijheel Circuit-2 |  | 33 | Import | BD017082 | 1 | 21372.33 | 21372.33 | 0 | 1000 | 3477600
11 | 33 kV Kamlapur Circuit |  | 33 | Import | BD017085 | 1 | 12870 | 12870 | 0 | 1000 | 0
|  |  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 9135600 | 1389000 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | BD017080 | 1 | 59310 | 64013 | 4703 | 888.88 |  | 4180402.64
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | BD017084 | 1 | 19670 | 23588 | 3918 | 888.88 |  | 3482631.84
|  |  | 10: Total |  | 7663034.48
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Sending Side |  | 4: 9152480.8613; 6: EXPORT TO OTHER S/S; 9=8-7: 1389000 | 33 KV NET IMPORT |  | 7763480.8613
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 7763480.8613 | 33 KV TX HV SIDE |  | 7663034.48
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 100446.3813
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.294%
| TOTAL IMPORT |  | 4: 9152480.8613
11 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
P&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 |  | 11 | Import | BD014056 | 1 | 77488.94 | 77660 | 171.06 | 1000 | 4180402.64 |  | 7763480.8613 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | BD014057 | 1 | 101349 | 101349 | 0 | 1000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 4180402.64 |  | 7763480.8613
| P&T 11 KV SIDE |  | 7: 0; 8: 0
12 | Inner Circular Road Feeder | A161Z | 11 |  | BD014042 | 1 | 42241 | 43389 | 1148 | 1000 |  | 1148000 | 1167930.2881 | Motijheel |  |  |  | Inner Circular Road Feeder | 1167930.2881 | 717359.185 | 450571.1032 | 62.8097 | FAULT
13 | NSI New Building Expres Feeder | D361NS | 11 |  | BD013982 | 1 | 10797 | 11095 | 298 | 1000 |  | 298000 | 303173.5417 | Ramna |  |  |  | NSI New Building Expres Feeder | 303173.5417 | 408763.2027 | -105589.661 | -25.8315 | OK
14 | Police Hospital RMU Feeder | D661H | 11 |  | BD014044 | 1 | 3920 | 4037 | 117 | 1000 |  | 117000 | 119031.2227 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 119031.2227 | 160874.6268 | -41843.4041 | -26.0099 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder |  | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | D661J | 11 |  | BD014013 | 1 | 36961 | 38143 | 1182 | 1000 |  | 1182000 | 1202520.558 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1202520.558 | 1451918.8017 | -249398.2437 | -17.1771 | OK
17 | Nayapalton Overhead Feeder | D361N | 11 |  | BD014014 | 1 | 26556 | 27311 | 755 | 1000 |  | 755000 | 768107.463 | Ramna |  |  |  | Nayapalton Overhead Feeder | 768107.463 | 920728.9962 | -152621.5332 | -16.5762 | OK
18 | Masjid Gali Over Head Feeder | D361MG | 11 |  | BD014016 | 1 | 16316 | 16992 | 676 | 1000 |  | 676000 | 687735.9536 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 687735.9536 | 843832.9482 | -156096.9945 | -18.4986 | OK
19 | Spare Feeder (Feeder-8) |  | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) |  | 11 |  | BD013988 | 1 | 13.18 | 13.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | D361MW | 11 |  | BD014015 | 1 | 24754 | 25465 | 711 | 1000 |  | 711000 | 723343.5844 | Ramna |  |  |  | Mid Way Over Head Feeder | 723343.5844 | 925787.9468 | -202444.3624 | -21.8672 | OK
24 | Palton Thana Over Head Feeder | D661F | 11 |  | BD014033 | 1 | 26289 | 27288 | 999 | 1000 |  | 999000 | 1016343.5173 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1016343.5173 | 1303185.6562 | -286842.1389 | -22.0108 | OK
25 | Police Hospital (South) U/G Feeder 7 |  | 11 |  | BD014034 | 1 | 12743 | 12871 | 128 | 1000 |  | 128000 | 130222.1924 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 130222.1924 | 174027.8982 | -43805.7058 | -25.1717 | OK
26 | China Town Express Feeder | D361CT | 11 |  | BD013943 | 1 | 6925 | 7132 | 207 | 1000 |  | 207000 | 210593.7018 | Ramna |  |  |  | China Town Express Feeder | 210593.7018 | 268124.378 | -57530.6762 | -21.4567 | OK
27 | Fakirapul Bazar O/H Feeder | A161FB | 11 |  | BD014032 | 1 | 32179 | 33315 | 1136 | 1000 |  | 1136000 | 1155721.9576 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1155721.9576 | 1453942.382 | -298220.4244 | -20.5112 | OK
28 | PWD Ouarter (RMU) | A161PW | 11 |  | BD013937 | 1 | 2615 | 2737 | 122 | 1000 |  | 122000 | 124118.0271 | Motijheel |  |  |  | PWD Ouarter (RMU) | 124118.0271 | 149744.9357 | -25626.9085 | -17.1137 | OK
29 | Postal Quarter RMU | A161PO | 11 |  | BD013945 | 1 | 3209 | 3356 | 147 | 1000 |  | 147000 | 149552.0491 | Motijheel |  |  |  | Postal Quarter RMU | 149552.0491 | 176051.4784 | -26499.4293 | -15.0521 | OK
30 | 11/0.4 kV AT-1 |  | 0.415 |  | DHKH4409 | 1 | 1476 | 1497 | 21 | 100 |  | 2100 | 2136.4578 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 2136.4578 | 0 | 2136.4578 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV AT-2 |  | 0.415 |  | DHKH4411 | 1 | 578 | 607 | 29 | 100 |  | 2900 | 2950.3465 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 2950.3465 | 5666.0246 | -2715.678 | -47.9292 | CHECK
|  |  | 10: Grand Total | 7763480.8613 | 7631000 | 7763480.8613 | 1.7361
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 2597322.322
[6 empty] | Ramna | at 33 KV level |  | 2692954.2445
[6 empty] | Rajarbag | at 33 KV level |  | 2473204.2948
[6 empty] | Total = |  |  | 7763480.8613 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 278.65 | 287.38 | 8.73 | 360000 | 0 | 3142800 | 3142003.8505
0 | 0 |  | 33 | Backup | 41812909595 | 1 | 278.66 | 287.5 | 8.84 | 360000 | 0 | 3182400 | 3181593.8189
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 113.56 | 121 | 7.44 | 360000 | 0 | 2678400 | 2677721.4946
0 | 0 |  | 33 | Backup | 41621865733 | 1 | 113.58 | 121.02 | 7.44 | 360000 | 0 | 2678400 | 2677721.4946
|  |  | 10: Total | 0 | 5860800 | 5859315.3135
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 |  | 33 | Import | 101 | 1 | 370.9 | 382.5 | 11.6 | 270000 | 3132000
6 | 33 kV Motijheel Circuit-2 |  | 33 | Import | 113 | 1 | 151.1 | 161 | 9.9 | 270000 | 2673000
|  |  | 7: 0; 8: 0; 10: Total | 5805000 | 0 | 0
[7 empty] | 0 | 0
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0
[7 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  | 7: 0; 8: 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | 103 | 1 | 356.3 | 369.4 | 13.1 | 240000 |  | 3144000
4 | 33 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | 104 | 1 | 177.1 | 188.2 | 11.1 | 240000 |  | 2664000
|  |  | 10: Total |  | 5808000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Kamalapur Railway 33 KV SIDE (Sending) |  | 4: 5859315.3135; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5859315.3135
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 5859315.3135 | 33 KV TX HV SIDE |  | 5808000
[11 empty] | LOSS UNITS=> |  | 51315.3135
[11 empty] | LOSS % IN => |  | 0.8758%
| TOTAL IMPORT |  | 4: 5859315.3135
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | 42 | 1 | 424.4 | 439.9 | 15.5 | 200000 | 3100000 |  | 3164438.5839
10 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | 64 | 1 | 210 | 223.2 | 13.2 | 200000 | 2640000 |  | 2694876.7295
|  |  | 7: 0; 8: 0; 10: Total | 5740000 |  | 5859315.3135
| KAMALAPUR RAILWAY 11 KV SIDE |  | 7: 0; 8: 0
1 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 452 | 469.4 | 17.4 | 40000 |  | 696000 | 698504.7602 | Rajarbag |  |  |  | Amtola O/H Feeder | 698504.7602 | 873041.3399 | -174536.5797 | -19.9918 | OK
2 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 78.6 | 81.8 | 3.2 | 40000 |  | 128000 | 128460.6456 | Rajarbag |  |  |  | Police Telecom | 128460.6456 | 186790.2402 | -58329.5946 | -31.2273 | OK
3 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 324.1 | 339.9 | 15.8 | 40000 |  | 632000 | 634274.4374 | Rajarbag |  |  |  | Railway Colony O/H | 634274.4374 | 775585.5625 | -141311.125 | -18.2199 | OK
4 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 768.6 | 792.7 | 24.1 | 40000 |  | 964000 | 967469.2368 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 967469.2368 | 1218197.2185 | -250727.9817 | -20.5819 | OK
5 | 11 KV Majar Feeder |  | 11 |  | 96 | 1 | 71.1 | 78.2 | 7.1 | 40000 |  | 284000 | 285022.0573 | Motijheel |  |  |  | 11 KV Majar Feeder | 285022.0573 | 369519.8229 | -84497.7656 | -22.8669 | OK
7 | 11 kV Feeder-6 |  | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 355.6 | 364.4 | 8.8 | 40000 |  | 352000 | 353266.7753 | Rajarbag |  |  |  | Momenbagh O/H | 353266.7753 | 495400.2022 | -142133.4269 | -28.6906 | OK
9 | 11 kV Feeder-8 |  | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 232.7 | 239.1 | 6.4 | 40000 |  | 256000 | 256921.2911 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 256921.2911 | 345155.8786 | -88234.5875 | -25.5637 | OK
12 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 363.8 | 379.3 | 15.5 | 40000 |  | 620000 | 622231.2519 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 622231.2519 | 1344077.5978 | -721846.3459 | -53.7057 | CHECK
13 | 11 kV Feeder-11 |  | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway |  | 11 | Motijheel | 150 | 1 | 71.8 | 74.6 | 2.8 | 40000 |  | 112000 | 112403.0649 | Motijheel |  |  |  | Dhaka Railway | 112403.0649 | 101516.4349 | 10886.63 | 10.724 | OK
15 | Jasimuddin Feeder-13 |  | 11 |  | 91 | 1 | 270.1 | 299.6 | 29.5 | 40000 |  | 1180000 | 1184246.5762 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1184246.5762 | 1445594.0326 | -261347.4565 | -18.0789 | OK
16 | Police Box Feeder-14 |  | 11 |  | 18 | 1 | 115.6 | 127.9 | 12.3 | 40000 |  | 492000 | 493770.6063 | Motijheel |  |  |  | Police Box Feeder-14 | 493770.6063 | 605037.9519 | -111267.3455 | -18.3901 | OK
17 | 11 kV Feeder-15 |  | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 |  | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) |  | 0.415 |  | DHKF 7632 | 1 | 1018.7 | 1052.87 | 34.17 | 100 |  | 3417 | 3429.2971 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 3429.2971 | 7083.8168 | -3654.5197 | -51.5897 | CHECK
20 | Auxiliary -1 (AT-2 ) |  | 0.415 |  | DHKF 7733 | 1 | 156.6 | 156.6 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 1938.9639 | -1938.9639 | -100 | CHECK
|  |  | 10: Grand Total | 5740000 | 5719417 | 5740000 | 0.35988
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Rajarbag | at 33 KV level |  | 3664557.6953
[6 empty] | Motijheel | at 33 KV level |  | 2075442.3047
[6 empty] | Total = |  |  | 5740000 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1 | 40.51 | 41.84 | 1.33 | 1200000 | 0 | 1596000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 |  | 132 |  | 41812909559 | 1 | 95.51 | 97.87 | 2.36 | 1200000 | 0 | 2832000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
|  |  | 10: Total | 0 | 4428000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
|  |  | 10: Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
BANGABHABAN 33 KV SIDE
|  |  | 3: 132; 4: NET IMPORT |  | 0
|  |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 4: 4428000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 4428000
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4428000 | 33 KV TX HV SIDE |  | 4428000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 4428000
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) |  | 11 | Import | 4150744 | 1 | 1527376.9 | 1530266.6 | 2889.7 | 1000 | 2889700 |  | 2939825.7553
12 | 11 kV 28/35 MVA Transformer (GT-1) |  | 11 | Import | 4150742 | 1 | 1444716.2 | 1446179 | 1462.8 | 1000 | 1462800 |  | 1488174.2447
|  |  | 7: 0; 8: 0; 10: Total | 4352500 |  | 4428000
| BANGABHABAN 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV DIT S/S-1 Feeder |  | 11 | Motijheel | 4150750 | 1 | 218543.72 | 219429.19 | 885.47 | 1000 | Estimated | 729797.04 | 734566.8339 | Motijheel | 62 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 734566.8339 | 730932.291 | 3634.543 | 0.49725 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 |  | 11 | Motijheel | 4150743 | 1 | 24310.71 | 24348.79 | 38.08 | 1000 |  | 38080 | 38328.8826 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 38328.8826 | 45380.4829 | -7051.6004 | -15.5388 | OK
3 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder |  | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation |  | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder |  | 11 | Ramna | 4150754 | 1 | 33902.7 | 33904.2 | 1.5 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 670942.44 | 675327.5731 | Motijheel | 57 | Meter Bad |  | 11 kV Modhumita via Ovisar | 675327.5731 | 670021.2667 | 5306.3064 | 0.79196 | OK
8 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16026.75 | 16090.3 | 63.55 | 1000 |  | 63550 | 63965.3489 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 63965.3489 | 73704.4745 | -9739.1255 | -13.2138 | OK
9 | 11 kV Motijheel-1 Feeder |  | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 250080.37 | 251097.91 | 1017.54 | 1000 |  | 1017540 | 1024190.419 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1024190.419 | 1159901.5065 | -135711.0875 | -11.7002 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 |  | 11 | Motijheel | 4150737 | 1 | 14984.45 | 15124.38 | 139.93 | 1000 |  | 139930 | 140844.5519 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 140844.5519 | 163473.9003 | -22629.3484 | -13.8428 | OK
14 | 11 kV Motijheel-2 Feeder |  | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 236957.0432 | 243644.097 | -6687.0538 | -2.7446 | OK
16 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 164831.63 | 165136.78 | 305.15 | 1000 |  | 305150 | 307144.3937 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 307144.3937 | 367060.1011 | -59915.7074 | -16.3231 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20763.9 | 20803.97 | 40.07 | 1000 | Estimated | 176563.8 | 177717.7824 | Motijheel | 15 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 177717.7824 | 182733.0727 | -5015.2903 | -2.7446 | OK
18 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82552.02 | 186.07 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | 20 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 236957.0432 | 243644.097 | -6687.0538 | -2.7446 | OK
19 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 123820.22 | 124061.84 | 241.62 | 1000 |  | 241620 | 243199.1755 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 243199.1755 | 300166.2046 | -56967.0291 | -18.9785 | OK
20 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273191.92 | 273251.62 | 59.7 | 1000 |  | 59700 | 60090.1862 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 60090.1862 | 0 | 60090.1862 | #DIV/0! | #DIV/0!
21 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 81979.59 | 82213.59 | 234 | 1000 |  | 234000 | 235529.3729 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 235529.3729 | 274686.6308 | -39157.258 | -14.2552 | OK
22 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192879.03 | 192985.49 | 106.46 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | 20 | Meter Bad |  | 11 kV BCIC Feeder | 236957.0432 | 243644.097 | -6687.0538 | -2.7446 | OK
23 | 11/0.4 kV AT-1 |  | 0.415 |  | 63412931 | 1 | 78910 | 90029 | 11119 | 1 |  | 11119 | 11191.6714 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 11191.6714 | 0 | 11191.6714 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV AT-2 |  | 0.415 |  | 63403117 | 1 | 22885.4 | 22902 | 16.6 | 1 | Estimated | 5000 | 5032.6789 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5032.6789 | 5007.7779 | 24.9011 | 0.49725 | OK
|  |  | 10: Grand Total | 4428000 | 4399247.48 | 4428000 | 0.65358
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 0
[6 empty] | Ramna | at 33 KV level |  | 0
[6 empty] | Swamibag | at 33 KV level |  | 0
[6 empty] | Motijheel | at 33 KV level |  | 4428000
[6 empty] | Total = |  |  | 4428000 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
0 | 132 kV Narinda Circuit-1 | 0 | 132 | EXPORT | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | From Downstream | 15729600 | 0 | 0 | Wrong Reading by Grid
0 | 132 kV Narinda Circuit-2 | 0 | 132 |  |  | 1 | 9009.55 | 9042.13 | 32.58 | 480000 | 0 | 15638400 | 0 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 31368000
|  |  | 10: Net Total | 31368000
NARINDA 132 KV SIDE (RECEIVING)
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 31368000
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 31368000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 4: 31368000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 31368000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 31368000 | 33 KV NET IMPORT |  | 31348800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 19200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.06121%
| 132 KV TOTAL IMPORT |  | 4: 31368000
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming |  | 33 | Import | 06604301 | 1 | 9375.73 | 9408.5 | 32.77 | 480000 | 15729600
7 | 132/33 kV 50/75 MVA GT-2 Incoming |  | 33 | Import | 06604304 | 1 | 9199.63 | 9232.17 | 32.54 | 480000 | 15619200
|  |  | 7: 0; 8: 0; 10: Total | 31348800 |  | 0
| NARINDA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 |  | 33 | Export | 06604300 | 1 | 9862.03 | 9897.59 | 35.56 | 180000 |  | 6400800 | 6415094.3661 |  | 13277585.6396 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 6415094.3661 | 8741872.5494 | -2326778.1834 | -26.6165 | OK
8 | 33 kV 20/28 MVA Transformer T-4 |  | 33 | Export | 06604303 | 1 | 9999.55 | 10037.59 | 38.04 | 180000 |  | 6847200 | 6862491.2735 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 6862491.2735 | 8729252.8118 | -1866761.5383 | -21.3851 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 13248000 | 13277585.6396 |  |  |  |  | 33 KV Feeders | 13277585.6396 | 17471125.3612 | -4193539.7217 | -24.0027 | OK
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1123200 | 1125708.3477 |  | 1125708.3477 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1125708.3477 | 1651382.812 | -525674.4643 | -31.8324 | OK
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 7078492.5761 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5750.32 | 5773.32 | 23 | 180000 |  | 4140000 | 4149245.5124 |  |  |  |  | 33 kV Kumertully-1 Feeder | 4149245.5124 | 4748626.9943 | -599381.4819 | -12.6222 | OK
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5649.5 | 5680.43 | 30.93 | 180000 |  | 5567400 | 5579833.2042 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 5579833.2042 | 6400009.8062 | -820176.602 | -12.8152 | OK
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder |  | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 7062720 | 7078492.5761 |  | 9729078.7166 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 7078492.5761 | 8693968.6263 | -1615476.0502 | -18.5816 | OK
|  |  | 10: Total |  | 17893320 | 17933279.6404 |  |  |  |  | 0 | 17933279.6404 | 21493988.2388 | -3560708.5983 | -16.5661 | OK
|  |  | 9=8-7: Grand Total | 31210865.28 | 31141320 | 31210865.28 | 0.22332
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 | Import | 06604351 | 1 | 11090.85 | 11130.34 | 39.49 | 160000 | 6318400 |  | 6433519.7166
9 | 33/11 kV 20/28 MVA T-4 Incoming |  | 11 | Import | 06604295 | 1 | 11430.91 | 11472.92 | 42.01 | 160000 | 6721600 |  | 6844065.9229
|  |  | 7: 0; 8: 0; 10: Total | 13040000 |  | 13277585.6396
| NARINDA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bonogram Feeder | B124B | 11 |  | 06604467 | 1 | 25159.72 | 25262.79 | 103.07 | 8000 |  | 824560 | 833343.2066 | Narinda |  |  |  | 11 kV Bonogram Feeder | 833343.2066 | 1081937.7982 | -248594.5916 | -22.9768 | OK
2 | 11 kV Sha Saheb Len Feeder | B524H | 11 |  | 06604469 | 1 | 16969.66 | 17038.74 | 69.08 | 8000 |  | 552640 | 558526.7169 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 558526.7169 | 661053.8831 | -102527.1662 | -15.5097 | OK
3 | 11 kV Sadiabad Water Treatment | B224W | 11 |  | 06604354 | 1 | 530.01 | 538.25 | 8.24 | 40000 |  | 329600 | 333110.8966 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 333110.8966 | 795173.7239 | -462062.8273 | -58.1084 | CHECK
4 | 11 kV Manashi Feeder | B124M | 11 |  | 06604353 | 1 | 5614.2 | 5635.85 | 21.65 | 40000 |  | 866000 | 875224.6252 | Narinda |  |  |  | 11 kV Manashi Feeder | 875224.6252 | 1137753.6547 | -262529.0296 | -23.0743 | OK
5 | 11 kV Jatrabari Feeder | B524E | 11 |  | 06604324 | 1 | 3581.5 | 3617.32 | 35.82 | 40000 |  | 1432800 | 1448062.1743 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 1448062.1743 | 2046581.4052 | -598519.2309 | -29.2448 | OK
6 | 11 kV Wari Feeder | B124W | 11 |  | 06604291 | 1 | 8679.86 | 8709.16 | 29.3 | 40000 |  | 1172000 | 1184484.1348 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1184484.1348 | 1567697.5349 | -383213.4002 | -24.4443 | OK
7 | 11 kV Narinda Feeder | B124N | 11 |  | 06604348 | 1 | 7414.52 | 7442.6 | 28.08 | 40000 |  | 1123200 | 1135164.3175 | Narinda |  |  |  | 11 kV Narinda Feeder | 1135164.3175 | 1444336.4028 | -309172.0852 | -21.4058 | OK
10 | 11 kV Distillary Feeder | B524D | 11 |  | 06604347 | 1 | 6095.73 | 6121.16 | 25.43 | 40000 |  | 1017200 | 1028035.2064 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1028035.2064 | 1274866.5196 | -246831.3133 | -19.3613 | OK
11 | 11 kV Thatari Bazar Feeder | B124T | 11 |  | 06604296 | 1 | 5110.49 | 5129.92 | 19.43 | 40000 |  | 777200 | 785478.7283 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 785478.7283 | 1002663.1035 | -217184.3752 | -21.6608 | OK
12 | 11 kV Swamibagh Feeder | B524C | 11 |  | 06604352 | 1 | 7894.28 | 7918.91 | 24.63 | 40000 |  | 985200 | 995694.3426 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 995694.3426 | 1313290.4788 | -317596.1362 | -24.1832 | OK
13 | 11 kV Tipu Sultan Feeder | B124S | 11 |  | 06604322 | 1 | 6459.68 | 6482.22 | 22.54 | 40000 |  | 901600 | 911203.8361 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 911203.8361 | 1115103.7419 | -203899.9059 | -18.2853 | OK
14 | 11 kV Spare |  | 11 |  | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | B124F | 11 |  | DHK00089 | 1 | 41171.3 | 43986.5 | 2815.2 | 444.44 |  | 1251187.488 | 1264515.1272 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1264515.1272 | 1585927.4386 | -321412.3113 | -20.2665 | OK
16 | 11 kV Bhajohari Feeder | B124V | 11 |  | DHK27842 | 1 | 424175 | 431839 | 7664 | 80 |  | 613120 | 619650.9494 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 619650.9494 | 785385.7258 | -165734.7764 | -21.1023 | OK
17 | 11 kV Lal mohon shaha Feeder | B124L | 11 |  | DHK00086 | 1 | 41548.8 | 43431.7 | 1882.9 | 444.44 |  | 836836.076 | 845750.0473 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 845750.0473 | 1056805.6006 | -211055.5533 | -19.9711 | OK
18 | 11 kV Dupkhola Feeder | B524A | 11 |  | 8838024/8838029 | 1 | 38567.6 | 39022.1 | 454.5 | 1000 |  | 454500 | 459341.3304 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 459341.3304 | 602548.3495 | -143207.0191 | -23.7669 | OK
1 | 11/0.4 kV Aux Transformer-1 |  | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 |  | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 13277585.6396 | 13137643.564 | 13277585.6396 | 1.0652
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Narinda | at 33 KV level |  | 8454814.9724
[6 empty] | Maniknagar | at 33 KV level |  | 333110.8966
[6 empty] | Swamibag | at 33 KV level |  | 4489659.7706
[6 empty] | Total = |  |  | 13277585.6396 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5750.32 | 5773.32 | 23 | 180000 | 0 | 4140000 | 4149245.5124
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5649.5 | 5680.43 | 30.93 | 180000 | 0 | 5567400 | 5579833.2042
| MITFORD 33 KV SIDE | [10 empty] | 9707400 | 9729078.7166 | bar: 4
1 | Kumartuly Circuit-1 |  | 33 | 0 | DHK-66493 | 1 | 1291902 | 1304145 | 12243 | 180 | 0 | 2343942 | 2343942
6 | Kumartuly Circuit-2 |  | 33 | 0 | DHK-60914 | 1.1 | 776528.4 | 786422.9 | 9894.5 | 180 | 0 | 1954260 | 1954260
|  |  | 10: Total |  | 4298202 | 4298202
| KUMERTULY 33 KV SIDE (RECEIVING) | [11 empty] | 14027280.7166
5 | 33 kV Mitford Circuit-1 |  | 33 | Import | DHK60965 | 1 | 286246.7 | 299268.6 | 13021.9 | 180 | 2343942
6 | 33 kV Narinda Circuit-1 |  | 33 | Import | DHK60959 | 1 | 1000840.4 | 1000840.4 | 0 | 540 | 0
9 | 33 kV Mitford Circuit-2 |  | 33 | Import | DHK86072 | 1 | 1777.6 | 1787.47 | 9.87 | 180000 | 1776600
10 | 33 kV Narinda Circuit-2 |  | 33 | Import | DHK60957 | 1 | 929717.4 | 940032.1 | 10314.7 | 540 | 5569938
|  |  | 7: 0; 8: 0; 10: Total | 9690480 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
|  |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 4120542
[7 empty] | 0 | 0
| KUMERTULY 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK60960 | 1 | 200236.7 | 222580.2 | 22343.5 | 180 |  | 4021830
8 | 33/11 kV 20/28 MVA Transformer (T-2) |  | 33 | Export | DHK60958 | 1 | 391638.5 | 418875.6 | 27237.1 | 180 |  | 4902678
|  |  | 10: Total |  | 8924508
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 9729078.7166; 6: EXPORT TO OTHER S/S; 9=8-7: 4298202 | 33 KV NET IMPORT |  | 8924508
| MITFORD 33 KV SIDE |  | 6: 33 KV NET IMPORT; 9=8-7: 8924508 | 33 KV TX HV SIDE |  | 9690480
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -765972
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -8.583%
| TOTAL IMPORT |  | 4: 9729078.7166
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 | Import | 06604403 | 1 | 7317.08 | 7342.08 | 25 | 160000 | 4021830 |  | 4025563.9446 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 | Import | 06604410 | 1 | 6774.74 | 6805.33 | 30.59 | 160000 | 4894400 |  | 4898944.0554
|  |  | 7: 0; 8: 0; 10: Total | 8916230 |  | 8924508
| KUMERTULY 11 KV SIDE |  | 7: 0; 8: 0
11 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63497.4 | 63748 | 250.6 | 2222.22 |  | 556888.332 | 559882.2686 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 559882.2686 | 648124.404 | -88242.1353 | -13.615 | OK
12 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4688.31 | 4714.17 | 25.86 | 40000 |  | 1034400 | 1039961.1294 | Banglabazar |  |  |  | 11kV Islampur Feeder | 1039961.1294 | 1308522.8246 | -268561.6952 | -20.524 | OK
13 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5181.29 | 5192.58 | 11.29 | 40000 |  | 451600 | 454027.8867 | Banglabazar |  | 120 |  | 11kV Majar O/H Feeder | 454027.8867 | 509541.8516 | -55513.9649 | -10.8949 | OK
15 | 11kV Spare |  | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  | 70 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5527.79 | 5552.12 | 24.33 | 40000 |  | 973200 | 978432.1066 | Banglabazar |  | 50 |  | 11kV Sadarghat Feeder | 978432.1066 | 1158159.6042 | -179727.4975 | -15.5184 | OK
17 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal |  | 16.6667 |  | 11kV Mitford Hospital Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4169.95 | 4194.33 | 24.38 | 40000 |  | 975200 | 980442.859 | Banglabazar |  | 86.6667 |  | 11kV Zindabahar Feeder | 980442.859 | 1163400.1454 | -182957.2863 | -15.7261 | OK
21 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 882819 | 887565.2014 | Banglabazar | 75 |  |  | 11kV Police fari Feeder | 887565.2014 | 1078713.9994 | -191148.798 | -17.7201 | OK
22 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 5983.44 | 6005.67 | 22.23 | 40000 |  | 889200 | 893980.5068 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 893980.5068 | 1075923.4193 | -181942.9124 | -16.9104 | OK
23 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8334.99 | 8373.78 | 38.79 | 40000 |  | 1551600 | 1559941.6941 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1559941.6941 | 1898688.3869 | -338746.6929 | -17.8411 | OK
24 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3791.32 | 3799.62 | 8.3 | 40000 |  | 332000 | 333784.8946 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 333784.8946 | 430127.4966 | -96342.602 | -22.3986 | OK
25 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7301.75 | 7326.5 | 24.75 | 40000 |  | 990000 | 995322.4266 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 995322.4266 | 1252086.2271 | -256763.8005 | -20.5069 | OK
26 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3606.94 | 3612.86 | 5.92 | 40000 |  | 236800 | 238073.0814 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 238073.0814 | 277345.5648 | -39272.4834 | -14.1601 | OK
27 | 11/0.4 kV AT-1 |  | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 |  | 0.415 |  | 05378636 | 1 | 176640.6 | 178179.3 | 1538.7 | 2 |  | 3077.4 | 3093.9447 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 3093.9447 | 5594.0762 | -2500.1315 | -44.6925 | CHECK
|  |  | 10: Grand Total | 8924508 | 8876784.732 | 8924508 | 0.53762
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 0
[6 empty] | Banglabazar | at 33 KV level |  | 8924508
[6 empty] | Total = |  |  | 8924508 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder |  | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 7062720 | 7078492.5761
|  |  | 10: Total | 0 | 7062720 | 7078492.5761
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 |  | 33 | Import | Mat-152447/1191738/007 | 1 | 126294600 | 128577100 | 2282500 | 1 | 2282500
5 | 33 kV Narinda Circuit-2 |  | 33 | Import | Mat-152447/1191738/002 | 1 | 254593400 | 259330000 | 4736600 | 1 | 4736600
|  |  | 7: 0; 8: 0; 10: Total | 7019100 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) |  | 33 | Export | Mat-152447/1191738/009 | 1 | 133504800 | 135799800 | 2295000 | 1 |  | 2295000 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) |  | 33 | Export | Mat-152447/1191738/004 | 1 | 252121300 | 256863000 | 4741700 | 1 |  | 4741700 |  |  | #VALUE!
|  |  | 10: Total |  | 7036700
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 7078492.5761; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7078492.5761
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 7078492.5761 | 33 KV TX HV SIDE |  | 7036700
[11 empty] | LOSS UNITS=> |  | 41792.5761
[11 empty] | LOSS % IN => |  | 0.5904%
| TOTAL IMPORT |  | 4: 7078492.5761
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 |  | 11 | Import | 340180016886 | 1 | 133533495 | 135833728 | 2300233 | 1 | 2300233 |  | 2305369.9161 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 |  | 11 | Import | 340180012685 | 1 | 255509124 | 260271611 | 4762487 | 1 | 4762487 |  | 4773122.66
|  |  | 7: 0; 8: 0; 10: Total | 7062720 |  | 7078492.5761
| BANGSHAL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 40639116 | 41256087 | 616971 | 1 |  | 616971 | 617669.4796 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 617669.4796 | 748100.1808 | -130430.7012 | -17.4349 | OK
2 | 11 kV Spare Feeder |  | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder |  | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 53863751 | 54945882 | 1082131 | 1 |  | 1082131 | 1083356.0922 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1083356.0922 | 1317991.7768 | -234635.6845 | -17.8025 | OK
5 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 22867036 | 23435352 | 568316 | 1 |  | 568316 | 568959.3967 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 568959.3967 | 737371.3191 | -168411.9224 | -22.8395 | OK
8 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 51129746 | 52356480 | 1226734 | 1 |  | 1226734 | 1228122.7989 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1228122.7989 | 1543005.6588 | -314882.86 | -20.4071 | OK
9 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 65782506 | 66698574 | 916068 | 1 |  | 916068 | 917105.0905 | Bangshal |  |  |  | 11 kV French Road Feeder | 917105.0905 | 1128071.6101 | -210966.5196 | -18.7015 | OK
10 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 32609799 | 33052156 | 442357 | 1 |  | 442357 | 442857.7972 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 442857.7972 | 505257.2343 | -62399.4371 | -12.35 | OK
11 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 67416873 | 68646258 | 1229385 | 1 |  | 1229385 | 1230776.8001 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1230776.8001 | 1482806.5471 | -252029.747 | -16.9968 | OK
12 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 54042708 | 55024234 | 981526 | 1 |  | 981526 | 982637.1962 | Narinda |  |  |  | 11 kV Suritolla Feeder | 982637.1962 | 1224359.1662 | -241721.97 | -19.7427 | OK
13 | AT-1 |  | 0.415 |  | DHK-4415 | 1 | 764.01 | 777.4 | 13.39 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 |  | 0.415 |  | DHK-4410 | 1 | 771.03 | 786.95 | 15.92 | 100 |  | 7000 | 7007.9248 | Bangshal |  |  |  | AT-2 | 7007.9248 | 7005.1331 | 2.7917 | 0.039852 | OK
|  |  | 10: Grand Total | 7078492.5761 | 7070488 | 7078492.5761 | 0.11321
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 5012499.2877
[6 empty] | Banglabazar | at 33 KV level |  | 1083356.0922
[6 empty] | Narinda | at 33 KV level |  | 982637.1962
[6 empty] | Total = |  |  | 7078492.5761 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING) Maniknagar 132
0 | 132 kV Kazla Circuit-1 | 0 | 132 | 0 | ABB03905 | 1 | 844535 | 870310 | 25775 | 1000 | 0 | 25775000
0 | 132 kV Kazla Circuit-2 | 0 | 132 |  |  | 1.3 | 640950 | 660390 | 19440 | 1000 | 0 | 25272000
|  |  | 9=8-7: Total Import/Export | 0 | 51047000
|  |  | 10: Net Total | 51047000
KAZLA 132 KV SIDE (RECEIVING)
3 | 132kV Maniknagar Circuit-1 |  | 132 | Main | 41812909505 | 1 | 705.51 | 727.64 | 22.13 | 1200000 | 26556000
|  |  | 132 | Backup | 41812909603 | 1 | 705.48 | 727.6 | 22.12 | 1200000 | 26544000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 |  | 132 | Main | 41812909540 | 1 | 533.06 | 553.18 | 20.12 | 1200000 | 24144000
|  |  | 132 | Backup | 41812909587 | 1 | 533.08 | 553.19 | 20.11 | 1200000 | 24132000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 50700000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 50700000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| KAZLA 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Main | 41812909542 | 1 | 706.4 | 728.45 | 22.05 | 1200000 |  | 26460000 |  |  | #DIV/0!
|  |  | 132 | Backup | 41812909589 | 1 | 706.81 | 728.87 | 22.06 | 1200000 |  | 26472000
7 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Main | 41812909501 | 1 | 532.43 | 552.58 | 20.15 | 1200000 |  | 24180000 |  |  | 100
|  |  | 132 | Backup | 41812909606 | 1 | 532.36 | 552.51 | 20.15 | 1200000 |  | 24180000
|  |  | 10: Total |  | 50640000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) Maniknagar 132 |  | 4: 51047000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 51047000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 51047000 | 33 KV NET IMPORT |  | 50558400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 488600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.9572%
| 132 KV TOTAL IMPORT |  | 4: 51047000
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) |  | 33 | Main | 41812909533 | 1 | 1172.62 | 1209.38 | 36.76 | 720000 | 26467200
|  |  | 33 | Backup | 41812909582 | 1 | 1172.72 | 1209.48 | 36.76 | 720000 | 26467200
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) |  | 33 | Main | 41812909479 | 1 | 884.52 | 917.98 | 33.46 | 720000 | 24091200
|  |  | 33 | Backup | 41812909622 | 1 | 884.39 | 917.85 | 33.46 | 720000 | 24091200
|  |  | 7: 0; 8: 0; 10: Total | 50558400 |  | 0
| KAZLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 |  | 33 | Main | 41812909465 | 1 | 1190.68 | 1231.81 | 41.13 | 240000 |  | 9871200 | 9885950.0203 |  | 31009867.2957 | Kazla 33/11 kv ss | 1.1659 | 33/11 kV 20/28 MVA T-1 | 9885950.0203 | 11627083.7597 | -1741133.7394 | -14.9748 | OK
|  |  | 33 | Backup | 41812909596 | 1 | 1190.366 | 1231.47 | 41.104 | 240000 |  | 9864960 | 9879700.6962 |  |  |  |  | 0 | 9879700.6962 | 11623728.18 | -1744027.4838 | -15.004 | OK
13 | 33/11 kV 28/35 MVA T-5 |  | 33 | Main | 41812909536 | 1 | 148.15 | 157.16 | 9.01 | 360000 |  | 3243600 | 3248446.7426 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 3248446.7426 | 3915242.4905 | -666795.7479 | -17.0308 | OK
|  |  | 33 | Backup | 41812909578 | 1 | 138.24 | 144.59 | 6.35 | 360000 |  | 2286000 | 2289415.8508 |  |  |  |  | 0 | 2289415.8508 | 3041593.3397 | -752177.4889 | -24.7297 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 | Main | 41812909554 | 1 | 1160.82 | 1187.47 | 26.65 | 240000 |  | 6396000 | 6405557.2099 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 6405557.2099 | 9297352.691 | -2891795.4811 | -31.1034 | OK
|  |  | 33 | Backup | 41812909613 | 1 | 1159.68 | 1186.29 | 26.61 | 240000 |  | 6386400 | 6395942.8651 |  |  |  |  | 0 | 6395942.8651 | 9287765.3203 | -2891822.4553 | -31.1358 | OK
17 | 33/11 kV 20/28 MVA T-3 |  | 33 | Main | 41812909544 | 1 | 1008.77 | 1039.39 | 30.62 | 240000 |  | 7348800 | 7359780.9293 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 7359780.9293 | 8477632.5001 | -1117851.5708 | -13.1859 | OK
|  |  | 33 | Backup | 41812909614 | 1 | 1008.8 | 1039.43 | 30.63 | 240000 |  | 7351200 | 7362184.5155 |  |  |  |  | 0 | 7362184.5155 | 8477632.5001 | -1115447.9846 | -13.1575 | OK
22 | 33/11 kV 10/14 MVA T-4 |  | 33 | Main | 41812909506 | 1 | 533.38 | 550.48 | 17.1 | 240000 |  | 4104000 | 4110132.3936 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 4110132.3936 | 4894352.7185 | -784220.3249 | -16.023 | OK
|  |  | 33 | Backup | 41812909602 | 1 | 533.54 | 550.62 | 17.08 | 240000 |  | 4099200 | 4105325.2212 |  |  |  |  | 0 | 4105325.2212 | 4896749.5612 | -791424.34 | -16.1622 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 30963600 | 31009867.2957 |  |  |  |  | 33 KV Feeders | 31009867.2957 | 38211664.1599 | -7201796.8642 | -18.8471 | OK
10 | 33 kV Shahriar Steel Feeder |  | 33 | Main | 41812909534 | 1 | 633.58 | 652.26 | 18.68 | 360000 |  | 6724800 | 6734848.5186 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 6734848.5186 | 7150980.086 | -416131.5674 | -5.8192 | OK
|  |  | 33 | Backup | 41812909580 | 1 | 633.52 | 652.2 | 18.68 | 360000 |  | 6724800 | 6734848.5186 |  |  |  |  | 0 | 6734848.5186 | 7150980.086 | -416131.5674 | -5.8192 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | A418S | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 |  | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 |  | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 |  | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Amulia Feeder |  | 33 | Main | 41812909523 | 1 | 17.72 | 23.56 | 5.84 | 360000 |  | 2102400 | 2105541.5069 |  |  |  |  | 33 kV Amulia Feeder | 2105541.5069 | 4612723.7056 | -2507182.1987 | -54.3536 | CHECK
|  |  | 33 | Backup | 41812909565 | 1 | 17.71 | 23.54 | 5.83 | 360000 |  | 2098800 | 2101936.1276 |  |  |  |  | 0 | 2101936.1276 | 4612723.7056 | -2510787.578 | -54.4318 | CHECK
21 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 721.82 | 751.24 | 29.42 | 360000 |  | 10591200 | 10607025.8788 | Kazla |  |  |  | 33 kV Zahir Steel | 10607025.8788 | 11059032.0485 | -452006.1697 | -4.0872 | OK
|  |  | 33 | Backup | 41812909563 | 1 | 722.09 | 751.52 | 29.43 | 360000 |  | 10594800 | 10610631.2581 |  |  |  |  | 0 | 10610631.2581 | 11066222.5765 | -455591.3184 | -4.117 | OK
| Auxiliary Transformer-3 (AT-3) |  | 0.415 |  |  | 1 | 2767.96 | 2874.18 | 106.22 | 160 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 19418400 | 19447415.9043 |  |  |  |  | 0 | 19447415.9043 | 22822735.8401 | -3375319.9358 | -14.7893 | OK
|  |  | 9=8-7: Grand Total | 50457283.2 | 50382000 | 50457283.2 | 0.14942
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | KAZLA at 33 KV level |  |  | 17341874.3974
[7 empty] | Kazla 33/11 KV Substation |  |  | 33115408.8026
|  |  | 9=8-7: Total =; 10: 50457283.2 | 0
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK-61009 | 1 | 8029363 | 8083027 | 53664 | 180 | 9659520 |  | 9885950.0203
30 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK-61124 | 1 | 963697.2 | 998043.7 | 34346.5 | 180 | 6182370 |  | 6405557.2099
24 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 |  | DHK-61015 | 1 | 579080.9 | 619717.8 | 40636.9 | 180 | 7314642 |  | 7359780.9293
39 | 33/11 kV 10/14 MVA T-4 Incoming |  | 11 |  | 8L55984 | 1 | 31703 | 32702.3 | 999.3 | 4000 | 3997200 |  | 4110132.3936
42 | 33/11 kv 28/35 MVA T-5 Incomer |  | 11 |  | DHK00112 | 1 | 18380.8 | 22038.3 | 3657.5 | 888.8 | 3250786 |  | 3248446.7426
|  |  | 7: 0; 8: 0; 10: Total | 30404518 |  | 31009867.2957
| KAZLA 11 kV SIDE |  | 7: 0; 8: 0
17 | 11 kV Nayanagor Feeder | A418N | 11 |  | DHK-61125 | 1 | 933689.8 | 957166.8 | 23477 | 60 |  | 1408620 | 1425042.8921 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1425042.8921 | 1775388.4538 | -350345.5617 | -19.7335 | OK
18 | 11 kV Madrasa Bazar Feeder | A418B | 11 |  | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1530219.6 | 1548060.2038 | Kazla | 130 |  |  | 11 kV Madrasa Bazar Feeder | 1548060.2038 | 1602675.9202 | -54615.7163 | -3.4078 | OK
19 | 11 kV Kazla Feeder | A418K | 11 |  | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2354184 | 2381631.0828 | Kazla | 200 |  |  | 11 kV Kazla Feeder | 2381631.0828 | 2712220.788 | -330589.7051 | -12.1889 | OK
20 | 11 kV Sayedabad Feeder | B218S | 11 |  | HA021101239-02 | 1 | 36964648 | 36964660 | 12 | 1000 | Estimated | 941673.6 | 952652.4331 | Maniknagar | 80 |  |  | 11 kV Sayedabad Feeder | 952652.4331 | 1232827.6309 | -280175.1978 | -22.7262 | OK
21 | 11 kV Zenith Feeder | old | 11 |  | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | B318P | 11 |  | HA-021200060 | 1 | 120971.5 | 122840.5 | 1869 | 1000 |  | 1869000 | 1890790.3944 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 1890790.3944 | 2010101.6778 | -119311.2834 | -5.9356 | OK
23 | 11 kV Matuail Feeder | A418M | 11 |  | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1471365 | 1488519.4268 | Kazla | 125 |  |  | 11 kV Matuail Feeder | 1488519.4268 | 1849241.4463 | -360722.0196 | -19.5065 | OK
25 | 11 kV Kutubkhali Feeder | B326C | 11 |  | DHK-61117 | 1 | 838596.4 | 873380.8 | 34784.4 | 60 |  | 2087064 | 2111396.7703 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2111396.7703 | 2432494.6655 | -321097.8952 | -13.2004 | OK
26 | 11 kV Mridhabari Feeder | A418R | 11 |  | DHK-61118 | 1 | 699957.1 | 722924.6 | 22967.5 | 60 |  | 1378050 | 1394116.481 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1394116.481 | 1532023.4409 | -137906.9599 | -9.0016 | OK
27 | 11 kV Muslim Nagar Feeder | A418U | 11 |  | DHK-61011 | 1 | 154325.8 | 192344.8 | 38019 | 60 |  | 2281140 | 2307735.4737 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2307735.4737 | 2627245.0572 | -319509.5835 | -12.1614 | OK
28 | 11 kV Jatrabari Thana Feeder | A418H | 11 |  | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | B518D | 11 |  | DHK-61008 | 1 | 348875.3 | 375123.8 | 26248.5 | 60 |  | 1574910 | 1593271.6426 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 1593271.6426 | 1997346.9786 | -404075.336 | -20.2306 | OK
31 | 11 kV Mukti Sharani Feeder | B318T | 11 |  | DHK-61014 | 1 | 213216.9 | 213219.9 | 3 | 60 |  | 180 | 182.0986 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 182.0986 | 1171257.2192 | -1171075.1206 | -99.9845 | CHECK
32 | 11 kV Kadamtali Feeder | B418K | 11 |  | DHK-61006 | 1 | 452013.2 | 485277.4 | 33264.2 | 60 |  | 1995852 | 2019121.3431 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 2019121.3431 | 2235311.7183 | -216190.3752 | -9.6716 | OK
33 | 11kV Rayerbagh Feeder | E218R | 11 |  | DHK-61012 | 1 | 448270.6 | 473065.1 | 24794.5 | 60 | 595068 | 1487670 | 1505014.5244 | Matuail | Export to Jurain |  |  | 11kV Rayerbagh Feeder | 1505014.5244 | 1463413.2136 | 41601.3107 | 2.8428 | OK
34 | 11 kV Donia Feeder | B318D | 11 |  | DHK-61013 | 1 | 2084796 | 2100163 | 15367 | 60 |  | 922020 | 932769.6947 | Jurain |  |  |  | 11 kV Donia Feeder | 932769.6947 | 2275838.0926 | -1343068.3979 | -59.0142 | CHECK
35 | 11 kV Nimtoli Feeder | A418T | 11 |  | HA-021100855-02 | 1 | 34003353 | 35425036 | 1421683 | 1 |  | 1421683 | 1438258.1917 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1438258.1917 | 1595582.0613 | -157323.8696 | -9.86 | OK
36 | 11 kV Gobindapur Feeder | A441G | 11 |  | HA-021101057-02 | 1 | 28747928 | 29299106 | 551178 | 1 |  | 551178 | 557604.1027 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 557604.1027 | 679496.8713 | -121892.7685 | -17.9387 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 |  | 9A56136 | 1 | 3801 | 3949.3 | 148.3 | 10000 |  | 1483000 | 1500290.0775 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1500290.0775 | 1773738.3704 | -273448.2929 | -15.4165 | OK
38 | 11 kV Samad Nagar Gate (Old) | old | 11 |  | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | A418D | 11 |  | 8K55676 | 1 | 814.2 | 820.6 | 6.4 | 4000 |  | 25600 | 25898.4666 | Kazla |  |  |  | 11 kV Dharmik Para | 25898.4666 | 0 | 25898.4666 | #DIV/0! | #DIV/0!
41 | 11 kV Sheikhdi Feeder | A418I | 11 |  | 9A56133 | 1 | 16766 | 17420.9 | 654.9 | 4000 |  | 2619600 | 2650141.5287 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 2650141.5287 | 3268543.7125 | -618402.1837 | -18.9198 | OK
43 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 |  | T-5 Sum | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | A418Z | 11 |  | 61903661 | 1 | 22659 | 23175.9 | 516.9 | 2000 | 3229000 | 1033800 | 1045852.9212 | Kazla | OMF Corrected |  |  | 11 kV Jenith Feeder | 1045852.9212 | 1210196.351 | -164343.4298 | -13.5799 | OK
45 | 11 KV Samad Nagor Gate | A418A | 11 |  | 61903675 | 1 | 19683 | 20299.2 | 616.2 | 2000 |  | 1232400 | 1246768.3692 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1246768.3692 | 1325742.7363 | -78974.3671 | -5.957 | OK
46 | 11 KV Bibir Bagicha | B218I | 11 |  | 61903557 | 1 | 38466 | 38947.4 | 481.4 | 2000 |  | 962800 | 974025.1427 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 974025.1427 | 1414936.4372 | -440911.2945 | -31.1612 | OK
47 | 33/0.4 kV AT-1 |  | 0.415 |  | 503043 | 1 | 96204 | 96207 | 3 | 10 |  | 30 | 30.3498 | Kazla |  |  |  | 33/0.4 kV AT-1 | 30.3498 | 0 | 30.3498 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 |  | 0.415 |  | 503044 | 1 | 95990 | 96336 | 346 | 10 |  | 3460 | 3500.3396 | Kazla |  |  |  | 33/0.4 kV AT-2 | 3500.3396 | 6121.9313 | -2621.5917 | -42.823 | CHECK
23 | Auxiliary Transformer |  | 0.415 |  | 41901920685 | 1 | 2767.96 | 2874.18 | 106.22 | 160 |  | 16995.2 | 17193.3445 | Kazla |  |  |  | Auxiliary Transformer | 17193.3445 | 19919.386 | -2726.0414 | -13.6854 | OK
|  |  | 10: Total | 31009867.2957 | 30652494.4 | 31009867.2957 | 1.1659
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 909946.5244
[6 empty] | Jurain | at 33 KV level |  | 5530206.958
[6 empty] | Swamibag | at 33 KV level |  | 1593271.6426
[6 empty] | Maniknagar | at 33 KV level |  | 1926677.5758
[6 empty] | Shyampur | at 33 KV level |  | 2019121.3431
[6 empty] | Kazla | at 33 KV level |  | 19030643.2518
[6 empty] | Total = |  |  | 31009867.2957 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT |  | 132 |  | 8993532 | 1 | 2229.915 | 2234.461 | 4.546 | 960000 | 0 | 4364160
|  |  | 132 |  |  | 1 | 667.19 | 667.558 | 0.368 | 960000 | 353280 | 0
1 | Tranformer - 1 at Shyampur 230/132 |  | 132 |  | 38992560 | 1 | 1553.392 | 1593.217 | 39.825 | 1920000 | 0 | 76464000
|  |  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 |  | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  |  | 132 |  | 38992559 | 1 | 1643.73 | 1683.807 | 40.077 | 1920000 | 0 | 76947840
| Aggrekko 100 MW (Brammhongao) |  | 132 |  | PN-1711A04601 | 1 | 0 | 6.982 | 6.982 | 960000 | 0 | 6702720
|  |  | 132 |  |  | 1 | 0 | 0.242 | 0.242 | 960000 | 232320 | 0
| Madanganj-Fatullah Exp |  | 132 |  | 38992544 | 1 | 33.497 | 33.859 | 0.362 | 960000 | 0 | 347520
| Madanganj-Fatullah Imp |  | 132 |  | 38992544 | 1 | 66.461 | 105.155 | 38.694 | 960000 | 37146240 | 0
|  |  | 9=8-7: Total Import/Export | 37731840 | 164826240
|  |  | 10: Net Total | 127094400
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) |  | 132 | Import | 08993727 | 1 | 9268.339 | 9332.709 | 64.37 | 720000 | 46346400
|  |  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) |  | 132 | Import | 08993726 | 1 | 6991.138 | 7051.441 | 60.303 | 720000 | 43418160
|  |  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 89764560 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 89764560
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 132 |  |  |  | 0 | 0
|  |  | 132 |  |  |  | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 37452000
| SHYAMPUR 132 KV SIDE |  | 7: 0; 8: 0
5 | 132 kV 80/120 MVA ( GT-1) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) |  | 132 | Export | ABB3902 | 1 | 2486388.1 | 2486388.1 | 0 | 1300 |  | 0
|  |  | 10: Total |  | 52312560
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 4: 127094400; 6: EXPORT TO OTHER S/S; 9=8-7: 37452000 | 132 KV NET IMPORT |  | 89642400
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 89642400 | 33 KV NET IMPORT |  | 89448432
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 193968
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2164%
| 132 KV TOTAL IMPORT |  | 4: 127094400
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) |  | 33 | Import | BD001826 | 1 | 3507.3328 | 3552.479 | 45.1462 | 480000 | 21670176
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) |  | 33 | Import | BD001850 | 1 | 3562.5122 | 3607.799 | 45.2868 | 480000 | 21737664
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) |  | 33 | Import | BD001835 | 1 | 3073.5188 | 3121.4169 | 47.8981 | 480000 | 22991088
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) |  | 33 | Import | BD001831 | 1 | 3956.8801 | 4004.8999 | 48.0198 | 480000 | 23049504
|  |  | 7: 0; 8: 0; 10: Total | 89448432
| SHYAMPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) |  | 33 | Export | BD001808 | 1 | 2208.0439 | 2242.62 | 34.5761 | 240000 |  | 8298264 | 8299487.545 |  | 26828491.1678 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 8299487.545 | 7438340.1673 | 861147.3777 | 11.5771 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) |  | 33 | Export | BD001834 | 1 | 2019.887 | 2054.427 | 34.54 | 240000 |  | 8289600 | 8290822.2675 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 8290822.2675 | 7404055.0259 | 886767.2416 | 11.9768 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) |  | 33 | Export | BD001846 | 1 | 1500.2162 | 1525.1669 | 24.9507 | 240000 |  | 5988168 | 5989050.9308 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 5989050.9308 | 6486633.5869 | -497582.6561 | -7.6709 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) |  | 33 | Export | BD001847 | 1 | 1340.1149 | 1357.817 | 17.7021 | 240000 |  | 4248504 | 4249130.4245 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 4249130.4245 | 4356516.2266 | -107385.8022 | -2.4649 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 26824536 | 26828491.1678 |  |  |  |  | 33 KV Feeders | 26828491.1678 | 25685545.0066 | 1142946.1612 | 4.4498 | OK
1 | 33 kV Rani RRM Feeder |  | 33 | Export | BD001809 | 1 | 760.393 | 772.98 | 12.587 | 240000 |  | 3020880 | 3021325.4164 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 3021325.4164 | 2543674.3806 | 477651.0358 | 18.778 | OK
2 | 33 kV Postogola Feeder-1. |  | 33 | Export | BD001804 | 1 | 1564.544 | 1564.544 | 0 | 240000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv s/s | Grid Has No Reading | 33 kV Postogola Feeder-1. | 0 | 479.848 | -479.848 | -100 | CHECK
5 | 33 kV Prime Textile Feeder. |  | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1366.304 | 1392.002 | 25.698 | 240000 | From Downstream | 6167520 | 6168429.3755 |  | 11324749.5417 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 6168429.3755 | 6982268.6119 | -813839.2364 | -11.6558 | OK
7 | 33 kV Nondolalpur -2 feeder |  | 33 | Export | BD001807 | 1 | 1180.8005 | 1202.282 | 21.4815 | 240000 |  | 5155560 | 5156320.1662 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 5156320.1662 | 5791885.6239 | -635565.4577 | -10.9734 | OK
8 | 33 kV Postogola Feeder-2. |  | 33 | Export | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Postogola Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Rahima Steel feeder |  | 33 | Export | BD001803 | 1 | 656.416 | 665.824 | 9.408 | 240000 |  | 2257920 | 2258252.921 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2258252.921 | 387957.1282 | 1870295.7928 | 482.0883 | FAULT
12 | 33 kV Salam Steel Feeder |  | 33 | Export | BD001849 | 1 | 1251.608 | 1293.7049 | 42.0969 | 240000 |  | 10103256 | 10104745.6836 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 10104745.6836 | 9425654.7552 | 679090.9284 | 7.2047 | OK
13 | 33 kV Fatullah Feeder-2. |  | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 210535.038 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2644.437 | 2679.862 | 35.425 | 240000 |  | 8672040 | 8673318.6567 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8673318.6567 | 8679817.373 | -6498.7163 | -0.074872 | OK
17 | 33 kV Akhter Steel Feeder |  | 33 | Export | BD001828 | 1 | 690.9784 | 691.8555 | 0.8771 | 240000 | Prime Textile | 210504 | 210535.038 | Fatullah | 18087458.5284 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 210535.038 | 1073036.1535 | -862501.1156 | -80.3795 | CHECK
18 | 33 kV Steel Famus feeder |  | 33 | Export | BD001806 | 1 | 153.6104 | 161.8755 | 8.2651 | 240000 |  | 1983624 | 1983916.4772 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1983916.4772 | 1855188.4343 | 128728.0429 | 6.9388 | OK
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.8992 | 1544.899 | -0.0002 | 240000 |  | -48 | -48.0071 |  | -48.0071 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | -48.0071 | 767.7568 | -815.7639 | -106.2529 | CHECK
20 | 33 kV Rani Kamal Steel Feeder |  | 33 | Export | BD001829 | 1 | 1593.2569 | 1618.8289 | 25.572 | 240000 |  | 6137280 | 6138184.9168 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 6138184.9168 | 5684015.7878 | 454169.1289 | 7.9903 | OK
23 | 33 kV Shyampur BSCIC-2. |  | 33 | Export | BD001827 | 1 | 2590.3112 | 2629.531 | 39.2198 | 240000 |  | 9412752 | 9414139.8717 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 9414139.8717 | 10883960.888 | -1469821.0164 | -13.5045 | OK
24 | 33 kV Chakda Steel Feeder |  | 33 | Export | BD001832 | 1 | 2477.8933 | 2517.3479 | 39.4546 | 240000 |  | 9469104 | 9470500.1805 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 9470500.1805 | 8724428.8439 | 746071.3367 | 8.5515 | OK
23 | Aux Tr-1 |  | 0.44kv | Export | DHKG9742 | 1.025 | 349.667 | 351.425 | 1.758 | 2400 |  | 4324.68 | 4324.68 | Fatullah
24 | Aux Tr-2 |  | 0.44kv | Export | DHKG9743 | 1.025 | 117.946 | 124.447 | 6.501 | 2400 |  | 15992.46 | 15992.46 | Fatullah
|  |  | 10: Total |  | 62610709.14 | 62619937.8365 |  |  |  |  | 0 | 62619937.8365 | 62057934.8452 | 562002.9914 | 0.90561 | OK
|  |  | 9=8-7: Grand Total | 89448432 | 89435245.14 | 89448429.0043 | 0.014741
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 32976925.5956
[6 empty] | Fatullah | at 33 KV level |  | 230852.178
[7 empty] | Export to Other SS |  | 56240651.2308
[6 empty] | Total = |  |  | 89448429.0043 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | BD001926 | 1 | 3001.13 | 3053.08 | 51.95 | 160000 | 8312000 |  | 8310913.0362 |  | 8312000
16 | 11 kV 20/28 MVA Transformer-2 |  | 11 |  | BD001952 | 1 | 3012.88 | 3064.67 | 51.79 | 160000 | 8286400 |  | 8285316.3839
27 | 11 kV20/28 MVA Transformer-3 |  | 11 |  | BD001927 | 1 | 2114.71 | 2152.17 | 37.46 | 160000 | 5993600 |  | 5992816.2143 |  | 1888144
36 | 11 kV 20/28 MVA Transformer-4 |  | 11 |  | BD001927 | 1 | 2005.36 | 2031.86 | 26.5 | 160000 | 4240000 |  | 4239445.5334 |  | 1888144
|  |  | 7: 0; 8: 0; 10: Total | 26832000 |  | 26828491.1678
| SHYAMPUR 11 kV SIDE |  | 7: 0; 8: 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur |  | 1 | 752.49 | 799.6936 | 47.2036 | 40000 |  | 1888144 | 1892333.6894 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1892333.6894 | 1814264.1154 | 78069.574 | 4.3031 | OK
6 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | B426E | 11 |  | BD001943 | 1 | 1085.02 | 1100.56 | 15.54 | 40000 |  | 621600 | 622979.2968 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 622979.2968 | 558390.1777 | 64589.119 | 11.567 | OK
8 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1583.91 | 1606.52 | 22.61 | 40000 |  | 904400 | 906406.8147 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 906406.8147 | 891408.4354 | 14998.3793 | 1.6825 | OK
10 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1473.51 | 1491.05 | 17.54 | 40000 |  | 701600 | 703156.8125 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 703156.8125 | 766828.9661 | -63672.1537 | -8.3033 | OK
11 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1390.8 | 1411.27 | 20.47 | 40000 |  | 818800 | 820616.8729 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 820616.8729 | 1034936.8854 | -214320.0125 | -20.7085 | OK
12 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3458.08 | 3529.38 | 71.3 | 40000 |  | 2852000 | 2858328.4338 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2858328.4338 | 2421034.6696 | 437293.7642 | 18.0623 | OK
13 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2255.93 | 2300.68 | 44.75 | 40000 |  | 1790000 | 1793971.9132 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1793971.9132 | 1756207.6637 | 37764.2495 | 2.1503 | OK
15 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 496.84 | 500.99 | 4.15 | 40000 |  | 166000 | 166368.345 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 166368.345 | 155220.3743 | 11147.9707 | 7.182 | OK
17 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3269.99 | 3319.55 | 49.56 | 40000 |  | 1982400 | 1986798.8384 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1986798.8384 | 1913040.7173 | 73758.1211 | 3.8555 | OK
18 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2051.33 | 2091.49 | 40.16 | 40000 |  | 1606400 | 1609964.5147 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1609964.5147 | 1509467.744 | 100496.7707 | 6.6578 | OK
19 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1523.24 | 1561.08 | 37.84 | 40000 |  | 1513600 | 1516958.5966 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1516958.5966 | 546698.2534 | 970260.3431 | 177.4764 | FAULT
20 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 864.46 | 891.78 | 27.32 | 40000 |  | 1092800 | 1095224.8641 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 1095224.8641 | 747879.9854 | 347344.8788 | 46.4439 | FAULT
22 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1370.29 | 1385.17 | 14.88 | 40000 |  | 595200 | 596520.7166 | Shyampur |  |  |  | 11 kV Delpara Feeder | 596520.7166 | 735784.8913 | -139264.1746 | -18.9273 | OK
23 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3205.07 | 3261.15 | 56.08 | 40000 |  | 2243200 | 2248177.5395 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2248177.5395 | 2749214.8896 | -501037.3501 | -18.2247 | OK
24 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1121.46 | 1128.58 | 7.12 | 40000 |  | 284800 | 285431.9558 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 285431.9558 | 272542.7871 | 12889.1687 | 4.7292 | OK
26 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2055.4 | 2088.29 | 32.89 | 40000 |  | 1315600 | 1318519.2453 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1318519.2453 | 1539705.4793 | -221186.234 | -14.3655 | OK
28 | 11 kV Spare Feeder | spare | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1411.57 | 1435.214 | 23.644 | 40000 |  | 945760 | 947858.5903 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 947858.5903 | 859154.8511 | 88703.7392 | 10.3245 | OK
30 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1384.37 | 1414.78 | 30.41 | 40000 |  | 1216400 | 1219099.1258 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 1219099.1258 | 1035743.225 | 183355.9008 | 17.7028 | OK
31 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2351.37 | 2381.97 | 30.6 | 40000 |  | 1224000 | 1226715.9898 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1226715.9898 | 1501001.1782 | -274285.1883 | -18.2735 | OK
35 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 175.82 | 178.05 | 2.23 | 40000 |  | 89200 | 89397.93 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 89397.93 | 41123.3199 | 48274.61 | 117.3899 | FAULT
37 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1256.25 | 1277.88 | 21.63 | 40000 |  | 865200 | 867119.832 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 867119.832 | 867218.2472 | -98.4152 | -0.011348 | OK
39 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3812.96 | 3859.6597 | 46.6997 | 40000 |  | 1867988 | 1872132.9644 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 1872132.9644 | 1624774.3078 | 247358.6566 | 15.2242 | OK
40 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1128.27 | 1132.87 | 4.6 | 40000 |  | 184000 | 184408.2861 | Shyampur |  |  |  | 11 kV Igloo Feeder | 184408.2861 | 343903.8423 | -159495.5563 | -46.378 | CHECK
41 | 11/0.4 kV Aux Transformer, T-1 |  | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) |  | 0.415 | DPDC | DHK26108 | 1 | 65260.8 | 65650.1 | 389.3 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) |  | 0.415 |  |  | 1 | 619265 | 625854 | 6589 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 |  | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 26828491.1678 | 26769092 | 26828491.1678 | 0.22189
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 986985.218
[6 empty] | Shyampur | at 33 KV level |  | 25841505.9498
[6 empty] | Total = |  |  | 26828491.1678 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2644.437 | 2679.862 | 35.425 | 240000 | 0 | 8672040 | 8673318.6567
23 | 33 kV Shyampur BSCIC-2. |  | 33 |  | BD001827 | 1 | 2590.3112 | 2629.531 | 39.2198 | 240000 | 0 | 9412752 | 9414139.8717
|  |  | 10: Total | 0 | 18084792 | 18087458.5284
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 |  | 33 | Import | DHK61071 | 1 | 1006470.9 | 1006470.9 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-2 |  | 33 | Import | DHK61067 | 1 | 824440.7 | 860148 | 35707.3 | 270 | 9640971
|  |  | 7: 0; 8: 0; 10: Total | 9640971 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  | 7: 0; 8: 0
2 | 33 kV 20/28 MVA Transformer-1 |  | 33 | Export | DHK61068 | 1 | 1024311.6 | 1024311.6 | 0 | 180 |  | 0
3 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Export | DHK61066 | 1 | 730036.7 | 730036.7 | 0 | 180 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 18087458.5284; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 18087458.5284
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 18087458.5284 | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 18087458.5284
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 4: 18087458.5284
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK61019 | 1.05 | 48255.9 | 123536.9 | 75281 | 180 | 14228109 |  | 10849592.6918 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK61018 | 1 | 849520.6 | 902252.3 | 52731.7 | 180 | 9491706 |  | 7237865.8366
|  |  | 7: 0; 8: 0; 10: Total | 23719815 |  | 18087458.5284
| SHYAMPUR BISIC 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nama shyampur Feeder |  | 11 | Shympur | HA-021101066-02 | 1 | 44443826 | 46233188 | 1789362 | 1 |  | 1789362 | 1775047.104 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 1775047.104 | 2124178.3588 | -349131.2548 | -16.4361 | OK
2 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 23612106 | 24282013 | 669907 | 1 |  | 669907 | 664547.744 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 664547.744 | 735518.3371 | -70970.5931 | -9.6491 | OK
3 | 11 kV H. R Steel |  | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) |  | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 528325.7 | 559360.2 | 31034.5 | 60 |  | 1862070 | 1847173.44 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1847173.44 | 1772799.78 | 74373.66 | 4.1953 | OK
6 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 668712.2 | 693053.6 | 24341.4 | 60 |  | 1460484 | 1448800.128 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1448800.128 | 1537289.4923 | -88489.3643 | -5.7562 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 685766.2 | 708041.4 | 22275.2 | 60 |  | 1336512 | 1325819.904 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1325819.904 | 1436086.1084 | -110266.2044 | -7.6782 | OK
8 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 403627.9 | 421306.3 | 17678.4 | 60 |  | 1060704 | 1052218.368 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1052218.368 | 1093174.4833 | -40956.1153 | -3.7465 | OK
9 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 521552.7 | 540442.3 | 18889.6 | 60 |  | 1133376 | 1124308.992 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 1124308.992 | 208419.6185 | 915889.3735 | 439.4449 | FAULT
12 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 12323.7 | 51207.4 | 38883.7 | 60 |  | 2333022 | 2314357.824 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2314357.824 | 2668033.8435 | -353676.0195 | -13.2561 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 328026.8 | 350357.3 | 22330.5 | 60 |  | 1339830 | 1329111.36 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1329111.36 | 1432539.3027 | -103427.9427 | -7.2199 | OK
14 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 498710.3 | 518177 | 19466.7 | 60 |  | 1168002 | 1158657.984 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 1158657.984 | 1382304.8305 | -223646.8465 | -16.1793 | OK
15 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 659724.2 | 694813.1 | 35088.9 | 60 |  | 2105334 | 2088491.328 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2088491.328 | 2541202.6985 | -452711.3705 | -17.8148 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 894406.3 | 907279.3 | 12873 | 60 |  | 772380 | 766200.96 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 766200.96 | 752054.1743 | 14146.7857 | 1.8811 | OK
17 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 38811.9 | 70053.1 | 31241.2 | 60 |  | 1874472 | 1859476.224 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1859476.224 | 1837006.5171 | 22469.7069 | 1.2232 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 43170.716 | -43170.716 | -100 | CHECK
| SUB-Station not match |  | 10: Grand Total | 18754211.36 | 18905455 | 18754211.36 | -0.8 |  |  |  | SUB-Station not match
| bscic 33/11 kv ss | [16 empty] | bscic 33/11 kv ss
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 6015853.056
[6 empty] | Jurain | at 33 KV level |  | 12738358.304
[6 empty] | Total = |  |  | 18754211.36 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1366.304 | 1392.002 | 25.698 | 240000 | From Downstream | 6167520 | 6168429.3755
7 | 33 kV Nondolalpur -2 feeder |  | 33 |  | BD001807 | 1 | 1180.8005 | 1202.282 | 21.4815 | 240000 | 0 | 5155560 | 5156320.1662
|  |  | 10: Total | 0 | 11323080 | 11324749.5417
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) |  | 33 | Import | 00000084 | 1 | 327871524 | 334080704 | 6209180 | 1 | 6209180
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) |  | 33 | Import | 00000070 | 1 | 303934336 | 309115200 | 5180864 | 1 | 5180864
|  |  | 7: 0; 8: 0; 10: Total | 11390044 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NANDALALPUR 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 28/35 MVA T-1 |  | 33 | Export | 00000086 | 1 | 328057280 | 334262976 | 6205696 | 1 |  | 6205696
5 | 33 kV, 28/35 MVA T-2 |  | 33 | Export | 00000083 | 1 | 303371200 | 308549248 | 5178048 | 1 |  | 5178048
|  |  | 10: Total |  | 11383744 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 4: 11324749.5417; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11324749.5417
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 11324749.5417 | 33 KV TX HV SIDE |  | 11383744
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -58994.4583
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.5209%
| TOTAL IMPORT |  | 4: 11324749.5417
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. |  | 11 |  | 00000036 | 1 | 326114944 | 332294976 | 6180032 | 1 | 6180032 |  | 6173654.6191 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000033 | 1 | 302055744 | 307212160 | 5156416 | 1 | 5156416 |  | 5151094.9226
|  |  | 7: 0; 8: 0; 10: Total | 11336448 |  | 11324749.5417
| NANDALALPUR 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Spare | spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | B889Z | 11 |  | 00000026 | 1 | 7422622 | 8000660 | 578038 | 1 |  | 578038 | 579356.8008 | Fatullah |  |  |  | 11 kV Khaza Moinuddin | 579356.8008 | 656635.1076 | -77278.3067 | -11.7688 | OK
10 | 11 kV Chitashal | B489Q | 11 |  | 00000027 | 1 | 35456592 | 36082072 | 625480 | 1 |  | 625480 | 626907.0404 | Shyampur |  |  |  | 11 kV Chitashal | 626907.0404 | 735704.304 | -108797.2637 | -14.7882 | OK
11 | 11 kV Local Feeder | B489G | 11 |  | 00000157 | 1.5 | 19031274 | 19190114 | 158840 | 1 | Estimated | 470836.8 | 471911.02 | Shyampur | 40 |  |  | 11 kV Local Feeder | 471911.02 | 670610.6986 | -198699.6786 | -29.6297 | OK
12 | 11 kV Rasel Germants |  | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 |  | 00000121 | 1 | 80634160 | 82827040 | 2192880 | 1 |  | 2192880 | 2197883.0829 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2197883.0829 | 2409135.9772 | -211252.8943 | -8.7688 | OK
14 | 11 kV Nandalalpur | B890X | 11 |  | 00000010 | 1 | 86136912 | 86980384 | 843472 | 1 |  | 843472 | 845396.3918 | Fatullah |  |  |  | 11 kV Nandalalpur | 845396.3918 | 817827.925 | 27568.4668 | 3.3709 | OK
15 | 11 kV Sharif Bagh | B489SB | 11 |  | 00000132 | 1 | 77028008 | 78453808 | 1425800 | 1 |  | 1425800 | 1429052.9803 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1429052.9803 | 1697558.3187 | -268505.3383 | -15.8171 | OK
18 | 11 kV Spare | spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | B890Y | 11 |  | 00000158 | 1 | 68472832 | 69477432 | 1004600 | 1 |  | 1004600 | 1006892.0073 | Fatullah |  |  |  | 11 KV Nayamati | 1006892.0073 | 1138166.5842 | -131274.5769 | -11.5339 | OK
20 | 11 kV Pulpar | B889S | 11 |  | 00000160 | 1 | 10315015 | 11257213 | 942198 | 1 |  | 942198 | 944347.6364 | Fatullah |  |  |  | 11 kV Pulpar | 944347.6364 | 974125.8442 | -29778.2078 | -3.0569 | OK
21 | 11 kV Shahi Bazar | B489X | 11 |  | 00000170 | 1 | 43318576 | 43910492 | 591916 | 1 |  | 591916 | 593266.4637 | Shyampur |  |  |  | 11 kV Shahi Bazar | 593266.4637 | 769069.4058 | -175802.9422 | -22.8592 | OK
22 | 11 kV Pagla Bazar | B890G | 11 |  | 00000060 | 1 | 52221152 | 52781312 | 560160 | 1 |  | 560160 | 561438.012 | Fatullah |  |  |  | 11 kV Pagla Bazar | 561438.012 | 651299.1372 | -89861.1253 | -13.7972 | OK
23 | 11 kV Delpara bazar | B489M | 11 |  | 00000063 | 1 | 83841392 | 85270552 | 1429160 | 1 |  | 1429160 | 1432420.6462 | Shyampur |  |  |  | 11 kV Delpara bazar | 1432420.6462 | 1512147.634 | -79726.9877 | -5.2724 | OK
24 | 11 kV Bhuighor (Board mill) | E289C | 11 |  | 00000146 | 1 | 45875048 | 46505368 | 630320 | 1 |  | 630320 | 631758.0829 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 631758.0829 | 736149.3859 | -104391.303 | -14.1807 | OK
25 | 11 kV Spare |  | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 |  | 11 |  | 7803 | 1 | 2600 | 2634 | 34 | 100 |  | 3400 | 3407.7571 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 3407.7571 | 4811.696 | -1403.9388 | -29.1776 | OK
27 | 33/0.415 kV, 200 kVA AT-2 |  | 11 |  | 7805 | 1 | 71.1 | 78.2 | 7.1 | 100 |  | 710 | 711.6199 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 711.6199 | 912.2174 | -200.5975 | -21.9901 | OK
|  |  | 10: Grand Total | 11324749.5417 | 11298970.8 | 11324749.5417 | 0.22815
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 4557677.5276
[6 empty] | Fatullah | at 33 KV level |  | 3937430.8484
[6 empty] | Matuail | at 33 KV level |  | 2829641.1657
[6 empty] | Total = |  |  | 11324749.5417 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 |  | 132 | Import | 4262 7826 | 1 | 378.796 | 402.926 | 24.13 | 960000 | 0 | 23164800
[6 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 |  | 132 |  | 4262 7815 | 1 | 159.248 | 165.737 | 6.489 | 960000 | 0 | 6229440
2 | [5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 29394240
|  |  | 10: Net Total | 29394240
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 |  | 132 | Main | 41808902823 | 1 | 302.81 | 322.1 | 19.29 | 1200000 | 23148000
|  |  | 132 | Backup | 41808904269 | 1 | 302.81 | 322.1 | 19.29 | 1200000 | 23148000
4 | 132kV Hasnabad Circuit-2 |  | 132 | Imp/Main | 41808902845 | 1 | 127.29 | 132.48 | 5.19 | 1200000 | 6228000
|  |  | 132 | Imp/Backup | 41808904256 | 1 | 127.29 | 132.48 | 5.19 | 1200000 | 6228000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 29376000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 29376000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| POSTOGOLA 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41808902871 | 1 | 313.92 | 333.18 | 19.26 | 1200000 |  | 23112000
|  |  | 132 | Exp/Backup | 41808904257 | 1 | 313.92 | 333.18 | 19.26 | 1200000 |  | 23112000
5 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41808902846 | 1 | 116.02 | 121.22 | 5.2 | 1200000 |  | 6240000
|  |  | 132 | Exp/Backup | 41808904243 | 1 | 116.02 | 121.22 | 5.2 | 1200000 |  | 6240000
|  |  | 10: Total |  | 29352000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 29394240; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 29394240
|  |  | 6: 132 KV NET IMPORT; 9=8-7: 29394240 | 33 KV NET IMPORT |  | 28260000
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1134240
[11 empty] | LOSS % IN => |  | 3.859%
| 132 KV TOTAL IMPORT |  | 4: 29394240
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE |  | 10: Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41808902807 | 1 | 521.43 | 552.38 | 30.95 | 720000 | 22284000
|  |  | 33 | Backup | 41808904286 | 1 | 521.43 | 552.38 | 30.95 | 720000 | 22284000
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41808902869 | 1 | 192.08 | 200.38 | 8.3 | 720000 | 5976000
|  |  | 33 | Backup | 41808904268 | 1 | 192.08 | 200.38 | 8.3 | 720000 | 5976000
|  |  | 7: 0; 8: 0; 10: Total | 28260000 |  | 29394240
| POSTOGOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 |  | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss | 1.3882 | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 475.3 | 495.61 | 20.31 | 360000 |  | 7311600 | 7293793.7007 |  | 14382887.135 | IG Gate 33/11 kv ss | 0 | 33 kV IG Gate Ckt-2 | 7293793.7007 | 9468000 | -2174206.2993 | -22.9637 | OK
|  |  | 33 | Backup | 41808904225 | 1 | 475.3 | 495.61 | 20.31 | 360000 |  | 7311600 | 7293793.7007 |  |  |  |  | 0 | 7293793.7007 | 9468000 | -2174206.2993 | -22.9637 | OK
8 | 33 kV Spare Feeder 2 |  | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 |  | 33 | Main | 41808902810 | 1 | 569.3 | 611.1 | 41.8 | 360000 |  | 15048000 | 15011352.865 |  |  |  |  | 33kV Postogola circuit-1 | 15011352.865 | 18446400 | -3435047.135 | -18.6218 | OK
|  |  | 33 | Backup | 41808904252 | 1 | 569.3 | 611.1 | 41.8 | 360000 |  | 15048000 | 15011352.865 |  |  |  |  | 0 | 15011352.865 | 18446400 | -3435047.135 | -18.6218 | OK
14 | 31 kV Spare Feeder 4 |  | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 |  | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 |  | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1.2 | 382.7 | 399.15 | 16.45 | 360000 |  | 7106400 | 7089093.4343 |  |  |  |  | 33 kV IG Gate Ckt-1 | 7089093.4343 | 7581600 | -492506.5657 | -6.4961 | OK
|  |  | 33 | Backup | 41812909573 | 1.2 | 382.7 | 399.15 | 16.45 | 360000 |  | 7106400 | 7089093.4343 |  |  |  |  | 0 | 7089093.4343 | 7581600 | -492506.5657 | -6.4961 | OK
|  |  | 10: Total |  | 29466000 | 29394240 |  |  |  |  | 0 | 29394240 | 35496000 | -6101760 | -17.19 | OK
|  |  | 9=8-7: Grand Total | 29394240 | 29466000 | 29394240 | -0.24353
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola |  | 33 | Import | BD001804 | 1 | 569.3 | 611.1 | 41.8 | 360000 | 15048000 |  | 15011352.865
2 | 33 kV Postogola Circuit-2 at Shyampur |  | 33 | Import | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 15048000 |  | 15011352.865
| POSTOGOLA 33 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) |  | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) |  | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0
| POSTOGOLA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK61027 | 1 | 376993.6 | 412476.1 | 35482.5 | 180 |  | 6386850 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60870 | 1 | 846711.4 | 897896.4 | 51185 | 180 |  | 9213300
|  |  | 7: 0; 8: 0; 10: Total |  | 15600150
| POSTOGOLA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV 20/28 MVA T-1 Incoming. |  | 11 |  | DHK61005 | 1.165 | 954321.5 | 985125.6 | 30804.1 | 180 | 6459619.77 |  | 15011352.865 |  | 31200300
9 | 11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK60861 | 1.165 | 1038479.9 | 1038479.9 | 0 | 180 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 6459619.77 |  | 15011352.865
| POSTOGOLA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 66131524 | 67083281 | 951757 | 1 |  | 951757 | 964969.6559 | Postogola |  |  |  | 11 kV Station Road Feeder | 964969.6559 | 1255334.9139 | -290365.258 | -23.1305 | OK
2 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 0 | 594 | 594 | 1000 | Estimated | 1188000 | 1204492.2718 | Jurain | Reading Converted to 30 days |  |  | 11 kV Samon & Sons Feeder. | 1204492.2718 | 1239052.6971 | -34560.4253 | -2.7893 | OK
3 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 25644920 | 26047328 | 402408 | 1 |  | 402408 | 407994.3823 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 407994.3823 | 537163.6113 | -129169.229 | -24.0465 | OK
4 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 79011228 | 80275699 | 1264471 | 1 |  | 1264471 | 1282024.8716 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1282024.8716 | 1532425.7761 | -250400.9045 | -16.3402 | OK
5 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 461916 | 471377.73 | 9461.73 | 60 |  | 567703.8 | 575584.882 | Postogola |  |  |  | 11 kV Cyca Feeder | 575584.882 | 676389.0131 | -100804.1311 | -14.9033 | OK
6 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 925873.2 | 941864.1 | 15990.9 | 60 |  | 959454 | 972773.5086 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 972773.5086 | 1191302.5568 | -218529.0482 | -18.3437 | OK
7 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 814922.6 | 831587.6 | 16665 | 60 |  | 999900 | 1013780.9955 | Postogola |  |  |  | 11 kV Munshi Bari | 1013780.9955 | 1266750.2722 | -252969.2768 | -19.9699 | OK
8 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 526393.2 | 528585.6 | 2192.4 | 60 |  | 131544 | 133370.1443 | Postogola |  |  |  | 11 kV Cantonment Feeder | 133370.1443 | 125848.0606 | 7522.0837 | 5.9771 | OK
9 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 905082.3 | 927947.6 | 22865.3 | 60 |  | 1371918 | 1390963.4921 | Postogola |  |  |  | 11 kV DIT Feeder. | 1390963.4921 | 1427602.3077 | -36638.8156 | -2.5665 | OK
10 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 445618.9 | 469020.9 | 23402 | 60 |  | 1404120 | 1423612.5326 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 1423612.5326 | 2449336.9799 | -1025724.4473 | -41.8776 | CHECK
11 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 45310492 | 47773398 | 2462906 | 1 |  | 2462906 | 2497097.0061 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 2497097.0061 | 2454381.4966 | 42715.5095 | 1.7404 | OK
12 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 15592.1 | 17714.8 | 2122.7 | 1000 |  | 2122700 | 2152168.1359 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2152168.1359 | 2435670.3328 | -283502.1969 | -11.6396 | OK
13 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 60970541 | 62312639 | 1342098 | 1 |  | 1342098 | 1360729.5194 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1360729.5194 | 1622380.5518 | -261651.0324 | -16.1276 | OK
14 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 0 | 53.1 | 53.1 | 1000 | Estimated | 106200 | 107674.3091 | Postogola | Reading Converted to 30 days |  |  | 11 kV Rajabari Feeder. | 107674.3091 | 247810.5394 | -140136.2303 | -56.5497 | CHECK
15 | 11/0.415 kV, 200 kVA AT-1+2 |  | 11 |  | ELIB67385 | 1 | 539.63 | 585.41 | 45.78 | 80 |  | 3662.4 | 3713.2428 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3713.2428 | 4606.8906 | -893.6478 | -19.3981 | OK
|  |  | 10: Total | 15490948.95 | 15278842.2 | 15490948.95 | 1.3882
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Postogola | at 33 KV level |  | 7805584.6213
[6 empty] | Jurain | at 33 KV level |  | 7685364.3287
[6 empty] | Total = |  |  | 15490948.95 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.8992 | 1544.899 | -0.0002 | 240000 | 0 | -48 | -48.0071
| Postogola 33 KV SIDE |  | 10: Total | 0 | -48 | -48.0071
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 475.3 | 495.61 | 20.31 | 360000 | 0 | 7311600 | 7293793.7007
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1.2 | 382.7 | 399.15 | 16.45 | 360000 | 0 | 7106400 | 7089093.4343
|  |  | 10: Total | 0 | 14418000 | 14382887.135
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 |  | 33 | Import | DHK60973 | 1 | 309189.6 | 322169.6 | 12980 | 540 | 7009200
6 | 33 kV Postogola Incoming Feeder-2 |  | 33 | Import | DHK60966 | 1 | 502284.8 | 515717.3 | 13432.5 | 540 | 7253550
|  |  | 7: 0; 8: 0; 10: Total | 14262750 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| IG GATE 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK60893 | 1 | 892147.6 | 931053.7 | 38906.1 | 180 |  | 7003098
5 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60975 | 1 | 518056.2 | 580754.6 | 62698.4 | 180 |  | 11285712
|  |  | 10: Total |  | 18288810
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 4: 14382887.135; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 14382887.135
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 14382887.135 | 33 KV TX HV SIDE |  | 18288810
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -3905922.865
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -27.16%
| TOTAL IMPORT |  | 4: 14382887.135
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month November-2023 |  |  | Name of Feeders. | Month November-2023 | Month October-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK68139 | 1 | 3829.57 | 3866.96 | 37.39 | 180000 | 6730200 |  | 7494093.5058 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK68137 | 1 | 4479.97 | 4514.34 | 34.37 | 180000 | 6186600 |  | 6888793.6292
|  |  | 7: 0; 8: 0; 10: Total | 12916800 |  | 14382887.135
| IG GATE 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Feeder-1 |  | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 |  | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | A619R | 11 |  | DHK60970 | 1 | 325962.4 | 354107.8 | 28145.4 | 60 |  | 1688724 | 1688724 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 1688724 | 1912589.3597 | -223865.3597 | -11.7048 | OK
4 | 11 kV Alom Gonj | A581A | 11 |  | DHK60894 | 1 | 511135.3 | 520758.3 | 9623 | 60 |  | 577380 | 577380 | Postogola |  |  |  | 11 kV Alom Gonj | 577380 | 601965.5066 | -24585.5066 | -4.0842 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 |  | DHK60895 | 1 | 625193.4 | 650759.1 | 25565.7 | 60 |  | 1533942 | 1533942 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1533942 | 1585262.0566 | -51320.0566 | -3.2373 | OK
6 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 |  | DHK68133 | 1 | 3683.69 | 3711.29 | 27.6 | 60000 |  | 1656000 | 1656000 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1656000 | 1845366.1756 | -189366.1756 | -10.2617 | OK
7 | 11 kV Doyaganj | B587Y | 11 |  | DHK68134 | 1 | 2463.08 | 2488.28 | 25.2 | 60000 |  | 1512000 | 1512000 | Swamibag |  |  |  | 11 kV Doyaganj | 1512000 | 1596436.5035 | -84436.5035 | -5.2891 | OK
10 | 11 kV Faridabad | A587F | 11 |  | DHK68140 | 1 | 838.74 | 857.46 | 18.72 | 60000 |  | 1123200 | 1123200 | Postogola |  |  |  | 11 kV Faridabad | 1123200 | 1253169.1806 | -129969.1806 | -10.3712 | OK
11 | 11 kV Gandaria | A524D | 11 |  | DHK60969 | 1 | 473557.9 | 503196.3 | 29638.4 | 60 |  | 1778304 | 1778304 | Postogola |  |  |  | 11 kV Gandaria | 1778304 | 1938857.8307 | -160553.8307 | -8.2808 | OK
12 | 11 kV Walter Road | A687W | 11 |  | DHK68136 | 1 | 1054.29 | 1075.44 | 21.15 | 60000 |  | 1269000 | 1269000 | Banglabazar |  |  |  | 11 kV Walter Road | 1269000 | 1348724.0914 | -79724.0914 | -5.9111 | OK
13 | 11 kV Murgitola Feeder (F-11) | B587G | 11 |  | DHK68138 | 1 | 4009.01 | 4043.16 | 34.15 | 60000 |  | 2049000 | 2049000 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2049000 | 2352354.9699 | -303354.9699 | -12.8958 | OK
14 | 11 kV Feeder-12 |  | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 |  | DHK60899 | 1 | 752453.5 | 777965.1 | 25511.6 | 60 |  | 1530696 | 1530696 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1530696 | 1678266.8077 | -147570.8077 | -8.793 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 |  | DHK60967 | 1 | 214602.5 | 228309.7 | 13707.2 | 60 |  | 822432 | 822432 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 822432 | 935068.7084 | -112636.7084 | -12.0458 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB2774 | 1 | 284380 | 285932 | 1552 | 1 |  | 1552 | 1552 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1552 | 1538.8094 | 13.1906 | 0.8572 | OK
|  |  | 10: Grand Total | 15542230 | 15542230 | 15542230 | 0
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Swamibag | at 33 KV level |  | 5091696
[6 empty] | Banglabazar | at 33 KV level |  | 4613724
[6 empty] | Postogola | at 33 KV level |  | 5836810
[6 empty] | Total = |  |  | 15542230 | 0
Note on J393: No Reading Due to PT Out
Note on L393: Reading From Higher Side
Note on J650: No Reading due to PT Open
Note on M650: Energy From Bangshal SS End
Note on M655: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month November-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month November-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.09.2023 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 7138892.7551 | 16335190.4879 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 7131536.6451 |  | North | 231227251.2158 | Tejgaon | 47414798.1367 | Tejgaon | 26821171.9379 | 33018095.2472 | -6196923.3092 | -18.7683 | North | 231227251.2158 | 303699254.015 | -31.3423 | Tejgaon | 47414798.1367 | 59346933 | -25.1654 | Tejgaon | 26821171.9379 | 31468806 | -17.3282 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 0 | [5 empty] | Kakrail | 20593626.1987 | 25773097.2445 | -5179471.0458 | -20.0964 | [8 empty] | Kakrail | 20593626.1987 | 27878127 | -35.3726 | 2 | Tejgaon | 31468806 | 196426 | 31665232 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | 5419984.962
|  |  |  | Maghbazar | 2064761.0876 |  |  |  | Moghbazar | 27938241.6106 | Moghbazar | 15252399.5754 | 19456170.4445 | -4203770.8691 | -21.6064 |  |  |  |  | Moghbazar | 27938241.6106 | 36894933 | -32.0589 | Moghbazar | 15252399.5754 | 20573106 | -34.8844 | 3 | Kakrail | 27878127 | 134050 | 28012177 | A1 | Motijheel | 22865869 | 164088 | 23029957
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 10776502.4746 |  |  |  |  | Khilgaon | 12685842.0352 | 15675155.8489 | -2989313.8137 | -19.0704 | [8 empty] | Khilgaon | 12685842.0352 | 16321827 | -28.6618 | 4 | Moghbazar | 20573106 | 63535 | 20636641 | A2 | Khilgaon | 16321827 | 59703 | 16381530
|  |  |  | Jigatola | 2067903.0443 |  |  |  | Satmasjid | 35370948.0369 | Satmosjid | 17020995.2428 | 21777495.0822 | -4756499.8395 | -21.8414 |  |  |  |  | Satmasjid | 35370948.0369 | 46167247 | -30.5231 | Satmosjid | 17020995.2428 | 22160943 | -30.1977 | 5 | Khilgaon | 16321827 | 59703 | 16381530 | A3 | Lalbag | 32204138 | 464799 | 32668937
|  |  |  | Paribagh | 8708599.4302 | [5 empty] | Sherebanglanagar | 18349952.7941 | 23478009.3575 | -5128056.5634 | -21.842 | [8 empty] | Sherebangla nagar | 18349952.7941 | 24006304 | -30.8249 | 6 | Satmosjid | 22160943 | 83495 | 22244438 | A4 | Kazla | 38390804 | 86446 | 38477250
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 10503000 |  |  | Dhanmondi | 39400198.8041 | Dhanmondi | 17445142.2053 | 22296608.5062 | -4851466.3009 | -21.7588 |  |  |  |  | Dhanmondi | 39400198.8041 | 53818759.15 | -36.5951 | Dhanmondi | 17445142.2053 | 24555384 | -40.7577 | 7 | Sherebanglanagar | 24006304 | 57477 | 24063781 | A5 | Postogola | 15925283 | 139839 | 16065122
[11 empty] | Jhigatala | 21955056.5988 | 27544349.6502 | -5589293.0514 | -20.292 | [8 empty] | Jhigatala | 21955056.5988 | 29263375.15 | -33.2876 | 8 | Dhanmondi | 24555384 | 124825 | 24680209 | A6 | Banglabazar | 16227586 | 65470 | 16293056
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 42433774.0747 | Azimpur | 15774856.9994 | 18790675.4911 | -3015818.4917 | -16.0495 |  |  |  |  | Azimpur | 42433774.0747 | 54252662.865 | -27.8526 | Azimpur | 15774856.9994 | 19587741 | -24.1706 | 9 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274 | A7 | N.Gonj (West) | 28707452 | 196212 | 28903664
|  |  |  | Dhanmondi | 10503000 | [5 empty] | Paribagh | 26658917.0753 | 33415225.182 | -6756308.1068 | -20.2193 | [8 empty] | Paribagh | 26658917.0753 | 34664921.865 | -30.0312 | 10 | Azimpur | 19587741 | 236081 | 19823822 | A8 | Siddirgonj | 49639472 | 532212 | 50171684
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 16441858.2452 | 16441858.2452 |  |  | Shamoly | 38669290.5528 | Shyamoli | 13993395.6523 | 17460263.4212 | -3466867.7689 | -19.8558 |  |  |  |  | Shamoly | 38669290.5528 | 53218719 | -37.6253 | Shyamoli | 13993395.6523 | 19516523 | -39.4695 | 11 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448 | A9 | Bashabo | 14583022 | 53363 | 14636385
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 10485743.2849 |  |  |  |  | Adabor | 24675894.9005 | 31934060.5098 | -7258165.6093 | -22.7286 | [8 empty] | Adabor | 24675894.9005 | 33702196 | -36.5794 | 12 | Shyamoli | 19516523 | 64518 | 19581041 | B1 | Narinda | 13978240 | 38770 | 14017010
|  |  |  | RAMNA | 827169.9762 |  | Central | 226661490.865 | Lalbagh | 72039485.1308 | Lalbagh | 34548667.0633 | 36837631.6772 | -2288964.6139 | -6.2137 | Central | 226661490.865 | 262953550.91 | -16.0116 | Lalbagh | 72039485.1308 | 70781931 | 1.7456 | Lalbagh | 34548667.0633 | 32204138 | 6.7862 | 13 | Adabor | 33702196 | 255452 | 33957648 | B2 | Maniknagar | 20970662 | 109760 | 21080422
|  |  |  | Kakrail | 1325835.5807 | [5 empty] | Kamrangirchar | 37490818.0675 | 41932811.2666 | -4441993.1991 | -10.5931 | [8 empty] | Kamrangirchar | 37490818.0675 | 38577793 | -2.8993 | 14 | Lalbagh | 32204138 | 464799 | 32668937 | B3 | Jurain | 27684985 | 453096 | 28138081
|  |  |  | Paribagh | 8332737.728 |  |  |  | Ramna | 35613319.5883 | Ramna | 21620213.0472 | 27061948.3663 | -5441735.3191 | -20.1084 |  |  |  |  | Ramna | 35613319.5883 | 47932700 | -34.5921 | Ramna | 21620213.0472 | 28702610 | -32.7582 | 15 | Kamrangirchar | 38577793 | 101944 | 38679737 | B4 | Shyampur | 66519316 | 426920 | 66946236
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 3335122.7566 |  |  |  |  | Rajarbagh | 13993106.5411 | 17834758.7896 | -3841652.2485 | -21.5403 | [8 empty] | Rajarbagh | 13993106.5411 | 19230090 | -37.4255 | 16 | Ramna | 28702610 | 211333 | 28913943 | B5 | Swamibag | 13880852 | 46920 | 13927772
|  |  |  | Kakrail | 264073.7292 |  |  |  | Bashabo | 30102467.8033 | Bashabo | 11054667.4475 | 14160522.2761 | -3105854.8285 | -21.9332 |  |  |  |  | Bashabo | 30102467.8033 | 39590401.91 | -31.5188 | Bashabo | 11054667.4475 | 14583022 | -31.9173 | 17 | Rajarbagh | 19230090 | 88052 | 19318142 | B6 | Bangshal | 19038085 | 79495 | 19117580
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 19047800.3557 | 24189458.9462 | -5141658.5905 | -21.2558 | [8 empty] | Bonossri | 19047800.3557 | 25007379.91 | -31.2875 | 18 | Bashabo | 14583022 | 53363 | 14636385 | B7 | N.Gonj (East) | 30757520 | 509964 | 31267484
|  |  |  | Shere Bangla Nagar | 3071049.0274 |  |  |  | Motijheel | 34102856.8002 | Motijheel | 19118019.4179 | 21964622.2777 | -2846602.8598 | -12.9599 |  |  |  |  | Motijheel | 34102856.8002 | 41523755 | -21.7603 | Motijheel | 19118019.4179 | 22865869 | -19.6038 | 19 | Bnossri | 25007379.91 | 102145 | 25109524.91 | B8 | Fateullah | 32245904 | 463782 | 32709686
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1868981.585 | 7125200 |  |  |  |  | Mughdapara | 14984837.3823 | 19039301.9827 | -4054464.6004 | -21.2952 | [8 empty] | Mughdapara | 14984837.3823 | 18657886 | -24.5118 | 20 | Motijheel | 22865869 | 164088 | 23029957 | B9 | Mugdapara | 18657886 | 36172 | 18694058
|  |  |  | Lalbagh | 301881.114 |  |  |  | Banglabazar | 30731015.4149 | Banglabazar | 14621588.0922 | 17230899.4035 | -2609311.3112 | -15.1432 |  |  |  |  | Banglabazar | 30731015.4149 | 35265671 | -14.756 | Banglabazar | 14621588.0922 | 16227586 | -10.9837 | 21 | Mughdapara | 18657886 | 36172 | 18694058 | C1 | Tejgaon | 31468806 | 196426 | 31665232
|  |  |  | Narinda | 367694.0766 | [5 empty] | Bongshal | 16109427.3226 | 19607341.8018 | -3497914.4792 | -17.8398 | [8 empty] | Bongshal | 16109427.3226 | 19038085 | -18.1798 | 22 | Banglabazar | 16227586 | 65470 | 16293056 | C2 | Satmasjid | 22160943 | 83495 | 22244438
|  |  |  | Motijheel | 335231.5364 |  |  |  | Narinda | 24072346.1275 | Narinda | 11735087.3128 | 14708156.3518 | -2973069.039 | -20.2137 |  |  |  |  | Narinda | 24072346.1275 | 27859092 | -15.7307 | Narinda | 11735087.3128 | 13978240 | -19.1149 | 23 | Bongshal | 19038085 | 79495 | 19117580 | C3 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448
|  |  |  | RAMNA | 4251411.688 | [5 empty] | Swamibagh | 12337258.8148 | 14671698.7712 | -2334439.9564 | -15.9112 | [8 empty] | Swamibagh | 12337258.8148 | 13880852 | -12.5116 | 24 | Narinda | 13978240 | 38770 | 14017010 | C6 | Kakrail | 27878127 | 134050 | 28012177
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 407137080.2926 | Kazla | 53039339.6375 | Kazla | 36372517.6492 | 40188148.6608 | -3815631.0116 | -9.4944 | South | 407137080.2926 | 418742139 | -2.8504 | Kazla | 53039339.6375 | 59361466 | -11.9197 | Kazla | 36372517.6492 | 38390804 | -5.5489 | 25 | Swamibagh | 13880852 | 46920 | 13927772 | D1 | Moghbazar | 20573106 | 63535 | 20636641
|  | Khillgaon 33/11KV S/S |  | Kakrail | 63748.0823 | 5818860 |  |  |  |  | Maniknagar | 16666821.9883 | 20860079.5389 | -4193257.5506 | -20.1018 | [8 empty] | Maniknagar | 16666821.9883 | 20970662 | -25.8228 | 26 | Kazla | 38390804 | 86446 | 38477250 | D2 | Dhanmondi | 24555384 | 124825 | 24680209
|  |  |  | Khilgaon | 180.4191 |  |  |  | Shyampur | 92470923.1969 | Shyampur | 71763111.7333 | 67619215.2097 | 4143896.5236 | 6.1283 |  |  |  |  | Shyampur | 92470923.1969 | 88513636 | 4.2795 | Shyampur | 71763111.7333 | 66519316 | 7.3071 | 27 | Maniknagar | 20970662 | 109760 | 21080422 | D3 | Ramna | 28702610 | 211333 | 28913943
| 9 |  |  | Maghbazaar | 104859.5814 | [5 empty] | Matuail | 20707811.4636 | 24069283.3962 | -3361471.9327 | -13.9658 | [8 empty] | Matuail | 20707811.4636 | 21994320 | -6.2127 | 28 | Shyampur | 66519316 | 426920 | 66946236 | D4 | Shyamoli | 19516523 | 64518 | 19581041
|  |  |  | Rajarbagh | 5650071.9172 |  |  |  | Postogola | 39596324.212 | Postogola | 13642394.6213 | 15666312.9746 | -2023918.3534 | -12.9189 |  |  |  |  | Postogola | 39596324.212 | 43610268 | -10.1372 | Postogola | 13642394.6213 | 15925283 | -16.7338 | 29 | Matuail | 21994320 | 179400 | 22173720 | D5 | Shere b.nagar | 24006304 | 57477 | 24063781
| 10 | Goran 33/11KV S/S |  | Bashabo | 1201195.1008 | 9994040 |  |  |  |  | Jurain | 25953929.5907 | 30390953.6558 | -4437024.0651 | -14.5998 | [8 empty] | Jurain | 25953929.5907 | 27684985 | -6.6697 | 30 | Postogola | 15925283 | 139839 | 16065122 | D6 | Rajarbag | 19230090 | 88052 | 19318142
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 61062759.9523 | Narayangonj-West | 30568733.713 | 34400925.3767 | -3832191.6638 | -11.1398 |  |  |  |  | Narayangonj | 61062759.9523 | 59464972 | 2.6166 | Narayangonj- West | 30568733.713 | 28707452 | 6.0888 | 31 | Jurain | 27684985 | 453096 | 28138081 | D8 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274
|  |  |  | Banosree | 8792844.8992 | [5 empty] | Narayangonj-East | 30494026.2393 | 33863455.0033 | -3369428.764 | -9.95 | [8 empty] | Narayangonj- East | 30494026.2393 | 30757520 | -0.86408 | 32 | Narayangonj-West | 28707452 | 196212 | 28903664 | D9 | Azimpur | 19587741 | 236081 | 19823822
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 9455491.151 | 12736053.4253 |  |  | Demra | 64593182.367 | Demra | 19815215.6472 | 24012632.971 | -4197417.3238 | -17.48 |  |  |  |  | Demra | 64593182.367 | 71702210 | -11.0058 | Demra | 19815215.6472 | 22062738 | -11.3424 | 33 | Narayangonj-East | 30757520 | 509964 | 31267484 | E1 | Demra | 22062738 | 533151 | 22595889
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 44777966.7198 | 50116500.2466 | -5338533.5268 | -10.6522 | [8 empty] | Siddhirgonj | 44777966.7198 | 49639472 | -10.8569 | 34 | Damra | 22062738 | 533151 | 22595889 | E2 | Matuail | 21994320 | 179400 | 22173720
|  |  |  | Bashabo | 3280562.2743 |  |  |  | Fatullah | 96374550.9269 | Fatulla | 31245273.6587 | 36403490.2891 | -5158216.6304 | -14.1696 |  |  |  |  | Fatullah | 96374550.9269 | 96089587 | 0.29568 | Fatulla | 31245273.6587 | 32245904 | -3.2025 | 35 | Siddhirgonj | 49639472 | 532212 | 50171684 | E3 | Sytalakha | 63843683 | 329125 | 64172808
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 16847460 |  |  |  |  | Shitalakha | 65129277.2683 | 69932866.0189 | -4803588.7506 | -6.8689 | [8 empty] | Sytalakhya | 65129277.2683 | 63843683 | 1.9739 | 36 | Fatulla | 32245904 | 463782 | 32709686 | F1 | Kamrangirchar | 38577793 | 101944 | 38679737
|  |  |  | Shyamoli | 2256166.4498 |  | TOTAL=> | 865025822.3734 | TOTAL=> | 865025822.3734 | TOTAL=> | 865025822.3734 | 1007382221.2377 | -142356398.8643 | -14.1313 |  | 865025822.3734 | 985394943.925 |  | TOTAL=> | 865025822.3734 | 985394943.925 |  | Total=> | 865025822.3734 | 985394943.925 | -13.9151 | 37 | Shitalokko | 63843683 | 329125 | 64172808 | F2 | Banosree | 25007379.91 | 102145 | 25109524.91
|  |  |  | Shere Bangla Nagar | 0 | [23 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823 | G1 | Adabor | 33702196 | 255452 | 33957648
|  |  |  | Satmosjid | 10055142.5831 | [14 empty] | 132KV Import => |  |  |  |  | 869565238.7175 | [8 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823
|  |  |  | Dhanmondi NOCS | 4536150.9671 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 869565238.7175 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 865025822.3734
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 865025822.3734 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.52203
| 13 | Japan garden Building |  | Adabor | 1130040 | 1130040 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.52203 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 985394943.925
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 4539416.3441 | [8 empty] | System loss at 132kv level => |  |  |  |  | -13.3204
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 1622400 | 1622400
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 8788678 | 9405728
| 16 |  |  | Shere Bangla Nagar | 617050
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 26275200 | 26275200
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1405027.1069 | 10898805.0291
|  |  |  | Lalbagh | 9493777.9222
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 6259292.8817
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 6259292.8817
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 1983350.7703 | 7210881.4068
|  |  |  | Rajarbaghl | 2205272.6337
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 3022258.0028 | 3022258.0028
|  | Banshal 33/11 KV S/S |  | Bangshal | 5012499.2877 | 7078492.5761
|  |  |  | Banglabazar | 1083356.0922
|  |  |  | Narinda | 982637.1962
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 8152615.0224 | 12168000
|  |  |  | Shamoly | 3437112.2506
|  |  |  | Satmosjit | 578272.7269
|  | Azimpur 33/11 KV |  | jigatola | 138499.1268 | 13814139.3422
|  |  |  | Azimpur | 12174754.4418
|  |  |  | RAMNA | 915548.2641
|  |  |  | Paribagh | 585337.5096
|  | T&T 33/11 KV |  | Kakrail | 2507966.1564 | 8358914.6524
|  |  |  | Mogbazar | 4579783.4163
|  |  |  | Khilgaon | 1271165.0797
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 2822383.7256 | 4960741.29
|  |  |  | Shamoly | 1615836.8399
|  |  |  | Tejgaon | 519187.344
|  |  |  | Satmosjit | 3333.3805
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 22505748.2573 | 25729900
|  |  |  | Kamrangirchar | 3224151.7427
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 3176400.1623 | 4521779.1
|  |  |  | Kakrail | 1345378.9377
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 920259.0738
|  |  |  | Shere Bangla Nagar | 1019613.4683
|  |  |  | Shamoly | 6684280.1121
|  |  |  | Satmosjit | 3285008.4302
|  | Banasree 33/11SS |  | Khilgaon | 1301180.9495
|  |  |  | Bansree | 7110926.9313 | 7110926.9313
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 657824.4358 | 13804016
|  |  |  | Bashabo | 5358222.1347
|  |  |  | Mugdapara | 3440557.6688
|  |  |  | Maniknagor | 4347411.7607
|  | DMC |  | Bangshal | 2376679.7958
|  |  |  | RAMNA | 1579592.2163 | 3385425.8403
|  |  |  | Lalbagh | 1805833.624
|  | Green Road Dormatory |  | Paribagh | 6614817.0276
|  |  |  | Shere Bangla Nagar | 4745658.7531
|  | BSMMU 33/11KV S/S |  | Kakrail | 1523209.5776
|  |  |  | Paribagh | 2417425.3798
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 6604561.878
|  |  |  | Satmasjid | 3099238.122
|  | Dhaka University 33/11 KV SS |  | RAMNA | 1460000
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 4121727.1531
|  |  |  | Kakrail | 1045130.2132
|  |  |  | Tejgaon | 2728589.7037
|  | BGB 33/11 KV SS |  | Kamrangirchar | 6655828.1535
|  |  |  | Jigatola | 3234326.3958
|  |  |  | Azimpur | 2195075.4507
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 1952470.6666
|  | BB Avenue 33/11 KV SS |  | Narinda | 1733355.0526
|  |  |  | Ramna | 4338748.9033
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 14891928.0319
|  |  |  | Dhanmondi | 1485732.1644
|  | Ispahani 33/11 KV SS |  | Moghbazar | 2243702.6084
|  |  |  | Kakrail | 2357133.1637
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 1335638.1714
|  |  |  | Total=> | 376505032.1245 | 258333823.8557
NORTH ZONE TOTAL=>
|  | NOCS |  | 376505032.1245 |  | 200857461
|  | diff |  |  | -376505032.1245
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 4428000
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 4428000
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 333110.8966 | 13277585.6396
|  |  |  | Swamibagh | 4489659.7706
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 8454814.9724
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 8924508
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 8924508
| 4 | Maderteck 33/11KV S/S |  | Banosree | 3144028.5252 | 14666188.0859
|  |  |  | Bashabo | 1214687.9378
|  |  |  | Maniknagar | 277461.6755
|  |  |  | Mugdapara | 10030009.9473
| 5 | Kazla 33/11KV S/S |  | Matual | 909946.5244 | 31009867.2957
|  |  |  | Jurain | 5530206.958
|  |  |  | Swamibagh | 1593271.6426
|  |  |  | Maniknagar | 1926677.5758
|  |  |  | Shyampur | 2019121.3431
|  |  |  | Kazla | 19030643.2518
|  | Shyampur 132/11KV S/S |  | Shyampur | 32976925.5956 | 33207777.7735
|  |  |  | Fatullah. | 230852.178
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 26828491.1678
|  |  |  | Fatullah | 986985.218
|  |  |  | Shyampur | 25841505.9498
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 6015853.056 | 18754211.36
|  |  |  | Jurain | 12738358.304
| 8 | Postogola 33/11KV S/S |  | Jurain | 7685364.3287 | 15490948.95
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 7805584.6213
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 8166465.0182 | 9435249.3386
|  |  |  | Narayanganj (West) | 1463880.2614
|  |  |  | Shitalakhy | 1268784.3203
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 1087576.9002 | 12646887.6127
|  |  |  | Shitalakhy | 9131788.651
|  |  |  | Narayanganj (West) | 2423811.1376
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 3710.9239
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 774957.8804
| 11 |  |  | Narayanganj (West) | 16506085.6729 | 17281043.5532
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 14956868.8684 | 14956868.8684
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 11299390.4922 | 11299390.4922
|  |  |  | Matuail | 379449.435
| 14 | Sarulia 33/11KV S/S |  | Demra | 12826265.6913 | 14871216.0485
|  |  |  | Matuail | 2044950.3572
|  | Demra 33/11KV S/S |  | Matuail | 6435390.6556 | 19436755.156
| 15 |  |  | Demra | 2065622.659
|  |  |  | Siddhirganj | 10935741.8414
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1062004.8821
| 16 |  |  | Narayanganj (East) | 5229145.888 | 12314104.2684
|  |  |  | Narayanganj (West) | 7084958.3804
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 3089998.2607 | 14558710.2159
|  |  |  | Narayanganj (East) | 11468711.9552
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 5620685.8527 | 17435727.8358
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 352028.2612
|  |  |  | Fatullah | 3354580.3961
|  |  |  | Matuail | 8108433.3257
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 3079152 | 3079152
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 468459.6796
|  |  |  | Maniknagar | 9313700.4 | 9313700.4
|  | IG Gate 33/11 kv |  | Swamibagh | 5091696 | 15542230
|  |  |  | Banglabazr | 4613724
|  |  |  | Postogola | 5836810
|  | Motijil 33/11kv |  | kamlapur | 5853926.8778 | 6248963.7
|  |  |  | RAMNA | 395036.8222
|  | Mitford 33/11kv |  | Banshal | 6851266.6542 | 7292692.8
|  |  |  | Lalbagh | 441426.1458
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 4557677.5276 | 11324749.5417
|  |  |  | Fatullah | 3937430.8484
|  |  |  | Matuail | 2829641.1657
|  | MI CEMENT |  | Shitalakhy | 12340320 | 12340320
|  | Dapa 33/11 kV |  | Fatullah | 14568960 | 14568960
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7087905.6432 | 14673871.1611
|  |  |  | Siddhirganj | 7585965.5179
|  | Amulia 33/11 KV SS |  | Mugdapara | 1514269.7663 | 6437597.0631
|  |  |  | Demra | 4923327.2969
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 11377182.2174
|  | P&T 33/11 KV SS |  | Motijeel | 2597322.322
|  |  |  | RAMNA | 2692954.2445
|  |  |  | Rajarbagh | 2473204.2948
|  | Kazla 132/33 KV SS |  | Kazla | 17341874.3974
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 3664557.6953
|  |  |  | Motijeel | 2075442.3047
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 12207376.3932
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 2611776.377
|  |  |  | Swamibagh | 1162631.4015
|  |  |  | Narinda | 196586.015
|  | 132 KV Shah Cement |  | Sitalakhya | 13884000
|  | 132 KV Metro Rail |  | Motijeel | 1216320
|  |  |  | Total=> | 488520790.2489 | 375965340.1037
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 488520790.2489
| Diff zone&Nocs |  |  |  | 24078452.0762
|  |  |  | Diff= | 0

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 26821171.9379 | 26821171.9379 | 0 | 0
Kakrail | 20593626.1987 | 20593626.1987 | 0 | 0
Moghbazar | 15252399.5754 | 15252399.5754 | 0 | 0
Khilgaon | 12685842.0352 | 12685842.0352 | 0 | 0
Satmosjid | 17020995.2428 | 17020995.2428 | 0 | 0
Sherebanglanagar | 18349952.7941 | 18349952.7941 | 0 | 0
Dhanmondi | 17445142.2053 | 17445142.2053 | 0 | 0
Jhigatala | 21955056.5988 | 21955056.5988 | 0 | 0
Azimpur | 15774856.9994 | 15774856.9994 | 0 | 0
Paribagh | 26658917.0753 | 26658917.0753 | 0 | 0
Shyamoli | 13993395.6523 | 13993395.6523 | 0 | 0
Adabor | 24675894.9005 | 24675894.9005 | 0 | 0
Lalbagh | 34548667.0633 | 34548667.0633 | 0 | 0
Kamrangirchar | 37490818.0675 | 37490818.0675 | 0 | 0
Ramna | 21620213.0472 | 21620213.0472 | 0 | 0
Rajarbagh | 13993106.5411 | 13993106.5411 | 0 | 0
Bashabo | 11054667.4475 | 11054667.4475 | 0 | 0
Bonoseeri | 19047800.3557 | 19047800.3557 | 0 | 0
Motijheel | 19118019.4179 | 19118019.4179 | 0 | 0
Mughdapara | 14984837.3823 | 14984837.3823 | 0 | 0
Banglabazar | 14621588.0922 | 14621588.0922 | 0 | 0
Bongshal | 16109427.3226 | 16109427.3226 | 0 | 0
Narinda | 11735087.3128 | 11735087.3128 | 0 | 0
Swamibagh | 12337258.8148 | 12337258.8148 | 0 | 0
Kazla | 36372517.6492 | 36372517.6492 | 0 | 0
Maniknagar | 16666821.9883 | 16666821.9883 | 0 | 0
Shyampur | 71763111.7333 | 71763111.7333 | 0 | 0
Matuail | 21302879.4636 | 20707811.4636 | -595068 | -2.8736
Postogola | 13642394.6213 | 13642394.6213 | 0 | 0
Jurain | 25358861.5907 | 25953929.5907 | 595068 | 2.2928
Narayangonj-West | 30568733.713 | 30568733.713 | 0 | 0
Narayangonj-East | 30494026.2393 | 30494026.2393 | 0 | 0
Damra | 19815215.6472 | 19815215.6472 | 0 | 0
Siddhirgonj | 44777966.7198 | 44777966.7198 | 0 | 0
Fatulla | 31245273.6587 | 31245273.6587 | 0 | 0
Shitalakha | 65129277.2683 | 65129277.2683 | 0 | 0
TOTAL=> | 865025822.3734 | 865025822.3734 | 0 | 0

## Linked_11KV
SL | Feeder_Name | FEEDER_NO | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | SUBSTN_CODE | October23_Consumption | September23_Consumption | August23_Consumption | July23_Consumption | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 10517508 | 11634850 | 1117342 | 1 | 0 | 1117342 | 1117275.2423 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1327224.0724 | 1457854.4301 | 1314371.1616 | 1273734.3863 | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | C301M | 11 | 0 | HA021100463-02 | 1 | 52334628 | 53414203 | 1079575 | 1 | 0 | 1079575 | 1079510.4987 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1506112.4428 | 1598079.2811 | 1562022.8871 | 1571851.4764 | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | C3011 | 11 | 0 | HA021101078-02 | 1 | 66739049 | 67706878 | 967829 | 1 | 0 | 967829 | 967771.1752 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1200141.0854 | 2105982.2036 | 2198394.2713 | 2202528.7234 | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 | 0 | DHK60882 | 1 | 236770.81 | 242194.26 | 5423.45 | 60 | 0 | 325407 | 325387.5579 | Paribag | Dhanmondi 33/11KV S/S | 1 | 424694.4888 | 424650.6487 | 429515.8245 | 406161.3393 | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | C301P | 11 | 0 | DHK60889 | 1 | 294533.1518 | 296567.58 | 2034.4282 | 60 | 0 | 122065.6901 | 122058.3971 | Paribag | Dhanmondi 33/11KV S/S | 1 | 224979.6606 | 224715.2737 | 240975.4757 | 236479.8549 | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 0 | 11 | 0 | DHK60890 | 1 | 720.79 | 726.52 | 5.73 | 60000 | 0 | 343800 | 343779.459 | Paribag | Dhanmondi 33/11KV S/S | 1 | 423304.2367 | 422384.6367 | 444161.7425 | 451511.4107 | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | D301H | 11 | 0 | DHK60880 | 1 | 576270.3 | 581064.2 | 4793.9 | 60 | 0 | 287634 | 287616.8148 | Ramna | Dhanmondi 33/11KV S/S | 1 | 330665.314 | 381236.2759 | 740264.9629 | 797710.3468 | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 0 | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0
9 | 11 kV TSC Feeder | D301U | 11 | 0 | DHK60873 | 1 | 956639.98 | 963916.78 | 7276.8 | 60 | 0 | 436608 | 436581.914 | Ramna | Dhanmondi 33/11KV S/S | 1 | 552858.9173 | 527789.8466 | 622520.63 | 596411.0072 | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | C301S | 11 | 0 | DHK60883 | 1 | 28791.31 | 28971.13 | 179.82 | 60 | 0 | 10789.2 | 10788.5554 | Paribag | Dhanmondi 33/11KV S/S | 1 | 14763.0376 | 14899.4821 | 7435.3517 | 6184.9227 | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 0 | 11 | 0 | DHK60871 | 1 | 549657.1 | 563612.73 | 13955.63 | 60 | 0 | 837337.8 | 837287.7716 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1020090.0393 | 1178402.3777 | 1167367.0478 | 1168612.8044 | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | C301E | 11 | 0 | DHK60981 | 1 | 131190.1 | 143677.95 | 12487.85 | 60 | 0 | 749271 | 749226.2334 | Paribag | Dhanmondi 33/11KV S/S | 1 | 894951.6314 | 961999.4403 | 1097238.176 | 1271574.285 | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | C301D | 11 | 0 | DHK61110 | 1 | 480431.1 | 501237.66 | 20806.56 | 60 | 0 | 1248393.6 | 1248319.0123 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1468536.7336 | 1572278.7706 | 1519703.9096 | 1444426.5973 | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 0 | 11 | 0 | DHK61115 | 1 | 426855.1 | 449664.26 | 22809.16 | 60 | 0 | 1368549.6 | 1368467.8334 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1667970.4775 | 1771267.2548 | 1745625.9685 | 1732224.4313 | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | D301M | 11 | 0 | DHK61107 | 1 | 554305.25 | 556021.54 | 1716.29 | 60 | 0 | 102977.4 | 102971.2474 | Ramna | Dhanmondi 33/11KV S/S | 1 | 132172.5149 | 123208.813 | 139745.6654 | 147111.9421 | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 0 | 11 | 0 | DHK61112 | 1 | 352032.55 | 354429.92 | 2397.37 | 60 | 0 | 143842.2 | 143833.6059 | Paribag | Dhanmondi 33/11KV S/S | 1 | 183722.5048 | 209615.174 | 205991.8784 | 207014.0635 | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | C601R | 11 | 0 | DHK61108 | 1 | 746291.96 | 756877.47 | 10585.51 | 60 | 0 | 635130.6 | 635092.6529 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 850234.9813 | 921150.1931 | 935875.2367 | 955769.4815 | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 0 | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0 | 0
19 | 11 kV DPH Sw/S-1 | 0 | 11 | 0 | DHK60978 | 1 | 826536.1 | 838049.17 | 11513.07 | 60 | 0 | 690784.2 | 690742.9278 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 869594.4982 | 880434.4894 | 909712.3671 | 894673.7786 | 964542.5031 | 717844.627
20 | WASA Bhaban | C605M | 11 | 0 | 8536188 | 1.18 | 271216 | 271216 | 0 | 1000 | 935160 | 935160 | 933040.8402 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1122893.6635 | 1128091.0061 | 1031848.2658 | 1051553.1772 | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 0 | 11 | 0 | 8536178 | 1.18 | 581779 | 586004 | 4225 | 44 | 0 | 219362 | 218864.9052 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 224818.1088 | 56030.9835 | 205730.3432 | 203697.4272 | 26163.5003 | 291323.9838
22 | Air Port Road (West) | D505A | 11 | 0 | 8536182 | 1.18 | 4157.6 | 4761.7 | 604.1 | 1000 | 0 | 712838 | 711222.6426 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1042454.0487 | 996313.4361 | 1009777.8086 | 1128128.4372 | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | C172C | 11 | 0 | 8536193 | 1.18 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0
24 | (UTC) Tower | D505U | 11 | 0 | DHK00183 | 1.18 | 17563.9 | 18092.4 | 528.5 | 444.44 | 0 | 277166.1172 | 276538.0329 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 285253.3218 | 290292.9413 | 349161.1513 | 363430.7232 | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | C605O | 11 | 0 | 8536190 | 1.18 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 47083.68 | 46976.984 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 110790.7123 | 63163.9823 | 0 | 0
26 | Panthopath | D505P | 11 | 0 | 8536184 | 1.18 | 38266.9 | 39056.5 | 789.6 | 1000 | 0 | 931728 | 929616.6174 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1035454.7302 | 1172086.0871 | 1196734.0813 | 1204221.3334 | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | C605N | 11 | 0 | DHK00190 | 1.18 | 57079.4 | 57494.3 | 414.9 | 444.44 | 0 | 217589.8241 | 217096.7452 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 236270.9269 | 238706.8937 | 200780.8678 | 155748.3677 | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 0 | 11 | 0 | DHK00021 | 1.18 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0
29 | Aux. Transformer, AT-1 | 0 | 11 | 0 | 85-12906 | 1.18 | 69276 | 69426 | 150 | 10 | 0 | 1770 | 1765.989 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 2388.6563 | 2990.8959 | 2900.021 | 3641.847 | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 0 | 11 | 0 | 85-12909 | 1.18 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0 | 0
31 | Police Bhaban | D315I | 11 | 0 | DHK 00005 | 1 | 74130.7 | 74352.7 | 222 | 444.44 | 0 | 98665.68 | 98323.9544 | Ramna | New Ramna 33/11KV S/S | 15 | 113280.4639 | 112636.0604 | 117855.6107 | 121266.9463 | 121013.0538 | 111715.2077
32 | Water Works | 0 | 11 | 0 | DHK 00010 | 1 | 0 | 681.6 | 681.6 | 444.44 | 0 | 302930.304 | 301881.114 | Lalbag | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0
33 | GPO | D3157 | 11 | 0 | DHK 00060 | 1 | 84.7 | 681.6 | 596.9 | 444.44 | 0 | 265286.236 | 264367.4251 | Ramna | New Ramna 33/11KV S/S | 15 | 254768.0345 | 252148.1113 | 248107.5506 | 224260.1714 | 278965.4908 | 233730.721
34 | Culvert Road | D315C | 11 | 0 | 8536184 | 1 | 40096.9 | 40342.5 | 245.6 | 444.44 | 50 | 588546 | 586507.5886 | Ramna | New Ramna 33/11KV S/S | 15 | 1175263.5465 | 1013459.3684 | 1052444.418 | 990314.9211 | 787025.6832 | 769934.2629
35 | Secretariat (East) | D315E | 11 | 0 | DHK00059 | 1 | 81730.6 | 81748.6 | 18 | 444.44 | 0 | 7999.92 | 7972.2125 | Ramna | New Ramna 33/11KV S/S | 15 | 1672.5368 | 765.313 | 950.0836 | 1673.5834 | 2240.1359 | 29358.1395
36 | Siddik Bazar | B615S | 11 | 0 | DHK00076 | 1 | 41750.6 | 45245.7 | 3495.1 | 444.44 | 0 | 1553362.244 | 1547982.2206 | Bangshal | New Ramna 33/11KV S/S | 15 | 1854662.4712 | 1902703.0751 | 1396125.2558 | 499406.3237 | 894134.2296 | 765262.7858
37 | Bokshi Bazar | D315X | 11 | 0 | DHK 00206 | 1 | 90253.3 | 91450.6 | 1197.3 | 444.44 | 0 | 532128.012 | 530285.0026 | Ramna | New Ramna 33/11KV S/S | 15 | 560480.6352 | 561829.7499 | 563173.3752 | 477921.1318 | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 0 | 11 | 0 | DHK00198 | 1 | 50244.2 | 51162 | 917.8 | 444.44 | 0 | 407907.032 | 406494.2583 | Ramna | New Ramna 33/11KV S/S | 15 | 588235.7049 | 500739.7682 | 521233.9697 | 36728.3702 | 1058898.5083 | 1085933.5304
39 | TNT RMU | D315Z | 11 | 0 | DHK 00207 | 1 | 64037.1 | 64922.1 | 885 | 444.44 | 0 | 393329.4 | 391967.1155 | Ramna | New Ramna 33/11KV S/S | 15 | 395125.5127 | 407146.495 | 424144.4724 | 438569.3066 | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 0 | 11 | 0 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 35665.375
41 | Secretariat (West) | D315W | 11 | 0 | DHK 00006 | 1 | 72394.3 | 73143.7 | 749.4 | 444.44 | 0 | 333063.336 | 331909.7812 | Ramna | New Ramna 33/11KV S/S | 15 | 504156.8291 | 472288.1335 | 522274.5375 | 534325.4145 | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 0 | 11 | 0 | DHK00197 | 1 | 89224 | 89232.8 | 8.8 | 444.44 | 0 | 3911.072 | 3897.5261 | Ramna | New Ramna 33/11KV S/S | 15 | 12747.4425 | 1125.4602 | 1246464.4649 | 757545.2503 | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | D315A | 11 | 0 | DHK00186 | 1 | 36023.9 | 38231 | 2207.1 | 444.44 | 0 | 980923.524 | 977526.1249 | Ramna | New Ramna 33/11KV S/S | 15 | 1189218.8524 | 1357169.9895 | 1293561.4671 | 1334026.873 | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | D3153 | 11 | 0 | DHK00030 | 1 | 56404.5 | 56794.4 | 389.9 | 444.44 | 0 | 173287.156 | 172686.9812 | Ramna | New Ramna 33/11KV S/S | 15 | 222492.5951 | 223201.274 | 228427.247 | 210464.4166 | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | D3152 | 11 | 0 | DHK 00008 | 1 | 443.7 | 564 | 120.3 | 444.44 | 0 | 53466.132 | 53280.9537 | Ramna | New Ramna 33/11KV S/S | 15 | 61024.9905 | 71264.1421 | 71075.3031 | 68978.774 | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 0 | 11 | 0 | DHK00196 | 1 | 29086.7 | 29843.6 | 756.9 | 444.44 | 0 | 336396.636 | 335231.5364 | Motijheel | New Ramna 33/11KV S/S | 15 | 454930.0034 | 443071.1857 | 477711.0916 | 494476.0375 | 481492.0598 | 701782.0483
47 | Jail | B678Z | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0 | 0
48 | Kosturi Bazar | D315K | 11 | 0 | HA021100713-02 | 1 | 77199099 | 77199099 | 0 | 1 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 15 | 254911.0541 | 109455.5914 | 110597.9648 | 782852.0054 | 108530.1819 | 101993.6695
49 | Kaptan Bazar | B124K | 11 | 0 | HA021101251-02 | 1 | 7930785 | 8299757 | 368972 | 1 | 0 | 368972 | 367694.0766 | Narinda | New Ramna 33/11KV S/S | 15 | 419318.091 | 424171.1844 | 443349.7565 | 434935.9868 | 427872.7434 | 409490.3581
50 | G.T.V | D315G | 11 | 0 | HA-021101054-02 | 1 | 73543399 | 73968193 | 424794 | 1 | 0 | 424794 | 423322.7388 | Ramna | New Ramna 33/11KV S/S | 15 | 579351.6265 | 620088.9847 | 609639.126 | 653967.7221 | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | B615K | 11 | 0 | HA021100951-02 | 1 | 7837719 | 8159834 | 322115 | 1 | 0 | 322115 | 320999.3644 | Bangshal | New Ramna 33/11KV S/S | 15 | 441368.6747 | 366764.7103 | 373997.3699 | 641935.1027 | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.4 | 0 | 2436 | 1 | 67703 | 67991 | 288 | 10 | 0 | 2880 | 2870.0252 | Ramna | New Ramna 33/11KV S/S | 15 | 2847.8614 | 0 | 0 | 0 | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.4 | 0 | 2437 | 1 | 90000 | 90000 | 0 | 10 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 15 | 4943.0737 | 3443.9428 | 3735.9019 | 3663.8273 | 3672.2594 | 3624.4279
54 | Pioneer | D304P | 11 | 0 | 06604395 | 1 | 24160.1 | 24231.18 | 71.08 | 8000 | 0 | 568640 | 570908.4836 | Ramna | Kakrail 33/11KV S/S | 4 | 784360.9682 | 828175.4667 | 850072.0555 | 872559.2 | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | D604L | 11 | 0 | DHK-00102 | 1 | 92942.8 | 95296.1 | 2353.3 | 444.444 | 0 | 1045910.0652 | 1050082.5289 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1392792.0181 | 1485476.6819 | 1494821.3647 | 1589289.5218 | 1570646.0565 | 1456807.534
56 | Montri Para | C604B | 11 | 0 | DHK-00110 | 1 | 12950.5 | 12973.5 | 23 | 2222.22 | 0 | 51111.06 | 51314.9581 | Kakrail | Kakrail 33/11KV S/S | 4 | 167051.5164 | 197223.0332 | 196663.3629 | 206488.6824 | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 0 | 11 | 0 | 9119865 | 1 | 72383.6 | 73065.6 | 682 | 1000 | 0 | 682000 | 684720.7122 | Kakrail | Kakrail 33/11KV S/S | 4 | 2230006.6883 | 2380457.3749 | 2409184.7946 | 2711345 | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0
59 | High Court | D3046 | 11 | 0 | 1025651 | 1 | 30010.8 | 30191.9 | 181.1 | 1000 | 0 | 181100 | 181822.4648 | Ramna | Kakrail 33/11KV S/S | 4 | 251110.6689 | 202322.6667 | 325169.1484 | 265125 | 281963.0422 | 304725.5352
60 | Secretaiat | 0 | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0 | 0
61 | Shanti Nagar Bazar | D604N | 11 | 0 | 06604402 | 1.1 | 5783.83 | 5809.98 | 26.15 | 40000 | 0 | 1150600 | 1155190.1048 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1443886.346 | 1590213.609 | 1510645.8477 | 1601052 | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 0 | 11 | 0 | 9119867 | 1.1 | 32987.8 | 33058.1 | 70.3 | 1000 | 0 | 77330 | 77638.4937 | Kakrail | Kakrail 33/11KV S/S | 4 | 216622.9377 | 242037.4816 | 236872.8291 | 224220 | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 0 | 11 | 0 | DHK00199 | 1.1 | 79591.4 | 79666.3 | 74.9 | 2222.22 | 0 | 183088.7058 | 183819.1042 | Kakrail | Kakrail 33/11KV S/S | 4 | 639993.908 | 715946.6275 | 682140.9217 | 703183.7413 | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 0 | 11 | 0 | DHK00027 | 1.1 | 57453.2 | 58241 | 787.8 | 2222.22 | 0 | 1925731.4076 | 1933413.755 | Kakrail | Kakrail 33/11KV S/S | 4 | 1067396.9898 | 1227916.0084 | 1208524.4599 | 1467416.3104 | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | D304B | 11 | 0 | D1025656 | 1.1 | 69884.3 | 70601.3 | 717 | 1000 | 0 | 788700 | 791846.372 | Ramna | Kakrail 33/11KV S/S | 4 | 917673.5431 | 1028330.0287 | 1027534.5089 | 1059146.6 | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | D304F | 11 | 0 | D0086137 | 1.1 | 27376 | 27773.3 | 397.3 | 1000 | 0 | 437030 | 438773.4499 | Ramna | Kakrail 33/11KV S/S | 4 | 432945.982 | 472221.3068 | 517539.8234 | 576508 | 916863.5723 | 907912.3538
67 | Judges Complex | C604JC | 11 | 0 | 06604344 | 1.1 | 684.38 | 686.38 | 2 | 40000 | 0 | 88000 | 88351.0596 | Kakrail | Kakrail 33/11KV S/S | 4 | 118357.8949 | 136165.0797 | 135933.8524 | 151904 | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 0 | 11 | 0 | 39333 | 1 | 496195 | 499183 | 2988 | 1 | 0 | 2988 | 2999.9201 | Kakrail | Kakrail 33/11KV S/S | 4 | 3752.665 | 0 | 0 | 0 | 0 | 0
69 | Auxiliary Transformer, AT-2 | 0 | 11 | 0 | 39254 | 1 | 1228762 | 1228762 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 4 | 1874.3332 | 6333.0946 | 25918.4591 | 0 | 0 | 0
70 | 11 kV Jamuna (F1) | C6101JG | 11 | 0 | BD017073 | 1 | 0.4073 | 0.4177 | 0.0104 | 2000 | 0 | 20.8 | 20.9345 | Kakrail | BSMMU 33/11KV S/S | 101 | 34.3292 | 8.7511 | 22.0654 | 24.7258 | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | C6101PP | 11 | 0 | BD017074 | 1 | 2992.52 | 3012.43 | 19.91 | 2000 | 0 | 39820 | 40077.555 | Kakrail | BSMMU 33/11KV S/S | 101 | 42742.7844 | 43083.9288 | 43219.8277 | 44627.1399 | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 | 0 | BD017075 | 1 | 1854.6 | 1878.4 | 23.8 | 2000 | 0 | 47600 | 47907.8759 | Kakrail | BSMMU 33/11KV S/S | 101 | 87211.9487 | 84458.3395 | 31822.749 | 77353.7092 | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 | 0 | BD017076 | 1 | 3278.62 | 3350.25 | 71.63 | 2000 | 0 | 143260 | 144186.603 | Kakrail | BSMMU 33/11KV S/S | 101 | 174503.2711 | 172111.8499 | 179215.5198 | 177543.6485 | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 | 0 | BD017077 | 1 | 15411.85 | 15660.41 | 248.56 | 2000 | 0 | 497120 | 500335.3629 | Kakrail | BSMMU 33/11KV S/S | 101 | 627271.1967 | 702896.8986 | 697529.5567 | 750881.7825 | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | C6101NH | 11 | 0 | BD017078 | 1 | 27649.1 | 27893.89 | 244.79 | 2000 | 0 | 489580 | 492746.5943 | Kakrail | BSMMU 33/11KV S/S | 101 | 733453.4805 | 641089.6752 | 636961.0675 | 681006.1346 | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | C31016 | 11 | 0 | BD017079 | 1 | 34271.31 | 34847.13 | 575.82 | 2000 | 0 | 1151640 | 1159088.7861 | Paribag | BSMMU 33/11KV S/S | 101 | 1451369.5422 | 1603019.2834 | 1597412.9298 | 1675286.7504 | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 | 0 | BD017080 | 1 | 7006.17 | 7150.9 | 144.73 | 2000 | 0 | 289460 | 291332.2219 | Paribag | BSMMU 33/11KV S/S | 101 | 378930.46 | 414273.243 | 428837.8596 | 457910.6397 | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 | 0 | BD017083 | 1 | 2501.72 | 2558.44 | 56.72 | 2000 | 0 | 113440 | 114173.7278 | Paribag | BSMMU 33/11KV S/S | 101 | 135094.1858 | 140648.5745 | 143344.075 | 137962.1897 | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | C6101RT | 11 | 0 | BD017084 | 1 | 1616.91 | 1722.15 | 105.24 | 2000 | 0 | 210480 | 211841.3807 | Kakrail | BSMMU 33/11KV S/S | 101 | 253083.3205 | 267336.0837 | 281930.9324 | 302057.3893 | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 | 0 | BD017085 | 1 | 2282.95 | 2325.72 | 42.77 | 2000 | 0 | 85540 | 86093.2711 | Kakrail | BSMMU 33/11KV S/S | 101 | 101598.4476 | 113805.0685 | 114841.2565 | 122402.9977 | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | C3101RM | 11 | 0 | BD017086 | 1 | 2299.99 | 2390.79 | 90.8 | 2000 | 0 | 181600 | 182774.5854 | Paribag | BSMMU 33/11KV S/S | 101 | 159898.4943 | 165660.4538 | 173668.8065 | 174287.0734 | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 | 0 | BD017087 | 1 | 4503.32 | 4595.64 | 92.32 | 2000 | 0 | 184640 | 185834.2481 | Paribag | BSMMU 33/11KV S/S | 101 | 231553.1807 | 239475.0074 | 241970.3048 | 234654.3262 | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 | 0 | BD017088 | 1 | 1117.1 | 1140.23 | 23.13 | 2000 | 0 | 46260 | 46559.2088 | Paribag | BSMMU 33/11KV S/S | 101 | 60542.3562 | 62295.6571 | 66843.9677 | 56065.3573 | 59004.3933 | 75292.0174
84 | Spare | 0 | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 0 | 0 | 0 | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | C310113 | 11 | 0 | BD017090 | 1 | 2155.2 | 2367.14 | 211.94 | 2000 | 0 | 423880 | 426621.648 | Paribag | BSMMU 33/11KV S/S | 101 | 459157.5154 | 528668.5024 | 530318.42 | 510819.9335 | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKD4418 | 1 | 2965 | 3035.81 | 70.81 | 100 | 0 | 7081 | 7126.7998 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 6033.1746 | 14842.5188 | 15407.4195 | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 1877.04 | 1915.93 | 38.89 | 100 | 0 | 3889 | 3914.154 | Paribag | BSMMU 33/11KV S/S | 101 | 12158.0799 | 8446.8515 | 487.8678 | 0 | 0 | 0
88 | Chata Mosjid | 0 | 11 | 0 | 0 | 1 | 178961 | 182187.1 | 3226.1 | 1000 | 0 | 3226100 | 3224151.7427 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 109 | 2448059.1892 | 2307606.3907 | 2543835.8742 | 2199148.6226 | 2319503.7751 | 2426211.3577
89 | AC mosjid | A3109X | 11 | 0 | 0 | 1 | 10394.041 | 11622.59 | 1228.549 | 1000 | 0 | 1228549 | 1227807.0733 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1300312.4106 | 1258989.8828 | 1405178.1975 | 1152835.6866 | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | A3109K | 11 | 0 | 0 | 1 | 27738.754 | 29890.208 | 2151.454 | 1000 | 0 | 2151454 | 2150154.7266 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2361420.5589 | 2255488.3746 | 2390177.1556 | 2000565.9387 | 2224217.61 | 2267338.6868
91 | Nazimuddin | A3109M | 11 | 0 | 0 | 1 | 7287.9168 | 7907.4712 | 619.5544 | 1000 | 0 | 619554.4 | 619180.2481 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 762703.8683 | 950975.5456 | 925339.67 | 477977.0793 | 0 | 0
92 | Kamal Bagh | A3109U | 11 | 0 | 0 | 1 | 20174.008 | 21734.92 | 1560.912 | 1000 | 0 | 1560912 | 1559969.3577 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2099983.5161 | 1567737.0505 | 1686096.534 | 1618577.1268 | 1589844.4629 | 1583845.5588
93 | Rahamatganj | A3109B | 11 | 0 | 0 | 1 | 18036.49 | 20350.666 | 2314.176 | 1000 | 0 | 2314176 | 2312778.458 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2488587.0183 | 2323808.6258 | 2495628.7814 | 2157043.5386 | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 0 | 11 | 0 | 0 | 1 | 4448.2884 | 6144.4552 | 1696.1668 | 1000 | 0 | 1696166.8 | 1695142.4767 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1852690.3414 | 1787173.2312 | 1980277.4376 | 1747210.9883 | 1862323.276 | 1854345.8684
95 | City Colony | A3109J | 11 | 0 | 0 | 1 | 1465.432 | 3450.24 | 1984.808 | 1000 | 0 | 1984808 | 1983609.3649 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2200330.7905 | 2079469.3659 | 2219309.3581 | 1859682.1079 | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 0 | 11 | 0 | 0 | 1 | 7701.988 | 10455.924 | 2753.936 | 1000 | 0 | 2753936 | 2752272.8848 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2717279.1674 | 2859477.1699 | 2599114.1368 | 2790703.3917 | 2997202.1128 | 3092062.2371
97 | Chun Goli | A3109H | 11 | 0 | 0 | 1 | 1678.5962 | 2584.3304 | 905.7342 | 1000 | 0 | 905734.2 | 905187.2228 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 976536.6596 | 927964.1813 | 983357.245 | 754718.4448 | 841380.8401 | 894878.3402
98 | Alir Ghat | A3109L | 11 | 0 | 0 | 1 | 127347 | 129316.3 | 1969.3 | 1000 | 0 | 1969300 | 1968110.7302 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2047969.8743 | 1928133.7897 | 2137361.0725 | 1734165.991 | 1904122.5273 | 2096766.6729
99 | Club Ghat | A3109C | 11 | 0 | 0 | 1 | 24630.07 | 27337.512 | 2707.442 | 1000 | 0 | 2707442 | 2705806.9627 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2856757.5327 | 2651623.7603 | 2977501.1852 | 2317579.0304 | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | A3109V | 11 | 0 | 0 | 1 | 1744.5846 | 4371.9 | 2627.3154 | 1000 | 0 | 2627315.4 | 2625728.7516 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2710169.0726 | 2405552.6316 | 2718263.3522 | 2261609.1864 | 2437761.5097 | 2619436.8857
101 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 0 | 0 | 0 | 0 | 0 | 0
102 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
103 | Sowari Ghat | A319R | 11 | 0 | 8838019 | 1 | 83080.1 | 83080.1 | 0 | 1000 | Estimated | 2827636.56 | 2836655.3487 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2802102.8851 | 2638720.3862 | 2802348.4469 | 2329233.6447 | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | A3202 | 11 | 0 | 8838014 | 1 | 82569.1 | 82569.1 | 0 | 1000 | Estimated | 541462.32 | 543189.3221 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 622689.53 | 658473.4491 | 560200.422 | 121854.324 | 118483.0867 | 132959.886
105 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
106 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
107 | Eidgah | A320A | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1203249.6 | 1207087.3824 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1369916.966 | 1376808.1209 | 1431623.3008 | 1096688.9157 | 1303313.9541 | 1329598.8604
108 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
109 | Modumoti | A3201 | 11 | 0 | 0 | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 2045524.32 | 2052048.5501 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2241682.3081 | 1975420.3474 | 2116312.7055 | 1584106.2116 | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | A320Y | 11 | 0 | 61389152 | 1 | 442711 | 443210 | 499 | 1000 | Estimated | 962599.68 | 965669.9059 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1120841.154 | 1197224.4529 | 1244889.8267 | 1181986.9425 | 1066347.7806 | 1087853.6131
111 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
112 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
113 | Water Works 11 kV Sw/S-2 | A320G | 11 | 0 | 61389109 | 1 | 404617 | 405569 | 952 | 1000 | 0 | 952000 | 955036.4181 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 858393.0961 | 972107.7743 | 1045286.2834 | 874589.6653 | 951212.9635 | 980831.1601
114 | Islambagh | A320D | 11 | 0 | 61389186 | 1 | 502493 | 503360 | 867 | 1000 | 0 | 867000 | 869765.3094 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 693124.8804 | 855693.6396 | 941158.1479 | 774407.5731 | 861627.8273 | 876487.4197
115 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
116 | WASA Low Lift Pump | A320F | 11 | 0 | 61389202 | 1 | 15689 | 15746 | 57 | 1000 | 0 | 57000 | 57181.8023 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 43069.8986 | 55719.5858 | 56068.996 | 57103.7926 | 61401.0484 | 45712.4958
117 | Shahi Mosjid | D920M | 11 | 0 | 06604459 | 1 | 36418.54 | 36593.61 | 175.07 | 8000 | 0 | 1400560 | 1405027.1069 | Azimpur | Lalbagh Old 33/11KV S/S | 20 | 1328075.3488 | 1734152.7099 | 1661564.6485 | 1773623.7611 | 1752245.002 | 1250534.8854
118 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | 5395822 | 1 | 60635.8 | 67756.97 | 7121.17 | 1 | 0 | 7121.17 | 7143.8831 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 13347.8624 | 8792.8491 | 9867.6427 | 0 | 0 | 0
120 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0
121 | Spare | 0 | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0
122 | Chawk Bazar | A319Z | 11 | 0 | DHK-60904 | 1 | 997275.1 | 1004599.4 | 7324.3 | 60 | 0 | 439458 | 440824.2804 | Lalbag | Mitford 33/11 kV | 88 | 524398.7147 | 501841.8638 | 526171.1474 | 480516.9276 | 522405.3875 | 508276.2976
123 | Spare | 0 | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0
124 | Chatrabas | B688D | 11 | 0 | DHK-66485 | 1 | 863260 | 867960 | 4700 | 60 | 0 | 282000 | 282876.7415 | Bangshal | Mitford 33/11 kV | 88 | 339280.009 | 1110389.3159 | 1353014.9285 | 1237900.3837 | 762976.1234 | 353557.5482
125 | Begum Bazar | B678G | 11 | 0 | DHK-66481 | 1 | 3787572 | 3818719 | 31147 | 60 | 0 | 1868820 | 1874630.1846 | Bangshal | Mitford 33/11 kV | 88 | 2344342.8516 | 2422961.4211 | 2446646.3554 | 2397460.098 | 2421237.7604 | 2357293.0663
126 | SCC ROAD | B688R | 11 | 0 | DHK-60901 | 1 | 157171.5 | 179474.4 | 22302.9 | 60 | 0 | 1338174 | 1342334.3996 | Bangshal | Mitford 33/11 kV | 88 | 1631812.3089 | 1626362.4279 | 1682445.687 | 1526989.2348 | 1650255.6547 | 1574186.7645
127 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0
128 | Armanitola | B619A | 11 | 0 | DHK-61104 | 1 | 733048.2 | 745406.5 | 12358.3 | 60 | 0 | 741498 | 743803.3265 | Bangshal | Mitford 33/11 kV | 88 | 925763.6241 | 975265.6139 | 991422.0466 | 974917.2355 | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 0 | 11 | 0 | DHK-61101 | 1 | 418515.6 | 425420.5 | 6904.9 | 60 | 0 | 414294 | 415582.0452 | Bangshal | Mitford 33/11 kV | 88 | 494194.5928 | 534862.6587 | 551030.4718 | 539101.6117 | 513839.5885 | 528540.0121
130 | Emamganj | B688I | 11 | 0 | DHK-68130 | 1 | 1478.28 | 1494.26 | 15.98 | 60000 | 0 | 958800 | 961780.9211 | Bangshal | Mitford 33/11 kV | 88 | 1149360.3885 | 350737.4618 | 168709.5633 | 161982.5873 | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | A319T | 11 | 0 | DHK-68129 | 1 | 1226.82 | 1226.83 | 0.01 | 60000 | 0 | 600 | 601.8654 | Lalbag | Mitford 33/11 kV | 88 | 0 | 0 | 84652.8551 | 538371.2175 | 628439.5052 | 594724.3345
132 | Spare | 0 | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0 | 0
133 | Panghat | B688P | 11 | 0 | DHK-68127 | 1 | 1597.26 | 1617.63 | 20.37 | 60000 | 0 | 1222200 | 1225999.835 | Bangshal | Mitford 33/11 kV | 88 | 1414831.0491 | 1293419.2063 | 1420021.8363 | 1363598.8715 | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | U0004460 | 1 | 5717.83 | 5760.29 | 42.46 | 100 | 0 | 4246 | 4259.2009 | Bangshal | Mitford 33/11 kV | 88 | 4363.7626 | 4064.0057 | 3905.7556 | 3927.8323 | 4152.4762 | 4434.1352
135 | Chadni chwok | 0 | 11 | 0 | DHK60916 | 1 | 444571 | 454152 | 9581 | 60 | 0 | 574860 | 585337.5096 | Paribag | Azimpur 33/11 KV | 66 | 659849.4891 | 735121.5421 | 735452.5478 | 623153.8648 | 792142.0147 | 648152.1238
136 | BGB | 0 | 11 | 0 | DHK61090 | 1 | 714040 | 716307 | 2267 | 60 | 0 | 136020 | 138499.1268 | Jigatola | Azimpur 33/11 KV | 66 | 715312.2841 | 771727.6444 | 791117.6745 | 677536.8748 | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | D920P | 11 | 0 | DHK61091 | 1 | 888592 | 919902 | 31310 | 60 | 0 | 1878600 | 1912839.727 | Azimpur | Azimpur 33/11 KV | 66 | 2177491.1776 | 2180695.2965 | 2262756.8158 | 2133225.2763 | 2225341.7622 | 2144033.6462
138 | Azimpur | D901P | 11 | 0 | DHK61086 | 1 | 356695 | 383398 | 26703 | 60 | 0 | 1602180 | 1631381.6426 | Azimpur | Azimpur 33/11 KV | 66 | 1038683.4379 | 1153765.578 | 1156672.3968 | 1153479.4596 | 1136633.6642 | 1104066.6214
139 | Aazd | D901Z | 11 | 0 | DHK61089 | 1 | 47477 | 64260 | 16783 | 60 | 0 | 1006980 | 1025333.4123 | Azimpur | Azimpur 33/11 KV | 66 | 1260231.211 | 1354793.0694 | 1347891.2826 | 1333174.551 | 1318714.278 | 1257709.9294
140 | Dayra Sharif | D966D | 11 | 0 | DHK61088 | 1 | 566604 | 579254 | 12650 | 60 | 0 | 759000 | 772833.6808 | Azimpur | Azimpur 33/11 KV | 66 | 1018901.3032 | 1035744.5659 | 1040264.9944 | 1036318.7466 | 1007533.0284 | 980271.2172
141 | Naya palton | D966U | 11 | 0 | DHK86065 | 1 | 1983.32 | 2006.64 | 23.32 | 60000 | 0 | 1399200 | 1424702.0899 | Azimpur | Azimpur 33/11 KV | 66 | 1594707.0602 | 1776436.6019 | 1764768.0283 | 1711787.3638 | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | D966V | 11 | 0 | DHK66477 | 1 | 1680319 | 1696824 | 16505 | 60 | 0 | 990300 | 1008349.3994 | Azimpur | Azimpur 33/11 KV | 66 | 1357200.0802 | 1489035.8491 | 1488032.8269 | 1499973.4477 | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | D966W | 11 | 0 | DHK66480 | 1 | 4079743 | 4107768 | 28025 | 60 | 0 | 1681500 | 1712147.3443 | Azimpur | Azimpur 33/11 KV | 66 | 1414604.6799 | 1497238.5543 | 1598200.8415 | 1506117.3895 | 1034936.4652 | 1287496.6695
144 | Lalbagh | D920L | 11 | 0 | DHK61093 | 1 | 844380 | 874634 | 30254 | 60 | 0 | 1815240 | 1848324.9154 | Azimpur | Azimpur 33/11 KV | 66 | 2271183.2515 | 2469993.6901 | 2465781.6021 | 2471750.3893 | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | D366J | 11 | 0 | DHK66497 | 1 | 1273675 | 1281591 | 7916 | 60 | 0 | 474960 | 483616.7128 | Ramna | Azimpur 33/11 KV | 66 | 594434.9453 | 771237.9306 | 746279.7208 | 668533.8709 | 616760.0188 | 675859.2968
146 | Eden College | D966E | 11 | 0 | DHK60917 | 1 | 957512 | 962562 | 5050 | 60 | 0 | 303000 | 308522.5366 | Azimpur | Azimpur 33/11 KV | 66 | 489031.3622 | 487693.6736 | 503127.1069 | 450271.8574 | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | D902N | 11 | 0 | DHK60918 | 1 | 510949 | 519580 | 8631 | 60 | 0 | 517860 | 527298.6165 | Azimpur | Azimpur 33/11 KV | 66 | 634848.7543 | 693863.1593 | 681133.1714 | 683984.9722 | 653358.8311 | 648152.1238
148 | BUET | D366BU | 11 | 0 | DHK66496 | 1 | 1008669 | 1015739 | 7070 | 60 | 0 | 424200 | 431931.5513 | Ramna | Azimpur 33/11 KV | 66 | 807548.0045 | 1180516.1912 | 815830.544 | 798043.2987 | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIG2780 | 1 | 401869 | 404836 | 2967 | 1 | 0 | 2967 | 3021.0771 | Azimpur | Azimpur 33/11 KV | 66 | 4277.027 | 4444.1522 | 3986.2756 | 4092.9197 | 4399.774 | 2203.9333
150 | Rasulpur | F120R | 11 | 0 | HA-021101042-02 | 1 | 96619539 | 97733809 | 1114270 | 1 | 0 | 1114270 | 1135070.1317 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1665082.8173 | 1532049.0872 | 1584215.5272 | 1403442.4135 | 1475786.882 | 1248201.2259
151 | Bheribadh | F120B | 11 | 0 | HA-021101105-02 | 1 | 71909539 | 74035356 | 2125817 | 1 | 0 | 2125817 | 2165499.7281 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2508479.0993 | 2458320.6942 | 2620926.9562 | 2327005.5404 | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 | 0 | 30799521 | 1 | 2651.27 | 2655.72 | 4.45 | 60000 | 0 | 267000 | 271984.1018 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 253194.3598 | 408741.1592 | 362911.631 | 314576.4303 | 364934.8739 | 488122.7019
153 | Panna Battery Express | F140E | 11 | 0 | DHK15431 | 1 | 5329.54 | 5345.3 | 15.76 | 60000 | 0 | 945600 | 963251.5607 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 788120.5732 | 1093857.5249 | 1220535.5698 | 1068349.9537 | 1060687.1709 | 1118589.0702
154 | Eidgah | F140I | 11 | 0 | 30799460 | 1 | 5487.62 | 5523.86 | 36.24 | 60000 | 0 | 2174400 | 2214989.6293 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2418400.8037 | 2321919.4185 | 2480917.8558 | 2121576.0406 | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | D840L | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 40 | 0 | 0 | 0 | 0 | 0 | 0
156 | Huzur Para | F140H | 11 | 0 | HA-021101055-02 | 1 | 7396376 | 9989092 | 2592716 | 1 | 0 | 2592716 | 2641114.3542 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2153483.8082 | 1914978.8856 | 2163917.8156 | 1832748.4977 | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | F103K | 11 | 0 | HA-021101015-02 | 1 | 27010939 | 29348087 | 2337148 | 1 | 0 | 2337148 | 2380775.6541 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2064906.2609 | 1863929.1371 | 2041804.9994 | 1873617.2189 | 1726065.7983 | 1737567.1439
158 | Munshihati | F140T | 11 | 0 | HA-021100854-02 | 1 | 55432498 | 56404546 | 972048 | 1 | 0 | 972048 | 990193.2667 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1294711.6864 | 1345431.4782 | 1376742.8712 | 1392932.3343 | 1212171.698 | 1205376.9608
159 | Jhawchar | F140J | 11 | 0 | HA-021101028-02 | 1 | 4801619 | 6004029 | 1202410 | 1 | 0 | 1202410 | 1224855.4453 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1505628.0528 | 1566579.6466 | 1562224.2267 | 1438582.214 | 1425641.3374 | 1328999.0751
160 | RMU Express | F140D | 11 | 0 | HA-021101248-02 | 1 | 7971838 | 8590513 | 618675 | 1 | 0 | 618675 | 630223.836 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 713470.7397 | 717231.4507 | 658611.0471 | 606779.6203 | 633839.2782 | 704501.3661
161 | Koyla Ghat | F140C | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 2067758.28 | 2106357.2232 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1907872.1438 | 2053915.4269 | 2183072.3937 | 1900877.505 | 2223108.4368 | 1816011.9444
162 | Muslimbagh | F140M | 11 | 0 | HA-021100908-02 | 1 | 31186206 | 34050945 | 2864739 | 1 | 0 | 2864739 | 2918215.2206 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1684632.0125 | 1681378.5129 | 1753494.5949 | 1596522.772 | 1696945.1326 | 1737474.4882
163 | Noyagaon | F140Y | 11 | 0 | HA-021101087-02 | 1 | 13945688 | 16193892 | 2248204 | 1 | 0 | 2248204 | 2290171.3321 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2533643.7042 | 2800404.9743 | 2891878.4964 | 2674100.301 | 2742632.8101 | 2660587.4202
164 | Nurbagh | F140N | 11 | 0 | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2250207.54 | 2292212.2723 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2098659.3582 | 2062025.6114 | 2315958.5809 | 1868573.9135 | 2159293.4513 | 2300317.433
165 | Ali Nagar | F140A | 11 | 0 | HA-021101022-02 | 1 | 29006769 | 30998173 | 1991404 | 1 | 0 | 1991404 | 2028577.6342 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2162413.4126 | 2438442.3104 | 2505512.4752 | 2290198.0816 | 2360084.8023 | 2402380.2856
166 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
167 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
168 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
169 | Nababgonj Park | D920K | 11 | 0 | 0 | 1 | 12267110 | 12523740 | 256630 | 1 | 0 | 256630 | 257344.0613 | Azimpur | BGB 33/11 KV S/S | 104 | 1028840.1279 | 1022665.2071 | 1042273.5833 | 1021134.2367 | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | F1104O | 11 | 0 | 0 | 1 | 85905840 | 88803750 | 2897910 | 1 | 0 | 2897910 | 2905973.3033 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 3092402.2195 | 2773618.4692 | 2851658.6512 | 2502740.2728 | 2762472.0542 | 2841690.4191
171 | Khalpar | F1104L | 11 | 0 | 0 | 1 | 89399920 | 91426620 | 2026700 | 1 | 0 | 2026700 | 2032339.2009 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 1943499.6703 | 1539343.6525 | 1698814.3914 | 1298185.7875 | 1375644.1828 | 1437529.7992
172 | Shahidnagar | D920S | 11 | 0 | 0 | 1 | 21734350 | 23321150 | 1586800 | 1 | 0 | 1586800 | 1591215.1991 | Azimpur | BGB 33/11 KV S/S | 104 | 1859313.6405 | 1906528.5825 | 1984753.7699 | 1856790.3941 | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | D9104G | 11 | 0 | 0 | 1 | 36808688 | 37153410 | 344722 | 1 | 0 | 344722 | 345681.1733 | Azimpur | BGB 33/11 KV S/S | 104 | 1312194.6593 | 1412422.3679 | 1466652.5091 | 1458588.073 | 1375749.2129 | 1318685.5995
174 | Ganaktuli | D8104J | 11 | 0 | 0 | 1 | 26164070 | 26868220 | 704150 | 1 | 0 | 704150 | 706109.2655 | Jigatola | BGB 33/11 KV S/S | 104 | 871530.0895 | 914191.5251 | 939625.3117 | 882817.4598 | 725654.1445 | 693078.4919
175 | Thana | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
176 | Bot Tola Mazar | D8104L | 11 | 0 | 0 | 1 | 38561747 | 39081811 | 520064 | 1 | 0 | 520064 | 521511.0545 | Jigatola | BGB 33/11 KV S/S | 104 | 2086773.692 | 2120352.147 | 2064384.9311 | 2207948.9744 | 2074198.5352 | 1909183.4664
177 | Sikder Medical | D8104K | 11 | 0 | 0 | 1 | 39247632 | 40142320 | 894688 | 1 | 0 | 894688 | 897177.4288 | Jigatola | BGB 33/11 KV S/S | 104 | 1152362.6885 | 1220473.4868 | 1221157.6998 | 1181050.1989 | 1134381.9061 | 1138392.2283
178 | Gas Field | F1104G | 11 | 0 | 0 | 1 | 60444680 | 62157430 | 1712750 | 1 | 0 | 1712750 | 1717515.6493 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2221738.1672 | 2114640.3455 | 2213538.6558 | 2063276.8361 | 2061072.7993 | 1985612.1672
179 | Hazaribagh | D8104H | 11 | 0 | 0 | 1 | 44324280 | 45430730 | 1106450 | 1 | 0 | 1106450 | 1109528.647 | Jigatola | BGB 33/11 KV S/S | 104 | 1387872.6757 | 1512565.9182 | 1534113.0489 | 1525507.7666 | 1485016.8997 | 1465699.7946
180 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
181 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 0 | 1 | 2295.89 | 2337.12 | 41.23 | 10 | 0 | 412.3 | 413.4472 | Azimpur | BGB 33/11 KV S/S | 104 | 551.1966 | 644.3721 | 611.8898 | 0 | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 1866.97 | 1909.01 | 42.04 | 10 | 0 | 420.4 | 421.5697 | Azimpur | BGB 33/11 KV S/S | 104 | 541.173 | 593.9263 | 558.558 | 0 | 0 | 0
184 | Salek Garden | 0 | 11 | 0 | 2761 | 1 | 718.18 | 749.07 | 30.89 | 60000 | 0 | 1853400 | 1864953.454 | Jigatola | Jigatola New 33/11 KV S/S |  | 2402250.1859 | 2551916.8348 | 2553649.2193 | 2650896.5462 | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 0 | 11 | 0 | 2850 | 1 | 557.19 | 578.8 | 21.61 | 60000 | 0 | 1296600 | 1304682.5555 | Jigatola | Jigatola New 33/11 KV S/S |  | 1679891.0289 | 1793125.2848 | 1780723.9511 | 1886527.6034 | 1807426.7227 | 1737565.9216
186 | Modina Rayer Bazar | 0 | 11 | 0 | 2851 | 1 | 628.51 | 662.99 | 34.48 | 60000 | 0 | 2068800 | 2081696.183 | Switching | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0
187 | City College | 0 | 11 | 0 | 2784 | 1 | 596.23 | 617.99 | 21.76 | 60000 | 0 | 1305600 | 1313738.6584 | Jigatola | Jigatola New 33/11 KV S/S |  | 1670267.593 | 1742699.2641 | 1753162.2749 | 1830510.0213 | 1777383.0604 | 2346194.6487
188 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
189 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
190 | Post Office | 0 | 11 | 0 | 2836 | 1 | 467.42 | 488.7 | 21.28 | 60000 | 0 | 1276800 | 1284759.1292 | Jigatola | Jigatola New 33/11 KV S/S |  | 1558395.1507 | 1658055.5864 | 1646510.5712 | 1676311.0857 | 1671629.3692 | 1589764.671
191 | Leather Institute | 0 | 11 | 0 | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 57222.2613 | 189875.9456 | 195265.8799
192 | Mina Bazar | 0 | 11 | 0 | 2853 | 1 | 229 | 237.44 | 8.44 | 60000 | 0 | 506400 | 509556.7223 | Jigatola | Jigatola New 33/11 KV S/S |  | 661611.218 | 704163.3609 | 701025.2432 | 763766.6032 | 746284.571 | 706562.076
193 | Mitali | 0 | 11 | 0 | 2852 | 1 | 519.49 | 536.6 | 17.11 | 60000 | 0 | 1026600 | 1032999.469 | Switching | Jigatola New 33/11 KV S/S |  | 2938155.2725 | 3066382.3082 | 3083312.7364
194 | Road-2 | 0 | 11 | 0 | 2839 | 1 | 742.81 | 774.77 | 31.96 | 60000 | 0 | 1917600 | 1929553.6546 | Jigatola | Jigatola New 33/11 KV S/S |  | 2419692.6635 | 2344809.964 | 2360717.4857 | 2376832.0316 | 2301945.4038 | 2450136.1786
195 | SS-2 | 0 | 11 | 0 | 2838 | 1 | 352.5 | 387.95 | 35.45 | 60000 | 0 | 2127000 | 2140258.9817 | Jigatola | Jigatola New 33/11 KV S/S |  | 1225183.6827 | 1208423.5682 | 1244469.5984 | 1139024.1692 | 1127238.2087 | 1112715.1061
196 | Spare | 0 | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
197 | Bou Bazar | 0 | 11 | 0 | 2843 | 1 | 596.66 | 620.73 | 24.07 | 60000 | 0 | 1444200 | 1453202.6428 | Jigatola | Jigatola New 33/11 KV S/S |  | 1833866.0032 | 1887974.2286 | 1919131.4991 | 1882311.2263 | 1850088.7231 | 1774816.6433
198 | BGB | 0 | 11 | 0 | 2764 | 1 | 201.95 | 214.64 | 12.69 | 60000 | 0 | 761400 | 766146.304 | Jigatola | Jigatola New 33/11 KV S/S |  | 453504.4167 | 461638.2136 | 445780.1547 | 580655.3671 | 1007063.5596 | 934872.9509
199 | Dhamondi-12 | 0 | 11 | 0 | 2763 | 1 | 487.48 | 499.01 | 11.53 | 60000 | 0 | 691800 | 696112.4417 | Dhanmondi | Jigatola New 33/11 KV S/S |  | 1536140.9551 | 2054260.035 | 1641717.2362 | 1520907.4708 | 1213163.0828 | 1602982.669
200 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 | 0 | DHK60907 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
201 | Mitali Road | D803D | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
202 | Bou Bazar | D803E | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
203 | Mina Bazar | D803I | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
204 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
205 | Simanto Square | D803R | 11 | 0 | DHK60946 | 1 | 1187.02 | 1199.27 | 12.25 | 60000 | 0 | 735000 | 732323.3006 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 891294.9856 | 910570.4517 | 922404.6994 | 967800 | 852145.3731 | 901151.3428
206 | Post Office | D803P | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
207 | Hazaribagh Sw/S-2 | D803S | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
208 | Green Road Via Park | D803G | 11 | 0 | DHK61070 | 1 | 3493.18 | 3506.97 | 13.79 | 60000 | 0 | 827400 | 824386.8012 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 963367.3565 | 1108520.5499 | 1276574.4307 | 1342800 | 1229862.9154 | 476757.7712
209 | PWD Quarters 11 kV Saleq Grand | D803A | 11 | 0 | DHK61028 | 1 | 3634.3 | 3635.35 | 1.05 | 60000 | 0 | 63000 | 62770.5686 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 73874.1801 | 78580.1905 | 73359.435 | 68400 | 74813.6195 | 63933.0345
210 | Road No.-2 | D803T | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
211 | Hzaribagh O/H | D803H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
212 | B.G.B | D803B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
213 | 11 kV City College | D803C | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
214 | Jigatala Local | D803Z | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0 | 0
215 | 33/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 243284 | 1 | 85276 | 85569 | 293 | 10 | 0 | 2930 | 2919.3296 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 1971.9801 | 3959.002 | 5251.4131 | 3680 | 2585.0234 | 3440.2061
216 | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 412277 | 1 | 39890 | 39890 | 0 | 10 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 1491.4977 | 769.8059 | 10.0218 | 1650 | 5393.0685 | 0
217 | Spare | 0 | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0
218 | D Block dhaka uddyan | G1103L | 11 | 0 | BD014031 | 1 | 50107.2 | 50391.3 | 284.1 | 1000 | 0 | 284100 | 285235.5277 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 367241.8104 | 387945.2586 | 382937.2777 | 364723.8055 | 376392.0985 | 356370.9019
219 | Dill Mohammad O/H | G1103DM | 11 | 0 | BD014027 | 1 | 23726.2 | 25238.4 | 1512.2 | 1000 | 0 | 1512200 | 1518244.1569 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1927925.8849 | 1986501.3323 | 2019494.4174 | 1931376.746 | 1945233.0858 | 1925614.3584
220 | Turag O/H | G1103U | 11 | 0 | BD014028 | 1 | 28276.4 | 28864.7 | 588.3 | 1000 | 0 | 588300 | 590651.3937 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 705567.8194 | 641819.4994 | 770193.2072 | 703573.3851 | 725059.1327 | 419185.0275
221 | Nabadoy O/H | G1103N | 11 | 0 | BD014025 | 1 | 38453.6 | 39575.1 | 1121.5 | 1000 | 0 | 1121500 | 1125982.5565 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 997660.9336 | 848979.0298 | 846778.6447 | 874784.3247 | 873886.7957 | 1264712.0241
222 | Chandrima O/H | G1103CH | 11 | 0 | BD014024 | 1 | 7893.5 | 8643.05 | 749.55 | 1000 | 0 | 749550 | 752545.8986 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 970880.6709 | 1055645.8739 | 1037828.5358 | 998647.327 | 974655.0029 | 879754.0777
223 | Shyamoli Housing Project-2 | G1103SH | 11 | 0 | BD014029 | 1 | 31072.7 | 31988.5 | 915.8 | 1000 | 0 | 915800 | 919460.3881 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1164941.4253 | 2147810.8671 | 1346057.1733 | 1686564.4606 | 1305126.5223 | 2226602.9518
224 | Spare | 0 | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0
225 | Spare | 0 | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0
226 | Spare | 0 | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0 | 0
227 | U Lab | C2103U | 11 | 0 | BD013959 | 1 | 44808.9 | 45500.4 | 691.5 | 1000 | 0 | 691500 | 694263.8768 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 2706800.3719 | 2673135.1804 | 1523999.7543 | 2168216.2175 | 2766170.13 | 2585824.4138
228 | Akota | G1103AK | 11 | 0 | BD014020 | 1 | 7699.4 | 8078.5 | 379.1 | 1000 | 0 | 379100 | 380615.236 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 526131.9628 | 548510.7365 | 553675.3788 | 518552.2147 | 529306.7232 | 494561.9781
229 | Burigonga O/H | G1103BU | 11 | 0 | BD014019 | 1 | 5871.8 | 6149.5 | 277.7 | 1000 | 0 | 277700 | 278809.9473 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 387230.8575 | 410809.9274 | 413097.2082 | 391376.3535 | 420977.1349 | 372374.7602
230 | Garden City | C2103G | 11 | 0 | BD014021 | 1 | 92171 | 94056.2 | 1885.2 | 1000 | 0 | 1885200 | 1892735.0117 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 2553547.6368 | 3028251.44 | 2810059.9564 | 2804225.2436 | 2395190.4943 | 2278829.2831
231 | Avenue O/H | G1103AV | 11 | 0 | BD014017 | 1 | 15936.5 | 16683.5 | 747 | 1000 | 0 | 747000 | 749985.7064 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 943169.2729 | 1027773.9029 | 1034448.2826 | 977183.594 | 966250.121 | 894892.5874
232 | Chand Uddyan | C2103D | 11 | 0 | BD014018 | 1 | 10428.5 | 10938.7 | 510.2 | 1000 | 0 | 510200 | 512239.2335 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 689384.282 | 764257.0863 | 760476.2406 | 759432.9748 | 732469.8888 | 645275.1572
233 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4416 | 1 | 1888.5 | 1917.01 | 28.51 | 100 | 0 | 2851 | 2862.3952 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 3787.2919 | 1595.7005 | 3776.8023 | 3734.949 | 3966.4616 | 1513.851
234 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4412 | 1 | 283.05 | 284.73 | 1.68 | 100 | 0 | 168 | 168.6715 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 3189.39 | 0 | 0 | 0 | 2409.7413
235 | Lalmatia O/H | C209M | 11 | 0 | DHK61042 | 1 | 3204.12 | 3220.42 | 16.3 | 60000 | 0 | 978000 | 970586.2531 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 911395.4616 | 1251951.9192 | 1243685.3152 | 1300189.4979 | 1240075.1783 | 1343819.1874
236 | Asad Avenue (South) | C209C | 11 | 0 | DHK 60999 | 1 | 2936 | 2949.71 | 13.71 | 60000 | 0 | 822600 | 816364.2657 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 854508.8922 | 1448736.6599 | 0 | 99461.5008 | 201384.8525 | 143036.2105
237 | Madrasha Road | 0 | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0
238 | Bashbari | C209H | 11 | 0 | DHK61002 | 1 | 2441.86 | 2461.86 | 20 | 60000 | 0 | 1200000 | 1190903.3781 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1245452.7622 | 1339544.3993 | 1690928.3933 | 1784914.5226 | 1599091.6268 | 1533732.8114
239 | Road-27 | C209A | 11 | 0 | DHK61001 | 1 | 1474.17 | 1479.65 | 5.48 | 60000 | 0 | 328800 | 326307.5256 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 422413.036 | 1160540.6933 | 560250.965 | 379271.8673 | 89903.952 | 435118.5562
240 | Boishakhi O/H | D209O | 11 | 0 | DHK61024 | 1 | 4226.72 | 4253.99 | 27.27 | 60000 | 0 | 1636200 | 1623796.756 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 2461251.8872 | 2676105.4034 | 2946106.036 | 2918535.965 | 3026167.0253 | 2814447.7883
241 | Katasur O/H | C209K | 11 | 0 | DHK61003 | 1 | 3674.52 | 3692.06 | 17.54 | 60000 | 0 | 1052400 | 1044422.2626 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1288420.2773 | 1430239.6103 | 1419182.7329 | 1436799.27 | 1431270.9163 | 1334804.3002
242 | Nurjahan Road | D409I | 11 | 0 | DHK61000 | 1 | 1885.68 | 1912.62 | 26.94 | 60000 | 0 | 1616400 | 1604146.8503 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1215193.9487 | 1433819.6844 | 1423372.644 | 1464960.0563 | 1437863.8728 | 1376873.7739
243 | polpar over head | D209W | 11 | 0 | DHK61003 | 1 | 1902.19 | 1928.75 | 26.56 | 60000 | 0 | 1593600 | 1581519.6861 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1999502.3937 | 2133127.4955 | 2142241.6706 | 2168380.5497 | 2135518.5405 | 2016930.7661
244 | Satmosjid Housing | C209S | 11 | 0 | DHK61043 | 1 | 2828.71 | 2852.16 | 23.45 | 60000 | 0 | 1407000 | 1396334.2108 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 0 | 189147.2492 | 1377283.6223 | 608153.1522 | 0 | 0
245 | Physical College | C209P | 11 | 0 | DHK61041 | 1 | 3391.12 | 3423.91 | 32.79 | 60000 | 0 | 1967400 | 1952486.0884 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 2469119.1787 | 2662381.786 | 2653410.8203 | 2677671.3668 | 2636583.2332 | 2184607.6683
246 | Asad Avenue (North) | D409V | 11 | 0 | DHK61022 | 1 | 2730.21 | 2730.21 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 288792.6455 | 0 | 3594.994 | 0 | 0
247 | Spare Feeder | 0 | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0 | 0
248 | Ghraphic artch college | D209Z | 11 | 0 | DHK61023 | 1 | 1148.21 | 1170.56 | 22.35 | 60000 | 0 | 1341000 | 1330834.525 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1448791.9887 | 1578216.0071 | 1715469.3009 | 1620743.1298 | 1570921.7218 | 1701409.7136
249 | Mohammadpur O/H | D409W | 11 | 0 | DHK61025 | 1 | 2241.73 | 2252.68 | 10.95 | 60000 | 0 | 657000 | 652019.5995 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1590403.2357 | 1624160.2917 | 1649627.8414 | 1683655.5249 | 1660825.6738 | 1343218.1949
250 | Bosila Feeder | C209V | 11 | 0 | DHK60997 | 1 | 4192.28 | 4231.8 | 39.52 | 60000 | 0 | 2371200 | 2353225.0751 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 2736001.9135 | 2540659.2659 | 2707281.1054 | 2444595.9223 | 2900301.4925 | 3015179.277
251 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIB 7375 | 1 | 6093.1 | 6168.9 | 75.8 | 60 | 0 | 4548 | 4513.5238 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 7345.0244 | 8176.8893 | 8159.5525 | 8272.6804 | 8691.9141 | 0
252 | Dhaka Uddyan | G186D | 11 | 0 | DHK86067 | 1 | 3252.83 | 3254.34 | 1.51 | 60000 | 0 | 90600 | 90112.6747 | Adabor | Japan Garden 33/11 KV | 86 | 43181.0046 | 44366.4049 | 46170.0157 | 47362.5115 | 34177.6075 | 0
253 | Shia Mosjid | D409H | 11 | 0 | DHK60950 | 1 | 3541.94 | 3569.61 | 27.67 | 60000 | 0 | 1660200 | 1651270.0056 | Shyamoli | Japan Garden 33/11 KV | 86 | 1965935.1818 | 2358614.0108 | 2312098.4465 | 2316566.3838 | 2321079.2736 | 1677029.4105
254 | Shekhar Tek | G186S | 11 | 0 | DHK60977 | 1 | 2443.6 | 2464.44 | 20.84 | 60000 | 0 | 1250400 | 1243674.2652 | Adabor | Japan Garden 33/11 KV | 86 | 1739834.6438 | 2042053.7165 | 2050068.6174 | 2089945.7593 | 2160384.5576 | 1966584.1503
255 | Madrasha Road | D434D | 11 | 0 | DHK61083 | 1 | 2064.99 | 2092.58 | 27.59 | 60000 | 0 | 1655400 | 1646495.8242 | Shyamoli | Japan Garden 33/11 KV | 86 | 1898764.7302 | 2311849.4219 | 1518214.0214 | 1459844.4991 | 1147648.0831 | 1148666.6379
256 | Baitul Aman Housing | G186B | 11 | 0 | DHK668115 | 1 | 4208.5 | 4242.38 | 33.88 | 60000 | 0 | 2032800 | 2021865.8399 | Adabor | Japan Garden 33/11 KV | 86 | 2579465.2888 | 2865829.9369 | 2799581.8586 | 2963454.3569 | 2980047.5303 | 2714650.3131
257 | Shyamoli Square | D486G | 11 | 0 | DHK86063 | 1 | 475.86 | 480.53 | 4.67 | 30000 | 0 | 140100 | 139346.4208 | Shyamoli | Japan Garden 33/11 KV | 86 | 179920.8525 | 180163.5766 | 172388.0455 | 167267.6038 | 170888.0374 | 163284.9924
258 | Mohammadi Housing | G186E | 11 | 0 | DHK60948 | 1 | 3873.73 | 3887.07 | 13.34 | 60000 | 0 | 800400 | 796094.7552 | Adabor | Japan Garden 33/11 KV | 86 | 1504138.327 | 1937732.7104 | 1867187.3865 | 2007211.2456 | 1954719.3056 | 1343295.1846
259 | Chand Housing | C286H | 11 | 0 | DHK60867 | 1 | 2213.38 | 2223.07 | 9.69 | 60000 | 0 | 581400 | 578272.7269 | Satmasjid | Japan Garden 33/11 KV | 86 | 1066930.6554 | 1224872.5023 | 796282.8675 | 850127.1046 | 960570.6526 | 891350.9825
260 | PC Culture Housing | 0 | 11 | 0 | DHK60979 | 1 | 4192.75 | 4222.72 | 29.97 | 60000 | 0 | 1798200 | 1788527.722 | Adabor | Japan Garden 33/11 KV | 86 | 2352165.2785 | 2602029.6916 | 2565134.1168 | 2719447.494 | 2646665.9554 | 2456140.6176
261 | Mehedibagh | G186H | 11 | 0 | DHK68121 | 1 | 2408.52 | 2445.54 | 37.02 | 60000 | 0 | 2221200 | 2209252.4615 | Adabor | Japan Garden 33/11 KV | 86 | 2861941.0273 | 3070874.6729 | 3016640.8933 | 3040793.1415 | 3013625.5306 | 2845397.7111
262 | 33/11 kV Incoming (Spare) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 0 | 0 | 0 | 0 | 0 | 0
263 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | 0 | 1 | 661926 | 665030 | 3104 | 1 | 0 | 3104 | 3087.304 | Adabor | Japan Garden 33/11 KV | 86 | 4523.0103 | 4813.3552 | 5033.7309 | 5179.9 | 5393.4663 | 0
264 | Mokarom Bhabon | D3108MB | 11 | 0 | 2761 | 1 | 60.6 | 63.51 | 2.91 | 60000 | 0 | 174600 | 174337.3 | Ramna | Dhaka University 33/11 KV S/S | 108 | 202329.0481 | 226720.401 | 207689.3161 | 186304.8566 | 168036.2342 | 191876.7922
265 | 11 kV Shaid Minar RMU | D3108SM | 11 | 0 | 2850 | 1 | 143.49 | 146.61 | 3.12 | 60000 | 0 | 187200 | 186918.3422 | Ramna | Dhaka University 33/11 KV S/S | 108 | 606987.1444 | 637120.699 | 361224.6845 | 367165.7402 | 336672.5979 | 339844.4752
266 | 11 kV Shaidulla Hall | D3108SH | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
267 | Spare | 0 | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
268 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
269 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
270 | MBA Bhabon | D3108MA | 11 | 0 | 2836 | 1 | 103.68 | 106.63 | 2.95 | 60000 | 0 | 177000 | 176733.689 | Ramna | Dhaka University 33/11 KV S/S | 108 | 232348.1947 | 278853.9691 | 280291.312 | 263125.3657 | 250253.9631 | 301348.8178
271 | Suprime Court | 0 | 11 | 0 | 2835 | 1 | 66 | 70.7 | 4.7 | 60000 | 0 | 282000 | 281575.7078 | Ramna | Dhaka University 33/11 KV S/S | 108 | 323006.0175 | 284309.8076 | 352893.3079 | 353253.3645 | 298264.3158 | 306762.2696
272 | Karjon Hall | D3108KH | 11 | 0 | 2853 | 1 | 72.86 | 76.92 | 4.06 | 60000 | 0 | 243600 | 243233.4838 | Ramna | Dhaka University 33/11 KV S/S | 108 | 317602.5711 | 349779.87 | 351108.0129 | 342970.3043 | 313267.551 | 333228.0341
273 | Spare | 0 | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
274 | Swimming Pool | D3108SP | 11 | 0 | 2839 | 1 | 2.33 | 2.73 | 0.4 | 60000 | 0 | 24000 | 23963.89 | Ramna | Dhaka University 33/11 KV S/S | 108 | 46229.4858 | 46071.5253 | 0 | 0 | 0 | 0
275 | Spare | 0 | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
276 | Police Head Quarter RMU | 0 | 11 | 0 | 2772 | 1 | 93.56 | 98.89 | 5.33 | 60000 | 0 | 319800 | 319318.8346 | Ramna | Dhaka University 33/11 KV S/S | 108 | 399254.6499 | 414643.728 | 474293.3666 | 554680.3686 | 488505.3381 | 444504.5437
277 | Spare | 0 | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
278 | Spare | 0 | 11 | 0 | 2764 | 1 | 1.48 | 2.38 | 0.9 | 60000 | Cheek Nocs & Feeder | 54000 | 53918.7526 | 0 | Dhaka University 33/11 KV S/S | 108 | 67242.8884 | 0 | 0 | 0 | 0 | 0
279 | Spare | 0 | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0 | 0
280 | Segunbagicha | D394S | 11 | 0 | DHK-C9360 | 1 | 13326.33 | 20686.9 | 7360.57 | 60 | 0 | 441634.2 | 443816.6143 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 585591.0985 | 595887.9152 | 652730.1844 | 660791.8145 | 648570.0837 | 628132.1417
281 | Secretariat RMU | D394FB | 11 | 0 | DHK-C9379 | 1 | 79602.83 | 81663.25 | 2060.42 | 60 | 0 | 123625.2 | 124236.116 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 153919.5822 | 147122.5127 | 169088.4911 | 173479.2405 | 157347.3651 | 189151.3106
282 | NBR RMU | D394NR | 11 | 0 | DHK-C9319 | 1 | 73234.86 | 78532.8 | 5297.94 | 60 | 0 | 317876.4 | 319447.2431 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 425924.9701 | 412789.7325 | 468220.1905 | 479026.3146 | 471677.0943 | 454185.7713
283 | Ramna 11 kV Sw/S-2 | 0 | 11 | 0 | DHK-C9364 | 1 | 50263.55 | 64314.76 | 14051.21 | 60 | 0 | 843072.6 | 847238.794 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 1202930.2093 | 1229384.6711 | 70113.1256 | 552257.97 | 1047973.9631 | 1309281.295
284 | Ramna 11 kV Sw/S-1 | 0 | 11 | 0 | DHK-C9375 | 1 | 55956.29 | 57677.67 | 1721.38 | 60 | 0 | 103282.8 | 103793.1904 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 54867.1796 | 213365.2082 | 295845.9008 | 960645.5509 | 37569.2064 | 3932.094
285 | Family Planning | D394FP | 11 | 0 | DHK-C9378 | 1 | 71774.93 | 77750.21 | 5975.28 | 60 | 0 | 358516.8 | 360288.4749 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 436247.6925 | 440914.9728 | 477616.3037 | 472965.3149 | 459978.3897 | 450311.5022
286 | Muktijuddho Montranalaya | D394MJ | 11 | 0 | DHK-C9376 | 1 | 88559.61 | 99696.86 | 11137.25 | 60 | 0 | 668235 | 671537.2027 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 860939.7125 | 912278.2358 | 979522.345 | 1003580.0431 | 989924.3443 | 925250.3935
287 | Purana Palton | D394R | 11 | 0 | DHK-C9318 | 1 | 65821.54 | 70819.4 | 4997.86 | 60 | 0 | 299871.6 | 301353.4691 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 347167.2021 | 309416.4011 | 349193.9997 | 350733.9486 | 318744.0733 | 328976.7665
288 | Tip Top Feeder | 0 | 11 | 0 | DHK-C9318 | 1 | 70239.61 | 92552.33 | 22312.72 | 60 | 0 | 1338763.2 | 1345378.9377 | Kakrail | Biddyut Bhaban 33/11 KV | 94 | 2213157.3667 | 1322789.6384 | 1326276.1291 | 1389761.4375 | 1427034.1549 | 1299449.2529
289 | 11/0.4 kV Auxiliary Transformer, AT | 0 | 0.415 | 0 | DHKD3784 | 1 | 355193 | 359859 | 4666 | 1 | 0 | 4666 | 4689.0579 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 5100.6865 | 4311.9923 | 4669.8501 | 4947.3654 | 4696.0253 | 4800.6724
290 | Nearest O/H | D398NE | 11 | 0 | 00000126 | 1 | 7943260.5 | 8118980 | 175719.5 | 1 | 0 | 175719.5 | 175545.4669 | Ramna | DMC 33/11 KV SS | 98 | 200195.8311 | 223877.2462 | 227289.0317 | 224820.1739 | 210729.7741 | 229906.9253
291 | Jagannath Hall | D398JA | 11 | 0 | 00000002 | 1 | 2968112.8 | 3050232 | 82119.2 | 1 | 0 | 82119.2 | 82037.8689 | Ramna | DMC 33/11 KV SS | 98 | 101039.4533 | 107985.9597 | 106229.8836 | 110593.2428 | 113276.1711 | 96242.8599
292 | Samsun Nahar Hall | D398SN | 11 | 0 | 00000024 | 1 | 10295055 | 10524494 | 229439 | 1 | 0 | 229439 | 229211.7629 | Ramna | DMC 33/11 KV SS | 98 | 277277.1279 | 321630.4227 | 329771.0476 | 322680.6125 | 293593.2672 | 312413.2678
293 | Spare, 4L | 0 | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0
294 | Board Office O/H, (5L) | A3983 | 11 | 0 | 00000023 | 1 | 22742504 | 23025144 | 282640 | 1 | 0 | 282640 | 282360.0725 | Lalbag | DMC 33/11 KV SS | 98 | 404116.548 | 474520.243 | 554924.1978 | 600144.1706 | 492983.2953 | 466712.6927
295 | OT- Complex | D398OT | 11 | 0 | 00000167 | 1 | 6834903.5 | 7175302 | 340398.5 | 1 | 0 | 340398.5 | 340061.3683 | Ramna | DMC 33/11 KV SS | 98 | 106528.8271 | 336918.4015 | 246189.5687 | 446170.5101 | 427837.7768 | 405707.0733
296 | Alia Mdrasha O/H, (7L) | A3984 | 11 | 0 | 00000148 | 1 | 9674696 | 9776616 | 101920 | 1 | 0 | 101920 | 101819.0581 | Lalbag | DMC 33/11 KV SS | 98 | 64901.5515 | 73635.9109 | 143184.6648 | 77701.5086 | 75154.3226 | 71193.4446
297 | Majed Sordar Road | B698J | 11 | 0 | 00000164 | 1 | 60280212 | 62242088 | 1961876 | 1 | 0 | 1961876 | 1959932.9522 | Bangshal | DMC 33/11 KV SS | 98 | 1719312.7006 | 1747073.1814 | 1774470.2621 | 1602752.7729 | 1759301.3409 | 1689289.8138
298 | Chankharpool, 9L | B698Q | 11 | 0 | 00000001 | 1 | 50333796 | 50750956 | 417160 | 1 | 0 | 417160 | 416746.8435 | Bangshal | DMC 33/11 KV SS | 98 | 1136431.6854 | 1199639.3416 | 1210601.5564 | 1176945.2408 | 1201456.0712 | 1157798.1959
299 | Shahidullah College O/H, (10L) | A3986 | 11 | 0 | 00000003 | 1 | 13594687 | 13802806 | 208119 | 1 | 0 | 208119 | 207912.8783 | Lalbag | DMC 33/11 KV SS | 98 | 235452.0398 | 255337.0354 | 264888.6074 | 263222.0224 | 263967.4494 | 265403.8751
300 | Ananda Bazar | D398AB | 11 | 0 | 00000111 | 1 | 15255803 | 15359723 | 103920 | 1 | 0 | 103920 | 103817.0773 | Ramna | DMC 33/11 KV SS | 98 | 119468.7736 | 114687.4296 | 145238.9396 | 167074.5674 | 216784.0965 | 169141.9631
301 | Hosseni Dalan O/H, (12L) | A3985 | 11 | 0 | 0 | 1 | 62.84 | 65.91 | 3.07 | 60000 | Estimated | 860184.9 | 859332.9703 | Lalbag | DMC 33/11 KV SS | 98 | 999393.6344 | 862949.5725 | 1039954.5727 | 1170127.1783 | 1629339.2554 | 1651805.4359
302 | Badrun Nessa College | A398W | 11 | 0 | 00000006 | 1 | 20999788 | 21354548 | 354760 | 1 | 0 | 354760 | 354408.6447 | Lalbag | DMC 33/11 KV SS | 98 | 469459.7974 | 504253.5009 | 510636.8949 | 522687.5196 | 511348.0734 | 487810.3149
303 | Dhaka Medical College, Unit-II | D398DM | 11 | 0 | 00000125 | 1 | 12612529 | 12836569 | 224040 | 1 | 0 | 224040 | 223818.1101 | Ramna | DMC 33/11 KV SS | 98 | 299392.072 | 310172.7151 | 327495.1248 | 332597.3491 | 314783.3957 | 318669.3545
304 | Spare, 15L | 0 | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0
305 | Sheikh Hasina National Burn Institute | D398SH | 11 | 0 | 00000127 | 1 | 21974666 | 22395106 | 420440 | 1 | 0 | 420440 | 420023.595 | Ramna | DMC 33/11 KV SS | 98 | 543136.2141 | 551404.561 | 585271.851 | 637362.5402 | 594088.462 | 527600.9918
306 | Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKF-7804 | 1 | 2872.86 | 2923.68 | 50.82 | 100 | 0 | 5082 | 5076.9668 | Ramna | DMC 33/11 KV SS | 98 | 7678.1323 | 7994.6127 | 7937.0165 | 8829.1604 | 8254.0596 | 7320.9952
307 | Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0 | 0
308 | Secratariet East | D363BS | 11 | 0 | BD 013966 | 1 | 4367.4 | 4544.19 | 176.79 | 1000 | 0 | 176790 | 176076.397 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 242760.0671 | 221126.0937 | 241216.6768 | 260076.7434 | 245293.0009 | 245463.3743
309 | Taher Bag O/H | B163G | 11 | 0 | BD 014045 | 1 | 20674.71 | 21284.07 | 609.36 | 1000 | 0 | 609360 | 606900.3521 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 725752.2867 | 829864.029 | 794329.1648 | 678707.287 | 744464.9674 | 740283.3012
310 | Al Raji Complex | D363AR | 11 | 0 | BD 013983 | 1 | 16069.61 | 16656.82 | 587.21 | 1000 | 0 | 587210 | 584839.7594 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 756317.9861 | 777798.4115 | 793783.38 | 773675.1898 | 784809.8778 | 793405.3649
311 | Raduni | D363RI | 11 | 0 | BD 013999 | 1 | 30757.71 | 31732.57 | 974.86 | 1000 | 0 | 974860 | 970925.0317 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 1082729.9623 | 1265333.7606 | 1301100.4786 | 623159.8339 | 1293358.488 | 1280815.0384
312 | Sundor Bon Square O/H | B163D | 11 | 0 | BD 013954 | 1 | 14187.74 | 14602.66 | 414.92 | 1000 | 0 | 414920 | 413245.1984 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 496614.8713 | 482395.9106 | 519829.721 | 434096.0289 | 473931.0551 | 515871.5523
313 | Shromo Bhobon O/H | D363SB | 11 | 0 | BD 013985 | 1 | 14129.96 | 14602.66 | 472.7 | 1000 | 0 | 472700 | 470791.9727 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 489342.1006 | 495640.2335 | 516585.3335 | 525134.9167 | 505142.6077 | 521299.6391
314 | Nawabpur Road | B163P | 11 | 0 | BD 013953 | 1 | 21924.28 | 22640.38 | 716.1 | 1000 | 0 | 716100 | 713209.502 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 834593.0606 | 843248.6095 | 904941.5553 | 800366.4326 | 843066.7121 | 849749.7199
315 | Spair | 0 | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0
316 | Spare | 0 | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0
317 | Ahad Police Box | D363AP | 11 | 0 | BD 013984 | 1 | 12043.51 | 12534.21 | 490.7 | 1000 | 0 | 490700 | 488719.3167 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 481256.786 | 438024.4232 | 458924.1778 | 366641.2546 | 470281.7667 | 423970.1788
318 | Nearest O/H | D363NE | 11 | 0 | BD 013997 | 1 | 2866.83 | 2970.68 | 103.85 | 1000 | 0 | 103850 | 103430.8152 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 124640.2411 | 121402.9541 | 117384.1651 | 114763.3233 | 117912.5625 | 115595.8875
319 | Natab Bhaban | D363NB | 11 | 0 | BD 014000 | 1 | 5346.21 | 5488.09 | 141.88 | 1000 | 0 | 141880 | 141307.3092 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 179461.8844 | 187424.2009 | 177268.8886 | 180013.0381 | 185708.2311 | 177165.0302
320 | Spare | 0 | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0 | 0
321 | Awami League Party Office | D363AO | 11 | 0 | BD 013956 | 1 | 1434.02 | 1452.23 | 18.21 | 1000 | 0 | 18210 | 18136.4963 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 10332.35 | 10118.5826 | 5579.1337 | 3568.1872 | 9417.1914 | 9250.1106
322 | Khaddar Bazar | D363KB | 11 | 0 | BD 014012 | 1 | 10910.83 | 11244.73 | 333.9 | 1000 | 0 | 333900 | 332552.2312 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 396371.0138 | 401687.6915 | 409449.7945 | 392931.5775 | 394275.1992 | 392631.6173
323 | Bangobondu National Stidium | D363NS | 11 | 0 | BD 014008 | 1 | 10449.23 | 11498.09 | 1048.86 | 1000 | 0 | 1048860 | 1044626.3348 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 1319581.5303 | 1315375.6615 | 1298280.5904 | 390265.4601 | 288658.7112 | 290128.194
324 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4418 | 1 | 1407.54 | 1481.27 | 73.73 | 100 | 0 | 7373 | 7343.2393 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 8140.4874 | 6640.1946 | 13693.1347 | 0 | 0 | 1718.8942
325 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 48.11 | 48.11 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 0 | 30.0552 | 597.3312 | 0 | 0 | 387.2849
326 | 11 KV Ring Road Feeder | G134R | 11 | 0 | 77816675 | 1 | 42349.9 | 42456.21 | 106.31 | 8000 | 0 | 850480 | 871742 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1122088 | 1191132 | 1186458 | 1209910 | 1172682 | 1124384
327 | 11 KV Gano Bhavan RMU | D534T | 11 | 0 | DHK14997 | 1 | 995.87 | 995.9 | 0.03 | 40000 | 0 | 1200 | 1230 | Shere b.nagar | Kallyanpur 33/11KV S/S | 34 | 2050 | 2050 | 1230 | 1230 | 1230 | 1230
328 | 11 KV Adabor O/H | D434A | 11 | 0 | DHK14957 | 1 | 4583.3 | 4620.87 | 37.57 | 40000 | 0 | 1502800 | 1540370 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2118880 | 2481320 | 2098790 | 1976610 | 2150040 | 2995460
329 | 11 KV Goidertek (DPDC) | G134G | 11 | 0 | DHK14996 | 1 | 9414.91 | 9431.09 | 16.18 | 40000 | 0 | 647200 | 663380 | Adabor | Kallyanpur 33/11KV S/S | 34 | 612540 | 617460 | 614590 | 586300 | 591220 | 558420
330 | 11 KV Beribandh Feeder. | G134K | 11 | 0 | DHK14960 | 1 | 9667.45 | 9673.06 | 5.61 | 40000 | 0 | 224400 | 230010 | Adabor | Kallyanpur 33/11KV S/S | 34 | 285360 | 348090 | 239440 | 234930 | 301350 | 184500
331 | 11 KV Sewarage Pump | G134P | 11 | 0 | DHK14959 | 1 | 2296.25 | 2350.06 | 53.81 | 40000 | 0 | 2152400 | 2206210 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2792510 | 1776530 | 2952000 | 2380460 | 2601450 | 535870
332 | 11 KV Technical School (DPDC) | G134T | 11 | 0 | DHK15019 | 1 | 8361.96 | 8401.63 | 39.67 | 40000 | 0 | 1586800 | 1626470 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2204980 | 2398910 | 2363240 | 2400960 | 2347660 | 2184890
333 | 11 KV Mansurabad | G134M | 11 | 0 | 77816681 | 1 | 52769.06 | 52970.34 | 201.28 | 8000 | 0 | 1610240 | 1650496 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2258116 | 2458196 | 2422936 | 2313630 | 2379804 | 2220888
334 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 40966.6 | 41105.9 | 139.3 | 1000 | 0 | 139300 | 140940.5878 | Kakrail | Moghbazar 33/11KV S/S | 8 | 170232.3057 | 173300.7767 | 177316.5531 | 65016.8533 | 1691.4448 | 1119.369
335 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 80957.2 | 81024 | 66.8 | 1000 | 0 | 66800 | 67586.7284 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 136288.0862 | 107803.7381 | 78656.0729 | 96666.9717 | 802696.2793 | 1023306.7911
336 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 1589911.0287
337 | 11 kV Tejgaon S/S-1 | 0 | 11 | T-1 | 30/11004-1101 | 1 | 120741.7 | 121092.2 | 350.5 | 1000 | 0 | 350500 | 354627.9687 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 467141.9849 | 391310.8557 | 416531.5604 | 434303.9973 | 326660.2796 | 342221.6327
338 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0
339 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 123990 | 125174.5 | 1184.5 | 1000 | Estimated | 1530219.6 | 1548241.5645 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1803211.1873 | 1782922.7783 | 2012798.2977 | 1909092.2251 | 1919578.4326 | 1819483.4353
340 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 132139.2 | 133873.6 | 1734.4 | 1000 | 0 | 1734400 | 1754826.6729 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 2252689.725 | 2523568.5136 | 2372564.6062 | 2579216.4264 | 2455343.5773 | 1989016.959
341 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 148899.1 | 150222.7 | 1323.6 | 1000 | 0 | 1323600 | 1339188.5287 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1537918.5242 | 1644738.2335 | 1666230.9769 | 1593234.7726 | 1205154.4296 | 1055666.7314
342 | 11 kV Vumi Bhaban | 0 | 11 | T-3 | 21101039 | 1 | 8997.2 | 9098.9 | 101.7 | 1000 | 0 | 101700 | 102897.7587 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 143547.2416 | 140604.4879 | 151132.7739 | 165331.6353 | 136267.0228 | 122011.2214
343 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 10125.5 | 10241.6 | 116.1 | 1000 | 0 | 116100 | 117467.3528 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 150704.1553 | 173927.5426 | 164434.1337 | 177991.6827 | 170095.919 | 154167.6401
344 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 128558 | 130036 | 1478 | 1000 | 0 | 1478000 | 1495406.9549 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1911100.4557 | 2221153.9574 | 2075012.1387 | 2269581.709 | 2138303.3901 | 1962152.1029
345 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 89088.7 | 90371.6 | 1282.9 | 1000 | 0 | 1282900 | 1298009.1897 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1555095.1172 | 1652781.7295 | 1586003.8772 | 1603212.6065 | 1595983.8968 | 78254.0694
346 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 178896.5 | 180854.9 | 1958.4 | 1000 | 0 | 1958400 | 1981464.8041 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 2346752.0201 | 2390485.2167 | 1095738.7944 | 1085008.9734 | 952812.0065 | 1869447.9972
347 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 124248.6 | 124552.3 | 303.7 | 1000 | 0 | 303700 | 307276.7877 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 363366.7355 | 399563.2736 | 370867.0494 | 398147.7603 | 399920.9831 | 690345.3929
348 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 116054.5 | 116794.1 | 739.6 | 1000 | 0 | 739600 | 748310.5439 | Kakrail | Moghbazar 33/11KV S/S | 8 | 931830.1708 | 991857.0675 | 900407.8011 | 994564.7368 | 950591.9851 | 944645.6784
349 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 44614.9 | 45007.6 | 392.7 | 1000 | 0 | 392700 | 397324.9737 | Kakrail | Moghbazar 33/11KV S/S | 8 | 478388.5637 | 514783.7418 | 344054.8595 | 0 | 0 | 323294.1205
350 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | 11653570.4165 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 1357.9928 | 0 | 0 | 0 | 0
351 | 11 kV TCB Feeder | C608P | 11 | T-4 | 0 | 1 | 36868.9 | 37126.3 | 257.4 | 1000 | 0 | 257400 | 275835.9679 | Kakrail | Moghbazar 33/11KV S/S | 8 | 327449.4305 | 337617.6819 | 593608.4852 | 1091208.9552 | 1058026.2525 | 587067.814
352 | 11 kV Tejgaon SS-2 | 0 | 11 | T-4 | 0 | 1 | 34285.7 | 35724.6 | 1438.9 | 1000 | 0 | 1438900 | 1541959.4958 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1519526.851 | 1537848.541 | 1385049.7687 | 1574127.4074 | 1532552.8114 | 1481122.0985
353 | Holy Day Inn | C108HY | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 306390 | 328334.8182 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 421689.4191 | 437235.9991 | 578900.3818 | 542740.3295 | 522630.1141 | 493817.3233
354 | Polly Bhabon-2 | C608PB | 11 | T-4 | 0 | 1 | 18384.8 | 18385 | 0.2 | 1000 | According to AMR meter reading | 16146 | 17302.438 | Kakrail | Moghbazar 33/11KV S/S | 8 | 23296.5077 | 25096.5994 | 28135.8532 | 27898.691 | 30058.9479 | 29444.1053
355 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 | 0 | 1 | 20174.3 | 21533.5 | 1359.2 | 1000 | 0 | 1359200 | 1456551.0784 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1783228.8258 | 1839066.8165 | 1861301.6803 | 1854771.9565 | 1842884.7823 | 1860061.7445
356 | 11 kV Tejturibazar | C608X | 11 | T-4 | 0 | 1 | 132923.9 | 133302 | 378.1 | 1000 | 0 | 378100 | 405180.9614 | Kakrail | Moghbazar 33/11KV S/S | 8 | 781650.0519 | 797094.2458 | 844174.6782 | 788742.3253 | 776669.7972 | 731592.6735
357 | Songsad | 0 | 11 | T-4 | 0 | 1 | 3864.8 | 3864.8 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Moghbazar 33/11KV S/S | 8 | 154587.5799 | 443228.713 | 416692.9 | 475259.7411 | 544550.7215 | 126381.9385
358 | Chennel 24 | 0 | 11 | T-4 | 0 | 1 | 7327.44 | 7329.92 | 2.48 | 1000 | 0 | 2480 | 2657.627 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 3644.2295 | 5053.7147 | 7574.2329 | 3766.4072 | 1700.7368 | 1164.858
359 | Sonargaon | C608K | 11 | T-4 | 0 | 1 | 41957.9 | 42568 | 610.1 | 1000 | 0 | 610100 | 653797.6846 | Kakrail | Moghbazar 33/11KV S/S | 8 | 888533.2859 | 916526.5008 | 698965.1841 | 733347.8124 | 844174.3497 | 839625.5215
360 | AT -1 | 0 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 7215.9345
361 | AT -2 | 0 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 4681620.0714 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0 | 0
362 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 208557 | 225815 | 17258 | 60 | 0 | 1035480 | 1045950.5553 | Kakrail | T&T 33/11 KV | 105 | 350929.0306 | 1384212.3787 | 1354639.697 | 1410640.1386 | 1413099.3422 | 1314936.3633
363 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 491607 | 508205 | 16598 | 60 | 0 | 995880 | 1005950.1284 | Kakrail | T&T 33/11 KV | 105 | 1232617.5702 | 1434115.4167 | 1367760.1292 | 1475917.0544 | 1466512.1688 | 1363050.3594
364 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 963754 | 968143 | 4389 | 60 | 0 | 263340 | 266002.8385 | Moghbazar | T&T 33/11 KV | 105 | 363967.9203 | 383823.6058 | 382050.2122 | 390823.0756 | 376350.3769 | 416269.8468
365 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1987746 | 1999157 | 11411 | 60 | 0 | 684660 | 691583.1374 | Moghbazar | T&T 33/11 KV | 105 | 808883.1556 | 925176.0601 | 915135.1719 | 946635.0529 | 901476.4809 | 862940.0791
366 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 670.9 | 690.8 | 19.9 | 60000 | 0 | 1194000 | 1206073.4761 | Moghbazar | T&T 33/11 KV | 105 | 1469087.5693 | 1653485.829 | 1672106.229 | 1759482.372 | 1708010.1623 | 1630130.9123
367 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 916060 | 923585 | 7525 | 60 | 0 | 451500 | 456065.4727 | Kakrail | T&T 33/11 KV | 105 | 614479.8006 | 616445.7818 | 601742.5641 | 617435.7813 | 612807.1598 | 591251.5937
368 | 11 kV cinema hall | 0 | 11 | Mogbazar | DHK60979 | 1 | 522676 | 535968 | 13292 | 60 | 0 | 797520 | 805584.354 | Moghbazar | T&T 33/11 KV | 105 | 981161.6979 | 1071064.8459 | 1069584.8264 | 1086052.1721 | 1077858.8375 | 1046359.7284
369 | 11 kV malibagh bazar | 0 | 11 | Khailgaon | DHK61106 | 1 | 782487 | 803461 | 20974 | 60 | 0 | 1258440 | 1271165.0797 | Khilgaon | T&T 33/11 KV | 105 | 1621719.2778 | 1701657.7808 | 1728362.3289 | 1686240.4748 | 1646555.4045 | 1662984.8723
370 | 11 kv Sherebangla | D1105G | 11 | 0 | DHK60915 | 1 | 765116 | 782199 | 17083 | 60 | 0 | 1024980 | 1035344.3815 | Moghbazar | T&T 33/11 KV | 105 | 1275392.2083 | 1525385.4467 | 1396637.0623 | 1544547.6466 | 1416880.2502 | 1438632.4204
371 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 355079 | 364525 | 9446 | 60 | 0 | 566760 | 572490.9575 | Moghbazar | T&T 33/11 KV | 105 | 647224.5235 | 706402.574 | 705627.6304 | 690498.0173 | 692746.3564 | 708065.6738
372 | Auxiliary | 0 | 0 | Export | U0004461 | 1 | 8288.88 | 8333.5 | 44.62 | 60 | 0 | 2677.2 | 2704.2713 | Moghbazar | T&T 33/11 KV | 105 | 3869.1873 | 7599.4686 | 0 | 4061.5417 | 3583.4605 | 3045.4245
373 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 706255.2 | 711283.282 | Moghbazar | Ullon local 33/11KV S/S | 92 | 977173.2999 | 1007307.2369 | 980334.5269 | 1038100.3806 | 1138226.0536 | 978294.9507
374 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1294801.2 | 1304019.3504 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1832199.9373 | 1836854.3731 | 1838127.2379 | 1648747.6632 | 1617479.1288 | 1406298.9916
375 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1235946.6 | 1244745.7435 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1526833.2811 | 1659094.2725 | 1654314.5141 | 1770877.1198 | 1677385.7633 | 1345155.5572
376 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 918131.76 | 924668.2666 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1038246.6311 | 1125813.9706 | 1102876.3427 | 1282359.2936 | 1317945.9568 | 1100581.8195
377 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1177092 | 1185472.1367 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1710053.2748 | 1718347.6394 | 1715585.422 | 1648747.6632 | 1557572.4944 | 1345155.5572
378 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 882819 | 889104.1025 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1099319.9624 | 1149515.3174 | 1225418.1586 | 1282359.2936 | 1377852.5912 | 1222868.6883
379 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0
380 | AT-1 | 0 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0
381 | AT-2 | 0 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0 | 0
382 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 15.7858 | 17.0895 | 1.3037 | 1000000 | 0 | 1303698 | 1312980.8765 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1733090.4653 | 1860379.5125 | 1839023.3133 | 1914129.2674 | 1830321.6533 | 1753548.1446
383 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 105215.6 | 106484.9 | 1269.3 | 1000 | 0 | 1269300 | 1278337.9483 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1814364.7668 | 1995837.5311 | 1955619.6426 | 2015001.2811 | 1947058.9925 | 1858521.5132
384 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 6227.8 | 7446.5 | 1218.7 | 1000 | 0 | 1218700 | 1227377.6551 | Mugdapara | Madarteck 33/11KV S/S | 21 | 2135456.6106 | 2140470.7173 | 2127980.2733 | 2037129.655 | 2033626.6462 | 1264456.5681
385 | Goran | A921G | 11 | 0 | X1390296 | 1 | 34326.4 | 35532.5 | 1206.1 | 1000 | 0 | 1206100 | 1214687.9378 | Bashabo | Madarteck 33/11KV S/S | 21 | 1825010.9149 | 1949936.5823 | 1924894.1079 | 2047460.5279 | 1968306.9598 | 1851494.7743
386 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 14225.436 | 15256.78 | 1031.344 | 1000 | 0 | 1031344 | 1038687.6018 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1446701.0468 | 1502775.9682 | 1533961.2033 | 1583000.8619 | 1493157.2972 | 2039169.8043
387 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 21 | 0 | 0 | 0 | 0 | 373198.8946 | 881499.2996
388 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1479.3345 | 1661.0999 | 181.7654 | 1000 | 0 | 181765.4 | 183059.6459 | Mugdapara | Madarteck 33/11KV S/S | 21 | 244346.2732 | 252299.2953 | 242642.782 | 236939.3158 | 229733.5056 | 209712.5124
389 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 4970.5368 | 5343.364 | 372.8272 | 1000 | 0 | 372827.2 | 375481.886 | Mugdapara | Madarteck 33/11KV S/S | 21 | 578366.2569 | 687579.7395 | 671883.3535 | 576962.6065 | 679941.1966 | 331641.7074
390 | Mugdapara | B921P | 11 | 0 | X0854272 | 1 | 4681.7 | 4957.2 | 275.5 | 1000 | 0 | 275500 | 277461.6755 | Maniknagar | Madarteck 33/11KV S/S | 21 | 259324.0979 | 280126.3587 | 262278.8244 | 99804.6 | 280453.0279 | 256934.2344
391 | Singapur | F221S | 11 | 0 | X1390302 (N) | 1 | 40431.5 | 41999.2 | 1567.7 | 1000 | 0 | 1567700 | 1578862.6815 | Banosree | Madarteck 33/11KV S/S | 21 | 2168600.2792 | 2400509.1335 | 2332917.0805 | 2449510.2642 | 2359732.7837 | 2200082.1244
392 | Trimohony | F221T | 11 | 0 | X1390308 | 1 | 32844.1 | 34398.2 | 1554.1 | 1000 | 0 | 1554100 | 1565165.8438 | Banosree | Madarteck 33/11KV S/S | 21 | 2029899.048 | 2144287.4264 | 2101565.9326 | 2104795.0854 | 2021980.735 | 1604947.893
393 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 17776.286 | 19281.996 | 1505.71 | 1000 | 0 | 1505710 | 1516431.2867 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1620835.8728 | 1884688.9362 | 1948965.1387 | 1816135.3069 | 1942171.9601 | 1839386.3794
394 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 7166.0944 | 7716.29 | 550.1956 | 1000 | 0 | 550195.6 | 554113.2234 | Mugdapara | Madarteck 33/11KV S/S | 21 | 808655.6976 | 863662.2068 | 854936.3865 | 710891.4812 | 850151.1099 | 596386.824
395 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 748752 | 755370 | 6618 | 200 | 0 | 1323600 | 1333024.5871 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1795382.4839 | 1921009.9451 | 1954912.1468 | 1661387.6173 | 1892982.4123 | 480873.3471
396 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 777256 | 783208 | 5952 | 200 | 0 | 1190400 | 1198876.1472 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1488652.8964 | 1652835.9122 | 1533042.4693 | 1508090.9874 | 1450702.4488 | 298789.1572
397 | Nakhal Para Feeder | C110U | 11 | 0 | DHK60950 | 1 | 305498.9 | 324180.3 | 18681.4 | 60 | 0 | 1120884 | 1127439.9287 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1500089.328 | 1599409.3479 | 1587033.6595 | 1590100.5899 | 1545202.0376 | 1536369.5556
398 | Badda-Meghna Feeder | C110N | 11 | 0 | DHK60979 | 1 | 940674.7 | 952442.1 | 11767.4 | 60 | 0 | 706044 | 710173.5747 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 794267.6303 | 812324.781 | 768867.2754 | 797427.1133 | 711868.0468 | 842649.7133
399 | Rasulbagh Feeder | C110K | 11 | 0 | DHK60948 | 1 | 82062.5 | 107045.9 | 24983.4 | 60 | 0 | 1499004 | 1507771.5116 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1806034.3017 | 1726738.2372 | 1932163.7903 | 1821935.9992 | 1845073.9247 | 1902151.6741
400 | Lukas | C171V | 11 | 0 | 8A021100948-02 | 1 | 73546915 | 75134351 | 1587436 | 1 | 0 | 1587436 | 1596720.7407 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2026298.4778 | 2352263.3192 | 2382018.4101 | 2450636.3287 | 2356930.5125 | 2345545.782
401 | PWD RMU | 0 | 11 | 0 | 0 | 1 | 660047.1 | 661501.9 | 1454.8 | 1 | 0 | 1454.8 | 1463.309 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1806.986 | 1917.0903 | 1854.955 | 1876.4622 | 1825.2484 | 1757.0539
402 | Civil Aviation Feeder | 0 | 11 | 0 | DHK60977 | 1 | 984210.7 | 1019068.7 | 34858 | 60 | 0 | 2091480 | 2103712.8393 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2870937.6357 | 3006456.2987 | 2816826.0828 | 2972868.5519 | 2843930.4649 | 2795399.6317
403 | Ahasanullah Eng. | C171L | 11 | 0 | DHK60867 | 1 | 900589.8 | 908328.2 | 7738.4 | 60 | 0 | 464304 | 467019.6637 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 571155.4762 | 575802.5636 | 668050.5071 | 681476.0179 | 638085.1899 | 673101.4258
404 | New GMG Feeder | C110M | 11 | 0 | DHK61106 | 1 | 151809.7 | 180726.9 | 28917.2 | 60 | 0 | 1735032 | 1745180.0137 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1868942.3881 | 2083647.5312 | 2435471.7452 | 2366892.1845 | 2233355.6797 | 2281871.6214
405 | Shikajo | C171Z | 11 | 0 | HA021101036-02 | 1 | 66059038 | 66732385 | 673347 | 1 | 0 | 673347 | 677285.3335 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 862880.7653 | 832111.8625 | 813808.0835 | 877169.4199 | 833321.8823 | 756034.1648
406 | Kahinur | 0 | 11 | 0 | 0 | 1 | 584798.7 | 602529.6 | 17730.9 | 60 | 0 | 1063854 | 1070076.3665 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1309013.1381 | 1330662.8857 | 1351230.8033 | 1347009.4431 | 1251045.3402 | 1294083.2246
407 | Link road | C171X | 11 | 0 | 8A021100380-02 | 1 | 66112857 | 66526725 | 413868 | 1 | 0 | 413868 | 416288.669 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 724119.8808 | 647867.3456 | 425896.0895 | 415317.8944 | 416737.628 | 435428.3198
408 | Shanta | C110E | 11 | 0 | 0 | 1 | 341520.5 | 350241.3 | 8720.8 | 60 | 0 | 523248 | 526308.4207 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 628311.0309 | 599004.2611 | 643052.4099 | 671568.0547 | 608607.1616 | 630895.3248
409 | Karnafuly Feeder | C110Y | 11 | 0 | DHK61084 | 1 | 36682 | 37300.6 | 618.6 | 1000 | 0 | 618600 | 622218.1242 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 807314.3803 | 766856.2088 | 716684.8588 | 722759.1976 | 686952.8872 | 738300.0364
410 | Butex | C110BT | 11 | 0 | 0 | 1 | 1299 | 1403 | 104 | 1000 | 0 | 104000 | 104608.2847 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 106281.4076 | 100920.6493 | 102946.4154 | 100374.7899 | 90006.1656 | 91610.1416
411 | OriON LAB | C171A | 11 | 0 | 0 | 1 | 8377954 | 8454240 | 76286 | 1 | 0 | 76286 | 76732.1885 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 90864.5418 | 93311.3932 | 93876.22 | 95833.6401 | 88588.4676 | 248723.2522
412 | Nina kabbo | C171Y | 11 | 0 | 201101025-2 | 1 | 17647767 | 17854558 | 206791 | 1 | 0 | 206791 | 208000.4981 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 261868.4978 | 264819.2014 | 285983.9298 | 281438.971 | 283127.915 | 99489.3009
413 | Satrong | C171S | 11 | 0 | HA021100515-2 | 1 | 97172731 | 98397161 | 1224430 | 1 | 0 | 1224430 | 1231591.5581 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1888984.3136 | 2007795.2093 | 1899691.7228 | 1806807.9399 | 1563100.3489 | 1367977.887
414 | South East RMU | 0 | 11 | 0 | 0 | 1 | 1108.7 | 1176.1 | 67.4 | 1000 | 0 | 67400 | 67794.2153 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 115171.8675 | 137308.3735 | 130223.6796 | 128807.568 | 139045.3993 | 149070.967
415 | Rangs Bhaban | 0 | 11 | 0 | HA021100939-2 | 1 | 881462 | 1006950 | 125488 | 1 | 0 | 125488 | 126221.9657 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 151848.0457 | 148545.345 | 152471.8244 | 163396.3968 | 151255.7649 | 161670.1139
416 | Babli | C171R | 11 | 0 | 0 | 1 | 60405.4 | 61327 | 921.6 | 1000 | 0 | 921600 | 926990.3383 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1047558.8549 | 1066401.5624 | 2240675.7095 | 2109084.7983 | 2111815.0669 | 1541422.4274
417 | SPL | 0 | 11 | 0 | 0 | 1 | 5307 | 5708.6 | 401.6 | 1000 | 0 | 401600 | 403948.9148 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 470689.2376 | 471130.5611 | 465633.0017 | 455733.9249 | 408962.9923 | 372268.4438
418 | DNCC Hospital | 0 | 11 | 0 | 0 | 1 | 17538 | 18258.1 | 720.1 | 1000 | 0 | 720100 | 724311.7867 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 958856.3113 | 1039161.0285 | 1028453.8853 | 1058083.8484 | 992388.6083 | 965076.0343
419 | 11/.415 kv Local transformer | 0 | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 0 | 0 | 0 | 0 | 6054.2264 | 6134.6077
420 | Gonobhaban | D570T | 11 | 0 | DHKC9332 | 1 | 82497.17 | 84785.44 | 2288.27 | 60 | 0 | 137296.2 | 138463.2177 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 186647.9358 | 199883.04 | 203554.794 | 226219.392 | 216875.2359 | 216836.1836
421 | Rapa Plaza Feeder | D270R | 11 | 0 | DHKC9339 | 1 | 31044.61 | 46040.31 | 14995.7 | 60 | 0 | 899742 | 907389.807 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 1054413.3744 | 1089910.392 | 1159561.608 | 1233509.5584 | 1199461.0668 | 1170856.0696
422 | Shukrabad/ South Plaza | D570S | 11 | 0 | DHKC9324 | 1 | 71432.99 | 85995.04 | 14562.05 | 60 | 0 | 873723 | 881149.6455 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 1103197.1415 | 1099590.636 | 1169672.112 | 1195401.7152 | 1120705.5276 | 1130327.1946
423 | Wasa O/H | C270W | 11 | 0 | DHKC9333 | 1 | 58765.81 | 70721.35 | 11955.54 | 60 | 0 | 717332.4 | 723429.7254 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 739783.158 | 1806723.552 | 986766.768 | 1324483.5744 | 2118683.8855 | 1049087.4751
424 | Bangabandhu Memorial Museum | 0 | 11 | 0 | DHKC9334 | 1 | 16332.37 | 16545.05 | 212.68 | 60 | 0 | 12760.8 | 12869.2668 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 18497.907 | 17876.394 | 21495.426 | 21201.264 | 20854.3329 | 20897.995
425 | Iqbal Road O/H | D470Q | 11 | 0 | DHKC9330 | 1 | 48276.24 | 66650.02 | 18373.78 | 60 | 0 | 1102426.8 | 1111797.4278 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1464338.9745 | 1539511.488 | 1602882.12 | 1776423.3984 | 1626760.4818 | 1601413.1174
426 | Town Hall | D470W | 11 | 0 | DHKC9351 | 1 | 3102.61 | 29529.34 | 26426.73 | 60 | 0 | 1585603.8 | 1599081.4323 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1961962.9278 | 2111520.342 | 2123219.172 | 2353752.1728 | 1991480.522 | 2338946.2013
427 | Post Office | D470P | 11 | 0 | DHKC9331 | 1 | 33036.5 | 50889.76 | 17853.26 | 60 | 0 | 1071195.6 | 1080300.7626 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1412012.952 | 1209158.466 | 1512426.318 | 1672604.0352 | 1378440.8932 | 1492441.2314
428 | Shangshad Bhaban | 0 | 11 | 0 | DHKC9370 | 1 | 24023.67 | 24023.68 | 0.01 | 60 | 0 | 0.6 | 0.6051 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 94824.6159 | 417958.806 | 245083.974 | 292942.1376 | 474363.1372 | 422562.5169
429 | Jakir Hossain Road | C270J | 11 | 0 | DHKC9373 | 1 | 67793.29 | 83237.19 | 15443.9 | 60 | 0 | 926634 | 934510.389 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1496705.7735 | 741916.104 | 1368356.484 | 1603359.2736 | 1792634.4006 | 1277863.2905
430 | New Colony O/H Feeder | C270N | 11 | 0 | DHKC9369 | 1 | 31606.58 | 48198.28 | 16591.7 | 60 | 0 | 995502 | 1003963.767 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1053637.6362 | 236025.486 | 1443709.554 | 1041715.3824 | 0 | 1328527.8719
431 | Aurangzeb Feeder | D470M | 11 | 0 | DHKC9321 | 1 | 34889.71 | 54002.53 | 19112.82 | 60 | 0 | 1146769.2 | 1156516.7382 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1667662.8612 | 711485.208 | 1577029.554 | 1636123.104 | 1847282.7847 | 2012075.4293
432 | Asadgate Local Feeder | C270E | 11 | 0 | DHKC9338 | 1 | 42257.12 | 52468.4 | 10211.28 | 60 | 0 | 612676.8 | 617884.5528 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1521583.8549 | 1037091.432 | 1943325.648 | 2129079.8592 | 2381609.9379 | 1832840.2298
433 | Sonarbangla Road | D470R | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 0 | 0 | 0 | 0 | 0 | 0
434 | Humayun Road | D470H | 11 | 0 | DHKC9366 | 1 | 57194.89 | 83086.82 | 25891.93 | 60 | 0 | 1553515.8 | 1566720.6843 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1813580.3058 | 1032128.898 | 1903127.244 | 1920389.3856 | 263604.1533 | 1670349.266
435 | NHA | D470B | 11 | 0 | DHKC9374 | 1 | 65850.12 | 68657.31 | 2807.19 | 60 | 0 | 168431.4 | 169863.0669 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 219431.6487 | 72214.596 | 237352.02 | 264138.5376 | 26450.7883 | 221861.5773
436 | Auxiliary transformer | 0 | 0.415 | 0 | 0 | 1 | 667095 | 672271 | 5176 | 1 | 0 | 5176 | 5219.996 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 7644.43 | 8345.63 | 17430.58 | 0 | 7372.3763 | 6148.5505
437 | Angur Jora | F292A | 11 | 0 | 141 | 1 | 2417760 | 3821920 | 1404160 | 1 | 0 | 1404160 | 1423037.4494 | Banosree | Banasree 33/11 SS | 99 | 2051370.0659 | 2226512.8044 | 2196051.2126 | 2182461.1184 | 2168323.5267 | 1879685.8324
438 | Block F-G Avenue | F299G | 11 | 0 | 68 | 1 | 5525600 | 6117160 | 591560 | 1 | 0 | 591560 | 599512.8999 | Banosree | Banasree 33/11 SS | 99 | 2148314.9942 | 2658158.1289 | 2630613.5558 | 2686465.1418 | 2772883.9436 | 2653782.5782
439 | Banasree Main Road(Monpura) | F292P | 11 | 0 | 168 | 1 | 276520 | 766400 | 489880 | 1 | 0 | 489880 | 496465.9196 | Banosree | Banasree 33/11 SS | 99 | 1014510.7585 | 1233831.441 | 1794844.8609 | 1857089.8973 | 1771391.1453 | 1640446.1666
440 | Baitul Kuddus | F292Q | 11 | 0 | 62 | 1 | 6205400 | 7869640 | 1664240 | 1 | 0 | 1664240 | 1686613.9505 | Banosree | Banasree 33/11 SS | 99 | 2119711.2807 | 2318179.6901 | 2240905.0671 | 2321761.5567 | 2248090.2296 | 2090165.4312
441 | Ideal | F214I | 11 | 0 | 0 | 1 | 538960 | 1080480 | 541520 | 1 | 0 | 541520 | 548800.1649 | Banosree | Banasree 33/11 SS | 99 | 698230.2076 | 798010.2701 | 777466.8098 | 813387.6289 | 785714.1589 | 730886.4987
442 | Central Mosque | F292C | 11 | 0 | 46 | 1 | 6352040 | 7883600 | 1531560 | 1 | #REF! | 1531560 | 1552150.2079 | Banosree | Banasree 33/11 SS | 99 | 2014405.8899 | 2216426.2192 | 2155463.3498 | 2252151.7613 | 2213991.1776 | 2027033.5767
443 | Larive | F299L | 11 | 0 | 47 | 1 | 3120560 | 3914200 | 793640 | 1 | 0 | 793640 | 804309.6523 | Banosree | Banasree 33/11 SS | 99 | 1248158.3596 | 1177386.9105 | 1133778.6787 | 1209136.6977 | 1154817.1834 | 1075325.8802
444 | Bank Colony | A299K | 11 | 0 | 0 | 1 | 8053280 | 8610600 | 557320 | 1 | 0 | 557320 | 564812.5793 | Khilgaon | Banasree 33/11 SS | 99 | 1882703.3 | 767992.5927 | 745817.2151 | 791659.8328 | 743707.201 | 684269.1356
445 | Salambagh | A299G | 11 | 0 | 0 | 1 | 6381080 | 6829880 | 448800 | 1 | 0 | 448800 | 454833.6424 | Khilgaon | Banasree 33/11 SS | 99 | 1308766.6526 | 927562.3697 | 1031151.1096 | 794065.0493 | 937481.2326 | 1234217.735
446 | Titas Road | A299T | 11 | 0 | 0 | 1 | 4635200 | 4913000 | 277800 | 1 | 0 | 277800 | 281534.7278 | Khilgaon | Banasree 33/11 SS | 99 | 1393019.0625 | 401204.0106 | 522157.3704 | 387724.9431 | 442215.7606 | 461564.0031
447 | AT-1 | 0 | 0.415 | 0 | 7734 | 1 | 3534.86 | 3571.06 | 36.2 | 1 | 0 | 36.2 | 36.6867 | Banosree | Banasree 33/11 SS | 99 | 64.6367 | 66.5715 | 73.8423 | 76.0089 | 145.5702 | 0
448 | AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 99 | 0 | 0 | 0 | 0 | 0 | 0
449 | Meradia | F214M | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 170 | 2001056.4 | 2033879.5103 | Banosree | Goran 33/11KV S/S | 14 | 378160.5224 | 0 | 0 | 0 | 0 | 0
450 | Shipahibagh | A914S | 11 | 0 | HA-021001030-02 | 1 | 42070870 | 43252680 | 1181810 | 1 | 0 | 1181810 | 1201195.1008 | Bashabo | Goran 33/11KV S/S | 14 | 1194417.5741 | 1488941.4076 | 1499139.6523 | 1654071.9922 | 1292900.8718 | 1411235.5236
451 | Farazi Hospital | F214F | 11 | 0 | HA-030701081-03 | 1 | 51724280 | 52545470 | 821190 | 1 | 0 | 821190 | 834659.8902 | Banosree | Goran 33/11KV S/S | 14 | 663014.2572 | 614880.5841 | 0 | 0 | 0 | 0
452 | West Bansree | F214W | 11 | 0 | New Meter | 1 | 98404140 | 99726960 | 1322820 | 1 | 0 | 1322820 | 1344518.0725 | Banosree | Goran 33/11KV S/S | 14 | 1500984.3633 | 1948580.2361 | 1917412.8456 | 1975561.8751 | 1966878.4605 | 1837316.4777
453 | Model School(Nearest) | F214D | 11 | 0 | HA-030701099-03 | 1 | 24729160 | 26588810 | 1859650 | 1 | 0 | 1859650 | 1890153.6365 | Banosree | Goran 33/11KV S/S | 14 | 2273552.5905 | 2474165.667 | 2481856.1691 | 2525253.4223 | 2475694.1412 | 2316464.2537
454 | Bhuiyan Para | F214V | 11 | 0 | HA-021100508-02 | 1 | 63138610 | 64706638 | 1568028 | 1 | 0 | 1568028 | 1593748.1926 | Banosree | Goran 33/11KV S/S | 14 | 2480699.3677 | 2656699.6806 | 2382096.4852 | 2607870.9453 | 2554505.4549 | 2408712.741
455 | Bonobithi (Ideal) School | F214B | 11 | 0 | HA-021100879-02 | 1 | 20164310 | 21242510 | 1078200 | 1 | 0 | 1078200 | 1095885.5972 | Banosree | Goran 33/11KV S/S | 14 | 1387260.9532 | 1569496.2633 | 1543598.2091 | 1587554.1504 | 1568260.1835 | 1428642.8767
456 | AT-01 | 0 | 0.415 | 0 | 3043122 | 1 | 7030.2 | 7030.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 14 | 562.2168 | 0 | 0 | 0 | 0 | 0
457 | AT-02 | 0 | 0.415 | 0 | 3043146 | 1 | 5084.2 | 5084.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 14 | 11959.1548 | 5508.1614 | 6933.6386 | 6257.2038 | 5424.4075 | 4669.3803
458 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1412510.4 | 1437106.4117 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1468016.3082 | 1541495.5501 | 1473463.6679 | 1695740.7049 | 1418643.1678 | 1399733.2864
459 | Bangabobondhu museum | D207B | 11 | Export | 0 | 1 | 629342 | 629342 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 1906.9492 | 0 | 0 | 0 | 0
460 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 86479670 | 87980510 | 1500840 | 1 | 0 | 1500840 | 1526974.093 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1886658.0381 | 1858256.0346 | 2288167.324 | 2330507.8061 | 2062161.6863 | 2160918.3029
461 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 7608679 | 8383244 | 774565 | 1 | 0 | 774565 | 788052.4828 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 2056165.5278 | 2227970.4742 | 2396456.6421 | 1846222.5257 | 2324395.3174 | 2181617.4346
462 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 0 | 0 | 0 | 0 | 0
463 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26183.9 | 26317.7 | 133.8 | 3333.33 | 0 | 445999.554 | 453765.7341 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 575970.5227 | 619531.2198 | 632620.8461 | 655652.5794 | 676925.663 | 643438.6457
464 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 71012.2 | 71326.8 | 314.6 | 3333.33 | 0 | 1048665.618 | 1066926.0087 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1423833.9987 | 1532206.4801 | 1409263.8848 | 1205565.6057 | 1637075.4163 | 1478674.7103
465 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 79007.3 | 79310 | 302.7 | 3333.33 | 0 | 1008998.991 | 1026568.6676 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1364158.3566 | 1534221.2158 | 1535115.0531 | 1547367.0274 | 1547019.5294 | 1459995.3095
466 | Road 25 | D207C | 11 | Export | 0 | 1 | 71389.6 | 71667.3 | 277.7 | 3333.3 | 0 | 925657.41 | 941775.8615 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1290390.3315 | 1318296.8446 | 1268595.2792 | 1429491.6026 | 1320696.1949 | 1108412.3257
467 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38220.6 | 38312.4 | 91.8 | 3333.33 | 0 | 305999.694 | 311328.0598 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 402642.9556 | 432160.8021 | 453939.1071 | 448887.9755 | 428853.4986 | 403274.921
468 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 63193708 | 64469326 | 1275618 | 1 | 0 | 1275618 | 1297830.3074 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1076949.6203 | 939422.8232 | 963337.8167 | 1202715.5447 | 1761856.4725 | 924073.8841
469 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 76131211 | 76131211 | 0 | 1 | Estimated | 1624386.96 | 1652672.3734 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 2233224.3406 | 2307141.6064 | 2239410.379 | 2263478.6281 | 2215613.0537 | 2070071.1797
470 | Lab aid/local RMU | C302L | 11 | 0 | 3C65883 | 1 | 73195 | 76794 | 3599 | 300 | 0 | 1079700 | 1099246.4449 | Paribag | Green Road 33/11KV S/S | 2 | 1368745.9116 | 1391721.2231 | 1482077.1317 | 1556841.7376 | 1536617.643 | 1422394.5672
471 | Green View | C302V | 11 | 0 | DHK000151 | 1 | 68313.2 | 68593.9 | 280.7 | 3333.33 | 0 | 935665.731 | 952604.6387 | Paribag | Green Road 33/11KV S/S | 2 | 1155247.0433 | 1226741.8962 | 1226475.691 | 1233531.7182 | 1202336.4681 | 1154869.3417
472 | Central Road | C302C | 11 | 0 | 65943 | 1 | 37616 | 41167 | 3551 | 300 | 0 | 1065300 | 1084585.7532 | Paribag | Green Road 33/11KV S/S | 2 | 1542540.4225 | 1699791.5522 | 1668170.2521 | 1747192.6716 | 1761466.4931 | 1692090.5953
473 | New Market | D802N | 11 | 0 | DHK000194 | 1 | 47697.9 | 48019.6 | 321.7 | 3333.33 | 0 | 1072332.261 | 1091745.3233 | Jigatola | Green Road 33/11KV S/S | 2 | 1265157.8423 | 1241755.0551 | 1233547.6266 | 1104020.9274 | 1190965.2748 | 1011316.673
474 | DPH Feeder | 0 | 11 | 0 | HA-021100459 | 1 | 41984 | 42140.3 | 156.3 | 1 | 25 | 294273 | 299600.3974 | Paribag | Green Road 33/11KV S/S | 2 | 308510.2151 | 353437.7385 | 245765.8495 | 244229.1636 | 236205.0715 | 247670.0176
475 | Dhanmondi Rd 4(md Banglo | D802F | 11 | 0 | 6604464 | 1 | 4573.53 | 4589.51 | 15.98 | 60000 | 0 | 958800 | 976157.721 | Jigatola | Green Road 33/11KV S/S | 2 | 1290523.1633 | 1536748.4833 | 1456011.9715 | 1566178.5714 | 1573640.9477 | 1319464.1465
476 | Green Road East | C302X | 11 | 0 | HA-021101050 | 1 | 99752905 | 100777480 | 1024575 | 1 | 0 | 1024575 | 1043123.4845 | Paribag | Green Road 33/11KV S/S | 2 | 1394173.8849 | 1544603.3759 | 1523648.0314 | 1576340.6608 | 1533242.4019 | 1471624.0188
477 | North Road | C302Z | 11 | 0 | HA-021100884 | 1 | 85256362 | 86548201 | 1291839 | 1 | 0 | 1291839 | 1315225.9221 | Paribag | Green Road 33/11KV S/S | 2 | 1610609.432 | 1705708.7444 | 1708178.2525 | 1755468.3191 | 1721328.8161 | 1634915.8518
478 | Green road SS | C302W | 11 | 0 | DHK00135 | 1 | 22261302 | 23172245 | 910943 | 1 | 0 | 910943 | 927434.3375 | Paribag | Green Road 33/11KV S/S | 2 | 1235249.8127 | 1304162.391 | 1263700.5929 | 1250797.3933 | 1224610.5159 | 1315498.6273
479 | Plane Moszid | C302A | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 706255.2 | 719040.9537 | Paribag | Green Road 33/11KV S/S | 2 | 740424.5162 | 1001406.9258 | 1044504.8605 | 976916.6543 | 944820.2858 | 990680.0705
480 | Malancha | C302H | 11 | 0 | HA-021100953 | 1 | 37784204 | 39024399 | 1240195 | 1 | 0 | 1240195 | 1262646.9803 | Paribag | Green Road 33/11KV S/S | 2 | 1505893.42 | 1581374.6424 | 1473084.6514 | 1290839.3587 | 1378192.0129 | 1148505.9825
481 | AT -1 | 0 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5090.5179 | Paribag | Green Road 33/11KV S/S | 2 | 5072.8112 | 5004.3913 | 5051.3876 | 5019.8031 | 5016.7079 | 5090.5253
482 | North Dhanmondi | C31002 | 11 | 0 | BD 014039 | 1 | 23293.96 | 23783.66 | 489.7 | 2000 | 0 | 979400 | 970901.1912 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1220415.3715 | 539516.6063 | 454897.5939 | 484039.8994 | 504079.3978 | 452285.2955
483 | Lake circus | C31004 | 11 | 0 | BD 014047 | 1 | 38490.6 | 39176.51 | 685.91 | 2000 | 0 | 1371820 | 1359915.9406 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1817014.2474 | 1989795.0818 | 1922931.395 | 2034236.8602 | 2046787.3073 | 1887308.9386
484 | Bashir Uddin | C31003 | 11 | 0 | BD 014037 | 1 | 15568.84 | 15830.71 | 261.87 | 2000 | 0 | 523740 | 519195.2113 | Paribag | Green Road Dormatory 33/11 SS | 100 | 699693.4639 | 775365.5929 | 750942.0597 | 792213.6477 | 798302.5936 | 740604.9957
485 | Raza Bazar | D5100R | 11 | 0 | BD 013939 | 1 | 23208.95 | 23815.99 | 607.04 | 2000 | 0 | 1214080 | 1203544.7399 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1251949.7098 | 1335486.8536 | 1305339.0743 | 1333290.6732 | 1329360.3858 | 1277085.001
486 | Rasel Squar | D5100RS | 11 | 0 | BD 013970 | 1 | 35203.1 | 35887.97 | 684.87 | 2000 | 0 | 1369740 | 1357853.9899 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1818453.1535 | 1979472.6721 | 1896362.0126 | 1946515.3317 | 1986224.7792 | 1860400.7233
487 | Bow Bazar | D5100O | 11 | 0 | BD 013967 | 1 | 26056.32 | 26716.98 | 660.66 | 2000 | 0 | 1321320 | 1309854.1577 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1211822.467 | 1271865.4648 | 1228245.6279 | 1315379.6859 | 1361417.0663 | 1195690.6937
488 | BRB Hospital | D5100S | 11 | 0 | BD 014003 | 1 | 14075.99 | 14382.67 | 306.68 | 2000 | 0 | 613360 | 608037.5277 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 807753.2915 | 817558.9445 | 861081.3012 | 841735.8151 | 735319.9448 | 733624.2823
489 | Green Road North | C31008 | 11 | 0 | BD 013969 | 1 | 17173.89 | 17616.03 | 442.14 | 2000 | 0 | 884280 | 876606.6014 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1205661.5166 | 1207219.8681 | 1206463.1592 | 1244662.5143 | 1225136.5003 | 1163648.4072
490 | Water Bhaban | D5100PB | 11 | 0 | BD 014004 | 1 | 5589.6 | 5723.95 | 134.35 | 2000 | 0 | 268700 | 266368.3378 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 341567.9548 | 321038.9901 | 360889.0448 | 369844.7631 | 332111.9703 | 301428.8307
491 | Alamin Road | C31007 | 11 | 0 | BD 014006 | 1 | 19439.5 | 19724.04 | 284.54 | 2000 | 0 | 569080 | 564141.7704 | Paribag | Green Road Dormatory 33/11 SS | 100 | 583425.7911 | 637499.1681 | 607978.2671 | 645158.196 | 644406.723 | 578607.7993
492 | Katal Bagan | C3100K | 11 | 0 | 0 | 1 | 10936.14 | 11681.91 | 745.77 | 2000 | 0 | 1491540 | 1478597.0623 | Paribag | Green Road Dormatory 33/11 SS | 100 | 2049711.7232 | 2213293.3253 | 2170885.4799 | 2232426.2667 | 2461917.3517 | 1880307.9323
493 | Eastern Pantho chaya | C310010 | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 100 | 0 | 0 | 0 | 0 | 0 | 0
494 | Kalabagan | 0 | 11 | 0 | BD 014005 | 1 | 6224.11 | 6367.44 | 143.33 | 2000 | 0 | 286660 | 284172.4888 | Paribag | Green Road Dormatory 33/11 SS | 100 | 308027.2544 | 333048.3305 | 321346.724 | 343995.7229 | 360201.2398 | 320179.3518
495 | Univer Hospital | C310012 | 11 | 0 | BD 013963 | 1 | 1281.57 | 1392.56 | 110.99 | 2000 | 0 | 221980 | 220053.7538 | Paribag | Green Road Dormatory 33/11 SS | 100 | 258516.7219 | 265852.2552 | 274362.5626 | 281740.4351 | 275219.2974 | 258266.1053
496 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 | 0 | BD 013971 | 1 | 10529.2 | 10701.31 | 172.11 | 2000 | 0 | 344220 | 341233.008 | Paribag | Green Road Dormatory 33/11 SS | 100 | 477291.2605 | 521121.028 | 519641.6074 | 508095.8262 | 507213.6524 | 520651.6433
497 | Matir Masjid | A229S | 11 | 0 | DHK00170 | 1 | 29471.9 | 31256.8 | 1784.9 | 888.8889 | 0 | 1586577.7778 | 1604310.6045 | Khilgaon | Taltola 33/11KV S/S | 29 | 1914137.6974 | 2132185.0742 | 2085431.7227 | 2167154.5553 | 2177028.2382 | 2023352.6919
498 | Hajipara | A229P | 11 | 0 | DHK-00108 | 1 | 6219.3 | 7020.3 | 801 | 2222.2222 | 0 | 1780000 | 1799894.6638 | Khilgaon | Taltola 33/11KV S/S | 29 | 1077292.6606 | 2330316.32 | 2323985.9847 | 2257545.6108 | 2323390.6234 | 1505682.5673
499 | Nearest Feeder | A929N | 11 | 0 | DHK-00106 | 1 | 91617.7 | 92041.4 | 423.7 | 2222.222 | 0 | 941555.4614 | 952079.0172 | Bashabo | Taltola 33/11KV S/S | 29 | 736977.684 | 448845.991 | 661064.6612 | 0 | 0 | 102528.7436
500 | Reazbagh | A229C | 11 | 0 | DHK-00109 | 1 | 98320.2 | 98929.8 | 609.6 | 2222.222 | 0 | 1354666.5312 | 1369807.3375 | Khilgaon | Taltola 33/11KV S/S | 29 | 1677297.9566 | 1831327.1429 | 1773544.5971 | 1831021.0001 | 1850181.9906 | 1693614.7124
501 | Chowdhury Para | A229F | 11 | 0 | DHK-00107 | 1 | 53269.4 | 53518 | 248.6 | 2222.222 | 0 | 552444.3892 | 558618.9372 | Khilgaon | Taltola 33/11KV S/S | 29 | 561029.5515 | 662951.963 | 585903.1258 | 625509.6106 | 653692.0598 | 575139.5465
502 | Model Colleg | A229D | 11 | 0 | 9122392 | 1 | 2584.74 | 2601.93 | 17.19 | 40000 | 0 | 687600 | 695285.1522 | Khilgaon | Taltola 33/11KV S/S | 29 | 561252.3268 | 1334690.1699 | 1248930.587 | 1283320.9871 | 723685.6707 | 1038453.9207
503 | East Rampura | A229B | 11 | 0 | DHK-00181 | 1 | 99587.6 | 100070 | 482.4 | 2222.222 | 0 | 1071999.8928 | 1083981.397 | Khilgaon | Taltola 33/11KV S/S | 29 | 632299.6811 | 1183684.3115 | 1041555.9945 | 1373711.9053 | 1177184.4648 | 1381135.5698
504 | Adarshabagh | A929A | 11 | 0 | DHK-00090 | 1 | 52389.5 | 53089.4 | 699.9 | 2222.222 | 0 | 1555333.1778 | 1572716.7906 | Bashabo | Taltola 33/11KV S/S | 29 | 2035653.077 | 2182105.9426 | 2139761.9297 | 2323799.4344 | 2249760.2414 | 2012766.0076
505 | Khailgaon Govt Colony | A229K | 11 | 0 | DHK00167 | 1 | 77198.2 | 77744.9 | 546.7 | 2222.222 | 0 | 1214888.7674 | 1228467.3088 | Khilgaon | Taltola 33/11KV S/S | 29 | 1508476.8371 | 1632974.0455 | 1590881.9934 | 1651220.4486 | 1644511.4325 | 1548206.2687
506 | TV Road | A214T | 11 | 0 | 6604434 | 1 | 5147.41 | 5174.98 | 27.57 | 40000 | 0 | 1102800 | 1115125.7501 | Khilgaon | Taltola 33/11KV S/S | 29 | 339156.7632 | 1446513.4037 | 1300316.995 | 1457589.2313 | 1435653.3713 | 1278251.1059
507 | Post Office | 0 | 11 | 0 | 06604476 | 1 | 6635.86 | 6654.54 | 18.68 | 40000 | 0 | 747200 | 755551.2881 | Bashabo | Taltola 33/11KV S/S | 29 | 1009051.5047 | 850255.946 | 1067472.334 | 544086.3384 | 925315.57 | 631719.4629
508 | Navana | A929V | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 0
509 | Shantipur | A929P | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0 | 232625.2878
510 | AT-01 | 0 | 0.415 | 0 | 9187958 | 1 | 787.71 | 790.37 | 2.66 | 80 | 0 | 212.8 | 215.1784 | Bashabo | Taltola 33/11KV S/S | 29 | 17609.6926 | 22368.6405 | 0 | 0 | 388.7134 | 5004.1149
511 | AT-02 | 0 | 0.415 | 0 | 9187959 | 1 | 237.76 | 237.76 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 164.5672 | 981.0492 | 0 | 0 | 1243.317 | 0
512 | Sher-e-Banglanagar Local | 0 | 11 | 0 | DHK 66503 | 1.28 | 84325 | 85742 | 1417 | 60 | 11 kv bus-1 R Phase PT missing | 108825.6 | 109846.5171 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 124871.9678 | 133378.1778 | 145611.0642 | 127632.9783 | 130259.0089 | 137740.1655
513 | Mirpur Road East | D550F | 11 | 0 | DHK 60961 | 1.28 | 849497 | 854603 | 5106 | 60 | 0 | 392140.8 | 395819.5598 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 504909.4833 | 511825.2027 | 595499.8531 | 565408.7832 | 579726.769 | 591320.8565
514 | Gonobhaban school | D550E | 11 | 0 | DHK 66492 | 1.28 | 534506 | 536080 | 1574 | 60 | 0 | 120883.2 | 122017.2321 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 162123.6893 | 177174.8965 | 204772.9102 | 187053.4171 | 201293.1928 | 178100.36
515 | Babor Road | D450B | 11 | 0 | DHK 66489 | 1.28 | 791315 | 798679 | 7364 | 60 | 0 | 565555.2 | 570860.7987 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 723610.3177 | 1641262.4555 | 827030.8546 | 821146.7988 | 2355047.2749 | 1531864.2685
516 | College Gate | D450K | 11 | 0 | DHK 66487 | 1.28 | 2705027 | 2718507 | 13480 | 60 | 0 | 1035264 | 1044976.0411 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 1347445.4847 | 1954707.1976 | 2003387.1217 | 2118896.2632 | 2029429.4244 | 1693179.314
517 | Parade ground | 0 | 11 | 0 | DHK 66490 | 1.28 | 938426 | 938469 | 43 | 60 | 0 | 3302.4 | 3333.3805 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 6820.7377 | 4879.6894 | 117.618 | 1062.133 | 1780.3054
518 | Hospital RMU | D550H | 11 | 0 | DHK 66491 | 1.28 | 921595 | 927197 | 5602 | 60 | 0 | 430233.6 | 434269.7168 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 581861.3963 | 629901.6383 | 661895.205 | 606359.9098 | 560499.4711 | 544171.0965
519 | Shamoly Square | 0 | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 0 | 0 | 0 | 0 | 0 | 0
520 | Gonobhaban RMU | D550D | 11 | 0 | DHK 60964 | 1 | 197469.2 | 198714.3 | 1245.1 | 60 | 0 | 74706 | 75406.8335 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 93681.1141 | 88021.1633 | 97246.5492 | 98796.0682 | 102753.2911 | 81921.1363
521 | Krishi University | D550V | 11 | 0 | DHK 60963 | 1 | 378971.9 | 386593 | 7621.1 | 60 | 0 | 457266 | 461555.7137 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 534152.4164 | 582966.2552 | 608461.3549 | 589560.5067 | 563852.3796 | 574020.0379
522 | NEC | D550X | 11 | 0 | DHK 86073 | 1 | 47.94 | 51.31 | 3.37 | 60000 | 0 | 202200 | 204096.883 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 274760.4607 | 284784.5503
523 | Novo Theater/Army Musium (41%) | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 417.87 | 432.4 | 14.53 | 60000 | 0 | 357438 | 360791.2051 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 457676.9299 | 439900.9902 | 454264.1779 | 491118.4828 | 467152.1267 | 453385.8053
524 | Novo Theater/Army Musium (59%) | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 417.87 | 432.4 | 14.53 | 60000 | 0 | 514362 | 519187.344 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 658608.2649 | 633028.2541 | 653697.2316 | 706731.4752 | 672243.3043 | 652433.232
525 | Netor | 0 | 11 | 0 | DHK 60962 | 1 | 143367.9 | 150829.4 | 7461.5 | 60 | 0 | 447690 | 451889.8792 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 546388.7354 | 587213.3923 | 617847.27 | 628517.1836 | 620062.5542 | 596532.4766
526 | BICC | D550VV | 11 | 0 | 0 | 1 | 47.94 | 51.31 | 3.37 | 60000 | 0 | 202200 | 204096.883 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 264748.3525 | 251816.0719 | 276990.3524 | 279104.941 | 193459.8492 | 69152.9813
527 | Auxiliary | 0 | 0.415 | 0 | 0 | 1 | 5396.67 | 5439.49 | 42.82 | 60 | 0 | 2569.2 | 2593.3022 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 3246.9365 | 3802.5432 | 2988.0849 | 4296.3279 | 3895.3081 | 5642.8833
528 | City Corporation | A997Y | 11 | 0 | 93 | 1 | 44005332 | 44783932 | 778600 | 1 | 0 | 778600 | 776082.8806 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 996604.0058 | 1085361.1698 | 1583920.0344 | 672002.1574 | 951549.8845 | 660250.7383
529 | Bot tola | B297L | 11 | 0 | 0 | 1 | 60692692 | 62504888 | 1812196 | 1 | 0 | 1812196 | 1806337.3901 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 2300581.3394 | 2406944.4276 | 2386526.2912 | 2395209.9678 | 2298336.7826 | 2240795.0697
530 | Jhilpar | B997J | 11 | 0 | 145 | 1 | 37775588 | 38598064 | 822476 | 1 | 0 | 822476 | 819817.0349 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 964321.9183 | 1048862.0833 | 1018967.1456 | 1203846.2525 | 1011093.8025 | 1160185.3486
531 | Central Bashaboo | A997C | 11 | 0 | 128 | 1 | 42422256 | 43766652 | 1344396 | 1 | 0 | 1344396 | 1340049.7308 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1729561.5012 | 1906586.5613 | 1065915.018 | 2018436.7723 | 1763582.1465 | 1733572.9987
532 | Kadamtala | B997L | 11 | 0 | 8 | 1.5 | 20022992 | 20429350 | 406358 | 1 | 0 | 609537 | 607566.4408 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 808410.7915 | 737461.0018 | 659233.1205 | 895857.2066 | 680353.9053 | 1958904.8441
533 | Ansar VDP | A297A | 11 | 0 | 119 | 1 | 21280468 | 21940426 | 659958 | 1 | 0 | 659958 | 657824.4358 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 97 | 1198004.0816 | 522827.1096 | 571466.9061 | 611327.4182 | 1128730.4864 | 727503.1317
534 | Mugda Hospital Express-01 | B997H | 11 | 0 | 0 | 1 | 6811903 | 7018583 | 206680 | 1 | 0 | 206680 | 206011.8286 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 296418.3041 | 309430.1308 | 314267.439 | 307500.5637 | 293639.1125 | 272764.3875
535 | Boro Masjid | B997Z | 11 | 0 | 7 | 1.22 | 51357956 | 52337832 | 979876 | 1 | 0 | 1195448.72 | 1191583.9793 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 1366718.9494 | 1456683.3289 | 1401094.4155 | 1717015.7129 | 1405726.812 | 1342757.2732
536 | Anandodhara | B297B | 11 | 0 | 120 | 1 | 49877200 | 50564636 | 687436 | 1 | 0 | 687436 | 685213.6028 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 1028241.2626 | 986769.0262 | 991611.9155 | 1008287.8477 | 964251.0175 | 915566.0508
537 | Culvert | A997L | 11 | 0 | 117 | 1 | 44077932 | 45451008 | 1373076 | 1 | 0 | 1373076 | 1368637.0118 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1587860.9817 | 1735000.3001 | 1917088.0393 | 2175998.5274 | 1824104.3237 | 1912589.1389
538 | Mugda Hospital Express-02 | 0 | 11 | 0 | 97 | 1 | 4845548 | 4870948 | 25400 | 1 | 0 | 25400 | 25317.8849 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0 | 0 | 0 | 0
539 | Jhor Pukur | A997J | 11 | 0 | 98 | 1 | 29356208 | 29587808 | 231600 | 1 | 0 | 231600 | 230851.2653 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 807820.7106 | 1233989.5056 | 952311.2849 | 1695311.8425 | 1643349.6255 | 1429146.8866
540 | T&T | B997T | 11 | 0 | 99 | 1 | 25139698 | 25731818 | 592120 | 1 | 0 | 592120 | 590205.7479 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 628322.5712 | 593432.5647 | 596600.2068 | 721459.9725 | 567104.166 | 852556.8368
541 | Haider Ali | B297H | 11 | 0 | 9 | 1 | 74741936 | 76603816 | 1861880 | 1 | 0 | 1861880 | 1855860.7678 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 2415267.9161 | 2486025.7818 | 2500945.5412 | 2687168.9248 | 2028073.3969 | 1439434.5953
542 | 11kv Tilpapara | A929T | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 1647928.8 | 1642601.2461 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 2219790.0622 | 2267480.2014 | 2153708.0482 | 2169910.6664 | 2181802.1625 | 2151612.2434
543 | AT-01 | 0 | 11 | 0 | 0 | 1 | 3207.07 | 3262 | 54.93 | 1 | 0 | 54.93 | 54.7524 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 80.2692 | 86.077 | 79.9328 | 89.8242 | 94.3756 | 0
544 | AT-02 | 0 | 11 | 0 | 0 | 1 | 17.34 | 17.34 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0 | 0.34315 | 0 | 8.4563
545 | Shantinagar s/s-1 | 0 | 11 | 0 | DHK60932 | 1 | 397140 | 430321 | 33181 | 60 | 0 | 1990860 | 1995495.3946 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1888358.4836 | 1327460.0638 | 1164408 | 2916346.3506 | 2755360.6206 | 2616486.0095
546 | Gulbagh | D606G | 11 | 0 | DHK60934 | 1 | 175960 | 189715 | 13755 | 60 | 0 | 825300 | 827221.5772 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1048994.4227 | 1110222.7304 | 1081462.2 | 329175.3109 | 325114.8574 | 314880.9114
547 | Rampura BTV | A206H | 11 | 0 | DHK60933 | 1 | 14073 | 14076 | 3 | 60 | 0 | 180 | 180.4191 | Khilgaon | Khillgaon 33/11KV S/S | 6 | 0 | 0 | 0 | 0 | 1220.4011 | 241.3343
548 | West Shantibag | D606W | 11 | 0 | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 706255.2 | 707899.6007 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1098102.3361 | 1003916.3939 | 885668.7 | 934072.7507 | 932020.3326 | 912726.2746
549 | East Malibagh | D606E | 11 | 0 | DHK60929 | 1 | 648732 | 665295 | 16563 | 60 | 0 | 993780 | 996093.8555 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1225702.646 | 1396586.5654 | 1214224.2 | 1558104.7013 | 1377100.6198 | 1289630.0978
550 | Police Line | D606S | 11 | 0 | DHK60930 | 1 | 594185 | 601907 | 7722 | 60 | 0 | 463320 | 464398.7655 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 567380.2526 | 593599.4922 | 600534.9 | 624772.6414 | 596226.9654 | 576125.2774
551 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 | 0 | DHK61017 | 1 | 199938 | 201786 | 1848 | 60 | 0 | 110880 | 111138.1661 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 133734.902 | 145615.9492 | 150301.2 | 152458.8445 | 149621.1769 | 146188.2445
552 | Benjir Bagan | D662R | 11 | 0 | DHK60985 | 1 | 173708 | 175954 | 2246 | 60 | 0 | 134760 | 135073.7668 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 193500.3195 | 197704.2286 | 195610.8 | 195480.6318 | 194653.9781 | 180699.0476
553 | AT-1 & AT-2 | 0 | 0.415 | 0 | ELIB 7374 | 1 | 2332.2 | 2427 | 94.8 | 60 | 0 | 5688 | 5701.2436 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 7360.8364 | 7097.6366 | 6669.159 | 7349.5039 | 14431.2432 | 0
554 | Spare | 0 | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0
555 | Monipuripara west | D572W | 11 | 0 | BD013947 | 1 | 32779.66 | 33710.12 | 930.46 | 1000 | 0 | 930460 | 935544.6228 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 814448.4485 | 843758.793 | 830035.6978 | 847623.509 | 861249.4503 | 873090.4062
556 | Biggan College | C672BC | 11 | 0 | BD013949 | 1 | 20808.54 | 21787.07 | 978.53 | 1000 | 0 | 978530 | 983877.3078 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 910214.7983 | 898340.4903 | 876599.5577 | 835521.2072 | 819870.1443 | 853994.1863
557 | Green Road South | D572G | 11 | 0 | BD013948 | 1 | 31642.23 | 32252.24 | 610.01 | 1000 | 0 | 610010 | 613343.481 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 1046963.2451 | 997691.2194 | 972408.44 | 975210.3173 | 1037302.1428 | 986346.7996
558 | BARC Building O/H | D572B | 11 | 0 | BD014010 | 1 | 14574.54 | 14613.61 | 39.07 | 1000 | 0 | 39070 | 39283.5032 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 553036.0194 | 605164.5353 | 601022.2433 | 634425.9824 | 629218.3029 | 632910.7169
559 | Indira Road (Green Road North) | D572NN | 11 | 0 | BD014036 | 1 | 62546.1 | 63504.96 | 958.86 | 1000 | 0 | 958860 | 964099.8184 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 1738404.7784 | 1930586.7401 | 1889476.4806 | 1966221.9789 | 1919532.2257 | 1871294.3358
560 | Chundrima Uddan | D572C | 11 | 0 | BD014035 | 1 | 32013.76 | 32488.76 | 475 | 1000 | 0 | 475000 | 477595.7009 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 964413.0153 | 995724.673 | 1002061.8966 | 1070591.3324 | 1032887.2799 | 1015615.1889
561 | RMU-1 Feeder | 0 | 11 | 0 | BD013940 | 1 | 1047.79 | 1367.45 | 319.66 | 1000 | 0 | 319660 | 321406.8247 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 250904.1991 | 255319.9358 | 263025.0554 | 137015.3458 | 147255.7457 | 0
562 | Farmgate foot over bridge RMU | 0 | 11 | 0 | BD013946 | 1 | 63.59 | 239.33 | 175.74 | 1000 | 0 | 175740 | 176700.3547 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0
563 | kawran Bazar North | C672K | 11 | 0 | BD013964 | 1 | 40456.52 | 40517.44 | 60.92 | 1000 | 0 | 60920 | 61252.9055 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 77104.1375 | 81762.1785 | 77492.626 | 79448.9981 | 30221.7434 | 0
564 | NAM Bhanan RMU | D572NM | 11 | 0 | BD013950 | 1 | 18200.87 | 18967.08 | 766.21 | 1000 | 0 | 766210 | 770397.0568 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 959936.9135 | 1011015.5749 | 965308.8823 | 1005888.2452 | 1030950.7605 | 1013545.3917
565 | Novo Theater | 0 | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0
566 | Monipuripara Nearest | C172I | 11 | 0 | BD013962 | 1 | 39654.38 | 40098.87 | 444.49 | 1000 | 0 | 444490 | 446918.9749 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 732201.3407 | 808641.8922 | 823257.478 | 844317.6909 | 794156.578 | 733061.8614
567 | Holy Cross | C172HC | 11 | 0 | BD013965 | 1 | 39906.37 | 40933.65 | 1027.28 | 1000 | 0 | 1027280 | 1032893.7086 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 1312589.0703 | 1258529.5254 | 1242673.6384 | 1267377.9768 | 1286005.418 | 1126874.592
568 | Honda Goli | C172HG | 11 | 0 | BD014011 | 1 | 16352.73 | 17161.03 | 808.3 | 1000 | 0 | 808300 | 812717.0632 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 996766.2388 | 1069470.1647 | 1059189.7376 | 1074102.0051 | 1068926.6085 | 953126.0337
569 | Navy Quarter | C172NQ | 11 | 0 | BD013941 | 1 | 5723.59 | 5981.54 | 257.95 | 1000 | 0 | 257950 | 259359.6022 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 175972.436 | 196544.2773 | 221522.2664 | 200143.5254 | 202962.2853 | 175339.91
570 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 2141.19 | 2170.58 | 29.39 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0
571 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 585.48 | 641.32 | 55.84 | 1 | 0 | 55.84 | 56.1451 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0 | 0
572 | Doctor Goli | D1113D | 11 | 0 | BD013944 | 1 | 10546.84 | 11220.97 | 674.13 | 1000 | 0 | 674130 | 680371.3877 | Moghbazar | Ispahani 33/11 KV SS | 113 | 917384.4784 | 958125.7556 | 963950.8063 | 948233.0953 | 958270.3835 | 898591.0283
573 | Ispahani | D1113S | 11 | 0 | BD013947 | 1 | 11780.12 | 12560.14 | 780.02 | 1000 | 0 | 780020 | 787241.7632 | Moghbazar | Ispahani 33/11 KV SS | 113 | 1000362.3505 | 1092016.0616 | 1087721.0462 | 1055882.4039 | 1058199.8531 | 999582.0108
574 | BTCL | C6113BT | 11 | 0 | BD013949 | 1 | 6098.75 | 6628.46 | 529.71 | 1000 | 0 | 529710 | 534614.2847 | Kakrail | Ispahani 33/11 KV SS | 113 | 552136.017 | 523407.6855 | 549951.6967 | 529591.2713 | 523726.617 | 532492.3633
575 | Vikarunnesa | C6113VQ | 11 | 0 | BD013948 | 1 | 8561.61 | 9308.85 | 747.24 | 1000 | 0 | 747240 | 754158.2718 | Kakrail | Ispahani 33/11 KV SS | 113 | 1059198.2594 | 1138092.7736 | 1152044.6426 | 1148347.0254 | 1136233.5895 | 1092064.7445
576 | OASIS | 0 | 11 | 0 | 0 | 1 | 310.99 | 424 | 113.01 | 1000 | 0 | 113010 | 114056.2956 | Kakrail | Ispahani 33/11 KV SS | 113 | 109560.3611 | 90109.3741 | 109400.2883 | 4342.8205 | 0 | 0
577 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
578 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
579 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
580 | Wireless | D1113W | 11 | 0 | 0 | 1 | 9982.44 | 10751.41 | 768.97 | 1000 | 0 | 768970 | 776089.4575 | Moghbazar | Ispahani 33/11 KV SS | 113 | 1063107.1511 | 1088068.9306 | 1084178.7327 | 1047125.901 | 1048087.1638 | 896344.5253
581 | Kazir Goli | C6113KG | 11 | 0 | 0 | 1 | 9531.61 | 10477.16 | 945.55 | 1000 | 0 | 945550 | 954304.3117 | Kakrail | Ispahani 33/11 KV SS | 113 | 1072332.5406 | 1195416.795 | 1197081.1949 | 1203659.779 | 1263311.3532 | 1182067.1763
582 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
583 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
584 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
585 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
586 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
587 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
588 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
589 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0 | 0
590 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | T1 | XA587377 | 1.1 | 220112.5 | 221836.7 | 1724.2 | 1000 | 0 | 1896620 | 1907566.3908 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2264304.2356 | 2396448.119 | 2486440.3485 | 2725888.0748 | 2549641.8301 | 2438789.3271
591 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | T1 | XA587359 | 1.1 | 17238.9 | 17327.3 | 88.4 | 1000 | 0 | 97240 | 97801.2231 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 114438.0991 | 122268.7906 | 127832.1205 | 148265.7961 | 145583.9006 | 138711.8093
592 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | T1 | XA586385 | 1.1 | 112545.1 | 113678.5 | 1133.4 | 1000 | 0 | 1246740 | 1253935.5917 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1366513.6955 | 1396305.5531 | 1491140.0618 | 1611243.3589 | 1535819.0344 | 1523513.0022
593 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | T1 | XA587376 | 1.1 | 177164.8 | 179110.6 | 1945.8 | 1000 | 0 | 2140380 | 2152733.2578 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2379446.8789 | 2449713.7307 | 2507460.7365 | 2663481.8388 | 2529191.2405 | 2405949.7847
594 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | T1 | XA575929 | 1.1 | 7210.5 | 7300.2 | 89.7 | 1000 | 0 | 98670 | 99239.4764 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 85853.7366 | 56292.0669 | 68291.1171 | 54248.5581 | 41407.382 | 36566.7297
595 | 11 kV Monowar Feeder (F-6) | A828L | 11 | T2 | XA587363 | 1 | 78690 | 79934 | 1244 | 1000 | 0 | 1244000 | 1251179.7778 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1359166.3065 | 1319938 | 1387647.3379 | 1431264.5899 | 1311672.4727 | 1337959.5143
596 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | T2 | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0
597 | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 11 | T2 | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0
598 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | T2 | XA587358 | 1 | 153390.8 | 155175.3 | 1784.5 | 1000 | 0 | 1784500 | 1794799.2873 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2274671.0995 | 2350345.1179 | 2375002.1192 | 2446793.5192 | 2328937.4468 | 2238024.8856
599 | 11 KV Jhilpar (F-10) | E228Z | 11 | T2 | XA587369 | 1 | 101.8282 | 111.26 | 9.4318 | 40000 | 0 | 377272 | 379449.435 | Matuail | Siddhirganj 33/11KV S/S | 28 | 283444.1488 | 297629.6761 | 330706.0205 | 314747.6869 | 291293.3394 | 424399.7103
600 | 11 kV Madrasha Road Feeder (F-11) | 0 | 11 | T2 | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0
601 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | T2 | XA587383 | 1 | 16306.6 | 16870.9 | 564.3 | 1000 | 0 | 564300 | 567556.8719 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 709475.9549 | 663499.8644 | 692465.8927 | 722974.2051 | 681450.0937 | 758130.0486
602 | Seven Horse Feeder (F-13) | A828H | 11 | T2 | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0 | 0
603 | 11 kV Shanti Nagar (F-14) | A828N | 11 | T2 | XA587371 | 1 | 154796.1 | 156958.2 | 2162.1 | 1000 | 0 | 2162100 | 2174578.6154 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2726585.8445 | 2843859.0812 | 2866014.2453 | 2915044.2314 | 2806489.0873 | 2820775.6603
604 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 | 0 | HA021101013-02 | 1 | 54945696 | 57648360 | 2702664 | 1 | 0 | 2702664 | 2709931.5892 | Matuail | Demra 33/11KV S/S | 16 | 3182659.205 | 3242375.7883 | 2482601.3667 | 2346002.1943 | 2312393.5546 | 2206583.7096
605 | 11 kV DND (WASA) Feeder. | A816B | 11 | 0 | HA021100992-02 | 1 | 6447792 | 6452560 | 4768 | 1 | 0 | 4768 | 4780.8214 | Siddirgonj | Demra 33/11KV S/S | 16 | 190285.6191 | 296942.4232 | 349346.3885 | 251256.153 | 80170.7162 | 6927.7253
606 | 11 kV Local Feeder | A816D | 11 | 0 | HA021100794-02 | 1 | 13337258 | 14233810 | 896552 | 1 | 0 | 896552 | 898962.87 | Siddirgonj | Demra 33/11KV S/S | 16 | 1098339.8454 | 1209825.1625 | 1190157.3614 | 1182388.6301 | 2088621.9879 | 1417684.9395
607 | 11 kV Mouchak Feeder | A816A | 11 | 0 | DHK60888 | 1 | 1013189.5 | 1047240.6 | 34051.1 | 60 | 0 | 2043066 | 2048559.8995 | Siddirgonj | Demra 33/11KV S/S | 16 | 2345108.3326 | 2403503.8665 | 2439051.751 | 2339275.7144 | 2308639.9015 | 2074135.4747
608 | 11 kV Overhead-1 Feeder | A816C | 11 | 0 | HA021100829-02 | 1 | 79563317 | 79937310 | 373993 | 1 | 0 | 373993 | 374998.6846 | Siddirgonj | Demra 33/11KV S/S | 16 | 432331.1497 | 507759.6491 | 490206.9454 | 1190489.8427 | 1095153.438 | 1095304.9401
609 | 11 kV Provati Steel Feeder | A816Z | 11 | 0 | DHK60874 | 1 | 601475.9 | 609350.3 | 7874.4 | 60 | 0 | 472464 | 473734.4777 | Siddirgonj | Demra 33/11KV S/S | 16 | 572313.5546 | 603535.6264 | 2095360.2501 | 124835.9443 | 0 | 0
610 | 11 kV Islambagh Feeder. | E116I | 11 | 0 | DHKA2190 | 1 | 1179.7411 | 1212.637 | 32.8959 | 60000 | 0 | 1973754 | 1979061.5163 | Matuail | Demra 33/11KV S/S | 16 | 2382248.0982 | 2479849.2574 | 3031414.6894 | 2979112.0563 | 3002442.9965 | 2983539.0327
611 | 11 kV Taj Jute Feeder. | A816E | 11 | 0 | DHK61062 | 1 | 679906.6 | 702990.4 | 23083.8 | 60 | 0 | 1385028 | 1388752.4047 | Siddirgonj | Demra 33/11KV S/S | 16 | 1608771.849 | 1850699.8521 | 525126.6242 | 1404410.5059 | 1676660.8446 | 1675376.4941
612 | 11 kV Al-Aksa Steel Feeder | A816S | 11 | 0 | DHK61061 | 1 | 848208.6 | 877240.8 | 29032.2 | 60 | 0 | 1741932 | 1746616.1362 | Siddirgonj | Demra 33/11KV S/S | 16 | 1742517.141 | 1948104.7891 | 1679729.0047 | 1595509.5853 | 1474597.4818 | 1597579.1906
613 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 | 0 | DHKA2189 | 1 | 1116.5269 | 1151.187 | 34.6601 | 60000 | 0 | 2079606 | 2085198.1573 | Siddirgonj | Demra 33/11KV S/S | 16 | 2525197.0695 | 2620588.9584 | 2664152.1809 | 2514049.716 | 2467512.3805 | 2370283.5934
614 | 11 kV Over Head Feeder-2. | E116V | 11 | 0 | HA021100488-02 | 1 | 33418808 | 35111950 | 1693142 | 1 | 0 | 1693142 | 1697694.9376 | Demra | Demra 33/11KV S/S | 16 | 2095936.8227 | 2186616.3464 | 2197276.8827 | 2204224.8423 | 2131027.6013 | 2071443.4949
615 | 11 kV Shimrail Express Feeder. | A8164 | 11 | 0 | HA021100511-02 | 1 | 8254376 | 8254917 | 541 | 1 | 0 | 541 | 542.4548 | Siddirgonj | Demra 33/11KV S/S | 16 | 30546.5041 | 1269.0967 | 53083.1379 | 75076.7556 | 29225.6688 | 0
616 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 | 0 | HA021100413-02 | 1 | 82154657 | 82521598 | 366941 | 1 | 0 | 366941 | 367927.7214 | Demra | Demra 33/11KV S/S | 16 | 330954.2369 | 688064.1207 | 409117.6527 | 331227.7744 | 650733.1002 | 409613.9007
617 | 11 kV Siddhirgonj Mazar Feeder | 0 | 11 | 0 | HA021100393-02 | 1 | 26069.366 | 26893.78 | 824.414 | 1000 | 0 | 824414 | 826630.8876 | Siddirgonj | Demra 33/11KV S/S | 16 | 1127913.2115 | 1241829.7858 | 1214207.0897 | 1262090.4156 | 281800.301 | 832832.3648
618 | 11 kV AST Beverage Feeder | A816J | 11 | 0 | 0 | 1 | 23064522 | 23358696 | 294174 | 1 | 0 | 294174 | 294965.0476 | Siddirgonj | Demra 33/11KV S/S | 16 | 533291.7199 | 269111.0012 | 890478.2395 | 1164572.2996 | 1051751.2525 | 1163750.6238
619 | 11 kV Karim Market Feeder | E216K | 11 | 0 | 0 | 1 | 62687.216 | 64428.93 | 1741.714 | 1000 | 0 | 1741714 | 1746397.55 | Matuail | Demra 33/11KV S/S | 16 | 2153249.6409 | 2251573.1315 | 2292212.1727 | 2119617.9699 | 2072299.946 | 2089377.8867
620 | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 16 | 0 | 0 | 0 | 0 | 0 | 0
621 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 | 0 | 2007755114 | 1 | 5918.8 | 5962.59 | 43.79 | 60000 | 0 | 2627400 | 2656170.9356 | Demra | Sarulia 33/11KV S/S | 83 | 3219680.3589 | 3402160.7226 | 2567812.3685 | 2674737.7934 | 2648546.8605 | 3036942.6611
622 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 | 0 | 30799484 | 1 | 22.0742 | 22.3065 | 0.2323 | 60000 | 0 | 13938 | 14090.6259 | Demra | Sarulia 33/11KV S/S | 83 | 14581.402 | 14754.6723 | 14656.6857 | 14157.8637 | 13577.9934 | 12817.0467
623 | 11 kV Konapara (=L13) **** | E183KL | 11 | 0 | DHKA2191 | 1 | 2208.3613 | 2242.8601 | 34.4988 | 60000 | 0 | 2069928 | 2092594.4251 | Demra | Sarulia 33/11KV S/S | 83 | 2580974.9024 | 2723567.5839 | 3439291.4731 | 3588042.0557 | 3482255.5223 | 2467003.1131
624 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 | 0 | 575926 | 1 | 58574.2 | 60597 | 2022.8 | 1000 | 0 | 2022800 | 2044950.3572 | Matuail | Sarulia 33/11KV S/S | 83 | 2502341.7238 | 2566996.3354 | 2566696.0166 | 2627544.9143 | 2556143.6589 | 2386518.0767
625 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 | 0 | 30799450 | 1 | 1825.25 | 1829.83 | 4.58 | 60000 | 0 | 274800 | 277809.1547 | Demra | Sarulia 33/11KV S/S | 83 | 324637.9555 | 325784.1394 | 326380.7042 | 261798.4288 | 295524.6849 | 302404.9427
626 | 11 kV Tengra Feeder (=L16) | E183T | 11 | 0 | 30799145 | 1 | 5610.1 | 5648.31 | 38.21 | 60000 | 0 | 2292600 | 2317704.7602 | Demra | Sarulia 33/11KV S/S | 83 | 2700866.43 | 2803570.4254 | 2888103.8805 | 2785803.7935 | 2203397.2826 | 3315319.3041
627 | 11 kV Police Line Feeder (=L17) | E183PL | 11 | 0 | 30799480 | 1 | 3379.8 | 3396.71 | 16.91 | 60000 | 0 | 1014600 | 1025710.2197 | Demra | Sarulia 33/11KV S/S | 83 | 1276100.2252 | 1292175.5957 | 1231843.5906 | 1213792.7153 | 1297576.8726 | 1183247.2468
628 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 | 0 | 30799119 | 1 | 1664.08 | 1670.44 | 6.36 | 60000 | 0 | 381600 | 385778.6515 | Demra | Sarulia 33/11KV S/S | 83 | 493328.3324 | 441483.1795 | 534022.1596 | 561432.5279 | 558765.1604 | 495803.4526
629 | 11 kV Spare Feeder (=F9) | 0 | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0
630 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 | 0 | HA021100493-02 | 1 | 89482972 | 91722476 | 2239504 | 1 | 0 | 2239504 | 2264027.3407 | Demra | Sarulia 33/11KV S/S | 83 | 2874690.3342 | 3063617.2119 | 3062145.1731 | 3047117.0714 | 3001937.8862 | 2753359.8865
631 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 | 0 | HA021100518-02 | 1 | 50895377 | 50895377 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 26104.5324 | 0 | 0 | 1592.7597 | 158210.2162 | 30254.1689
632 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 | 0 | HA021100697-02 | 1 | 29322895 | 31095860 | 1772965 | 1 | 0 | 1772965 | 1792379.5779 | Demra | Sarulia 33/11KV S/S | 83 | 2145386.6161 | 2228761.3555 | 2265661.5752 | 2324189.2905 | 2304863.862 | 2171918.011
633 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0
634 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0 | 0
635 | 11 kV Khanpur Feeder | B723B | 11 | 0 | DHKC 9348 | 1 | 32799.1 | 55005.6 | 22206.5 | 60 | 0 | 1332390 | 1344397.4603 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1671397.6523 | 1767813.7522 | 1753296.6737 | 1849730.4598 | 1858439.2031 | 1689432.0922
636 | 11 kV Mission Para Feeder. | B723T | 11 | 0 | DHKC 9347 | 1 | 12889.86 | 33948.22 | 21058.36 | 60 | 0 | 1263501.6 | 1274888.2401 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1557478.0335 | 1662446.9196 | 1652830.7535 | 1736094.2229 | 1666330.9001 | 1591097.4109
637 | 11 kV Esha Kha Feeder | B723M | 11 | 0 | DHKC 9311 | 1 | 29602.88 | 42944.3 | 13341.42 | 60 | 0 | 800485.2 | 807699.1496 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1039293.9368 | 1004043.7507 | 968513.5517 | 939733.5453 | 917602.1317 | 1040108.3114
638 | 11 kV New Hazigonj Feeder | B723F | 11 | 0 | DHKC 9314 | 1 | 275.24 | 302.18 | 26.94 | 60000 | 0 | 1616400 | 1630966.9503 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 2057845.6627 | 2170066.5597 | 2135314.0661 | 2193735.673 | 2054393.8757 | 2135156.6373
639 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
640 | 11 kV Hospital RMU Feeder. | B723H | 11 | 0 | 6604412 | 1 | 8.03 | 8.79 | 0.76 | 60000 | 0 | 45600 | 46010.9459 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 61862.7343 | 64307.2562 | 63695.448 | 65004.0756 | 61352.3895 | 59949.0945
641 | 11 kV Old Hajiganj Feeder. | B723E | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
642 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 | 0 | 06604389 | 1 | 70259.15 | 85919.8 | 15660.65 | 60 | 0 | 939639 | 948106.9996 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1250130.6264 | 1328944.0291 | 1304005.3624 | 1304824.3795 | 1324560.4284 | 1260578.6756
643 | 11 kV Spare Feeder. | 0 | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
644 | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
645 | 11 kV B. B. Road West Feeder. | A723A | 11 | 0 | 6604415 | 1 | 375.72 | 413.32 | 37.6 | 40000 | 0 | 1504000 | 1517554.0047 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1864372.9936 | 1918297.585 | 1915716.4264 | 1976042.8964 | 1840166.7201 | 1800087.6245
646 | 11 kV Mondalpara Feeder. | 0 | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
647 | 11 kV B. B. Road East Feeder. | B723C | 11 | 0 | 06604392 | 1 | 293.14 | 323.08 | 29.94 | 40000 | 0 | 1197600 | 1208392.7367 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1428099.2005 | 1517085.0182 | 1504830.2349 | 1509066.5776 | 1463548.0912 | 1396793.7162
648 | 11 kV Bishaw Road Feeder. | B723A | 11 | 0 | 06604393 | 1 | 308.98 | 332.61 | 23.63 | 40000 | 0 | 945200 | 953718.1152 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1117572.534 | 1216580.0413 | 1210820.1352 | 1222724.6371 | 1779421.78 | 1969640.6189
649 | 11 kV Chasara Feeder. | A723B | 11 | 0 | 06604391 | 1 | 410.64 | 449.6 | 38.96 | 40000 | 0 | 1558400 | 1572444.256 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1942004.6602 | 2118903.8684 | 2081122.3834 | 2195963.227 | 2115948.7484 | 2048765.3497
650 | 11 kV Pathan Tully Feeder. | B723G | 11 | 0 | 06604388 | 1 | 65.03 | 78.12 | 13.09 | 40000 | 0 | 523600 | 528318.6681 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 576981.1889 | 529827.0791 | 160552.9705 | 39690.9621 | 0 | 0
651 | 11 kV Spare Feeder. | 0 | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
652 | 11 kV Nayamati Feeder. | B722J | 11 | 0 | 6604289 | 1 | 266.66 | 294.9 | 28.24 | 40000 | 0 | 1129600 | 1139779.9227 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1329442.2908 | 1269562.7492 | 1343468.4333 | 1193968.9401 | 1316545.3361 | 1343505.6323
653 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
654 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
655 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0 | 0
656 | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0.415 | 0 | 412109 | 1 | 9204 | 9234.3 | 30.3 | 10 | 0 | 303 | 305.7306 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 270.9022 | 317.4918 | 324.5435 | 42.526 | 0 | 0
657 | 33/0.415 kV Auxiliary Transformer-2 | 0 | 0.415 | 0 | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 | 0 | 3000 | 3027.0359 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 3032.487 | 3033.3611 | 3033.1166 | 3037.5736 | 3037.247 | 3027.732
658 | 11 kV Link Road Feeder | B741N | 11 | 0 | HA021100475-02 | 1 | 97092.756 | 99970.287 | 2877.531 | 1000 | 0 | 2877531 | 2900288.7042 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 3109326.5102 | 2934230.0248 | 2975929.581 | 2607402.2302 | 1951841.3049 | 1877540.2045
659 | 11 kV Lamapara Express Feeder | B723L | 11 | 0 | HA021100928-03 | 1 | 80182.444 | 81154.775 | 972.331 | 1000 | 0 | 972331 | 980020.9332 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1044271.2809 | 777935.2019 | 1101665.3091 | 726895.7131 | 1017580.9915 | 1063497.0225
660 | 11 kV Kutubpur Feeder*** | B741Q | 11 | 0 | DHK66616 | 1 | 18290.01 | 18505.85 | 215.84 | 8000 | 0 | 1726720 | 1740376.2153 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1768072.7988 | 1341995.221 | 1569417.834 | 1641482.3695 | 1554956.8642 | 1703285.4205
661 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 | 0 | DHK66625 | 1 | 3580.6 | 3598.24 | 17.64 | 60000 | 0 | 1058400 | 1066770.6323 | Fatullah | Matuail 33/11KV S/S | 41 | 1419365.2857 | 1418275.2675 | 1534196.2033 | 1364062.3916 | 1338941.0426 | 835792.1765
662 | 11 kV Tushardhara Feeder (F2) | E241T | 11 | 0 | DHK66623 | 1 | 3931.53 | 3975.1 | 43.57 | 60000 | 0 | 2614200 | 2634875.0823 | Matuail | Matuail 33/11KV S/S | 41 | 2672602.3834 | 2999054.9265 | 2829014.2755 | 2689931.0362 | 2755784.1096 | 2760297.6743
663 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 | 0 | DHK66627 | 1 | 3332.15 | 3345.82 | 13.67 | 60000 | 0 | 820200 | 826686.7655 | Matuail | Matuail 33/11KV S/S | 41 | 937957.3247 | 903475.9079 | 1019170.5275 | 792368.687 | 795452.7012 | 696897.8308
664 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 | 0 | HA021101044-02 | 1 | 66528.706 | 66770.571 | 241.865 | 1000 | 0 | 241865 | 243777.8524 | Matuail | Matuail 33/11KV S/S | 41 | 299669.3822 | 351957.4279 | 332319.5113 | 349545.5347 | 361905.6203 | 323912.9361
665 | 11 kV Shibu Market Feeder (F7) | B841B | 11 | 0 | DHK66624 | 1 | 2390.92 | 2396.07 | 5.15 | 60000 | 0 | 309000 | 311443.8071 | Fatullah | Matuail 33/11KV S/S | 41 | 425021.3863 | 388070.1886 | 515025.6758 | 398306.2183 | 387075.6832 | 615623.4101
666 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 | 0 | HA060300286-03 | 1 | 5075.064 | 6365.598 | 1290.534 | 1000 | 0 | 1290534 | 1300740.5246 | Fatullah | Matuail 33/11KV S/S | 41 | 1507092.8931 | 1340202.4176 | 1497969.2549 | 1502329.9696 | 1201993.7471 | 1110650.3388
667 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 | 0 | DHK66626 | 1 | 4509.48 | 4543.46 | 33.98 | 60000 | 0 | 2038800 | 2054924.3814 | Matuail | Matuail 33/11KV S/S | 41 | 2632586.1045 | 2681928.8192 | 2638599.8531 | 2625668.5413 | 2669361.5514 | 2690547.2387
668 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | 0 | DHK6622 | 1 | 4256.29 | 4277.24 | 20.95 | 60000 | 0 | 1257000 | 1266941.3122 | Matuail | Matuail 33/11KV S/S | 41 | 1346002.1078 | 1350362.9845 | 1363125.4682 | 1274337.3987 | 1416234.4574 | 1374993.3702
669 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 | 0 | DHKA2187 | 1 | 126.118 | 131.7799 | 5.6619 | 60000 | 0 | 339714 | 342400.7167 | Shyampur | Matuail 33/11KV S/S | 41 | 335087.831 | 248953.0896 | 243349.6318 | 240620.6059 | 244740.1643 | 218634.2568
670 | 11 kV Bhuighor Bazar | 0 | 11 | 0 | HA021100861-02 | 1 | 2266.614 | 3332.199 | 1065.585 | 1000 | 0 | 1065585 | 1074012.4568 | Matuail | Matuail 33/11KV S/S | 41 | 1411612.637 | 1387743.4624 | 1286702.6096 | 1290448.3093 | 1462145.9342 | 1034107.8281
671 | 11 kV Tokkar Math Feeder | B8416 | 11 | 0 | HA021200298-02 | 1 | 82630.261 | 83283.485 | 653.224 | 1000 | 0 | 653224 | 658390.1923 | Fatullah | Matuail 33/11KV S/S | 41 | 791536.1434 | 789253.9157 | 797388.0996 | 771061.022 | 778486.6953 | 733095.2742
672 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 | 0 | XA575922 | 1 | 232.8 | 249.9 | 17.1 | 1000 | 0 | 17100 | 17235.2398 | Fatullah | Matuail 33/11KV S/S | 41 | 19603.9346 | 10611.2942 | 9873.3404 | 9194.7909 | 13287.9755 | 64493.8811
673 | 33/0.415 KV Transformer, AT-1 | 0 | 0.415 | 0 | 2001123043119 | 1 | 7578.2 | 7626.4 | 48.2 | 160 | 0 | 7712 | 7772.9924 | Shyampur | Matuail 33/11KV S/S | 41 | 11624.9311 | 12240.3805 | 12799.0731 | 12965.6656 | 12496.7831 | 11807.0303
674 | 33/0.415 KV Transformer, AT-2 | 0 | 0.415 | 0 | 2001123043157 | 1 | 4715.3 | 4726.8 | 11.5 | 160 | 0 | 1840 | 1854.5521 | Shyampur | Matuail 33/11KV S/S | 41 | 0 | 0 | 0 | 0 | 0 | 129.3921
675 | 11 kV Godnail (F16) | A8963 | 11 | 0 | 00000109 | 1 | 30618406 | 32205162 | 1586756 | 1 | 0 | 1586756 | 1608130.1776 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1902311.4075 | 2038403.821 | 2022169.7421 | 1902174.2906 | 1848814.9706 | 1869406.9017
676 | 11 kV M. Circus (F15) | B796C | 11 | 0 | 00000123 | 1 | 112349288 | 114200200 | 1850912 | 1 | 0 | 1850912 | 1875844.4545 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1681278.3417 | 1521029.259 | 1828274.6635 | 1936785.1498 | 1975646.3394 | 2135882.0516
677 | 11 kV Wapderpool (F14) | B723W | 11 | 0 | 00000190 | 1 | 58342616 | 59257536 | 914920 | 1 | 0 | 914920 | 927244.3035 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 798221.6352 | 482340.828 | 822312.035 | 474935.0147 | 619875.2088 | 595303.4365
678 | 11 kV Chowdhury Bari (F13) | A896C | 11 | 0 | 00000191 | 1 | 105146864 | 107236336 | 2089472 | 1 | 0 | 2089472 | 2117617.9441 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2183088.6246 | 2226891.1005 | 2193767.4037 | 2204031.0267 | 2287431.9192 | 2194488.2982
679 | 11 kV Ailpara (F12) | B7966 | 1 | 0 | 00000192 | 1 | 58996976 | 61060412 | 2063436 | 1 | 0 | 2063436 | 2091231.2297 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2449465.553 | 2507772.6658 | 2664936.682 | 2385423.2662 | 2312455.9158 | 2506620.5244
680 | 11 kV Spare (F11) | 0 | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0
681 | 11 kV Spare (F10) | 0 | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0
682 | 11 kV Spare (F9) | 0 | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0
683 | 11 kV Spare (F8) | 0 | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0
684 | 11 kV Zulfiqur Steel | A8962H | 11 | 0 | 00000197 | 1 | 18664354 | 19720952 | 1056598 | 1 | 0 | 1056598 | 1070830.7575 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1205147.4911 | 881898.0967 | 1269192.9831 | 1109871.8066 | 1233882.0915 | 1248729.4855
685 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 | 0 | 00000198 | 1 | 4241549 | 4290309 | 48760 | 1 | 0 | 48760 | 49416.8148 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 38314.1839 | 81476.5739 | 45981.5802 | 80821.2927 | 12574.267 | 42071.0581
686 | 11 kV Lucky Bazar (F5) | B796Z | 11 | 0 | 00000199 | 1 | 92459576 | 93619848 | 1160272 | 1 | 0 | 1160272 | 1175901.2838 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1409832.0895 | 1363293.8581 | 1360268.1394 | 1265880.4844 | 1332623.2308 | 1392661.9878
687 | 11 kV Enayetnagar (F4) | A896Y | 11 | 0 | 00000200 | 1 | 35538712 | 36816152 | 1277440 | 1 | 0 | 1277440 | 1294647.5791 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1539178.9886 | 1637703.7047 | 1666199.7304 | 1606948.7378 | 1544300.7721 | 1576051.8888
688 | 11 kV Bhuiyapara (F3) | A896V | 11 | 0 | 00000201 | 1 | 69299712 | 70774584 | 1474872 | 1 | 0 | 1474872 | 1494739.0596 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1820491.9548 | 1638474.4387 | 1895985.9869 | 1703398.6781 | 2021560.4921 | 1949356.1666
689 | 11 kV Arambagh (F2) | B796D | 11 | 0 | 00000202 | 1 | 11191773 | 12144210 | 952437 | 1 | 0 | 952437 | 965266.6711 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1110256.976 | 1096967.543 | 1072171.1368 | 1011302.9055 | 1033739.3311 | 1073358.7436
690 | 11 kV Spare (F1) | 0 | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0 | 0
691 | 11/0.415 kV Aux. Transformer-1 | 0 | 0.415 | 0 | 00000204 | 1 | 1753.31 | 1782.91 | 29.6 | 100 | 0 | 2960 | 2999.8723 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 4062.7646 | 4590.7608 | 4148.0738 | 5028.3475 | 4509.4616 | 4713.1396
692 | 11/0.415 kV Aux. Transformer-2 | 0 | 0.415 | 0 | 00000205 | 1 | 61.16 | 61.17 | 0.01 | 100 | 0 | 1 | 1.0135 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 44.6458 | 0 | 0 | 0.99927 | 0 | 0
693 | 11 kV Minan Steel Feeder | A717R | 11 | New | 0 | 1 | 77458900 | 78084808 | 625908 | 1 | 0 | 625908 | 632806.8774 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 639787.7036 | 668682.8226 | 690626.9008 | 493276.6302 | 608736.535 | 686221.5647
694 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 90382612 | 91204625 | 822013 | 1 | 0 | 822013 | 831073.3841 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 837776.7717 | 798148.0435 | 798255.2776 | 675313.5877 | 687996.4568 | 904286.638
695 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 205819 | 228288.5 | 22469.5 | 60 | 0 | 1348170 | 1363029.7869 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1190995.536 | 1654746.3681 | 1713127.7082 | 1429973.3518 | 1348752.6633 | 1520277.0648
696 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
697 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 358618.1 | 370704.6 | 12086.5 | 60 | 0 | 725190 | 733183.1825 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 994384.377 | 1017275.0549 | 998917.0422 | 983661.4804 | 966418.4358 | 973413.7301
698 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 67878.2 | 94344.4 | 26466.2 | 60 | 0 | 1587972 | 1605474.9303 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1916663.5337 | 1932341.6728 | 1605143.4286 | 2269442.86 | 1903765.6601 | 1898489.4903
699 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 91772.6 | 102086.1 | 10313.5 | 60 | 0 | 618810 | 625630.6419 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 700600.4968 | 623925.9784 | 637276.1792 | 646164.6825 | 667510.2274 | 661387.5474
700 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 661621.5 | 676359 | 14737.5 | 60 | 0 | 884250 | 893996.3722 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 935867.4295 | 898188.9867 | 879720.3375 | 817413.76 | 827156.9088 | 863427.9271
701 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 559147.2 | 576544.9 | 17397.7 | 60 | 0 | 1043862 | 1055367.6461 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1081150.4699 | 1065440.2479 | 1123770.5196 | 1043132.595 | 1256184.2479 | 1130265.9765
702 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 877493.5 | 882166.7 | 4673.2 | 60 | 0 | 280392 | 283482.5341 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 300394.2285 | 217235.7079 | 274279.1183 | 230613.5281 | 268951.939 | 461817.7457
703 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538934.5 | 538934.5 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 3404.6005 | 458632.0662 | 1006566.474 | 739323.8488 | 888156.2557 | 505747.1466
704 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 2534578 | 3152340 | 617762 | 1 | 0 | 617762 | 624571.0906 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 739019.2541 | 764214.6584 | 798862.9891 | 731731.9387 | 686782.5544 | 645276.6941
705 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 25882355 | 26146252 | 263897 | 1 | 0 | 263897 | 266805.7231 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 329009.9458 | 336317.7733 | 326230.0217 | 318326.9039 | 335635.5116 | 326421.8579
706 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 16128427 | 16501720 | 373293 | 1 | 0 | 373293 | 377407.5066 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 371813.5071 | 231457.5089 | 350113.1813 | 373857.3757 | 329133.6781 | 311868.8913
707 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
708 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 123409.7429 | 535601.4665
709 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 17649412 | 18251948 | 602536 | 1 | 0 | 602536 | 609177.2667 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 739088.5512 | 985608.2317 | 2067941.9788 | 1957359.7515 | 2145386.8814 | 2599917.6327
710 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
711 | 0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
712 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 179956 | 1166208 | 986252 | 1 | 0 | 986252 | 997122.6577 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1798366.2205 | 1947566.1648 | 1839951.043 | 1845653.8856 | 1844325.072 | 1788794.6263
713 | 11 kV Spare Feeder | 0 | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
714 | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0 | 0
715 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
716 | 11 kV Outgoing Feeder-2 (=F2) | 0 | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
717 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 999.44 | 1032.15 | 32.71 | 60000 | 0 | 1962600 | 1967161.5939 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2374197.2935 | 2139879.5383 | 2225117.9731 | 1919103.2774 | 1925513.8961 | 2018573.5941
718 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 497.96 | 519.22 | 21.26 | 60000 | 0 | 1275600 | 1278564.8268 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1599035.1072 | 1814088.8895 | 1616939.3533 | 1431521.3433 | 1476167.1668 | 1492878.3256
719 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 563.73 | 572.34 | 8.61 | 60000 | 0 | 516600 | 517800.713 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 643462.7923 | 673220.5289 | 698887.9434 | 713358.7902 | 702593.0118 | 691704.3007
720 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1267.53 | 1292.66 | 25.13 | 60000 | 0 | 1507800 | 1511304.5202 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1737349.5392 | 1778023.504 | 1913418.8206 | 1823628.4898 | 1708359.7204 | 1811062.3039
721 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
722 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
723 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
724 | 11 kV Outgoing Feeder-10 (=F8) | 0 | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
725 | 11 kV Outgoing Feeder-11 (=F9) | 0 | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
726 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 213.78 | 227.78 | 14 | 60000 | 0 | 840000 | 841952.3789 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1083663.5063 | 1145075.9889 | 1196876.0424 | 1264590.5826 | 1201867.1554 | 1168078.0452
727 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 98.21 | 105.2 | 6.99 | 60000 | 0 | 419400 | 420374.7949 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 572501.475 | 611308.2838 | 620963.1553 | 614881.6508 | 573262.9625 | 566596.0446
728 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1178.03 | 1220.63 | 42.6 | 60000 | 0 | 2556000 | 2561940.8101 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2204010.4054 | 1471467.7275 | 1601110.8808 | 1579237.0524 | 1146525.925 | 1680540.7098
729 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1452.18 | 1490.06 | 37.88 | 60000 | 0 | 2272800 | 2278082.5795 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2618352.3343 | 2670641.7946 | 2813206.6084 | 2526178.8135 | 2500581.4639 | 2536449.5967
730 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0 | 0
731 | 11 kV Katherpol Feeder | B8919 | 11 | 0 | 00000031 | 1 | 69331312 | 71074344 | 1743032 | 1 | 0 | 1743032 | 1780543.7815 | Fatullah | Dapa 33/11 kV | 91 | 2017920.9065 | 1907068.817 | 2019617.347 | 1872668.2415 | 1825325.1091 | 2095256.7912
732 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
733 | 11 kV Union Parishad Feeder | B8918 | 11 | 0 | 00000032 | 1 | 69825752 | 71909144 | 2083392 | 1 | 0 | 2083392 | 2128228.6671 | Fatullah | Dapa 33/11 kV | 91 | 2252272.5782 | 1663620.755 | 1557194.9668 | 1351133.0591 | 1174339.0851 | 1364658.7564
734 | 11 kV Shiachar Feeder | B891G | 11 | 0 | 00000030 | 1 | 71832544 | 73433864 | 1601320 | 1 | 0 | 1601320 | 1635781.9984 | Fatullah | Dapa 33/11 kV | 91 | 2031118.288 | 2032383.0231 | 2001560.8541 | 1924678.9852 | 1907532.8668 | 1901950.2285
735 | 11 kV Sastapur Feeder | B8913 | 11 | 0 | 00000106 | 1 | 71818424 | 72296704 | 478280 | 1 | 0 | 478280 | 488573.0611 | Fatullah | Dapa 33/11 kV | 91 | 516338.7434 | 559825.9548 | 395679.6151 | 1143053.371 | 1344939.9892 | 1492863.3157
736 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
737 | 11 kV Jalal Ahmed Express | B891JA | 11 | 0 | 00000172 | 1 | 5637386 | 5879505 | 242119 | 1 | 0 | 242119 | 247329.6416 | Fatullah | Dapa 33/11 kV | 91 | 398396.8352 | 281983.6134 | 872.8694 | 163.171 | 71453.7073 | 791901.0884
738 | 11 kV Hajibari Feeder | 0 | 11 | 0 | 00000105 | 1 | 80 | 164959 | 164879 | 1 | 0 | 164879 | 168427.36 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
739 | 11 kV Railine Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 195799 | 195799 | 1 | 0 | 195799 | 200012.7891 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
740 | 11 kV Lalpur Feeder | B8911 | 11 | 0 | 00000044 | 1 | 84092032 | 86381512 | 2289480 | 1 | 0 | 2289480 | 2338751.8857 | Fatullah | Dapa 33/11 kV | 91 | 2709693.2174 | 2479807.3342 | 1402820.0857 | 1449235.5198 | 1159780.4978 | 373576.7292
741 | 11 kV Kotaler Bag Feeder | B8912 | 11 | 0 | 00000050 | 1 | 89610784 | 91574936 | 1964152 | 1 | 0 | 1964152 | 2006422.5038 | Fatullah | Dapa 33/11 kV | 91 | 2309410.8982 | 2305548.0804 | 2521037.1496 | 1462297.3552 | 1401235.8745 | 1515181.1462
742 | 11 kV Idrakpur Feeder | B8915 | 11 | 0 | 00000021 | 1 | 79058888 | 80022008 | 963120 | 1 | 0 | 963120 | 983847.2999 | Fatullah | Dapa 33/11 kV | 91 | 1146390.3941 | 1054879.9219 | 1213883.5456 | 1042540.0593 | 1114166.2721 | 1068664.5804
743 | 11 kV Isdair Feeder | B8914 | 11 | 0 | 00000029 | 1 | 42475456 | 43086456 | 611000 | 1 | 0 | 611000 | 624149.3274 | Fatullah | Dapa 33/11 kV | 91 | 790469.7993 | 829018.6896 | 795100.6656 | 849835.155 | 794122.676 | 792940.801
744 | 11 kV Shah Fateullah Express | 0 | 11 | 0 | 0000051 | 1 | 2873073 | 4770108 | 1897035 | 1 | 0 | 1897035 | 1937861.0792 | Fatullah | Dapa 33/11 kV | 91 | 1875856.2789 | 1015342.7418 | 0 | 0 | 0 | 0
745 | 11 kV Boubazar Feeder | 0 | 11 | 0 | 00000151 | 1 | 0 | 23719 | 23719 | 1 | 0 | 23719 | 24229.4565 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
746 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
747 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0 | 0.415 | 0 | DHKF 7522 | 1 | 3192 | 3239 | 47 | 100 | 0 | 4700 | 4801.1487 | Fatullah | Dapa 33/11 kV | 91 | 6039.9915 | 6235.0379 | 5653.8129 | 5914.9473 | 5529.8501 | 5198.5629
748 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0 | 0
749 | 11 kV Bholail Feeder (F-3) | E330V | 11 | 0 | DHK 9335 | 1 | 70399.8787 | 115853.9958 | 45454.1171 | 60 | 0 | 2727247.026 | 2733762.095 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 2632122.2753 | 3204950.7718 | 3202295.2627 | 3113891.785 | 3046734.2178 | 2464743.5384
750 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 | 0 | DHK 9336 | 1 | 17372.339 | 34520.8952 | 17148.5562 | 60 | 0 | 1028913.372 | 1031371.3237 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1296469.7835 | 1414735.196 | 1450857.7553 | 1198137.3888 | 1083589.5043 | 1409860.9795
751 | 11 kV Baburail Feeder (F-5) | A730R | 11 | 0 | DHK 9322 | 1 | 84762.3796 | 111014.0086 | 26251.629 | 60 | 0 | 1575097.74 | 1578860.4613 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 1983304.4857 | 2103409.2909 | 2067517.7824 | 2058052.5984 | 2038840.2789 | 1960329.6227
752 | 11 kV Goghchar Feeder (F-1) | E330G | 11 | 0 | DHK 9323 | 1 | 76884.4867 | 93927.0295 | 17042.5428 | 60 | 0 | 1022552.568 | 1024995.3245 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1237157.8572 | 1317359.8624 | 1330855.5581 | 1324242.6499 | 1303267.9767 | 1261095.5642
753 | 11 kV Norshinghopur (F-2) | E330N | 11 | 0 | DHK 9365 | 1 | 66325.1503 | 92611.445 | 26286.2947 | 60 | 0 | 1577177.682 | 1580945.372 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1560990.7311 | 1355613.7656 | 1460780.2783 | 1404336.8639 | 1352601.3966 | 1471201.0567
754 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 | 0 | DHK 9367 | 1 | 15212.6093 | 27485.0632 | 12272.4539 | 60 | 0 | 736347.234 | 738106.28 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 517148.8821 | 0 | 0 | 0 | 0 | 554462.5713
755 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 | 0 | H/A030701125-03 | 1 | 73783.826 | 73961.68 | 177.854 | 1000 | 0 | 177854 | 178278.8721 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 227804.4627 | 240354.077 | 235334.8005 | 246133.1449 | 234255.9876 | 224598.6372
756 | 11 kV Kashipur Feeder (F-7) | E317K | 11 | 0 | H/A030800169-03 | 1 | 40041.956 | 41289.934 | 1247.978 | 1000 | 0 | 1247978 | 1250959.2711 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1588658.98 | 1710138.4368 | 1760370.7558 | 1741847.8978 | 1664580.229 | 1652181.4751
757 | 11 kV Spare Feeder (F-6) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 0 | 0 | 0 | 0 | 0 | 0
758 | 11 kV Paikpara Feeder (F-8) | A730D | 11 | 0 | H/A030701098-03 | 1 | 81538.063 | 82381 | 842.937 | 1000 | 0 | 842937 | 844950.6763 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 1070234.6333 | 1102912.6399 | 1118443.5796 | 1135381.2606 | 1090515.7468 | 1082731.082
759 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 | 0 | H/A030800205-03 | 1 | 97166.397 | 98073.528 | 907.131 | 1000 | 0 | 907131 | 909298.0281 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 937852.0624 | 845475.6866 | 838157.9765 | 729788.4502 | 786055.2221 | 765048.1281
760 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 | 0 | H/A030701091-03 | 1 | 56283.66 | 57053.47 | 769.81 | 1000 | 0 | 769810 | 771648.9846 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1009051.2889 | 1042925.7746 | 1035234.9191 | 1075488.4842 | 1015821.5301 | 958950.0681
761 | 11 kV River View | B793U | 11 | 0 | 00000061 | 1 | 8849520 | 9679440 | 829920 | 1 | 0 | 829920 | 834579.227 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 838291.0284 | 794103.9859 | 844731.2094 | 841728.9793 | 838140.6773 | 803073.4017
762 | 11 kV Railgate B.B. Road | B793F | 11 | 0 | 00000191 | 1 | 24783300 | 25321458 | 538158 | 1 | 0 | 538158 | 541179.2554 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 698256.3766 | 634632.2838 | 651403.112 | 672012.4136 | 662899.4007 | 611819.3181
763 | 11 kV DIT | A722D | 11 | 0 | 00000174 | 1 | 145783200 | 148263920 | 2480720 | 1 | 0 | 2480720 | 2494646.9299 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 3067765.2362 | 3157724.5261 | 3006495.8053 | 3105959.8639 | 3165323.9759 | 2992837.0935
764 | 11 kV Dalpatti | B7227 | 11 | 0 | 00000182 | 1 | 5882705 | 6596464 | 713759 | 1 | 0 | 713759 | 717766.0913 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 789288.224 | 719006.8368 | 711194.3901 | 640949.3228 | 661646.5082 | 714092.6513
765 | 11 kV South Chasara | A793S | 11 | 0 | 00000043 | 1 | 102195272 | 104270584 | 2075312 | 1 | 0 | 2075312 | 2086962.942 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 2534727.6524 | 2702179.486 | 2680027.0984 | 2791666.2107 | 2659640.365 | 2565218.7341
766 | 11 kV Spare | 0 | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0
767 | 11 kV NCC Express | B7225 | 11 | 0 | 00000019 | 1 | 213639 | 237799 | 24160 | 1 | 0 | 24160 | 24295.6359 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 23419.6471 | 28768.3897 | 31678.5827 | 33494.5516 | 30069.4219 | 22516.8296
768 | 11 kV Spare | 0 | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0
769 | 11 kV Masuya Bazar | B7229 | 11 | 0 | 00000173 | 1 | 8565979 | 9690976 | 1124997 | 1 | 0 | 1124997 | 1131312.8093 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 1152492.2619 | 1058401.5124 | 1053995.629 | 1019425.3124 | 1009868.8027 | 967617.4501
770 | 11 kV Nitaigonj | B722G | 11 | 0 | 00000189 | 1 | 60384252 | 61101972 | 717720 | 1 | 0 | 717720 | 721749.3286 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 797467.0545 | 710089.0378 | 797549.9114 | 692971.3447 | 773236.8002 | 671875.6098
771 | 11 kV Shahid Nagar | E323T | 11 | 0 | 00000020 | 1 | 60968412 | 62024488 | 1056076 | 1 | 0 | 1056076 | 1062004.8821 | Sytalakhya | Mondalpara 33/11KV S/S | 22 | 1271995.6228 | 1341667.6936 | 1338376.1519 | 1319788.4916 | 1324869.236 | 1256708.9709
772 | 11 kV Bangla Bazar | A793Z | 11 | 0 | 00000139 | 1 | 74210456 | 75510416 | 1299960 | 1 | 0 | 1299960 | 1307258.0634 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1631386.9501 | 1686165.1422 | 1670015.7997 | 1659253.7348 | 1635218.8108 | 1605498.2865
773 | 11 kV Vogoban Gonj | B7228 | 11 | 0 | 00000181 | 1 | 3768630 | 4220269 | 451639 | 1 | 0 | 451639 | 454174.5319 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 474606.7675 | 456596.7336 | 480180.888 | 455263.1874 | 451404.0608 | 442440.5963
774 | 11 kV Tanbazar | B722I | 11 | 0 | 00000138 | 1 | 51622392 | 52421992 | 799600 | 1 | 0 | 799600 | 804089.0085 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 976523.0891 | 1000661.8275 | 1022544.4626 | 983939.833 | 990185.2541 | 977004.8332
775 | 11 kV SS Road | A793O | 11 | 0 | 00000175 | 1 | 69392152 | 70578344 | 1186192 | 1 | 0 | 1186192 | 1192851.3622 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1337205.7052 | 1396187.0064 | 1386083.0342 | 1389631.5256 | 1367265.5042 | 1304240.0244
776 | 11 kV Spare | 0 | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0
777 | 33/0.415 kV Auxiliary-1 | 0 | 0.415 | 0 | 0 | 1 | 2640.91 | 2673.12 | 32.21 | 100 | 0 | 3221 | 3239.0829 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 4162.6017 | 6314.1794 | 3653.8216 | 8763.4945 | 8081.1571 | 8402.5235
778 | 33/0.415 kV Auxiliary-2 | 0 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0 | 0
779 | 11 kV Masdair Feeder (F-8) | A727M | 11 | 0 | XA575914 | 1 | 222435 | 225307.3 | 2872.3 | 1000 | 0 | 2872300 | 2875854.6768 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 3291294.4584 | 3221867.4125 | 3104675.7264 | 3190609.1379 | 3086175.0273 | 3077099.4263
780 | 11 kV Narayangonj (F-7) | A727N | 11 | 0 | XA575915 | 1 | 169847.6 | 171294.6 | 1447 | 1000 | 0 | 1447000 | 1448790.766 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1519105.835 | 1446695.3457 | 1509012.0982 | 1221622.7778 | 1186514.4598 | 1307443.1804
781 | 11 kV Nearest Feeder (F-6) | A727B | 11 | 0 | XA575927 | 1 | 108569.7 | 109777.2 | 1207.5 | 1000 | 0 | 1207500 | 1208994.3676 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1130497.3656 | 1036613.3317 | 1067352.4897 | 767732.4068 | 814473.5094 | 997748.2737
782 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 | 0 | XA575916 | 1 | 120037.9 | 121288 | 1250.1 | 1000 | 0 | 1250100 | 1251647.0882 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1407639.7693 | 1294481.9465 | 1274162.1574 | 1118663.9439 | 1197874.4889 | 1341268.5888
783 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 | 0 | XA575912 | 1 | 57538.4 | 58701.7 | 1163.3 | 1000 | 0 | 1163300 | 1164739.667 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 905839.439 | 991802.3648 | 906095.6122 | 696086.8403 | 614760.142 | 701320.2188
784 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 | 0 | DHK66615 | 1 | 246.1468 | 262.4459 | 16.2991 | 60000 | 0 | 977948.46 | 979158.7412 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1098396.235 | 953150.2952 | 1090118.5393 | 864699.4622 | 933339.9033 | 1045632.3523
785 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 | 0 | XA575920 | 1 | 234533.8 | 235307.8 | 774 | 1000 | 0 | 774000 | 774957.8804 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 27 | 1276885.4045 | 676995.0442 | 906804.2112 | 982770.4437 | 813154.9346 | 1189560.6195
786 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 | 0 | XA575929 | 1 | 23731.9 | 24939.8 | 1207.9 | 1000 | 0 | 1207900 | 1209394.8627 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1314142.277 | 1121815.8354 | 1179007.44 | 1159908.2799 | 1225868.8461 | 1274022.8667
787 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 | 0 | HA021100913-02 | 1 | 44435.628 | 46643.437 | 2207.809 | 1000 | 0 | 2207809 | 2210541.3216 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2452393.5389 | 1730245.9891 | 1391497.0345 | 582908.1262 | 649651.6597 | 916096.371
788 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 | 0 | HA021100682-02 | 1 | 66687.61 | 69020.842 | 2333.232 | 1000 | 0 | 2333232 | 2336119.5415 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2520803.045 | 2363695.2567 | 2414952.831 | 1958482.735 | 2197501.257 | 2366722.3025
789 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 | 0 | HA021100455-02 | 1 | 59670.325 | 61478.231 | 1807.906 | 1000 | 0 | 1807906 | 1810143.413 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1837185.1157 | 1324011.9627 | 2155990.2798 | 1459919.7827 | 1675803.0813 | 1827353.8856
790 | 11/0.415 KV Transformer,AT-1 | 0 | 0.415 | Analog | 2001123043161 | 1 | 3995.5 | 4048.1 | 52.6 | 160 | 0 | 8416 | 8426.4154 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 10606.5342 | 9471.9695 | 9523.57 | 9809.4637 | 10077.9686 | 6902.8139
791 | 11/0.415 KV Transformer,AT-2 | 0 | 0.415 | Analog | 2001123043118 | 1 | 4108.1 | 4122.3 | 14.2 | 160 | 0 | 2272 | 2274.8118 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 292.37 | 213.7771 | 583.0757 | 16.214 | 519.3156 | 421.2985
792 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
793 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 | 0 | 041808902749 | 1 | 468.54 | 484.37 | 15.83 | 60000 | 0 | 949800 | 945964.8168 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1302048.296 | 1299547.0336 | 1326519.4669 | 1258154.7044 | 1256317.0074 | 1308593.1901
794 | 11 kV UltraTech Cement Feeder (=F3) | 0 | 11 | 0 | 041808902759 | 1 | 492.75 | 515.1 | 22.35 | 60000 | 0 | 1341000 | 1335585.1962 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1070865.8478 | 1018127.8829 | 1172245.3124 | 1166152.8884 | 1226848.5855 | 1401162.4833
795 | 11 kV Outgoing Feeder-4 (=F4) | 0 | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
796 | 11 kV Outgoing Feeder-5 (=F5) | 0 | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
797 | 11 kV Outgoing Feeder-6 (=F6) | 0 | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
798 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
799 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
800 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
801 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 | 0 | 041808902786 | 1 | 356.76 | 379.9 | 23.14 | 60000 | 0 | 1388400 | 1382793.8004 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1588331.224 | 1607255.8715 | 1649959.1034 | 1406910.8874 | 1384414.4332 | 1059738.0772
802 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 | 0 | 041808902789 | 1 | 215.77 | 230.47 | 14.7 | 60000 | 0 | 882000 | 878438.5854 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 830100.7076 | 664412.0926 | 761840.3225 | 831600.8302 | 763171.9877 | 845746.7241
803 | 11 kV Outgoing Feeder-12 (=F10) | 0 | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
804 | 11 kV Outgoing Feeder-13 (=F11) | 0 | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
805 | 11 kV Outgoing Feeder-14 (=F12) | 0 | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
806 | 11 kV Outgoing Feeder-15 (=F13) | 0 | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
807 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
808 | 33/0.415 kV Transformer AT-1 | 0 | 0.415 | 0 | 041811907976 | 1 | 1916.44 | 1995.97 | 79.53 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
809 | 33/0.415 kV Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0 | 0
810 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 72083645 | 73017725 | 934080 | 1 | 0 | 934080 | 938316.3983 | Mugdapara | Amulia 33/11 kv | 102 | 618877.1744 | 747742.2401 | 669679.7315 | 704760.429 | 655997.4572 | 731782.37
811 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0
812 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 18045139 | 19053674 | 1008535 | 1 | 0 | 1008535 | 1013109.0793 | Demra | Amulia 33/11 kv | 102 | 1328671.185 | 1368274.6157 | 1317757.7287 | 1370677.2015 | 1292488.6152 | 1242034.7233
813 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 2394570 | 2915432 | 520862 | 1 | 0 | 520862 | 523224.3018 | Demra | Amulia 33/11 kv | 102 | 581908.8947 | 369688.6181 | 572405.5108 | 546070.575 | 498813.9667 | 550647.0061
814 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 71254185 | 73339160 | 2084975 | 1 | 0 | 2084975 | 2094431.1329 | Demra | Amulia 33/11 kv | 102 | 2508124.4895 | 2591251.8147 | 2450741.6785 | 2341533.0936 | 2143176.0462 | 2258006.7634
815 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 16052331 | 16625684 | 573353 | 1 | 0 | 573353 | 575953.3679 | Mugdapara | Amulia 33/11 kv | 102 | 671288.426 | 654683.7051 | 639938.2711 | 588274.3679 | 552448.5186 | 1045691.8176
816 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra | 0 | 1 | 52158655 | 52278896 | 120241 | 1 | 0 | 120241 | 120786.3374 | Demra | Amulia 33/11 kv | 102 | 168139.8027 | 155971.1495 | 189931.2691 | 165276.4 | 158821.9675 | 145542.9861
817 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 15044850 | 16211336 | 1166486 | 1 | 0 | 1166486 | 1171776.4455 | Demra | Amulia 33/11 kv | 102 | 1342546.4505 | 1461872.9578 | 1326521.6668 | 1251754.1184 | 1263380.0786 | 1242709.7581
818 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0
819 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0
820 | 33/0.415 kV Transformer, AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0 | 0
821 | 11 kV Nearest Feeder | B2110N | 11 | 0 | HA021101060-02 | 1 | 80316933 | 81633988 | 1317055 | 1 | 0 | 1317055 | 1313766.3455 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1615577.819 | 1668539.8072 | 1666551.6834 | 1691601.9901 | 1589546.8433 | 1558145.6337
822 | 11kV Spare | 0 | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
823 | 11 kV City Palli Feeder | B2110C | 11 | 0 | HA021100937-02 | 1 | 79831670 | 80522134 | 690464 | 1 | 0 | 690464 | 688739.9281 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 831311.9243 | 885994.3441 | 907412.698 | 936164.8797 | 876024.4652 | 849393.0553
824 | 11 kV R K Mission Road Feeder | B2110R | 11 | 0 | HA021101035-02 | 1 | 18813697 | 20022438 | 1208741 | 1 | 0 | 1208741 | 1205722.8029 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1505793.7255 | 1587170.4652 | 1556832.94 | 1647566.9154 | 1564049.4804 | 1502639.6704
825 | 11 kV Janapath Feeder | B2110J | 11 | 0 | HA021100864-02 | 1 | 33876168 | 35472819 | 1596651 | 1 | 0 | 1596651 | 1592664.201 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 2018970.5577 | 2145298.3795 | 2127410.4471 | 2194112.6593 | 2093083.5306 | 2005205.5254
826 | 11 kV Dhalpur Feeder | B2110D | 11 | 0 | HA021100851-02 | 1 | 88732684 | 89539002 | 806318 | 1 | 0 | 806318 | 804304.6434 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 844139.0145 | 879803.8192 | 873504.546 | 859344.4269 | 844664.2379 | 860069.6023
827 | 11kV WTP | B2110O | 11 | 0 | X0599387 | 1 | 2253.4 | 2506.6 | 253.2 | 1000 | 0 | 253200 | 252567.7657 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 285986.2262 | 561982.597 | 0 | 0 | 145877.5724
828 | 11kV Kamalapur Water pumping | B2110F | 11 | 0 | HA021100474-02 | 1 | 7657094 | 7681209 | 24115 | 1 | 0 | 24115 | 24054.7854 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 97542.6949 | 82536.7668 | 73055.4392 | 36822.7275 | 20221.1849 | 24456.8935
829 | 11 kV Wasa Road Feeder | B2110A | 11 | 0 | HA021001011-02 | 1 | 26301986 | 28031254 | 1729268 | 1 | 0 | 1729268 | 1724950.0596 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 2072782.2659 | 2063419.1707 | 2142959.5506 | 2098895.465 | 1863737.1947 | 2040994.3579
830 | 11kV Sutikhalpar Feeder | B2110K | 11 | 0 | HA021101047-02 | 1 | 80885566 | 82588606 | 1703040 | 1 | 0 | 1703040 | 1698787.5503 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1889889.713 | 1886554.6703 | 2069904.1114 | 2025250.0101 | 1882771.0147 | 2076315.0532
831 | 11kV Spare | 0 | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
832 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
833 | 11kV Spare | 0 | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
834 | 11kV Spare | 0 | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
835 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
836 | AT-1 | 0 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0 | 0
837 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 | 0 | DHK86058 | 1 | 1749.51 | 1763.67 | 14.16 | 60000 | 0 | 849600 | 859250.5994 | Motijheel | Motijheel old 33/11 kV | 75 | 1078290.2684 | 1069121.0153 | 1083441.1947 | 1084055.9235 | 997541.2473 | 913140.3988
838 | 11kV Station Road Feeder | A175H | 11 | 0 | DHK86075 | 1 | 2381.38 | 2382.7 | 1.32 | 60000 | 0 | 79200 | 80099.6322 | Motijheel | Motijheel old 33/11 kV | 75 | 97417.5285 | 97902.6548 | 101497.5399 | 109816.6442 | 95033.1244 | 121832.4707
839 | 11kV Box Culvert Road Feeder | A175F | 11 | 0 | DHK86071 | 1 | 3251.61 | 3279.86 | 28.25 | 60000 | 0 | 1695000 | 1714253.4911 | Motijheel | Motijheel old 33/11 kV | 75 | 1945915.1314 | 1920213.4191 | 1954278.0752 | 1833753.908 | 1479451.1554 | 1996966.8828
840 | 11kV Mohamedan Club Feeder | A174V | 11 | 0 | DHK86062 | 1 | 1722.37 | 1734.42 | 12.05 | 60000 | 0 | 723000 | 731212.5511 | Motijheel | Motijheel old 33/11 kV | 75 | 895632.4025 | 840281.0677 | 917081.3217 | 976079.7817 | 1139171.2585 | 731597.9549
841 | 11kV Amina Ahmed Co. | 0 | 11 | 0 | DHK95754 | 1 | 119456 | 122809 | 3353 | 60 | 0 | 201180 | 203465.202 | Motijheel | Motijheel old 33/11 kV | 75 | 231731.9459 | 212983.3214 | 238309.0167 | 251289.93 | 373020.341 | 139323.2709
842 | 11kV Bangabhaban -1 | 0 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0
843 | 11kV Sonali Bank | A175SB | 11 | 0 | DHK95753 | 1 | 84919 | 89291 | 4372 | 60 | 0 | 262320 | 265299.6907 | Motijheel | Motijheel old 33/11 kV | 75 | 525993.7678 | 476719.8595 | 524063.6289 | 553807.1772 | 446839.6196 | 345775.0268
844 | 11kV NCC Bank Feeder | A133S | 11 | 0 | DHK68123 | 1 | 331.8 | 335.29 | 3.49 | 60000 | 0 | 209400 | 211778.5729 | Motijheel | Motijheel old 33/11 kV | 75 | 238064.0852 | 224635.5392 | 249239.521 | 237424.8118 | 404044.0578 | 147163.9744
845 | 11kV IFIC BANK Feeder | 0 | 11 | 0 | DHK68116 | 1 | 419.59 | 426.1 | 6.51 | 60000 | 0 | 390600 | 395036.8222 | Ramna | Motijheel old 33/11 kV | 75 | 459080.103 | 425846.5168 | 457039.218 | 500616.6574 | 354381.5863 | 554880.5594
846 | 11kV Arambagh Feeder | A174X | 11 | 0 | DHK68117 | 1 | 3437.26 | 3445.31 | 8.05 | 60000 | 0 | 483000 | 488486.393 | Motijheel | Motijheel old 33/11 kV | 75 | 1367498.5561 | 1397665.5071 | 1278373.3459 | 1267688.622 | 59250.2714 | 488536.1447
847 | 11kV Nikotborti Feeder | A175K | 11 | 0 | DHK68114 | 1 | 1439.72 | 1443.26 | 3.54 | 60000 | 0 | 212400 | 214812.6499 | Motijheel | Motijheel old 33/11 kV | 75 | 275204.518 | 264277.1049 | 302690.8881 | 931907.7237 | 862042.4055 | 655000.3125
848 | 11kV Agrani Bank Feeder | A174O | 11 | 0 | DHK95756 | 1 | 378789 | 381960 | 3171 | 60 | 0 | 190260 | 192421.1618 | Motijheel | Motijheel old 33/11 kV | 75 | 232340.8054 | 213403.7622 | 236867.6315 | 255891.186 | 369219.0161 | 144691.1372
849 | 11kV Bangladesh Bank-2 | A133D | 11 | 0 | DHK95755 | 1 | 546 | 552 | 6 | 60000 | Estimated | 882819 | 892846.9338 | Motijheel | Motijheel old 33/11 kV | 75 | 987430.8879 | 706996.5136 | 913123.8185 | 781881.091 | 669891.5592 | 180939.3128
850 | 11kV PDB Design Feeder 14 | 0 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0
851 | 11kV Bangabhaban-2 | 0 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0 | 0
852 | 11/0.4 kV AT | 0 | 0.415 | 0 | ELIC5429 | 1 | 422280 | 422280 | 0 | 1 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 5453.7184 | 4994.8 | 6386.5434 | 8270.9474 | 3518.2644
853 | 11 kV Central Weman | A1111CW | 11 | 0 | 41812909492 | 1 | 179.49 | 188.77 | 9.28 | 60000 | 0 | 556800 | 559606.8157 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 780631.0755 | 589767.3774 | 585552.4072 | 614594.3851 | 602582.0913 | 559727.7485
854 | 11 kV Spare Feeder 2 | 0 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
855 | 11 kV K. M. Das Len | 0 | 11 | 0 | 41812909499 | 1 | 297.27 | 308.53 | 11.26 | 60000 | 0 | 675600 | 679005.6837 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 845732.5401 | 957285.5746 | 992186.0233 | 1031748.0667 | 1006914.6746 | 933883.7569
856 | 11 kV Gopibag | A1111GP | 11 | 0 | 41812909517 | 1 | 44.79 | 46.6 | 1.81 | 60000 | 0 | 108600 | 109147.45 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 151903.4174 | 162651.6346 | 159641.3456 | 169750.8488 | 161492.0005 | 148216.3898
857 | 11kV SPICE TV | B1111E | 11 | 0 | 41812909518 | 1 | 26.14 | 29.4 | 3.26 | 60000 | 0 | 195600 | 196586.015 | Narinda | Motijheel 33/11 KV SS (new) | 111 | 229907.875 | 224111.6034 | 223497.8838 | 229344.2319 | 216326.9708 | 196416.8418
858 | 11 kV Spare Feeder 6 | 0 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
859 | 11 kV Spare Feeder 7 | 0 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
860 | 11 kV BPT-1 | 0 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
861 | 11 kV BPT-2 | 0 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
862 | 10 kV Spare Feeder 8 | 0 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
863 | 11 kV Spare Feeder 9 | 0 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
864 | 11 kV South Kamlapur | A1111SK | 11 | 0 | 41812909473 | 1 | 406.2 | 413.52 | 7.32 | 60000 | 0 | 439200 | 441413.9968 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 616997.6645 | 555002.1425 | 559648.3398 | 571253.7429 | 550760.0315 | 1048359.8303
865 | 11 kV Spare Feeder 11 | 0 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0 | 0
866 | 11 kV Answer Camp | A1111AC | 11 | 0 | 41812909514 | 1 | 215.83 | 225.49 | 9.66 | 60000 | 0 | 579600 | 582521.7499 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 703799.6173 | 759868.7052 | 750615.5343 | 784345.2339 | 758048.2709 | 729031.836
867 | 11 kV Shapla Chattar | A1111SC | 11 | 0 | 41812909516 | 1 | 194.83 | 210.07 | 15.24 | 60000 | 0 | 914400 | 919009.4688 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 1155990.8714 | 1143527.9043 | 1182550.7976 | 639274.4731 | 598966.5988 | 591058.0422
868 | 11 kV Sayedabad | 0 | 11 | 0 | 41812909497 | 1 | 110.21 | 118.23 | 8.02 | 60000 | 0 | 481200 | 483625.7179 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 303220.3351 | 309783.0751 | 311451.2289 | 306394.2625 | 315753.0159 | 300047.8135
869 | 33/0.4 kV Aux Transformer | 0 | 0.415 | 0 | 41901920686 | 1 | 1382.5 | 1459.01 | 76.51 | 1 | 0 | 76.51 | 76.8957 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 83.5078 | 86.4785 | 0 | 0 | 0 | 0
870 | Inner Circular Road Feeder | A161Z | 11 | 0 | BD014042 | 1 | 42241 | 43389 | 1148 | 1000 | 0 | 1148000 | 1167930.2881 | Motijheel | P & T 33/11 KV SS | 61 | 717359.185 | 740621.6003 | 751211.0308 | 786225.5313 | 2044037.2926 | 2028898.6132
871 | NSI New Building Expres Feeder | D361NS | 11 | 0 | BD013982 | 1 | 10797 | 11095 | 298 | 1000 | 0 | 298000 | 303173.5417 | Ramna | P & T 33/11 KV SS | 61 | 408763.2027 | 366793.6012 | 408464.6789 | 417588.6558 | 429529.4901 | 413128.6457
872 | Police Hospital RMU Feeder | D661H | 11 | 0 | BD014044 | 1 | 3920 | 4037 | 117 | 1000 | 0 | 117000 | 119031.2227 | Rajarbag | P & T 33/11 KV SS | 61 | 160874.6268 | 178874.6877 | 184011.3157 | 189813.0254 | 182072.2195 | 167833.5123
873 | Jonaki O/H Feeder | D661J | 11 | 0 | BD014013 | 1 | 36961 | 38143 | 1182 | 1000 | 0 | 1182000 | 1202520.558 | Rajarbag | P & T 33/11 KV SS | 61 | 1451918.8017 | 1556611.7488 | 1494333.6521 | 1501520.9321 | 1581312.3149 | 1420129.7195
874 | Nayapalton Overhead Feeder | D361N | 11 | 0 | BD014014 | 1 | 26556 | 27311 | 755 | 1000 | 0 | 755000 | 768107.463 | Ramna | P & T 33/11 KV SS | 61 | 920728.9962 | 1002904.148 | 1013073.2878 | 1003011.9866 | 1008941.636 | 976215.0449
875 | Masjid Gali Over Head Feeder | D361MG | 11 | 0 | BD014016 | 1 | 16316 | 16992 | 676 | 1000 | 0 | 676000 | 687735.9536 | Ramna | P & T 33/11 KV SS | 61 | 843832.9482 | 902412.7504 | 918034.4764 | 899114.3306 | 924444.0314 | 878891.4697
876 | Spare Feeder (Feeder-8) | 0 | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 61 | 0 | 0 | 0 | 0 | 0 | 0
877 | Mid Way Over Head Feeder | D361MW | 11 | 0 | BD014015 | 1 | 24754 | 25465 | 711 | 1000 | 0 | 711000 | 723343.5844 | Ramna | P & T 33/11 KV SS | 61 | 925787.9468 | 990845.1803 | 982741.7522 | 1022992.3051 | 1000894.2451 | 972242.6541
878 | Palton Thana Over Head Feeder | D661F | 11 | 0 | BD014033 | 1 | 26289 | 27288 | 999 | 1000 | 0 | 999000 | 1016343.5173 | Rajarbag | P & T 33/11 KV SS | 61 | 1303185.6562 | 1382761.6309 | 1360874.8956 | 1387633.1169 | 1346932.0545 | 1294006.3108
879 | Police Hospital (South) U/G Feeder 7 | 0 | 11 | 0 | BD014034 | 1 | 12743 | 12871 | 128 | 1000 | 0 | 128000 | 130222.1924 | Rajarbag | P & T 33/11 KV SS | 61 | 174027.8982 | 183899.2576 | 186033.4181 | 181820.898 | 172012.9808 | 167833.5123
880 | China Town Express Feeder | D361CT | 11 | 0 | BD013943 | 1 | 6925 | 7132 | 207 | 1000 | 0 | 207000 | 210593.7018 | Ramna | P & T 33/11 KV SS | 61 | 268124.378 | 282380.8272 | 287138.5367 | 264739.2196 | 295741.6161 | 284025.9439
881 | Fakirapul Bazar O/H Feeder | A161FB | 11 | 0 | BD014032 | 1 | 32179 | 33315 | 1136 | 1000 | 0 | 1136000 | 1155721.9576 | Motijheel | P & T 33/11 KV SS | 61 | 1453942.382 | 1464159.663 | 1476134.7307 | 1280738.4132 | 1354979.4454 | 1402253.9607
882 | PWD Ouarter (RMU) | A161PW | 11 | 0 | BD013937 | 1 | 2615 | 2737 | 122 | 1000 | 0 | 122000 | 124118.0271 | Motijheel | P & T 33/11 KV SS | 61 | 149744.9357 | 156766.5803 | 149635.5754 | 151850.4203 | 150888.5797 | 145985.3628
883 | Postal Quarter RMU | A161PO | 11 | 0 | BD013945 | 1 | 3209 | 3356 | 147 | 1000 | 0 | 147000 | 149552.0491 | Motijheel | P & T 33/11 KV SS | 61 | 176051.4784 | 181889.4296 | 177945.0086 | 177824.8343 | 174024.8285 | 164854.2192
884 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | DHKH4409 | 1 | 1476 | 1497 | 21 | 100 | 0 | 2100 | 2136.4578 | Rajarbag | P & T 33/11 KV SS | 61 | 0 | 4220.6387 | 5762.9918 | 6093.9971 | 301.7772 | 0
885 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | DHKH4411 | 1 | 578 | 607 | 29 | 100 | 0 | 2900 | 2950.3465 | Rajarbag | P & T 33/11 KV SS | 61 | 5666.0246 | 1406.8796 | 0 | 5394.686 | 0 | 5362.7276
886 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 452 | 469.4 | 17.4 | 40000 | 0 | 696000 | 698504.7602 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 873041.3399 | 948762.3589 | 895110.6473 | 1426015.7648 | 1381038.2208 | 1302977.567
887 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 78.6 | 81.8 | 3.2 | 40000 | 0 | 128000 | 128460.6456 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 186790.2402 | 199525.1313 | 209665.557 | 202559.0575 | 214648.1692 | 201076.785
888 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 324.1 | 339.9 | 15.8 | 40000 | 0 | 632000 | 634274.4374 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 775585.5625 | 851035.764 | 818502.0784 | 866952.7661 | 866692.6078 | 735941.0332
889 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 768.6 | 792.7 | 24.1 | 40000 | 0 | 964000 | 967469.2368 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 1218197.2185 | 1388532.036 | 1274121.462 | 2264610.2629 | 2211281.1394 | 2079133.9572
890 | 11 KV Majar Feeder | 0 | 11 | 0 | 96 | 1 | 71.1 | 78.2 | 7.1 | 40000 | 0 | 284000 | 285022.0573 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 369519.8229 | 407194.1454 | 391106.9045 | 417271.6585 | 400946.5802 | 382045.8916
891 | 11 kV Feeder-6 | 0 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0
892 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 355.6 | 364.4 | 8.8 | 40000 | 0 | 352000 | 353266.7753 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 495400.2022 | 517136.5647 | 483843.5932 | 563114.1799 | 1081340.777 | 1001362.3894
893 | 11 kV Feeder-8 | 0 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0
894 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 232.7 | 239.1 | 6.4 | 40000 | 0 | 256000 | 256921.2911 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 345155.8786 | 354258.9065 | 330626.4553 | 352452.7601 | 340197.0984 | 337808.9988
895 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 363.8 | 379.3 | 15.5 | 40000 | 0 | 620000 | 622231.2519 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 1344077.5978 | 2296574.9803 | 2165200.0794 | 449681.1077 | 437396.2693 | 402153.5701
896 | 11 kV Feeder-11 | 0 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0
897 | Dhaka Railway | 0 | 11 | Motijheel | 150 | 1 | 71.8 | 74.6 | 2.8 | 40000 | 0 | 112000 | 112403.0649 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 101516.4349 | 199525.1313 | 209665.557 | 230917.3256 | 222748.1001 | 217162.9278
898 | Jasimuddin Feeder-13 | 0 | 11 | 0 | 91 | 1 | 270.1 | 299.6 | 29.5 | 40000 | 0 | 1180000 | 1184246.5762 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 1445594.0326 | 1653208.2305 | 1568459.6478 | 1713649.6265 | 1656435.8718 | 1097879.2463
899 | Police Box Feeder-14 | 0 | 11 | 0 | 18 | 1 | 115.6 | 127.9 | 12.3 | 40000 | 0 | 492000 | 493770.6063 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 605037.9519 | 655582.5742 | 628996.6711 | 656291.3463 | 664194.3349 | 643445.7121
900 | 11 kV Feeder-15 | 0 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0
901 | 11 kV Feeder-16 | 0 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0 | 0
902 | Auxiliary -1 (AT-1 ) | 0 | 0.415 | 0 | DHKF 7632 | 1 | 1018.7 | 1052.87 | 34.17 | 100 | 0 | 3417 | 3429.2971 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 7083.8168 | 0 | 4701.3469 | 8715.1034 | 2871.4255 | 5128.4634
903 | Auxiliary -1 (AT-2 ) | 0 | 0.415 | 0 | DHKF 7733 | 1 | 156.6 | 156.6 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 1938.9639 | 1823.2118 | 0 | 0 | 0 | 0
904 | 11 kV DIT S/S-1 Feeder | 0 | 11 | Motijheel | 4150750 | 1 | 218543.72 | 219429.19 | 885.47 | 1000 | Estimated | 729797.04 | 734566.8339 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 730932.291 | 825621.5358 | 884099.9496 | 816951.1322 | 793502.3098 | 860468.6016
905 | 11 kV Bangabhaban Switching Circuit-1 | 0 | 11 | Motijheel | 4150743 | 1 | 24310.71 | 24348.79 | 38.08 | 1000 | 0 | 38080 | 38328.8826 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 45380.4829 | 61964.371 | 72049.9558 | 82523.1488 | 83389.7606 | 79020.0597
906 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0
907 | 11 kV Bangladesh Bank Feeder | 0 | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 240728.715
908 | 11 kV P & T Substation | 0 | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0
909 | 11 kV Osmani Feeder | 0 | 11 | Ramna | 4150754 | 1 | 33902.7 | 33904.2 | 1.5 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 20212.3186
910 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 670942.44 | 675327.5731 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 670021.2667 | 766648.569 | 798145.7878 | 731598.0289 | 710599.0834 | 737544.5157
911 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 16026.75 | 16090.3 | 63.55 | 1000 | 0 | 63550 | 63965.3489 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 73704.4745 | 67064.6079 | 76956.258 | 79365.3753 | 70158.8804 | 76837.1293
912 | 11 kV Motijheel-1 Feeder | 0 | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0
913 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 250080.37 | 251097.91 | 1017.54 | 1000 | 0 | 1017540 | 1024190.419 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 1159901.5065 | 1104426.7361 | 1181560.7231 | 1155594.7497 | 1181422.0182 | 1217478.907
914 | 11 kV Bangabhaban Switching Circuit-2 | 0 | 11 | Motijheel | 4150737 | 1 | 14984.45 | 15124.38 | 139.93 | 1000 | 0 | 139930 | 140844.5519 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 163473.9003 | 173027.2895 | 175243.8256 | 162199.2891 | 174416.2041 | 171420.6744
915 | 11 kV Motijheel-2 Feeder | 0 | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0 | 0
916 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 243644.097 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
917 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 164831.63 | 165136.78 | 305.15 | 1000 | 0 | 305150 | 307144.3937 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 367060.1011 | 339501.426 | 365711.3213 | 363925.8833 | 326878.2024 | 270087.1078
918 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20763.9 | 20803.97 | 40.07 | 1000 | Estimated | 176563.8 | 177717.7824 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 182733.0727 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
919 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82552.02 | 186.07 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
920 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 123820.22 | 124061.84 | 241.62 | 1000 | 0 | 241620 | 243199.1755 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 300166.2046 | 298839.8125 | 325451.3768 | 302665.0764 | 348419.8864 | 313139.3465
921 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273191.92 | 273251.62 | 59.7 | 1000 | 0 | 59700 | 60090.1862 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 98812.5217 | 790606.2505 | 819439.2218 | 796304.7174
922 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 81979.59 | 82213.59 | 234 | 1000 | 0 | 234000 | 235529.3729 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 274686.6308 | 474442.2708 | 529113.3929 | 587426.078 | 481785.1466 | 474463.9677
923 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192879.03 | 192985.49 | 106.46 | 1000 | Estimated | 235418.4 | 236957.0432 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 243644.097 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
924 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 63412931 | 1 | 78910 | 90029 | 11119 | 1 | 0 | 11119 | 11191.6714 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 5939.9222 | 6215.6589 | 3575.8026 | 0 | 0
925 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 63403117 | 1 | 22885.4 | 22902 | 16.6 | 1 | Estimated | 5000 | 5032.6789 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 5007.7779 | 5010.0559 | 5047.636 | 5012.339 | 5030.7529 | 5053.0797
926 | 11 kV Bonogram Feeder | B124B | 11 | 0 | 06604467 | 1 | 25159.72 | 25262.79 | 103.07 | 8000 | 0 | 824560 | 833343.2066 | Narinda | Narinda 33/11KV S/S | 24 | 1081937.7982 | 1068648.5129 | 1111412.0708 | 1143423.9412 | 1139801.4532 | 1096395.2732
927 | 11 kV Sha Saheb Len Feeder | B524H | 11 | 0 | 06604469 | 1 | 16969.66 | 17038.74 | 69.08 | 8000 | 0 | 552640 | 558526.7169 | Swamibag | Narinda 33/11KV S/S | 24 | 661053.8831 | 660371.6402 | 659718.6519 | 672430.175 | 685656.1379 | 629657.0471
928 | 11 kV Sadiabad Water Treatment | B224W | 11 | 0 | 06604354 | 1 | 530.01 | 538.25 | 8.24 | 40000 | 0 | 329600 | 333110.8966 | Maniknagar | Narinda 33/11KV S/S | 24 | 795173.7239 | 352381.8247 | 28757.3823 | 552771.4205 | 653217.1868 | 492385.8425
929 | 11 kV Manashi Feeder | B124M | 11 | 0 | 06604353 | 1 | 5614.2 | 5635.85 | 21.65 | 40000 | 0 | 866000 | 875224.6252 | Narinda | Narinda 33/11KV S/S | 24 | 1137753.6547 | 1160429.802 | 1160826.1643 | 1102291.2443 | 1122855.7324 | 1066634.3599
930 | 11 kV Jatrabari Feeder | B524E | 11 | 0 | 06604324 | 1 | 3581.5 | 3617.32 | 35.82 | 40000 |  | 1432800 | 1448062.1743 | Swamibag | Narinda 33/11KV S/S | 24 | 2046581.4052 | 2127657.1553 | 2119945.619 | 2124511.9226 | 2030258.73 | 1913892.8816
931 | 11 kV Wari Feeder | B124W | 11 | 0 | 06604291 | 1 | 8679.86 | 8709.16 | 29.3 | 40000 | 0 | 1172000 | 1184484.1348 | Narinda | Narinda 33/11KV S/S | 24 | 1567697.5349 | 1678876.6245 | 1616488.912 | 1686359.282 | 1652611.2397 | 1532808.0158
932 | 11 kV Narinda Feeder | B124N | 11 | 0 | 06604348 | 1 | 7414.52 | 7442.6 | 28.08 | 40000 | 0 | 1123200 | 1135164.3175 | Narinda | Narinda 33/11KV S/S | 24 | 1444336.4028 | 1555745.5042 | 1546013.0737 | 1594908.1278 | 1590073.4608 | 1585232.3889
933 | 11 kV Distillary Feeder | B524D | 11 | 0 | 06604347 | 1 | 6095.73 | 6121.16 | 25.43 | 40000 | 0 | 1017200 | 1028035.2064 | Swamibag | Narinda 33/11KV S/S | 24 | 1274866.5196 | 1339455.9704 | 1343496.2969 | 1318115.968 | 1326607.8506 | 1271895.9437
934 | 11 kV Thatari Bazar Feeder | B124T | 11 | 0 | 06604296 | 1 | 5110.49 | 5129.92 | 19.43 | 40000 | 0 | 777200 | 785478.7283 | Narinda | Narinda 33/11KV S/S | 24 | 1002663.1035 | 1062005.913 | 1059567.7759 | 1097413.8494 | 1083315.7174 | 1015016.5156
935 | 11 kV Swamibagh Feeder | B524C | 11 | 0 | 06604352 | 1 | 7894.28 | 7918.91 | 24.63 | 40000 | 0 | 985200 | 995694.3426 | Swamibag | Narinda 33/11KV S/S | 24 | 1313290.4788 | 1313533.6293 | 1354837.2364 | 1370141.5135 | 1100261.4381 | 886375.1694
936 | 11 kV Tipu Sultan Feeder | B124S | 11 | 0 | 06604322 | 1 | 6459.68 | 6482.22 | 22.54 | 40000 | 0 | 901600 | 911203.8361 | Narinda | Narinda 33/11KV S/S | 24 | 1115103.7419 | 1147873.668 | 1151915.4261 | 1136839.4581 | 1115189.8112 | 1101315.099
937 | 11 kV Spare | 0 | 11 | 0 | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0
938 | 11 kV Folder Street Feeder | B124F | 11 | 0 | DHK00089 | 1 | 41171.3 | 43986.5 | 2815.2 | 444.44 | 0 | 1251187.488 | 1264515.1272 | Narinda | Narinda 33/11KV S/S | 24 | 1585927.4386 | 1742899.9791 | 1675427.0415 | 1798340.7365 | 1748933.3106 | 1624153.5662
939 | 11 kV Bhajohari Feeder | B124V | 11 | 0 | DHK27842 | 1 | 424175 | 431839 | 7664 | 80 | 0 | 613120 | 619650.9494 | Narinda | Narinda 33/11KV S/S | 24 | 785385.7258 | 835023.4135 | 806745.8319 | 813305.5973 | 819688.7194 | 775800.0686
940 | 11 kV Lal mohon shaha Feeder | B124L | 11 | 0 | DHK00086 | 1 | 41548.8 | 43431.7 | 1882.9 | 444.44 | 0 | 836836.076 | 845750.0473 | Narinda | Narinda 33/11KV S/S | 24 | 1056805.6006 | 1090752.6026 | 1096369.8618 | 1097222.2328 | 1092539.7614 | 1048880.237
941 | 11 kV Dupkhola Feeder | B524A | 11 | 0 | 8838024/8838029 | 1 | 38567.6 | 39022.1 | 454.5 | 1000 | 0 | 454500 | 459341.3304 | Swamibag | Narinda 33/11KV S/S | 24 | 602548.3495 | 612719.0865 | 555706.0354 | 579800.3171 | 568589.4506 | 537047.3757
942 | 11/0.4 kV Aux Transformer-1 | 0 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0
943 | 11/0.4 kV Aux Transformer-2 | 0 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0 | 0
944 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63497.4 | 63748 | 250.6 | 2222.22 | 0 | 556888.332 | 559882.2686 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 648124.404 | 633672.3537 | 653524.1946 | 604954.0102 | 476949.7245 | 555416.4351
945 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4688.31 | 4714.17 | 25.86 | 40000 | 0 | 1034400 | 1039961.1294 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1308522.8246 | 1300047.3482 | 1372334.5518 | 1164609.944 | 1430849.1736 | 1481110.4937
946 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0
947 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5181.29 | 5192.58 | 11.29 | 40000 | 0 | 451600 | 454027.8867 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 509541.8516 | 496023.0204 | 523045.3096 | 442936.2442 | 536568.4401 | 493703.4979
948 | 11kV Spare | 0 | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0
949 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5527.79 | 5552.12 | 24.33 | 40000 | 0 | 973200 | 978432.1066 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1158159.6042 | 1128130.2786 | 1172692.7423 | 878663.7611 | 1216221.7976 | 1419397.5564
950 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 40077.0255 | 0
951 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4169.95 | 4194.33 | 24.38 | 40000 | 0 | 975200 | 980442.859 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1163400.1454 | 1221939.8271 | 1252630.6213 | 1111745.9438 | 834662.018 | 740555.2468
952 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 882819 | 887565.2014 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1078713.9994 | 1184790.4407 | 1110503.0608 | 1217802.7423 | 1144679.3389 | 925694.0585
953 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 5983.44 | 6005.67 | 22.23 | 40000 | 0 | 889200 | 893980.5068 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1075923.4193 | 1095518.3755 | 1129680.4826 | 931127.2764 | 1021492.1651 | 1019206.2302
954 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8334.99 | 8373.78 | 38.79 | 40000 | 0 | 1551600 | 1559941.6941 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1898688.3869 | 2041666.1823 | 1567512.8248 | 2037666.9172 | 1989498.8221 | 1947085.7372
955 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3791.32 | 3799.62 | 8.3 | 40000 | 0 | 332000 | 333784.8946 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 430127.4966 | 443280.3129 | 472729.0813 | 450545.4563 | 410865.9482 | 427409.0643
956 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7301.75 | 7326.5 | 24.75 | 40000 | 0 | 990000 | 995322.4266 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1252086.2271 | 586209.0241 | 1209618.3616 | 1050071.2769 | 1251993.0269 | 1073805.1079
957 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3606.94 | 3612.86 | 5.92 | 40000 | 0 | 236800 | 238073.0814 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 277345.5648 | 287870.5029 | 292158.7455 | 264720.4859 | 275126.2119 | 281286.3072
958 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0 | 0
959 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 05378636 | 1 | 176640.6 | 178179.3 | 1538.7 | 2 | 0 | 3077.4 | 3093.9447 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 5594.0762 | 5930.3337 | 4006.0239 | 7168.6788 | 4775.6076 | 4915.4072
960 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 40639116 | 41256087 | 616971 | 1 | 0 | 616971 | 617669.4796 | Bangshal | Banshal 33/11KV S/S | 78 | 748100.1808 | 769760.338 | 773303.2759 | 760951.1172 | 778854.3109 | 716311.3918
961 | 11 kV Spare Feeder | 0 | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0
962 | 11 kV Siddikbazar Feeder | 0 | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0
963 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 53863751 | 54945882 | 1082131 | 1 | 0 | 1082131 | 1083356.0922 | Banglabazar | Banshal 33/11KV S/S | 78 | 1317991.7768 | 1424094.0148 | 1411190.2742 | 1426877.2604 | 1429747.5487 | 1353751.6158
964 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 22867036 | 23435352 | 568316 | 1 | 0 | 568316 | 568959.3967 | Bangshal | Banshal 33/11KV S/S | 78 | 737371.3191 | 742977.1081 | 744097.7084 | 751903.1259 | 737930.5287 | 715455.6721
965 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 51129746 | 52356480 | 1226734 | 1 | 0 | 1226734 | 1228122.7989 | Bangshal | Banshal 33/11KV S/S | 78 | 1543005.6588 | 1634853.1578 | 1636226.6255 | 1167271.1296 | 1660584.0104 | 1409457.3709
966 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 65782506 | 66698574 | 916068 | 1 | 0 | 916068 | 917105.0905 | Bangshal | Banshal 33/11KV S/S | 78 | 1128071.6101 | 1204002.0348 | 1205928.3277 | 1183358.8995 | 1169829.7548 | 1127796.6211
967 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 32609799 | 33052156 | 442357 | 1 | 0 | 442357 | 442857.7972 | Bangshal | Banshal 33/11KV S/S | 78 | 505257.2343 | 581501.911 | 1106821.025 | 1430551.6276 | 1633419.2244 | 1486833.0286
968 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 67416873 | 68646258 | 1229385 | 1 | 0 | 1229385 | 1230776.8001 | Bangshal | Banshal 33/11KV S/S | 78 | 1482806.5471 | 1592214.2158 | 1582391.9071 | 1508639.2033 | 1596892.4609 | 1498407.2378
969 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 54042708 | 55024234 | 981526 | 1 | 0 | 981526 | 982637.1962 | Narinda | Banshal 33/11KV S/S | 78 | 1224359.1662 | 1261180.3015 | 1301441.3762 | 1139549.3681 | 1267199.3373 | 1145519.8164
970 | AT-1 | 0 | 0.415 | 0 | DHK-4415 | 1 | 764.01 | 777.4 | 13.39 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0 | 0
971 | AT-2 | 0 | 0.415 | 0 | DHK-4410 | 1 | 771.03 | 786.95 | 15.92 | 100 | 0 | 7000 | 7007.9248 | Bangshal | Banshal 33/11KV S/S | 78 | 7005.1331 | 7007.3859 | 7008.295 | 7021.7228 | 7023.9917 | 6997.7081
972 | 11 kV Nayanagor Feeder | A418N | 11 | 0 | DHK-61125 | 1 | 933689.8 | 957166.8 | 23477 | 60 | 0 | 1408620 | 1425042.8921 | Kazla | Kazla 33/11KV S/S | 18 | 1775388.4538 | 1866468.623 | 1836553.7788 | 1866699.9643 | 1792344.292 | 1710856.4639
973 | 11 kV Madrasa Bazar Feeder | A418B | 11 | 0 | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1530219.6 | 1548060.2038 | Kazla | Kazla 33/11KV S/S | 18 | 1602675.9202 | 1563148.5482 | 1846586.4161 | 1853855.1196 | 1913492.0332 | 1855425.2355
974 | 11 kV Kazla Feeder | A418K | 11 | 0 | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2354184 | 2381631.0828 | Kazla | Kazla 33/11KV S/S | 18 | 2712220.788 | 2825691.6063 | 2954538.2657 | 3027963.362 | 3049627.928 | 2968680.3768
975 | 11 kV Sayedabad Feeder | B218S | 11 | 0 | HA021101239-02 | 1 | 36964648 | 36964660 | 12 | 1000 | Estimated | 941673.6 | 952652.4331 | Maniknagar | Kazla 33/11KV S/S | 18 | 1232827.6309 | 1202421.9601 | 1231057.6107 | 988722.7304 | 1076339.2687 | 556627.5706
976 | 11 kV Zenith Feeder | A418Z | 11 | 0 | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0
977 | 11 kV Paterbagh Feeder | B318P | 11 | 0 | HA-021200060 | 1 | 120971.5 | 122840.5 | 1869 | 1000 | 0 | 1869000 | 1890790.3944 | Jurain | Kazla 33/11KV S/S | 18 | 2010101.6778 | 2308939.6211 | 2025231.2443 | 2541656.3466 | 2207984.2138 | 2092993.2394
978 | 11 kV Matuail Feeder | A418M | 11 | 0 | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1471365 | 1488519.4268 | Kazla | Kazla 33/11KV S/S | 18 | 1849241.4463 | 1803632.9402 | 1969692.1771 | 1730264.7783 | 1734102.1551 | 1855425.2355
979 | 11 kV Kutubkhali Feeder | B326C | 11 | 0 | DHK-61117 | 1 | 838596.4 | 873380.8 | 34784.4 | 60 | 0 | 2087064 | 2111396.7703 | Jurain | Kazla 33/11KV S/S | 18 | 2432494.6655 | 2317847.2676 | 2260753.1891 | 2379719.4891 | 2279252.9698 | 2232712.5636
980 | 11 kV Mridhabari Feeder | A418R | 11 | 0 | DHK-61118 | 1 | 699957.1 | 722924.6 | 22967.5 | 60 | 0 | 1378050 | 1394116.481 | Kazla | Kazla 33/11KV S/S | 18 | 1532023.4409 | 1493309.739 | 1567790.1074 | 1353302.4526 | 1381440.9902 | 1371332.0993
981 | 11 kV Muslim Nagar Feeder | A418U | 11 | 0 | DHK-61011 | 1 | 154325.8 | 192344.8 | 38019 | 60 | 0 | 2281140 | 2307735.4737 | Kazla | Kazla 33/11KV S/S | 18 | 2627245.0572 | 2655800.5175 | 2583205.2246 | 2385633.1534 | 2345596.1288 | 2459477.0573
982 | 11 kV Jatrabari Thana Feeder | A418H | 11 | 0 | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0
983 | 11 kV Mirhazirbag Feeder | B518D | 11 | 0 | DHK-61008 | 1 | 348875.3 | 375123.8 | 26248.5 | 60 | 0 | 1574910 | 1593271.6426 | Swamibag | Kazla 33/11KV S/S | 18 | 1997346.9786 | 2119778.8003 | 2106094.7503 | 2092254.4374 | 2069592.0061 | 1962979.7252
984 | 11 kV Mukti Sharani Feeder | B318T | 11 | 0 | DHK-61014 | 1 | 213216.9 | 213219.9 | 3 | 60 | 0 | 180 | 182.0986 | Jurain | Kazla 33/11KV S/S | 18 | 1171257.2192 | 2474942.6039 | 2420269.7538 | 2465205.4697 | 2452063.3964 | 2370251.5382
985 | 11 kV Kadamtali Feeder | B418K | 11 | 0 | DHK-61006 | 1 | 452013.2 | 485277.4 | 33264.2 | 60 | 0 | 1995852 | 2019121.3431 | Shyampur | Kazla 33/11KV S/S | 18 | 2235311.7183 | 2567504.4926 | 2822437.563 | 2221373.5062 | 2471771.8805 | 3092469.9692
986 | 11kV Rayerbagh Feeder | E218R | 11 | 0 | DHK-61012 | 1 | 448270.6 | 473065.1 | 24794.5 | 60 | 595068 | 1487670 | 1505014.5244 | Matuail | Kazla 33/11KV S/S | 18 | 1463413.2136 | 898785.6229 | 322767.8137 | 1280357.0984 | 1277473.0974 | 837095.6004
987 | 11 kV Donia Feeder | B318D | 11 | 0 | DHK-61013 | 1 | 2084796 | 2100163 | 15367 | 60 | 0 | 922020 | 932769.6947 | Jurain | Kazla 33/11KV S/S | 18 | 2275838.0926 | 2097995.927 | 2006588.1861 | 2090084.0617 | 2017361.1702 | 1952856.964
988 | 11 kV Nimtoli Feeder | A418T | 11 | 0 | HA-021100855-02 | 1 | 34003353 | 35425036 | 1421683 | 1 | 0 | 1421683 | 1438258.1917 | Kazla | Kazla 33/11KV S/S | 18 | 1595582.0613 | 1529815.767 | 1526570.9331 | 1509829.6282 | 1633862.5979 | 1591423.3402
989 | 11 kV Gobindapur Feeder | A441G | 11 | 0 | HA-021101057-02 | 1 | 28747928 | 29299106 | 551178 | 1 | 0 | 551178 | 557604.1027 | Kazla | Kazla 33/11KV S/S | 18 | 679496.8713 | 715534.2901 | 710807.5855 | 721136.817 | 697773.6086 | 686441.9856
990 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 | 0 | 9A56136 | 1 | 3801 | 3949.3 | 148.3 | 10000 | 0 | 1483000 | 1500290.0775 | Kazla | Kazla 33/11KV S/S | 18 | 1773738.3704 | 1822390.0739 | 1778276.5099 | 1887901.7718 | 1946667.4736 | 1703398.1226
991 | 11 kV Samad Nagar Gate (Old) | A418A | 11 | 0 | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0
992 | 11 kV Dharmik Para | A418D | 11 | 0 | 8K55676 | 1 | 814.2 | 820.6 | 6.4 | 4000 | 0 | 25600 | 25898.4666 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 23977.7413 | 1140208.9403
993 | 11 kV Sheikhdi Feeder | A418I | 11 | 0 | 9A56133 | 1 | 16766 | 17420.9 | 654.9 | 4000 | 0 | 2619600 | 2650141.5287 | Kazla | Kazla 33/11KV S/S | 18 | 3268543.7125 | 3436798.8591 | 3359798.9198 | 3415699.9979 | 3248780.7482 | 3103743.9224
994 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | T-5 Sum | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 0
995 | 11 kV Jenith Feeder | A418Z | 11 | 0 | 61903661 | 1 | 22659 | 23175.9 | 516.9 | 2000 | 3229000 | 1033800 | 1045852.9212 | Kazla | Kazla 33/11KV S/S | 18 | 1210196.351 | 1200080.6383 | 617589.258 | 551840.3941 | 574043.3834 | 0
996 | 11 KV Samad Nagor Gate | A418A | 11 | 0 | 61903675 | 1 | 19683 | 20299.2 | 616.2 | 2000 | 0 | 1232400 | 1246768.3692 | Kazla | Kazla 33/11KV S/S | 18 | 1325742.7363 | 1296103.4337 | 1368574.557 | 1134163.594 | 1293375.6231 | 1288887.6302
997 | 11 KV Bibir Bagicha | B218I | 11 | 0 | 61903557 | 1 | 38466 | 38947.4 | 481.4 | 2000 | 0 | 962800 | 974025.1427 | Maniknagar | Kazla 33/11KV S/S | 18 | 1414936.4372 | 1478955.3526 | 1458247.4647 | 1460126.3972 | 1445370.1189 | 1356006.601
998 | 33/0.4 kV AT-1 | 0 | 0.415 | 0 | 503043 | 1 | 96204 | 96207 | 3 | 10 | 0 | 30 | 30.3498 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0 | 244.069
999 | 33/0.4 kV AT-2 | 0 | 0.415 | 0 | 503044 | 1 | 95990 | 96336 | 346 | 10 | 0 | 3460 | 3500.3396 | Kazla | Kazla 33/11KV S/S | 18 | 6121.9313 | 14219.5459 | 6072.6574 | 6096.5612 | 6096.0359 | 6101.7246
1000 | Auxiliary Transformer | 0 | 0.415 | 0 | 41901920685 | 1 | 2767.96 | 2874.18 | 106.22 | 160 | 0 | 16995.2 | 17193.3445 | Kazla | Kazla 33/11KV S/S | 18 | 19919.386 | 20587.2873 | 0 | 0 | 0 | 0
1001 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur | 0 | 1 | 752.49 | 799.6936 | 47.2036 | 40000 | 0 | 1888144 | 1892333.6894 | Shyampur | Shyampur 33/11KV S/S | 26 | 1814264.1154 | 1610415.5328 | 1658511.8396 | 1848660.4463 | 1329002.2614 | 1796570.0888
1002 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1003 | 11 kV Road No.-21 Feeder | B426E | 11 | 0 | BD001943 | 1 | 1085.02 | 1100.56 | 15.54 | 40000 | 0 | 621600 | 622979.2968 | Shyampur | Shyampur 33/11KV S/S | 26 | 558390.1777 | 490213.532 | 606607.4764 | 536986.5578 | 689153.8135 | 726162.1684
1004 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1583.91 | 1606.52 | 22.61 | 40000 | 0 | 904400 | 906406.8147 | Shyampur | Shyampur 33/11KV S/S | 26 | 891408.4354 | 575920.7998 | 812129.1164 | 684264.5087 | 768373.9842 | 842780.9272
1005 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1473.51 | 1491.05 | 17.54 | 40000 | 0 | 701600 | 703156.8125 | Shyampur | Shyampur 33/11KV S/S | 26 | 766828.9661 | 770964.9094 | 745215.0941 | 653846.0494 | 678120.977 | 664045.6474
1006 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1390.8 | 1411.27 | 20.47 | 40000 | 0 | 818800 | 820616.8729 | Fatullah | Shyampur 33/11KV S/S | 26 | 1034936.8854 | 1058124.3068 | 991363.1049 | 1100803.9423 | 1060453.8119 | 1011898.1651
1007 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3458.08 | 3529.38 | 71.3 | 40000 | 0 | 2852000 | 2858328.4338 | Shyampur | Shyampur 33/11KV S/S | 26 | 2421034.6696 | 2293670.6681 | 2291008.6698 | 1731865.3068 | 2347543.3088 | 2415731.5404
1008 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1009 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2255.93 | 2300.68 | 44.75 | 40000 | 0 | 1790000 | 1793971.9132 | Shyampur | Shyampur 33/11KV S/S | 26 | 1756207.6637 | 1462630.5709 | 1686790.98 | 1265223.6985 | 1510257.147 | 1400226.6095
1010 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 496.84 | 500.99 | 4.15 | 40000 | 0 | 166000 | 166368.345 | Fatullah | Shyampur 33/11KV S/S | 26 | 155220.3743 | 135769.9243 | 127455.2807 | 91577.1387 | 112254.6055 | 96981.9232
1011 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3269.99 | 3319.55 | 49.56 | 40000 | 0 | 1982400 | 1986798.8384 | Shyampur | Shyampur 33/11KV S/S | 26 | 1913040.7173 | 1822681.1962 | 2162756.7937 | 1853587.4081 | 1927999.1795 | 1824622.7112
1012 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2051.33 | 2091.49 | 40.16 | 40000 | 0 | 1606400 | 1609964.5147 | Shyampur | Shyampur 33/11KV S/S | 26 | 1509467.744 | 1396147.3632 | 1389660.8569 | 915888.0248 | 1677475.7016 | 1601003.2355
1013 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1523.24 | 1561.08 | 37.84 | 40000 | 0 | 1513600 | 1516958.5966 | Shyampur | Shyampur 33/11KV S/S | 26 | 546698.2534 | 888712.2774 | 1726620.7552 | 1517234.7817 | 1359049.2203 | 1887540.7358
1014 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1015 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 864.46 | 891.78 | 27.32 | 40000 | 0 | 1092800 | 1095224.8641 | Shyampur | Shyampur 33/11KV S/S | 26 | 747879.9854 | 273141.8536 | 751986.1559 | 501987.0295 | 565017.3838 | 552636.6613
1016 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1370.29 | 1385.17 | 14.88 | 40000 | 0 | 595200 | 596520.7166 | Shyampur | Shyampur 33/11KV S/S | 26 | 735784.8913 | 764156.3881 | 763138.4929 | 788989.597 | 774228.7961 | 1030332.7456
1017 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3205.07 | 3261.15 | 56.08 | 40000 | 0 | 2243200 | 2248177.5395 | Shyampur | Shyampur 33/11KV S/S | 26 | 2749214.8896 | 3128315.2765 | 2945013.5787 | 2827927.2998 | 2567335.031 | 2104748.1835
1018 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1019 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1121.46 | 1128.58 | 7.12 | 40000 | 0 | 284800 | 285431.9558 | Shyampur | Shyampur 33/11KV S/S | 26 | 272542.7871 | 255119.2973 | 227029.7187 | 174848.8273 | 295251.5179 | 251271.3464
1020 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2055.4 | 2088.29 | 32.89 | 40000 | 0 | 1315600 | 1318519.2453 | Shyampur | Shyampur 33/11KV S/S | 26 | 1539705.4793 | 1292017.0377 | 1541412.3005 | 1200352.7042 | 1365805.0805 | 1428279.2319
1021 | 11 kV Spare Feeder | spare | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1022 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1411.57 | 1435.214 | 23.644 | 40000 | 0 | 945760 | 947858.5903 | Shyampur | Shyampur 33/11KV S/S | 26 | 859154.8511 | 801803.5058 | 808146.1389 | 598969.7492 | 543740.6288 | 732574.1964
1023 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1384.37 | 1414.78 | 30.41 | 40000 | 0 | 1216400 | 1219099.1258 | Shyampur | Shyampur 33/11KV S/S | 26 | 1035743.225 | 446558.8956 | 946355.4589 | 931203.8377 | 1080348.9594 | 971021.4868
1024 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1025 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1026 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1027 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2351.37 | 2381.97 | 30.6 | 40000 | 0 | 1224000 | 1226715.9898 | Shyampur | Shyampur 33/11KV S/S | 26 | 1501001.1782 | 1526310.2699 | 1579250.5869 | 1494594.8892 | 1526560.1151 | 1250345.4555
1028 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 175.82 | 178.05 | 2.23 | 40000 | 0 | 89200 | 89397.93 | Shyampur | Shyampur 33/11KV S/S | 26 | 41123.3199 | 3604.5113 | 82447.6347 | 75834.9927 | 95891.5675 | 84558.6189
1029 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1030 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1256.25 | 1277.88 | 21.63 | 40000 | 0 | 865200 | 867119.832 | Shyampur | Shyampur 33/11KV S/S | 26 | 867218.2472 | 889112.7786 | 908118.8747 | 695610.598 | 869607.7672 | 875642.5706
1031 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3812.96 | 3859.6597 | 46.6997 | 40000 | 0 | 1867988 | 1872132.9644 | Shyampur | Shyampur 33/11KV S/S | 26 | 1624774.3078 | 1797850.1185 | 1620673.5531 | 2160897.1026 | 1905144.5888 | 2092324.8793
1032 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1128.27 | 1132.87 | 4.6 | 40000 | 0 | 184000 | 184408.2861 | Shyampur | Shyampur 33/11KV S/S | 26 | 343903.8423 | 438548.8705 | 532125.7967 | 778413.3204 | 463585.7706 | 590307.3256
1033 | 11/0.4 kV Aux Transformer, T-1 | 0 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1034 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0.415 | DPDC | DHK26108 | 1 | 65260.8 | 65650.1 | 389.3 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1035 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0.415 | 0 | 0 | 1 | 619265 | 625854 | 6589 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1036 | 11/0.4 kV Aux Transformer, T-2 | 0 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0 | 0
1037 | 11 kV Nama shyampur Feeder | 0 | 11 | Shympur | HA-021101066-02 | 1 | 44443826 | 46233188 | 1789362 | 1 | 0 | 1789362 | 1775047.104 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 2124178.3588 | 2141060 | 2242087.5527 | 2142439.5507 | 2098065.1104 | 2051822.5774
1038 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 23612106 | 24282013 | 669907 | 1 | 0 | 669907 | 664547.744 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 735518.3371 | 786111 | 782826.8086 | 745206.3758 | 738065.3088 | 731764.9753
1039 | 11 kV H. R Steel | 0 | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0
1040 | 11 kV Shyampur Incoming (F1) | 0 | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0 | 0
1041 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 528325.7 | 559360.2 | 31034.5 | 60 | 0 | 1862070 | 1847173.44 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1772799.78 | 1740318 | 1920297.8361 | 1596859.747 | 1920766.0882 | 1940683.7189
1042 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 668712.2 | 693053.6 | 24341.4 | 60 | 0 | 1460484 | 1448800.128 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1537289.4923 | 1379322 | 1531676.01 | 1098969.809 | 1475476.6819 | 1381608.0185
1043 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 685766.2 | 708041.4 | 22275.2 | 60 | 0 | 1336512 | 1325819.904 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1436086.1084 | 1338426 | 1403188.8641 | 1231235.1282 | 1429313.0963 | 1378277.4296
1044 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 403627.9 | 421306.3 | 17678.4 | 60 | 0 | 1060704 | 1052218.368 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1093174.4833 | 818646 | 1160551.0823 | 887582.2839 | 954363.7317 | 1019394.7492
1045 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 521552.7 | 540442.3 | 18889.6 | 60 | 0 | 1133376 | 1124308.992 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 208419.6185 | 288 | 3130.962 | 385792.207 | 8184.8678 | 8596.203
1046 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 12323.7 | 51207.4 | 38883.7 | 60 | 0 | 2333022 | 2314357.824 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2668033.8435 | 2872542 | 2819649.0049 | 2794077.3284 | 2700808.4363 | 2561826.8196
1047 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 328026.8 | 350357.3 | 22330.5 | 60 | 0 | 1339830 | 1329111.36 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1432539.3027 | 1270602 | 1528603.9007 | 1237892.1591 | 1229098.1908 | 1284557.7074
1048 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 498710.3 | 518177 | 19466.7 | 60 | 0 | 1168002 | 1158657.984 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1382304.8305 | 530982 | 646002.2013 | 711159.0569 | 480060.5409 | 1215195.8482
1049 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 659724.2 | 694813.1 | 35088.9 | 60 | 0 | 2105334 | 2088491.328 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2541202.6985 | 2715606 | 2647616.7695 | 2636452.1751 | 2526376.4464 | 2465450.8355
1050 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 894406.3 | 907279.3 | 12873 | 60 | 0 | 772380 | 766200.96 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 752054.1743 | 714972 | 785812.6007 | 661368.2767 | 689554.7346 | 725640.3272
1051 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 38811.9 | 70053.1 | 31241.2 | 60 | 0 | 1874472 | 1859476.224 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1837006.5171 | 1401510 | 1411640.1073 | 1301431.6729 | 1235612.3209 | 1199610.0995
1052 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB7380 | 1 | 659160 | 659160 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 43170.716 | 3507 | 3715.5651 | 3553.7906 | 3904.2091 | 3633.5474
1053 | 11 kV Spare | spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0
1054 | 11 kV Khaza Moinuddin | B889Z | 11 | 0 | 00000026 | 1 | 7422622 | 8000660 | 578038 | 1 | 0 | 578038 | 579356.8008 | Fatullah | Nandalalpur 33/11 kV | 89 | 656635.1076 | 680847.6789 | 682477.6462 | 727695.4191 | 676115.2751 | 672821.6526
1055 | 11 kV Chitashal | B489Q | 11 | 0 | 00000027 | 1 | 35456592 | 36082072 | 625480 | 1 | 0 | 625480 | 626907.0404 | Shyampur | Nandalalpur 33/11 kV | 89 | 735704.304 | 743621.9237 | 740092.1663 | 801503.5058 | 725908.576 | 676035.0889
1056 | 11 kV Local Feeder | B489G | 11 | 0 | 00000157 | 1.5 | 19031274 | 19190114 | 158840 | 1 | Estimated | 470836.8 | 471911.02 | Shyampur | Nandalalpur 33/11 kV | 89 | 670610.6986 | 650428.6635 | 670079.927 | 673810.7719 | 652026.96 | 610908.7086
1057 | 11 kV Rasel Germants | 0 | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0
1058 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 | 0 | 00000121 | 1 | 80634160 | 82827040 | 2192880 | 1 | 0 | 2192880 | 2197883.0829 | Matuail | Nandalalpur 33/11 kV | 89 | 2409135.9772 | 2474142.3426 | 2710158.1798 | 2342109.1991 | 2438091.1118 | 2521439.5722
1059 | 11 kV Nandalalpur | B890X | 11 | 0 | 00000010 | 1 | 86136912 | 86980384 | 843472 | 1 | 0 | 843472 | 845396.3918 | Fatullah | Nandalalpur 33/11 kV | 89 | 817827.925 | 726019.9781 | 743459.691 | 869061.7913 | 928548.3765 | 892208.2473
1060 | 11 kV Sharif Bagh | B489SB | 11 | 0 | 00000132 | 1 | 77028008 | 78453808 | 1425800 | 1 | 0 | 1425800 | 1429052.9803 | Shyampur | Nandalalpur 33/11 kV | 89 | 1697558.3187 | 1769871.618 | 1607397.0329 | 1797879.9406 | 1716982.5939 | 1682233.437
1061 | 11 kV Spare | spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0
1062 | 11 KV Nayamati | B890Y | 11 | 0 | 00000158 | 1 | 68472832 | 69477432 | 1004600 | 1 | 0 | 1004600 | 1006892.0073 | Fatullah | Nandalalpur 33/11 kV | 89 | 1138166.5842 | 1094447.1869 | 1160143.2858 | 1059913.8974 | 1145403.0364 | 1037983.1413
1063 | 11 kV Pulpar | B889S | 11 | 0 | 00000160 | 1 | 10315015 | 11257213 | 942198 | 1 | 0 | 942198 | 944347.6364 | Fatullah | Nandalalpur 33/11 kV | 89 | 974125.8442 | 814027.697 | 905763.961 | 653442.1412 | 808373.695 | 916555.6279
1064 | 11 kV Shahi Bazar | B489X | 11 | 0 | 00000170 | 1 | 43318576 | 43910492 | 591916 | 1 | 0 | 591916 | 593266.4637 | Shyampur | Nandalalpur 33/11 kV | 89 | 769069.4058 | 789833.0592 | 884250.6672 | 830388.5657 | 784445.919 | 785444.6114
1065 | 11 kV Pagla Bazar | B890G | 11 | 0 | 00000060 | 1 | 52221152 | 52781312 | 560160 | 1 | 0 | 560160 | 561438.012 | Fatullah | Nandalalpur 33/11 kV | 89 | 651299.1372 | 675946.8632 | 703594.2894 | 679748.7175 | 834561.5067 | 783154.3223
1066 | 11 kV Delpara bazar | B489M | 11 | 0 | 00000063 | 1 | 83841392 | 85270552 | 1429160 | 1 | 0 | 1429160 | 1432420.6462 | Shyampur | Nandalalpur 33/11 kV | 89 | 1512147.634 | 1531851.518 | 1668168.7326 | 1521265.0516 | 1508132.7308 | 1527622.8486
1067 | 11 kV Bhuighor (Board mill) | E289C | 11 | 0 | 00000146 | 1 | 45875048 | 46505368 | 630320 | 1 | 0 | 630320 | 631758.0829 | Matuail | Nandalalpur 33/11 kV | 89 | 736149.3859 | 684221.3852 | 711807.7641 | 702632.7597 | 668462.9794 | 1074021.0416
1068 | 11 kV Spare | 0 | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0 | 0
1069 | 33/0.415 kV, 200 kVA AT-1 | 0 | 11 | 0 | 7803 | 1 | 2600 | 2634 | 34 | 100 | 0 | 3400 | 3407.7571 | Shyampur | Nandalalpur 33/11 kV | 89 | 4811.696 | 5827.1281 | 5909.6952 | 6446.2091 | 6244.3055 | 5725.7228
1070 | 33/0.415 kV, 200 kVA AT-2 | 0 | 11 | 0 | 7805 | 1 | 71.1 | 78.2 | 7.1 | 100 | 0 | 710 | 711.6199 | Shyampur | Nandalalpur 33/11 kV | 89 | 912.2174 | 1004.6773 | 100.1643 | 0 | 0 | 0
1071 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 66131524 | 67083281 | 951757 | 1 | 0 | 951757 | 964969.6559 | Postogola | Postogola 33/11KV S/S | 25 | 1255334.9139 | 1334586.3999 | 1219095.1394 | 1335055.4691 | 1307497.2614 | 1269812.3426
1072 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | XC570270 | 1 | 0 | 594 | 594 | 1000 | Estimated | 1188000 | 1204492.2718 | Jurain | Postogola 33/11KV S/S | 25 | 1239052.6971 | 1255387.5265 | 1323367.1334 | 1374189.6942 | 1360936.1962 | 1367079.5822
1073 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 25644920 | 26047328 | 402408 | 1 | 0 | 402408 | 407994.3823 | Jurain | Postogola 33/11KV S/S | 25 | 537163.6113 | 519931.6597 | 537056.744 | 474949.556 | 542387.1952 | 435813.5436
1074 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 79011228 | 80275699 | 1264471 | 1 | 0 | 1264471 | 1282024.8716 | Postogola | Postogola 33/11KV S/S | 25 | 1532425.7761 | 1609308.7492 | 1557430.4575 | 1587221.6201 | 1546887.4107 | 1509702.7057
1075 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 461916 | 471377.73 | 9461.73 | 60 | 0 | 567703.8 | 575584.882 | Postogola | Postogola 33/11KV S/S | 25 | 676389.0131 | 678803.9555 | 662617.3772 | 636891.4703 | 664686.4068 | 678488.3278
1076 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 925873.2 | 941864.1 | 15990.9 | 60 | 0 | 959454 | 972773.5086 | Postogola | Postogola 33/11KV S/S | 25 | 1191302.5568 | 1270287.67 | 1139734.1436 | 1267305.3443 | 1258808.5211 | 1186933.4512
1077 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 814922.6 | 831587.6 | 16665 | 60 | 0 | 999900 | 1013780.9955 | Postogola | Postogola 33/11KV S/S | 25 | 1266750.2722 | 1384014.8487 | 1419724.1658 | 1247409.4401 | 1227619.0196 | 1164704.2052
1078 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 526393.2 | 528585.6 | 2192.4 | 60 | 0 | 131544 | 133370.1443 | Postogola | Postogola 33/11KV S/S | 25 | 125848.0606 | 126732.5803 | 134717.5169 | 129509.8262 | 124992.5587 | 126222.4118
1079 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 905082.3 | 927947.6 | 22865.3 | 60 | 0 | 1371918 | 1390963.4921 | Postogola | Postogola 33/11KV S/S | 25 | 1427602.3077 | 1330189.3065 | 1373424.2339 | 1052907.1287 | 1323292.4846 | 1331811.5849
1080 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 445618.9 | 469020.9 | 23402 | 60 | 0 | 1404120 | 1423612.5326 | Jurain | Postogola 33/11KV S/S | 25 | 2449336.9799 | 2475377.6895 | 2446524.7479 | 2443876.2234 | 2429557.5202 | 2393972.4885
1081 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 45310492 | 47773398 | 2462906 | 1 | 0 | 2462906 | 2497097.0061 | Jurain | Postogola 33/11KV S/S | 25 | 2454381.4966 | 2115704.7964 | 2221056.7969 | 2061497.5542 | 2071894.6482 | 1933992.5359
1082 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 15592.1 | 17714.8 | 2122.7 | 1000 | 0 | 2122700 | 2152168.1359 | Jurain | Postogola 33/11KV S/S | 25 | 2435670.3328 | 2485795.0121 | 2477072.4328 | 2360182.711 | 2388027.6504 | 2351667.7366
1083 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 60970541 | 62312639 | 1342098 | 1 | 0 | 1342098 | 1360729.5194 | Postogola | Postogola 33/11KV S/S | 25 | 1622380.5518 | 1682719.5891 | 1655098.2 | 1632466.5583 | 1639249.0712 | 1571920.5306
1084 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | DHK09113 | 1 | 0 | 53.1 | 53.1 | 1000 | Estimated | 106200 | 107674.3091 | Postogola | Postogola 33/11KV S/S | 25 | 247810.5394 | 239121.4336 | 245164.3984 | 245637.4316 | 262708.1006 | 303872.8913
1085 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 11 | 0 | ELIB67385 | 1 | 539.63 | 585.41 | 45.78 | 80 | 0 | 3662.4 | 3713.2428 | Postogola | Postogola 33/11KV S/S | 25 | 4606.8906 | 4570.7831 | 4670.5121 | 4307.9725 | 5751.9551 | 4375.6621
1086 | 11 kV Feeder-1 | 0 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0
1087 | 11 kV Feeder-2 | 0 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0
1088 | 11 kV Dholaikal RMU | A619R | 11 | 0 | DHK60970 | 1 | 325962.4 | 354107.8 | 28145.4 | 60 | 0 | 1688724 | 1688724 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1912589.3597 | 2044107.1526 | 2258178.5414 | 2013206.2605 | 1942348.072 | 1890634.7965
1089 | 11 kV Alom Gonj | A581A | 11 | 0 | DHK60894 | 1 | 511135.3 | 520758.3 | 9623 | 60 | 0 | 577380 | 577380 | Postogola | IG Gate GIS 33/11 kV | 87 | 601965.5066 | 622652.7534 | 676806.1857 | 596654.2301 | 589855.3321 | 589628.102
1090 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 | 0 | DHK60895 | 1 | 625193.4 | 650759.1 | 25565.7 | 60 | 0 | 1533942 | 1533942 | Postogola | IG Gate GIS 33/11 kV | 87 | 1585262.0566 | 1935090.8799 | 1875565.0903 | 1850628.0181 | 1792355.2732 | 1711977.4089
1091 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 | 0 | DHK68133 | 1 | 3683.69 | 3711.29 | 27.6 | 60000 | 0 | 1656000 | 1656000 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1845366.1756 | 1846529.6992 | 2047321.2801 | 1803939.5949 | 1748762.5817 | 1815572.1775
1092 | 11 kV Doyaganj | B587Y | 11 | 0 | DHK68134 | 1 | 2463.08 | 2488.28 | 25.2 | 60000 | 0 | 1512000 | 1512000 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1596436.5035 | 1387958.4974 | 1645033.4081 | 1687142.9696 | 1819772.2117 | 1955417.8504
1093 | 11 kV Faridabad | A587F | 11 | 0 | DHK68140 | 1 | 838.74 | 857.46 | 18.72 | 60000 | 0 | 1123200 | 1123200 | Postogola | IG Gate GIS 33/11 kV | 87 | 1253169.1806 | 1329183.0163 | 1411966.4378 | 1296128.1808 | 1292615.9757 | 1233789.9626
1094 | 11 kV Gandaria | A524D | 11 | 0 | DHK60969 | 1 | 473557.9 | 503196.3 | 29638.4 | 60 | 0 | 1778304 | 1778304 | Postogola | IG Gate GIS 33/11 kV | 87 | 1938857.8307 | 2106445.8973 | 2096887.3731 | 2186472.7241 | 2176408.4497 | 2008723.2675
1095 | 11 kV Walter Road | A687W | 11 | 0 | DHK68136 | 1 | 1054.29 | 1075.44 | 21.15 | 60000 | 0 | 1269000 | 1269000 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1348724.0914 | 2063264.286 | 1501529.2301 | 1391040.5522 | 1437042.3417 | 1402694.4766
1096 | 11 kV Murgitola Feeder (F-11) | B587G | 11 | 0 | DHK68138 | 1 | 4009.01 | 4043.16 | 34.15 | 60000 | 0 | 2049000 | 2049000 | Swamibag | IG Gate GIS 33/11 kV | 87 | 2352354.9699 | 2412855.9498 | 2416392.1157 | 2307519.2472 | 2337901.7997 | 2438521.0841
1097 | 11 kV Feeder-12 | 0 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0 | 0
1098 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 | 0 | DHK60899 | 1 | 752453.5 | 777965.1 | 25511.6 | 60 | 0 | 1530696 | 1530696 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1678266.8077 | 1754827.7038 | 1727816.5375 | 1778252.8009 | 1741101.9665 | 1809148.9629
1099 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 | 0 | DHK60967 | 1 | 214602.5 | 228309.7 | 13707.2 | 60 | 0 | 822432 | 822432 | Postogola | IG Gate GIS 33/11 kV | 87 | 935068.7084 | 1005323.9927 | 1010280.3195 | 1031522.1618 | 1006862.3928 | 984580.1304
1100 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB2774 | 1 | 284380 | 285932 | 1552 | 1 | 0 | 1552 | 1552 | Postogola | IG Gate GIS 33/11 kV | 87 | 1538.8094 | 3608.1717 | 0 | 1665.5005 | 1667.9239 | 1718.3058
1101 | Nizambag | F1114Z | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 233456.58 | 234080.9166 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1217190.9472 | 1180785.7325 | 1158100.6579 | 1095738.2283 | 1008260.1492 | 972380.6635
1102 | Merry Stopes | F1114P | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 54930.96 | 55077.8627 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 304297.7368 | 318812.1478 | 329144.3975 | 365246.0761 | 355856.5232 | 364642.7488
1103 | Mujibur Ghat | F1114V | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 274654.8 | 275389.3137 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1278050.4946 | 1298864.3057 | 1340958.6566 | 1217486.9203 | 1304807.2519 | 1337023.4124
1104 | Madrasa | F1114U | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 329585.76 | 330467.1764 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1582348.2314 | 1653100.0255 | 1462863.989 | 1424459.6968 | 1542044.934 | 1701666.1612
1105 | Thana | F1114Q | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 247189.32 | 247850.3823 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1217190.9472 | 1298864.3057 | 1219053.3241 | 1217486.9203 | 1423426.093 | 1337023.4124
1106 | Al-Hera | 0 | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0
1107 | Waz Uddin School | F1114W | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 192258.36 | 192772.5196 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 852033.6631 | 1003667.8726 | 975242.6593 | 730492.1522 | 830331.8876 | 972380.6635
1108 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0 | 0
1109 | Bashundhara City | 0 | 33 | 0 | 660434 | 1 | 803.19 | 814.02 | 10.83 | 180000 | 0 | 1949400 | 1952470.6666 | Shere b.nagar | Moghbazar 132/33/11KV S/S |  | 2191476.9852 | 2303155.9363 | 2253160.9458 | 2286948.2926 | 2480389.347 | 2161081.9864
1110 | 33 kV Apollo Ispat Feeder | 0 | 33 | DPDC | 7389486 | 1 | 4592.74 | 4616.75 | 24.01 | 240000 | 0 | 5762400 | 5757883.9148 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 5345006.6439 | 5626849.4493 | 4868511.8333 | 6352475.5818 | 7317548.4229 | 5615154.9463
1111 | 33 kV Adamjee EPZ Feeder | 0 | 33 | DPDC | ABB03919 | 1 | 375764.6 | 380367.7 | 4603.1 | 2000 | 0 | 9206200 | 9198984.9536 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 9835003.2885 | 9088565.8308 | 9139513.6232 | 7905743.5896 | 8068621.1441 | 8850787.3005
1112 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1019.06 | 1022.36 | 3.3 | 240000 | 0 | 792000 | 792000 | Siddirgonj | Demra 33/11KV S/S | 16 | 799200 | 616800 | 492000 | 571200 | 446400 | 0
1113 | 33 kV ACI Pharmacuticles Feeder | 0 | 33 | 0 | DHKC4791 | 1 | 943.24 | 960.83 | 17.59 | 90000 | 0 | 1583100 | 1583100 | N.Gonj (East) | Khanpur 33/11KV S/S |  | 1440900 | 1206900 | 1225800 | 1291500 | 1045800 | 0
1114 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC | 0 | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 7200 | 7215.4751 | Matuail | Matuail 132/33 KV S/S | 41 | 8160.0632 | 8383.4623 | 9119.9454 | 10440.0638 | 10260.3419 | 10991.7418
1115 | 33 KV Shah Cement Feeder (F2) | 0 | 33 | DPDC | H/A030800181-03 | 1 | 41084.427 | 41084.427 | 0 | 1000 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 108.9746 | 64646.4953 | 944204.0986 | 2494536.8881 | 923421.8011 | 1229303.7954
1116 | 33/0.415 KV Transformer AT-1 | 0 | 0.415 | DPDC | 2001123043108 | 1 | 6559.9 | 6583.1 | 23.2 | 160 | 0 | 3712 | 3710.9239 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 639.8509 | 0 | 0 | 0 | 0 | 0
1117 | 33/0.415 KV Transformer AT-2 | 0 | 0.415 | DPDC | 2001123043171 | 1 | 4786.1 | 4786.1 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 3647.1499 | 6180.7322 | 7797.005 | 4755.5609 | 4035.644 | 2848.7249
1118 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 0 | 33 | Main | 041808902866 | 1 | 361.28 | 375.17 | 13.89 | 360000 | 0 | 5000400 | 5005228.5182 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 6404881.1253 | 5779395.3475 | 7171154.3348 | 6850018.059 | 6815752.3123 | 6616060.3155
1119 | 33 kV Delta Agro Premier Cement (=H2) | 0 | 33 | Main | 041808902876 | 1 | 122.98 | 130.36 | 7.38 | 360000 | 0 | 2656800 | 2659365.4762 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 2937522.8571 | 2682130.383 | 2390384.7783 | 2530901.4092 | 2430058.343 | 2458012.5886
1120 | 33 kV Outgoing Feeder-3 (=H3) | 0 | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
1121 | 33 kV Outgoing Feeder-4 (=H4) | 0 | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
1122 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 400185.2656 | 1006790.1928 | 1108090.8439
1123 | 33 kV Outgoing Feeder-6 (=H12) | 0 | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
1124 | 33 kV Outgoing Feeder-7 (=H13) | 0 | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0 | 0
1125 | 33 kV Shah Cement VRM (=H14) | 0 | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 2277825.3993 | 11858183.3118 | 9272761.2883 | 10712537.375 | 10817421.0397
1126 | 11 KV Shahidbagh Feeder | 0 | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 406104 | 407049.5473 | Rajarbag | Santinagar Switching S/S |  | 492002.3987 | 599477.6789 | 597504.11 | 524779.3911 | 36416.7693 | -3994.0825
1127 | 11 Fortune(MogBazar)-new | 0 | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 104616 | 104859.5814 | Moghbazar | Santinagar Switching S/S |  | 122203.1256 | 123551.4515 | 107474.29 | 138756.0658 | 127666.1608 | 126229.899
1128 | Centerpoint-Kakrail | 0 | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 63600 | 63748.0823 | Kakrail | Santinagar Switching S/S |  | 61390.4591 | 62067.8095 | 43848 | 71600.1051 | 81766.8748 | 80846.9863
1129 | 11 KV Shyamoli O/H | 0 | 11 | 0 | DHK-15026 | 1 | 9219.86 | 9229.09 | 9.23 | 40000 | 0 | 369200 | 378430 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 520290 | 602290 | 545300 | 584660 | 530950
1130 | 11 KV Nearest RMU | 0 | 11 | 0 | DHK-15027 | 1 | 3875.73 | 3878 | 2.27 | 40000 | 0 | 90800 | 93070 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 157030 | 160310 | 164820 | 182450 | 165230
1131 | 11 KV Sher-e-bangla Nagar | 0 | 11 | 0 | DHK-15025 | 1 | 3980.52 | 3984.04 | 3.52 | 40000 | 0 | 140800 | 144320 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 33620 | 51660 | 44280 | 49610 | 45920
1132 | Export to DESCO | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 0 | 0 | 0 | 0 | -13837.5
1133 | 33/0.4 kV, 500 kVA AT-1 | 0 | 0.4 | 0 | 84.2659 | 1 | 323466 | 325367 | 1901 | 10 | 0 | 19010 | 19032.3858 | Paribag | Dhanmondi 33/11KV S/S |  | 23956.6474 | 23982.7488 | 25078.0786 | 24914.239 | 24707.6715
1134 | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0.4 | 0 | 84.2673 | 1 | 478776 | 478776 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S |  | 0 | 875.2094 | 10.0032 | 0 | 0
1135 | 33 KV Japan Genden City | 0 | 33 | 0 | DHK15681 | 1 | 687.9 | 750.68 | 62.78 | 18000 | 0 | 1130040 | 1130040 | Adabor | Japan Garden 33/11 KV |  | 1459800 | 1502640 | 1451700 | 1519200 | 1531620
1136 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKE6223 | 1 | 43619.2 | 43796.79 | 177.59 | 120 | 0 | 21310.8 | 21708.6097 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 23301.1673 | 23194.682 | 23415.1565 | 24412.3409 | 25361.4506
1137 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 0 | 0 | 0 | 0 | 0
1138 | AT-1 | 0 | 0.415 | 0 | 0 | 1 | 950.84 | 1021.24 | 70.4 | 80 | 0 | 5632 | 5672.1022 | Mugdapara | Madarteck 33/11KV S/S |  | 12954.5544 | 10606.4337 | 12573.2122 | 11708.7885 | 9611.7345
1139 | AT-2 | 0 | 0.415 | 0 | 63394003 | 1 | 475.19 | 549.25 | 74.06 | 80 | 0 | 5924.8 | 5966.9871 | Mugdapara | Madarteck 33/11KV S/S |  | 6056.6539 | 7745.9106 | 5649.4556 | 6156.9427 | 5477.3433
1140 | 33 kV Shahriar Steel Feeder | 0 | 33 | Main | 41812909534 | 1 | 633.58 | 652.26 | 18.68 | 360000 | 0 | 6724800 | 6734848.5186 | Kazla | Kazla 132/133 KV SS |  | 7150980.086 | 7435235.4244 | 7833434.8553 | 7323524.0635 | 7145780.8426
1141 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 721.82 | 751.24 | 29.42 | 360000 | 0 | 10591200 | 10607025.8788 | Kazla | Kazla 132/133 KV SS |  | 11059032.0485 | 10618692.0573 | 11070629.7471 | 10019388.2364 | 9121125.0936
1142 | 33kV Water Treatment Plant | 0 | 33 | Digital | 80379618 | 1 | 21815 | 22050 | 235 | 2000 | 0 | 470000 | 468459.6796 | Maniknagar | Maniknagar 132/33 KV SS |  | 526937.9846 | 686173.136 | 531621.6224 | 605078.9898 | 1062218.4705
1143 | Axuxilary -1 | 0 | 0.415 | 0 | AH14044078 | 1 | 420573.6 | 424443.4 | 3869.8 | 1 | 0 | 3869.8 | 3860.1372 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 5837.95 | 5955.9261 | 5213.2044 | 5831.4157 | 6475.0369
1144 | Axuxilary -2 | 0 | 0.415 | 0 | AH14044072 | 1 | 388432.8 | 392725.7 | 4292.9 | 1 | 0 | 4292.9 | 4282.1807 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 4943.482 | 4558.0495 | 4382.3431 | 5377.7142 | 4841.9103
1145 | 33 kV Rani RRM Feeder | 0 | 33 | Export | BD001809 | 1 | 760.393 | 772.98 | 12.587 | 240000 | 0 | 3020880 | 3021325.4164 | Shyampur | Shyampur 132/33KV S/S |  | 2543674.3806 | 3093749.2487 | 2731257.9254 | 2448780.2928 | 2460914.9302
1146 | 33 kV Rahima Steel feeder | 0 | 33 | Export | BD001803 | 1 | 656.416 | 665.824 | 9.408 | 240000 | 0 | 2257920 | 2258252.921 | Shyampur | Shyampur 132/33KV S/S |  | 387957.1282 | 1848762.9304 | 2408497.5549 | 1851141.9981 | 2281164.2763
1147 | 33 kV Salam Steel Feeder | 0 | 33 | Export | BD001849 | 1 | 1251.608 | 1293.7049 | 42.0969 | 240000 | 0 | 10103256 | 10104745.6836 | Shyampur | Shyampur 132/33KV S/S |  | 9425654.7552 | 6942639.1851 | 9555598.3573 | 9761265.4061 | 10754060.1599
1148 | 33 kV Steel Famus feeder | 0 | 33 | Export | BD001806 | 1 | 153.6104 | 161.8755 | 8.2651 | 240000 | 0 | 1983624 | 1983916.4772 | Shyampur | Shyampur 132/33KV S/S |  | 1855188.4343 | 668060.7526 | 1802076.7353 | 1343089.4196 | 1442423.9509
1149 | 33 kV Rani Kamal Steel Feeder | 0 | 33 | Export | BD001829 | 1 | 1593.2569 | 1618.8289 | 25.572 | 240000 | 0 | 6137280 | 6138184.9168 | Shyampur | Shyampur 132/33KV S/S |  | 5684015.7878 | 6636959.5785 | 7405918.76 | 5422228.9014 | 6501978.5941
1150 | 33 kV Chakda Steel Feeder | 0 | 33 | Export | BD001832 | 1 | 2477.8933 | 2517.3479 | 39.4546 | 240000 | 0 | 9469104 | 9470500.1805 | Shyampur | Shyampur 132/33KV S/S |  | 8724428.8439 | 9042995.7002 | 9230581.7605 | 8256580.7385 | 8640663.1605
1151 | 33 kV Akhter Steel Feeder | 0 | 33 | Export | BD001828 | 1 | 690.9784 | 691.8555 | 0.8771 | 240000 | Prime Textile | 210504 | 210535.038 | Fatullah | Shyampur 132/33KV S/S |  | 1073036.1535 | 1039008.3182 | 1167285.0702 | 1147950.5517 | 674551.2513
1152 | Aux Tr-1 | 0 | 0.44kv | Export | DHKG9742 | 1.025 | 349.667 | 351.425 | 1.758 | 2400 | 0 | 4324.68 | 4324.68 | Fatullah | Shyampur 132/33KV S/S |  | 5222.58 | 5052.84 | 5102.04 | 5527.62 | 10071.24
1153 | Aux Tr-2 | 0 | 0.44kv | Export | DHKG9743 | 1.025 | 117.946 | 124.447 | 6.501 | 2400 | 0 | 15992.46 | 15992.46 | Fatullah | Shyampur 132/33KV S/S |  | 19576.68 | 17894.04 | 18044.1 | 19434 | 11042.94
1154 | 132 kV MI Cement Feeder [MICFL] | 0 | 132 | P. Cell | 08993599 | 1 | 350.233 | 375.928 | 25.695 | 480000 |  | 12340320 | 12340320 | Sytalakhya | MI CEMENT 132/33 kV |  | 12087360 | 11905920 | 10329120 | 10749120 | 9239520
1155 | 33 kV Shah Cement Feeder | 0 | 33 | 0 | 8993 841 | 1 | 39516.99 | 39602.522 | 85.532 | 36000 | 0 | 3079152 | 3079152 | Sytalakhya | Madonganj 132/33 KV SS |  | 1948464 | 817416 | 2360592 | 3210156 | 3227092
1156 | 33 kV Mondol Para (Premire cement) Feeder | 0 | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS |  | 0 | 0 | 0 | 0 | 0
1157 | 11 kV Rayer Bazar Feeder | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 784728 | 789619.7227 | Dhanmondi | Jigatola Switching |  | 0 | 0 | 0 | 679467.069
1158 | 11 kV Madina Masjid Feeder | 0 | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1216328.4 | 1223910.5702 | Jigatola | Jigatola Switching |  | 1463157.2985 | 1648779.5998 | 1579031.3193 | 1587392.6308
1159 | 11 kV Mitali | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1094343.6 | 1101165.3592 | Jigatola | Jigatola Switching |  | 1474997.974 | 1417602.7084 | 1504281.4171 | 1520651.6572
1160 | 132 kV Shah Cement | 0 | 132 | EXPORT | 042003953369 | 1 | 21.5 | 33.07 | 11.57 | 1200000 |  | 13884000 | 13884000 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 15096000 | 10668000
1161 | 132 KV Metro Rail -1 | 0 | 132 | 0 | 42627805 | 1 | 0.006 | 0.239 | 0.233 | 480000 | 0 | 111840 | 111840 | Motijheel | Maniknagar 132/33 S/S
1162 | 132 KV Metro Rail -2 | 0 | 132 | 0 | 42627793 | 1 | 0.002 | 2.303 | 2.301 | 480000 | 0 | 1104480 | 1104480 | Motijheel | Maniknagar 132/33 S/S
1163 | Import from Matuail | [10 empty] | 595068 | 595068 | Jurain | Kazla 33/11KV S/S
1164 | Export to Jurain | [10 empty] | -595068 | -595068 | Matuail | Kazla 33/11KV S/S

## SS List
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2305.89 | 2324.72 | 18.83 | 720000 | 13557600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2274.38 | 2292.58 | 18.2 | 720000 | 13104000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2024.16 | 2046.44 | 22.28 | 720000 | 16041600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1886.38 | 1909.93 | 23.55 | 480000 | 11304000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2170.41 | 2191.32 | 20.91 | 240000 | 0 | 5018400 | 5024309.5707 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2475.1 | 2497.75 | 22.65 | 240000 | 0 | 5436000 | 5442401.3284 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1512.88 | 1527.47 | 14.59 | 240000 | 0 | 3501600 | 3505723.4164 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 890.27 | 900.82 | 10.55 | 240000 | 0 | 2532000 | 2534981.6342 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1890.5 | 1904.37 | 13.87 | 240000 | 0 | 3328800 | 3332719.9304 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1236.03 | 1246.56 | 10.53 | 240000 | 0 | 2527200 | 2530175.9818 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.44 | 0.01 | 240000 | 0 | 2400 | 2402.8262 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 446.7 | 464.63 | 17.93 | 240000 | 0 | 4303200 | 4308267.365 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2172.52 | 2193.69 | 21.17 | 240000 | 0 | 5080800 | 5086783.0517 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1676.76 | 1696.22 | 19.46 | 240000 | 0 | 4670400 | 4675899.7726 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 755.4 | 766.57 | 11.17 | 240000 | 0 | 2680800 | 2683956.8582 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2057.42 | 2072.37 | 14.95 | 240000 | 0 | 3588000 | 3592225.1593 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1867.53 | 1885.43 | 17.9 | 240000 | 0 | 4296000 | 4301058.8864 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 170.67 | 175.9 | 5.23 | 240000 | 0 | 1255200 | 1256678.0992 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1502.1 | 1526.05 | 23.95 | 240000 | 0 | 5748000 | 5754768.7335 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.12.2023 | Reading at 00.00hr 01.12.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2305.89 | 2324.72 | 18.83 | 720000 | 13557600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2274.38 | 2292.58 | 18.2 | 720000 | 13104000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 2024.16 | 2046.44 | 22.28 | 720000 | 16041600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1886.38 | 1909.93 | 23.55 | 480000 | 11304000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2170.41 | 2191.32 | 20.91 | 240000 | 0 | 5018400 | 5024309.5707 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2475.1 | 2497.75 | 22.65 | 240000 | 0 | 5436000 | 5442401.3284 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1512.88 | 1527.47 | 14.59 | 240000 | 0 | 3501600 | 3505723.4164 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 890.27 | 900.82 | 10.55 | 240000 | 0 | 2532000 | 2534981.6342 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1890.5 | 1904.37 | 13.87 | 240000 | 0 | 3328800 | 3332719.9304 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1236.03 | 1246.56 | 10.53 | 240000 | 0 | 2527200 | 2530175.9818 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.44 | 0.01 | 240000 | 0 | 2400 | 2402.8262 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 446.7 | 464.63 | 17.93 | 240000 | 0 | 4303200 | 4308267.365 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2172.52 | 2193.69 | 21.17 | 240000 | 0 | 5080800 | 5086783.0517 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1676.76 | 1696.22 | 19.46 | 240000 | 0 | 4670400 | 4675899.7726 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 755.4 | 766.57 | 11.17 | 240000 | 0 | 2680800 | 2683956.8582 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2057.42 | 2072.37 | 14.95 | 240000 | 0 | 3588000 | 3592225.1593 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1867.53 | 1885.43 | 17.9 | 240000 | 0 | 4296000 | 4301058.8864 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 170.67 | 175.9 | 5.23 | 240000 | 0 | 1255200 | 1256678.0992 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1502.1 | 1526.05 | 23.95 | 240000 | 0 | 5748000 | 5754768.7335 | 0 | Dhanmondi 132/33/11KV S/S