## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month October-2023 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 532 | 1 | 960000 | 2227.617 | 2229.915 | 2.298 |  | 2206080 | 1950.36 | 1950.526 | 0.166 |  | 159360 | 1725120 | -1577280 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 666.689 | 667.19 | 0.501 | 480960 |  | 377.027 | 378.836 | 1.809 | 1736640 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 349.978 | 378.796 | 28.818 |  | 27665280 | 156.25 | 169.543 | 13.293 |  | 12761280 | 27665280 | 12761280 | 0.91 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 150.919 | 159.248 | 8.329 |  | 7995840 | 51.409 | 53.833 | 2.424 |  | 2327040 | 7995840 | 2327040 | 0.96 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Exp | PN-1711A04601 | 1 | 960000 | 363.871 | 363.871 | 0 |  | 0 | 211.998 | 211.998 | 0 |  | 0 | 0 | 0 |  |  | 0
|  |  | 132 | Imp |  |  | 960000 | 5.419 | 5.419 | 0 | 0 |  | 4.069 | 4.069 | 0 | 0 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 480960 | 37867200 |  |  | Total=> | 1736640 | 15247680 | 37386240 | 13511040 | 0.94 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 8993 624 | 1 | 960000 | 4836.3 | 4864.387 | 28.087 |  | 26963520 | 2393.979 | 2401.046 | 7.067 |  | 6784320 | 26886720 | 6749760 | 0.97 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 11.003 | 11.083 | 0.08 | 76800 |  | 7.78 | 7.816 | 0.036 | 34560 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 76800 | 26963520 |  |  | Total=> | 34560 | 6784320 | 26886720 | 6749760 | 0.97 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 8993 518 | 1 | 960000 | 1155.737 | 1173.431 | 17.694 |  | 16986240 | 775.383 | 781.529 | 6.146 |  | 5900160 | 16943040 | 5870400 | 0.94 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 70.056 | 70.101 | 0.045 | 43200 |  | 141.151 | 141.182 | 0.031 | 29760 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 333.082 | 350.838 | 17.756 |  | 17045760 | 129.782 | 136.132 | 6.35 |  | 6096000 | 17000640 | 6091200 | 0.94 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.361 | 4.408 | 0.047 | 45120 |  | 30.494 | 30.499 | 0.005 | 4800
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 88320 | 34032000 |  |  | Total=> | 34560 | 11996160 | 33943680 | 11961600 | 0.94
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 2905.949 | 2948.743 | 42.794 |  | 20541120 | 1181.312 | 1197.064 | 15.752 |  | 7560960 | 20541120 | 7560960 | 0.94 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8501.42 | 8541.707 | 40.287 |  | 19337760 | 4976.81 | 4996.746 | 19.936 |  | 9569280 | 19337760 | 9569280 | 0.9 | 0 | 0
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8454.115 | 8494.043 | 39.928 |  | 19165440 | 4936.523 | 4956.296 | 19.773 |  | 9491040 | 19165440 | 9491040 | 0.9 | 0 | 0
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 325.051 | 350.233 | 25.182 |  | 12087360 | 62.036 | 66.568 | 4.532 |  | 2175360 | 12087360 | 2175360 | 0.98 | 0 | 0
[10 empty] | Total=> | 0 | 71131680 |  |  | Total=> | 0 | 28796640 | 71131680 | 28796640 | 0.93
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 8993 683 | 1 | 960000 | 8412.164 | 8449.443 | 37.279 |  | 35787840 | 4681.784 | 4698.185 | 16.401 |  | 15744960 | 35787840 | 15744960 | 0.92 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 8993 682 | 1 | 960000 | 8402.119 | 8439.078 | 36.959 |  | 35480640 | 4676.378 | 4692.679 | 16.301 |  | 15648960 | 35480640 | 15648960 | 0.91 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 8993 681 | 1 | 1440000 | 2689.328 | 2714.49 | 25.162 |  | 36233280 | 1382.643 | 1387.291 | 4.648 |  | 6693120 | 36233280 | 6693120 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 9.184 | 9.184 | 0 | 0 |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 8993 680 | 1 | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 22.279 | 22.279 | 0 | 0 |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 8993 555 | 1 | 1440000 | 2837.573 | 2867.349 | 29.776 |  | 42877440 | 1320.895 | 1333.673 | 12.778 |  | 18400320 | 42877440 | 18400320 | 0.92 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 771.699 | 771.699 | 0 | 0 |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 0 | 150379200 |  |  | Total=> | 0 | 56487360 | 150379200 | 56487360 | 0.94 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993 631 | 1 | 960000 | 5884.59 | 5922.51 | 37.92 |  | 36403200 | 3000.836 | 3017.843 | 17.007 |  | 16326720 | 36403200 | 16326720 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993 659 | 1 | 960000 | 5013.741 | 5042.863 | 29.122 |  | 27957120 | 2545.716 | 2558.736 | 13.02 |  | 12499200 | 27957120 | 12499200 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4427.865 | 4438.485 | 10.62 |  | 10195200 | 1772.548 | 1773.32 | 0.772 |  | 741120 | 10195200 | 741120 | 1 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.561 | 1.561 | 0 | 0 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993 660 | 1 | 960000 | 4111.695 | 4121.721 | 10.026 |  | 9624960 | 1636.054 | 1637.224 | 1.17 |  | 1123200 | 9624960 | 1123200 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.33 | 1.33 | 0 | 0 |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 5014 6667 | 1 | 960000 | 1842.02 | 1867.274 | 25.254 |  | 24243840 | 676.022 | 686.153 | 10.131 |  | 9725760 | 24243840 | 9725760 | 0.93 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 5014 6668 | AMR | 960000 | 1635.972 | 1661.144 | 25.172 |  | 24165120 | 701.249 | 711.371 | 10.122 |  | 9717120 | 24165120 | 9717120 | 0.93 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 4262 7810 | 1 | 960000 | 192.576 | 201.909 | 9.333 |  | 8959680 | 3.49 | 3.49 | 0 |  | 0 | 8959680 | 0 | 0 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 63.03 | 67.85 | 4.82 | 4627200 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 4262 7812 | 1 | 960000 | 194.305 | 203.94 | 9.635 |  | 9249600 | 2.445 | 2.463 | 0.018 |  | 17280 | 9249600 | 17280 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 66.978 | 72.042 | 5.064 | 4861440
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 0 | 150798720 |  |  | Total=> | 9488640 | 50150400 | 150798720 | 40661760 | 0.97 |  | 0
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3273.275 | 3318.886 | 45.611 |  | 87573120 | 1647.259 | 1665.595 | 18.336 |  | 35205120 | 87573120 | 35205120 | 0.93 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3265.408 | 3311.084 | 45.676 |  | 87697920 | 1644.291 | 1662.662 | 18.371 |  | 35272320 | 87697920 | 35272320 | 0.93 | 0 | 0
[10 empty] | Total=> |  | 175271040 |  |  | Total=> | 0 | 70477440 | 175271040 | 70477440 | 0.93
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1511.889 | 1553.392 | 41.503 |  | 79685760 | 734.941 | 755.156 | 20.215 |  | 38812800 | 79685760 | 38812800 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1602.462 | 1643.73 | 41.268 |  | 79234560 | 774.967 | 795.209 | 20.242 |  | 38864640 | 79234560 | 38864640 | 0.94 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 158920320 |  |  | Total=> | 0 | 77677440 | 158920320 | 77677440 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 956.211 | 991.183 | 34.972 |  | 50359680 | 203.395 | 209.048 | 5.653 |  | 8140320 | 50359680 | 8056800 | 0.99 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.021 | 0 | 0 |  | 0.836 | 0.894 | 0.058 | 83520
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 681.016 | 718.358 | 37.342 |  | 53772480 | 286.051 | 304.05 | 17.999 |  | 25918560 | 53772480 | 25909920 | 0.9 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.831 | 0.837 | 0.006 | 8640 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 0 | 104132160 |  |  | Total=> | 92160 | 34058880 | 104132160 | 33966720 | 0.95
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 283.871 | 296.146 | 12.275 |  | 11784000 | 73.16 | 75.817 | 2.657 |  | 2550720 | 11784000 | 2550720 | 0.98 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 202.657 | 220.999 | 18.342 |  | 17608320 | 46.224 | 50.718 | 4.494 |  | 4314240 | 17608320 | 4314240 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 32.492 | 33.497 | 1.005 |  | 964800 | 16.215 | 16.216 | 0.001 |  | 960 | 964800 | 960
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 33.196 | 66.461 | 33.265 | 31934400 |  | 25.752 | 57.754 | 32.002 | 30721920
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[10 empty] | Total=> | 31934400 | 30357120 |  |  | Total=> | 30721920 | 6865920 | -1577280 | -23856000 | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 32580480 | 939852960 |  |  |  | 42108480 | 358542240
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 907272480 |  |  |  |  | 316433760 | 907272480 | 316433760 | 0.94 |  | 0 |  | 0.94422
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 907272480 |  | 316433760 |  | 0.94 | 0
[8 empty] | PDB Unit |  | 907272480 |  | KWH
[8 empty] | PGCB Unit |  | 907272480 |  | KWH
33 KV LEVEL | [10 empty] | Month October-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  |  | 0
| Shah Cement | Madangonj Grid | 33 | Exp | 8993 841 | 1 | 18000 | 29344.892 | 29344.892 | 0 |  | 0 | 7711.314 | 7711.314 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Shah Cement |  | 33 | Exp | 8993 841 | 1 | 36000 | 39462.866 | 39516.99 | 54.124 |  | 1948464 | 10420.789 | 10433.048 | 12.259 |  | 441324 | 1948464 | 441324 | 0.9753 | 0 | 0 | 1551
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 1948464 |  |  | Total=> | 0 | 441324 | 1948464 | 441324 | 0.9753 |  |  | 1551
6 | Jigatala (JP garden) | Kallyanpur | 33 | Exp | 8993834 (old) | 1 | 180000 | 1072.053 | 1072.053 | 0 |  | 0 | 547.36 | 547.36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.34 | 1.405 | 0.065 |  | 11700 | 0.103 | 0.104 | 0.001 |  | 180 | 11700 | 180 | 0.99988 | 0 | 0 | 19
7 | Shere Bangla |  | 33 | Exp | 8993 833 | 1 | 180000 | 317.734 | 317.734 | 0 |  | 0 | 244.376 | 244.376 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Satmosjid-1 |  | 33 | Exp | 8993 638E | 1 | 180000 | 4208.156 | 4216.182 | 8.026 |  | 1444680 | 2257.03 | 2258.095 | 1.065 |  | 191700 | 1444680 | 191700 | 0.99131 | 0 | 0 | 2299
9 | Satmosjid -2 |  | 33 | Exp | 8993 669E | 1 | 180000 | 5898.119 | 5941.853 | 43.734 |  | 7872120 | 2675.465 | 2692.955 | 17.49 |  | 3148200 | 7872120 | 3148200 | 0.9285 | 0 | 0 | 12525
10 | Kallayanpur T3 |  | 33 | Exp | 8993 831 | 1 | 180000 | 6570.523 | 6605.491 | 34.968 |  | 6294240 | 3203.655 | 3218.73 | 15.075 |  | 2713500 | 6294240 | 2713500 | 0.9183 | 0 | 0 | 10015
11 | Kallayanpur T4 |  | 33 | Exp | 8993 839 | 1 | 180000 | 8772.538 | 8813.321 | 40.783 |  | 7340940 | 4082.494 | 4100.067 | 17.573 |  | 3163140 | 7340940 | 3163140 | 0.91837 | 0 | 0 | 11680
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 170.633 | 182.172 | 11.539 |  | 2077020 | 45.504 | 51.275 | 5.771 |  | 1038780 | 2077020 | 1038780 | 0.89438 | 0.005 | 0 | 3305
| Exp to Desco at 11 KV | [9 empty] | 4469623.2 |  |  |  |  | 1230688.8 |  | -4469623.2 | -1230688.8 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Exp | 8993 836E | 1 | 180000 | 5452.879 | 5452.879 | 0 |  | 0 | 2686.619 | 2686.623 | 0.004 |  | 720 | 0 | 720 | 0 | 0 | 0 | 0
[10 empty] | Total=> | 4469623.2 | 25040700 |  |  | Total=> | 1230688.8 | 10256220 | 20571076.8 | 9025531.2 | 0.91574 |  |  | 39843
SATMOSJID 132/33KV SS
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3232.217 | 3275.612 | 43.395 |  | 32546250 | 1613.526 | 1630.967 | 17.441 |  | 13080750 | 32546250 | 13080750 | 0.92786 | 0 | 0 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 2873.592 | 2917.773 | 44.181 |  | 33135750 | 1410.279 | 1428 | 17.721 |  | 13290750 | 33135750 | 13290750 | 0.92812 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 65682000 |  |  | Total=> | 0 | 26371500 | 65682000 | 26371500 | 0.928 | 0 | 0 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1 | 180000 | 1963.391 | 1983.503 | 20.112 |  | 3620160 | 655.423 | 658.662 | 3.239 |  | 583020 | 3620160 | 583020 | 0.98728 | 0 | 0 | 4733.63
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1 | 180000 | 694.282 | 708.985 | 14.703 |  | 2646540 | 49.256 | 50.302 | 1.046 |  | 188280 | 2646540 | 188280 | 0.99748 | 0 | 0 | 3460.549
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1 | 180000 | 106.915 | 108.018 | 1.103 |  | 198540 | 4.16 | 4.16 | 0 |  | 0 | 198540 | 0 | 0 | 0 | 0 | 259.6059
19 | Monipuripara-1 |  |  |  |  | 1 | 180000 | 1133.802 | 1168.374 | 34.572 |  | 6222960 | 470.618 | 482.334 | 11.716 |  | 2108880 | 6222960 | 2108880 | 0.94709 | 0 | 0 | 8136.986
20 | Monipuripara-2 |  |  |  |  | 1 | 180000 | 815.083 | 838.951 | 23.868 |  | 4296240 | 293.063 | 299.53 | 6.467 |  | 1164060 | 4296240 | 1164060 | 0.9652 | 0 | 0 | 5617.655
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 16984440 |  |  | Total=> | 0 | 4044240 | 16984440 | 4044240 | 0.9728 |  |  | 22208.4259
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 414749.8 | 420573.6 | 5823.8 |  | 5969.395 | 265907.4 | 269629.8 | 3722.4 |  | 3815.46 | 5969.395 | 3815.46 | 0.84259 | 0.05 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 383501.3 | 388432.8 | 4931.5 |  | 5054.7875 | 134671.5 | 136479.6 | 1808.1 |  | 1853.3025 | 5054.7875 | 1853.3025 | 0.93888 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 11024.1825 |  |  | Total=> | 0 | 5668.7625 | 11024.1825 | 5668.7625 | 0.88931 |  |  | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 347.544 | 349.667 | 2.123 |  | 5222.58 | 221.77 | 223.421 | 1.651 |  | 4061.46 | 5222.58 | 4061.46 | 0.78939 | 0.105 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 109.988 | 117.946 | 7.958 |  | 19576.68 | 58.869 | 63.748 | 4.879 |  | 12002.34 | 19576.68 | 12002.34 | 0.85253 | 0.04 | 0 | 0
[10 empty] | Total=> | 0 | 24799.26 |  |  | Total=> | 0 | 16063.8 | 24799.26 | 16063.8 | 0.8393 |  |  | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 4469623.2 | 109691427.4425 |  |  |  | 1230688.8 | 41135016.5625 | [5 empty] | 63602.4259 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 105221804.2425 |  |  |  |  | 39904327.7625 | 105221804.2425 | 39904327.7625 | 0.93502 |  | 0 |  | 0.93502
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 733900 |  |  | 105955704.2425
33 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 105221804.2425 |  | 39904327.7625 |  | 0.93502 | 0
[8 empty] | PDB Unit |  | 105221804.2425 |  | KWH
[8 empty] | PGCB Unit |  | 105221804.2425 |  | KWH
11 KV LEVEL | [10 empty] | Month October-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [9 empty] | Total=> |  | 0 |  |  |  |  | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 1502 6 | 1 | 40000 | 9207.17 | 9219.86 | 12.69 |  | 507600 | 3470.13 | 3474.29 | 4.16 |  | 166400 | 520290 | 170560 | 0.95024 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 1502 7 | 1 | 40000 | 3871.9 | 3875.73 | 3.83 |  | 153200 | 1263.49 | 1263.65 | 0.16 |  | 6400 | 157030 | 6560 | 0.99913 | 1 |  | 6400 | RMU Feeder KVARH Back Calculation as per KWH Percentage
3a | PD Betar |  | 11 | Imp | 2612 100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612 100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 1502 5 | 1 | 40000 | 3979.7 | 3980.52 | 0.82 |  | 32800 | 1889.83 | 1890.52 | 0.69 |  | 27600 | 33620 | 28290 | 0.76515 | 1.1762
5 | BICC - U/G |  | 11 | Exp | 1502 4 | 1 | 40000 | 1038.34 | 1038.9 | 0.56 |  | 22400 | 297.33 | 297.34 | 0.01 |  | 400 | 22960 | 410 | 0.99984 | 1
6 | NEC |  | 11 | Exp | 1502 3 | 1 | 40000 | 431.67 | 431.67 | 0 |  | 0 | 56.31 | 56.31 | 0 |  | 0 | 0 | 0 | 0 | 1
7 | Manikmia Avenue |  | 11 | Exp | 7602 6327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 716000 |  |  |  | 0 | 200800 | 733900 | 205820 | 0.96285
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 716000 |  |  |  | 0 | 200800
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 716000 |  |  |  |  | 200800
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 733900 |  |  |  |  | 205820 | 733900 | 205820 | 0.96285 |  | 0 |  | 0.96285
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 733900 |  | 205820 |  | 0.96285 | 0
[8 empty] | PDB Unit |  | 733900 |  | KWH
[8 empty] | PGCB Unit |  | 733900 |  | KWH

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month October-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 907272480 | 8.1335 | 7379300716 |  |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 907272480 | 907272480 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 7379300716 | 7379300716 | 0
2a | 33kv | 105221804.2425 | 8.22 | 864923231 |  |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 105221804.2425 | 105221804.2425 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 864923231 | 864923231 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 733900 | 8.22 | 6032658 |  |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 733900 | 733900 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 6032658 | 6032658 | 0
2c | Bus Loss Units (33kv) | 63601.6359 | 8.22 | 522805 |  |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 63601.6359 | 63601.6359 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 522805 | 522805 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 106019305.8784 |  | 871478694 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 106019305.8784 | 106019305.8784 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 871478694 | 871478694 | 0
4 | TOTAL 132kv & 33kv (1+3) | 1013291785.8784 |  | 8250779410 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 1013291785.8784 | 1013291785.8784 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 8250779410 | 8250779410 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 0 | 8.22 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 0 |  | 0 |  |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 0 | 0 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 0 | 0 | 0
8 | TOTAL Billed Amount => (4+7) | 1013291785.8784 |  | 8250779410 |  | 8250779410 |  | 10 | সর্বমোট (৬+৯) | 1013291785.8784 | 1013291785.8784 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 8250779410 | 8250779410 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 495046765 | Source Tax | [10 empty] | 11 | উৎস কর (মোট বিলের উপর ৬%) | 495046765 | 495046765 | -
10 | NET BILL TOTAL => (8-9) |  |  | 7755732645 |  | 7755732645 | , কমা চেইঞ্জার | [8 empty] | 12 | কর পরবর্তী মোট পরিশোধ যোগ্য বিল (১০-১১) | 7755732645 | 7755732645 | -
11*** | 24th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  |  | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 7755732645
"In word: Taka Seven Hundred Seventy Five Crore Fifty Seven Lac Thirty Two Thousand Six Hundred and Forty Five Only"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | 31683869.1762 | 2021-10-01
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid | 30306309.6468 | 2021-11-01
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid | 28928750.1174 | 2021-12-01
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid | 27551190.588 | 2022-01-01
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid | 26173631.0586 | 2022-02-01
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid | 24796071.5292 | 2022-03-01
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid | 23418511.9998 | 2022-04-01
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid | 22040952.4704 | 2022-05-01
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid | 20663392.941 | 2022-06-01
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid | 19285833.4116 | 2022-07-01
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid | 17908273.8822 | 2022-08-01
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid | 16530714.3528 | 2022-09-01
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid | 15153154.8234 | 2022-10-01
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid | 13775595.294 | 2022-11-01
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid | 12398035.7646 | 2022-12-01
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid | 11020476.2352 | 2023-01-01
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid | 9642916.7058 | 2023-02-01
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid | 8265357.1764 | 2023-03-01
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid | 6887797.647 | 2023-04-01 |  | 366430834.8204
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid | 5510238.1176 | 2023-05-01 |  | 20971130269.73
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid | 4132678.5882 | 2023-06-01
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Paid | 2755119.0588 | 2023-07-01
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94 | Paid | 1377559.5294 | 2023-08-01 |  | 20604699434.9096
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0 | Certified For Payment | 380206430.1144
| Total | 3306142870.56
20984905865.024
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month October-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [9 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[12 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month October-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 907272480 | 0.2886 | 261838837.728 |  | 293050922 | , কমা চেইঞ্জার | 1 | 132 †Kwf (GbvwR©) | 907272480 | 907272480 | 907272480 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 7379300716 | 261838837.728 | 261838837.728 | 0
2a | 33kv Level | 105221804.2425 | 0.2944 | 30977299.169 |  |  |  | 2 | 33 †Kwf (GbvwR©) | 105221804.2425 | 105221804.2425 | 105221804.2425 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 864923231 | 30977299.169 | 30977299.169 | 0 |  | 33KV Amount (2+3+4) => | 31212083.9906
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 733900 | 0.2944 | 216060.16 |  |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 733900 | 733900 | 733900 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 6032658 | 216060.16 | 216060.16 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 63601.6359 | 0.2944 | 18724.6616 |  |  |  | 4 | 33 ‡Kwf evm jm | 63601.6359 | 63601.6359 | 63601.6359 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 522805 | 18724.6616 | 18724.6616 | 0 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 106019305.8784 | 0.2944 | 31212083.9906 |  |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 106019305.8784 | 106019305.8784 | 106019305.8784 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 871478694 | 31212083.9906 | 31212083.9906 | 0
4 | TOTAL=> (1+3) | 1013291785.8784 |  | 293050921.7186 |  |  |  | 6 | me©‡gvU (1+5) | 1013291785.8784 | 1013291785.8784 | 1013291785.8784 | 0 |  |  | 6 | me©‡gvU (1+5) | 8250779410 | 293050921.7186 | 293050921.7186 | 0
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000 | [12 empty] | 298330160 | , কমা চেইঞ্জার
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 13th Installment ) |  |  | 25993419.79 |  |  |  | ‡gvU (GbvwR©) |  | 1013228184.2425 | 1013228184.2425 | 1013228184.2425 | 0 |  |  | ‡gvU (GbvwR©) |  | 8250256605 | 293032197.057 | 31212083.9906 | 261820113.0664
7 | Grand TOTAL=> (4-5+6) |  |  | 317544341.5086
| CERTIFIED UNITS |  |  | 1013291785.8784 |  | 317544342 | , কমা চেইঞ্জার
| CERTIFIED TAKA |  |  | 293050921.7186
| CERTIFIED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 13th Installment of Wheeling Charge Due) |  |  | 317544341.5086
evsjv
In word: Taka Thirty One Crore Seventy Five Lac Forty Four Thousand Three Hundred and Forty Two
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Paid
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Paid
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06 | Paid
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27 | Paid
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48 | Paid
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69 | Certified For Payment
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check (hidden)
[6 empty] | Month October-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 129700639.26 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 129208272 | Fatullah Grid | 41464800 | 492367.26 | 0.3796%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 2206080 |  |  |  | Shyampur Grid | 87743472
|  |  | 132 | Import |  | 480960 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 27665280 | 35661120 | Postogola 132/33 KV Grid | 35496000 | Postogola Grid | 35496000 | 165120 | 0.463%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 7995840
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 480960 | 37867200
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 26963520 | 101149440 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 100463291.336 | Ullon Grid | 21476863.536 | 686148.664 | 0.6784%
|  |  | 132 | Import |  | 76800 | 0 |  |  |  | Dhanmondi Grid | 64435811
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 76800 | 26963520 |  |  |  | DU Grid | 14550616.8
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 16986240 | 138075840 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 135951360 | Lalbagh Grid | 53300160 | 2124480 | 1.539%
|  |  | 132 | Import |  | 43200 | 0 |  |  |  | Kamrangirchar Grid | 32179200
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 17045760 |  |  |  | Jigatola Grid | 50472000
|  |  | 132 | Import |  | 45120 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 88320 | 34032000
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 20541120 | 59044320 | Sitalakhya 132/33 KV Grid | 58939814.187 | Sitalakhya Grid | 58939814.187 | 104505.813 | 0.177%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 19337760
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 19165440
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 12087360 | 12087360 | Sitalakhya NOCS | 12087360 | Sitalakhya NOCS | 12087360 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 71131680
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 35787840 | 71268480 | Siddirganj 132/33 KV Grid | 71054674.56 | Siddirganj Grid | 71054674.56 | 213805.44 | 0.3%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 35480640
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 36233280 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 42877440 | 42877440 | Matuail 132/33 KV Grid | 42712541.816 | Matuail Grid | 42712541.816 | 164898.184 | 0.3846%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 150379200
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 36403200 | 64360320 | Moghbazar 132/33 KV Grid | 64055712 | Moghbazar Gird | 64055712 | 304608 | 0.4733%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 27957120
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 10195200 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 9624960
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 24243840 | 48408960 | Madartek 132/33 KV Grid | 48360551.04 | Madartek Grid | 48360551.04 | 48408.96 | 0.1%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 24165120
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 8959680 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 9249600
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 150798720
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 87573120 | 175271040 | Maniknagar 132/33 KV Grid | 174749093.6 | Kazla Grid | 61034400 | 521946.4 | 0.2978%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 87697920 |  |  |  | Motijheel Grid | 21549600
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 175271040 |  |  |  | Narinda Grid | 38965113.6
[11 empty] | Bangabhaban Grid | 4704000
[11 empty] | Maniknagar Grid | 48495980
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 79685760 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 79234560
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 158920320
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 50359680 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 53772480
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 104132160
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 11784000 | 29392320 | Charsyedpur 132/33 KV Grid | 29352000 | Charsyedpur Grid | 29352000 | 40320 | 0.1372%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 17608320
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 964800 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 31934400 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 31934400 | 30357120 | 907297279.26 |  | 902430670.539 |  | 902430670.539 | 4866608.721 | 0.5364%
[9 empty] | 33 KV Transmission Loss |  | 105197004.9825 | 105697903.7491 | -500898.7666 | -0.4762%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 733900 | 735950 | -2050 | -0.2793%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 1013228184.2425 | 1008864524.2881 | 4363659.9544 | 0.4307%
[9 empty] | From Summary Sheet |  |  |  | 5909564.6407 | 0.5832%
[9 empty] | Mismatch in KWH |  |  |  | -1545904.6863
| 33 KV LEVEL |  |  |  |  | Month October-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 1948464 | 1948464 | Sitalakhya NOCS | 1948464 | Sitalakhya NOCS | 1948464 | 0 | 0%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 1948464
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 11700 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 11700 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 11700
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 1444680 | 74998800 | Shatmasjid 132/33 KV Grid | 75536335.4972 | Asadgate SS | 15815925.4972 | -537535.4972 | -0.7167%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 7872120 |  |  |  | Lalmatia SS | 13778010
[11 empty] | Japan Garden SS | 16196800
[11 empty] | Jigatola Old SS | 1932000
[11 empty] | Shatmasjid SS | 18649800
[11 empty] | BGB SS | 9163800
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 6294240 | 11242576.8 | Adabor NOCS | 11394474 | Adabor NOCS | 11394474 | -151897.2 | -1.351%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 7340940
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 2077020
| Export to Desco at 11 KV |  |  |  |  | 4469623.2 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 0 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 4469623.2 | 25040700
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 32546250 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 33135750
AGARGAON 132/33KV SS | [5 empty] | 0 | 65682000
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 3620160 | 6465240 | Sherebanglanagar 33/11 KV SS | 6274894.179 | Sherebanglanagar SS | 6274894.179 | 190345.821 | 2.944%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 2646540
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 198540
19 | Monipuripara-1 |  |  |  |  | 0 | 6222960 | 10519200 | Monipuripara 33/11 KV SS | 10532954.641 | Monipuripara SS | 10532954.641 | -13754.641 | -0.1308%
20 | Monipuripara-2 |  |  |  |  | 0 | 4296240
| Maniknagar 230/132 kv |  |  |  |  | 0 | 16984440
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 5969.395 | 11024.1825 | Maniknagar 33/11 KV SS | 10781.4319 | Maniknagar 33/11 KV SS | 10781.4319 | 242.7506 | 2.202%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 5054.7875
Shyampur 230/132 kv | [5 empty] | 0 | 11024.1825
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 5222.58 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 19576.68
[6 empty] | 0 | 24799.26
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 4469623.2 | 109691427.4425 | 105197004.9825 |  | 105697903.7491 |  | 105697903.7491 | -500898.7666 | -0.4762%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 507600 | 733900 | Sherebanglanagar NOCS | 735950 | Sherebanglanagar NOCS | 735950 | -2050 | -0.2793%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 153200
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 32800
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 22400
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 716000
TOTAL => | [5 empty] | 0 | 716000 | 733900 |  | 735950 |  | 735950 | -2050 | -0.2793%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 182.172 | 170.633 |  | 11.539 | 180000 | 2077020 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8813.321 | 8772.538 |  | 40.783 | 180000 | 7340940 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.87 | #REF!
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6605.491 | 6570.523 |  | 34.968 | 180000 | 6294240 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9667.45 | #REF!
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4583.3 | #REF!
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 4382.3 | 4140.7 |  | 247.64 | 8000 | 1981120 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 52769.06 | #REF!
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 42349.9 | #REF!
03 |  | 11 KV Bashir Uddin |  | 74819925 | 934.477 | 934.064 |  | 0.42333 | 16000 | 6773.2 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 2296.25 | #REF!
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8361.96 | #REF!
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1131.24 | 1131.24 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9414.91 | #REF!
05 |  | 11 KV Lalkuthy |  | DHK15018 | 1001.83 | 1001.83 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9750.48 | 9689.95 |  | 62.0432 | 40000 | 2481730 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [5 empty] | #REF!
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 52769.06 | 52493.68 |  | 282.2645 | 8000 | 2258116 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  | #REF!
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8361.96 | 8308.18 |  | 55.1245 | 40000 | 2204980 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  | #REF!
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2296.25 | 2228.14 |  | 69.8128 | 40000 | 2792510 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  | #REF!
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  | #REF!
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.705 | 3273.705 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  | #REF!
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9667.45 | 9660.49 |  | 7.134 | 40000 | 285360 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  | #REF!
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9414.91 | 9399.97 |  | 15.3135 | 40000 | 612540 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  | #REF!
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4583.3 | 4531.62 |  | 52.972 | 40000 | 2118880 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  | #REF!
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.87 | 995.82 |  | 0.05125 | 40000 | 2050 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 42349.9 | 42213.06 |  | 140.261 | 8000 | 1122088 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 4469623.2 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 11242576.8 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48 | 48 | 48 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41 | 41 | 41 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [136 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | 89 | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [176 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[139 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.36993 | 0.1982 | 0.22066 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 3.3831 | 4.7675 | 6.4099 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.4562 | 0.087826 | 1.0278 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.57703 | 0.73688 | 0.95024 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.028 | 0.51858 | 1.0269 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | -1.6675 | -0.51228 | -0.14892 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.40506 | 0.59878 | 0.032224 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.78672 | 0.71164 | 0.1718 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.090354 | 1.8004 | 0.72315 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.7093 | 1.2924 | 1.7957 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.012837 | 0.076849 | 0.070408 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.42244 | 0.67755 | 0.74731 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | -0.035562 | 1.3133 | 1.1413 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.31121 | 1.418 | 1.5 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 0.39586 | 0.22128 | 3.0565 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.22363 | -0.15783 | 0.36408 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | 0.86271 | -0.5535 | -0.24021 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 0.10052 | -0.025203 | 0.21781 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.2611 | 0.97617 | -0.13914 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.1968 | 2.1342 | 2.1711 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.16255 | -0.50074 | 0.12321 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.07333 | 0.10551 | 0.1185 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.043971 | -0.075665 | -0.064901 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.1357 | 2.0237 | 1.9508 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.5119 | 0.40513 | -1.985 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.14868 | 0.41233 | 0.10871 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 1.5455 | 1.2197 | 1.7549 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 0.85 | 1 | 1 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | 2.0082 | -2.831 | -2.6717 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.2163 | 0.86585 | 1.5712 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | 1.3885 | 1.3864 | 1.1808 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | 0.15826 | 0.3214 | 0.74913 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 1.3314 | 0.41255 | 0.56541 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | -0.78277 | 1.757 | 1.2174 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 1.2104 | 0.54824 | 0.90308 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.026513 | 0.047491 | -0.25931 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 0.063822 | 1.034 | -0.81695 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 1.0407 | 0.334 | 0.41807 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.23578 | 1.0938 | 1.7781 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 0.31408 | 0.18399 | 1.0713 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.092639 | -0.05005 | 0.074283 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.24412 | 0.051628 | -0.13885 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 1.2666 | 0.69212 | 0.34882 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.070914 | 0.3138 | 0.22403 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | September-2023 % of Loss | August-2023 % of Loss | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.15556 | 0.20112 | 0.95272 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.15665 | 0.20537 | 0.20884 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.1157 | 1.2591 | 1.2584 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.77964 | 0.65402 | 1.444 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 0.17832 | 0.31771 | 1.0687 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 0.24297 | 0.17031 | 0.10378 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.10878 | -0.085961 | 0.041539 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.43536 | 0.43971 | 1.0708 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.13156 | -0.4174 | 0.13595 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.3565 | 2.1519 | 1.211 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | -0.031653 | -0.01844 | 0.010028 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.79245 | 0.12531 | -0.42556 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.48244 | 0 | -1.9122 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -1.0495e-13 | -0.04852 | -0.048314 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.8683 | 1.573 | 0.29445 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 0.43069 | 0.068963 | -0.86273 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | -0.023304 | 0.076622 | 0.064233 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.18888 | 0.15171 | 0.25381 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.5174 | 2.7774 | 1.2284 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.48766 | 0.66641 | -0.41499 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.64916 | 0.88184 | 0.57602 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.32352 | 0.80196 | -0.26653 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.25534 | 0.44829 | 1.0739 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.0829 | 1.112 | 1.1039 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.33276 | 0.71435 | 0.23019 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 1.0512 | 1.0599 | 0.74837 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.1333 | 1.4904 | 1.4865 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 1.4383 | 2.0408 | 0.18209 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.4766 | 0.10496 | 0.096193 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | 1.2474 | -0.24532 | -0.64219 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.28876 | -0.62244 | 1.8284 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.24367 | 0.46773 | 0.16433 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | 0.66653 | 0.56513 | -0.8103 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.4676 | 1.9489 | 1.3703 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | 1.3208 | 0.33477 | -0.12622 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.057847 | -0.086839 | 0.038802 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.22785 | 0.18163 | 1.4646 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | 1.179 | 0.4914 | 1.1051 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.044529 | -0.040721 | -0.12694 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | -2.2501 | 3.468 | 0.40336 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 1.5164 | 1.7985 | 0.80075 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.12007 | 0.27405 | 0.15019 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.18029 | -0.41785 | -0.72448 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 0 | 0 | 0 | 0.033974

## ALL SS Loss History (hidden)
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68
|  | DPDC TOTAL SS | 89 | 89
NORTH
[7 empty] | HV Side |  |  |  | LV Side |  |  | % LOSS
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export / Import | XFR-Sending | XFR-Receiving | Feeder Total | Corrected Feeder Total | S_FT | R_FT | XS_FT | XR_FT
[7 empty] | S | R | EI | XS | XR | FT | CFT | %S | %R | %XS | %XR
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.36993 | 132 | 33 | 64360320 | 64612800 | 0 | 64612800 | 64377600 | 63819626 | 64055712 | 0.84722 | 1.2428 | 1.2428 | 0.8743
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 3.3831 | 33 | 11 |  |  |  | 20151872.4546 | 19956600 | 19492433.18 | 20151872.4546 | -100 | -100 | 3.3831 | 2.3813
N-2 | 3 | Green Road 33/11KV S/S | 3 | 1.4562 | 33 | 11 | 13422148.4753 | 0 | 0 | 0 | 14162700 | 13229497.421 | 13422148.4753 | 1.4562 | -100 | -100 | 7.054
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 0.57703 | 33 | 11 | 14054705.8227 | 0 | 0 | 0 | 13778010 | 13698963.505 | 13778010 | 2.5969 | -100 | -100 | 0.57703
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.028 | 33 | 11 | 20863294.4968 | 0 | 0 | 22313702 | 20242118 | 20651011.6 | 20863294.4968 | 1.028 | -100 | 8.0514 | -1.98
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | -1.6675 | 33 | 11 | 9369331.9415 | 2865960 | 0 | 5117400 | 4283640 | 9528214.8 | 9369331.9415 | -1.6675 | -69.9213 | -46.2921 | -55.0426
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.40506 | 132 | 33 | 0 | 65057000 | 3503000 | 65021000 | 63501600 | 64175860 | 64435811 | -100 | 1.373 | 1.3169 | -1.0506
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.78672 | 33 | 11 |  |  |  | 13092016.6366 | 6281854.2 | 12989822.7099 | 13092016.6366 | -100 | -100 | 0.78672 | -51.6402
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.090354 | 33 | 11 | 3949533.4562 | 4571100 | 0 | 3902400 | 3839000 | 3945968.1161 | 3949533.4562 | 0.090354 | 15.8423 | -1.1041 | -2.7108
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.7093 | 33 | 11 | 9160074.8495 | 0 | 0 | 0 | 9090800 | 8938019.34 | 9090800 | 2.4844 | -100 | -100 | 1.7093
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.012837 | 132 | 33 | 82940160 | 0 | 61542000 | 21398160 | 21541488 | 21474107 | 21476863.536 | 286.2333 | -100 | -0.35367 | 0.31378
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.42244 | 33 | 11 |  |  |  | 8183826.3867 | 8182776 | 8149400.28 | 8183826.3867 | -100 | -100 | 0.42244 | 0.40955
N-1 | 13 | Kakrail 33/11KV S/S | 13 | -0.035562 | 33 | 11 | 9667826.4596 | 8229600 | 0 | 0 | 9605334.534 | 9671265.7316 | 9667826.4596 | -0.035562 | -14.9067 | -100 | -0.68172
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 0.31121 | 33 | 11 | 6838730.1823 | 914760 | 0 | 6670800 | 6594300 | 6817513.56 | 6838730.1823 | 0.31121 | -86.5822 | -2.152 | -3.2741
N-2 | 15 | Goran 33/11KV S/S | 15 | 0.39586 | 33 | 11 | 9906765.1961 | 0 | 0 | 9896000 | 9890611 | 9851612.44 | 9890611 | 0.55983 | -100 | 0.45056 | 0.39586
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.22363 | 33 | 11 | 12367299.3317 | 0 | 0 | 0 | 12070400 | 12043467.2198 | 12070400 | 2.6889 | -100 | -100 | 0.22363
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | 0.86271 | 33 | 11 |  |  |  | 19024333.1694 | 18649800 | 18490282.2 | 18649800 | -100 | -100 | 2.8883 | 0.86271
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | 0.10052 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 33 | 11 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | -0.2611 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 1.1968 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.16255 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.07333 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.043971 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.1357 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 0.5119 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.14868 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 1.5455 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 0.85 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | 2.0082 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 31 | Banasree 33/11 SS | 31 | 1.2163 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 32 | Mugdhapara Hospital | 32 | 1.3885 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 33 | DMC | 33 | 0.15826 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 1.3314 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 35 | BSMMU 33/11KV S/S | 35 | -0.78277 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 1.2104 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.026513 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 0.063822 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 1.0407 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.23578 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 0.31408 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.092639 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.24412 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 1.2666 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.070914 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
|  | SOUTH |  |  |  |  | S: HV Side; XR: LV Side
| Sl. No. | Name of S/S | Page No. | October-2023 % of Loss | HV Votage Level | LV Votage Level | Sending | Receiving | Export | XFR-Sending | XFR-Receiving | Feeder Total | Feeder Total
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.15556 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.15665 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.1157 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.77964 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 0.17832 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 0.24297 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 7 | Madarteck 132/33KV S/S | 6 | 0.10878 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 0.43536 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 9 | Kazla 132/133 KV SS | 39 | -0.13156 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.3565 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 11 | Shyampur 132/33KV S/S | 9 | -0.031653 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.79245 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.48244 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -1.0495e-13 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 15 | Postogola 33/11KV S/S | 12 | 1.8683 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | 0.43069 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | -0.023304 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.18888 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.5174 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.48766 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 0.64916 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 22 | Demra 33/11KV S/S | 20 | 0.32352 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.25534 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.0829 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.33276 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 26 | Matuail 33/11KV S/S | 23 | 1.0512 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.1333 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 1.4383 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 1.4766 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 30 | Mitford 33/11 kV | 29 | 1.2474 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.28876 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.24367 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 33 | Dapa 33/11 kV | 32 | 0.66653 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.4676 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 35 | Amulia 33/11 kv | 34 | 1.3208 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.057847 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.22785 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 38 | P & T 33/11 KV SS | 37 | 1.179 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.044529 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | -2.2501 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 1.5164 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.12007 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.18029 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 132 | 33 | %S: #DIV/0!; %R: #DIV/0!; %XS: #DIV/0!; %XR: #DIV/0!

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Feeder Code | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) |  | 3: 132; 4: IMPORT; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) |  | 3: 132; 6: 1; 10: 1000
| 132 KV DHANMONDI-3 CKT(EXP) |  | 3: 132; 6: 1; 10: 1000
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 10: Net Total | 61554000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 |  | 132 |  | SIEM0480 | 1 | 1632756 | 1632768 | 12 | 1000 | 12000
| 132 kV Dhaka University |  | 132 |  | SIEM0480 | 1 | 116377 | 119880 | 3503 | 1000 | 3503000
3 | 132 kV Dhaka University |  | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 |  | 132 |  | SIEM0481 | 1 | 2181074 | 2212585 | 31511 | 1000 | 31511000
8 | 132 kV Ullon Circuit-3 |  | 132 |  | SIEM0484 | 1 | 2944081 | 2974112 | 30031 | 1000 | 30031000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 65057000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 65057000
| DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhaka University (Export) |  | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) |  | 132 |  |  | 1 | 116377 | 119880 | 3503 | 1000 |  | 3503000
|  |  | 7: 0; 8: 0; 10: Total |  | 3503000
| DHANMONDI 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) |  | 132 | NET IMPORT | SIEM0487 | 1 | 900783 | 909704 | 8921 | 1000 |  | 8921000
5 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | SIEM0496 | 1 | 1481372 | 1489700 | 8328 | 2000 |  | 16656000
9 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | SIEM0493 | 1 | 1351635 | 1359750 | 8115 | 2000 |  | 16230000
10 | 132/33kV, 80/120 MVA GT-3 (HV) |  | 132 |  | SIEM0497 | 1 | 1319768 | 1331375 | 11607 | 2000 |  | 23214000
|  |  | 10: Total |  | 65021000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 4: 65021000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 65021000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 65021000 | 132/33 kv GT LV Side |  | 63501600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1519400
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.337%
| 132 KV TOTAL IMPORT |  | 4: 65021000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming |  | 33 | IMPORT | BD001860 | 1 | 2283.1 | 2305.89 | 22.79 | 720000 | 16408800
12 | 132/33 kV GT-2 Incoming |  | 33 |  | BD001818 | 1 | 2252.99 | 2274.38 | 21.39 | 720000 | 15400800
17 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001863 | 1 | 1992.33 | 2024.16 | 31.83 | 720000 | 22917600
24 | 132/33 kV GT-4 Incoming |  | 33 |  | BD001916 | 1 | 1868.1 | 1886.38 | 18.28 | 480000 | 8774400
|  |  | 7: 0; 8: 0; 10: Total | 63501600 |  | 0
| DHANMONDI 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 |  |  |  |  | 13092016.6366 | Dhanmondi 33/11 kv ss | 0.78672 |  | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 |  | 33 |  | BD001861 | 1 | 2143.91 | 2170.41 | 26.5 | 240000 |  | 6360000 | 6385761.8419 | [5 empty] | 33/11 kV 20/28 MVA T-1 | 6385761.8419 | 7247940.7959 | -862178.954 | -11.8955 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 |  | BD001892 | 1 | 2447.27 | 2475.1 | 27.83 | 240000 |  | 6679200 | 6706254.7947 | [5 empty] | 33/11 kV 20/28 MVA T-2 | 6706254.7947 | 7528007.7954 | -821753.0007 | -10.9159 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 13039200 | 13092016.6366 | [5 empty] | 33 KV Feeders | 13092016.6366 | 14775948.5913 | -1683931.9547 | -11.3964 | OK
5 | New Ramna Circuit-1 |  | 33 |  | BD001919 | 1 | 1494.65 | 1512.88 | 18.23 | 240000 |  | 4375200 | 4392922.2029 |  | 7508692.0375 | New Ramna 33/11 kv ss | 1.7093 |  | New Ramna Circuit-1 | 4392922.2029 | 4292751.0777 | 100171.1253 | 2.3335 | OK
8 | Kakrail Circuit-1 |  | 33 |  | BD001825 | 1 | 870.12 | 890.27 | 20.15 | 240000 |  | 4836000 | 4855588.7213 | [5 empty] | Kakrail Circuit-1 | 4855588.7213 | 5130537.7053 | -274948.984 | -5.3591 | OK
9 | Kawran Bazar Circuit-1 |  | 33 |  | BD001820 | 1 | 1874.11 | 1890.5 | 16.39 | 240000 |  | 3933600 | 3949533.4562 |  | 9667802.4565 | Kakrail 33/11 kv ss | -0.035562 |  | Kawran Bazar Circuit-1 | 3949533.4562 | 3228013.6057 | 721519.8505 | 22.3518 | OK
10 | New Ramna Circuit-2 |  | 33 |  | BD001816 | 1 | 1223.1 | 1236.03 | 12.93 | 240000 |  | 3103200 | 3115769.8346 | [5 empty] | New Ramna Circuit-2 | 3115769.8346 | 3073493.8818 | 42275.9527 | 1.3755 | OK
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 |  | 0 | 0 |  | 3949533.4562 | Kawran Bazar 33/11 kv ss | 0.090354 |  | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder |  | 33 |  | BD001840 | 1 | 433.43 | 446.7 | 13.27 | 240000 |  | 3184800 | 3197700.3639 | [5 empty] | DMC Hospital Feeder | 3197700.3639 | 3102466.33 | 95234.0338 | 3.0696 | OK
15 | Green Road Circuit-2 (U/G) |  | 33 |  | BD001918 | 1 | 2145.29 | 2172.52 | 27.23 | 240000 |  | 6535200 | 6561671.5077 |  | 3197700.3639 | DMC Hospital 33/11 kv ss | 0.15826 |  | Green Road Circuit-2 (U/G) | 6561671.5077 | 7035476.1757 | -473804.6679 | -6.7345 | OK
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1656.79 | 1676.76 | 19.97 | 240000 |  | 4792800 | 4812213.7352 | [5 empty] | Kakrail Circuit-2 | 4812213.7352 | 5381632.2565 | -569418.5213 | -10.5808 | OK
18 | BSMMU Hospital Circuit-1 |  | 33 |  | BD001920 | 1 | 740.94 | 755.4 | 14.46 | 240000 |  | 3470400 | 3484457.2164 |  | 13422148.4753 | Green Road 33/11 kv ss | 1.4562 |  | BSMMU Hospital Circuit-1 | 3484457.2164 | 3609484.1739 | -125026.9575 | -3.4638 | OK
19 | Azimpur Circuit-1 |  | 33 |  | BD001822 | 1 | 2023.72 | 2057.42 | 33.7 | 240000 |  | 8088000 | 8120761.2858 | [5 empty] | Azimpur Circuit-1 | 8120761.2858 | 1755247.4879 | 6365513.7979 | 362.6562 | FAULT
20 | Azimpur Circuit-2 |  | 33 |  | BD001857 | 1 | 1865.27 | 1867.53 | 2.26 | 240000 |  | 542400 | 544597.0477 |  | 4908602.5932 | BSMMU 33/11 kv ss | -0.78277 |  | Azimpur Circuit-2 | 544597.0477 | 5193311.3431 | -4648714.2955 | -89.5135 | CHECK
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 164.76 | 170.67 | 5.91 | 240000 |  | 1418400 | 1424145.3768 | [5 empty] | BSMMU Hospital Circuit-2 | 1424145.3768 | 1583827.1693 | -159681.7924 | -10.082 | OK
23 | Green Road Circuit-1 |  | 33 |  | BD001865 | 1 | 1473.63 | 1502.1 | 28.47 | 240000 |  | 6832800 | 6860476.9675 |  | 8665358.3334 | Azimpur 33/11 kv ss | 1.1357 |  | Green Road Circuit-1 | 6860476.9675 | 7556980.2436 | -696503.2761 | -9.2167 | OK
26 | 33/0.4 kV, 500 kVA AT-1 |  | 0.4 |  | 84.2659 | 1 | 321080 | 323466 | 2386 | 10 |  | 23860 | 23956.6474 | Paribag |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 23956.6474 | 23982.7488 | -26.1014 | -0.10883 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 |  | 0.4 |  | 84.2673 | 1 | 478776 | 478776 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 875.2094 | -875.2094 | -100 | CHECK
|  |  | 10: Total |  | 51136660 | 51343794.3634 | [6 empty] | 51343794.3634 | 50968079.4087 | 375714.9547 | 0.73716 | OK
|  |  | 9=8-7: Grand Total | 64435811 | 64175860 | 64435811 | 0.40506
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming |  | 11 | IMPORT | DHK60884 | 1 | 975119.32 | 975119.32 | 0 | 180 | 0 |  | 0
16 | 33/11 kV Transformer-1 Incoming |  | 11 |  | DHK60976 | 1 | 576879.23 | 611778.42 | 34899.19 | 180 | 6281854.2 |  | 13092016.6366
|  |  | 7: 0; 8: 0; 10: Total | 6281854.2 |  | 13092016.6366
| DHANMONDI 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 9200644 | 10517508 | 1316864 | 1 |  | 1316864 | 1327224.0724 | Paribag |  |  |  |  | 11 kV Balaka Feeder | 1327224.0724 | 1457854.4301 | -130630.3578 | -8.9605 | OK
5 | 11 kV Mogbazar O/H | C301M | 11 |  | HA021100463-02 | 1 | 50840272 | 52334628 | 1494356 | 1 |  | 1494356 | 1506112.4428 | Paribag |  |  |  |  | 11 kV Mogbazar O/H | 1506112.4428 | 1598079.2811 | -91966.8383 | -5.7548 | OK
6 | 11 kV Panthopath Feeder | C3011 | 11 |  | HA021101078-02 | 1 | 65548276 | 66739049 | 1190773 | 1 |  | 1190773 | 1200141.0854 | Paribag |  |  |  |  | 11 kV Panthopath Feeder | 1200141.0854 | 2105982.2036 | -905841.1181 | -43.0128 | CHECK
7 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 |  | DHK60882 | 1 | 229747.82 | 236770.81 | 7022.99 | 60 |  | 421379.4 | 424694.4888 | Paribag |  |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 424694.4888 | 424650.6487 | 43.8401 | 0.010324 | OK
8 | 11 kV P G Hospital Feeder | C301P | 11 |  | DHK60889 | 1 | 290812.76 | 294533.1518 | 3720.3918 | 60 |  | 223223.5099 | 224979.6606 | Paribag |  |  |  |  | 11 kV P G Hospital Feeder | 224979.6606 | 224715.2737 | 264.3869 | 0.11765 | OK
9 | 11 kV Abdul Monem Ltd |  | 11 |  | DHK60890 | 1 | 713.79 | 720.79 | 7 | 60000 |  | 420000 | 423304.2367 | Paribag |  |  |  |  | 11 kV Abdul Monem Ltd | 423304.2367 | 422384.6367 | 919.6 | 0.21772 | OK
10 | 11 kV Surjasen Hall Feeder | D301H | 11 |  | DHK60880 | 1 | 570802.23 | 576270.3 | 5468.07 | 60 |  | 328084.2 | 330665.314 | Ramna |  |  |  |  | 11 kV Surjasen Hall Feeder | 330665.314 | 381236.2759 | -50570.9619 | -13.265 | OK
11 | 11 kV Azimpur-1 Feeder |  | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | D301U | 11 |  | DHK60873 | 1 | 947497.59 | 956639.98 | 9142.39 | 60 |  | 548543.4 | 552858.9173 | Ramna |  |  |  |  | 11 kV TSC Feeder | 552858.9173 | 527789.8466 | 25069.0707 | 4.7498 | OK
13 | 11 kV SCADA Bhaban | C301S | 11 |  | DHK60883 | 1 | 28547.18 | 28791.31 | 244.13 | 60 |  | 14647.8 | 14763.0376 | Paribag |  |  |  |  | 11 kV SCADA Bhaban | 14763.0376 | 14899.4821 | -136.4445 | -0.91577 | OK
14 | 11 kV DPH Sw/S-2 |  | 11 |  | DHK60871 | 1 | 532788.31 | 549657.1 | 16868.79 | 60 |  | 1012127.4 | 1020090.0393 | Paribag |  |  |  |  | 11 kV DPH Sw/S-2 | 1020090.0393 | 1178402.3777 | -158312.3384 | -13.4345 | OK
17 | 11 kV New Elephant Road Feeder | C301E | 11 |  | DHK60981 | 1 | 116390.67 | 131190.1 | 14799.43 | 60 |  | 887965.8 | 894951.6314 | Paribag |  |  |  |  | 11 kV New Elephant Road Feeder | 894951.6314 | 961999.4403 | -67047.8089 | -6.9696 | OK
18 | 11 kV Dhanmondi O/H Feeder | C301D | 11 |  | DHK61110 | 1 | 456146.54 | 480431.1 | 24284.56 | 60 |  | 1457073.6 | 1468536.7336 | Paribag |  |  |  |  | 11 kV Dhanmondi O/H Feeder | 1468536.7336 | 1572278.7706 | -103742.0371 | -6.5982 | OK
19 | 11 kV Sonargaon Feeder |  | 11 |  | DHK61115 | 1 | 399272.59 | 426855.1 | 27582.51 | 60 |  | 1654950.6 | 1667970.4775 | Paribag |  |  |  |  | 11 kV Sonargaon Feeder | 1667970.4775 | 1771267.2548 | -103296.7773 | -5.8318 | OK
20 | 11 kV Museum Feeder | D301M | 11 |  | DHK61107 | 1 | 552119.57 | 554305.25 | 2185.68 | 60 |  | 131140.8 | 132172.5149 | Ramna |  |  |  |  | 11 kV Museum Feeder | 132172.5149 | 123208.813 | 8963.7019 | 7.2752 | OK
21 | 11 kV Shanta property |  | 11 |  | DHK61112 | 1 | 348994.41 | 352032.55 | 3038.14 | 60 |  | 182288.4 | 183722.5048 | Paribag |  |  |  |  | 11 kV Shanta property | 183722.5048 | 209615.174 | -25892.6692 | -12.3525 | OK
22 | 11 kV BIRDEM RMU Feeder | C601R | 11 |  | DHK61108 | 1 | 732231.99 | 746291.96 | 14059.97 | 60 |  | 843598.2 | 850234.9813 | Kakrail |  |  |  |  | 11 kV BIRDEM RMU Feeder | 850234.9813 | 921150.1931 | -70915.2117 | -7.6986 | OK
23 | 11 kV Azimpur-2 Feeder |  | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 |  | 11 |  | DHK60978 | 1 | 812155.99 | 826536.1 | 14380.11 | 60 |  | 862806.6 | 869594.4982 | Kakrail |  |  |  |  | 11 kV DPH Sw/S-1 | 869594.4982 | 880434.4894 | -10839.9912 | -1.2312 | OK
|  |  | 10: Total | 13092016.6366 | 12989822.7099 | 13092016.6366 | 0.78672
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Paribag at 33 KV level |  |  | 10380447.0584
[7 empty] | Azimpur at 33 KV level |  |  | 0
[7 empty] | Ramna at 33 KV level |  |  | 1015696.7461
[7 empty] | Kakrail at 33 KV level |  |  | 1719829.4795
|  |  | 7: Total =; 10: 13115973.2841 | -2.7067e-09
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 |  | 33 | 0 | BD001820 | 1 | 1874.11 | 1890.5 | 16.39 | 240000 | 0 | 3933600 | 3949533.4562
11 | Kawran BazarCircuit-2 |  | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 3933600 | 3949533.4562
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar |  | 33 | 0 | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 | Check | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAWRANBAZAR 33 KV SIDE (RECEIVING) | [10 empty] | 3933600 | 3949533.4562
1 | 33 kV Dhanmondi Circuit-1 |  | 33 |  | DHK61036 | 1 | 3447.89 | 3462.35 | 14.46 | 270000 | 3904200
5 | 33 kV Dhanmondi Circuit-2 |  | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar |  | 33 |  | DHK 61038 | 1 | 1059.48 | 1061.95 | 2.47 | 270000 | 666900
|  |  | 7: 0; 8: 0; 10: Total | 4571100 | 0 | 3949533.4562
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | DHK61039 | 1 | 5179.43 | 5201.11 | 21.68 | 180000 |  | 3902400
3 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 3902400
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4: 3949533.4562; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 3949533.4562
| MOGBAZAR 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 3949533.4562 | 33 KV TX HV SIDE |  | 3902400
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 47133.4562
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.193%
| TOTAL IMPORT |  | 4: 3949533.4562
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK00182 | 1 | 14839.3 | 15223.2 | 383.9 | 10000 | 3839000 |  | 3949533.4562
15 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 3839000 |  | 3949533.4562
| KAWRANBAZAR 11 KV SIDE |  | 7: 0; 8: 0
6 | WASA Bhaban | C605M | 11 |  | 8536188 | 1.11 | 271216 | 271216 | 0 | 1000 | 1121880 | 1121880 | 1122893.6635 | Shere b.nagar | From Customer End | 80 |  |  | WASA Bhaban | 1122893.6635 | 1128091.0061 | -5197.3427 | -0.46072 | OK
7 | Sangsad Bhaban |  | 11 |  | 8536178 | 1.11 | 577180 | 581779 | 4599 | 44 |  | 224615.16 | 224818.1088 | Shere b.nagar |  | 20 |  |  | Sangsad Bhaban | 224818.1088 | 56030.9835 | 168787.1252 | 301.2389 | FAULT
8 | Air Port Road (West) | D505A | 11 |  | 8536182 | 1.11 | 3219.3 | 4157.6 | 938.3 | 1000 |  | 1041513 | 1042454.0487 | Shere b.nagar |  | 60 |  |  | Air Port Road (West) | 1042454.0487 | 996313.4361 | 46140.6126 | 4.6311 | OK
9 | ICC (PM Office) | C172C | 11 |  | 8536193 | 1.11 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  | 20 |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | D505U | 11 |  | DHK00183 | 1.11 | 16986.2 | 17563.9 | 577.7 | 444.44 |  | 284995.8167 | 285253.3218 | Shere b.nagar |  | 40 |  |  | (UTC) Tower | 285253.3218 | 290292.9413 | -5039.6194 | -1.736 | OK
11 | Sonargaon Hotel | C605O | 11 |  | 8536190 | 1.11 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | No Load |  |  |  | Sonargaon Hotel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Panthopath | D505P | 11 |  | 8536184 | 1.11 | 37334.9 | 38266.9 | 932 | 1000 |  | 1034520 | 1035454.7302 | Shere b.nagar |  |  |  |  | Panthopath | 1035454.7302 | 1172086.0871 | -136631.3569 | -11.6571 | OK
13 | Titas Bhaban | C605N | 11 |  | DHK00190 | 1.11 | 56600.9 | 57079.4 | 478.5 | 444.44 |  | 236057.6394 | 236270.9269 | Kakrail |  |  |  |  | Titas Bhaban | 236270.9269 | 238706.8937 | -2435.9668 | -1.0205 | OK
16 | Green Road Dormatory s/s |  | 11 |  | DHK00021 | 1.11 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | [5 empty] | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 |  | 11 |  | 85-12906 | 1.11 | 69061 | 69276 | 215 | 10 |  | 2386.5 | 2388.6563 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-1 | 2388.6563 | 2990.8959 | -602.2396 | -20.1358 | OK
27 | Aux. Transformer, AT-2 |  | 11 |  | 85-12909 | 1.11 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 3949533.4562 | 3945968.1161 | 3949533.4562 | 0.090354
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail at 33 KV level |  |  | 236270.9269
[6 empty] | Shere b.nagar at 33 KV level |  |  | 3713262.5293
[6 empty] | Total = |  |  | 3949533.4562 | 0
|  |  | 9=8-7: Customer Name; 10: Customer Number | Feeder name | Consumption | OMF
|  |  | 9=8-7: Square Hospital; 10: 27529489 | Wasa Bhaban | 1121880 | 6000
|  |  | 9=8-7: NOCS Name; 10: Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
|  |  | 9=8-7: ShereBangla Nagar; 10: 2739.64 | 2874.54 | 1078.27 | 1130.35
[11 empty] | 2874.54 | 1130.35
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 |  | 33 | 0 | BD001919 | 1 | 1494.65 | 1512.88 | 18.23 | 240000 | 0 | 4375200 | 4392922.2029
10 | New Ramna Circuit-2 |  | 33 | 0 | BD001816 | 1 | 1223.1 | 1236.03 | 12.93 | 240000 | 0 | 3103200 | 3115769.8346
|  |  | 10: Total | 0 | 7478400 | 7508692.0375
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1648800 | 1651382.812
|  |  | 10: Total | 0 | 1648800 | 1651382.812
| NEW RAMNA 33 KV SIDE (RECEIVING) | [10 empty] | 9127200 | 9160074.8495
|  |  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
|  |  | 10: Total |  | 0 | 9160074.8495
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 9=8-7: 0 |  | 0
| Feeder No.2 |  | 3: 33; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.3. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 9160074.8495 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 7508692.0375; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9160074.8495
| NARINDA 33 KV SIDE |  | 4: 1651382.812; 6: 33 KV NET IMPORT; 9=8-7: 9160074.8495 | 33 KV TX HV SIDE |  | 9160074.8495
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 9160074.8495
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK 00002 | 1 | 25960 | 26395 | 435 | 10000 | 4350000 |  | 4383148.4133
15 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK 00007 | 1 | 14275.1 | 14584.3 | 309.2 | 10000 | 3092000 |  | 3115562.0446
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming |  | 11 |  | DHKA2182 | 1 | 613.91 | 623.07 | 9.16 | 180000 | 1648800 |  | 1661364.3917
|  |  | 7: 0; 8: 0; 10: Total | 9090800 |  | 9160074.8495
| NEW RAMNA 11 KV SIDE |  | 7: 0; 8: 0
4 | Police Bhaban | D315I | 11 |  | DHK 00005 | 1 | 73880.1 | 74130.7 | 250.6 | 444.44 |  | 111376.664 | 113280.4639 | Ramna |  |  |  |  | Police Bhaban | 113280.4639 | 112636.0604 | 644.4035 | 0.57211 | OK
5 | Water Works |  | 11 |  | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Lalbag |  |  |  |  | Water Works | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | GPO | D3157 | 11 |  | DHK 00060 | 1 | 99521.1 | 100084.7 | 563.6 | 444.44 |  | 250486.384 | 254768.0345 | Ramna |  |  |  |  | GPO | 254768.0345 | 252148.1113 | 2619.9232 | 1.039 | OK
7 | Culvert Road | D315C | 11 |  | 8536184 | 1 | 39940.4 | 40096.9 | 156.5 | 444.44 | 95 | 1155511.98 | 1175263.5465 | Ramna | Estimated |  |  |  | Culvert Road | 1175263.5465 | 1013459.3684 | 161804.1781 | 15.9655 | OK
8 | Secretariat (East) | D315E | 11 |  | DHK00059 | 1 | 81726.9 | 81730.6 | 3.7 | 444.44 |  | 1644.428 | 1672.5368 | Ramna |  |  |  |  | Secretariat (East) | 1672.5368 | 765.313 | 907.2238 | 118.5429 | FAULT
9 | Siddik Bazar | B615S | 11 |  | DHK00076 | 1 | 37647.7 | 41750.6 | 4102.9 | 444.44 |  | 1823492.876 | 1854662.4712 | Bangshal |  |  |  |  | Siddik Bazar | 1854662.4712 | 1902703.0751 | -48040.6039 | -2.5249 | OK
10 | Bokshi Bazar | D315X | 11 |  | DHK 00206 | 1 | 89013.4 | 90253.3 | 1239.9 | 444.44 |  | 551061.156 | 560480.6352 | Ramna |  |  |  |  | Bokshi Bazar | 560480.6352 | 561829.7499 | -1349.1147 | -0.24013 | OK
11 | Ramna 11 kV Sw/S Circuit-1 |  | 11 |  | DHK00198 | 1 | 48942.9 | 50244.2 | 1301.3 | 444.44 |  | 578349.772 | 588235.7049 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 588235.7049 | 500739.7682 | 87495.9367 | 17.4733 | OK
12 | TNT RMU | D315Z | 11 |  | DHK 00207 | 1 | 63163 | 64037.1 | 874.1 | 444.44 |  | 388485.004 | 395125.5127 | Ramna |  |  |  |  | TNT RMU | 395125.5127 | 407146.495 | -12020.9823 | -2.9525 | OK
13 | DIT 11 kV Sw/S Circuit-1 |  | 11 |  | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | D315W | 11 |  | DHK 00006 | 1 | 71279 | 72394.3 | 1115.3 | 444.44 |  | 495683.932 | 504156.8291 | Ramna |  |  |  |  | Secretariat (West) | 504156.8291 | 472288.1335 | 31868.6956 | 6.7477 | OK
17 | Ramna 11 kV Sw/S Circuit-2 |  | 11 |  | DHK00197 | 1 | 89195.8 | 89224 | 28.2 | 444.44 |  | 12533.208 | 12747.4425 | Ramna |  |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 12747.4425 | 1125.4602 | 11621.9822 | 1032.6426 | FAULT
18 | Sayed Nazrul Islam Road | D315A | 11 |  | DHK00186 | 1 | 33393.1 | 36023.9 | 2630.8 | 444.44 |  | 1169232.752 | 1189218.8524 | Ramna |  |  |  |  | Sayed Nazrul Islam Road | 1189218.8524 | 1357169.9895 | -167951.1371 | -12.3751 | OK
19 | Gulistan Complex | D3153 | 11 |  | DHK00030 | 1 | 55912.3 | 56404.5 | 492.2 | 444.44 |  | 218753.368 | 222492.5951 | Ramna |  |  |  |  | Gulistan Complex | 222492.5951 | 223201.274 | -708.6789 | -0.31751 | OK
20 | Mohanagor Nattomanso | D3152 | 11 |  | DHK 00008 | 1 | 308.7 | 443.7 | 135 | 444.44 |  | 59999.4 | 61024.9905 | Ramna |  |  |  |  | Mohanagor Nattomanso | 61024.9905 | 71264.1421 | -10239.1516 | -14.3679 | OK
21 | DIT 11 kV Sw/S Circuit-2 |  | 11 |  | DHK00196 | 1 | 28080.3 | 29086.7 | 1006.4 | 444.44 |  | 447284.416 | 454930.0034 | Motijheel |  |  |  |  | DIT 11 kV Sw/S Circuit-2 | 454930.0034 | 443071.1857 | 11858.8177 | 2.6765 | OK
22 | Jail | B678Z | 11 |  | DHK00009 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | D315K | 11 |  | HA021100713-02 | 1 | 76948472 | 77199099 | 250627 | 1 |  | 250627 | 254911.0541 | Ramna |  |  |  |  | Kosturi Bazar | 254911.0541 | 109455.5914 | 145455.4627 | 132.8899 | FAULT
24 | Kaptan Bazar | B124K | 11 |  | HA021101251-02 | 1 | 7518514 | 7930785 | 412271 | 1 |  | 412271 | 419318.091 | Narinda |  |  |  |  | Kaptan Bazar | 419318.091 | 424171.1844 | -4853.0934 | -1.1441 | OK
25 | G.T.V | D315G | 11 |  | HA-021101054-02 | 1 | 72973784 | 73543399 | 569615 | 1 |  | 569615 | 579351.6265 | Ramna |  |  |  |  | G.T.V | 579351.6265 | 620088.9847 | -40737.3583 | -6.5696 | OK
26 | Kazi Alauddin Road | B615K | 11 |  | HA021100951-02 | 1 | 7403768 | 7837719 | 433951 | 1 |  | 433951 | 441368.6747 | Bangshal |  |  |  |  | Kazi Alauddin Road | 441368.6747 | 366764.7103 | 74603.9645 | 20.3411 | OK
28 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.4 |  | 2436 | 1 | 67423 | 67703 | 280 | 10 |  | 2800 | 2847.8614 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 2847.8614 | 0 | 2847.8614 | #DIV/0! | #DIV/0!
29 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.4 |  | 2437 | 1 | 89514 | 90000 | 486 | 10 |  | 4860 | 4943.0737 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 4943.0737 | 3443.9428 | 1499.1309 | 43.5295 | FAULT
|  |  | 10: Grand Total | 9090800 | 8938019.34 | 9090800 | 1.7093
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 5920520.7596
[6 empty] | Lalbag | at 33 KV level |  | 0
[6 empty] | Bangshal | at 33 KV level |  | 2296031.146
[6 empty] | Motijheel | at 33 KV level |  | 454930.0034
[6 empty] | Narinda | at 33 KV level |  | 419318.091
[6 empty] | Total = |  |  | 9090800 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 |  | 33 | 0 | BD001825 | 1 | 870.12 | 890.27 | 20.15 | 240000 | 0 | 4836000 | 4855588.7213
16 | Kakrail Circuit-2 |  | 33 |  | BD001821 | 1 | 1656.79 | 1676.76 | 19.97 | 240000 | 0 | 4792800 | 4812213.7352
|  |  | 10: Total | 0 | 9628800 | 9667802.4565
ULLON 33 KV SIDE
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9123 | 1163.9124 | 0.0001 | 240000 | 0 | 24 | 24.0031
|  |  | 10: Total | 0 | 24 | 24.0031
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder.(import) |  | 33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
| KAKRAIL 33 KV SIDE (RECEIVING) | [10 empty] | 9628824 | 9667826.4596
5 | 33 kV Dhanmondi-2 |  | 33 |  | 06604376 | 1 | 5344.05 | 5370.95 | 26.9 | 180000 | 4842000
2 | 33 kV Dhanmondi-1 |  | 33 |  | 06604375 | 1 | 2096.54 | 2115.36 | 18.82 | 180000 | 3387600
| 33 KV Kakrail From ULLON |  | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola |  | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
|  |  | 10: Total | 8229600
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 4: 9667802.4565; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KAKRAIL 33 KV NET IMPORT |  | 9667826.4596
| ULLON 33 KV SIDE |  | 4: 24.0031; 6: KAKRAIL 33 KV NET IMPORT; 9=8-7: 9667826.4596 | KAKRAIL KV NET IMPORT |  | 9605334.534
| Taltola 33 KV SIDE |  | 4: 0 | LOSS UNITS=> |  | 62491.9256
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.6464%
| TOTAL IMPORT |  | 4: 9667826.4596
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK00017 | 1 | 20156.7 | 20700.9 | 544.2 | 8888.89 | 4837333.938 |  | 4868805.4408
15 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK00018 | 1 | 6876.6 | 7413 | 536.4 | 8888.89 | 4768000.596 |  | 4799021.0188
|  |  | 7: 0; 8: 0; 10: Total | 9605334.534 |  | 9667826.4596
| KAKRAIL 11 KV SIDE |  | 7: 0; 8: 0
7 | Pioneer | D304P | 11 |  | 06604395 | 1 | 24062.02 | 24160.1 | 98.08 | 8000 |  | 784640 | 784360.9682 | Ramna |  |  |  |  | Pioneer | 784360.9682 | 828175.4667 | -43814.4985 | -5.2905 | OK
8 | Pir Saheber Goli | D604L | 11 |  | DHK-00102 | 1 | 89807.9 | 92942.8 | 3134.9 | 444.444 |  | 1393287.4956 | 1392792.0181 | Rajarbag |  |  |  |  | Pir Saheber Goli | 1392792.0181 | 1485476.6819 | -92684.6638 | -6.2394 | OK
9 | Montri Para | C604B | 11 |  | DHK-00110 | 1 | 12875.3 | 12950.5 | 75.2 | 2222.22 |  | 167110.944 | 167051.5164 | Kakrail |  |  |  |  | Montri Para | 167051.5164 | 197223.0332 | -30171.5168 | -15.2982 | OK
10 | Baily Road 11 kV Sw/S-2 |  | 11 |  | 9119865 | 1 | 70152.8 | 72383.6 | 2230.8 | 1000 |  | 2230800 | 2230006.6883 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-2 | 2230006.6883 | 2380457.3749 | -150450.6866 | -6.3202 | OK
11 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | D3046 | 11 |  | 1025651 | 1 | 29759.6 | 30010.8 | 251.2 | 1000 |  | 251200 | 251110.6689 | Ramna |  |  |  |  | High Court | 251110.6689 | 202322.6667 | 48788.0021 | 24.114 | OK
13 | Secretaiat |  | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | D604N | 11 |  | 06604402 | 1 | 5747.72 | 5783.83 | 36.11 | 40000 |  | 1444400 | 1443886.346 | Rajarbag |  |  |  |  | Shanti Nagar Bazar | 1443886.346 | 1590213.609 | -146327.263 | -9.2017 | OK
17 | Tottho Bhovon |  | 11 |  | 9119867 | 1 | 32771.1 | 32987.8 | 216.7 | 1000 |  | 216700 | 216622.9377 | Kakrail |  |  |  |  | Tottho Bhovon | 216622.9377 | 242037.4816 | -25414.544 | -10.5003 | OK
18 | Central Police Hospital/ PNT (Circuit House) |  | 11 |  | DHK00199 | 1 | 79303.3 | 79591.4 | 288.1 | 2222.22 |  | 640221.582 | 639993.908 | Kakrail |  |  |  |  | Central Police Hospital/ PNT (Circuit House) | 639993.908 | 715946.6275 | -75952.7196 | -10.6087 | OK
19 | Baily Road 11 kV Sw/S-1 |  | 11 |  | DHK00027 | 1 | 56972.7 | 57453.2 | 480.5 | 2222.22 |  | 1067776.71 | 1067396.9898 | Kakrail |  |  |  |  | Baily Road 11 kV Sw/S-1 | 1067396.9898 | 1227916.0084 | -160519.0185 | -13.0725 | OK
20 | Bijoy Nagar | D304B | 11 |  | D1025656 | 1 | 68966.3 | 69884.3 | 918 | 1000 |  | 918000 | 917673.5431 | Ramna |  |  |  |  | Bijoy Nagar | 917673.5431 | 1028330.0287 | -110656.4857 | -10.7608 | OK
21 | Shilpakala Academy | D304F | 11 |  | D0086137 | 1 | 26942.9 | 27376 | 433.1 | 1000 |  | 433100 | 432945.982 | Ramna |  |  |  |  | Shilpakala Academy | 432945.982 | 472221.3068 | -39275.3248 | -8.3171 | OK
22 | Judges Complex | C604JC | 11 |  | 06604344 | 1 | 681.42 | 684.38 | 2.96 | 40000 |  | 118400 | 118357.8949 | Kakrail |  |  |  |  | Judges Complex | 118357.8949 | 136165.0797 | -17807.1848 | -13.0776 | OK
23 | Auxiliary Transformer, AT-1 |  | 11 |  | 39333 | 1 | 492441 | 496195 | 3754 | 1 |  | 3754 | 3752.665 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-1 | 3752.665 | 0 | 3752.665 | #DIV/0! | #DIV/0!
24 | Auxiliary Transformer, AT-2 |  | 11 |  | 39254 | 1 | 1226887 | 1228762 | 1875 | 1 |  | 1875 | 1874.3332 | Kakrail |  |  |  |  | Auxiliary Transformer, AT-2 | 1874.3332 | 6333.0946 | -4458.7614 | -70.4041 | CHECK
|  |  | 10: Grand Total | 9667826.4596 | 9671265.7316 | 9667826.4596 | -0.035562
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2386091.1622
[6 empty] | Rajarbag | at 33 KV level |  | 2836678.3641
[6 empty] | Kakrail | at 33 KV level |  | 4445056.9333
[6 empty] | Total = |  |  | 9667826.4596 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 |  | 33 | 0 | BD001920 | 1 | 740.94 | 755.4 | 14.46 | 240000 | 0 | 3470400 | 3484457.2164
22 | BSMMU Hospital Circuit-2 |  | 33 |  | BD001862 | 1 | 164.76 | 170.67 | 5.91 | 240000 | 0 | 1418400 | 1424145.3768
|  |  | 10: Total |  | 4888800 | 4908602.5932 | 0.40506
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 |  | 33 |  | BD017073 | 1 | 74998.17 | 78529.65 | 3531.48 | 1000 | 3531480
4 | 33 kV Dhanmondi Incoming Circuit-2 |  | 33 |  | BD017074 | 1 | 39473.98 | 40908.72 | 1434.74 | 1000 | 1434740
| 33 KV Ullon-1 Feeder |  | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 4966220 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0 |  | Total
[7 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017072 | 1 | 104707.64 | 104707.64 | 0 | 888.89 |  | 0
6 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017076 | 1 | 37273.56 | 38893.33 | 1619.77 | 888.89 |  | 1439797.3553
|  |  | 10: Total |  | 1439797.3553
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4: 4908602.5932; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4908602.5932
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 4908602.5932 | 33/11 KV XF HV SIDE |  | 1439797.3553
[11 empty] | LOSS UNITS=> |  | 3468805.2379
[11 empty] | LOSS % IN => |  | 70.67%
| TOTAL IMPORT |  | 4: 4908602.5932
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD017081 | 1 | 80779.98 | 84305.1 | 3525.12 | 1000 | 3525120 |  | 3504070.0298
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD017082 | 1 | 32240.59 | 33653.56 | 1412.97 | 1000 | 1412970 |  | 1404532.5634
|  |  | 7: 0; 8: 0; 10: Total | 4938090 |  | 4908602.5932
| BSMMU HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Jamuna (F1) | C6101JG | 11 |  | BD017073 | 1 | 0.39 | 0.4073 | 0.0173 | 2000 |  | 34.6 | 34.3292 | Kakrail |  |  |  |  | 11 kV Jamuna (F1) | 34.3292 | 8.7511 | 25.5781 | 292.2837 | FAULT
9 | 11 kV Pukur Par (F2) | C6101PP | 11 |  | BD017074 | 1 | 2970.98 | 2992.52 | 21.54 | 2000 |  | 43080 | 42742.7844 | Kakrail |  |  |  |  | 11 kV Pukur Par (F2) | 42742.7844 | 43083.9288 | -341.1444 | -0.79181 | OK
10 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 |  | BD017075 | 1 | 1810.65 | 1854.6 | 43.95 | 2000 |  | 87900 | 87211.9487 | Kakrail |  |  |  |  | 11 kV BSMMU Convention center (F3) | 87211.9487 | 84458.3395 | 2753.6092 | 3.2603 | OK
11 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 |  | BD017076 | 1 | 3190.68 | 3278.62 | 87.94 | 2000 |  | 175880 | 174503.2711 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 174503.2711 | 172111.8499 | 2391.4213 | 1.3895 | OK
12 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 |  | BD017077 | 1 | 15095.74 | 15411.85 | 316.11 | 2000 |  | 632220 | 627271.1967 | Kakrail |  |  |  |  | 11 kV Holi Family Feeder (F5) | 627271.1967 | 702896.8986 | -75625.7019 | -10.7591 | OK
13 | 11 kV Navy House Feeder (F6) | C6101NH | 11 |  | BD017078 | 1 | 27279.48 | 27649.1 | 369.62 | 2000 |  | 739240 | 733453.4805 | Kakrail |  |  |  |  | 11 kV Navy House Feeder (F6) | 733453.4805 | 641089.6752 | 92363.8053 | 14.4073 | OK
14 | 11 kV Paribagh Feeder (F7) | C31016 | 11 |  | BD017079 | 1 | 33539.9 | 34271.31 | 731.41 | 2000 |  | 1462820 | 1451369.5422 | Paribag |  |  |  |  | 11 kV Paribagh Feeder (F7) | 1451369.5422 | 1603019.2834 | -151649.7412 | -9.4603 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 |  | BD017080 | 1 | 6815.21 | 7006.17 | 190.96 | 2000 |  | 381920 | 378930.46 | Paribag |  |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 378930.46 | 414273.243 | -35342.783 | -8.5313 | OK
18 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 |  | BD017083 | 1 | 2433.64 | 2501.72 | 68.08 | 2000 |  | 136160 | 135094.1858 | Paribag |  |  |  |  | 11 kV Oncology Bhaban (F9) | 135094.1858 | 140648.5745 | -5554.3887 | -3.9491 | OK
19 | Rupayan Trade Center | C6101RT | 11 |  | BD017084 | 1 | 1489.37 | 1616.91 | 127.54 | 2000 |  | 255080 | 253083.3205 | Kakrail |  |  |  |  | Rupayan Trade Center | 253083.3205 | 267336.0837 | -14252.7633 | -5.3314 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 |  | BD017085 | 1 | 2231.75 | 2282.95 | 51.2 | 2000 |  | 102400 | 101598.4476 | Kakrail |  |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 101598.4476 | 113805.0685 | -12206.6209 | -10.7259 | OK
21 | 11 kV BSMMU RMU (F12) | C3101RM | 11 |  | BD017086 | 1 | 2219.41 | 2299.99 | 80.58 | 2000 |  | 161160 | 159898.4943 | Paribag |  |  |  |  | 11 kV BSMMU RMU (F12) | 159898.4943 | 165660.4538 | -5761.9595 | -3.4782 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 |  | BD017087 | 1 | 4386.63 | 4503.32 | 116.69 | 2000 |  | 233380 | 231553.1807 | Paribag |  |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 231553.1807 | 239475.0074 | -7921.8267 | -3.308 | OK
23 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 |  | BD017088 | 1 | 1086.59 | 1117.1 | 30.51 | 2000 |  | 61020 | 60542.3562 | Paribag |  |  |  |  | 11 kV BCS Academy RMU (F14) | 60542.3562 | 62295.6571 | -1753.301 | -2.8145 | OK
24 | Spare |  | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | C310113 | 11 |  | BD017090 | 1 | 1923.81 | 2155.2 | 231.39 | 2000 |  | 462780 | 459157.5154 | Paribag |  |  |  |  | BSMMU Super Specialist Hospital RMU | 459157.5154 | 528668.5024 | -69510.9869 | -13.1483 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKD4418 | 1 | 2965 | 2965 | 0 | 100 |  | 0 | 0 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 6033.1746 | -6033.1746 | -100 | CHECK
27 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 1754.5 | 1877.04 | 122.54 | 100 |  | 12254 | 12158.0799 | Paribag |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 12158.0799 | 8446.8515 | 3711.2283 | 43.9362 | FAULT
|  |  | 10: Grand Total | 4908602.5932 | 4947328.6 | 4908602.5932 | -0.78277
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 2019898.7787
[6 empty] | Paribag | at 33 KV level |  | 2888703.8145
[6 empty] | Total = |  |  | 4908602.5932 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 |  | 132 |  | 8993518 | 1 | 1155.737 | 1173.431 | 17.694 | 960000 | 0 | 16986240
|  |  | 132 |  |  | 1 | 70.056 | 70.101 | 0.045 | 960000 | 43200 | 0
3 | Kallyanpur to Lalbagh 2 |  | 132 |  | 5014660 | 1 | 333.082 | 350.838 | 17.756 | 960000 | 0 | 17045760
|  |  | 132 |  |  | 1 | 4.361 | 4.408 | 0.047 | 960000 | 45120 | 0
7 | Keraniganj to Lalbagh-3 |  | 132 |  | 38992597 | 1 | 681.016 | 718.358 | 37.342 | 1440000 | 0 | 53772480
|  |  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 88320 | 87804480
|  |  | 10: Net Total | 87716160
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 |  | 132 | RECEIVE | 6604452 | 1 | 310213 | 326613 | 16400 | 1000 | 16400000
|  |  | 132 |  |  | 1 | 6755 | 6797 | 42 | 1000 |  | 42000
| Hasnabad (Keranigonj) |  | 132 |  |  | 1 | 4481804 | 4535442 | 53638 | 1000 | 53638000
|  |  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar |  | 132 |  |  | 1 | 7526 | 7584 | 58 | 1000 | 58000
|  |  | 132 |  |  | 1 | 585281 | 617805 | 32524 | 1000 |  | 32524000
| Kallyanpur-2 |  | 132 |  | 6604428 | 1 | 408087 | 424205 | 16118 | 1000 | 16118000
|  |  | 132 |  |  | 1 | 7111 | 7153 | 42 | 1000 |  | 42000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 86214000 | 32608000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 53606000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
6 | Kamrangirchar |  | 132 |  | SIEM491 | 1 | 7526 | 7584 | 58 | 1000 | 58000
|  |  | 132 |  | SIEM491 | 1 | 585281 | 617805 | 32524 | 1000 |  | 32524000
|  |  | 7: 0; 8: 0; 10: Total |  | 32524000
| LALBAGH 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 | NET IMPORT | SIEM494 | 1 | 2248335 | 2275159 | 26824 | 1000 |  | 26824000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | SIEM499 | 1 | 2359970 | 2386769 | 26799 | 1000 |  | 26799000
|  |  | 10: Total |  | 53623000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 87716160; 6: EXPORT TO OTHER S/S; 9=8-7: 32524000 | 132 KV NET IMPORT |  | 55192160
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 55192160 | 132/33 KV GT LV SIDE |  | 53568000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1624160
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.943%
| 132 KV TOTAL IMPORT |  | 4: 87716160
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | SIEM0517 | 1 | 2247640 | 2274394 | 26754 | 1000 | 26754000
16 | 132/33 kV GT-2 Incoming (LV) |  | 33 |  | SIEM0518 | 1 | 2334013 | 2360827 | 26814 | 1000 | 26814000
|  |  | 7: 0; 8: 0; 10: Total | 53568000 |  | 0
| LALBAGH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SIEM0502 | 1 | 850281 | 856934 | 6653 | 2000 |  | 13306000 | 13325783.2033 |  | 26935988.6545 | Lalbagh New 33/11 kv ss | 1.5455 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 13325783.2033 | 12549533.5387 | 776249.6646 | 6.1855 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SIEM0501 | 1 | 843964 | 850759 | 6795 | 2000 |  | 13590000 | 13610205.4512 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 13610205.4512 | 12888927.2286 | 721278.2226 | 5.5961 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 26896000 | 26935988.6545 | [5 empty] | 33 KV Feeders | 26935988.6545 | 25438460.7673 | 1497527.8872 | 5.8869 | OK
9 | Spare |  | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 8088007.3012 | Mitford 33/11 kv ss | 1.2474 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 |  | 33 |  | SIEM0513 | 1 | 324976 | 327222 | 2246 | 2000 |  | 4492000 | 4498678.6524 | [5 empty] | Mitford Circuit-1 | 4498678.6524 | 5064798.1413 | -566119.4888 | -11.1775 | OK
12 | Azimpur Circuit-1 |  | 33 |  | SIEM0503 | 1 | 74385 | 74595 | 210 | 2000 |  | 420000 | 420624.451 |  | 7372945.7345 | Azimpur 33/11 kv ss | 1.1357 |  | Azimpur Circuit-1 | 420624.451 | 7512850.8511 | -7092226.4 | -94.4013 | CHECK
15 | Azimpur Circuit-2 |  | 33 |  | SIEM0507 | 1 | 86603 | 90074 | 3471 | 2000 |  | 6942000 | 6952321.2835 | [5 empty] | Azimpur Circuit-2 | 6952321.2835 | 3140897.8164 | 3811423.4671 | 121.3482 | FAULT
17 | Lalbagh old |  | 33 |  | SIEM0509 | 1 | 234031 | 239469 | 5438 | 2000 |  | 10876000 | 10892170.3081 |  | 10892170.3081 | Lalbagh old 33/11 kv ss | 0.16255 |  | Lalbagh old | 10892170.3081 | 11473113.3152 | -580943.0071 | -5.0635 | OK
18 | Mitford Circuit-2 |  | 33 |  | SIEM0511 | 1 | 361287 | 363079 | 1792 | 2000 |  | 3584000 | 3589328.6488 | [5 empty] | Mitford Circuit-2 | 3589328.6488 | 1464011.8339 | 2125316.8149 | 145.1707 | FAULT
19 | 33/0.4 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKC7982 | 1 | 7469.48 | 7561.41 | 91.93 | 120 |  | 11031.6 | 11048.0017 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-1 | 11048.0017 | 11707.2749 | -659.2732 | -5.6313 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHU02670 | 1 | 27089.5 | 27089.5 | 0 | 120 |  | 0 | 0 | [5 empty] | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 26325031.6 | 26364171.3455 | [5 empty] | 0 | 26364171.3455 | 28667379.2327 | -2303207.8872 | -8.0342 | OK
|  |  | 9=8-7: Grand Total | 53300160 | 53221031.6 | 53300160 | 0.14868
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK98833 | 1 | 601951.2 | 608591 | 6639.8 | 2000 | 13279600 |  | 13335638.1488
11 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK98832 | 1 | 598651.2 | 605422.8 | 6771.6 | 2000 | 13543200 |  | 13600350.5058
|  |  | 7: 0; 8: 0; 10: Total | 26822800 |  | 26935988.6545
| LALBAGH 11 kV SIDE |  | 7: 0; 8: 0
3 | Chata Mosjid |  | 11 |  |  | 1 | 176550.2 | 178961 | 2410.8 | 1000 |  | 2410800 | 2448059.1892 | Kamrangirchar |  | 275 |  |  | Chata Mosjid | 2448059.1892 | 2307606.3907 | 140452.7985 | 6.0865 | OK
4 | AC mosjid | A3109X | 11 |  |  | 1 | 9113.5192 | 10394.041 | 1280.5218 | 1000 |  | 1280521.8 | 1300312.4106 | Lalbag |  | 200 |  |  | AC mosjid | 1300312.4106 | 1258989.8828 | 41322.5278 | 3.2822 | OK
5 | Kazi Reaz Uddin Road | A3109K | 11 |  |  | 1 | 25413.274 | 27738.754 | 2325.48 | 1000 |  | 2325480 | 2361420.5589 | Lalbag |  | 75 |  |  | Kazi Reaz Uddin Road | 2361420.5589 | 2255488.3746 | 105932.1843 | 4.6966 | OK
6 | Nazimuddin | A3109M | 11 |  |  | 1 | 6536.8212 | 7287.9168 | 751.0956 | 1000 |  | 751095.6 | 762703.8683 | Lalbag |  | 25 |  |  | Nazimuddin | 762703.8683 | 950975.5456 | -188271.6773 | -19.7977 | OK
7 | Kamal Bagh | A3109U | 11 |  |  | 1 | 18105.986 | 20174.008 | 2068.022 | 1000 |  | 2068022 | 2099983.5161 | Lalbag |  | 225 |  |  | Kamal Bagh | 2099983.5161 | 1567737.0505 | 532246.4656 | 33.95 | OK
8 | Rahamatganj | A3109B | 11 |  |  | 1 | 15585.779 | 18036.49 | 2450.711 | 1000 |  | 2450711 | 2488587.0183 | Lalbag |  |  |  |  | Rahamatganj | 2488587.0183 | 2323808.6258 | 164778.3925 | 7.0909 | OK
9 | Water Works 11kV Sw/S-1 |  | 11 |  |  | 1 | 2538.9734 | 4448.2884 | 1909.315 | 1000 | Estimated | 1824492.6 | 1852690.3414 | Lalbag | 150 |  |  |  | Water Works 11kV Sw/S-1 | 1852690.3414 | 1787173.2312 | 65517.1102 | 3.666 | OK
12 | City Colony | A3109J | 11 |  |  | 1 | 28562.332 | 1465.432 | -27096.9 | 1000 | Meter Reset | 2166842 | 2200330.7905 | Lalbag | Reading at 11.10.23 = 29263.742 | 29263.742 |  |  | City Colony | 2200330.7905 | 2079469.3659 | 120861.4246 | 5.8121 | OK
13 | Water Works 11kV Sw/S-2 |  | 11 |  |  | 1 | 4678.0648 | 7701.988 | 3023.9232 | 1000 | Estimated | 2675922.48 | 2717279.1674 | Lalbag | 220 |  |  |  | Water Works 11kV Sw/S-2 | 2717279.1674 | 2859477.1699 | -142198.0025 | -4.9729 | OK
14 | Chun Goli | A3109H | 11 |  |  | 1 | 716.9223 | 1678.5962 | 961.6739 | 1000 |  | 961673.88 | 976536.6596 | Lalbag |  |  |  |  | Chun Goli | 976536.6596 | 927964.1813 | 48572.4783 | 5.2343 | OK
15 | Alir Ghat | A3109L | 11 |  |  | 1 | 125330.2 | 127347 | 2016.8 | 1000 |  | 2016800 | 2047969.8743 | Lalbag |  |  |  |  | Alir Ghat | 2047969.8743 | 1928133.7897 | 119836.0846 | 6.2151 | OK
16 | Club Ghat | A3109C | 11 |  |  | 1 | 21816.792 | 24630.07 | 2813.278 | 1000 |  | 2813278 | 2856757.5327 | Lalbag |  |  |  |  | Club Ghat | 2856757.5327 | 2651623.7603 | 205133.7724 | 7.7362 | OK
17 | Debidas Ghat | A3109V | 11 |  |  | 1 | 34120.9 | 1744.5846 | -32376.3154 | 1000 | Meter Reset | 2668920.6 | 2710169.0726 | Lalbag | Reading at 11.10.23 = 35045.236 | 35045.236 |  |  | Debidas Ghat | 2710169.0726 | 2405552.6316 | 304616.441 | 12.6631 | OK
18 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 26822800 | 26414559.96 | 26822800 | 1.5455
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 2448059.1892
[6 empty] | Lalbag | at 33 KV level |  | 24374740.8108
[6 empty] | Total = |  |  | 26822800 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old |  | 33 | 0 | SIEM0509 | 1 | 234031 | 239469 | 5438 | 2000 | 0 | 10876000 | 10892170.3081
|  |  | 10: Total |  | 10876000 | 10892170.3081 | 0.14868
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 |  | 33 | 0 | 30799098 | 1 | 1759.82 | 1760.66 | 0.84 | 240000 | 0 | 201600 | 201073.6214
|  |  | 10: Total |  | 201600 | 201073.6214
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming |  | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 |  | 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0 | 11093243.9295
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) |  | 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 4: 10892170.3081; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALBAGH OLD 33 KV NET IMPORT |  | 11093243.9295
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 201073.6214; 6: LALBAGH OLD 33 KV NET IMPORT; 9=8-7: 11093243.9295 | 33 KV TX HV SIDE |  | 11093243.9295
[11 empty] | LOSS UNITS=> |  | 0
[11 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 11093243.9295
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [5 empty] | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) |  | 11 |  | 8838010 | 1 | 87603.8 | 88171.7 | 567.9 | 1000 | 567900 |  | 1435262.073
27 | 33/11 kV T1 Incoming (LV) |  | 11 |  | 06604426 | 1 | 36137.5 | 36285.09 | 147.59 | 16000 | 2361440 |  | 5968102.2534
28 | 33/11 kV T2 Incoming (LV) |  | 11 |  |  | 1 | 607657 | 609117 | 1460 | 1000 | 1460000 |  | 3689879.6031
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 4389340 |  | 11093243.9295
| LALBAGH OLD 11 KV SIDE |  | 7: 0; 8: 0
15 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 110 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | A319R | 11 |  | 8838019 | 1 | 82662.7 | 83080.1 | 417.4 | 1000 | Estimated | 2797555.32 | 2802102.8851 | Lalbag | 225 | 90 |  |  | Sowari Ghat | 2802102.8851 | 2638720.3862 | 163382.4989 | 6.1917 | OK
17 | Novo Kumar (Kara Odidoptor) | A3202 | 11 |  | 8838014 | 1 | 82451 | 82569.1 | 118.1 | 1000 | Estimated | 621678.96 | 622689.53 | Lalbag | 50 |  |  |  | Novo Kumar (Kara Odidoptor) | 622689.53 | 658473.4491 | -35783.9191 | -5.4344 | OK
19 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 20 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 6.6667 |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | A320A | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1367693.712 | 1369916.966 | Lalbag | 110 | 96.6667 |  |  | Eidgah | 1369916.966 | 1376808.1209 | -6891.1548 | -0.50052 | OK
23 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | A3201 | 11 |  |  | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 2238044.256 | 2241682.3081 | Lalbag | 180 |  |  |  | Modumoti | 2241682.3081 | 1975420.3474 | 266261.9607 | 13.4787 | OK
25 | Lalbagh O/H | A320Y | 11 |  | 61389152 | 1 | 442226 | 442711 | 485 | 1000 | Estimated | 1119022.128 | 1120841.154 | Lalbag | 90 |  |  |  | Lalbagh O/H | 1120841.154 | 1197224.4529 | -76383.2989 | -6.38 | OK
26 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | A320G | 11 |  | 61389109 | 1 | 403760 | 404617 | 857 | 1000 |  | 857000 | 858393.0961 | Lalbag |  |  |  |  | Water Works 11 kV Sw/S-2 | 858393.0961 | 972107.7743 | -113714.6782 | -11.6977 | OK
31 | Islambagh | A320D | 11 |  | 61389186 | 1 | 501801 | 502493 | 692 | 1000 |  | 692000 | 693124.8804 | Lalbag |  |  |  |  | Islambagh | 693124.8804 | 855693.6396 | -162568.7592 | -18.9985 | OK
32 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | A320F | 11 |  | 61389202 | 1 | 15646 | 15689 | 43 | 1000 |  | 43000 | 43069.8986 | Lalbag |  |  |  |  | WASA Low Lift Pump | 43069.8986 | 55719.5858 | -12649.6872 | -22.7024 | OK
34 | Shahi Mosjid | D920M | 11 |  | 06604459 | 1 | 36252.8 | 36418.54 | 165.74 | 8000 |  | 1325920 | 1328075.3488 | Azimpur |  |  |  |  | Shahi Mosjid | 1328075.3488 | 1734152.7099 | -406077.3611 | -23.4165 | OK
35 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer |  | 0.415 |  | 5395822 | 1 | 47309.6 | 60635.8 | 13326.2 | 1 |  | 13326.2 | 13347.8624 | Lalbag |  |  |  |  | 33/0.4 kV Auxiliary Transformer | 13347.8624 | 8792.8491 | 4555.0133 | 51.8036 | FAULT
|  |  | 7: 4391673; 8: 4391673; 10: Grand Total | 11093243.9295 | 11075240.576 | 11093243.9295 | 0.16255
33/0.4 kV Auxiliary Transformer meter change at 30 April 2023
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Lalbag | at 33 KV level |  | 9765168.5807
[6 empty] | Azimpur | at 33 KV level |  | 1328075.3488
[6 empty] | Total = |  |  | 11093243.9295 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 |  | 33 | 0 | SIEM0513 | 1 | 324976 | 327222 | 2246 | 2000 | 0 | 4492000 | 4498678.6524
18 | Mitford Circuit-2 |  | 33 | 0 | SIEM0511 | 1 | 361287 | 363079 | 1792 | 2000 | 0 | 3584000 | 3589328.6488
|  |  | 10: Total | 0 | 8076000 | 8088007.3012
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 1251.66 | 1260.55 | 8.89 | 540000 |  | 4800600
| Lalbagh Circuit-2 |  | 33 |  | DHK68131 | 1 | 1301.74 | 1307.9 | 6.16 | 540000 |  | 3326400
|  |  | 7: 0; 8: 0; 10: Total |  | 8127000
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
1 | Kumartuly Circuit-1 |  | 33 |  | DHK-66493 | 1 | 1290134 | 1291902 | 1768 | 180 |  | 318600 |  |  | From Kumertully End
6 | Kumartuly Circuit-2 |  | 33 |  | DHK-60914 | 1.1 | 774406 | 776528.4 | 2122.4 | 180 |  | 421740 |  |  | From Kumertully End
|  |  | 7: 0; 8: 0; 10: Total |  | 740340
[7 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-66494 | 1 | 2949259 | 2992345 | 43086 | 180 | From Downstream | 4716900
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHKA-2193 | 1 | 614.716 | 636.7265 | 22.0105 | 180000 |  | 3961884.6
|  |  | 10: Total |  | 8678784.6
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 4: 8088007.3012; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8828347.3012
| IMPORT-2 |  | 4: 740340; 6: 33 KV NET IMPORT; 9=8-7: 8828347.3012 | 33 KV TX HV SIDE |  | 8678784.6
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 149562.7012
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.694%
| TOTAL IMPORT |  | 4: 8828347.3012
11 KV SIDE of___MIDFORT 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) |  | 11 |  | DHK-66484 | 1 | 2812094 | 2838299 | 26205 | 180 | 4716900 |  | 4802516.8361
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK-66476 | 1 | 2097772 | 2119739 | 21967 | 180 | 3954060 |  | 4025830.4651
|  |  | 7: 0; 8: 0; 10: Total | 8670960 |  | 8828347.3012
| MIDFORT 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | A319Z | 11 |  | DHK-60904 | 1 | 988642.8 | 997275.1 | 8632.3 | 60 |  | 517938 | 524398.7147 | Lalbag |  |  |  |  | Chawk Bazar | 524398.7147 | 501841.8638 | 22556.8508 | 4.4948 | OK
10 | Spare |  | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | B688D | 11 |  | DHK-66485 | 1 | 857675 | 863260 | 5585 | 60 |  | 335100 | 339280.009 | Bangshal |  |  |  |  | Chatrabas | 339280.009 | 1110389.3159 | -771109.3069 | -69.445 | CHECK
12 | Begum Bazar | B678G | 11 |  | DHK-66481 | 1 | 3748981 | 3787572 | 38591 | 60 |  | 2315460 | 2344342.8516 | Bangshal |  |  |  |  | Begum Bazar | 2344342.8516 | 2422961.4211 | -78618.5695 | -3.2447 | OK
13 | SCC ROAD | B688R | 11 |  | DHK-60901 | 1 | 130309.7 | 157171.5 | 26861.8 | 60 |  | 1611708 | 1631812.3089 | Bangshal |  |  |  |  | SCC ROAD | 1631812.3089 | 1626362.4279 | 5449.8809 | 0.3351 | OK
16 | Spare |  | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | B619A | 11 |  | DHK-61104 | 1 | 717808.9 | 733048.2 | 15239.3 | 60 |  | 914358 | 925763.6241 | Bangshal |  |  |  |  | Armanitola | 925763.6241 | 975265.6139 | -49501.9897 | -5.0757 | OK
18 | Mitford Hospital (RMU) |  | 11 |  | DHK-61101 | 1 | 410380.5 | 418515.6 | 8135.1 | 60 |  | 488106 | 494194.5928 | Bangshal |  |  |  |  | Mitford Hospital (RMU) | 494194.5928 | 534862.6587 | -40668.0658 | -7.6035 | OK
19 | Emamganj | B688I | 11 |  | DHK-68130 | 1 | 1459.36 | 1478.28 | 18.92 | 60000 |  | 1135200 | 1149360.3885 | Bangshal |  |  |  |  | Emamganj | 1149360.3885 | 350737.4618 | 798622.9267 | 227.6982 | FAULT
20 | Kamal Dho Road | A319T | 11 |  | DHK-68129 | 1 | 1226.82 | 1226.82 | 0 | 60000 |  | 0 | 0 | Lalbag |  |  |  |  | Kamal Dho Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | Spare |  | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | B688P | 11 |  | DHK-68127 | 1 | 1573.97 | 1597.26 | 23.29 | 60000 |  | 1397400 | 1414831.0491 | Bangshal |  |  |  |  | Panghat | 1414831.0491 | 1293419.2063 | 121411.8427 | 9.3869 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | U0004460 | 1 | 5674.73 | 5717.83 | 43.1 | 100 |  | 4310 | 4363.7626 | Bangshal |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4363.7626 | 4064.0057 | 299.7568 | 7.3759 | OK
|  |  | 10: Grand Total | 8828347.3012 | 8719580 | 8828347.3012 | 1.2474
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 8303948.5866
[6 empty] | Lalbag | at 33 KV level |  | 524398.7147
[6 empty] | Total = |  |  | 8828347.3012 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 |  | 33 | 0 | SIEM0503 | 1 | 74385 | 74595 | 210 | 2000 | 0 | 420000 | 420624.451
15 | Azimpur Circuit-2 |  | 33 | 0 | SIEM0507 | 1 | 86603 | 90074 | 3471 | 2000 | 0 | 6942000 | 6952321.2835
|  |  | 10: Total | 0 | 7362000 | 7372945.7345
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 |  | 33 | 0 | BD001822 | 1 | 2023.72 | 2057.42 | 33.7 | 240000 | 0 | 8088000 | 8120761.2858
20 | Azimpur Circuit-2 |  | 33 | 0 | BD001857 | 1 | 1865.27 | 1867.53 | 2.26 | 240000 | 0 | 542400 | 544597.0477
|  |  | 10: Total | 0 | 8630400 | 8665358.3334
|  |  | 10: GRAND TOTAL |  | 15992400 | 16038304.0679
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 |  | 33 | RECEIVE | DHK60891 | 1 | 825685 | 828004 | 2319 | 180 |  | 417420
| Dhanmondi Circuit-1 |  | 33 |  | DHK68131 | 1 | 1205797 | 1220950 | 15153 | 540 |  | 8182620
| Dhanmondi Circuit-2 |  | 33 |  |  | 1 | 160277 | 161289 | 1012 | 540 |  | 546480
| Lalbagh Circuit-2 |  | 33 |  | DHK68132 | 1 | 960963 | 999490 | 38527 | 180 |  | 6934860
|  |  | 7: 0; 8: 0; 10: Total |  | 16081380 | #REF!
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
| Feeder No.2 |  | 3: 33; 6: 1; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  | 7: 0; 8: 0
2 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK61094 | 1 | 389714 | 437555 | 47841 | 180 |  | 8611380
4 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK60919 | 1 | 501565 | 543166 | 41601 | 180 |  | 7488180
|  |  | 10: Total |  | 16099560 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 4: 7372945.7345; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | AZIMPUR 33 KV NET IMPORT |  | 16038304.0679
| DHANMONDI 33 kV SIDE |  | 4: 8665358.3334; 6: AZIMPUR 33 KV NET IMPORT; 9=8-7: 16038304.0679 | 33 KV TX HV SIDE |  | 16099560
[11 empty] | LOSS UNITS=> |  | -61255.9321
[11 empty] | LOSS % IN => |  | -0.3819%
| TOTAL IMPORT |  | 4: 16038304.0679
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) |  | 11 |  | DHK60909 | 1 | 389714 | 440607 | 50893 | 180 | 9160740 |  | 8811233.3102
15 | 33/11 kV T2 Incoming (LV) |  | 11 |  | DHK60902 | 1 | 517275 | 559018 | 41743 | 180 | 7513740 |  | 7227070.7577
|  |  | 7: 0; 8: 0; 10: Total | 16674480 |  | 16038304.0679
| AZIMPUR 11 KV SIDE |  | 7: 0; 8: 0
7 | Chadni chwok |  | 11 |  | DHK60916 | 1 | 433697 | 444571 | 10874 | 60 |  | 652440 | 659849.4891 | Paribag |  |  |  |  | Chadni chwok | 659849.4891 | 735121.5421 | -75272.053 | -10.2394 | OK
8 | BGB |  | 11 |  | DHK61090 | 1 | 702252 | 714040 | 11788 | 60 |  | 707280 | 715312.2841 | Jigatola |  |  |  |  | BGB | 715312.2841 | 771727.6444 | -56415.3603 | -7.3103 | OK
9 | Pari Bibi Mazar | D920P | 11 |  | DHK61091 | 1 | 852708 | 888592 | 35884 | 60 |  | 2153040 | 2177491.1776 | Azimpur |  |  |  |  | Pari Bibi Mazar | 2177491.1776 | 2180695.2965 | -3204.1189 | -0.14693 | OK
10 | Azimpur | D901P | 11 |  | DHK61086 | 1 | 339578 | 356695 | 17117 | 60 |  | 1027020 | 1038683.4379 | Azimpur |  |  |  |  | Azimpur | 1038683.4379 | 1153765.578 | -115082.14 | -9.9745 | OK
11 | Aazd | D901Z | 11 |  | DHK61089 | 1 | 26709 | 47477 | 20768 | 60 |  | 1246080 | 1260231.211 | Azimpur |  |  |  |  | Aazd | 1260231.211 | 1354793.0694 | -94561.8583 | -6.9798 | OK
12 | Dayra Sharif | D966D | 11 |  | DHK61088 | 1 | 549813 | 566604 | 16791 | 60 |  | 1007460 | 1018901.3032 | Azimpur |  |  |  |  | Dayra Sharif | 1018901.3032 | 1035744.5659 | -16843.2628 | -1.6262 | OK
13 | Naya palton | D966U | 11 |  | DHK86065 | 1 | 1957.04 | 1983.32 | 26.28 | 60000 |  | 1576800 | 1594707.0602 | Azimpur |  |  |  |  | Naya palton | 1594707.0602 | 1776436.6019 | -181729.5417 | -10.23 | OK
16 | Viqarunnisa Noon School | D966V | 11 |  | DHK66477 | 1 | 1657953 | 1680319 | 22366 | 60 |  | 1341960 | 1357200.0802 | Azimpur |  |  |  |  | Viqarunnisa Noon School | 1357200.0802 | 1489035.8491 | -131835.7689 | -8.8538 | OK
17 | Subal Das Lane | D966W | 11 |  | DHK66480 | 1 | 4056431 | 4079743 | 23312 | 60 |  | 1398720 | 1414604.6799 | Azimpur |  |  |  |  | Subal Das Lane | 1414604.6799 | 1497238.5543 | -82633.8744 | -5.5191 | OK
18 | Lalbagh | D920L | 11 |  | DHK61093 | 1 | 806952 | 844380 | 37428 | 60 |  | 2245680 | 2271183.2515 | Azimpur |  |  |  |  | Lalbagh | 2271183.2515 | 2469993.6901 | -198810.4386 | -8.049 | OK
19 | Zahrul Haque Hall | D366J | 11 |  | DHK66497 | 1 | 1263879 | 1273675 | 9796 | 60 |  | 587760 | 594434.9453 | Ramna |  |  |  |  | Zahrul Haque Hall | 594434.9453 | 771237.9306 | -176802.9854 | -22.9246 | OK
20 | Eden College | D966E | 11 |  | DHK60917 | 1 | 949453 | 957512 | 8059 | 60 |  | 483540 | 489031.3622 | Azimpur |  |  |  |  | Eden College | 489031.3622 | 487693.6736 | 1337.6886 | 0.27429 | OK
21 | Nilkhet/ PWD-01 | D902N | 11 |  | DHK60918 | 1 | 500487 | 510949 | 10462 | 60 |  | 627720 | 634848.7543 | Azimpur |  |  |  |  | Nilkhet/ PWD-01 | 634848.7543 | 693863.1593 | -59014.405 | -8.5052 | OK
22 | BUET | D366BU | 11 |  | DHK66496 | 1 | 995361 | 1008669 | 13308 | 60 |  | 798480 | 807548.0045 | Ramna |  |  |  |  | BUET | 807548.0045 | 1180516.1912 | -372968.1867 | -31.5937 | OK
23 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIG2780 | 1 | 397640 | 401869 | 4229 | 1 |  | 4229 | 4277.027 | Azimpur |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4277.027 | 4444.1522 | -167.1252 | -3.7606 | OK
|  |  | 10: Grand Total | 16038304.0679 | 15858209 | 16038304.0679 | 1.1357
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 659849.4891
[6 empty] | Jigatola | at 33 KV level |  | 715312.2841
[6 empty] | Azimpur | at 33 KV level |  | 13261159.345
[6 empty] | Ramna | at 33 KV level |  | 1401982.9497
[6 empty] | Total = |  |  | 16038304.0679 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar |  | 132 |  | 38992596 | 1 | 956.211 | 991.183 | 34.972 | 1440000 | 0 | 50359680
|  |  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 50359680
|  |  | 10: Net Total | 50359680
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj |  | 132 | RECEIVE |  | 1 | 5795.85 | 5848.3 | 52.45 | 960000 | 50352000
|  |  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh |  | 132 |  |  | 1 | 3118.62 | 3152.31 | 33.69 | 960000 | 32342400
|  |  | 132 |  |  | 1 | 7.78 | 7.84 | 0.06 | 960000 |  | 57600
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 82694400 | 57600
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 82636800
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
5 | 132 kV Jigatola-1 |  | 132 |  | 42003953362 | 1 | 243.54 | 261 | 17.46 | 1440000 |  | 25142400
6 | 132 kV Jigatola-2 |  | 132 |  | 42003953364 | 1 | 238.13 | 255.14 | 17.01 | 1440000 |  | 24494400
|  |  | 7: 0; 8: 0; 10: Total |  | 49636800
| KAMRANGIRCHAR 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) |  | 132 |  | 30799138 | 1 | 3408.21 | 3419.21 | 11 | 960000 |  | 10560000
2 | 132/33 kV, 50/75 MVA GT-1 (HV) |  | 132 |  | 30799148 | 1 | 3385.78 | 3396.81 | 11.03 | 960000 |  | 10588800
7 | 132/33 kV, 50/75 MVA GT-3 (HV) |  | 132 |  | BD001910 | 1 | 1187.51 | 1199.08 | 11.57 | 960000 |  | 11107200
|  |  | 10: Total |  | 32256000 | 81892800
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 4: 50359680; 6: EXPORT TO OTHER S/S; 9=8-7: 49636800 | 132 KV NET IMPORT |  | 33065280
| FROM LALBAGH 132/33 KV GRID |  | 4: 32342400; 6: 132 KV NET IMPORT; 9=8-7: 33065280 | 33 KV NET IMPORT |  | 32179200
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 886080
[11 empty] | LOSS % IN => |  | 2.68%
| 132 KV TOTAL IMPORT |  | 4: 82702080
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming |  | 33 |  | BD001914 | 1 | 2389.77 | 2412.91 | 23.14 | 480000 | 11107200 |  | 11413045.6325
14 | 132/33 kV GT-1 Incoming (LV) |  | 33 |  | 30799094 | 1 | 6916.49 | 6938.61 | 22.12 | 480000 | 10617600 |  | 10909964.105
19 | 132/33 kV GT-2 Incoming |  | 33 |  | 30799150 | 1 | 6816.41 | 6838.19 | 21.78 | 480000 | 10454400 |  | 10742270.2625
|  |  | 7: 0; 8: 0; 10: Total | 32179200 |  | 33065280
| KAMRANGIRCHAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) |  | 33 |  | 30799129 | 1 | 6914.16 | 6951.01 | 36.85 | 240000 |  | 8844000 | 8820908.2726 |  | 25708698.7376 | Kamrangir Char 33/11 kv ss | 1.1968 |  | 33/11 kV, 20/28 MVA T31 (HV) | 8820908.2726 | 8811584.9304 | 9323.3422 | 0.10581 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) |  | 33 |  | 30799110 | 1 | 6810.69 | 6846.9 | 36.21 | 240000 |  | 8690400 | 8667709.323 | [5 empty] | 33/11 kV, 20/28 MVA T32 (HV) | 8667709.323 | 8734035.2281 | -66325.9051 | -0.7594 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) |  | 33 |  | 30799137 | 1 | 3955.5 | 3989.84 | 34.34 | 240000 |  | 8241600 | 8220081.142 | [5 empty] | 33/11 kV, 20/28 MVA T-33 (HV) | 8220081.142 | 8993342.0453 | -773260.9033 | -8.5981 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 25776000 | 25708698.7376 | [5 empty] | 33 KV Feeders | 25708698.7376 | 26538962.2039 | -830263.4662 | -3.1285 | OK
8 | Dhaka Uddyan 2 |  | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | 1.2104 |  | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 |  | 33 |  | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 |  | 0 | 0 | [5 empty] | Dhaka Uddyan 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare Feeder -2 |  | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) |  | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 |  | 33 |  | 30799098 | 1 | 1759.82 | 1760.66 | 0.84 | 240000 |  | 201600 | 201073.6214 |  | 6451112.0203 | Kamrangir Char-2 33/11 kv ss | 0.070914 |  | Lalbagh Circuit-1 | 201073.6214 | 0 | 201073.6214 | #DIV/0! | #DIV/0!
16 | Zigatola Circuit-1 (BGB-1) |  | 33 |  | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | Check | 0 | 0 | [5 empty] | Zigatola Circuit-1 (BGB-1) | 0 | 1051767.8382 | -1051767.8382 | -100 | CHECK
17 | Spare Feeder-1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 | [5 empty] | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 |  | 33 |  | 30799147 | 1 | 1571.85 | 1597.96 | 26.11 | 240000 |  | 6266400 | 6250038.3989 |  | 19389.2421 | BGB 33/11 kv ss | 0.23578 |  | Kamrangir Char-2 | 6250038.3989 | 6754094.3897 | -504055.9909 | -7.463 | OK
22 | Zigatola Circuit-2 (BGB-2) |  | 33 |  | 30799131 | 1.35 | 1884.9 | 1884.96 | 0.06 | 240000 |  | 19440 | 19389.2421 |  |  |  |  | Grid Has No Reading | Zigatola Circuit-2 (BGB-2) | 19389.2421 | 6337143.5682 | -6317754.3261 | -99.694 | CHECK
|  |  | 10: Total |  | 6487440 | 6470501.2624 | [5 empty] | 0 | 6470501.2624 | 14143005.7961 | -7672504.5338 | -54.2495 | CHECK
|  |  | 9=8-7: Grand Total | 32179200 | 32263440 | 32179200 | -0.2611
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 8739000 |  | 8785571.2626
11 | 33/11 kV T-32 Incoming |  | 11 |  | 6604433 | 1 | 7671.63 | 7720.18 | 48.55 | 180000 | 8739000 |  | 8785571.2626
22 | 33/11 kV T-33 Incoming |  | 11 |  | DHK 95817 | 1 | 4651161 | 4696130 | 44969 | 180 | 8094420 |  | 8137556.2124
|  |  | 7: 0; 8: 0; 10: Total | 25572420 |  | 25708698.7376
| KAMRANGIRCHAR 11 kV SIDE |  | 7: 0; 8: 0
4 | Rasulpur | F120R | 11 |  | HA-021101042-02 | 1 | 94974148 | 96619539 | 1645391 | 1 |  | 1645391 | 1665082.8173 | Kamrangirchar |  | 224 |  |  | Rasulpur | 1665082.8173 | 1532049.0872 | 133033.7301 | 8.6834 | OK
5 | Bheribadh | F120B | 11 |  | HA-021101105-02 | 1 | 69430726 | 71909539 | 2478813 | 1 |  | 2478813 | 2508479.0993 | Kamrangirchar |  | 120 |  |  | Bheribadh | 2508479.0993 | 2458320.6942 | 50158.4051 | 2.0404 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 |  | 30799521 | 1 | 2647.1 | 2651.27 | 4.17 | 60000 |  | 250200 | 253194.3598 | Kamrangirchar |  | 104 |  |  | Panna Tower 11 KV Faridpur Tower Express | 253194.3598 | 408741.1592 | -155546.7994 | -38.0551 | OK
8 | Panna Battery Express | F140E | 11 |  | DHK15431 | 1 | 5316.56 | 5329.54 | 12.98 | 60000 |  | 778800 | 788120.5732 | Kamrangirchar |  | 34.6667 |  |  | Panna Battery Express | 788120.5732 | 1093857.5249 | -305736.9517 | -27.9503 | OK
9 | Eidgah | F140I | 11 |  | 30799460 | 1 | 5447.79 | 5487.62 | 39.83 | 60000 |  | 2389800 | 2418400.8037 | Kamrangirchar |  | 154.6667 |  |  | Eidgah | 2418400.8037 | 2321919.4185 | 96481.3853 | 4.1552 | OK
10 | Bot Tola Mazar | D840L | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | F140H | 11 |  | HA-021101055-02 | 1 | 5268360 | 7396376 | 2128016 | 1 |  | 2128016 | 2153483.8082 | Kamrangirchar |  |  |  |  | Huzur Para | 2153483.8082 | 1914978.8856 | 238504.9225 | 12.4547 | OK
13 | Kamrangirchar | F103K | 11 |  | HA-021101015-02 | 1 | 24970453 | 27010939 | 2040486 | 1 |  | 2040486 | 2064906.2609 | Kamrangirchar |  |  |  |  | Kamrangirchar | 2064906.2609 | 1863929.1371 | 200977.1238 | 10.7824 | OK
14 | Munshihati | F140T | 11 |  | HA-021100854-02 | 1 | 54153098 | 55432498 | 1279400 | 1 |  | 1279400 | 1294711.6864 | Kamrangirchar |  |  |  |  | Munshihati | 1294711.6864 | 1345431.4782 | -50719.7918 | -3.7698 | OK
15 | Jhawchar | F140J | 11 |  | HA-021101028-02 | 1 | 3313797 | 4801619 | 1487822 | 1 |  | 1487822 | 1505628.0528 | Kamrangirchar |  |  |  |  | Jhawchar | 1505628.0528 | 1566579.6466 | -60951.5938 | -3.8907 | OK
16 | RMU Express | F140D | 11 |  | HA-021101248-02 | 1 | 7266805 | 7971838 | 705033 | 1 |  | 705033 | 713470.7397 | Kamrangirchar |  |  |  |  | RMU Express | 713470.7397 | 717231.4507 | -3760.711 | -0.52434 | OK
17 | Koyla Ghat | F140C | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 1885309.02 | 1907872.1438 | Kamrangirchar | 150 |  |  |  | Koyla Ghat | 1907872.1438 | 2053915.4269 | -146043.2831 | -7.1105 | OK
18 | Muslimbagh | F140M | 11 |  | HA-021100908-02 | 1 | 29521497 | 31186206 | 1664709 | 1 |  | 1664709 | 1684632.0125 | Kamrangirchar |  |  |  |  | Muslimbagh | 1684632.0125 | 1681378.5129 | 3253.4997 | 0.1935 | OK
19 | Noyagaon | F140Y | 11 |  | HA-021101087-02 | 1 | 11442008 | 13945688 | 2503680 | 1 |  | 2503680 | 2533643.7042 | Kamrangirchar |  |  |  |  | Noyagaon | 2533643.7042 | 2800404.9743 | -266761.2701 | -9.5258 | OK
20 | Nurbagh | F140N | 11 |  | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2073839.922 | 2098659.3582 | Kamrangirchar | 165 |  |  |  | Nurbagh | 2098659.3582 | 2062025.6114 | 36633.7468 | 1.7766 | OK
21 | Ali Nagar | F140A | 11 |  | HA-021101022-02 | 1 | 26869929 | 29006769 | 2136840 | 1 |  | 2136840 | 2162413.4126 | Kamrangirchar |  |  |  |  | Ali Nagar | 2162413.4126 | 2438442.3104 | -276028.8978 | -11.3199 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKE6223 | 1 | 43427.32 | 43619.2 | 191.88 | 120 |  | 23025.6 | 23301.1673 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 23301.1673 | 23194.682 | 106.4853 | 0.45909 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 25776000 | 25471164.542 | 25776000 | 1.1968
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 25776000
[6 empty] | Jigatola | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 25776000 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | Check | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.9 | 1884.96 | 0.06 | 240000 | 0 | 19440 | 19389.2421
|  |  | 10: TOTAL |  | 19440 | 19389.2421
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old |  | 33 | 0 | 43998033 | 1 | 243.94 | 277.88 | 33.94 | 270000 |  | 9163800 | 9347831.3064
|  |  | 10: TOTAL |  | 9163800 | 9163800
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 |  | 33 | 0 | 0 | 1 | 79.31 | 79.33 | 0.02 | 360000 | 0 | 7200 | 7193.33
11 | BGB-2 |  | 33 | 0 | 0 | 1 | 277.92 | 299.67 | 21.75 | 360000 | 0 | 7830000 | 7822746.3835
|  |  | 10: Total | 0 | 7837200 | 7829939.7135
|  |  | 10: GRAND TOTAL |  | 17020440 | 17013128.9556
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 |  | 33 |  | 43998032 | 1 | 1047.72 | 1047.72 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old |  | 33 |  | 43998033 | 1 | 243.94 | 277.88 | 33.94 | 270000 | 9163800
| 33 kV Zigatola-1 |  | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 |  | 33 |  | 43998027 | 1 | 781.033 | 781.12 | 0.087 | 270000 | 23490
| 33 kV Zigatola-2 |  | 33 |  | 43998031 | 1 | 369.629 | 398.008 | 28.379 | 270000 | 7662330
|  |  | 7: 0; 8: 0; 10: Total | 16849620 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BGB 33 KV SIDE |  | 7: 0; 8: 0
6 | 33/11 kV T1 |  | 33 |  | 43998028 | 1 | 823.223 | 857.502 | 34.279 | 270000 |  | 9255330
9 | 33/11 kV T2 |  | 33 |  | 43998029 | 1 | 817.561 | 846.088 | 28.527 | 270000 |  | 7702290
11 | 33/11 kV T3 |  | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 16957620
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW JIGATOLA 33 KV SIDE |  | 4: 17013128.9556; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BGB 33 KV NET IMPORT |  | 17013128.9556
|  |  | 6: BGB 33 KV NET IMPORT; 9=8-7: 17013128.9556 | 33 KV TX HV SIDE |  | 16957620
[11 empty] | LOSS UNITS=> |  | 55508.9556
[11 empty] | LOSS % IN => |  | 0.3263%
| TOTAL IMPORT |  | 4: 17013128.9556
11 KV SIDE of___BGB 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming |  | 11 |  |  | 1 | 20518000 | 29743100 | 9225100 | 1 | 9225100 |  | 9251833.6956
29 | 33/11 kV T-2 Incoming |  | 11 |  |  | 1 | 18772240 | 26455760 | 7683520 | 1 | 7683520 |  | 7705786.3044
30 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 16908620 |  | 16957620
| BGB 11 KV SIDE |  | 7: 0; 8: 0
12 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | D920K | 11 |  |  | 1 | 11240690 | 12267110 | 1026420 | 1 |  | 1026420 | 1028840.1279 | Azimpur |  |  |  |  | Nababgonj Park | 1028840.1279 | 1022665.2071 | 6174.9209 | 0.60381 | OK
16 | Kholamura Ghat | F1104O | 11 |  |  | 1 | 82820712 | 85905840 | 3085128 | 1 |  | 3085128 | 3092402.2195 | Kamrangirchar |  |  |  |  | Kholamura Ghat | 3092402.2195 | 2773618.4692 | 318783.7503 | 11.4934 | OK
17 | Khalpar | F1104L | 11 |  |  | 1 | 87460992 | 89399920 | 1938928 | 1 |  | 1938928 | 1943499.6703 | Kamrangirchar |  |  |  |  | Khalpar | 1943499.6703 | 1539343.6525 | 404156.0178 | 26.2551 | OK
18 | Shahidnagar | D920S | 11 |  |  | 1 | 19879410 | 21734350 | 1854940 | 1 |  | 1854940 | 1859313.6405 | Azimpur |  |  |  |  | Shahidnagar | 1859313.6405 | 1906528.5825 | -47214.9419 | -2.4765 | OK
19 | BGB 1 No Gate | D9104G | 11 |  |  | 1 | 35499580 | 36808688 | 1309108 | 1 |  | 1309108 | 1312194.6593 | Azimpur |  |  |  |  | BGB 1 No Gate | 1312194.6593 | 1412422.3679 | -100227.7086 | -7.0962 | OK
21 | Ganaktuli | D8104J | 11 |  |  | 1 | 25294590 | 26164070 | 869480 | 1 |  | 869480 | 871530.0895 | Jigatola |  |  |  |  | Ganaktuli | 871530.0895 | 914191.5251 | -42661.4356 | -4.6666 | OK
22 | Thana |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | D8104L | 11 |  |  | 1 | 36479882 | 38561747 | 2081865 | 1 |  | 2081865 | 2086773.692 | Jigatola |  |  |  |  | Bot Tola Mazar | 2086773.692 | 2120352.147 | -33578.4551 | -1.5836 | OK
24 | Sikder Medical | D8104K | 11 |  |  | 1 | 38097980 | 39247632 | 1149652 | 1 |  | 1149652 | 1152362.6885 | Jigatola |  |  |  |  | Sikder Medical | 1152362.6885 | 1220473.4868 | -68110.7982 | -5.5807 | OK
25 | Gas Field | F1104G | 11 |  |  | 1 | 58228168 | 60444680 | 2216512 | 1 |  | 2216512 | 2221738.1672 | Kamrangirchar |  |  |  |  | Gas Field | 2221738.1672 | 2114640.3455 | 107097.8217 | 5.0646 | OK
26 | Hazaribagh | D8104H | 11 |  |  | 1 | 42939672 | 44324280 | 1384608 | 1 |  | 1384608 | 1387872.6757 | Jigatola |  |  |  |  | Hazaribagh | 1387872.6757 | 1512565.9182 | -124693.2424 | -8.2438 | OK
27 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  |  | 1 | 2240.9 | 2295.89 | 54.99 | 10 |  | 549.9 | 551.1966 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-1 | 551.1966 | 644.3721 | -93.1755 | -14.4599 | OK
32 | 11/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  |  | 1 | 1812.98 | 1866.97 | 53.99 | 10 |  | 539.9 | 541.173 | Azimpur |  |  |  |  | 11/0.4 kV Aux. Transformer AT-2 | 541.173 | 593.9263 | -52.7533 | -8.8821 | OK
|  |  | 10: Grand Total | 16957620 | 16917730.8 | 16957620 | 0.23578
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Azimpur | at 33 KV level |  | 4201440.7973
[6 empty] | Kamrangirchar | at 33 KV level |  | 7257640.057
[6 empty] | Jigatola | at 33 KV level |  | 5498539.1457
[6 empty] | Total = |  |  | 16957620 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 |  | 132 | 0 | 42003953362 | 1 | 243.54 | 261 | 17.46 | 1440000 | 0 | 25142400 | 0
6 | 132 kV Jigatola-2 |  | 132 | 0 |  | 1 | 238.13 | 255.14 | 17.01 | 1440000 | 0 | 24494400 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 49636800
|  |  | 10: Net Total | 49636800
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 |  | 132 | RECEIVE | 6604452 | 1 | 291.97 | 313.35 | 21.38 | 1200000 | 25656000
| 132 kV Kamrangirchar 2 |  | 132 |  |  | 1 | 285.65 | 306.5 | 20.85 | 1200000 | 25020000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 50676000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 50676000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| JIGATOLA 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  |  | 1 | 236.47 | 257.76 | 21.29 | 1200000 |  | 25548000
3 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  |  | 1 | 341 | 361.92 | 20.92 | 1200000 |  | 25104000
|  |  | 10: Total |  | 50652000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 49636800; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 49636800
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 49636800 | 33 KV NET IMPORT |  | 50472000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -835200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -1.683%
| 132 KV TOTAL IMPORT |  | 4: 49636800
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  |  | 1 | 391.91 | 427.26 | 35.35 | 720000 | 25452000
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  |  | 1 | 566.16 | 600.91 | 34.75 | 720000 | 25020000
|  |  | 7: 0; 8: 0; 10: Total | 50472000 |  | 0
| JIGATOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  |  | 1 | 602.45 | 626.43 | 23.98 | 240000 |  | 5755200 | 5749868.4529 |  | 18378958.17 | JIGATOLA NEW 3/11 KV SS | 0.24412 |  | 33/11 kV 28/35 MVA T-1 | 5749868.4529 | 6133728.5285 | -383860.0756 | -6.2582 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  |  | 1 | 473.51 | 505.05 | 31.54 | 240000 |  | 7569600 | 7562587.6149 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 7562587.6149 | 7690548.9489 | -127961.334 | -1.6639 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  |  | 1 | 390.2 | 411.33 | 21.13 | 240000 |  | 5071200 | 5066502.1022 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 5066502.1022 | 5649171.1712 | -582669.069 | -10.3142 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 18396000 | 18378958.17 | [5 empty] | 33 KV Feeders | 18378958.17 | 19473448.6486 | -1094490.4786 | -5.6204 | OK
2 | BGB-1 |  | 33 |  |  | 1 | 79.31 | 79.33 | 0.02 | 360000 |  | 7200 | 7193.33 |  | 7829939.7135 | BGB 33/11 kv ss | 0.23578 |  | BGB-1 | 7193.33 | 0 | 7193.33 | #DIV/0! | #DIV/0!
2 | Spair |  | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 |  | 33 |  |  | 1 | 226.65 | 243.8 | 17.15 | 360000 |  | 6174000 | 6168280.4817 | [5 empty] | Dhaka Uddyan-1 | 6168280.4817 | 7012888.2883 | -844607.8066 | -12.0437 | OK
4 | Green Road -1 |  | 33 |  |  | 1 | 23.76 | 33.92 | 10.16 | 360000 |  | 3657600 | 3654211.644 |  | 13944270.2202 | Dhaka Uddan 33/11 kv ss | 1.2104 |  | Green Road -1 | 3654211.644 | 0 | 3654211.644 | #DIV/0! | #DIV/0!
9 | Green Road -2 |  | 33 |  |  | 1 | 64.23 | 77.32 | 13.09 | 360000 |  | 4712400 | 4708034.4901 | [5 empty] | Green Road -2 | 4708034.4901 | 4857567.5676 | -149533.0774 | -3.0784 | OK
10 | Dhaka Uddyan-2 |  | 33 |  |  | 1 | 239.4 | 261.02 | 21.62 | 360000 |  | 7783200 | 7775989.7385 | [5 empty] | Dhaka Uddyan-2 | 7775989.7385 | 8513336.9369 | -737347.1985 | -8.6611 | OK
11 | BGB-2 |  | 33 |  |  | 1 | 277.92 | 299.67 | 21.75 | 360000 |  | 7830000 | 7822746.3835 |  | 1956585.7621 | Jigatla Old 33/11 kv ss | 0.10052 |  | BGB-2 | 7822746.3835 | 1176610.8108 | 6646135.5727 | 564.8542 | FAULT
12 | Jigatola Old |  | 33 |  |  | 1 | 29.02 | 34.46 | 5.44 | 360000 |  | 1958400 | 1956585.7621 | [5 empty] | Jigatola Old | 1956585.7621 | 2101347.7477 | -144761.9856 | -6.889 | OK
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 32122800 | 32093041.83 | [5 empty] | 0 | 32093041.83 | 23661751.3514 | 8431290.4786 | 35.6326 | OK
|  |  | 9=8-7: Grand Total | 50472000 | 50518800 | 50472000 | -0.092639
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 172.35 | 195.3 | 22.95 | 250000 | 5737500 |  | 5744206.5913
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 195.99 | 226.24 | 30.25 | 250000 | 7562500 |  | 7571339.8426
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 141.72 | 161.95 | 20.23 | 250000 | 5057500 |  | 5063411.7361
|  |  | 7: 0; 8: 0; 10: Total | 18357500 |  | 18378958.17
| JIGATOLA 11 kV SIDE |  | 7: 0; 8: 0
| Salek Garden |  | 11 |  | 2761 | 1 | 678.24 | 718.18 | 39.94 | 60000 |  | 2396400 | 2402250.1859 | Jigatola |  |  |  |  | Salek Garden | 2402250.1859 | 2551916.8348 | -149666.6489 | -5.8649 | OK
4 | Jigatola Local |  | 11 |  | 2850 | 1 | 529.26 | 557.19 | 27.93 | 60000 |  | 1675800 | 1679891.0289 | Jigatola |  |  |  |  | Jigatola Local | 1679891.0289 | 1793125.2848 | -113234.2559 | -6.3149 | OK
5 | Modina Rayer Bazar |  | 11 |  | 2851 | 1 | 628.51 | 628.51 | 0 | 60000 |  | 0 | 0 | Switching | Grid has No Reading |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | City College |  | 11 |  | 2784 | 1 | 568.46 | 596.23 | 27.77 | 60000 |  | 1666200 | 1670267.593 | Jigatola |  |  |  |  | City College | 1670267.593 | 1742699.2641 | -72431.6711 | -4.1563 | OK
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office |  | 11 |  | 2836 | 1 | 441.51 | 467.42 | 25.91 | 60000 |  | 1554600 | 1558395.1507 | Jigatola |  |  |  |  | Post Office | 1558395.1507 | 1658055.5864 | -99660.4358 | -6.0107 | OK
11 | Leather Institute |  | 11 |  | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 |  | 0 | 0 | Jigatola | Grid has No Reading |  |  |  | Leather Institute | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Mina Bazar |  | 11 |  | 2853 | 1 | 218 | 229 | 11 | 60000 |  | 660000 | 661611.218 | Jigatola |  |  |  |  | Mina Bazar | 661611.218 | 704163.3609 | -42552.143 | -6.0429 | OK
13 | Mitali |  | 11 |  | 2852 | 1 | 470.64 | 519.49 | 48.85 | 60000 |  | 2931000 | 2938155.2725 | Switching |  |  |  |  | Mitali | 2938155.2725 | 3066382.3082 | -128227.0358 | -4.1817 | OK
14 | Road-2 |  | 11 |  | 2839 | 1 | 702.58 | 742.81 | 40.23 | 60000 |  | 2413800 | 2419692.6635 | Jigatola |  |  |  |  | Road-2 | 2419692.6635 | 2344809.964 | 74882.6995 | 3.1936 | OK
15 | SS-2 |  | 11 |  | 2838 | 1 | 332.13 | 352.5 | 20.37 | 60000 |  | 1222200 | 1225183.6827 | Jigatola |  |  |  |  | SS-2 | 1225183.6827 | 1208423.5682 | 16760.1145 | 1.3869 | OK
16 | Spare |  | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar |  | 11 |  | 2843 | 1 | 566.17 | 596.66 | 30.49 | 60000 |  | 1829400 | 1833866.0032 | Jigatola |  |  |  |  | Bou Bazar | 1833866.0032 | 1887974.2286 | -54108.2253 | -2.8659 | OK
18 | BGB |  | 11 |  | 2764 | 1 | 194.41 | 201.95 | 7.54 | 60000 |  | 452400 | 453504.4167 | Jigatola |  |  |  |  | BGB | 453504.4167 | 461638.2136 | -8133.7969 | -1.7619 | OK
19 | Dhamondi-12 |  | 11 |  | 2763 | 1 | 461.94 | 487.48 | 25.54 | 60000 |  | 1532400 | 1536140.9551 | Dhanmondi |  |  |  |  | Dhamondi-12 | 1536140.9551 | 2054260.035 | -518119.0799 | -25.2217 | OK
|  |  | 10: Total | 18378958.17 | 18334200 | 18378958.17 | 0.24412
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Jigatola | at 33 KV level |  | 16842817.2149 | Including Switching
[6 empty] | Dhanmondi | at 33 KV level |  | 1536140.9551
[6 empty] | Total = |  |  | 18378958.17 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [14 empty] | Month October-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | 4: CF; 5: Number; 7: 2023-04-01; 8: 2023-04-01 | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar |  | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 0 | 60000 | 0 | 0 | 0 |  | 0
13 | Mitali |  | 11 | 0 | 2852 | 1 | 470.64 | 519.49 | 48.85 | 60000 | 0 | 2931000 | 2938155.2725 |  | 120
|  |  | 10: Total |  | 2931000 | 2938155.2725
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 0 | 0 | Dhanmondi | Load Zero
3 | 11 kV Madina Masjid Feeder |  | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1459594.08 | 1463157.2985 | Jigatola
3 | 11 kV Mitali |  | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1471405.92 | 1474997.974 | Jigatola | Switching Total - Madina - Rayer Bazar
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) |  | 33 | 0 | 30799088 | 1 | 5965.78 | 5965.78 | 0 | 240000 | Check | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) |  | 33 | 0 | 30799131 | 1.35 | 1884.9 | 1884.96 | 0.06 | 240000 | 0 | 19440 | 19389.2421
|  |  | 10: Total |  | 19440 | 19389.2421
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit |  | 33 | 0 | 214393/37-2711 | 1 | 26.3348 | 35.6193 | 9.2845 | 1000 | Estimated | 1566000 | 1597449.0742
|  |  | 10: Total |  | 1566000 | 1597449.0742
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  |  | 3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 3: 33; 6: 1; 9=8-7: 0 |  | 0
|  |  | 10: Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 | NET IMPORT | DHK61073 | 1 | 4033.96 | 4042.01 | 8.05 | 240000 |  | 1932000
2 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
|  |  | 10: Total |  | 1932000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 1597449.0742
| Satmasjid 33 KV SIDE |  | 4: 1597449.0742; 6: 33 KV NET IMPORT; 9=8-7: 1597449.0742 | ZIGATOLA OLD 11 KV NET IMPORT |  | 1932000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -334550.9258
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -20.94%
| TOTAL IMPORT |  | 4: 1597449.0742
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0
16 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0
17 | 33/11 kV T-1 Incoming |  | 11 |  | DHK61028 | 1.32 | 1865.57 | 1873.29 | 7.72 | 180000 | 1834272
|  |  | 7: 0; 8: 0; 10: Total | 1834272 |  | 1932000
| ZIGATOLA OLD 11 KV SIDE |  | 7: 0; 8: 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | D803D | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | D803E | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | D803I | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | D803R | 11 |  | DHK60946 | 1 | 1172.18 | 1187.02 | 14.84 | 60000 |  | 890400 | 891294.9856 | Jigatola |  |  |  |  | Simanto Square | 891294.9856 | 910570.4517 | -19275.4661 | -2.1169 | OK
12 | Post Office | D803P | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | D803S | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | D803G | 11 |  | DHK61070 | 1 | 3477.14 | 3493.18 | 16.04 | 60000 |  | 962400 | 963367.3565 | Jigatola |  |  |  |  | Green Road Via Park | 963367.3565 | 1108520.5499 | -145153.1934 | -13.0943 | OK
15 | PWD Quarters 11 kV Saleq Grand | D803A | 11 |  | DHK61028 | 1 | 3633.07 | 3634.3 | 1.23 | 60000 |  | 73800 | 73874.1801 | Jigatola |  |  |  |  | PWD Quarters 11 kV Saleq Grand | 73874.1801 | 78580.1905 | -4706.0104 | -5.9888 | OK
18 | Road No.-2 | D803T | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | D803H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | D803B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | D803C | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | D803M | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | D803Z | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 |  | 0.415 |  | 243284 | 1 | 85079 | 85276 | 197 | 10 |  | 1970 | 1971.9801 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 1971.9801 | 3959.002 | -1987.0218 | -50.19 | CHECK
25 | 33/0.4 kV Aux. Transformer AT-2 |  | 0.415 |  | 412277 | 1 | 39741 | 39890 | 149 | 10 |  | 1490 | 1491.4977 | Jigatola |  |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 1491.4977 | 769.8059 | 721.6917 | 93.7498 | FAULT
|  |  | 10: Grand Total | 1932000 | 1930060 | 1932000 | 0.10052
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Jigatola | at 33 KV level |  | 1932000
[6 empty] | Total = |  |  | 1932000 | 0
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) |  | 33 | 0 | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 |  | 33 | 0 | 0 | 1 | 226.65 | 243.8 | 17.15 | 360000 | 0 | 6174000 | 6168280.4817
10 | Dhaka Uddyan-2 |  | 33 | 0 | 0 | 1 | 239.4 | 261.02 | 21.62 | 360000 | 0 | 7783200 | 7775989.7385
|  |  | 10: Total | 0 | 13957200 | 13944270.2202
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) |  | 33 | RECEIVE | BD017107 | 1 | 90469.03 | 90469.03 | 0 | 1125 |  | 0
| 33 kV Jigatala Incoming Circuit-1 |  | 33 |  | BD017098 | 1 | 72164.29 | 77583.6 | 5419.31 | 1125 |  | 6096723.75
| 33 kV Jigatala Incoming Circuit-2 |  | 33 |  | BD017097 | 1 | 76325.53 | 83159.4 | 6833.87 | 1125 |  | 7688103.75
| 33 kV Kamrangirchar Circuit-2 (O/H) |  | 33 |  | BD017108 | 1 | 73739.05 | 73739.05 | 0 | 1125 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 13784827.5 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD017100 | 1 | 83745.19 | 89836.5 | 6091.31 | 1000 |  | 6091310
3 | 33/11 kV, 28/35 MVA T-3 (Future) |  | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD017109 | 1 | 69335.22 | 77076.6 | 7741.38 | 1000 |  | 7741380
|  |  | 10: Total |  | 13832690 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 13944270.2202
| JIGATOLA 33 KV SIDE |  | 4: 13944270.2202; 6: 33 KV NET IMPORT; 9=8-7: 13944270.2202 | 33 KV TX HV |  | 13832690
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 111580.2202
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.8002%
| TOTAL IMPORT |  | 4: 13944270.2202
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD014060 | 1 | 82684.86 | 88750.1 | 6065.24 | 1000 | 6065240 |  | 6138291.5704
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD014061 | 1 | 68649.12 | 76362.2 | 7713.08 | 1000 | 7713080 |  | 7805978.6498
|  |  | 7: 0; 8: 0; 10: Total | 13778320 |  | 13944270.2202
| DHAKA UDDYAN 11 KV SIDE |  | 7: 0; 8: 0
7 | Spare |  | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | G1103L | 11 |  | BD014031 | 1 | 49744.35 | 50107.2 | 362.85 | 1000 |  | 362850 | 367241.8104 | Adabor |  |  |  |  | D Block dhaka uddyan | 367241.8104 | 387945.2586 | -20703.4482 | -5.3367 | OK
8 | Dill Mohammad O/H | G1103DM | 11 |  | BD014027 | 1 | 21821.33 | 23726.2 | 1904.87 | 1000 |  | 1904870 | 1927925.8849 | Adabor |  |  |  |  | Dill Mohammad O/H | 1927925.8849 | 1986501.3323 | -58575.4474 | -2.9487 | OK
9 | Turag O/H | G1103U | 11 |  | BD014028 | 1 | 27579.27 | 28276.4 | 697.13 | 1000 |  | 697130 | 705567.8194 | Adabor |  |  |  |  | Turag O/H | 705567.8194 | 641819.4994 | 63748.32 | 9.9324 | OK
10 | Nabadoy O/H | G1103N | 11 |  | BD014025 | 1 | 37467.87 | 38453.6 | 985.73 | 1000 |  | 985730 | 997660.9336 | Adabor |  |  |  |  | Nabadoy O/H | 997660.9336 | 848979.0298 | 148681.9037 | 17.513 | OK
11 | Chandrima O/H | G1103CH | 11 |  | BD014024 | 1 | 6934.23 | 7893.5 | 959.27 | 1000 |  | 959270 | 970880.6709 | Adabor |  |  |  |  | Chandrima O/H | 970880.6709 | 1055645.8739 | -84765.203 | -8.0297 | OK
12 | Shyamoli Housing Project-2 | G1103SH | 11 |  | BD014029 | 1 | 29921.69 | 31072.7 | 1151.01 | 1000 |  | 1151010 | 1164941.4253 | Adabor |  |  |  |  | Shyamoli Housing Project-2 | 1164941.4253 | 2147810.8671 | -982869.4418 | -45.7615 | CHECK
13 | Spare |  | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare |  | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare |  | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | C2103U | 11 |  | BD013959 | 1 | 42134.47 | 44808.9 | 2674.43 | 1000 |  | 2674430 | 2706800.3719 | Satmasjid |  |  |  |  | U Lab | 2706800.3719 | 2673135.1804 | 33665.1914 | 1.2594 | OK
19 | Akota | G1103AK | 11 |  | BD014020 | 1 | 7179.56 | 7699.4 | 519.84 | 1000 |  | 519840 | 526131.9628 | Adabor |  |  |  |  | Akota | 526131.9628 | 548510.7365 | -22378.7737 | -4.0799 | OK
20 | Burigonga O/H | G1103BU | 11 |  | BD014019 | 1 | 5489.2 | 5871.8 | 382.6 | 1000 |  | 382600 | 387230.8575 | Adabor |  |  |  |  | Burigonga O/H | 387230.8575 | 410809.9274 | -23579.0699 | -5.7397 | OK
21 | Garden City | C2103G | 11 |  | BD014021 | 1 | 89647.99 | 92171 | 2523.01 | 1000 |  | 2523010 | 2553547.6368 | Satmasjid |  |  |  |  | Garden City | 2553547.6368 | 3028251.44 | -474703.8032 | -15.6758 | OK
22 | Avenue O/H | G1103AV | 11 |  | BD014017 | 1 | 15004.61 | 15936.5 | 931.89 | 1000 |  | 931890 | 943169.2729 | Adabor |  |  |  |  | Avenue O/H | 943169.2729 | 1027773.9029 | -84604.63 | -8.2318 | OK
23 | Chand Uddyan | C2103D | 11 |  | BD014018 | 1 | 9747.36 | 10428.5 | 681.14 | 1000 |  | 681140 | 689384.282 | Satmasjid |  |  |  |  | Chand Uddyan | 689384.282 | 764257.0863 | -74872.8043 | -9.7968 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4416 | 1 | 1851.08 | 1888.5 | 37.42 | 100 |  | 3742 | 3787.2919 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3787.2919 | 1595.7005 | 2191.5914 | 137.3435 | FAULT
25 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4412 | 1 | 283.05 | 283.05 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 3189.39 | -3189.39 | -100 | CHECK
|  |  | 10: Grand Total | 13944270.2202 | 13777512 | 13944270.2202 | 1.2104
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 7994537.9296
[6 empty] | Satmasjid | at 33 KV level |  | 5949732.2906
[6 empty] | Total = |  |  | 13944270.2202 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 |  | 33 | IMPORT | 8993 638E | 1 | 4208.156 | 4216.182 | 8.026 | 180000 | 0 | 1444680
9 | Satmosjid -2 |  | 33 |  | 8993 669E | 1 | 5898.119 | 5941.853 | 43.734 | 180000 | 0 | 7872120
13 | Lalmatia |  | 33 |  |  | 1 | 5452.879 | 5452.879 | 0 | 180000 | 0 | 0
14 | Transformer-1 |  | 33 |  | 50147586E | 1 | 3232.217 | 3275.612 | 43.395 | 750000 | 0 | 32546250
15 | Transformer-2 |  | 33 |  | 50148569E | 1 | 2873.592 | 2917.773 | 44.181 | 750000 | 0 | 33135750
|  |  | 9=8-7: Total Import/Export | 0 | 74998800
|  |  | 10: Net Total | 74998800
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | 4: RECEIVE; 6: 1; 9=8-7: 0
| 33 KV GT-2 Incomming |  | 6: 1; 9=8-7: 0
| 33 KV Satmosjid-1 Incomming |  | 6: 1; 9=8-7: 0
Total Import/Export
|  |  | 9=8-7: Net Total | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 4: EXPORT |  | 0
| Feeder No.2 | [10 empty] | 0
|  |  | 10: Total |  | 0
SATMOSJID 132 KV SIDE
|  |  | 10: Total |  | 0
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 4: 74998800; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 74998800
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 74998800 | 33 KV NET IMPORT |  | 74998800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 74998800
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming |  | 33 |  | 50147586 | 1 | 3232.217 | 3232.217 | 0 | 750000 | 0
10 | 132/33 kV, 80/120 MVA GT-2 Incoming |  | 33 |  | 50148569 | 1 | 2873.592 | 2873.592 | 0 | 750000 | 0
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 74998800
| SATMOSJID 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 |  | SICAM | 1 | 4214 | 4214 | 0 | 1000 | From Downstream | 9212400 | 9397407.3121 |  | 0.86271 | Satmasjid 3/11 kv ss | 19024333.1694 |  | 33/11 kV, 20/28 MVA T-1 (HV) | 9397407.3121 | 10529234.8089 | -1131827.4967 | -10.7494 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 |  | SICAM | 1 | 4298 | 4298 | 0 | 1000 | From Downstream | 9437400 | 9626925.8573 | [5 empty] | 33/11 kV, 20/28 MVA T-2 (HV) | 9626925.8573 | 10620185.0099 | -993259.1526 | -9.3526 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 18649800 | 19024333.1694 | [5 empty] | 33 KV Feeders | 19024333.1694 | 21149419.8188 | -2125086.6494 | -10.048 | OK
6 | BGB |  | 33 |  | 214393/40-2711 | 1 | 1804.4082 | 5807.1386 | 4002.7304 | 1000 | From Downstream | 9163800 | 9347831.3064 |  | 0.23578 | BGB 33/11 KV SS | 9347831.3064 |  | BGB | 9347831.3064 | 8815960.3974 | 531870.909 | 6.033 | OK
| Asad Gate Circuit-1 |  | 33 |  | 214393/44-2711 | 1 | 81.6289 | 89.5259 | 7.897 | 1000 | Estimated | 5302119.6 | 5408599.0077 |  | 0.85 | ASADGATE 33/11 KV SS | 13431919.1854 |  | Asad Gate Circuit-1 | 5408599.0077 | 8250388.3215 | -2841789.3138 | -34.4443 | OK
8 | Lalmatia Circuit-2 |  | 33 |  | SICAM | 1 | 30.1 | 4612 | 4581.9 | 1000 | Estimated | 13778010 | 14054705.8227 |  | 0.57703 | LALMATIA 33/11 KV SS | 14054705.8227 |  | Lalmatia Circuit-2 | 14054705.8227 | 13907422.6115 | 147283.2112 | 1.059 | OK
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 7865364.6 | 8023320.1777 |  | 0.10052 | JIGATOLA OLD 33/11 KV SS | 1597449.0742 |  | Asad Gate Circuit-2 | 8023320.1777 | 4118685.0997 | 3904635.0779 | 94.803 | FAULT
13 | Jigatola U/G Circuit |  | 33 |  | 214393/37-2711 | 1 | 26.3348 | 35.6193 | 9.2845 | 1000 | Estimated | 1566000 | 1597449.0742 |  | -0.043971 | JAPAN GARDEN 33/11 KV SS | 17542561.442 |  | Jigatola U/G Circuit | 1597449.0742 | 1521666.8245 | 75782.2496 | 4.9802 | OK
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 17197200 | 17542561.442 | [5 empty] | Japan Garden City-2 | 17542561.442 | 19492726.9266 | -1950165.4846 | -10.0046 | OK
|  |  | 10: Total |  | 54872494.2 | 55974466.8306 | [5 empty] | 0 | 55974466.8306 | 56106850.1812 | -132383.3506 | -0.23595 | OK
|  |  | 9=8-7: Grand Total | 74998800 | 73522294.2 | 74998800 | 2.0082
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming |  | 11 |  | DHK60998 | 1 | 4915.69 | 4966.87 | 51.18 | 180000 | 9212400 |  | 9397407.3121
24 | 33/11 kV T-2 Incoming |  | 11 |  | DHK61044 | 1 | 5006 | 5058.43 | 52.43 | 180000 | 9437400 |  | 9626925.8573
|  |  | 7: 0; 8: 0; 10: Total | 18649800 |  | 19024333.1694
| SATMOSJID 11 kV SIDE |  | 7: 0; 8: 0
16 | Lalmatia O/H | C209M | 11 |  | DHK61042 | 1 | 3189.06 | 3204.12 | 15.06 | 60000 |  | 903600 | 911395.4616 | Satmasjid |  |  |  |  | Lalmatia O/H | 911395.4616 | 1251951.9192 | -340556.4576 | -27.202 | OK
16 | Asad Avenue (South) | C209C | 11 |  | DHK 60999 | 1 | 2921.88 | 2936 | 14.12 | 60000 |  | 847200 | 854508.8922 | Satmasjid |  |  |  |  | Asad Avenue (South) | 854508.8922 | 1448736.6599 | -594227.7676 | -41.017 | CHECK
17 | Madrasha Road |  | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | C209H | 11 |  | DHK61002 | 1 | 2421.28 | 2441.86 | 20.58 | 60000 |  | 1234800 | 1245452.7622 | Satmasjid |  |  |  |  | Bashbari | 1245452.7622 | 1339544.3993 | -94091.6371 | -7.0242 | OK
19 | Road-27 | C209A | 11 |  | DHK61001 | 1 | 1467.19 | 1474.17 | 6.98 | 60000 |  | 418800 | 422413.036 | Satmasjid |  |  |  |  | Road-27 | 422413.036 | 1160540.6933 | -738127.6574 | -63.602 | CHECK
20 | Boishakhi O/H | D209O | 11 |  | DHK61024 | 1 | 4186.05 | 4226.72 | 40.67 | 60000 |  | 2440200 | 2461251.8872 | Dhanmondi |  |  |  |  | Boishakhi O/H | 2461251.8872 | 2676105.4034 | -214853.5162 | -8.0286 | OK
21 | Katasur O/H | C209K | 11 |  | DHK61003 | 1 | 3653.23 | 3674.52 | 21.29 | 60000 |  | 1277400 | 1288420.2773 | Satmasjid |  |  |  |  | Katasur O/H | 1288420.2773 | 1430239.6103 | -141819.3329 | -9.9158 | OK
22 | Nurjahan Road | D409I | 11 |  | DHK61000 | 1 | 1865.6 | 1885.68 | 20.08 | 60000 |  | 1204800 | 1215193.9487 | Shyamoli |  |  |  |  | Nurjahan Road | 1215193.9487 | 1433819.6844 | -218625.7356 | -15.2478 | OK
25 | polpar over head | D209W | 11 |  | DHK61003 | 1 | 1869.15 | 1902.19 | 33.04 | 60000 |  | 1982400 | 1999502.3937 | Dhanmondi |  |  |  |  | polpar over head | 1999502.3937 | 2133127.4955 | -133625.1017 | -6.2643 | OK
26 | Satmosjid Housing | C209S | 11 |  | DHK61043 | 1 | 2828.71 | 2828.71 | 0 | 60000 |  | 0 | 0 | Satmasjid | Check |  |  |  | Satmosjid Housing | 0 | 189147.2492 | -189147.2492 | -100 | CHECK
27 | Physical College | C209P | 11 |  | DHK61041 | 1 | 3350.32 | 3391.12 | 40.8 | 60000 |  | 2448000 | 2469119.1787 | Satmasjid |  |  |  |  | Physical College | 2469119.1787 | 2662381.786 | -193262.6072 | -7.259 | OK
28 | Asad Avenue (North) | D409V | 11 |  | DHK61022 | 1 | 2730.21 | 2730.21 | 0 | 60000 |  | 0 | 0 | Shyamoli | Check |  |  |  | Asad Avenue (North) | 0 | 288792.6455 | -288792.6455 | -100 | CHECK
29 | Spare Feeder |  | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | D209Z | 11 |  | DHK61023 | 1 | 1124.27 | 1148.21 | 23.94 | 60000 |  | 1436400 | 1448791.9887 | Dhanmondi |  |  |  |  | Ghraphic artch college | 1448791.9887 | 1578216.0071 | -129424.0185 | -8.2007 | OK
31 | Mohammadpur O/H | D409W | 11 |  | DHK61025 | 1 | 2215.45 | 2241.73 | 26.28 | 60000 |  | 1576800 | 1590403.2357 | Shyamoli |  |  |  |  | Mohammadpur O/H | 1590403.2357 | 1624160.2917 | -33757.056 | -2.0784 | OK
32 | Bosila Feeder | C209V | 11 |  | DHK60997 | 1 | 4147.07 | 4192.28 | 45.21 | 60000 |  | 2712600 | 2736001.9135 | Satmasjid |  |  |  |  | Bosila Feeder | 2736001.9135 | 2540659.2659 | 195342.6475 | 7.6887 | OK
33 | 11/0.4 kV Auxiliary Transformer |  | 0.415 |  | ELIB 7375 | 1 | 5971.73 | 6093.1 | 121.37 | 60 |  | 7282.2 | 7345.0244 | Satmasjid |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 7345.0244 | 8176.8893 | -831.8649 | -10.1734 | OK
|  |  | 10: Total | 18649800 | 18490282.2 | 18649800 | 0.86271
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Satmasjid | at 33 KV level |  | 9934656.5459
[6 empty] | Shyamoli | at 33 KV level |  | 2805597.1844
[6 empty] | Dhanmondi | at 33 KV level |  | 5909546.2697
[6 empty] | Total = |  |  | 18649800 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 |  | 33 |  | 38992490 (new) | 1 | 1.34 | 1.405 | 0.065 | 180000 | 0 | 11700 | 11700
| Kallyanpur to Japangarden-2 |  | 33 |  | 8993669E | 1 | 5898.119 | 5941.853 | 43.734 | 180000 | 0 | 7872120 | 7872120
14 | Japan Garden City-2 |  | 33 |  | SICAM | 1 | 41020 | 41020 | 0 | 1000 | Estimated | 17197200 | 17542561.442
|  |  | 10: Total | 0 | 25081020 | 25426381.442
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G |  | 33 | RECEIVE | DHK86051 | 1 | 3040.43 | 3050.92 | 10.49 | 270000 |  | 2832300
| kallyanpur U/G-2 |  | 33 |  | DHK61100 | 1 | 2902.98 | 2932.12 | 29.14 | 270000 |  | 7867800
|  |  | 10: Total |  | 10700100
JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Japan Genden City |  | 33 |  | DHK15681 | 1 | 606.8 | 687.9 | 81.1 | 18000 |  | 1459800 | 1459800 | Adabor | Customer Number:-27111298
[7 empty] | 0 | 0
|  |  | 10: Total |  | 1459800
JAPAN GERDEN CITY 33 KV SIDE
| 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK61080 | 1 | 4327.03 | 4370.75 | 43.72 | 180000 |  | 7869600
3 | 33/11 kV 20/28 MVA T-1 (HV) |  | 33 |  | 86052 | 1 | 5092.55 | 5196.91 | 104.36 | 180000 |  | 7867800 |  |  | Check Meter
|  |  | 10: Total |  | 15737400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 4: 17197200; 6: Adabor NOCS; 9=8-7: 1459800 | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 15737400
| IMPORT-2 |  | 6: JAPAN GERDEN CITY 33 KV NET IMPORT; 9=8-7: 15737400 | 33 KV TX HV SIDE |  | 15737400
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 17197200
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 |  | DHK61079 | 1 | 5745.13 | 5796.91 | 51.78 | 160000 | 8284800 |  | 8049813.0199
10 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK61082 | 1 | 4815.98 | 4865.43 | 49.45 | 160000 | 7912000 |  | 7687586.9801
|  |  | 7: 0; 8: 0; 10: Total | 16196800 |  | 15737400
| JAPAN GERDEN CITY 11 KV SIDE |  | 7: 0; 8: 0
5 | Dhaka Uddyan | G186D | 11 |  | DHK86067 | 1 | 3252.11 | 3252.83 | 0.72 | 60000 |  | 43200 | 43181.0046 | Adabor |  |  |  |  | Dhaka Uddyan | 43181.0046 | 44366.4049 | -1185.4003 | -2.6718 | OK
| Shia Mosjid | D409H | 11 |  | DHK60950 | 1 | 3509.16 | 3541.94 | 32.78 | 60000 |  | 1966800 | 1965935.1818 | Shyamoli |  |  |  |  | Shia Mosjid | 1965935.1818 | 2358614.0108 | -392678.829 | -16.6487 | OK
6 | Shekhar Tek | G186S | 11 |  | DHK60977 | 1 | 2414.59 | 2443.6 | 29.01 | 60000 |  | 1740600 | 1739834.6438 | Adabor |  |  |  |  | Shekhar Tek | 1739834.6438 | 2042053.7165 | -302219.0727 | -14.7998 | OK
7 | Madrasha Road | D434D | 11 |  | DHK61083 | 1 | 2033.33 | 2064.99 | 31.66 | 60000 |  | 1899600 | 1898764.7302 | Shyamoli |  |  |  |  | Madrasha Road | 1898764.7302 | 2311849.4219 | -413084.6917 | -17.8681 | OK
8 | Baitul Aman Housing | G186B | 11 |  | DHK668115 | 1 | 4165.49 | 4208.5 | 43.01 | 60000 |  | 2580600 | 2579465.2888 | Adabor |  |  |  |  | Baitul Aman Housing | 2579465.2888 | 2865829.9369 | -286364.648 | -9.9924 | OK
11 | Shyamoli Square | D486G | 11 |  | DHK86063 | 1 | 469.86 | 475.86 | 6 | 30000 |  | 180000 | 179920.8525 | Shyamoli |  |  |  |  | Shyamoli Square | 179920.8525 | 180163.5766 | -242.7241 | -0.13472 | OK
12 | Mohammadi Housing | G186E | 11 |  | DHK60948 | 1 | 3848.65 | 3873.73 | 25.08 | 60000 |  | 1504800 | 1504138.327 | Adabor |  |  |  |  | Mohammadi Housing | 1504138.327 | 1937732.7104 | -433594.3835 | -22.3764 | OK
13 | Chand Housing | C286H | 11 |  | DHK60867 | 1 | 2195.59 | 2213.38 | 17.79 | 60000 |  | 1067400 | 1066930.6554 | Satmasjid |  |  |  |  | Chand Housing | 1066930.6554 | 1224872.5023 | -157941.8469 | -12.8946 | OK
14 | PC Culture Housing |  | 11 |  | DHK60979 | 1 | 4153.53 | 4192.75 | 39.22 | 60000 |  | 2353200 | 2352165.2785 | Adabor |  |  |  |  | PC Culture Housing | 2352165.2785 | 2602029.6916 | -249864.4131 | -9.6027 | OK
15 | Mehedibagh | G186H | 11 |  | DHK68121 | 1 | 2360.8 | 2408.52 | 47.72 | 60000 |  | 2863200 | 2861941.0273 | Adabor |  |  |  |  | Mehedibagh | 2861941.0273 | 3070874.6729 | -208933.6457 | -6.8037 | OK
16 | 33/11 kV Incoming (Spare) |  | 11 |  |  | 1 | 0 | 0 | 0 | 160000 |  | 0 | 0 | Adabor |  |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer |  | 11 |  |  | 1 | 657401 | 661926 | 4525 | 1 |  | 4525 | 4523.0103 | Adabor |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 4523.0103 | 4813.3552 | -290.3449 | -6.0321 | OK
|  |  | 10: Grand Total | 16196800 | 16203925 | 16196800 | -0.043971
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Adabor | at 33 KV level |  | 11085248.5802
[6 empty] | Shyamoli | at 33 KV level |  | 4044620.7644
[6 empty] | Satmasjid | at 33 KV level |  | 1066930.6554
[6 empty] | Total = |  |  | 16196800 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | #REF! |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) |  | 132 |  | 42627810 | 1 | 192.576 | 201.909 | 9.333 | 960000 | 0 | 8959680
2 | Dhaka University-1 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) |  | 132 |  | 42627812 | 1 | 194.305 | 203.94 | 9.635 | 960000 | 0 | 9249600
3 | Dhaka University-2 (Imp) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 18209280
|  |  | 10: Net Total | 18209280
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 |  | 132 |  | 2877 | 1 | 154.13 | 161.6 | 7.47 | 1200000 |  | 8964000
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 |  | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 |  | 132 |  | 2811 | 1 | 155.44 | 163.14 | 7.7 | 1200000 |  | 9240000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 18204000
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 18204000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 KV Dhanmondi |  | 132 | 0 | SIEM0480 | 1 | 116377 | 119880 | 3503 | 1000 |  | 3503000
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 3503000
| DHAKA UNIVERSITY 132 KV SIDE |  | 7: 0; 8: 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) |  | 132 |  | 2752 | 1 | 214.11 | 220.25 | 6.14 | 1200000 |  | 7368000
4 | 132/33kV, 80/120 MVA GT-2 (HV) |  | 132 |  | 2867 | 1 | 232.16 | 238.28 | 6.12 | 1200000 |  | 7344000
|  |  | 10: Total |  | 14712000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 4: 18209280; 6: EXPORT TO OTHER S/S; 9=8-7: 3503000 | 132 KV NET IMPORT |  | 14712000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 14712000 | 33 KV NET IMPORT |  | 14594400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 117600
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.7993%
| 132 KV TOTAL IMPORT |  | 4: 18209280
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming |  | 33 |  | 2769 | 1 | 354.2 | 364.32 | 10.12 | 720000 | 7286400
7 | 132/33 kV 80/120 MVA GT-2 Incomming |  | 33 |  | 2830 | 1 | 383.48 | 393.63 | 10.15 | 720000 | 7308000
|  |  | 7: 0; 8: 0; 10: Total | 14594400 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [8 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 |  | 33 |  | 2751 | 1 | 36.62 | 38.87 | 2.25 | 240000 |  | 540000 | 540143.1709 |  | 0.063822 | DHAKA UNIVERSITY 33/11 KV SS | 2018935.1408 |  | 33/11 kV 28/35 MVA T-1 | 540143.1709 | 576273.5476 | -36130.3767 | -6.2697 | OK
8 | 33/11 kV 28/35 MVA T-2 |  | 33 |  | 4253 | 1 | 58.94 | 62.84 | 3.9 | 240000 |  | 936000 | 936248.1628 | [5 empty] | 33/11 kV 28/35 MVA T-2 | 936248.1628 | 958054.7728 | -21806.61 | -2.2761 | OK
13 | 33/11 kV 28/35 MVA T-3 |  | 33 |  | 2808 | 1 | 22.46 | 24.72 | 2.26 | 240000 |  | 542400 | 542543.8072 | [5 empty] | 33/11 kV 28/35 MVA T-3 | 542543.8072 | 388984.6446 | 153559.1626 | 39.4769 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 2018400 | 2018935.1408 | [5 empty] | 33 KV Feeders | 2018935.1408 | 1923312.965 | 95622.1758 | 4.9717 | OK
2 | Spare |  | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 |  | 33 |  | 2804 | 1.5 | 165.94 | 174.5 | 8.56 | 360000 |  | 4622400 | 4623625.5425 |  | 0.31408 | BB AVENUE 33/11 KV SS | 7147894.6276 |  | BB Avenue-1 | 4623625.5425 | 4878515.7511 | -254890.2087 | -5.2247 | OK
3 | DMC Circuit-1 |  | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 | [5 empty] | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 |  | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | 0.15826 | DMC 33/11 KV SS | 3486084.0247 |  | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 |  | 33 |  | 2753 | 1 | 421.19 | 426.46 | 5.27 | 360000 |  | 1897200 | 1897703.0069 | [5 empty] | Biddyut Bhaban Circuit-2 | 1897703.0069 | 342162.4189 | 1555540.5881 | 454.6205 | FAULT
10 | DMC Circuit-2 |  | 33 |  | 2803 | 1.05 | 320.53 | 329.75 | 9.22 | 360000 |  | 3485160 | 3486084.0247 |  | 0.28876 | BIDDYUT BHABAN 33/11 KV SS | 1897703.0069 |  | DMC Circuit-2 | 3486084.0247 | 3989613.804 | -503529.7794 | -12.621 | OK
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 198.03 | 205.04 | 7.01 | 360000 |  | 2523600 | 2524269.0851 | [5 empty] | BB Avenue-2 | 2524269.0851 | 2517595.0609 | 6674.0242 | 0.2651 | OK
12 | Spare |  | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 |  | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | [5 empty] | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 12528360 | 12531681.6592 | [5 empty] | 0 | 12531681.6592 | 11727887.035 | 803794.6242 | 6.8537 | OK
|  |  | 9=8-7: Grand Total | 14550616.8 | 14546760 | 14550616.8 | 0.026513
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming |  | 11 |  | 2762 | 1 | 45.98 | 49.17 | 3.19 | 250000 | 797500 |  | 733531.1047
9 | 33/11 kV Transformer-2 Incoming |  | 11 |  | 2771 | 1 | 55.08 | 58.77 | 3.69 | 250000 | 922500 |  | 848504.6321
20 | 33/11 kV Transformer-3 Incoming |  | 11 |  | DHK61108 | 1 | 20.9 | 22.8 | 1.9 | 250000 | 475000 |  | 436899.4041
|  |  | 7: 0; 8: 0; 10: Total | 2195000 |  | 2018935.1408
| DHAKA UNIVERSITY 11 kV SIDE |  | 7: 0; 8: 0
| Mokarom Bhabon | D3108MB | 11 |  | 2761 | 1 | 57.23 | 60.6 | 3.37 | 60000 |  | 202200 | 202329.0481 | Ramna |  |  |  |  | Mokarom Bhabon | 202329.0481 | 226720.401 | -24391.3528 | -10.7583 | OK
4 | 11 kV Shaid Minar RMU | D3108SM | 11 |  | 2850 | 1 | 133.38 | 143.49 | 10.11 | 60000 |  | 606600 | 606987.1444 | Ramna |  |  |  |  | 11 kV Shaid Minar RMU | 606987.1444 | 637120.699 | -30133.5546 | -4.7296 | OK
5 | 11 kV Shaidulla Hall | D3108SH | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | D3108MA | 11 |  | 2836 | 1 | 99.81 | 103.68 | 3.87 | 60000 |  | 232200 | 232348.1947 | Ramna |  |  |  |  | MBA Bhabon | 232348.1947 | 278853.9691 | -46505.7744 | -16.6775 | OK
11 | Suprime Court |  | 11 |  | 2835 | 1 | 60.62 | 66 | 5.38 | 60000 |  | 322800 | 323006.0175 | Ramna |  |  |  |  | Suprime Court | 323006.0175 | 284309.8076 | 38696.2099 | 13.6106 | OK
12 | Karjon Hall | D3108KH | 11 |  | 2853 | 1 | 67.57 | 72.86 | 5.29 | 60000 |  | 317400 | 317602.5711 | Ramna |  |  |  |  | Karjon Hall | 317602.5711 | 349779.87 | -32177.2988 | -9.1993 | OK
13 | Spare |  | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | D3108SP | 11 |  | 2839 | 1 | 1.56 | 2.33 | 0.77 | 60000 |  | 46200 | 46229.4858 | Ramna |  |  |  |  | Swimming Pool | 46229.4858 | 46071.5253 | 157.9604 | 0.34286 | OK
15 | Spare |  | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU |  | 11 |  | 2772 | 1 | 86.91 | 93.56 | 6.65 | 60000 |  | 399000 | 399254.6499 | Ramna |  |  |  |  | Police Head Quarter RMU | 399254.6499 | 414643.728 | -15389.0781 | -3.7114 | OK
17 | Spare |  | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare |  | 11 |  | 2764 | 1 | 0.36 | 1.48 | 1.12 | 60000 | Cheek Nocs & Feeder | 67200 | 67242.8884 | [5 empty] | Spare | 67242.8884 | 0 | 67242.8884 | #DIV/0! | #DIV/0!
19 | Spare |  | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 2195000 | 2193600 | 2195000 | 0.063822
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 2195000
[6 empty] | Total = |  |  | 2195000 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 |  | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 |  | 33 | 0 | 2753 | 1 | 421.19 | 426.46 | 5.27 | 360000 | 0 | 1897200 | 1897703.0069
|  |  | 10: Total | 0 | 1897200 | 1897703.0069
0 | 33kV Biddyut Bhaban Circuit |  | 33 | Export | 0 | 1 | 496351 | 503691 | 7340 | 600 | 0 | 4404000 | 0 | 0
|  |  | 10: Total | 0 | 4404000 | 0
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 53107.52 | 69353.02 | 16245.5 | 270 | 0 | 4386285
| Motijheel Incoming |  | 33 |  | DHK-C9344 | 1 | 21216.15 | 21216.28 | 0.13 | 270 |  | 35.1
| Dhaka University Incoming-1 |  | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 | 0
| Dhaka University Incoming-2 |  | 33 |  | DHK-C9343 | 1 | 62562.3 | 69597.58 | 7035.28 | 270 |  | 1899525.6
|  |  | 7: 0; 8: 0; 10: Total |  | 6285845.7 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| PNT S/W |  | 33 |  | DGK-C9340 | 1 | 58694.04 | 58694.04 | 0 | 270 |  | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 20/28 MVA T1 (HV) |  | 33 |  | DHK-C9342 | 1 | 93061.82 | 99167.93 | 6106.11 | 270 |  | 1648649.7
3 | 33/11 kV, 20/28 MVA T2 (HV) |  | 33 |  | DHK-C9308 | 1 | 43512.98 | 58019.02 | 14506.04 | 270 |  | 3916630.8
|  |  | 10: Total |  | 5565280.5 | 5565280.5
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 4: 6285845.7; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6285845.7
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 6285845.7 | 33 KV TX HV SIDE |  | 5565280.5
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 720565.2
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 11.46%
| TOTAL IMPORT |  | 4: 6285845.7
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) |  | 11 |  | DHK-C9316 | 1 | 72236.54 | 82092.02 | 9855.48 | 240 | 2365315.2 |  | 2370793.7689
10 | 33/11 kV T-2 Incoming (LV) |  | 11 |  | DHK-C9377 | 1 | 97192.82 | 113467.84 | 16275.02 | 240 | 3906004.8 |  | 3915051.9311
|  |  | 7: 0; 8: 0; 10: Total | 6271320 |  | 6285845.7
| BIDDYUT BHABAN 11 KV SIDE |  | 7: 0; 8: 0
6 | Segunbagicha | D394S | 11 |  | DHK-C9360 | 1 | 3594.58 | 13326.33 | 9731.75 | 60 |  | 583905 | 585591.0985 | Ramna |  |  |  |  | Segunbagicha | 585591.0985 | 595887.9152 | -10296.8167 | -1.728 | OK
| Secretariat RMU | D394FB | 11 |  | DHK-C9379 | 1 | 77044.89 | 79602.83 | 2557.94 | 60 |  | 153476.4 | 153919.5822 | Ramna |  |  |  |  | Secretariat RMU | 153919.5822 | 147122.5127 | 6797.0695 | 4.62 | OK
7 | NBR RMU | D394NR | 11 |  | DHK-C9319 | 1 | 66156.55 | 73234.86 | 7078.31 | 60 |  | 424698.6 | 425924.9701 | Ramna |  |  |  |  | NBR RMU | 425924.9701 | 412789.7325 | 13135.2377 | 3.1821 | OK
8 | Ramna 11 kV Sw/S-2 |  | 11 |  | DHK-C9364 | 1 | 30272.44 | 50263.55 | 19991.11 | 60 |  | 1199466.6 | 1202930.2093 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-2 | 1202930.2093 | 1229384.6711 | -26454.4618 | -2.1518 | OK
11 | Ramna 11 kV Sw/S-1 |  | 11 |  | DHK-C9375 | 1 | 55044.47 | 55956.29 | 911.82 | 60 |  | 54709.2 | 54867.1796 | Ramna |  |  |  |  | Ramna 11 kV Sw/S-1 | 54867.1796 | 213365.2082 | -158498.0286 | -74.2849 | CHECK
12 | Family Planning | D394FP | 11 |  | DHK-C9378 | 1 | 64525.07 | 71774.93 | 7249.86 | 60 |  | 434991.6 | 436247.6925 | Ramna |  |  |  |  | Family Planning | 436247.6925 | 440914.9728 | -4667.2804 | -1.0585 | OK
13 | Muktijuddho Montranalaya | D394MJ | 11 |  | DHK-C9376 | 1 | 74251.93 | 88559.61 | 14307.68 | 60 |  | 858460.8 | 860939.7125 | Ramna |  |  |  |  | Muktijuddho Montranalaya | 860939.7125 | 912278.2358 | -51338.5233 | -5.6275 | OK
14 | Purana Palton | D394R | 11 |  | DHK-C9318 | 1 | 60052.08 | 65821.54 | 5769.46 | 60 |  | 346167.6 | 347167.2021 | Ramna |  |  |  |  | Purana Palton | 347167.2021 | 309416.4011 | 37750.801 | 12.2006 | OK
15 | Tip Top Feeder |  | 11 |  | DHK-C9318 | 1 | 33459.86 | 70239.61 | 36779.75 | 60 |  | 2206785 | 2213157.3667 | Kakrail |  |  |  |  | Tip Top Feeder | 2213157.3667 | 1322789.6384 | 890367.7283 | 67.3099 | FAULT
16 | 11/0.4 kV Auxiliary Transformer, AT |  | 0.415 |  | DHKD3784 | 1 | 350107 | 355193 | 5086 | 1 |  | 5086 | 5100.6865 | Ramna |  |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 5100.6865 | 4311.9923 | 788.6942 | 18.2907 | OK
|  |  | 10: Grand Total | 6285845.7 | 6267746.8 | 6285845.7 | 0.28876
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 4072688.3333
[6 empty] | Kakrail | at 33 KV level |  | 2213157.3667
[6 empty] | Total = |  |  | 6285845.7 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 |  | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 |  | 33 | 0 | 2803 | 1.05 | 320.53 | 329.75 | 9.22 | 360000 | 0 | 3485160 | 3486084.0247
|  |  | 10: Total | 0 | 3485160 | 3486084.0247
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder |  | 33 | 0 | BD001840 | 1 | 433.43 | 446.7 | 13.27 | 240000 | 0 | 3184800 | 3197700.3639
|  |  | 10: Total |  | 3184800 | 3197700.3639
| DMCH 33 KV SIDE (RECEIVING) | [11 empty] | 6683784.3885
| 33 kV DU Incoming Circuit-1 |  | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming |  | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 |  | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0 | 0
| DMCH 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DMCH 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | 00000069 | 1 | 132156000 | 135049440 | 2893440 | 1 |  | 2893440
2 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 10: Total |  | 2893440
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 4: 3486084.0247; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6683784.3885
| DHANMONDI 33 kV SIDE |  | 4: 3197700.3639; 6: 33 KV NET IMPORT; 9=8-7: 6683784.3885 | 33 KV TX HV SIDE |  | 6683784.3885
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 6683784.3885
11 KV SIDE of___DMCH 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000056 | 1 | 130872864 | 133739664 | 2866800 | 1 | 2866800 |  | 2956685.606
14 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000034 | 1 | 159433680 | 163047472 | 3613792 | 1 | 3613792 |  | 3727098.7825
|  |  | 7: 0; 8: 0; 10: Total | 6480592 |  | 6683784.3885
| DMCH 11 KV SIDE |  | 7: 0; 8: 0
6 | Nearest O/H | D398NE | 11 |  | 00000126 | 1 | 7743381 | 7943260.5 | 199879.5 | 1 |  | 199879.5 | 200195.8311 | Ramna |  |  |  |  | Nearest O/H | 200195.8311 | 223877.2462 | -23681.415 | -10.5779 | OK
| Jagannath Hall | D398JA | 11 |  | 00000002 | 1 | 2867233 | 2968112.8 | 100879.8 | 1 |  | 100879.8 | 101039.4533 | Ramna |  |  |  |  | Jagannath Hall | 101039.4533 | 107985.9597 | -6946.5065 | -6.4328 | OK
7 | Samsun Nahar Hall | D398SN | 11 |  | 00000024 | 1 | 10018216 | 10295055 | 276839 | 1 |  | 276839 | 277277.1279 | Ramna |  |  |  |  | Samsun Nahar Hall | 277277.1279 | 321630.4227 | -44353.2947 | -13.7901 | OK
8 | Spare, 4L |  | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | A3983 | 11 |  | 00000023 | 1 | 22339026 | 22742504 | 403478 | 1 |  | 403478 | 404116.548 | Lalbag |  |  |  |  | Board Office O/H, (5L) | 404116.548 | 474520.243 | -70403.6951 | -14.8368 | OK
10 | OT- Complex | D398OT | 11 |  | 00000167 | 1 | 6728543 | 6834903.5 | 106360.5 | 1 |  | 106360.5 | 106528.8271 | Ramna |  |  |  |  | OT- Complex | 106528.8271 | 336918.4015 | -230389.5744 | -68.3814 | CHECK
11 | Alia Mdrasha O/H, (7L) | A3984 | 11 |  | 00000148 | 1 | 9609897 | 9674696 | 64799 | 1 |  | 64799 | 64901.5515 | Lalbag |  |  |  |  | Alia Mdrasha O/H, (7L) | 64901.5515 | 73635.9109 | -8734.3594 | -11.8615 | OK
12 | Majed Sordar Road | B698J | 11 |  | 00000164 | 1 | 58563616 | 60280212 | 1716596 | 1 |  | 1716596 | 1719312.7006 | Bangshal |  |  |  |  | Majed Sordar Road | 1719312.7006 | 1747073.1814 | -27760.4807 | -1.589 | OK
15 | Chankharpool, 9L | B698Q | 11 |  | 00000001 | 1 | 49199160 | 50333796 | 1134636 | 1 |  | 1134636 | 1136431.6854 | Bangshal |  |  |  |  | Chankharpool, 9L | 1136431.6854 | 1199639.3416 | -63207.6562 | -5.2689 | OK
16 | Shahidullah College O/H, (10L) | A3986 | 11 |  | 00000003 | 1 | 13359607 | 13594687 | 235080 | 1 |  | 235080 | 235452.0398 | Lalbag |  |  |  |  | Shahidullah College O/H, (10L) | 235452.0398 | 255337.0354 | -19884.9956 | -7.7877 | OK
17 | Ananda Bazar | D398AB | 11 |  | 00000111 | 1 | 15136523 | 15255803 | 119280 | 1 |  | 119280 | 119468.7736 | Ramna |  |  |  |  | Ananda Bazar | 119468.7736 | 114687.4296 | 4781.3441 | 4.169 | OK
18 | Hosseni Dalan O/H, (12L) | A3985 | 11 |  |  | 1 | 58.94 | 62.84 | 3.9 | 60000 | Estimated | 997814.484 | 999393.6344 | Lalbag | Estimated from Grid SAS Data |  |  |  | Hosseni Dalan O/H, (12L) | 999393.6344 | 862949.5725 | 136444.0618 | 15.8114 | OK
19 | Badrun Nessa College | A398W | 11 |  | 00000006 | 1 | 20531070 | 20999788 | 468718 | 1 |  | 468718 | 469459.7974 | Lalbag |  |  |  |  | Badrun Nessa College | 469459.7974 | 504253.5009 | -34793.7035 | -6.9 | OK
20 | Dhaka Medical College, Unit-II | D398DM | 11 |  | 00000125 | 1 | 12313610 | 12612529 | 298919 | 1 |  | 298919 | 299392.072 | Ramna |  |  |  |  | Dhaka Medical College, Unit-II | 299392.072 | 310172.7151 | -10780.6431 | -3.4757 | OK
21 | Spare, 15L |  | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | [5 empty] | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | D398SH | 11 |  | 00000127 | 1 | 21432388 | 21974666 | 542278 | 1 |  | 542278 | 543136.2141 | Ramna |  |  |  |  | Sheikh Hasina National Burn Institute | 543136.2141 | 551404.561 | -8268.3468 | -1.4995 | OK
23 | Aux. Transformer, AT-1 |  | 0.415 |  | DHKF-7804 | 1 | 2796.2 | 2872.86 | 76.66 | 100 |  | 7666 | 7678.1323 | Ramna |  |  |  |  | Aux. Transformer, AT-1 | 7678.1323 | 7994.6127 | -316.4804 | -3.9587 | OK
24 | Aux. Transformer, AT-2 |  | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 6683784.3885 | 6673223.284 | 6683784.3885 | 0.15826
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 1654716.4315
[6 empty] | Lalbag | at 33 KV level |  | 2173323.571
[6 empty] | Bangshal | at 33 KV level |  | 2855744.386
[6 empty] | Total = |  |  | 6683784.3885 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 |  | 33 | 0 | 2804 | 1.5 | 165.94 | 174.5 | 8.56 | 360000 | 0 | 4622400 | 4623625.5425
11 | BB Avenue-2 |  | 33 |  | 2820 | 1 | 198.03 | 205.04 | 7.01 | 360000 | 0 | 2523600 | 2524269.0851
|  |  | 10: Total | 0 | 7146000 | 7147894.6276
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 |  | 33 |  | BD 017078 | 1 | 0 | 0 | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 |  | 33 |  | BD 017090 | 1 | 71146.79 | 73665.36 | 2518.57 | 1125 |  | 2833391.25
|  |  | 7: 0; 8: 0; 10: Total | 0 | 2833391.25 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) |  | 33 |  | BD 017093 | 1 | 101888.79 | 106526.14 | 4637.35 | 1000 |  | 4637350
3 | 33/11 kV, 28/35 MVA T-2 (HV) |  | 33 |  | BD 017094 | 1 | 56551.47 | 59075.6 | 2524.13 | 1000 |  | 2524130
|  |  | 10: Total |  | 7161480
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 7147894.6276; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BB AVENEU 33 KV NET IMPORT |  | 7147894.6276
|  |  | 6: BB AVENEU 33 KV NET IMPORT; 9=8-7: 7147894.6276 | 33 KV TX HV SIDE |  | 7161480
[11 empty] | LOSS UNITS=> |  | -13585.3724
[11 empty] | LOSS % IN => |  | -0.1901%
| TOTAL IMPORT |  | 4: 7147894.6276
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming |  | 11 |  | BD 014052 | 1 | 102066.98 | 106679.74 | 4612.76 | 1000 | 4612760 |  | 4629043.8977
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming |  | 11 |  | BD 014055 | 1 | 56001.91 | 58511.9 | 2509.99 | 1000 | 2509990 |  | 2518850.7299
|  |  | 7: 0; 8: 0; 10: Total | 7122750 |  | 7147894.6276
| BB AVENEU 11 KV SIDE |  | 7: 0; 8: 0
6 | Secratariet East | D363BS | 11 |  | BD 013966 | 1 | 4125.4 | 4367.4 | 242 | 1000 |  | 242000 | 242760.0671 | Ramna |  |  |  |  | Secratariet East | 242760.0671 | 221126.0937 | 21633.9734 | 9.7835 | OK
| Taher Bag O/H | B163G | 11 |  | BD 014045 | 1 | 19951.23 | 20674.71 | 723.48 | 1000 |  | 723480 | 725752.2867 | Narinda |  |  |  |  | Taher Bag O/H | 725752.2867 | 829864.029 | -104111.7423 | -12.5456 | OK
7 | Al Raji Complex | D363AR | 11 |  | BD 013983 | 1 | 15315.66 | 16069.61 | 753.95 | 1000 |  | 753950 | 756317.9861 | Ramna |  |  |  |  | Al Raji Complex | 756317.9861 | 777798.4115 | -21480.4254 | -2.7617 | OK
8 | Raduni | D363RI | 11 |  | BD 013999 | 1 | 29678.37 | 30757.71 | 1079.34 | 1000 |  | 1079340 | 1082729.9623 | Ramna |  |  |  |  | Raduni | 1082729.9623 | 1265333.7606 | -182603.7983 | -14.4313 | OK
9 | Sundor Bon Square O/H | B163D | 11 |  | BD 013954 | 1 | 13692.68 | 14187.74 | 495.06 | 1000 |  | 495060 | 496614.8713 | Narinda |  |  |  |  | Sundor Bon Square O/H | 496614.8713 | 482395.9106 | 14218.9606 | 2.9476 | OK
10 | Shromo Bhobon O/H | D363SB | 11 |  | BD 013985 | 1 | 13642.15 | 14129.96 | 487.81 | 1000 |  | 487810 | 489342.1006 | Ramna |  |  |  |  | Shromo Bhobon O/H | 489342.1006 | 495640.2335 | -6298.1329 | -1.2707 | OK
11 | Nawabpur Road | B163P | 11 |  | BD 013953 | 1 | 21092.3 | 21924.28 | 831.98 | 1000 |  | 831980 | 834593.0606 | Narinda |  |  |  |  | Nawabpur Road | 834593.0606 | 843248.6095 | -8655.5489 | -1.0265 | OK
12 | Spair |  | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare |  | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | D363AP | 11 |  | BD 013984 | 1 | 11563.76 | 12043.51 | 479.75 | 1000 |  | 479750 | 481256.786 | Ramna |  |  |  |  | Ahad Police Box | 481256.786 | 438024.4232 | 43232.3628 | 9.8699 | OK
17 | Nearest O/H | D363NE | 11 |  | BD 013997 | 1 | 2742.58 | 2866.83 | 124.25 | 1000 |  | 124250 | 124640.2411 | Ramna |  |  |  |  | Nearest O/H | 124640.2411 | 121402.9541 | 3237.2869 | 2.6666 | OK
18 | Natab Bhaban | D363NB | 11 |  | BD 014000 | 1 | 5167.31 | 5346.21 | 178.9 | 1000 |  | 178900 | 179461.8844 | Ramna |  |  |  |  | Natab Bhaban | 179461.8844 | 187424.2009 | -7962.3165 | -4.2483 | OK
19 | Spare |  | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | [5 empty] | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | D363AO | 11 |  | BD 013956 | 1 | 1423.72 | 1434.02 | 10.3 | 1000 |  | 10300 | 10332.35 | Ramna |  |  |  |  | Awami League Party Office | 10332.35 | 10118.5826 | 213.7674 | 2.1126 | OK
21 | Khaddar Bazar | D363KB | 11 |  | BD 014012 | 1 | 10515.7 | 10910.83 | 395.13 | 1000 |  | 395130 | 396371.0138 | Ramna |  |  |  |  | Khaddar Bazar | 396371.0138 | 401687.6915 | -5316.6778 | -1.3236 | OK
22 | Bangobondu National Stidium | D363NS | 11 |  | BD 014008 | 1 | 9133.78 | 10449.23 | 1315.45 | 1000 |  | 1315450 | 1319581.5303 | Ramna |  |  |  |  | Bangobondu National Stidium | 1319581.5303 | 1315375.6615 | 4205.8688 | 0.31975 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 |  | 0.415 |  | DHKH4418 | 1 | 1326.39 | 1407.54 | 81.15 | 100 |  | 8115 | 8140.4874 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 8140.4874 | 6640.1946 | 1500.2928 | 22.5941 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 |  | 0.415 |  | DHKH4413 | 1 | 48.11 | 48.11 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 30.0552 | -30.0552 | -100 | CHECK
|  |  | 10: Grand Total | 7147894.6276 | 7125515 | 7147894.6276 | 0.31408
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Ramna | at 33 KV level |  | 5090934.409
[6 empty] | Narinda | at 33 KV level |  | 2056960.2186
[6 empty] | Total = |  |  | 7147894.6276 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 |  | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
|  |  | 10: Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 |  | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 |  | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 |  | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 0
|  |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 0 | KALLYANPUR 11 KV NET IMPORT |  | 0
|  |  | 6: TOTAL EXPORT; 9=8-7: 0 | LOSS UNITS=> |  | 0
|  |  | 6: 132KV NET LOSS =>; 9=8-7: #DIV/0! | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 4: 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming |  | 11 |  | 74819926 | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  | 7: 0; 8: 0
A | From Kallyanpur S/S. |  | 7: 0; 8: 0
| 11 KV Gano Bhavan RMU | D534T | 11 |  | DHK14997 | 1 | 995.82 | 995.87 | 0.05 | 40000 |  | 2000 | 2050 | Shere b.nagar |  |  |  |  | 11 KV Gano Bhavan RMU | 2050 | 2050 | -4.6612e-09 | -2.2737e-10 | OK
| 11 KV Beribandh Feeder. | G134K | 11 |  | DHK14960 | 1 | 9660.49 | 9667.45 | 6.96 | 40000 |  | 278400 | 285360 | Adabor |  |  |  |  | 11 KV Beribandh Feeder. | 285360 | 348090 | -62730 | -18.0212 | OK
| 11 KV Adabor O/H | D434A | 11 |  | DHK14957 | 1 | 4531.62 | 4583.3 | 51.68 | 40000 |  | 2067200 | 2118880 | Adabor |  |  |  |  | 11 KV Adabor O/H | 2118880 | 2481320 | -362440 | -14.6067 | OK
| 11 KV Mansurabad | G134M | 11 |  | 77816681 | 1 | 52493.68 | 52769.06 | 275.38 | 8000 |  | 2203040 | 2258116 | Adabor |  |  |  |  | 11 KV Mansurabad | 2258116 | 2458196 | -200080 | -8.1393 | OK
| 11 KV Ring Road Feeder | G134R | 11 |  | 77816675 | 1 | 42213.06 | 42349.9 | 136.84 | 8000 |  | 1094720 | 1122088 | Adabor |  |  |  |  | 11 KV Ring Road Feeder | 1122088 | 1191132 | -69044 | -5.7965 | OK
| 11 KV Sewarage Pump | G134P | 11 |  | DHK14959 | 1 | 2228.14 | 2296.25 | 68.11 | 40000 |  | 2724400 | 2792510 | Adabor |  |  |  |  | 11 KV Sewarage Pump | 2792510 | 1776530 | 1015980 | 57.189 | FAULT
| 11 KV Technical School (DPDC) | G134T | 11 |  | DHK15019 | 1 | 8308.18 | 8361.96 | 53.78 | 40000 |  | 2151200 | 2204980 | Adabor |  |  |  |  | 11 KV Technical School (DPDC) | 2204980 | 2398910 | -193930 | -8.0841 | OK
| 11 KV Goidertek (DPDC) | G134G | 11 |  | DHK14996 | 1 | 9399.97 | 9414.91 | 14.94 | 40000 |  | 597600 | 612540 | Adabor |  |  |  |  | 11 KV Goidertek (DPDC) | 612540 | 617460 | -4920 | -0.79681 | OK
B | From Agargaon S/S. |  | 3: 11 |  |  | 0
| 11 KV P.C Culture Housing | G186C | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H |  | 11 |  | DHK-15026 | 1 | 9207.17 | 9219.86 | 12.69 | 40000 |  | 507600 | 520290 | Shere b.nagar
| 11 KV Nearest RMU |  | 11 |  | DHK-15027 | 1 | 3871.9 | 3875.73 | 3.83 | 40000 |  | 153200 | 157030 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar |  | 11 |  | DHK-15025 | 1 | 3979.7 | 3980.52 | 0.82 | 40000 |  | 32800 | 33620 | Shere b.nagar
| 11 KV BICC Feeder. |  | 11 |  | DHK-15024 | 1 | 1038.34 | 1038.9 | 0.56 | 40000 |  | 22400 | 22960 | Shere b.nagar
| 11 KV NEC Feeder. |  | 11 |  | DHK-15023 | 1 | 431.67 | 431.67 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
| 11 KV Manik Mia Feeder. |  | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0 | Shere b.nagar
|  |  | 7: Export To Desco; 9=8-7: 0; 10: Grand Total | 0 | 11834560 | 12130424 | 2.5
DESCO | 11 kV Tolarbugh |  | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil |  | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy |  | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari |  | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H |  | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur |  | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S |  | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 0 | 0 | 0 | #DIV/0!
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Adabor | at 33 KV level |  | 11394474
[6 empty] | Shere b.nagar | at 33 KV level |  | 735950
[6 empty] | Satmasjid | at 33 KV level
[6 empty] | DESCO | at 33 KV level |  | 0
[6 empty] | Total = |  |  | 12130424 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 |  | 33 | 0 | 30799147 | 1 | 1571.85 | 1597.96 | 26.11 | 240000 | 0 | 6266400 | 6451112.0203
|  |  | 10: Total | 0 |  | 6451112.0203
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
|  |  | 10: Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming |  | 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
| Lalbagh Incoming |  | 3: 33; 9=8-7: 0; 10: 240000 |  | 0
|  |  | 10: Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 |  | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 |  | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 4: 6451112.0203; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 6451112.0203
| IMPORT-2 |  | 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 6451112.0203 | KALLYANPUR 11 KV NET IMPORT |  | 6451112.0203
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 6451112.0203
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [14 empty] | Month October-2023 |  |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 320
8 | 33/11 kV, 20/28 MVA T3 Incoming |  | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0 |  |  |  |  | 100
9 | 33/11 kV, 20/28 MVA T4 Incoming |  | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0 |  |  |  |  | 220
|  |  | 10: Total | 0 |  | 6451112.0203 |  |  | 73.3333
| Kamrangirchar-2 11 KV SIDE | [14 empty] | 173.3333
1 | Nizambag | F1114Z | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1216328.4 | 1217190.9472 | Kamrangirchar | 100 |  |  |  | Nizambag | 1217190.9472 | 1180785.7325 | 36405.2148 | 3.0831 | OK
2 | Merry Stopes | F1114P | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 304082.1 | 304297.7368 | Kamrangirchar | 25 |  |  |  | Merry Stopes | 304297.7368 | 318812.1478 | -14514.411 | -4.5527 | OK
3 | Mujibur Ghat | F1114V | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1277144.82 | 1278050.4946 | Kamrangirchar | 105 |  |  |  | Mujibur Ghat | 1278050.4946 | 1298864.3057 | -20813.8111 | -1.6025 | OK
4 | Madrasa | F1114U | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1581226.92 | 1582348.2314 | Kamrangirchar | 130 |  |  |  | Madrasa | 1582348.2314 | 1653100.0255 | -70751.7941 | -4.2799 | OK
5 | Thana | F1114Q | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1217190.9472 | Kamrangirchar | 100 |  |  |  | Thana | 1217190.9472 | 1298864.3057 | -81673.3585 | -6.2881 | OK
6 | Al-Hera |  | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | F1114W | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 851429.88 | 852033.6631 | Kamrangirchar | 70 |  |  |  | Waz Uddin School | 852033.6631 | 1003667.8726 | -151634.2095 | -15.108 | OK
8 | 11/0.4 kV Auxiliary Transformer |  | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off |  | 10: Grand Total | 6451112.0203 | 6446540.52 | 6451112.0203 | 0.070914
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kamrangirchar | at 33 KV level |  | 6451112.0203
[6 empty] | Total = |  |  | 6451112.0203 | 0
Note on G935: User: Grid CF=1.5

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) |  | 132 | IMPORT | 8993631 | 1 | 5884.59 | 5922.51 | 37.92 | 960000 | 0 | 36403200
| 132 KV Mogbazar-2 CKT(EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) |  | 132 |  | 8993659 | 1 | 5013.741 | 5042.863 | 29.122 | 960000 | 0 | 27957120
| 132 KV Mogbazar-1 CKT(EXP) |  | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 64360320
|  |  | 10: Net Total | 64360320
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE | 6604452 | 1 | 9419.02 | 9469.87 | 50.85 | 720000 | 36612000
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  | 6604428 | 1 | 5666.56 | 5705.45 | 38.89 | 720000 | 28000800
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
|  |  | 9=8-7: Total Import/Export | 64612800 | 0
|  |  | 9=8-7: Net Total | 64612800 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0 |  |  | future Scope
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0 |  |  | No meter
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 64612800
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 64360320; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 64360320
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 64360320 | MOGBAZAR 33 KV NET IMPORT |  | 64377600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -17280
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.02685%
| 132 KV TOTAL IMPORT |  | 4: 64360320
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming |  | 33 | IMPORT | 76026303 | 1 | 10017.33 | 10062.5 | 45.17 | 480000 | 21681600 |  | 21675780.3042
| 132/33 KV GT-2 Incomming |  | 33 |  | 76026307 | 1 | 10012.35 | 10057.53 | 45.18 | 480000 | 21686400 |  | 21680579.0158
| 132/33 KV GT-3 Incomming |  | 33 |  |  | 1 | 8217.53 | 8261.3 | 43.77 | 480000 | 21009600 |  | 21003960.68
|  |  | 7: 0; 8: 0; 10: Total | 64377600 |  | 64360320
| MOGBAZAR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. |  | 33 |  | 6604465 | 1 | 7009.03 | 7025.58 | 16.55 | 180000 |  | 2979000 | 2990020.124 |  | 20151872.4546 | MOGBAZAR 33/11 KV SS | 3.3831 | 33/11 KV Transformer No.1. | 2990020.124 | 3013761.605 | -23741.481 | -0.78777 | OK
| 33/11 KV Transformer No.2. |  | 33 |  | 202006985 | 1 | 35661489016.6 | 35663032846 | 1543829.4 | 3 | T2 Incomer side | 5366200 | 5386051.0203 |  |  |  |  | 33/11 KV Transformer No.2. | 5386051.0203 | 5828429.377 | -442378.3567 | -7.59 | OK
| 33/11 KV Transformer No.3. |  | 33 |  | 6604338 | 1 | 7106.76 | 7139.46 | 32.7 | 180000 |  | 5886000 | 5907773.9006 |  |  |  |  | 33/11 KV Transformer No.3. | 5907773.9006 | 6242147.7648 | -334373.8642 | -5.3567 | OK
| 33/11 KV Transformer No.4 |  | 33 |  |  | 1 | 1102036 | 1134977 | 32941 | 180000 | T4 Incomer side | 5846400 | 5868027.4096 |  |  |  |  | 33/11 KV Transformer No.4 | 5868027.4096 | 6364589.9711 | -496562.5615 | -7.802 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 20077600 | 20151872.4546 |  |  |  |  | 33 KV Feeders | 20151872.4546 | 21448928.718 | -1297056.2634 | -6.0472 | OK
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 |  | 76026300 | 1 | 6763.97 | 6785.52 | 21.55 | 360000 |  | 7758000 | 7786698.9333 |  | 20863294.4968 | Tejgoan 33/11 kv ss | 1.028 | 33 kV Tejgaon U/G Feeder-1 | 7786698.9333 | 8094411.7794 | -307712.8461 | -3.8015 | OK
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 |  | 06604453 | 1 | 6592.78 | 6628.97 | 36.19 | 360000 |  | 13028400 | 13076595.5636 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 13076595.5636 | 13570043.2772 | -493447.7136 | -3.6363 | OK
10 | Bashundhara City |  | 33 |  | 660434 | 1 | 791.06 | 803.19 | 12.13 | 180000 |  | 2183400 | 2191476.9852 | Shere b.nagar | 5774081.1579 | Ispahani 33/11 kv ss | 1.2666 | Bashundhara City | 2191476.9852 | 2303155.9363 | -111678.9512 | -4.849 | OK
11 | Ispahani-1 |  | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Ispahani-2 |  | 33 |  |  | 1 | 3925.09 | 3957.05 | 31.96 | 180000 |  | 5752800 | 5774081.1579 |  | 5689057.7928 | Green Road Dormatory 33/11 kv ss | 1.3314 | Ispahani-2 | 5774081.1579 | 6085237.376 | -311156.2181 | -5.1133 | OK
13 | 33 kV Green Road Dormitory |  | 33 |  | 76026305 | 1 | 8095.81 | 8111.66 | 15.85 | 180000 | Reading From G. Dormitory Side | 5668090 | 5689057.7928 |  |  |  |  | 33 kV Green Road Dormitory | 5689057.7928 | 9350566.6139 | -3661508.8211 | -39.1581 | OK
14 | 33 KV T&T-1 |  | 33 |  | 6604337 | 1 | 4630.22 | 4653.65 | 23.43 | 180000 |  | 4217400 | 4233001.2995 |  | 9369331.9415 | T&T 33/11 kv ss | -1.6675 | 33 KV T&T-1 | 4233001.2995 | 5798470.1138 | -1565468.8143 | -26.998 | OK
13 | 33 KV T&T-2 |  | 33 |  | 6604336 | 1 | 5717.09 | 5745.52 | 28.43 | 180000 |  | 5117400 | 5136330.6421 |  |  |  |  | 33 KV T&T-2 | 5136330.6421 | 5610899.0743 | -474568.4323 | -8.458 | OK
14 | 33KV Karwan Bazar |  | 33 |  | 74605366~4 | 1 | 1192.72 | 1192.72 | 0 | 180000 | Check | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.090354 | 33KV Karwan Bazar | 0 | 656498.6381 | -656498.6381 | -100 | CHECK
19 | AT-1 |  | 33 |  | 6603338 | 1 | 2362.56 | 2569.26 | 206.7 | 80 |  | 16536 | 16597.1711 |  |  |  |  | AT-1 | 16597.1711 | 32188.4729 | -15591.3018 | -48.4375 | CHECK
20 | AT-2 |  | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 43742026 | 43903839.5454 |  |  |  |  | 0 | 43903839.5454 | 51501471.282 | -7597631.7366 | -14.7523 | OK
|  |  | 9=8-7: Grand Total | 64055712 | 63819626 | 64055712 | 0.36993
-0.3377
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2191476.9852
|  |  | 9=8-7: Total =; 10: 2191476.9852 | 0 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 |  | 11 | Import | 6604457 | 1 | 541272.4 | 544213.6 | 2941.2 | 1000 | 2941200 |  | 2969979.2181
2 | 33/11 kV Transformer-2 |  | 11 | Import | 30/11009-1101 | 1 | 591157.2 | 596523.4 | 5366.2 | 1000 | 5366200 |  | 5418707.4936
3 | 33/11 kV Transformer-3 |  | 11 | Import | 6604454 | 1 | 586647.5 | 592450.3 | 5802.8 | 1000 | 5802800 |  | 5859579.5616
4 | 33/11 kV Transformer-4 |  | 11 | Import |  | 1 | 1087.62 | 1124.16 | 36.54 | 160000 | 5846400 |  | 5903606.1813
|  |  | 7: 0; 8: 0; 10: Total | 19956600 |  | 20151872.4546
| MOGBAZAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 40800.1 | 40966.6 | 166.5 | 1000 |  | 166500 | 170232.3057 | Kakrail |  |  |  | 11 kV Doctor's Lane | 170232.3057 | 173300.7767 | -3068.471 | -1.7706 | OK
2 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 80823.9 | 80957.2 | 133.3 | 1000 |  | 133300 | 136288.0862 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 136288.0862 | 107803.7381 | 28484.3481 | 26.4224 | OK
3 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 |  | 11 | T-1 | 30/11004-1101 | 1 | 120284.8 | 120741.7 | 456.9 | 1000 |  | 456900 | 467141.9849 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 467141.9849 | 391310.8557 | 75831.1292 | 19.3787 | OK
7 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 129935.9 | 132139.2 | 2203.3 | 1000 |  | 2203300 | 2252689.725 | Moghbazar |  |  |  | 11KV Ambagan | 2252689.725 | 2523568.5136 | -270878.7885 | -10.734 | OK
[7 empty] | 0 | 0
5 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 147394.9 | 148899.1 | 1504.2 | 1000 |  | 1504200 | 1537918.5242 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1537918.5242 | 1644738.2335 | -106819.7093 | -6.4946 | OK
3 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 9978.1 | 10125.5 | 147.4 | 1000 |  | 147400 | 150704.1553 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 150704.1553 | 173927.5426 | -23223.3873 | -13.3523 | OK
4 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 126688.8 | 128558 | 1869.2 | 1000 |  | 1869200 | 1911100.4557 | Kakrail |  |  |  | 11 kV Bangla Motor | 1911100.4557 | 2221153.9574 | -310053.5018 | -13.9591 | OK
1 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 176601.2 | 178896.5 | 2295.3 | 1000 |  | 2295300 | 2346752.0201 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 2346752.0201 | 2390485.2167 | -43733.1966 | -1.8295 | OK
[7 empty] | 0 | 0
6 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 122629 | 123990 | 1361 | 1000 | Estimated | 1763676.18 | 1803211.1873 | Kakrail | 145 |  |  | 11 kV Iskaton | 1803211.1873 | 1782922.7783 | 20288.409 | 1.1379 | OK
5 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 87567.7 | 89088.7 | 1521 | 1000 |  | 1521000 | 1555095.1172 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1555095.1172 | 1652781.7295 | -97686.6123 | -5.9104 | OK
2 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 123893.2 | 124248.6 | 355.4 | 1000 |  | 355400 | 363366.7355 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 363366.7355 | 399563.2736 | -36196.5382 | -9.059 | OK
3 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 115143.1 | 116054.5 | 911.4 | 1000 |  | 911400 | 931830.1708 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 931830.1708 | 991857.0675 | -60026.8967 | -6.052 | OK
4 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 44147 | 44614.9 | 467.9 | 1000 |  | 467900 | 478388.5637 | Kakrail |  |  |  | 11 kV BSRS Feeder | 478388.5637 | 514783.7418 | -36395.1781 | -7.07 | OK
2 | 11 kV Vumi Bhaban |  | 11 | T-3 | 21101039 | 1 | 8856.8 | 8997.2 | 140.4 | 1000 |  | 140400 | 143547.2416 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 143547.2416 | 140604.4879 | 2942.7537 | 2.0929 | OK
5 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | check | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 1357.9928 | -1357.9928 | -100 | CHECK
|  |  | 7: 0; 8: 0 | 14248266.2732 | 13935876.18 | 14248266.2732 | 2.2416 |  |  |  |  | 14248266.2732 | 15110159.9059
1 | 11 kV TCB Feeder | C608P | 11 | T-4 |  | 1 | 36560.7 | 36868.9 | 308.2 | 1000 |  | 308200 | 327449.4305 | Kakrail |  |  |  | 11 kV TCB Feeder | 327449.4305 | 337617.6819 | -10168.2514 | -3.0118 | OK
2 | 11 kV Tejgaon SS-2 |  | 11 | T-4 |  | 1 | 32855.5 | 34285.7 | 1430.2 | 1000 |  | 1430200 | 1519526.851 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1519526.851 | 1537848.541 | -18321.69 | -1.1914 | OK
3 | Holy Day Inn | C108HY | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 396900 | 421689.4191 | Tejgaon |  |  |  | Holy Day Inn | 421689.4191 | 437235.9991 | -15546.5801 | -3.5556 | OK
4 | Polly Bhabon-2 | C608PB | 11 | T-4 |  | 1 | 18384.8 | 18384.8 | 0 | 1000 | According to AMR meter reading | 21927 | 23296.5077 | Kakrail |  |  |  | Polly Bhabon-2 | 23296.5077 | 25096.5994 | -1800.0917 | -7.1727 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 |  | 1 | 18495.9 | 20174.3 | 1678.4 | 1000 |  | 1678400 | 1783228.8258 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1783228.8258 | 1839066.8165 | -55837.9907 | -3.0362 | OK
6 | 11 kV Tejturibazar | C608X | 11 | T-4 |  | 1 | 132188.2 | 132923.9 | 735.7 | 1000 |  | 735700 | 781650.0519 | Kakrail |  |  |  | 11 kV Tejturibazar | 781650.0519 | 797094.2458 | -15444.1939 | -1.9376 | OK
7 | Songsad |  | 11 | T-4 |  | 1 | 3719.3 | 3864.8 | 145.5 | 1000 |  | 145500 | 154587.5799 | Shere b.nagar |  |  |  | Songsad | 154587.5799 | 443228.713 | -288641.1331 | -65.1224 | CHECK
| Chennel 24 |  | 11 | T-4 |  | 1 | 7324.01 | 7327.44 | 3.43 | 1000 |  | 3430 | 3644.2295 | Moghbazar |  |  |  | Chennel 24 | 3644.2295 | 5053.7147 | -1409.4851 | -27.8901 | OK
8 | Sonargaon | C608K | 11 | T-4 |  | 1 | 41121.6 | 41957.9 | 836.3 | 1000 |  | 836300 | 888533.2859 | Kakrail |  |  |  | Sonargaon | 888533.2859 | 916526.5008 | -27993.2149 | -3.0543 | OK
| AT -1 |  | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 |  | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[11 empty] | 5903606.1813 | 5556557 | 5903606.1813 | 6.2458
|  |  | 10: Total | 20151872.4546 | 19492433.18 | 20151872.4546 | 3.3831
|  |  | 6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH | [13 empty] | AMR Meter Information
|  |  | 6: Moghbazar; 7: at 33 KV level; 9=8-7: 2619700.69 | [13 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
|  |  | 6: Tejgaon; 7: at 33 KV level; 9=8-7: 8278663.3996 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 80070 | 3000
|  |  | 6: Kakrail; 7: at 33 KV level; 9=8-7: 9098920.785 | [13 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 316830 | 3000
|  |  | 6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 154587.5799 | [13 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 21927 | 300
[6 empty] | Total = |  |  | 20151872.4546 | 0
AMR Meter Information
[24 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[24 empty] | Shah Garments | 811.81 | 832.6 | 223.32 | 229.22
[24 empty] | Habib Hotel | 2716.73 | 2794.53 | 897.68 | 925.49
[24 empty] | The Joint Director BRDB | 1303.24 | 1367.9 | 254.47 | 262.9
[26 empty] | 832.6 | 229.22
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [24 empty] | 2794.53 | 925.49
[26 empty] | 1367.9 | 262.9
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 |  | 33 | 0 | 6604337 | 1 | 4630.22 | 4653.65 | 23.43 | 180000 | 0 | 4217400 | 4233001.2995
13 | 33 KV T&T-2 |  | 33 | 0 | 6604336 | 1 | 5717.09 | 5745.52 | 28.43 | 180000 | 0 | 5117400 | 5136330.6421
0 | Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 9334800 | 9369331.9415
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder |  | 33 | Import | DHK60891 | 1 | 999061 | 1006947 | 7886 | 360 | 2838960
2 | 33 kV Moghbazar-2 Feeder |  | 33 | Import | DHK68131 | 1 | 898200 | 898200 | 0 | 360 | 0
| 33 kV Ullon Feeder |  | 33 | Import | DHK68132 | 1 | 349.75 | 349.9 | 0.15 | 180000 | 27000
|  |  | 7: 0; 8: 0; 10: Total | 2865960 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 1031989 | 1031989 | 0 | 180 |  | 0
4 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 881138 | 900418 | 19280 | 180 |  | 5117400 |  |  | Meter Problem
|  |  | 10: Total |  | 5117400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 9369331.9415; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9369331.9415
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 9369331.9415 | 33/11 KV XF LV SIDE |  | 4283640
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 5085691.9415
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 54.28%
| TOTAL IMPORT |  | 4: 9369331.9415
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 112245 | 136043 | 23798 | 180 | 4283640 |  | 9369331.9415 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 1021744 | 1021744 | 0 | 180 | 0 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 4283640 |  | 9369331.9415 | 118.7236 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 202609 | 208557 | 5948 | 60 |  | 356880 | 350929.0306 | Kakrail |  |  |  | 11 kV post office | 350929.0306 | 1384212.3787 | -1033283.3481 | -74.6477 | CHECK
2 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 470715 | 491607 | 20892 | 60 |  | 1253520 | 1232617.5702 | Kakrail |  |  |  | 11 kV anarkoli | 1232617.5702 | 1434115.4167 | -201497.8465 | -14.0503 | OK
3 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 957585 | 963754 | 6169 | 60 |  | 370140 | 363967.9203 | Moghbazar |  |  |  | 11 kV sonalibagh | 363967.9203 | 383823.6058 | -19855.6855 | -5.1731 | OK
4 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1974036 | 1987746 | 13710 | 60 |  | 822600 | 808883.1556 | Moghbazar |  |  |  | 11 Kv desh tv | 808883.1556 | 925176.0601 | -116292.9044 | -12.5698 | OK
5 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 646 | 670.9 | 24.9 | 60000 |  | 1494000 | 1469087.5693 | Moghbazar |  |  |  | 11 Kv Btcl | 1469087.5693 | 1653485.829 | -184398.2597 | -11.1521 | OK
1 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 905645 | 916060 | 10415 | 60 |  | 624900 | 614479.8006 | Kakrail |  |  |  | 11 kV century | 614479.8006 | 616445.7818 | -1965.9812 | -0.31892 | OK
2 | 11 kV cinema hall |  | 11 | Mogbazar | DHK60979 | 1 | 506046 | 522676 | 16630 | 60 |  | 997800 | 981161.6979 | Moghbazar |  |  |  | 11 kV cinema hall | 981161.6979 | 1071064.8459 | -89903.1479 | -8.3938 | OK
3 | 11 kV malibagh bazar |  | 11 | Khailgaon | DHK61106 | 1 | 755000 | 782487 | 27487 | 60 |  | 1649220 | 1621719.2778 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1621719.2778 | 1701657.7808 | -79938.503 | -4.6977 | OK
4 | 11 kv Sherebangla | D1105G | 11 |  | DHK60915 | 1 | 743499 | 765116 | 21617 | 60 |  | 1297020 | 1275392.2083 | Moghbazar |  |  |  | 11 kv Sherebangla | 1275392.2083 | 1525385.4467 | -249993.2385 | -16.3889 | OK
5 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 344109 | 355079 | 10970 | 60 |  | 658200 | 647224.5235 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 647224.5235 | 706402.574 | -59178.0505 | -8.3774 | OK
6 | Auxiliary |  |  | Export | U0004461 | 1 | 8223.3 | 8288.88 | 65.58 | 60 |  | 3934.8 | 3869.1873 | Moghbazar |  |  |  | Auxiliary | 3869.1873 | 7599.4686 | -3730.2814 | -49.0861 | CHECK
|  |  | 10: Grand Total | 9369331.9415 | 9528214.8 | 9369331.9415 | -1.6675
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Kakrail | at 33 KV level |  | 2198026.4014
[6 empty] | Moghbazar | at 33 KV level |  | 5549586.2622
[6 empty] | Khilgaon | at 33 KV level |  | 1621719.2778
[6 empty] | Total = |  |  | 9369331.9415 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 |  | 132 | IMPORT | 8993681 | 1 | 2689.328 | 2714.49 | 25.162 | 1440000 | 0 | 36233280
| Ullon-1 |  | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 |  | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 36233280
|  |  | 9=8-7: Net Total | 36233280
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) |  | 132 |  | 8993624 | 1 | 4836.3 | 4864.387 | 28.087 | 960000 | 0 | 26963520
| Maniknager-2 (new line to ullon) |  | 132 |  |  | 1 | 11.003 | 11.083 | 0.08 | 960000 | 76800 | 0
|  |  | 9=8-7: Total Import/Export | 76800 | 26963520
|  |  | 9=8-7: Net Total | 26886720
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 |  | 132 |  | 8993659 | 1 | 4427.865 | 4438.485 | 10.62 | 960000 | 0 | 10195200
| Ullon U/G-1 |  | 132 |  |  | 1 | 1.561 | 1.561 | 0 | 960000 | 0 | 0
| Ullon U/G-2 |  | 132 |  | 8993660 | 1 | 4111.695 | 4121.721 | 10.026 | 960000 | 0 | 9624960
| Ullon U/G-2 |  | 132 |  |  | 1 | 1.33 | 1.33 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 19820160
|  |  | 9=8-7: Net Total | 19820160
| ULLON 132 KV SIDE (RECEIVING) | [9 empty] | 82940160
| 132 KV Rampura-1 (IMP) |  | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) |  | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) |  | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) |  | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder |  | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder |  | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) |  | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
| EXPORT TO OTHERS 132/33 KV SS | [13 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 |  | 132 |  |  | 1 | 1632756 | 1632768 | 12 | 1000 |  | 12000 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 |  | 132 |  |  | 1 | 2181074 | 2212585 | 31511 | 1000 |  | 31511000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 |  | 132 |  |  | 1 | 2944081 | 2974112 | 30031 | 1000 |  | 30031000 |  |  | 132 kV Ullon CKT-3 | 31978000
|  |  | 10: Total |  | 61542000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 21398160
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 4: 36233280; 6: EXPORT TO OTHER S/S; 9=8-7: 61542000 | 132 KV NET IMPORT |  | 21398160
| HORIPUR 132 SIDE (TARIFF POINT) |  | 4: 26886720; 6: 132 KV Net EXPORT; 9=8-7: 21398160 | 132/33 KV GT LV Side |  | 21541488
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 19820160 | LOSS UNITS=>(132 HV-33 LV) |  | -143328
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.6698%
| 132 KV TOTAL IMPORT |  | 4: 82940160
33 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | BD001812 | 1 | 2212.1337 | 2234.826 | 22.6923 | 480000 | 10892304 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming |  | 33 | Import | BD001858 | 1 | 2132.8557 | 2155.0415 | 22.1858 | 480000 | 10649184 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming |  | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 21541488 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1629.0994 | 1666.769 | 37.6696 | 240000 |  | 9040704 | 9041864.5151 |  | 12367299.3317 | Taltola 33/11 kv ss | 0.22363 | Taltala-1 | 9041864.5151 | 7693491.8461 | 1348372.6691 | 17.5261 | OK
| Mgbazar T&T |  | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Mgbazar T&T | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Kakrail |  | 33 | North-1 | BD001811 | 1 | 1163.9123 | 1163.9124 | 0.0001 | 240000 |  | 24 | 24.0031 |  | 0 | Mgbazar T&T 33/11 kv ss | -1.6675 | Kakrail | 24.0031 | 648.498 | -624.4949 | -96.2987 | CHECK
2 | Taltala-2 |  | 33 | Export | BD001837 | 1 | 2596.7593 | 2610.6135 | 13.8542 | 240000 |  | 3325008 | 3325434.8165 |  |  |  |  | Taltala-2 | 3325434.8165 | 8143285.2432 | -4817850.4266 | -59.1635 | CHECK
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 24.0031 | Kakrail 33/11 kv ss | -0.035562 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 0.39586 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 75.4774 | 79.3194 | 3.842 | 240000 |  | 922080 | 922198.3633 |  | 0 | Tejgoan 33/11 kv ss | 1.028 | Khailgaon | 922198.3633 | 130324.0761 | 791874.2872 | 607.6193 | FAULT
4 | AT at GIS Building |  | 415 | Export | DHKE4577 | 1 | 151699 | 155214 | 3515 | 1 |  | 3515 | 3515.4512 |  | 922198.3633 | Khilgoan 33/11 kv ss | 0.31121 | AT at GIS Building | 3515.4512 | 3592.7589 | -77.3077 | -2.1518 | OK
|  |  | 7: 0; 8: 0; 10: TOTAL= |  | 13291331 | 13293037.1493 |  |  |  |  | 0 | 13293037.1493 | 15971342.4222 | -2678305.2729 | -16.7694 | OK
| 33 KV Local Feeder -1 |  | 33 | NET IMPORT |  | 1 | 1170.3343 | 1187.637 | 17.3027 | 240000 |  | 4152648 | 4153181.057 |  | 8183826.3867 | Ullon 33/11 kv ss | 0.42244 | 33 KV Local Feeder -1 | 4153181.057 | 4316834.9052 | -163653.8482 | -3.7911 | OK
| 33KV Local Feeder- 2 |  | 33 |  |  | 1 | 897.6098 | 914.402 | 16.7922 | 240000 |  | 4030128 | 4030645.3297 |  |  |  |  | 33KV Local Feeder- 2 | 4030645.3297 | 4180097.9046 | -149452.5749 | -3.5753 | OK
|  |  | 10: TOTAL= |  | 8182776 | 8183826.3867 |  |  |  |  | 0 | 8183826.3867 | 8496932.8098 | -313106.4231 | -3.6849 | OK
|  |  | 10: Grand Total | 21476863.536 | 21474107 | 21476863.536 | 0.012837
11 KV SIDE of___ULLON 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 186 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 |  |  |  |  | 100 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 8182776 |  | 8183826.3867 |  |  | 86 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [14 empty] | 28.6667 |  |  |  |  | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 973062.72 | 977173.2999 | Moghbazar | 80 | 128.6667 |  | West Malibagh | 977173.2999 | 1007307.2369 | -30133.937 | -2.9915 | OK
2 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1824492.6 | 1832199.9373 | Moghbazar | 150 |  |  | Ullon | 1832199.9373 | 1836854.3731 | -4654.4358 | -0.25339 | OK
3 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1520410.5 | 1526833.2811 | Moghbazar | 125 |  |  | Mohanagar | 1526833.2811 | 1659094.2725 | -132260.9914 | -7.9719 | OK
4 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1033879.14 | 1038246.6311 | Moghbazar | 85 |  |  | Bagichartek | 1038246.6311 | 1125813.9706 | -87567.3395 | -7.7781 | OK
1 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1702859.76 | 1710053.2748 | Moghbazar | 140 |  |  | Mirbagh | 1710053.2748 | 1718347.6394 | -8294.3645 | -0.48269 | OK
2 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 1094695.56 | 1099319.9624 | Moghbazar | 90 |  |  | West Rampura | 1099319.9624 | 1149515.3174 | -50195.355 | -4.3667 | OK
3 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 |  | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 |  | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 8183826.3867 | 8149400.28 | 8183826.3867 | 0.42244
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 8183826.3867
[6 empty] | Total = |  |  | 8183826.3867 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 |  | 132 | Export | 50146667 | 1 | 1842.02 | 1867.274 | 25.254 | 960000 | 0 | 24243840
2 | Rampura to Madartek-2 |  | 132 | Export | 50146668 | 1 | 1635.972 | 1661.144 | 25.172 | 960000 | 0 | 24165120
|  |  | 9=8-7: Total Import/Export | 0 | 48408960
|  |  | 9=8-7: Net Total | 48408960
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 |  | 132 | Import | SIEM0492 | 1 | 1625866 | 1650013 | 24147 | 1000 | 24147000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 |  | 132 | Import | SIEM0489 | 1 | 1575371 | 1599552 | 24181 | 1000 | 24181000
|  |  | 132 | Export |  | 1 | 0 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 48328000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 48328000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| MADERTEK 132 KV SIDE |  | 7: 0; 8: 0
3 | 133 kV GT-1 |  | 132 | Export |  | 1 | 1462276 | 1486557 | 24281 | 1000 |  | 24281000
4 | 133 kV GT-2 |  | 132 | Export |  | 1 | 1450296 | 1474412 | 24116 | 1000 |  | 24116000
|  |  | 10: Total |  | 48397000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 4: 48408960; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 48408960
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 48408960 | 33 KV NET IMPORT |  | 48560000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -151040
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.312%
| 132 KV TOTAL IMPORT |  | 4: 48408960
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0516 | 1 | 1610950 | 1635234 | 24284 | 1000 | 24284000 |  | 24208467.5585
2 | 132/33 kV XF-1 Incoming |  | 33 | Import | SIEM0515 | 3 | 534985 | 543077 | 8092 | 1000 | 24276000 |  | 24200492.4415
|  |  | 7: 0; 8: 0; 10: Total | 48560000 |  | 48408960
| MADERTEK 33 KV SIDE |  | 7: 0; 8: 0
| 33/11 kv Transforfers |  | 7: 0; 8: 0
1 | 33 kV T-1 |  | 33 | Import | SIEM0512 | 1 | 416708 | 420830 | 4122 | 2000 |  | 8244000 | 8252968.0958 |  | 19967697.9184 | Madartek 33/11 kv ss
2 | 33 kV T-3 |  | 33 | Export |  | 1 | 79491 | 81155 | 1664 | 2000 |  | 3328000 | 3331620.3085
2 | 33 kV T-2 |  | 33 | Export | SIEM0505 | 1 | 419769 | 423956 | 4187 | 2000 |  | 8374000 | 8383109.5141
| 33 kv Feeders |  | 7: 0; 8: 0; 10: Total |  | 19946000 | 19967697.9184 |  | 15879255.2082 | Banasree 33/11 kv ss
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 112863 | 116881 | 4018 | 2000 |  | 8036000 | 8044741.8266
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 360310 | 365258 | 4948 | 2000 |  | 9896000 | 9906765.1961 |  | 9906765.1961 | Goran 33/11 kv ss
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 38552 | 38986 | 434 | 6000 |  | 2604000 | 2606832.7173
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 96502 | 100415 | 3913 | 2000 |  | 7826000 | 7834513.3816 |  | 2606832.7173 | Amulia 33/11 kv ss
|  |  | 10: Total |  | 28362000 | 28392853.1216
|  |  | 9=8-7: Grand Total | 48360551.04 | 48308000 | 48360551.04 | 0.10878
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming |  | 11 | Import | GJU 71154 | 1 | 389513.5 | 393620.5 | 4107 | 2000 | 8214000 |  | 8249156.0813 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming |  | 11 | Import | GJU 71155 | 1 | 392737.5 | 396916.7 | 4179.2 | 2000 | 8358400 |  | 8394174.1161 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming |  | 11 | Import | 6604399 | 1 | 4727.18 | 4745.57 | 18.39 | 180000 | 3310200 |  | 3324367.721 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 19882600 |  | 19967697.9184 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 14.0602 | 15.7858 | 1.7256 | 1000000 |  | 1725578 | 1733090.4653 | Mugdapara |  |  |  | Sobujbagh | 1733090.4653 | 1860379.5125 | -127289.0472 | -6.8421 | OK
2 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 103409.1 | 105215.6 | 1806.5 | 1000 |  | 1806500 | 1814364.7668 | Mugdapara |  |  |  | Madertek | 1814364.7668 | 1995837.5311 | -181472.7643 | -9.0926 | OK
3 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 4101.6 | 6227.8 | 2126.2 | 1000 |  | 2126200 | 2135456.6106 | Mugdapara |  |  |  | Rajarbagh | 2135456.6106 | 2140470.7173 | -5014.1067 | -0.23425 | OK
| Goran | A921G | 11 |  | X1390296 | 1 | 32509.3 | 34326.4 | 1817.1 | 1000 |  | 1817100 | 1825010.9149 | Bashabo |  |  |  | Goran | 1825010.9149 | 1949936.5823 | -124925.6675 | -6.4067 | OK
5 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 12785.006 | 14225.436 | 1440.43 | 1000 |  | 1440430 | 1446701.0468 | Mugdapara |  |  |  | Dhakhingaon | 1446701.0468 | 1502775.9682 | -56074.9214 | -3.7314 | OK
6 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | Manda | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1236.0474 | 1479.3345 | 243.2871 | 1000 |  | 243287.1 | 244346.2732 | Mugdapara |  |  |  | Green Model Town | 244346.2732 | 252299.2953 | -7953.0221 | -3.1522 | OK
1 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 4394.6776 | 4970.5368 | 575.8592 | 1000 |  | 575859.2 | 578366.2569 | Mugdapara |  |  |  | Biswa Road | 578366.2569 | 687579.7395 | -109213.4826 | -15.8838 | OK
2 | Mugdapara | B921P | 11 |  | X0854272 | 1 | 4423.5 | 4681.7 | 258.2 | 1000 |  | 258200 | 259324.0979 | Maniknagar |  |  |  | Mugdapara | 259324.0979 | 280126.3587 | -20802.2609 | -7.426 | OK
| Singapur | F221S | 11 |  | X1390302 (N) | 1 | 38272.3 | 40431.5 | 2159.2 | 1000 |  | 2159200 | 2168600.2792 | Banosree |  |  |  | Singapur | 2168600.2792 | 2400509.1335 | -231908.8543 | -9.6608 | OK
| Trimohony | F221T | 11 |  | X1390308 | 1 | 30823 | 32844.1 | 2021.1 | 1000 |  | 2021100 | 2029899.048 | Banosree |  |  |  | Trimohony | 2029899.048 | 2144287.4264 | -114388.3785 | -5.3346 | OK
5 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 16162.476 | 17776.286 | 1613.81 | 1000 |  | 1613810 | 1620835.8728 | Mugdapara |  |  |  | Mayakanon | 1620835.8728 | 1884688.9362 | -263853.0634 | -13.9998 | OK
6 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 6360.944 | 7166.0944 | 805.1504 | 1000 |  | 805150.4 | 808655.6976 | Mugdapara |  |  |  | Ahmedbagh | 808655.6976 | 863662.2068 | -55006.5092 | -6.369 | OK
1 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 739814 | 748752 | 8938 | 200 |  | 1787600 | 1795382.4839 | Mugdapara |  |  |  | Wasa Road | 1795382.4839 | 1921009.9451 | -125627.4612 | -6.5397 | OK
2 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 769845 | 777256 | 7411 | 200 |  | 1482200 | 1488652.8964 | Mugdapara |  |  |  | Nandipara | 1488652.8964 | 1652835.9122 | -164183.0158 | -9.9334 | OK
| AT-1 |  | 0.415 |  |  | 1 | 789.61 | 950.84 | 161.23 | 80 |  | 12898.4 | 12954.5544 | Mugdapara |  |  |  | AT-1 | 12954.5544 | 10606.4337 | 2348.1207 | 22.1386 | OK
3 | AT-2 |  | 0.415 |  | 63394003 | 1 | 399.81 | 475.19 | 75.38 | 80 |  | 6030.4 | 6056.6539 | Mugdapara |  |  |  | AT-2 | 6056.6539 | 7745.9106 | -1689.2567 | -21.8084 | OK
|  |  | 10: Total | 19967697.9184 | 19881143.5 | 19967697.9184 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 19967697.9184 | 19881143.5 | 19967697.9184 | 0.43536
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 4198499.3272
[6 empty] | Bashabo | at 33 KV level |  | 1825010.9149
[6 empty] | Maniknagar | at 33 KV level |  | 259324.0979
[6 empty] | Mugdapara | at 33 KV level |  | 13684863.5785
[6 empty] | Total = |  |  | 19967697.9184 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 |  | 33 | 0 | 76026300 | 1 | 6763.97 | 6785.52 | 21.55 | 360000 | 0 | 7758000 | 7786698.9333
9 | 33 kV Tejgaon U/G Feeder-2 |  | 33 | 0 | 06604453 | 1 | 6592.78 | 6628.97 | 36.19 | 360000 | 0 | 13028400 | 13076595.5636
0 | Tejgaon |  | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 20786400 | 20863294.4968
TEJGOAN 33 KV SIDE (RECEIVING)
|  |  | 7: 0; 8: 0; 10: Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  | 7: 0; 8: 0
1 | 33/11 kV Transfomer-1 (T1) |  | 33 | Export | DHK61080 | 1 | 731542.5 | 760200.3 | 28657.8 | 270 |  | 7737606
2 | 33/11 kV Transfomer-2 (T2) |  | 33 | Export | DHK61100 | 1 | 591197.8 | 639645 | 48447.2 | 180 |  | 8720496
3 | 33/11 kV Transfomer-3 (T3) |  | 33 | Export | BD001872 | 1 | 229532 | 235387.6 | 5855.6 | 180000 |  | 5855600
|  |  | 10: Total |  | 22313702 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 20863294.4968; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TEJGOAN 33 KV NET IMPORT |  | 20863294.4968
| IMPORT-2 |  | 6: TEJGOAN 33 KV NET IMPORT; 9=8-7: 20863294.4968 | 33 KV TX HV Side |  | 22313702
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -1450407.5032
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -6.952%
| TOTAL IMPORT |  | 4: 20863294.4968
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHK61079 | 1 | 919952.6 | 960009.4 | 40056.8 | 180 | 7210224 |  | 7431486.5026 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHK61082 | 1 | 832808 | 872676.3 | 39868.3 | 180 | 7176294 |  | 7396515.2816 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming |  | 11 | Import | BD001875 | 1 | 229532 | 235387.6 | 5855.6 | 1000 | 5855600 |  | 6035292.7127 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 20242118 |  | 20863294.4968 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | C110U | 11 |  | DHK60950 | 1 | 280751.8 | 305498.9 | 24747.1 | 60 |  | 1484826 | 1500089.328 | Tejgaon |  |  |  | Nakhal Para Feeder | 1500089.328 | 1599409.3479 | -99320.0198 | -6.2098 | OK
2 | Badda-Meghna Feeder | C110N | 11 |  | DHK60979 | 1 | 927571.6 | 940674.7 | 13103.1 | 60 |  | 786186 | 794267.6303 | Tejgaon |  |  |  | Badda-Meghna Feeder | 794267.6303 | 812324.781 | -18057.1507 | -2.2229 | OK
3 | Rasulbagh Feeder | C110K | 11 |  | DHK60948 | 1 | 52268.2 | 82062.5 | 29794.3 | 60 |  | 1787658 | 1806034.3017 | Tejgaon |  |  |  | Rasulbagh Feeder | 1806034.3017 | 1726738.2372 | 79296.0644 | 4.5922 | OK
4 | Lukas | C171V | 11 |  | 8A021100948-02 | 1 | 71541234 | 73546915 | 2005681 | 1 |  | 2005681 | 2026298.4778 | Tejgaon |  |  |  | Lukas | 2026298.4778 | 2352263.3192 | -325964.8414 | -13.8575 | OK
5 | PWD RMU |  | 11 |  |  | 1 | 658258.5 | 660047.1 | 1788.6 | 1 |  | 1788.6 | 1806.986 | Tejgaon |  |  |  | PWD RMU | 1806.986 | 1917.0903 | -110.1043 | -5.7433 | OK
1 | Civil Aviation Feeder |  | 11 |  | DHK60977 | 1 | 936848.6 | 984210.7 | 47362.1 | 60 |  | 2841726 | 2870937.6357 | Tejgaon |  |  |  | Civil Aviation Feeder | 2870937.6357 | 3006456.2987 | -135518.6631 | -4.5076 | OK
2 | Ahasanullah Eng. | C171L | 11 |  | DHK60867 | 1 | 891167.4 | 900589.8 | 9422.4 | 60 |  | 565344 | 571155.4762 | Tejgaon |  |  |  | Ahasanullah Eng. | 571155.4762 | 575802.5636 | -4647.0875 | -0.80706 | OK
3 | New GMG Feeder | C110M | 11 |  | DHK61106 | 1 | 120977.6 | 151809.7 | 30832.1 | 60 |  | 1849926 | 1868942.3881 | Tejgaon |  |  |  | New GMG Feeder | 1868942.3881 | 2083647.5312 | -214705.1431 | -10.3043 | OK
4 | Shikajo | C171Z | 11 |  | HA021101036-02 | 1 | 65204937 | 66059038 | 854101 | 1 |  | 854101 | 862880.7653 | Tejgaon |  |  |  | Shikajo | 862880.7653 | 832111.8625 | 30768.9027 | 3.6977 | OK
5 | Kahinur |  | 11 |  |  | 1 | 563203.8 | 584798.7 | 21594.9 | 60 |  | 1295694 | 1309013.1381 | Tejgaon |  |  |  | Kahinur | 1309013.1381 | 1330662.8857 | -21649.7476 | -1.627 | OK
6 | Link road | C171X | 11 |  | 8A021100380-02 | 1 | 65396105 | 66112857 | 716752 | 1 |  | 716752 | 724119.8808 | Tejgaon |  |  |  | Link road | 724119.8808 | 647867.3456 | 76252.5351 | 11.7698 | OK
7 | Shanta | C110E | 11 |  |  | 1 | 331155.2 | 341520.5 | 10365.3 | 60 |  | 621918 | 628311.0309 | Tejgaon |  |  |  | Shanta | 628311.0309 | 599004.2611 | 29306.7697 | 4.8926 | OK
1 | Karnafuly Feeder | C110Y | 11 |  | DHK61084 | 1 | 35882.9 | 36682 | 799.1 | 1000 |  | 799100 | 807314.3803 | Tejgaon |  |  |  | Karnafuly Feeder | 807314.3803 | 766856.2088 | 40458.1715 | 5.2758 | OK
2 | Butex | C110BT | 11 |  |  | 1 | 1193.8 | 1299 | 105.2 | 1000 |  | 105200 | 106281.4076 | Tejgaon |  |  |  | Butex | 106281.4076 | 100920.6493 | 5360.7583 | 5.3119 | OK
3 | OriON LAB | C171A | 11 |  |  | 1 | 8288014 | 8377954 | 89940 | 1 |  | 89940 | 90864.5418 | Tejgaon |  |  |  | OriON LAB | 90864.5418 | 93311.3932 | -2446.8514 | -2.6222 | OK
4 | Nina kabbo | C171Y | 11 |  | 201101025-2 | 1 | 17388563 | 17647767 | 259204 | 1 |  | 259204 | 261868.4978 | Tejgaon |  |  |  | Nina kabbo | 261868.4978 | 264819.2014 | -2950.7036 | -1.1142 | OK
5 | Satrong | C171S | 11 |  | HA021100515-2 | 1 | 95302967 | 97172731 | 1869764 | 1 |  | 1869764 | 1888984.3136 | Tejgaon |  |  |  | Satrong | 1888984.3136 | 2007795.2093 | -118810.8957 | -5.9175 | OK
6 | South East RMU |  | 11 |  |  | 1 | 994.7 | 1108.7 | 114 | 1000 |  | 114000 | 115171.8675 | Tejgaon |  |  |  | South East RMU | 115171.8675 | 137308.3735 | -22136.5059 | -16.1217 | OK
7 | Rangs Bhaban |  | 11 |  | HA021100939-2 | 1 | 731159 | 881462 | 150303 | 1 |  | 150303 | 151848.0457 | Tejgaon |  |  |  | Rangs Bhaban | 151848.0457 | 148545.345 | 3302.7007 | 2.2234 | OK
8 | Babli | C171R | 11 |  |  | 1 | 59368.5 | 60405.4 | 1036.9 | 1000 |  | 1036900 | 1047558.8549 | Tejgaon |  |  |  | Babli | 1047558.8549 | 1066401.5624 | -18842.7075 | -1.7669 | OK
| SPL |  | 11 |  |  | 1 | 4841.1 | 5307 | 465.9 | 1000 |  | 465900 | 470689.2376 | Tejgaon |  |  |  | SPL | 470689.2376 | 471130.5611 | -441.3235 | -0.093673 | OK
9 | DNCC Hospital |  | 11 |  |  | 1 | 16588.9 | 17538 | 949.1 | 1000 |  | 949100 | 958856.3113 | Tejgaon |  |  |  | DNCC Hospital | 958856.3113 | 1039161.0285 | -80304.7173 | -7.7278 | OK
| 11/.415 kv Local transformer |  | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
|  |  | 10: Grand Total | 20863294.4968 | 20651011.6 | 20863294.4968 | 1.028
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Tejgaon | at 33 KV level |  | 20863294.4968
[6 empty] | Total = |  |  | 20863294.4968 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 |  | 33 | 0 | 214393/44-2711 | 1 | 81.6289 | 89.5259 | 7.897 | 1000 | Estimated | 5302119.6 | 5408599.0077
12 | Asad Gate Circuit-2 |  | 33 |  | 214393/43-2711 | 1 | 9396.2208 | 9396.2208 | 0 | 1000 | Estimated | 7865364.6 | 8023320.1777
|  |  | 10: Total |  | 13167484.2 | 13431919.1854
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 33 | Import | DHKC9350 | 1 | 111497.5 | 111497.5 | 0 | 270 | 0
2 | Shatmasjid-2 |  | 33 | Import | DHKC9354 | 1 | 123054.55 | 123054.55 | 0 | 270 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  | 7: 0; 8: 0
1 | Transfomer-1 (T1) |  | 33 | Export | DHKC9353 | 1 | 136616.88 | 136616.88 | 0 | 180 |  | 0
2 | Transfomer-2 (T2) |  | 33 | Export | DHKC9305 | 1 | 121859.12 | 121859.12 | 0 | 180 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 4: 13431919.1854; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | ASADGATE 33 KV NET IMPORT |  | 13431919.1854
| IMPORT-2 |  | 6: ASADGATE 33 KV NET IMPORT; 9=8-7: 13431919.1854 | ASADGATE 11 KV NET IMPORT |  | 15815925.4972
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | -2384006.3118
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -17.75%
| TOTAL IMPORT |  | 4: 13431919.1854
11 KV SIDE of___ASADGATE 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming |  | 11 | Import | DHKC9371 | 1 | 5948.84 | 35405.06 | 29456.22 | 180 | 5302119.6 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming |  | 11 | Import | DHKC9337 | 1 | 22310.36 | 66006.83 | 43696.47 | 180 | 7865364.6 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 13167484.2 |  | 13431919.1854 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | D570T | 11 |  | DHKC9332 | 1 | 79412.59 | 82497.17 | 3084.58 | 60 |  | 185074.8 | 186647.9358 | Shere b.nagar |  |  |  | Gonobhaban | 186647.9358 | 199883.04 | -13235.1042 | -6.6214 | OK
2 | Rapa Plaza Feeder | D270R | 11 |  | DHKC9339 | 1 | 13619.17 | 31044.61 | 17425.44 | 60 |  | 1045526.4 | 1054413.3744 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1054413.3744 | 1089910.392 | -35497.0176 | -3.2569 | OK
3 | Shukrabad/ South Plaza | D570S | 11 |  | DHKC9324 | 1 | 53201.34 | 71432.99 | 18231.65 | 60 |  | 1093899 | 1103197.1415 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 1103197.1415 | 1099590.636 | 3606.5055 | 0.32799 | OK
4 | Wasa O/H | C270W | 11 |  | DHKC9333 | 1 | 46540.01 | 58765.81 | 12225.8 | 60 |  | 733548 | 739783.158 | Satmasjid |  |  |  | Wasa O/H | 739783.158 | 1806723.552 | -1066940.394 | -59.0539 | CHECK
5 | Bangabandhu Memorial Museum |  | 11 |  | DHKC9334 | 1 | 16026.67 | 16332.37 | 305.7 | 60 |  | 18342 | 18497.907 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 18497.907 | 17876.394 | 621.513 | 3.4767 | OK
6 | Iqbal Road O/H | D470Q | 11 |  | DHKC9330 | 1 | 24076.29 | 48276.24 | 24199.95 | 60 |  | 1451997 | 1464338.9745 | Shyamoli |  |  |  | Iqbal Road O/H | 1464338.9745 | 1539511.488 | -75172.5135 | -4.8829 | OK
7 | Town Hall | D470W | 11 |  | DHKC9351 | 1 | 70678.83 | 103102.61 | 32423.78 | 60 |  | 1945426.8 | 1961962.9278 | Shyamoli |  |  |  | Town Hall | 1961962.9278 | 2111520.342 | -149557.4142 | -7.0829 | OK
8 | Post Office | D470P | 11 |  | DHKC9331 | 1 | 9701.3 | 33036.5 | 23335.2 | 60 |  | 1400112 | 1412012.952 | Shyamoli |  |  |  | Post Office | 1412012.952 | 1209158.466 | 202854.486 | 16.7765 | OK
9 | Shangshad Bhaban |  | 11 |  | DHKC9370 | 1 | 22456.58 | 24023.67 | 1567.09 | 60 |  | 94025.4 | 94824.6159 | Shere b.nagar |  |  |  | Shangshad Bhaban | 94824.6159 | 417958.806 | -323134.1901 | -77.3124 | CHECK
10 | Jakir Hossain Road | C270J | 11 |  | DHKC9373 | 1 | 43058.44 | 67793.29 | 24734.85 | 60 |  | 1484091 | 1496705.7735 | Satmasjid |  |  |  | Jakir Hossain Road | 1496705.7735 | 741916.104 | 754789.6695 | 101.7352 | FAULT
11 | New Colony O/H Feeder | C270N | 11 |  | DHKC9369 | 1 | 14193.96 | 31606.58 | 17412.62 | 60 |  | 1044757.2 | 1053637.6362 | Satmasjid |  |  |  | New Colony O/H Feeder | 1053637.6362 | 236025.486 | 817612.1502 | 346.4084 | FAULT
12 | Aurangzeb Feeder | D470M | 11 |  | DHKC9321 | 1 | 7329.59 | 34889.71 | 27560.12 | 60 |  | 1653607.2 | 1667662.8612 | Shyamoli |  |  |  | Aurangzeb Feeder | 1667662.8612 | 711485.208 | 956177.6532 | 134.3918 | FAULT
13 | Asadgate Local Feeder | C270E | 11 |  | DHKC9338 | 1 | 17111.13 | 42257.12 | 25145.99 | 60 |  | 1508759.4 | 1521583.8549 | Satmasjid |  |  |  | Asadgate Local Feeder | 1521583.8549 | 1037091.432 | 484492.4229 | 46.7165 | FAULT
14 | Sonarbangla Road | D470R | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | D470H | 11 |  | DHKC9366 | 1 | 27223.31 | 57194.89 | 29971.58 | 60 |  | 1798294.8 | 1813580.3058 | Shyamoli |  |  |  | Humayun Road | 1813580.3058 | 1032128.898 | 781451.4078 | 75.7126 | FAULT
16 | NHA | D470B | 11 |  | DHKC9374 | 1 | 62223.75 | 65850.12 | 3626.37 | 60 |  | 217582.2 | 219431.6487 | Shyamoli |  |  |  | NHA | 219431.6487 | 72214.596 | 147217.0527 | 203.8605 | FAULT
17 | Auxiliary transformer |  | 0.415 |  |  | 1 | 659515 | 667095 | 7580 | 1 |  | 7580 | 7644.43 | Satmasjid |  |  |  | Auxiliary transformer | 7644.43 | 8345.63 | -701.2 | -8.402 | OK
|  |  | 10: Grand Total | 15815925.4972 | 15682623.2 | 15815925.4972 | 0.85
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 1384669.6932
[6 empty] | Dhanmondi | at 33 KV level |  | 1072911.2814
[6 empty] | Satmasjid | at 33 KV level |  | 4819354.8526
[6 empty] | Shyamoli | at 33 KV level |  | 8538989.67
at 33 KV level
[6 empty] | Total = |  |  | 15815925.4972 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 |  | 33 | Export | SIEM0504 | 1 | 112863 | 116881 | 4018 | 2000 | 0 | 8036000 | 8044741.8266
4 | Banasree-2 |  | 33 | Export | SIEM0506 | 1 | 96502 | 100415 | 3913 | 2000 | 0 | 7826000 | 7834513.3816
|  |  | 10: Total |  | 15862000 | 15879255.2082 | 0.10878
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import |  | 1 | 15589610 | 15589610 | 0 | 1 | 0
2 | Madertek Circuit-02 |  | 33 | Import |  | 1 | 11242090 | 11242090 | 0 | 1 | 0
3 | Ullon O/H |  | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
|  |  | 10: Total | 0 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 |  | 33 | Export | 14 | 1 | 11612560 | 11612560 | 0 | 1 |  | 0
2 | Transformer-02 |  | 33 | Export | 74 | 1 | 13639440 | 13639440 | 0 | 1 |  | 0 |  |  | Meter Problem
|  |  | 10: Total |  | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 4: 15879255.2082; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 15879255.2082
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 15879255.2082 | 33 KV TX HV SIDE |  | 0
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 15879255.2082
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 100%
| TOTAL IMPORT |  | 4: 15879255.2082
11 KV SIDE of___BANASREE 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 0 |  | #DIV/0! |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | 198 | 1 | 0 | 0 | 0 | 1 | 0 |  | #DIV/0! | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 0 |  | 15879255.2082 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | F292A | 11 |  | 141 | 1 | 391040 | 2417760 | 2026720 | 1 |  | 2026720 | 2051370.0659 | Banosree |  |  |  | Angur Jora | 2051370.0659 | 2226512.8044 | -175142.7384 | -7.8662 | OK
2 | Block F-G Avenue | F299G | 11 |  | 68 | 1 | 3403100 | 5525600 | 2122500 | 1 |  | 2122500 | 2148314.9942 | Banosree |  |  |  | Block F-G Avenue | 2148314.9942 | 2658158.1289 | -509843.1348 | -19.1803 | OK
3 | Banasree Main Road(Monpura) | F292P | 11 |  | 168 | 1 | 9274200 | 10276520 | 1002320 | 1 |  | 1002320 | 1014510.7585 | Banosree |  |  |  | Banasree Main Road(Monpura) | 1014510.7585 | 1233831.441 | -219320.6825 | -17.7756 | OK
4 | Baitul Kuddus | F292Q | 11 |  | 62 | 1 | 4111160 | 6205400 | 2094240 | 1 |  | 2094240 | 2119711.2807 | Banosree |  |  |  | Baitul Kuddus | 2119711.2807 | 2318179.6901 | -198468.4094 | -8.5614 | OK
5 | Ideal | F214I | 11 |  |  | 1 | 9849120 | 10538960 | 689840 | 1 |  | 689840 | 698230.2076 | Banosree |  |  |  | Ideal | 698230.2076 | 798010.2701 | -99780.0626 | -12.5036 | OK
6 | Central Mosque | F292C | 11 |  | 46 | 1 | 4361840 | 6352040 | 1990200 | 1 |  | 1990200 | 2014405.8899 | Banosree |  |  |  | Central Mosque | 2014405.8899 | 2216426.2192 | -202020.3293 | -9.1147 | OK
7 | Larive | F299L | 11 |  | 47 | 1 | 1887400 | 3120560 | 1233160 | 1 |  | 1233160 | 1248158.3596 | Banosree |  |  |  | Larive | 1248158.3596 | 1177386.9105 | 70771.4491 | 6.0109 | OK
8 | Bank Colony | A299K | 11 |  |  | 1 | 6193200 | 8053280 | 1860080 | 1 |  | 1860080 | 1882703.3 | Khilgaon |  |  |  | Bank Colony | 1882703.3 | 767992.5927 | 1114710.7073 | 145.146 | FAULT
9 | Salambagh | A299G | 11 |  |  | 1 | 5088040 | 6381080 | 1293040 | 1 |  | 1293040 | 1308766.6526 | Khilgaon |  |  |  | Salambagh | 1308766.6526 | 927562.3697 | 381204.2828 | 41.0974 | FAULT
10 | Titas Road | A299T | 11 |  |  | 1 | 3258920 | 4635200 | 1376280 | 1 |  | 1376280 | 1393019.0625 | Khilgaon |  |  |  | Titas Road | 1393019.0625 | 401204.0106 | 991815.0519 | 247.2097 | FAULT
11 | AT-1 |  | 0.415 |  | 7734 | 1 | 3471 | 3534.86 | 63.86 | 1 |  | 63.86 | 64.6367 | Banosree |  |  |  | AT-1 | 64.6367 | 66.5715 | -1.9348 | -2.9063 | OK
12 | AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 15879255.2082 | 15688443.86 | 15879255.2082 | 1.2163
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 11294766.1931
[6 empty] | Khilgaon | at 33 KV level |  | 4584489.0151
[6 empty] | Total = |  |  | 15879255.2082 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran |  | 33 | Export | SIEM0510 | 1 | 360310 | 365258 | 4948 | 2000 | 0 | 9896000 | 9906765.1961
ULLON 33 KV SIDE | bar: 4
1 | Goran |  | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total | 0 | 9896000 | 9906765.1961
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 |  | 33 | Import | HA-030701133-03 | 1 | 108926360 | 108926360 | 0 | 1 | 0
2 | Ullon O/H |  | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GORAN 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | HA-030800176-03 | 1 | 21133914 | 23372460 | 2238546 | 1 |  | 2238546
2 | Transformer-02 |  | 33 | Export | HA-030701133-03 | 1 | 87707866 | 91501130 | 3793264 | 1 |  | 3793264
3 | Transformer-03 |  | 33 | Export | DHK-57075 | 1 | 12123.64 | 12285.5 | 161.86 | 120000 |  | 3864190 |  |  | Problem
|  |  | 10: Total |  | 9896000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 4: 9906765.1961; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9906765.1961
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 9906765.1961 | 33 KV TX HV SIDE |  | 9896000
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 10765.1961
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.1087%
| TOTAL IMPORT |  | 4: 9906765.1961
11 KV SIDE of___GORAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming |  | 11 | IMPORT |  | 1 | 61719009 | 63953260 | 2234251 | 1 | 2234251 |  | 2237900.1708
| 33/11 kV Transfomer-2 Incoming |  | 11 |  |  | 1 | 95219964 | 99003240 | 3783276 | 1 | 3783276 |  | 3789455.1716
| 33/11 kV Transfomer-3 Incoming |  | 11 |  |  | 1 | 80170676 | 84043760 | 3873084 | 1 | 3873084 |  | 3879409.8537
|  |  | 7: 0; 8: 0; 10: Total | 9890611 |  | 9906765.1961
| GORAN 11 KV SIDE |  | 7: 0; 8: 0
1 | Meradia | F214M | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 160 | 376669.44 | 378160.5224 | Banosree | 6 days Load Calculated |  |  | Meradia | 378160.5224 | 0 | 378160.5224 | #DIV/0! | #DIV/0!
2 | Shipahibagh | A914S | 11 |  | HA-021001030-02 | 1 | 40881162 | 42070870 | 1189708 | 1 |  | 1189708 | 1194417.5741 | Bashabo |  |  |  | Shipahibagh | 1194417.5741 | 1488941.4076 | -294523.8335 | -19.7808 | OK
3 | Farazi Hospital | F214F | 11 |  | HA-030701081-03 | 1 | 51063880 | 51724280 | 660400 | 1 |  | 660400 | 663014.2572 | Banosree | Start again from SEP-23 |  |  | Farazi Hospital | 663014.2572 | 614880.5841 | 48133.6732 | 7.8281 | OK
4 | West Bansree | F214W | 11 |  | New Meter | 1 | 96909074 | 98404140 | 1495066 | 1 |  | 1495066 | 1500984.3633 | Banosree |  |  |  | West Bansree | 1500984.3633 | 1948580.2361 | -447595.8729 | -22.9704 | OK
5 | Model School(Nearest) | F214D | 11 |  | HA-030701099-03 | 1 | 22464572 | 24729160 | 2264588 | 1 |  | 2264588 | 2273552.5905 | Banosree |  |  |  | Model School(Nearest) | 2273552.5905 | 2474165.667 | -200613.0765 | -8.1083 | OK
6 | Bhuiyan Para | F214V | 11 |  | HA-021100508-02 | 1 | 60667692 | 63138610 | 2470918 | 1 |  | 2470918 | 2480699.3677 | Banosree |  |  |  | Bhuiyan Para | 2480699.3677 | 2656699.6806 | -176000.3129 | -6.6248 | OK
7 | Bonobithi (Ideal) School | F214B | 11 |  | HA-021100879-02 | 1 | 18782519 | 20164310 | 1381791 | 1 |  | 1381791 | 1387260.9532 | Banosree |  |  |  | Bonobithi (Ideal) School | 1387260.9532 | 1569496.2633 | -182235.31 | -11.6111 | OK
8 | AT-01 |  | 0.415 |  | 3043122 | 1 | 7023.2 | 7030.2 | 7 | 80 |  | 560 | 562.2168 | Banosree |  |  |  | AT-01 | 562.2168 | 0 | 562.2168 | #DIV/0! | #DIV/0!
9 | AT-02 |  | 0.415 |  | 3043146 | 1 | 4935.3 | 5084.2 | 148.9 | 80 |  | 11912 | 11959.1548 | Banosree |  |  |  | AT-02 | 11959.1548 | 5508.1614 | 6450.9934 | 117.117 | FAULT
|  |  | 10: Grand Total | 9890611 | 9851612.44 | 9890611 | 0.39586
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Banosree | at 33 KV level |  | 8696193.4259
[6 empty] | Bashabo | at 33 KV level |  | 1194417.5741
[6 empty] | Total = |  |  | 9890611 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 |  | 33 | 0 | SICAM | 1 | 30.1 | 4612 | 4581.9 | 1000 | Estimated | 13778010 | 14054705.8227
|  |  | 10: Total |  | 13778010 | 14054705.8227
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
2 | Shatmasjid-2 |  | 3: 33; 4: Import; 6: 1; 9=8-7: 0 | 0
3 | Kallayanpur |  | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
|  |  | 10: Total | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 |  | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 |  | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE |  | 4: 14054705.8227; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALMATIA 33 KV NET IMPORT |  | 14054705.8227
| IMPORT-2 |  | 6: LALMATIA 33 KV NET IMPORT; 9=8-7: 14054705.8227 | LALMATIA 11 KV NET IMPORT |  | 13778010
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 276695.8227
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.969%
| TOTAL IMPORT |  | 4: 14054705.8227
11 KV SIDE of___LALMATIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming |  | 11 | Import | DHK000180 | 1 | 2935017 | 3002013 | 66996 | 90 | 6029640 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming |  | 11 | Import | DHK000177 | 1 | 2967813 | 3053906 | 86093 | 90 | 7748370 | [9 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 13778010 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1459594.08 | 1468016.3082 | Dhanmondi | Estimated | 160 |  | Shankor O/H | 1468016.3082 | 1541495.5501 | -73479.242 | -4.7668 | OK
2 | Bangabobondhu museum | D207B | 11 | Export |  | 1 | 629342 | 629342 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 100 |  | Bangabobondhu museum | 0 | 1906.9492 | -1906.9492 | -100 | CHECK
3 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 84603836 | 86479670 | 1875834 | 1 |  | 1875834 | 1886658.0381 | Dhanmondi |  | 60 |  | Road No-13/A | 1886658.0381 | 1858256.0346 | 28402.0035 | 1.5284 | OK
4 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 5564310 | 7608679 | 2044369 | 1 |  | 2044369 | 2056165.5278 | Dhanmondi |  | 20 |  | Jaforabad | 2056165.5278 | 2227970.4742 | -171804.9464 | -7.7113 | OK
5 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  | 120 |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26012.1 | 26183.9 | 171.8 | 3333.33 |  | 572666.094 | 575970.5227 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 575970.5227 | 619531.2198 | -43560.6971 | -7.0312 | OK
1 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 70587.5 | 71012.2 | 424.7 | 3333.33 |  | 1415665.251 | 1423833.9987 | Dhanmondi |  |  |  | Road No -15 | 1423833.9987 | 1532206.4801 | -108372.4814 | -7.073 | OK
2 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 78600.4 | 79007.3 | 406.9 | 3333.33 |  | 1356331.977 | 1364158.3566 | Dhanmondi |  |  |  | Road No-27 South | 1364158.3566 | 1534221.2158 | -170062.8592 | -11.0846 | OK
| Road 25 | D207C | 11 | Export |  | 1 | 71004.7 | 71389.6 | 384.9 | 3333.3 |  | 1282987.17 | 1290390.3315 | Dhanmondi |  |  |  | Road 25 | 1290390.3315 | 1318296.8446 | -27906.5131 | -2.1169 | OK
3 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38100.5 | 38220.6 | 120.1 | 3333.33 |  | 400332.933 | 402642.9556 | Dhanmondi |  |  |  | Ibne Sina | 402642.9556 | 432160.8021 | -29517.8465 | -6.8303 | OK
4 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 62122937 | 63193708 | 1070771 | 1 |  | 1070771 | 1076949.6203 | Dhanmondi |  |  |  | Road No-31 (PARI) | 1076949.6203 | 939422.8232 | 137526.7971 | 14.6395 | OK
5 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 73910799 | 76131211 | 2220412 | 1 |  | 2220412 | 2233224.3406 | Dhanmondi |  |  |  | Satmoszid Road West | 2233224.3406 | 2307141.6064 | -73917.2658 | -3.2038 | OK
|  |  | 10: Grand Total | 13778010 | 13698963.505 | 13778010 | 0.57703
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Dhanmondi | at 33 KV level |  | 13778010
[6 empty] | Total = |  |  | 13778010 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) |  | 33 | 0 | BD001918 | 1 | 2145.29 | 2172.52 | 27.23 | 240000 | 0 | 6535200 | 6561671.5077
23 | Green Road Circuit-1 |  | 33 | 0 | BD001865 | 1 | 1473.63 | 1502.1 | 28.47 | 240000 | 0 | 6832800 | 6860476.9675
|  |  | 10: Total | 0 | 13368000 | 13422148.4753
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory |  | 3: 33; 4: EXPORT |  | 0
| Green Road Dormatory |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0
| 33/11 KV Transformer No.2. |  | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0
|  |  | 10: Total |  | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 4: 13422148.4753; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | Green Road 33 KV NET IMPORT |  | 13422148.4753
| IMPORT-2 |  | 6: Green Road 33 KV NET IMPORT; 9=8-7: 13422148.4753 | Green Road 11 KV NET IMPORT |  | 13422148.4753
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 13422148.4753 | LOSS UNITS=> |  | 0
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 13422148.4753
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 00138 | 1 | 3188963 | 3265238 | 76275 | 100 | 7627500
2 | Transfomer-2 Incoming |  | 11 | Import | HA-021101496 | 1 | 4221.0772 | 5650.806 | 1429.7288 | 10000 | 6535200
|  |  | 7: 0; 8: 0; 10: Total | 14162700 |  | 13422148.4753
| Green Road 11 KV SIDE |  | 7: 0; 8: 0 | [5 empty] | 125
1 | Lab aid/local RMU | C302L | 11 |  | 3C65883 | 1 | 68698 | 73195 | 4497 | 300 |  | 1349100 | 1368745.9116 | Paribag |  | 30 |  | Lab aid/local RMU | 1368745.9116 | 1391721.2231 | -22975.3115 | -1.6509 | OK
2 | Green View | C302V | 11 |  | DHK000151 | 1 | 67971.6 | 68313.2 | 341.6 | 3333.33 |  | 1138665.528 | 1155247.0433 | Paribag |  | 95 |  | Green View | 1155247.0433 | 1226741.8962 | -71494.8529 | -5.828 | OK
3 | Central Road | C302C | 11 |  | 65943 | 1 | 32548 | 37616 | 5068 | 300 |  | 1520400 | 1542540.4225 | Paribag |  | 31.6667 |  | Central Road | 1542540.4225 | 1699791.5522 | -157251.1296 | -9.2512 | OK
4 | New Market | D802N | 11 |  | DHK000194 | 1 | 47323.8 | 47697.9 | 374.1 | 3333.33 |  | 1246998.753 | 1265157.8423 | Jigatola |  | 61.6667 |  | New Market | 1265157.8423 | 1241755.0551 | 23402.7871 | 1.8847 | OK
5 | DPH Feeder |  | 11 |  | HA-021100459 | 1 | 41862.9 | 41984 | 121.1 | 1 | 25 | 304082.1 | 308510.2151 | Paribag | Estimated |  |  | DPH Feeder | 308510.2151 | 353437.7385 | -44927.5234 | -12.7116 | OK
6 | Dhanmondi Rd 4(md Banglo | D802F | 11 |  | 6604464 | 1 | 4552.33 | 4573.53 | 21.2 | 60000 |  | 1272000 | 1290523.1633 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1290523.1633 | 1536748.4833 | -246225.32 | -16.0225 | OK
1 | Green Road East | C302X | 11 |  | HA-021101050 | 1 | 98378742 | 99752905 | 1374163 | 1 |  | 1374163 | 1394173.8849 | Paribag |  |  |  | Green Road East | 1394173.8849 | 1544603.3759 | -150429.491 | -9.739 | OK
2 | North Road | C302Z | 11 |  | HA-021100884 | 1 | 83668870 | 85256362 | 1587492 | 1 |  | 1587492 | 1610609.432 | Paribag |  |  |  | North Road | 1610609.432 | 1705708.7444 | -95099.3124 | -5.5754 | OK
3 | Green road SS | C302W | 11 |  | DHK00135 | 1 | 21043782 | 22261302 | 1217520 | 1 |  | 1217520 | 1235249.8127 | Paribag |  |  |  | Green road SS | 1235249.8127 | 1304162.391 | -68912.5783 | -5.284 | OK
4 | Plane Moszid | C302A | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 729797.04 | 740424.5162 | Paribag | Estimated |  |  | Plane Moszid | 740424.5162 | 1001406.9258 | -260982.4096 | -26.0616 | OK
5 | Malancha | C302H | 11 |  | HA-021100953 | 1 | 36299925 | 37784204 | 1484279 | 1 |  | 1484279 | 1505893.42 | Paribag |  |  |  | Malancha | 1505893.42 | 1581374.6424 | -75481.2223 | -4.7731 | OK
| AT -1 |  | 7: 22891; 8: 22891; 10: 1 |  | 5000 | 5072.8112 | Paribag |  |  |  | AT -1 | 5072.8112 | 5004.3913 | 68.4199 | 1.3672 | OK
|  |  | 10: Grand Total | 13422148.4753 | 13229497.421 | 13422148.4753 | 1.4562
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 10866467.4697
[6 empty] | Jigatola | at 33 KV level |  | 2555681.0055
[6 empty] | Total = |  |  | 13422148.4753 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory |  | 33 | 0 | 76026305 | 1 | 8095.81 | 8111.66 | 15.85 | 180000 | Reading From G. Dormitory Side | 5668090 | 5689057.7928
|  |  | 10: Total | 0 | 5668090 | 5689057.7928
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 |  | 33 | 0 | 0 | 1 | 23.76 | 33.92 | 10.16 | 360000 | 0 | 3657600 | 3654211.644
9 | Green Road -2 |  | 33 | 0 | 0 | 1 | 64.23 | 77.32 | 13.09 | 360000 | 0 | 4712400 | 4708034.4901
|  |  | 10: Total | 0 | 8370000 | 8362246.1341
| GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) | [10 empty] | 14038090 | 14051303.9269
1 | Mogbazar Grid |  | 33 | Import | BD 017064 | 1 | 51596.7 | 57264.79 | 5668.09 | 1000 | 5668090
2 | Green Road SS |  | 33 | Import | BD 017070 | 1 | 32911.3 | 32923.13 | 11.83 | 1000 | 11830
3 | Jigatola Ckt-1 |  | 33 | Import |  | 1 | 8490.31 | 12056.02 | 3565.71 | 1000 | 3565710
NEW | Jigatola Ckt-2 |  | 33 |  |  | 1 | 23084.08 | 27752.82 | 4668.74 | 1000 | 4668740 |  |  |  | NEW FOUND
|  |  | 7: 0; 8: 0; 10: Total | 13914370 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  | 7: 0; 8: 0
1 | Transformer-01 |  | 33 | Export | BD 017065 | 1 | 108288.53 | 108288.53 | 0 | 888.89 |  | 0
2 | Transformer-02 |  | 33 | Export | BD 017069 | 1 | 105577.05 | 105577.05 | 0 | 888.89 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 4: 14051303.9269; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 14051303.9269
|  |  | 6: GREEN ROAD DORMITORY 33 KV NET IMPORT; 9=8-7: 14051303.9269 | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 14051303.9269
|  |  | 6: TOTAL EXPORT; 9=8-7: 14051303.9269 | LOSS UNITS=> |  | 0
|  |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 14051303.9269
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD 014050 | 1 | 100124.44 | 100124.44 | 0 | 1000 | 0
2 | Transformer-02 Incoming |  | 11 | Import | BD 014059 | 1 | 86324.36 | 90985.34 | 4660.98 | 1000 | 4660980
|  |  | 7: 0; 8: 0; 10: Total | 4660980 |  | 14051303.9269
| GREEN ROAD DORMITORY 11 KV SIDE |  | 7: 0; 8: 0
1 | North Dhanmondi | C31002 | 11 |  | BD 014039 | 1 | 22691.77 | 23293.96 | 602.19 | 2000 |  | 1204380 | 1220415.3715 | Paribag |  |  |  | North Dhanmondi | 1220415.3715 | 539516.6063 | 680898.7651 | 126.2053 | FAULT
2 | Lake circus | C31004 | 11 |  | BD 014047 | 1 | 37594.03 | 38490.6 | 896.57 | 2000 |  | 1793140 | 1817014.2474 | Paribag |  |  |  | Lake circus | 1817014.2474 | 1989795.0818 | -172780.8345 | -8.6833 | OK
3 | Bashir Uddin | C31003 | 11 |  | BD 014037 | 1 | 15223.59 | 15568.84 | 345.25 | 2000 |  | 690500 | 699693.4639 | Paribag |  |  |  | Bashir Uddin | 699693.4639 | 775365.5929 | -75672.1291 | -9.7595 | OK
4 | Raza Bazar | D5100R | 11 |  | BD 013939 | 1 | 22591.2 | 23208.95 | 617.75 | 2000 |  | 1235500 | 1251949.7098 | Shere b.nagar |  |  |  | Raza Bazar | 1251949.7098 | 1335486.8536 | -83537.1438 | -6.2552 | OK
5 | Rasel Squar | D5100RS | 11 |  | BD 013970 | 1 | 34305.82 | 35203.1 | 897.28 | 2000 |  | 1794560 | 1818453.1535 | Shere b.nagar |  |  |  | Rasel Squar | 1818453.1535 | 1979472.6721 | -161019.5186 | -8.1345 | OK
6 | Bow Bazar | D5100O | 11 |  | BD 013967 | 1 | 25458.37 | 26056.32 | 597.95 | 2000 |  | 1195900 | 1211822.467 | Shere b.nagar |  |  |  | Bow Bazar | 1211822.467 | 1271865.4648 | -60042.9979 | -4.7209 | OK
7 | BRB Hospital | D5100S | 11 |  | BD 014003 | 1 | 13677.42 | 14075.99 | 398.57 | 2000 |  | 797140 | 807753.2915 | Shere b.nagar |  |  |  | BRB Hospital | 807753.2915 | 817558.9445 | -9805.653 | -1.1994 | OK
8 | Green Road North | C31008 | 11 |  | BD 013969 | 1 | 16578.98 | 17173.89 | 594.91 | 2000 |  | 1189820 | 1205661.5166 | Paribag |  |  |  | Green Road North | 1205661.5166 | 1207219.8681 | -1558.3516 | -0.12909 | OK
1 | Water Bhaban | D5100PB | 11 |  | BD 014004 | 1 | 5421.06 | 5589.6 | 168.54 | 2000 |  | 337080 | 341567.9548 | Shere b.nagar |  |  |  | Water Bhaban | 341567.9548 | 321038.9901 | 20528.9647 | 6.3945 | OK
2 | Alamin Road | C31007 | 11 |  | BD 014006 | 1 | 19151.62 | 19439.5 | 287.88 | 2000 |  | 575760 | 583425.7911 | Paribag |  |  |  | Alamin Road | 583425.7911 | 637499.1681 | -54073.377 | -8.4821 | OK
3 | Katal Bagan | C3100K | 11 |  |  | 1 | 9924.75 | 10936.14 | 1011.39 | 2000 |  | 2022780 | 2049711.7232 | Paribag |  |  |  | Katal Bagan | 2049711.7232 | 2213293.3253 | -163581.6022 | -7.3909 | OK
4 | Eastern Pantho chaya | C310010 | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan |  | 11 |  | BD 014005 | 1 | 6072.12 | 6224.11 | 151.99 | 2000 |  | 303980 | 308027.2544 | Paribag |  |  |  | Kalabagan | 308027.2544 | 333048.3305 | -25021.0761 | -7.5127 | OK
6 | Univer Hospital | C310012 | 11 |  | BD 013963 | 1 | 1154.01 | 1281.57 | 127.56 | 2000 |  | 255120 | 258516.7219 | Paribag |  |  |  | Univer Hospital | 258516.7219 | 265852.2552 | -7335.5332 | -2.7593 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 |  | BD 013971 | 1 | 10293.69 | 10529.2 | 235.51 | 2000 |  | 471020 | 477291.2605 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 477291.2605 | 521121.028 | -43829.7676 | -8.4107 | OK
|  |  | 10: Grand Total | 14051303.9269 | 13866680 | 14051303.9269 | 1.3314
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag | at 33 KV level |  | 8619757.3503
[6 empty] | Shere b.nagar | at 33 KV level |  | 5431546.5766
[6 empty] | Total = |  |  | 14051303.9269 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 |  | 33 | Export | BD001906 | 1 | 1629.0994 | 1666.769 | 37.6696 | 240000 | 0 | 9040704 | 9041864.5151
2 | Taltala-2 |  | 33 |  | BD001837 | 1 | 2596.7593 | 2610.6135 | 13.8542 | 240000 | 0 | 3325008 | 3325434.8165
|  |  | 10: Total | 0 | 12365712 | 12367299.3317
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming |  | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 |  | 0
| 33 KV Ullon-ckt-2 incoming |  | 3: 33; 6: 1; 9=8-7: 0; 10: 1000 |  | 0
|  |  | 10: Total |  | 0 | 12367299.3317
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) |  | 3: 33; 4: EXPORT |  | 0
| 33 KV Khilgaon Feeder(Import) |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. |  | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
| 33/11 KV Transformer No.2. |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
|  |  | 10: Total |  | 0 | 12367299.3317 | #DIV/0!
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 4: 12367299.3317; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TALTOLA 33 KV NET IMPORT |  | 12367299.3317
| IMPORT-2 |  | 6: TALTOLA 33 KV NET IMPORT; 9=8-7: 12367299.3317 | TALTOLA 11 KV NET IMPORT |  | 12070400
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 12367299.3317 | LOSS UNITS=> |  | 296899.3317
| IMPORT-4 |  | 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 2.401%
| TOTAL IMPORT |  | 4: 12367299.3317
11 KV SIDE of___TALTOLA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming |  | 11 | Import | 06604431 | 1 | 8652.51 | 8689.58 | 37.07 | 160000 | 5931200
2 | Transformer-02 Incoming |  | 11 | Import | 06604341 | 1 | 9372.1 | 9410.47 | 38.37 | 160000 | 6139200
3 | Transformer-03 Incoming |  | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
|  |  | 7: 0; 8: 0; 10: Total | 12070400 |  | 12367299.3317
| TALTOLA 11 KV SIDE |  | 7: 0; 8: 0
1 | Matir Masjid | A229S | 11 |  | DHK00170 | 1 | 27323.3 | 29471.9 | 2148.6 | 888.8889 |  | 1909866.6667 | 1914137.6974 | Khilgaon |  |  |  | Matir Masjid | 1914137.6974 | 2132185.0742 | -218047.3768 | -10.2265 | OK
2 | Hajipara | A229P | 11 |  | DHK-00108 | 1 | 5735.6 | 6219.3 | 483.7 | 2222.2222 |  | 1074888.8889 | 1077292.6606 | Khilgaon |  |  |  | Hajipara | 1077292.6606 | 2330316.32 | -1253023.6593 | -53.7705 | CHECK
3 | Nearest Feeder | A929N | 11 |  | DHK-00106 | 1 | 91286.8 | 91617.7 | 330.9 | 2222.222 |  | 735333.2598 | 736977.684 | Bashabo |  |  |  | Nearest Feeder | 736977.684 | 448845.991 | 288131.693 | 64.1939 | FAULT
4 | Reazbagh | A229C | 11 |  | DHK-00109 | 1 | 97567.1 | 98320.2 | 753.1 | 2222.222 |  | 1673555.3882 | 1677297.9566 | Khilgaon |  |  |  | Reazbagh | 1677297.9566 | 1831327.1429 | -154029.1863 | -8.4108 | OK
5 | Chowdhury Para | A229F | 11 |  | DHK-00107 | 1 | 53017.5 | 53269.4 | 251.9 | 2222.222 |  | 559777.7218 | 561029.5515 | Khilgaon |  |  |  | Chowdhury Para | 561029.5515 | 662951.963 | -101922.4115 | -15.374 | OK
6 | Model Colleg | A229D | 11 |  | 9122392 | 1 | 2570.74 | 2584.74 | 14 | 40000 |  | 560000 | 561252.3268 | Khilgaon |  |  |  | Model Colleg | 561252.3268 | 1334690.1699 | -773437.8431 | -57.9489 | CHECK
1 | East Rampura | A229B | 11 |  | DHK-00181 | 1 | 99303.7 | 99587.6 | 283.9 | 2222.222 |  | 630888.8258 | 632299.6811 | Khilgaon |  |  |  | East Rampura | 632299.6811 | 1183684.3115 | -551384.6304 | -46.5821 | CHECK
2 | Adarshabagh | A929A | 11 |  | DHK-00090 | 1 | 51475.5 | 52389.5 | 914 | 2222.222 |  | 2031110.908 | 2035653.077 | Bashabo |  |  |  | Adarshabagh | 2035653.077 | 2182105.9426 | -146452.8656 | -6.7115 | OK
3 | Khailgaon Govt Colony | A229K | 11 |  | DHK00167 | 1 | 76520.9 | 77198.2 | 677.3 | 2222.222 |  | 1505110.9606 | 1508476.8371 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1508476.8371 | 1632974.0455 | -124497.2084 | -7.624 | OK
4 | TV Road | A214T | 11 |  | 6604434 | 1 | 5138.95 | 5147.41 | 8.46 | 40000 |  | 338400 | 339156.7632 | Khilgaon |  |  |  | TV Road | 339156.7632 | 1446513.4037 | -1107356.6405 | -76.5535 | CHECK
5 | Post Office |  | 11 |  | 06604476 | 1 | 6610.69 | 6635.86 | 25.17 | 40000 |  | 1006800 | 1009051.5047 | Bashabo |  |  |  | Post Office | 1009051.5047 | 850255.946 | 158795.5587 | 18.6762 | OK
1 | Navana | A929V | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | A929P | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 |  | 0.415 |  | 9187958 | 1 | 568.08 | 787.71 | 219.63 | 80 |  | 17570.4 | 17609.6926 | Bashabo |  |  |  | AT-01 | 17609.6926 | 22368.6405 | -4758.9478 | -21.2751 | OK
3 | AT-02 |  | 0.415 |  | 9187959 | 1 | 221.34 | 237.76 | 16.42 | 10 |  | 164.2 | 164.5672 | Bashabo |  |  |  | AT-02 | 164.5672 | 981.0492 | -816.482 | -83.2254 | CHECK
|  |  | 10: Grand Total | 12070400 | 12043467.2198 | 12070400 | 0.22363
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Khilgaon | at 33 KV level |  | 8270943.4744
[6 empty] | Bashabo | at 33 KV level |  | 3799456.5256
[6 empty] | Total = |  |  | 12070400 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 |  | 33 | Import | 35786569 | 1 | 1963.391 | 1983.503 | 20.112 | 180000 | 0 | 3620160 | 4733.63
2 | Sher-e-Banglanagar Ckt-02 |  | 33 | Import | 35786575 | 1 | 694.282 | 708.985 | 14.703 | 180000 | 0 | 2646540 | 3460.549
|  |  | 10: Total | 0 | 6266700 | 8194.179
|  |  | 10: Net Total | 6274894.179
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 |  | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
|  |  | 10: Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 33 |  | 0
|  |  | 10: Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 |  | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 |  | 33 | Export | DHK 66500 | 1 | 760794 | 775578 | 14784 | 180 |  | 2661120
|  |  | 10: Total |  | 2661120 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 4: 6274894.179; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 6274894.179
| IMPORT-2 |  | 6: SHER-E-BANGLANAGAR 33 KV NET IMPORT; 9=8-7: 6274894.179 | 33 KV TX HV SIDE |  | 6274894.179
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 4: 6274894.179
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming |  | 11 | Import | DHK 66503 | 1 | 2236461 | 2256757 | 20296 | 180 | 3653280 |  | 3623296.6018
2 | Transfomer-2 Incoming |  | 11 | Import | DHK 66495 | 1 | 743303 | 758156 | 14853 | 180 | 2673540 |  | 2651597.5772
|  |  | 7: 0; 8: 0; 10: Total | 6326820 |  | 6274894.179
| SHER-E-BANGLANAGAR 11 KV SIDE |  | 7: 0; 8: 0
1 | Sher-e-Banglanagar Local |  | 11 |  | DHK 66503 | 1.45 | 82897 | 84325 | 1428 | 60 | 11 kv bus-1 R Phase PT missing | 124236 | 124871.9678 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 124871.9678 | 133378.1778 | -8506.21 | -6.3775 | OK
2 | Mirpur Road East | D550F | 11 |  | DHK 60961 | 1.45 | 843723 | 849497 | 5774 | 60 |  | 502338 | 504909.4833 | Shere b.nagar |  |  |  | Mirpur Road East | 504909.4833 | 511825.2027 | -6915.7194 | -1.3512 | OK
3 | Gonobhaban school | D550E | 11 |  | DHK 66492 | 1.45 | 532652 | 534506 | 1854 | 60 |  | 161298 | 162123.6893 | Shere b.nagar |  |  |  | Gonobhaban school | 162123.6893 | 177174.8965 | -15051.2072 | -8.4951 | OK
4 | Babor Road | D450B | 11 |  | DHK 66489 | 1.45 | 783040 | 791315 | 8275 | 60 |  | 719925 | 723610.3177 | Shyamoli |  |  |  | Babor Road | 723610.3177 | 1641262.4555 | -917652.1378 | -55.9114 | CHECK
5 | College Gate | D450K | 11 |  | DHK 66487 | 1.45 | 2689618 | 2705027 | 15409 | 60 |  | 1340583 | 1347445.4847 | Shyamoli |  |  |  | College Gate | 1347445.4847 | 1954707.1976 | -607261.713 | -31.0666 | OK
6 | Parade ground |  | 11 |  | DHK 66490 | 1.45 | 938348 | 938426 | 78 | 60 |  | 6786 | 6820.7377 | Satmasjid |  |  |  | Parade ground | 6820.7377 | 4879.6894 | 1941.0483 | 39.7781 | OK
7 | Hospital RMU | D550H | 11 |  | DHK 66491 | 1.45 | 914941 | 921595 | 6654 | 60 |  | 578898 | 581861.3963 | Shere b.nagar |  |  |  | Hospital RMU | 581861.3963 | 629901.6383 | -48040.2421 | -7.6266 | OK
1 | Shamoly Square |  | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | D550D | 11 |  | DHK 60964 | 1 | 195915.8 | 197469.2 | 1553.4 | 60 |  | 93204 | 93681.1141 | Shere b.nagar |  |  |  | Gonobhaban RMU | 93681.1141 | 88021.1633 | 5659.9507 | 6.4302 | OK
3 | Krishi University | D550V | 11 |  | DHK 60963 | 1 | 370114.7 | 378971.9 | 8857.2 | 60 |  | 531432 | 534152.4164 | Shere b.nagar |  |  |  | Krishi University | 534152.4164 | 582966.2552 | -48813.8388 | -8.3734 | OK
4 | NEC | D550X | 11 |  | DHK 86073 | 1 | 43.55 | 47.94 | 4.39 | 60000 |  | 263400 | 264748.3525 | Shere b.nagar |  |  |  | NEC | 264748.3525 | 251816.0719 | 12932.2806 | 5.1356 | OK
5 | Novo Theater/Army Musium | D550A | 11 |  | DHK 86074 | 1 | 399.36 | 417.87 | 18.51 | 60000 |  | 1110600 | 1116285.1948 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 1116285.1948 | 1072929.2443 | 43355.9505 | 4.0409 | OK
6 | Netor |  | 11 |  | DHK 60962 | 1 | 134307.8 | 143367.9 | 9060.1 | 60 |  | 543606 | 546388.7354 | Shere b.nagar |  |  |  | Netor | 546388.7354 | 587213.3923 | -40824.6568 | -6.9523 | OK
7 | BICC | D550VV | 11 |  |  | 1 | 43.55 | 47.94 | 4.39 | 60000 |  | 263400 | 264748.3525 | Shere b.nagar |  |  |  | BICC | 264748.3525 | 251816.0719 | 12932.2806 | 5.1356 | OK
8 | Auxiliary |  | 0.415 |  |  | 1 | 5342.83 | 5396.67 | 53.84 | 60 |  | 3230.4 | 3246.9365 | Shere b.nagar |  |  |  | Auxiliary | 3246.9365 | 3802.5432 | -555.6067 | -14.6114 | OK
|  |  | 10: Grand Total | 6274894.179 | 6242936.4 | 6274894.179 | 0.5119
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 3538409.374 | Including 41% of Novo Theatre
[6 empty] | Shyamoli | at 33 KV level |  | 2071055.8024
[6 empty] | Satmasjid | at 33 KV level |  | 6820.7377
[6 empty] | Tejgaon | at 33 KV level |  | 658608.2649 | 59% of Novo Theatre
[6 empty] | Total = |  |  | 6274894.179 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 9073344 | 9089523.9553
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 |  | ABB03918 | 1 | 306967 | 311588 | 4621 | 2000 | 0 | 9242000 | 9258480.7096
|  |  | 10: Total | 0 | 18315344 | 18348004.6649
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 |  | 33 | Import | 38 | 1 | 309050912 | 318124256 | 9073344 | 1 | 9073344
2 | Maniknagor Incoming-02 |  | 33 | Import | 15 | 1 | 224149136 | 233208176 | 9059040 | 1 | 9059040
|  |  | 7: 0; 8: 0; 10: Total | 18132384 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  | 7: 0; 8: 0
3 | Transformer-01 |  | 33 | Export | 16 | 1 | 297658816 | 306727680 | 9068864 | 1 |  | 9068864
4 | Transformer-02 |  | 33 | Export | 196 | 1 | 235405440 | 244464960 | 9059520 | 1 |  | 9059520
|  |  | 10: Total |  | 18128384 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 4: 18348004.6649; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 18348004.6649
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 18348004.6649 | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 18128384
[11 empty] | LOSS UNITS=> |  | 219620.6649
[11 empty] | LOSS % IN => |  | 1.197%
| TOTAL IMPORT |  | 4: 18348004.6649
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | 192 | 1 | 295515136 | 304537952 | 9022816 | 1 | 9022816 |  | 9174108.0763
2 | Transformer-02 Incoming |  | 11 | Import | 118 | 1 | 233815712 | 242838320 | 9022608 | 1 | 9022608 |  | 9173896.5886
|  |  | 7: 0; 8: 0; 10: Total | 18045424 |  | 18348004.6649
| MUGDAPARA HOSPITAL 11 KV SIDE |  | 7: 0; 8: 0
1 | City Corporation | A997Y | 11 |  | 93 | 1 | 43022376 | 44005332 | 982956 | 1 |  | 982956 | 996604.0058 | Bashabo |  |  |  | City Corporation | 996604.0058 | 1085361.1698 | -88757.164 | -8.1777 | OK
2 | Bot tola | B297L | 11 |  |  | 1 | 58423616 | 60692692 | 2269076 | 1 |  | 2269076 | 2300581.3394 | Maniknagar |  |  |  | Bot tola | 2300581.3394 | 2406944.4276 | -106363.0883 | -4.419 | OK
3 | Jhilpar | B997J | 11 |  | 145 | 1 | 36824472 | 37775588 | 951116 | 1 |  | 951116 | 964321.9183 | Mugdapara |  |  |  | Jhilpar | 964321.9183 | 1048862.0833 | -84540.1649 | -8.0602 | OK
4 | Central Bashaboo | A997C | 11 |  | 128 | 1 | 40716380 | 42422256 | 1705876 | 1 |  | 1705876 | 1729561.5012 | Bashabo |  |  |  | Central Bashaboo | 1729561.5012 | 1906586.5613 | -177025.0601 | -9.2849 | OK
5 | Kadamtala | B997L | 11 |  | 8 | 1.5 | 19491432 | 20022992 | 531560 | 1 |  | 797340 | 808410.7915 | Mugdapara |  |  |  | Kadamtala | 808410.7915 | 737461.0018 | 70949.7897 | 9.6208 | OK
6 | Ansar VDP | A297A | 11 |  | 119 | 1 | 20098870 | 21280468 | 1181598 | 1 |  | 1181598 | 1198004.0816 | Khilgaon |  |  |  | Ansar VDP | 1198004.0816 | 522827.1096 | 675176.972 | 129.1396 | FAULT
7 | Mugda Hospital Express-01 | B997H | 11 |  |  | 1 | 6519544 | 6811903 | 292359 | 1 |  | 292359 | 296418.3041 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 296418.3041 | 309430.1308 | -13011.8267 | -4.2051 | OK
8 | Boro Masjid | B997Z | 11 |  | 7 | 1.22 | 50253036 | 51357956 | 1104920 | 1 |  | 1348002.4 | 1366718.9494 | Mugdapara |  |  |  | Boro Masjid | 1366718.9494 | 1456683.3289 | -89964.3795 | -6.176 | OK
1 | Anandodhara | B297B | 11 |  | 120 | 1 | 48863040 | 49877200 | 1014160 | 1 |  | 1014160 | 1028241.2626 | Maniknagar |  |  |  | Anandodhara | 1028241.2626 | 986769.0262 | 41472.2364 | 4.2028 | OK
2 | Culvert | A997L | 11 |  | 117 | 1 | 42511816 | 44077932 | 1566116 | 1 |  | 1566116 | 1587860.9817 | Bashabo |  |  |  | Culvert | 1587860.9817 | 1735000.3001 | -147139.3184 | -8.4807 | OK
3 | Mugda Hospital Express-02 |  | 11 |  | 97 | 1 | 4845548 | 4845548 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | A997J | 11 |  | 98 | 1 | 28559450 | 29356208 | 796758 | 1 |  | 796758 | 807820.7106 | Bashabo |  | 218 |  | Jhor Pukur | 807820.7106 | 1233989.5056 | -426168.795 | -34.5359 | OK
5 | T&T | B997T | 11 |  | 99 | 1 | 24519980 | 25139698 | 619718 | 1 |  | 619718 | 628322.5712 | Mugdapara |  | 130 |  | T&T | 628322.5712 | 593432.5647 | 34890.0064 | 5.8794 | OK
6 | Haider Ali | B297H | 11 |  | 9 | 1 | 72359744 | 74741936 | 2382192 | 1 |  | 2382192 | 2415267.9161 | Maniknagar |  | 159.3333 |  | Haider Ali | 2415267.9161 | 2486025.7818 | -70757.8657 | -2.8462 | OK
| 11kv Tilpapara | A929T | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 2189391.12 | 2219790.0622 | Bashabo | 180 |  |  | 11kv Tilpapara | 2219790.0622 | 2267480.2014 | -47690.1391 | -2.1032
7 | AT-01 |  | 11 |  |  | 1 | 3127.9 | 3207.07 | 79.17 | 1 |  | 79.17 | 80.2692 | Mugdapara |  |  |  | AT-01 | 80.2692 | 86.077 | -5.8078 | -6.7472 | OK
8 | AT-02 |  | 11 |  |  | 1 | 17.34 | 17.34 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 18348004.6649 | 18096737.69 | 18348004.6649 | 1.3885
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bashabo | at 33 KV level |  | 7341637.2615
[6 empty] | Maniknagar | at 33 KV level |  | 5744090.518
[6 empty] | Mugdapara | at 33 KV level |  | 4064272.8038
[6 empty] | Khilgaon | at 33 KV level |  | 1198004.0816
[6 empty] | Total = |  |  | 18348004.6649 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon |  | 33 | Export | BD001895 | 1 | 75.4774 | 79.3194 | 3.842 | 240000 | 0 | 922080 | 922198.3633
MANKNAGAR 33 KV SIDE | bar: 4
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 275583 | 278536 | 2953 | 2000 | 0 | 5906000 | 5916531.8189
|  |  | 10: Total | 0 | 6828080 | 6838730.1823
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming |  | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming |  | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming |  | 33 |  |  | 1 | 68526 | 71914 | 3388 | 270 |  | 914760
| 33 kV Maniknagor Incoming |  | 33 |  |  | 1.08 | 1007578 | 1007578 | 0 | 180 |  | 0
|  |  | 10: Total |  | 914760
KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 0
KHILGOAN 33 KV SIDE
3 | Transformer -01 |  | 33 | Export | DHK60982 | 1 | 824575 | 829685 | 5110 | 180 |  | 919800
4 | Transformer -02 |  | 33 | Export | DHK60947 | 1 | 812390 | 844340 | 31950 | 180 |  | 5751000
|  |  | 10: Total |  | 6670800 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 4: 6838730.1823; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6838730.1823
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 6838730.1823 | 33 KV TX HV SIDE |  | 6670800
[11 empty] | LOSS UNITS=> |  | 167930.1823
[11 empty] | LOSS % IN => |  | 2.456%
| TOTAL IMPORT |  | 4: 6838730.1823
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | DHK60927 | 1 | 824600 | 829484 | 4884 | 180 | 879120 |  | 911706.2429
2 | Transformer-02 Incoming |  | 11 | Import | DHK60928 | 1 | 970976 | 1002727 | 31751 | 180 | 5715180 |  | 5927023.9393
|  |  | 7: 0; 8: 0; 10: Total | 6594300 |  | 6838730.1823
| KHILGOAN 11 KV SIDE |  | 7: 0; 8: 0 | [5 empty] | 140
1 | Shantinagar s/s-1 |  | 11 |  | DHK60932 | 1 | 365765 | 397140 | 31375 | 60 |  | 1882500 | 1888358.4836 | Rajarbag |  | 60 |  | Shantinagar s/s-1 | 1888358.4836 | 1327460.0638 | 560898.4198 | 42.2535 | FAULT
2 | Gulbagh | D606G | 11 |  | DHK60934 | 1 | 158531 | 175960 | 17429 | 60 |  | 1045740 | 1048994.4227 | Rajarbag |  | 80 |  | Gulbagh | 1048994.4227 | 1110222.7304 | -61228.3078 | -5.515 | OK
3 | Rampura BTV | A206H | 11 |  | DHK60933 | 1 | 14073 | 14073 | 0 | 60 |  | 0 | 0 | Khilgaon |  | 26.6667 |  | Rampura BTV | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | West Shantibag | D606W | 11 |  | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 1094695.56 | 1098102.3361 | Rajarbag | 90 | 86.6667 |  | West Shantibag | 1098102.3361 | 1003916.3939 | 94185.9422 | 9.3819 | OK
1 | East Malibagh | D606E | 11 |  | DHK60929 | 1 | 628367 | 648732 | 20365 | 60 |  | 1221900 | 1225702.646 | Rajarbag |  |  |  | East Malibagh | 1225702.646 | 1396586.5654 | -170883.9194 | -12.2358 | OK
2 | Police Line | D606S | 11 |  | DHK60930 | 1 | 584758 | 594185 | 9427 | 60 |  | 565620 | 567380.2526 | Rajarbag |  |  |  | Police Line | 567380.2526 | 593599.4922 | -26219.2396 | -4.417 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 |  | DHK61017 | 1 | 197716 | 199938 | 2222 | 60 |  | 133320 | 133734.902 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 133734.902 | 145615.9492 | -11881.0472 | -8.1592 | OK
4 | Benjir Bagan | D662R | 11 |  | DHK60985 | 1 | 170493 | 173708 | 3215 | 60 |  | 192900 | 193500.3195 | Rajarbag |  |  |  | Benjir Bagan | 193500.3195 | 197704.2286 | -4203.9091 | -2.1264 | OK
5 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 872098 | 883323 | 11225 | 60 |  | 673500 | 675595.9834 | Switching |  |  |  | Shantinagar s/s-2 | 675595.9834 | 785096.9399 | -109500.9565 | -13.9474 | OK
6 | AT-1 & AT-2 |  | 0.415 |  | ELIB 7374 | 1 | 2209.9 | 2332.2 | 122.3 | 60 |  | 7338 | 7360.8364 | Rajarbag |  |  |  | AT-1 & AT-2 | 7360.8364 | 7097.6366 | 263.1998 | 3.7083 | OK
|  |  | 10: Grand Total | 6838730.1823 | 6817513.56 | 6838730.1823 | 0.31121
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[6 empty] | Rajarbag | at 33 KV level |  | 6655136.5976 | Including Switching
[6 empty] | Khilgaon | at 33 KV level |  | 0
[6 empty] | Moghbazar | at 33 KV level |  | 122203.1256
[6 empty] | Kakrail | at 33 KV level |  | 61390.4591
[6 empty] | Total = |  |  | 6838730.1823 | 0
11 KV SIDE of___Santinagar Switching S/S | [14 empty] | Month October-2023
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 |  | 11 |  | DHK60935 | 1 | 872098 | 883323 | 11225 | 60 |  | 673500 | 675595.9834 | 0.31121
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder |  | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 490476 | 492002.3987 | Rajarbag
2 | 11 Fortune(MogBazar)-new |  | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 121824 | 122203.1256 | Moghbazar
3 | Centerpoint-Kakrail |  | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 61200 | 61390.4591 | Kakrail
[12 empty] | 673500 | 675595.9834 | 0.31121
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 |  | 33 | Import |  | 1 | 1133.802 | 1168.374 | 34.572 | 180000 | 0 | 6222960 | 8136.986
2 | Sherebangla to Monipuripara-2 |  | 33 | Import |  | 1 | 815.083 | 838.951 | 23.868 | 180000 | 0 | 4296240 | 5617.655
|  |  | 10: Total | 0 | 10519200 | 13754.641
|  |  | 10: Net Total | 10532954.641
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 |  | 33 | Import | BD017103 | 1 | 41589.96 | 47130.77 | 5540.81 | 1000 | 5540810
2 | Agargaon Ckt-02 |  | 33 | Import | BD017104 | 1 | 30307.9 | 34130.21 | 3822.31 | 1000 | 3822310
|  |  | 10: Total | 9363120 | 0 | 0
MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 0
MONIPURIPARA 33 KV SIDE
3 | Transformer-01 |  | 33 | Export | BD017102 | 1 | 104683.5 | 104683.5 | 0 | 888.8889 |  | 0
4 | Transformer-02 |  | 33 | Export | BD017105 | 1 | 47148.85 | 51463.55 | 4314.7 | 888.8889 |  | 3835288.9368
|  |  | 10: Total |  | 3835288.9368 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 4: 10532954.641; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10532954.641
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 10532954.641 | 33 KV TX HV SIDE |  | 3835288.9368
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 6697665.7042
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 63.59%
| TOTAL IMPORT |  | 4: 10532954.641
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import | BD014058 | 1 | 103951.91 | 103951.91 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import | BD014062 | 1 | 46200.6 | 50491.18 | 4290.58 | 1000 | 4290580 |  | 10532954.641
|  |  | 7: 0; 8: 0; 10: Total | 4290580 | 0 | 10532954.641
| MONIPURIPARA 11 KV SIDE |  | 7: 0; 8: 0
1 | Spare |  | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | D572W | 11 |  | BD013947 | 1 | 31973.6 | 32779.66 | 806.06 | 1000 |  | 806060 | 814448.4485 | Shere b.nagar |  |  |  | Monipuripara west | 814448.4485 | 843758.793 | -29310.3445 | -3.4738 | OK
3 | Biggan College | C672BC | 11 |  | BD013949 | 1 | 19907.7 | 20808.54 | 900.84 | 1000 |  | 900840 | 910214.7983 | Kakrail |  |  |  | Biggan College | 910214.7983 | 898340.4903 | 11874.3081 | 1.3218 | OK
4 | Green Road South | D572G | 11 |  | BD013948 | 1 | 30606.05 | 31642.23 | 1036.18 | 1000 |  | 1036180 | 1046963.2451 | Shere b.nagar |  |  |  | Green Road South | 1046963.2451 | 997691.2194 | 49272.0257 | 4.9386 | OK
5 | BARC Building O/H | D572B | 11 |  | BD014010 | 1 | 14027.2 | 14574.54 | 547.34 | 1000 |  | 547340 | 553036.0194 | Shere b.nagar |  |  |  | BARC Building O/H | 553036.0194 | 605164.5353 | -52128.5159 | -8.6139 | OK
6 | Green Road North | D572NN | 11 |  | BD014036 | 1 | 60825.6 | 62546.1 | 1720.5 | 1000 |  | 1720500 | 1738404.7784 | Shere b.nagar |  |  |  | Green Road North | 1738404.7784 | 1930586.7401 | -192181.9618 | -9.9546 | OK
7 | Chundrima Uddan | D572C | 11 |  | BD014035 | 1 | 31059.28 | 32013.76 | 954.48 | 1000 |  | 954480 | 964413.0153 | Shere b.nagar |  |  |  | Chundrima Uddan | 964413.0153 | 995724.673 | -31311.6577 | -3.1446 | OK
8 | RMU-1 Feeder |  | 11 |  | BD013940 | 1 | 799.47 | 1047.79 | 248.32 | 1000 |  | 248320 | 250904.1991 | Shere b.nagar |  |  |  | RMU-1 Feeder | 250904.1991 | 255319.9358 | -4415.7367 | -1.7295 | OK
1 | Spare-03 |  | 11 |  | BD013946 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-03 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | C672K | 11 |  | BD013964 | 1 | 40380.21 | 40456.52 | 76.31 | 1000 |  | 76310 | 77104.1375 | Kakrail |  |  |  | kawran Bazar North | 77104.1375 | 81762.1785 | -4658.041 | -5.6971 | OK
3 | NAM Bhanan RMU | D572NM | 11 |  | BD013950 | 1 | 17250.82 | 18200.87 | 950.05 | 1000 |  | 950050 | 959936.9135 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 959936.9135 | 1011015.5749 | -51078.6614 | -5.0522 | OK
4 | Novo Theater |  | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | C172I | 11 |  | BD013962 | 1 | 38929.72 | 39654.38 | 724.66 | 1000 |  | 724660 | 732201.3407 | Tejgaon |  |  |  | Monipuripara Nearest | 732201.3407 | 808641.8922 | -76440.5514 | -9.453 | OK
6 | Holy Cross | C172HC | 11 |  | BD013965 | 1 | 38607.3 | 39906.37 | 1299.07 | 1000 |  | 1299070 | 1312589.0703 | Tejgaon |  |  |  | Holy Cross | 1312589.0703 | 1258529.5254 | 54059.5449 | 4.2955 | OK
7 | Honda Goli | C172HG | 11 |  | BD014011 | 1 | 15366.23 | 16352.73 | 986.5 | 1000 |  | 986500 | 996766.2388 | Tejgaon |  |  |  | Honda Goli | 996766.2388 | 1069470.1647 | -72703.9259 | -6.7981 | OK
8 | Navy Quarter | C172NQ | 11 |  | BD013941 | 1 | 5549.43 | 5723.59 | 174.16 | 1000 |  | 174160 | 175972.436 | Tejgaon |  |  |  | Navy Quarter | 175972.436 | 196544.2773 | -20571.8412 | -10.4668 | OK
9 | AT-01 |  | 0.415 |  |  | 1 | 2063.78 | 2141.19 | 77.41 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 585.48 | 585.48 | 0 | 1 |  | 0 | 0 | Shere b.nagar |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 10532954.641 | 10424470 | 10532954.641 | 1.0407
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shere b.nagar | at 33 KV level |  | 6328106.6193
[6 empty] | Kakrail | at 33 KV level |  | 987318.9359
[6 empty] | Tejgaon | at 33 KV level |  | 3217529.0858
[6 empty] | Total = |  |  | 10532954.641 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 |  | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 |  | 33 | 0 | 0 | 1 | 3925.09 | 3957.05 | 31.96 | 180000 | 0 | 5752800 | 5774081.1579
|  |  | 10: Total | 0 | 5752800 | 5774081.1579
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 |  | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 |  | 33 | Import |  | 1 | 38389.89 | 44123.44 | 5733.55 | 1000 | 5733550
|  |  | 10: Total | 5733550 | 0 | 0
Ispahani 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 0
Ispahani 33 KV SIDE
3 | Transformer-01 |  | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 |  | 33 | Export |  | 1 | 37528.15 | 43978.86 | 6450.71 | 888.8889 |  | 5733964.5161
|  |  | 10: Total |  | 5733964.5161 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 4: 5774081.1579; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5774081.1579
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 5774081.1579 | 33 KV TX HV SIDE |  | 5733964.5161
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 40116.6418
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.6948%
| TOTAL IMPORT |  | 4: 5774081.1579
11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming |  | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming |  | 11 | Import |  | 1 | 10864.17 | 12740.85 | 1876.68 | 1000 | 5733964.5161 |  | 5774081.1579 |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 5733964.5161 | 0 | 5774081.1579
| Ispahani 11 KV SIDE |  | 7: 0; 8: 0
1 | Doctor Goli | D1113D | 11 |  | BD013944 | 1 | 9640.93 | 10546.84 | 905.91 | 1000 |  | 905910 | 917384.4784 | Moghbazar |  |  |  | Doctor Goli | 917384.4784 | 958125.7556 | -40741.2773 | -4.2522 | OK
2 | Ispahani | D1113S | 11 |  | BD013947 | 1 | 10792.27 | 11780.12 | 987.85 | 1000 |  | 987850 | 1000362.3505 | Moghbazar |  |  |  | Ispahani | 1000362.3505 | 1092016.0616 | -91653.7111 | -8.3931 | OK
3 | BTCL | C6113BT | 11 |  | BD013949 | 1 | 5553.52 | 6098.75 | 545.23 | 1000 |  | 545230 | 552136.017 | Kakrail |  |  |  | BTCL | 552136.017 | 523407.6855 | 28728.3315 | 5.4887 | OK
4 | Vikarunnesa | C6113VQ | 11 |  | BD013948 | 1 | 7515.66 | 8561.61 | 1045.95 | 1000 |  | 1045950 | 1059198.2594 | Kakrail |  |  |  | Vikarunnesa | 1059198.2594 | 1138092.7736 | -78894.5143 | -6.9322 | OK
5 | OASIS |  | 11 |  |  | 1 | 202.8 | 310.99 | 108.19 | 1000 |  | 108190 | 109560.3611 | Kakrail |  |  |  | OASIS | 109560.3611 | 90109.3741 | 19450.9869 | 21.586 | OK
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | D1113W | 11 |  |  | 1 | 8932.63 | 9982.44 | 1049.81 | 1000 |  | 1049810 | 1063107.1511 | Moghbazar |  |  |  | Wireless | 1063107.1511 | 1088068.9306 | -24961.7796 | -2.2941 | OK
2 | Kazir Goli | C6113KG | 11 |  |  | 1 | 8472.69 | 9531.61 | 1058.92 | 1000 |  | 1058920 | 1072332.5406 | Kakrail |  |  |  | Kazir Goli | 1072332.5406 | 1195416.795 | -123084.2544 | -10.2963 | OK
3 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare |  | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 5774081.1579 | 5701860 | 5774081.1579 | 1.2666
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Moghbazar | at 33 KV level |  | 2980853.9799
[6 empty] | Kakrail | at 33 KV level |  | 2793227.178
[6 empty] | Total = |  |  | 5774081.1579 | 0

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 |  | 132 | IMPORT | 8993683 | 1 | 8412.164 | 8449.443 | 37.279 | 960000 | 0 | 35787840
| XFR- T2 |  | 132 |  | 8993682 | 1 | 8402.119 | 8439.078 | 36.959 | 960000 | 0 | 35480640
|  |  | 10: Total | 0 | 71268480
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** |  | 132 | P. Cell | 08993685 | 1 | 8412.15 | 8449.443 | 37.293 | 960000 | 35801280
| 132/33 kV Transformer-2(HV) ** |  | 132 | P. Cell | 08993684 | 1 | 8402.108 | 8439.078 | 36.97 | 960000 | 35491200
|  |  | 10: Total | 71292480
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 4: 71268480; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 71268480
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 71268480 | 33 KV NET IMPORT |  | 71393280
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 71268480 | LOSS UNITS=>(132 HV-33 LV) |  | -124800
| IMPORT-4 |  | 6: Loss Units=> (132 IMP-132 EXP); 9=8-7: 0 | LOSS % IN => |  | -0.1751%
| 132 KV TOTAL IMPORT |  | 4: 71268480; 6: 132 KV NET LOSS =>; 9=8-7: 0%
| 33 KV GT INCOMING-NOCS |  | 4: 71393280
| Loss Units=> (132 IMP-33 IMP) |  | 4: -124800
| LOSS % IN => |  | 4: -0.1751%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | 4: IMPORT
3 | 132/33 kV Transformer, T-1 (LV) |  | 33 | PGCB | J2002016494 | 1 | 22361.077 | 22609.343 | 248.266 | 144000 | 35750304
4 | 132/33 kV Transformer, T-2 (LV) |  | 33 | PGCB | J2002016859 | 1 | 32335.796 | 32581.943 | 246.147 | 144000 | 35445168
| DPDC |  | 7: 0; 8: 0; 10: Total | 71195472
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | DPDC | 07389553 | 1 | 1754.23 | 1828.88 | 74.65 | 480000 | 35832000
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | DPDC | 07389485 | 1.038 | 1135.22 | 1204.02 | 68.8 | 480000 | 34278912
| P.Cell |  | 7: 0; 8: 0; 10: Total | 70110912
| 132/33 kV Transformer-1 (GT-1) Incoming |  | 33 | P.Cell | 08993674 | 1 | 11019.346 | 11093.974 | 74.628 | 480000 | 35821440
| 132/33 kV Transformer-2 (GT-2) Incoming |  | 33 | P.Cell | 8993667 | 1 | 10928.186 | 11002.294 | 74.108 | 480000 | 35571840
|  |  | 7: 0; 8: 0; 10: Total | 71393280
| SIDDHIRGANJ 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) |  | 33 | DPDC | 07389555 | 1 | 5694.79 | 5723.1 | 28.31 | 240000 |  | 6794400 | 6761266.2239 |  | 14131547.95 | Siddhirganj 33/11 kv ss | 0.64916 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 6761266.2239 | 7028125.8256 | -266859.6018 | -3.797 | OK
|  |  | 33 | P.Cell | 08993675 | 1 | 5022.34 | 5022.34 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) |  | 33 | DPDC | 07389487 | 1 | 5871.73 | 5902.59 | 30.86 | 240000 |  | 7406400 | 7370281.7262 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 7370281.7262 | 7569308.4262 | -199026.7 | -2.6294 | OK
|  |  | 33 | P.Cell | 08993666 | 1 | 5135.966 | 5166.841 | 30.875 | 240000 |  | 7410000 | 7373864.1703 |  |  |  |  | 0 | 7373864.1703 | 7570758.0224 | -196893.8521 | -2.6007 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 14200800 | 14131547.95 |  |  |  |  | 33 KV Feeders | 14131547.95 | 14597434.2518 | -465886.3018 | -3.1916 | OK
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4326.249 | 4367.621 | 41.372 | 240000 |  | 9929280 | 9880858.5734 |  | 18158692.8129 | Sarulia 33/11 kv ss |  | 33 kV Sarulia-1 Feeder | 9880858.5734 | 10212163.9919 | -331305.4185 | -3.2442 | OK
|  |  | 33 | P.Cell | 08993679 | 1 | 4327.069 | 4368.442 | 41.373 | 240000 |  | 9929520 | 9881097.403 |  |  |  |  | 0 | 9881097.403 | 10208781.6006 | -327684.1976 | -3.2098 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) |  | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss |  | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6217.19 | 6258.43 | 41.24 | 240000 |  | 9897600 | 9849333.0651 |  |  |  |  | 33 kV Demra-1 Feeder | 9849333.0651 | 10217237.5788 | -367904.5137 | -3.6008 | OK
|  |  | 33 | P.Cell | 08993676 | 1 | 5862.773 | 5904.017 | 41.244 | 240000 |  | 9898560 | 9850288.3835 |  |  |  |  | 0 | 9850288.3835 | 10213130.3894 | -362842.0059 | -3.5527 | OK
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5752.38 | 5809.89 | 57.51 | 240000 |  | 13802400 | 13735090.7995 |  | 23584423.8646 | Demra 33/11 kv ss |  | 33 kV Demra-2 Feeder | 13735090.7995 | 14201211.2764 | -466120.4769 | -3.2823 | OK
|  |  | 33 | P.Cell | 08993665 | 1 | 5460.594 | 5518.105 | 57.511 | 240000 |  | 13802640 | 13735329.6291 |  |  |  |  | 0 | 13735329.6291 | 14683443.6294 | -948114.0003 | -6.457 | OK
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder |  | 33 | DPDC | 7389486 | 1 | 4570.36 | 4592.74 | 22.38 | 240000 |  | 5371200 | 5345006.6439 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 5345006.6439 | 5626849.4493 | -281842.8053 | -5.0089 | OK
|  |  | 33 | P.Cell | 08993678 | 1 | 3816.031 | 3838.41 | 22.379 | 240000 |  | 5370960 | 5344767.8143 |  |  |  |  | 0 | 5344767.8143 | 5624675.0549 | -279907.2406 | -4.9764 | OK
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4031.36 | 4066.02 | 34.66 | 240000 |  | 8318400 | 8277834.2395 |  |  |  |  | 33 kV Sarulia-2 Feeder | 8277834.2395 | 8654089.621 | -376255.3815 | -4.3477 | OK
|  |  | 33 | P.Cell | 08993663 | 1 | 3753.224 | 3787.867 | 34.643 | 240000 |  | 8314320 | 8273774.1361 |  |  |  |  | 0 | 8273774.1361 | 8649982.4316 | -376208.2955 | -4.3492 | OK
17 | 33 kV Adamjee EPZ Feeder |  | 33 | DPDC | ABB03919 | 1 | 370823 | 375764.6 | 4941.6 | 2000 |  | 9883200 | 9835003.2885 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 9835003.2885 | 9088565.8308 | 746437.4577 | 8.2129 | OK
|  |  | 10: Total | 71054674.56 | 71402880 | 71054674.56 | -0.48766
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 15180009.9325
[6 empty] | Total = |  |  | 15180009.9325 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | 4: IMPORT
8 | 33/11 kV Transformer-1 Incoming |  | 11 | New | XA587379 | 1 | 692669.6 | 698853 | 6183.4 | 1000 | 6183400 |  | 6442174.7133
9 | 33/11 kV Transformer-2 Incoming |  | 11 | New | DHKA9985 | 1 | 323323.3 | 330703.8 | 7380.5 | 1000 | 7380500 |  | 7689373.2367
|  |  | 7: 0; 8: 0; 10: Total | 13563900 |  | 14131547.95
| SIDDHIRGANJ 11 kV SIDE |  | 4: EXPORT; 7: 0; 8: 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | New | XA587377 | 1 | 217862.8 | 220112.5 | 2249.7 | 1000 |  | 2249700 | 2264304.2356 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 2264304.2356 | 2396448.119 | -132143.8834 | -5.5142 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | New | XA587359 | 1 | 17125.2 | 17238.9 | 113.7 | 1000 |  | 113700 | 114438.0991 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 114438.0991 | 122268.7906 | -7830.6915 | -6.4045 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | New | XA586385 | 1 | 111187.4 | 112545.1 | 1357.7 | 1000 |  | 1357700 | 1366513.6955 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1366513.6955 | 1396305.5531 | -29791.8577 | -2.1336 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | New | XA587376 | 1 | 174800.7 | 177164.8 | 2364.1 | 1000 |  | 2364100 | 2379446.8789 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2379446.8789 | 2449713.7307 | -70266.8518 | -2.8684 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | New | XA575929 | 1 | 7125.2 | 7210.5 | 85.3 | 1000 |  | 85300 | 85853.7366 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 85853.7366 | 56292.0669 | 29561.6697 | 52.5148 | FAULT
10 | 11 kV Monowar Feeder (F-6) | A828L | 11 | New | XA587363 | 1 | 77339.6 | 78690 | 1350.4 | 1000 |  | 1350400 | 1359166.3065 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1359166.3065 | 1319938 | 39228.3066 | 2.972 | OK
11 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) |  | 11 | New |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | New | XA587358 | 1 | 151130.8 | 153390.8 | 2260 | 1000 |  | 2260000 | 2274671.0995 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 2274671.0995 | 2350345.1179 | -75674.0184 | -3.2197 | OK
14 | 11 KV Jhilpar (F-10) | E228Z | 11 | New | XA587369 | 1 | 94.7878 | 101.8282 | 7.0404 | 40000 |  | 281616 | 283444.1488 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 283444.1488 | 297629.6761 | -14185.5273 | -4.7662 | OK
15 | 11 kV Madrasha Road Feeder (F-11) |  | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | New | XA587383 | 1 | 15601.7 | 16306.6 | 704.9 | 1000 |  | 704900 | 709475.9549 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 709475.9549 | 663499.8644 | 45976.0905 | 6.9293 | OK
17 | Seven Horse Feeder (F-13) | A828H | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | A828N | 11 | New | XA587371 | 1 | 152087.1 | 154796.1 | 2709 | 1000 |  | 2709000 | 2726585.8445 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2726585.8445 | 2843859.0812 | -117273.2367 | -4.1237 | OK
|  |  | 10: Total | 13563900 | 13476416 | 13563900 | 0.64916
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Siddirgonj | at 33 KV level |  | 13280455.8512
[6 empty] | Matuail | at 33 KV level |  | 283444.1488
[6 empty] | Total = |  |  | 13563900 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder |  | 33 | DPDC | 07389489 | 1 | 6217.19 | 6258.43 | 41.24 | 240000 | 0 | 9897600 | 9849333.0651
0 | 0 |  | 33 | P.Cell | 08993676 | 1 | 5862.773 | 5904.017 | 41.244 | 240000 | 0 | 9898560 | 9850288.3835
13 | 33 kV Demra-2 Feeder |  | 33 | DPDC | 07389484 | 1 | 5752.38 | 5809.89 | 57.51 | 240000 | 0 | 13802400 | 13735090.7995
0 | 0 |  | 33 | P.Cell | 08993665 | 1 | 5460.594 | 5518.105 | 57.511 | 240000 | 0 | 13802640 | 13735329.6291
|  |  | 10: Total | 0 | 23700000 | 23584423.8646
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 |  | 33 | Digital | DHK60885 | 3 | 376210.4 | 405772.8 | 29562.4 | 240 | 21284928
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) |  | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
|  |  | 10: Total | 21284928 | 0 | 0
DEMRA 33 KV SIDE (EXPORT TO OTHER S/S)
10 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1015.73 | 1019.06 | 3.33 | 240000 |  | 799200 |  | Siddirgonj
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 799200
DEMRA 33 KV SIDE
7 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60886 | 1 | 827740.6 | 870056.3 | 42315.7 | 240 |  | 10155768
8 | 33/11 kV, 10/14 MVA T-2 (HV) |  | 33 | Digital | 05002303 | 1 | 39.55 | 52.29 | 12.74 | 240000 |  | 3057600
9 | 33/11 kV, 20/28 MVA T-3 (HV) |  | 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0
|  |  | 10: Total |  | 13213368 | 0
[6 empty] | 33 KV Export-Import |  |  | KWH
[6 empty] | Total Import |  |  | 23584423.8646
[6 empty] | Siddirgonj NOCS |  |  | 799200
[6 empty] | Net Import to Demra 33/11 KV SS |  |  | 22785223.8646
11 KV SIDE of___DEMRA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK60881 | 1 | 408460.6 | 464775.3 | 56314.7 | 180 | 10136646 |  | 10333268.6258
19 | 33/11 kV, 20/28 MVA T-3 Incoming. |  | 11 |  | DHK60925 | 1 | 806740.7 | 856253.7 | 49513 | 180 | 8912340 |  | 9085214.5083
| 33/11 kV, 10/14 MVA T-2 Incoming. |  | 11 |  |  | 1 | 12405.49 | 15708.168 | 3302.678 | 1000 | 3302678 |  | 3366740.7305
|  |  | 7: 0; 8: 0; 10: Total | 22351664 |  | 22785223.8646
| DEMRA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 |  | HA021101013-02 | 1 | 51773300 | 54945696 | 3172396 | 1 |  | 3172396 | 3182659.205 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 3182659.205 | 3242375.7883 | -59716.5833 | -1.8418 | OK
12 | 11 kV DND (WASA) Feeder. | A816B | 11 |  | HA021100992-02 | 1 | 6258120 | 6447792 | 189672 | 1 |  | 189672 | 190285.6191 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 190285.6191 | 296942.4232 | -106656.8042 | -35.9183 | OK
13 | 11 kV Local Feeder | A816D | 11 |  | HA021100794-02 | 1 | 12242460 | 13337258 | 1094798 | 1 |  | 1094798 | 1098339.8454 | Siddirgonj |  |  |  | 11 kV Local Feeder | 1098339.8454 | 1209825.1625 | -111485.317 | -9.215 | OK
14 | 11 kV Mouchak Feeder | A816A | 11 |  | DHK60888 | 1 | 974230.4 | 1013189.5 | 38959.1 | 60 |  | 2337546 | 2345108.3326 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2345108.3326 | 2403503.8665 | -58395.5338 | -2.4296 | OK
15 | 11 kV Overhead-1 Feeder | A816C | 11 |  | HA021100829-02 | 1 | 79132380 | 79563317 | 430937 | 1 |  | 430937 | 432331.1497 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 432331.1497 | 507759.6491 | -75428.4994 | -14.8552 | OK
16 | 11 kV Provati Steel Feeder | A816Z | 11 |  | DHK60874 | 1 | 591968.1 | 601475.9 | 9507.8 | 60 |  | 570468 | 572313.5546 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 572313.5546 | 603535.6264 | -31222.0718 | -5.1732 | OK
17 | 11 kV Islambagh Feeder. | E116I | 11 |  | DHKA2190 | 1 | 1140.165 | 1179.7411 | 39.5761 | 60000 |  | 2374566 | 2382248.0982 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 2382248.0982 | 2479849.2574 | -97601.1591 | -3.9358 | OK
20 | 11 kV Taj Jute Feeder. | A816E | 11 |  | DHK61062 | 1 | 653180.2 | 679906.6 | 26726.4 | 60 |  | 1603584 | 1608771.849 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1608771.849 | 1850699.8521 | -241928.0031 | -13.0722 | OK
21 | 11 kV Al-Aksa Steel Feeder | A816S | 11 |  | DHK61061 | 1 | 819260.3 | 848208.6 | 28948.3 | 60 |  | 1736898 | 1742517.141 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1742517.141 | 1948104.7891 | -205587.6482 | -10.5532 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 |  | DHKA2189 | 1 | 1074.576 | 1116.5269 | 41.9509 | 60000 |  | 2517054 | 2525197.0695 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2525197.0695 | 2620588.9584 | -95391.8889 | -3.6401 | OK
23 | 11 kV Over Head Feeder-2. | E116V | 11 |  | HA021100488-02 | 1 | 31329630 | 33418808 | 2089178 | 1 |  | 2089178 | 2095936.8227 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 2095936.8227 | 2186616.3464 | -90679.5237 | -4.147 | OK
24 | 11 kV Shimrail Express Feeder. | A8164 | 11 |  | HA021100511-02 | 1 | 8223928 | 8254376 | 30448 | 1 |  | 30448 | 30546.5041 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 30546.5041 | 1269.0967 | 29277.4074 | 2306.9485 | FAULT
25 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 |  | HA021100413-02 | 1 | 81824770 | 82154657 | 329887 | 1 |  | 329887 | 330954.2369 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 330954.2369 | 688064.1207 | -357109.8838 | -51.9007 | CHECK
26 | 11 kV Siddhirgonj Mazar Feeder |  | 11 |  | HA021100393-02 | 1 | 24945.09 | 26069.366 | 1124.276 | 1000 |  | 1124276 | 1127913.2115 | Siddirgonj |  |  |  | 11 kV Siddhirgonj Mazar Feeder | 1127913.2115 | 1241829.7858 | -113916.5743 | -9.1733 | OK
27 | 11 kV AST Beverage Feeder | A816J | 11 |  |  | 1 | 22532950 | 23064522 | 531572 | 1 |  | 531572 | 533291.7199 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 533291.7199 | 269111.0012 | 264180.7187 | 98.1679 | FAULT
28 | 11 kV Karim Market Feeder | E216K | 11 |  |  | 1 | 60540.91 | 62687.216 | 2146.306 | 1000 |  | 2146306 | 2153249.6409 | Matuail |  |  |  | 11 kV Karim Market Feeder | 2153249.6409 | 2251573.1315 | -98323.4906 | -4.3669 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 |  | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 22351664 | 22279586 | 22351664 | 0.32352
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 7718156.9441
[6 empty] | Demra | at 33 KV level |  | 2426891.0596
[6 empty] | Siddirgonj | at 33 KV level |  | 12206615.9963
[6 empty] | Total = |  |  | 22351664 | 0
33 KV SIDE of___ SARULIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder |  | 33 | DPDC | 7389488 | 1 | 4326.249 | 4367.621 | 41.372 | 240000 | 0 | 9929280 | 9880858.5734
0 | 0 |  | 33 | P.Cell | 08993679 | 1 | 4327.069 | 4368.442 | 41.373 | 240000 | 0 | 9929520 | 9881097.403
16 | 33 kV Sarulia-2 Feeder |  | 33 | DPDC | 07389491 | 1 | 4031.36 | 4066.02 | 34.66 | 240000 | 0 | 8318400 | 8277834.2395
| 0 |  | 33 | P.Cell | 08993663 | 1 | 3753.224 | 3787.867 | 34.643 | 240000 | 0 | 8314320 | 8273774.1361
|  |  | 10: Total | 0 | 18247680 | 18158692.8129
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) |  | 33 |  | 30799103 | 1 | 4406.17 | 4440.54 | 34.37 | 240000 | 8248800
7 | 33 kV Siddhirgonj-1 Incoming (=L41) |  | 33 |  | 30799100 | 1 | 4345 | 4385.63 | 40.63 | 240000 | 9751200
|  |  | 7: 0; 8: 0; 10: Total | 18000000 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SARULIA 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV Transformer-1 (=T31) |  | 33 |  | 30799099 | 1 | 4742.79 | 4788.57 | 45.78 | 180000 |  | 8240400
5 | 33/11 kV Transformer-2 (=T32) |  | 33 |  | 30799139 | 1 | 4075.12 | 4102.02 | 26.9 | 180000 |  | 4842000
6 | 33/11 kV Transformer-3 (=T33) |  | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
|  |  | 10: Total |  | 13082400 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 4: 18158692.8129; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 18158692.8129
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 18158692.8129 | 33 KV NET Receiving |  | 18000000
| IMPORT-3 |  | 6: TOTAL EXPORT; 9=8-7: 18158692.8129 | LOSS UNITS=> |  | 158692.8129
| IMPORT-4 |  | 6: 132KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0.8739%
| TOTAL IMPORT |  | 4: 18158692.8129
11 KV SIDE of___SARULIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) |  | 11 |  | 2007754972 | 1 | 9411.14 | 9462.068 | 50.928 | 160000 | 8148480 |  | 8525665.9027
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) |  | 11 |  | 30799500 | 1 | 8879.35 | 8932.09 | 52.74 | 80000 | 4219200 |  | 4414503.021
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) |  | 11 |  | HA021100368-02 | 1 | 54074083 | 59061733 | 4987650 | 1 | 4987650 |  | 5218523.8891
|  |  | 7: 0; 8: 0; 10: Total | 17355330 |  | 18158692.8129
| SARULIA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 |  | 2007755114 | 1 | 5865.74 | 5918.8 | 53.06 | 60000 |  | 3183600 | 3219680.3589 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 3219680.3589 | 3402160.7226 | -182480.3637 | -5.3637 | OK
9 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 |  | 30799484 | 1 | 21.8339 | 22.0742 | 0.2403 | 60000 |  | 14418 | 14581.402 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 14581.402 | 14754.6723 | -173.2703 | -1.1743 | OK
11 | 11 kV Konapara (=L13) **** | E183KL | 11 |  | DHKA2191 | 1 | 2165.8271 | 2208.3613 | 42.5342 | 60000 |  | 2552052 | 2580974.9024 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 2580974.9024 | 2723567.5839 | -142592.6815 | -5.2355 | OK
12 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 |  | 575926 | 1 | 56099.9 | 58574.2 | 2474.3 | 1000 |  | 2474300 | 2502341.7238 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2502341.7238 | 2566996.3354 | -64654.6116 | -2.5187 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 |  | 30799450 | 1 | 1819.9 | 1825.25 | 5.35 | 60000 |  | 321000 | 324637.9555 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 324637.9555 | 325784.1394 | -1146.1838 | -0.35182 | OK
14 | 11 kV Tengra Feeder (=L16) | E183T | 11 |  | 30799145 | 1 | 5565.59 | 5610.1 | 44.51 | 60000 |  | 2670600 | 2700866.43 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 2700866.43 | 2803570.4254 | -102703.9954 | -3.6633 | OK
16 | 11 kV Police Line Feeder (=L17) | E183PL | 11 |  | 30799480 | 1 | 3358.77 | 3379.8 | 21.03 | 60000 |  | 1261800 | 1276100.2252 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1276100.2252 | 1292175.5957 | -16075.3706 | -1.2441 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 |  | 30799119 | 1 | 1655.95 | 1664.08 | 8.13 | 60000 |  | 487800 | 493328.3324 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 493328.3324 | 441483.1795 | 51845.1529 | 11.7434 | OK
18 | 11 kV Spare Feeder (=F9) |  | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 |  | HA021100493-02 | 1 | 86640496 | 89482972 | 2842476 | 1 |  | 2842476 | 2874690.3342 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 2874690.3342 | 3063617.2119 | -188926.8777 | -6.1668 | OK
21 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 |  | HA021100518-02 | 1 | 50869565 | 50895377 | 25812 | 1 |  | 25812 | 26104.5324 | Demra | No Reading in Grid |  |  | 11 kV Baser Pool Feeder (=L11) | 26104.5324 | 0 | 26104.5324 | #DIV/0! | #DIV/0!
22 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 |  | HA021100697-02 | 1 | 27201550 | 29322895 | 2121345 | 1 |  | 2121345 | 2145386.6161 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 2145386.6161 | 2228761.3555 | -83374.7394 | -3.7409 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) |  | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) |  | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 18158692.8129 | 17955203 | 18158692.8129 | 1.1333
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Demra | at 33 KV level |  | 15656351.089
[6 empty] | Matuail | at 33 KV level |  | 2502341.7238
[6 empty] | Total = |  |  | 18158692.8129 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 29336.973 | 38383.46 | 9046.487 | 1000 | 0 | 9046487 | 9044378.7642
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 474.2031 | 508.7791 | 34.576 | 240000 | 0 | 8298240 | 8296306.1392
| Siddhirganj 33 KV SIDE |  | 10: Total |  | 17344727 | 17340684.9033
7 | 33 kV Khanpur-1 Feeder |  | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder |  | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 |  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
|  |  | 10: Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) |  | 33 |  | 84663042 | 1 | 481.64 | 516.19 | 34.55 | 240000 | 8292000
6 | 33 kV Shitalakhya-2 Feeder (Old) |  | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 9046487 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 |  | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 |  | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 17338487 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
11 | 33 kV ACI Pharmacuticles Feeder |  | 33 |  | DHKC4791 | 1 | 927.23 | 943.24 | 16.01 | 90000 |  | 1440900 |  | N.Gonj (East)
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 1440900
[7 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  | 7: 0; 8: 0
9 | 33/11 kV, 20/28 MVA T1 Transformer |  | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer |  | 33 |  | DHKC 9361 | 1 | 40559.36 | 40559.36 | 0 | 240 |  | 0 |  |  | Meter Problem
|  |  | 10: Total |  | 15897587 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 17340684.9033; 6: EXPORT TO N.Gonj (East); 9=8-7: 1440900 | 33 KV NET IMPORT |  | 15899784.9033
| SIDDIRGANJ 33 KV SIDE |  | 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 15899784.9033 | 33 KV TX HV SIDE |  | 15897587
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 2197.9033
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.01382%
| TOTAL IMPORT |  | 4: 17340684.9033
11 KV SIDE of___KHANPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. |  | 11 |  | DHKC 9313 | 1 | 30250040.78 | 34465175.91 | 4215135.13 | 1 | 4215135.13 |  | 4311237.2304
18 | 33/11 kV Transformer-2 Incoming. |  | 11 |  | DHKC 9346 | 1 | 48942518.8 | 52103145.32 | 3160626.52 | 1 | 3160626.52 |  | 3232686.5697
24 | 33/11 kV 20/28 MVA T4 Incoming |  | 11 |  | 06604325 | 1 | 162.98 | 183.27 | 20.29 | 240000 | 4869600 |  | 4980623.4367
30 | 33/11 kV 20/28 MVA T1 Incoming |  | 11 |  | 06604374 | 1 | 90.99 | 104.74 | 13.75 | 240000 | 3300000 |  | 3375237.6665
|  |  | 7: 0; 8: 0; 10: Total | 15545361.65 |  | 15899784.9033
| KHANPUR 11 KV SIDE |  | 7: 0; 8: 0
12 | 11 kV Khanpur Feeder | B723B | 11 |  | DHKC 9348 | 1 | 5240.9 | 32799.1 | 27558.2 | 60 |  | 1653492 | 1671397.6523 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1671397.6523 | 1767813.7522 | -96416.0999 | -5.454 | OK
13 | 11 kV Mission Para Feeder. | B723T | 11 |  | DHKC 9347 | 1 | 87209.98 | 112889.86 | 25679.88 | 60 |  | 1540792.8 | 1557478.0335 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1557478.0335 | 1662446.9196 | -104968.8861 | -6.3141 | OK
14 | 11 kV Esha Kha Feeder | B723M | 11 |  | DHKC 9311 | 1 | 12466.88 | 29602.88 | 17136 | 60 |  | 1028160 | 1039293.9368 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 1039293.9368 | 1004043.7507 | 35250.1861 | 3.5108 | OK
15 | 11 kV New Hazigonj Feeder | B723F | 11 |  | DHKC 9314 | 1 | 241.31 | 275.24 | 33.93 | 60000 |  | 2035800 | 2057845.6627 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 2057845.6627 | 2170066.5597 | -112220.8969 | -5.1713 | OK
16 | 11 kV Spare Feeder. |  | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | B723H | 11 |  | 6604412 | 1 | 7.01 | 8.03 | 1.02 | 60000 |  | 61200 | 61862.7343 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 61862.7343 | 64307.2562 | -2444.5218 | -3.8013 | OK
20 | 11 kV Old Hajiganj Feeder. | B723E | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 |  | 06604389 | 1 | 49646.85 | 70259.15 | 20612.3 | 60 |  | 1236738 | 1250130.6264 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 1250130.6264 | 1328944.0291 | -78813.4027 | -5.9305 | OK
22 | 11 kV Spare Feeder. |  | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming |  | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | A723A | 11 |  | 6604415 | 1 | 329.61 | 375.72 | 46.11 | 40000 |  | 1844400 | 1864372.9936 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1864372.9936 | 1918297.585 | -53924.5914 | -2.8111 | OK
26 | 11 kV Mondalpara Feeder. |  | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | B723C | 11 |  | 06604392 | 1 | 257.82 | 293.14 | 35.32 | 40000 |  | 1412800 | 1428099.2005 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1428099.2005 | 1517085.0182 | -88985.8178 | -5.8656 | OK
28 | 11 kV Bishaw Road Feeder. | B723A | 11 |  | 06604393 | 1 | 281.34 | 308.98 | 27.64 | 40000 |  | 1105600 | 1117572.534 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 1117572.534 | 1216580.0413 | -99007.5073 | -8.1382 | OK
29 | 11 kV Chasara Feeder. | A723B | 11 |  | 06604391 | 1 | 362.61 | 410.64 | 48.03 | 40000 |  | 1921200 | 1942004.6602 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 1942004.6602 | 2118903.8684 | -176899.2082 | -8.3486 | OK
31 | 11 kV Pathan Tully Feeder. | B723G | 11 |  | 06604388 | 1 | 50.76 | 65.03 | 14.27 | 40000 |  | 570800 | 576981.1889 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 576981.1889 | 529827.0791 | 47154.1097 | 8.8999 | OK
32 | 11 kV Spare Feeder. |  | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | B722J | 11 |  | 6604289 | 1 | 233.78 | 266.66 | 32.88 | 40000 |  | 1315200 | 1329442.2908 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1329442.2908 | 1269562.7492 | 59879.5416 | 4.7165 | OK
34 | 11 kV Spare Feeder. |  | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. |  | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. |  | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 |  | 0.415 |  | 412109 | 1 | 9177.2 | 9204 | 26.8 | 10 |  | 268 | 270.9022 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 270.9022 | 317.4918 | -46.5896 | -14.6743 | OK
38 | 33/0.415 kV Auxiliary Transformer-2 |  | 0.415 |  | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 |  | 3000 | 3032.487 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3032.487 | 3033.3611 | -0.87416 | -0.028818 | OK
|  |  | 10: Grand Total | 15899784.9033 | 15729450.8 | 15899784.9033 | 1.0829
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (West) | at 33 KV level |  | 3806377.6538
[6 empty] | N.Gonj (East) | at 33 KV level |  | 12093407.2495
[6 empty] | Total = |  |  | 15899784.9033 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail |  | 132 | Impt | 8993555 | 1 | 2837.573 | 2867.349 | 29.776 | 1440000 | 0 | 42877440
|  |  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar |  | 3: 132; 4: Impt; 6: 1; 9=8-7: 0 | 0 | 0
|  |  | 3: 132; 4: Expt; 6: 1; 9=8-7: 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 42877440
|  |  | 10: Net Total | 42877440
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder |  | 132 | Impt |  | 1 | 0 | 0 | 0 | 1 | 0
|  |  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  |  | 132 | Expt |  | 1 | 8835168 | 8845764 | 10596 | 1 | 10596
|  |  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder |  | 132 | Impt | HA040700237-03 | 1 | 35292309 | 35292309 | 0 | 1
|  |  | 132 |  | 06604364 | 1 | 6097.39 | 6104.46 | 7.07 | 960000 | 6787200
|  |  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  |  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
|  |  | 9=8-7: Total Import/Export | 6797796 | 0
|  |  | 9=8-7: Net Total | 6797796
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 10: Total |  | 0
MOGBAZAR 132 KV SIDE
4 | 132/33 KV Transformer, GT-1 |  | 132 | DPDC | H/A040700240-03 | 1 | 79245.839 | 100656.262 | 21410.423 | 1000 |  | 21410423
|  |  | 132 | P. Cell | 08993572 | 1 | 5035.178 | 5035.178 | 0 | 480000 |  | 0
5 | 132/33 KV Transformer, GT-2 |  | 132 | DPDC | H/A030700918-03 | 1 | 40023.186 | 61470.348 | 21447.162 | 1000 |  | 21447162
|  |  | 132 | P. Cell | 08993577 | 1 | 5096.89 | 5141.562 | 44.672 | 480000 |  | 21442560
|  |  | 10: Total |  | 42857585
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 4: 42877440; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 42877440
| 132 KV Sending From Maniknagar |  | 4: 0; 6: 132 KV NET IMPORT; 9=8-7: 42877440 | 132/33 KV GT LV Side |  | 42970364
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -92924
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -0.2167%
| 132 KV TOTAL IMPORT |  | 4: 42877440
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | 4: IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 70980.761 | 92536.341 | 21555.58 | 1000 | 21555580
|  |  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | DPDC | H/A060300186-03 | 1 | 91498.226 | 112913.01 | 21414.784 | 1000 | 21414784
|  |  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
|  |  | 7: 0; 8: 0; 10: Total | 42970364 |  | 0
| MATUAIL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 |  | 33 | DPDC | H/A060300287-03 | 1.45 | 72725.355 | 80475.35 | 7749.995 | 1000 |  | 11237492.75 | 11274886.4179 |  | 19731432.9348 | Matuail 33/11 kv ss | 1.0512 | 33/11 KV Transformer, T-3 | 11274886.4179 | 10617809.1354 | 657077.2825 | 6.1884 | OK
|  |  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 |  | 33 | DPDC | H/A060300190-03 | 1 | 70575.182 | 79030.852 | 8455.67 | 1000 |  | 8455670 | 8483806.9272 |  |  |  |  | 33/11 KV Transformer, T-4 | 8483806.9272 | 8327750.1358 | 156056.7915 | 1.8739 | OK
|  |  | 33 | P. Cell | 08993581 | 1 | 6296.141 | 6342.966 | 46.825 | 180000 |  | 8428500 | 8456546.5169 |  |  |  |  | 0 | 8456546.5169 | 8318481.3944 | 138065.1225 | 1.6597 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 19665992.75 | 19731432.9348 |  |  |  |  | 33 KV Feeders | 19731432.9348 | 18936290.5298 | 795142.405 | 4.199 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 4175600 | 11280320 | 7104720 | 1 |  | 7104720 | 7128361.5316 |  | 16141694.6563 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 7128361.5316 | 6696698.3984 | 431663.1332 | 6.4459 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.258 | 39497.26 | 0.002 | 1000 |  | 3 | 3.01 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 3.01 | 1.5107 | 1.4993 | 99.2422 | FAULT
|  |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC |  | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 8133 | 8160.0632 | Matuail | Customer Number 35568341 |  |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 8160.0632 | 8383.4623 | -223.3991 | -2.6648 | OK
|  |  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 3.01 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 75609.32 | 82417.915 | 6808.595 | 1000 |  | 6808595 | 6831251.1517 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 6831251.1517 | 6057595.363 | 773655.7887 | 12.7717 | OK
|  |  | 33 | P. Cell | 08993580 | 1.5 | 1388.271 | 1413.422 | 25.151 | 180000 |  | 6790770 | 6813366.8376 |  |  |  |  | 0 | 6813366.8376 | 6053405.6462 | 759961.1914 | 12.5543 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 6831251.1517 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 | DPDC | 00000154 | 1 | 9119600 | 18103040 | 8983440 | 1 |  | 8983440 | 9013333.1247 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 9013333.1247 | 8784144.2518 | 229188.8729 | 2.6091 | OK
|  |  | 10: Total |  | 22904891 | 22981108.8812 |  |  |  |  | 0 | 22981108.8812 | 21546822.9862 | 1434285.895 | 6.6566 | OK
|  |  | 9=8-7: Grand Total | 42712541.816 | 42570883.75 | 42712541.816 | 0.33276
[6 empty] | 33 KV EXPORT |  |  | KWH
[6 empty] | EXPORT TO Matuail |  |  | 8160.0632
[6 empty] | Total Export |  |  | 8160.0632 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426631 | 1 | 7759571 | 7846895 | 87324 | 90 | 7859160 |  | 9562441.5169
11 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | 51426633 | 1 | 7386812 | 7479675 | 92863 | 90 | 8357670 |  | 10168991.4179
|  |  | 7: 0; 8: 0; 10: Total | 16216830 |  | 19731432.9348
| MATUAIL 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Link Road Feeder | B741N | 11 | Backup | DHK66629 | 1 | 24307.85 | 24693.58 | 385.73 | 8000 |  | 3085840 | 3118278.6369 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 3118278.6369 | 2941976.2695 | 176302.3673 | 5.9927 | OK
|  |  | 11 |  | HA021100475-02 | 1 | 94015.775 | 97092.756 | 3076.981 | 1000 |  | 3076981 | 3109326.5102 | N.Gonj (East) |  |  |  | 0 | 3109326.5102 | 2934230.0248 | 175096.4855 | 5.9674 | OK
4 | 11 kV Lamapara Express Feeder | B723L | 11 |  | HA021100928-03 | 1 | 79149.036 | 80182.444 | 1033.408 | 1000 |  | 1033408 | 1044271.2809 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1044271.2809 | 777935.2019 | 266336.0791 | 34.2363 | OK
5 | 11 kV Kutubpur Feeder*** | B741Q | 11 |  | DHK66616 | 1 | 18071.3 | 18290.01 | 218.71 | 8000 |  | 1749680 | 1768072.7988 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1768072.7988 | 1341995.221 | 426077.5777 | 31.7496 | OK
|  |  | 11 | Backup | XA575929 | 1 | 43481.2 | 45228.5 | 1747.3 | 1000 |  | 1747300 | 1765667.78 | N.Gonj (East) |  |  |  | 0 | 1765667.78 | 1341469.7093 | 424198.0707 | 31.6219 | OK
6 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 |  | DHK66625 | 1 | 3557.19 | 3580.6 | 23.41 | 60000 |  | 1404600 | 1419365.2857 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1419365.2857 | 1418275.2675 | 1090.0183 | 0.076855 | OK
|  |  | 11 | Backup |  | 1 | 8395.82 | 8395.82 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Tushardhara Feeder (F2) | E241T | 11 |  | DHK66623 | 1 | 3887.45 | 3931.53 | 44.08 | 60000 |  | 2644800 | 2672602.3834 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2672602.3834 | 2999054.9265 | -326452.5431 | -10.8852 | OK
8 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 |  | DHK66627 | 1 | 3316.68 | 3332.15 | 15.47 | 60000 |  | 928200 | 937957.3247 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 937957.3247 | 903475.9079 | 34481.4168 | 3.8165 | OK
|  |  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 |  | HA021101044-02 | 1 | 66232.154 | 66528.706 | 296.552 | 1000 |  | 296552 | 299669.3822 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 299669.3822 | 351957.4279 | -52288.0457 | -14.8564 | OK
12 | 11 kV Shibu Market Feeder (F7) | B841B | 11 |  | DHK66624 | 1 | 2383.91 | 2390.92 | 7.01 | 60000 |  | 420600 | 425021.3863 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 425021.3863 | 388070.1886 | 36951.1977 | 9.5218 | OK
13 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 |  | HA060300286-03 | 1 | 3583.649 | 5075.064 | 1491.415 | 1000 |  | 1491415 | 1507092.8931 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 1507092.8931 | 1340202.4176 | 166890.4755 | 12.4526 | OK
14 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 |  | DHK66626 | 1 | 4466.06 | 4509.48 | 43.42 | 60000 |  | 2605200 | 2632586.1045 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2632586.1045 | 2681928.8192 | -49342.7147 | -1.8398 | OK
15 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK6622 | 1 | 4234.09 | 4256.29 | 22.2 | 60000 |  | 1332000 | 1346002.1078 | Matuail |  |  |  | 0 | 1346002.1078 | 1350362.9845 | -4360.8767 | -0.32294 | OK
16 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 |  | DHKA2187 | 1 | 120.5913 | 126.118 | 5.5267 | 60000 |  | 331602 | 335087.831 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 335087.831 | 248953.0896 | 86134.7414 | 34.5988 | OK
17 | 11 kV Bhuighor Bazar |  | 11 |  | HA021100861-02 | 1 | 869.686 | 2266.614 | 1396.928 | 1000 |  | 1396928 | 1411612.637 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 1411612.637 | 1387743.4624 | 23869.1745 | 1.72 | OK
18 | 11 kV Tokkar Math Feeder | B8416 | 11 |  | HA021200298-02 | 1 | 81846.959 | 82630.261 | 783.302 | 1000 |  | 783302 | 791536.1434 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 791536.1434 | 789253.9157 | 2282.2277 | 0.28916 | OK
19 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 |  | XA575922 | 1 | 213.4 | 232.8 | 19.4 | 1000 |  | 19400 | 19603.9346 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 19603.9346 | 10611.2942 | 8992.6404 | 84.7459 | FAULT
16 | 33/0.415 KV Transformer, AT-1 |  | 0.415 |  | 2001123043119 | 1 | 7506.3 | 7578.2 | 71.9 | 160 |  | 11504 | 11624.9311 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 11624.9311 | 12240.3805 | -615.4494 | -5.028 | OK
17 | 33/0.415 KV Transformer, AT-2 |  | 0.415 |  | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 |  | 0 | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 19731432.9348 | 19526172 | 19731432.9348 | 1.0512
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 5921670.5899
[6 empty] | Shyampur | at 33 KV level |  | 346712.7622
[6 empty] | Fatullah | at 33 KV level |  | 4162619.6431
[6 empty] | Matuail | at 33 KV level |  | 9300429.9395
[6 empty] | Total = |  |  | 19731432.9348 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** |  | 33 | DPDC | 00000073 | 1 | 4175600 | 11280320 | 7104720 | 1 | 0 | 7104720 | 7128361.5316
15 | 33 kV Laxmi Narayan Cotton Mill-2**** |  | 33 |  | 00000154 | 1 | 9119600 | 18103040 | 8983440 | 1 | 0 | 8983440 | 9013333.1247
|  |  | 10: Total | 0 | 16088160 | 16141694.6563
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder |  | 33 |  | 00000079 | 1 | 346348704 | 355244928 | 8896224 | 1 | 8896224
7 | 33 kV Matuail-1 Feeder |  | 33 |  | 00000114 | 1 | 282230176 | 289280960 | 7050784 | 1 | 7050784
|  |  | 7: 0; 8: 0; 10: Total | 15947008 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000075 | 1 | 361067264 | 369965504 | 8898240 | 1 |  | 8898240
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000156 | 1 | 267582240 | 274632704 | 7050464 | 1 |  | 7050464
|  |  | 10: Total |  | 15948704
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 16141694.6563; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 16141694.6563
| IMPORT-2 |  | 6: 33 KV Net Import; 9=8-7: 16141694.6563 | 33 KV TX HV Side |  | 15948704
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 192990.6563
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.196%
| TOTAL IMPORT |  | 4: 16141694.6563
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming |  | 11 |  | 00000144 | 1 | 359756960 | 368629376 | 8872416 | 1 | 8872416 |  | 9008064.4675
18 | 11 kV T-1 Incoming |  | 11 |  | 00000054 | 1 | 265967936 | 272994144 | 7026208 | 1 | 7026208 |  | 7133630.1889
|  |  | 7: 0; 8: 0; 10: Total | 15898624 |  | 16141694.6563
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Godnail (F16) | A8963 | 11 |  | 00000109 | 1 | 28743610 | 30618406 | 1874796 | 1 |  | 1874796 | 1902311.4075 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1902311.4075 | 2038403.821 | -136092.4135 | -6.6764 | OK
2 | 11 kV M. Circus (F15) | B796C | 11 |  | 00000123 | 1 | 110692328 | 112349288 | 1656960 | 1 |  | 1656960 | 1681278.3417 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1681278.3417 | 1521029.259 | 160249.0826 | 10.5356 | OK
3 | 11 kV Wapderpool (F14) | B723W | 11 |  | 00000190 | 1 | 57555940 | 58342616 | 786676 | 1 |  | 786676 | 798221.6352 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 798221.6352 | 482340.828 | 315880.8072 | 65.4891 | FAULT
4 | 11 kV Chowdhury Bari (F13) | A896C | 11 |  | 00000191 | 1 | 102995352 | 105146864 | 2151512 | 1 |  | 2151512 | 2183088.6246 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2183088.6246 | 2226891.1005 | -43802.4759 | -1.967 | OK
5 | 11 kV Ailpara (F12) | B7966 | 1 |  | 00000192 | 1 | 56582940 | 58996976 | 2414036 | 1 |  | 2414036 | 2449465.553 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2449465.553 | 2507772.6658 | -58307.1128 | -2.3251 | OK
6 | 11 kV Spare (F11) |  | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) |  | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) |  | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) |  | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | A8962H | 11 |  | 00000197 | 1 | 17476638 | 18664354 | 1187716 | 1 |  | 1187716 | 1205147.4911 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1205147.4911 | 881898.0967 | 323249.3944 | 36.6538 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 |  | 00000198 | 1 | 4203789 | 4241549 | 37760 | 1 |  | 37760 | 38314.1839 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 38314.1839 | 81476.5739 | -43162.39 | -52.9752 | CHECK
12 | 11 kV Lucky Bazar (F5) | B796Z | 11 |  | 00000199 | 1 | 91070136 | 92459576 | 1389440 | 1 |  | 1389440 | 1409832.0895 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1409832.0895 | 1363293.8581 | 46538.2314 | 3.4137 | OK
13 | 11 kV Enayetnagar (F4) | A896Y | 11 |  | 00000200 | 1 | 34021796 | 35538712 | 1516916 | 1 |  | 1516916 | 1539178.9886 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1539178.9886 | 1637703.7047 | -98524.7161 | -6.016 | OK
14 | 11 kV Bhuiyapara (F3) | A896V | 11 |  | 00000201 | 1 | 67505552 | 69299712 | 1794160 | 1 |  | 1794160 | 1820491.9548 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1820491.9548 | 1638474.4387 | 182017.5161 | 11.109 | OK
15 | 11 kV Arambagh (F2) | B796D | 11 |  | 00000202 | 1 | 10097575 | 11191773 | 1094198 | 1 |  | 1094198 | 1110256.976 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 1110256.976 | 1096967.543 | 13289.433 | 1.2115 | OK
16 | 11 kV Spare (F1) |  | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 |  | 0.415 |  | 00000204 | 1 | 1713.27 | 1753.31 | 40.04 | 100 |  | 4004 | 4062.7646 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 4062.7646 | 4590.7608 | -527.9962 | -11.5013 | OK
18 | 11/0.415 kV Aux. Transformer-2 |  | 0.415 |  | 00000205 | 1 | 60.72 | 61.16 | 0.44 | 100 |  | 44 | 44.6458 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 44.6458 | 0 | 44.6458 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 16141694.6563 | 15908218 | 16141694.6563 | 1.4676
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 7491476.1897
[6 empty] | Siddirgonj | at 33 KV level |  | 8650218.4666
[6 empty] | Total = |  |  | 16141694.6563 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) |  | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.258 | 39497.26 | 0.002 | 1000 | 0 | 3 | 3.01
0 | 0 |  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) |  | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 |  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side |  | 10: Total | 0 | 3 | 3.01
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 739.8 | 763.72 | 23.92 | 360000 | 0 | 8611200 | 8606218.6846
0 | 0 |  | 33 | Backup | 041808904262 | 1 | 739.81 | 763.74 | 23.93 | 360000 | 0 | 8614800 | 8609816.6021
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 510.23 | 521.27 | 11.04 | 360000 | 0 | 3974400 | 3972100.9313
0 | 0 |  | 33 | Backup | 041808904258 | 1 | 510.42 | 521.47 | 11.05 | 360000 | 0 | 3978000 | 3975698.8488
|  |  | 10: Total | 0 | 12585600 | 12578319.6159
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) |  | 33 | Digital | DHK60875 | 1 | 312538.4 | 348151.5 | 35613.1 | 240 | 8547144
9 | 33 kV New Fatulla-2 |  | 33 | Digital | DHK2186 | 1 | 354.6214 | 365.6807 | 11.0593 | 360000 | 3981348
|  |  | 7: 0; 8: 0; 10: Total | 12528492 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  | 7: 0; 8: 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) |  | 33 | Digital | DHK60980 | 1 | 979442.9 | 1005390.6 | 25947.7 | 240 |  | 6227448
13 | 33/11 kV, 20/28 MVA T-2 (HV) |  | 33 | Digital | DHK60952 | 1 | 530367.2 | 539976.3 | 9609.1 | 240 |  | 8547144 |  |  | Meter Problem
|  |  | 10: Total |  | 14774592 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 4: 3.01; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 12578322.6259
| New Fatullah 33 kv Side |  | 4: 12578319.6159; 6: 33 KV Net Import; 9=8-7: 12578322.6259 | 33 KV TX HV Side |  | 14774592
[11 empty] | LOSS UNITS=> |  | -2196269.3741
[11 empty] | LOSS % IN => |  | -17.46%
| TOTAL IMPORT |  | 4: 12578322.6259
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [19 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming |  | 11 | New | DHK61060 | 1 | 178380 | 210760.5 | 32380.5 | 180 | 5828490 |  | 6067756.2779 | [7 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming |  | 11 | New | DHK61054 | 1 | 425687.3 | 438470.1 | 12782.8 | 180 | 2300904 |  | 2395358.7792 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming |  | 11 | New | DHK60924 | 1.1 | 479786.3 | 487046.8 | 7260.5 | 180 | 1437579 |  | 1496593.2861 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming |  | 11 | New | DHK61051 | 1 | 978371.5 | 1006319.9 | 27948.4 | 90 | 2515356 |  | 2618614.2826 | [7 empty] | 0 | #DIV/0! | #DIV/0!
|  |  | 7: 0; 8: 0; 10: Total | 12082329 |  | 12578322.6259 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE |  | 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | A717R | 11 | New |  | 1 | 76821856 | 77458900 | 637044 | 1 |  | 637044 | 639787.7036 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 639787.7036 | 668682.8226 | -28895.119 | -4.3212 | OK
15 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 89548428 | 90382612 | 834184 | 1 |  | 834184 | 837776.7717 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 837776.7717 | 798148.0435 | 39628.7281 | 4.9651 | OK
16 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 186054.2 | 205819 | 19764.8 | 60 |  | 1185888 | 1190995.536 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1190995.536 | 1654746.3681 | -463750.8321 | -28.0255 | OK
17 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 342116.1 | 358618.1 | 16502 | 60 |  | 990120 | 994384.377 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 994384.377 | 1017275.0549 | -22890.6778 | -2.2502 | OK
19 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 36070.8 | 67878.2 | 31807.4 | 60 |  | 1908444 | 1916663.5337 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1916663.5337 | 1932341.6728 | -15678.1391 | -0.81135 | OK
20 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 80146 | 91772.6 | 11626.6 | 60 |  | 697596 | 700600.4968 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 700600.4968 | 623925.9784 | 76674.5183 | 12.289 | OK
23 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 646090.6 | 661621.5 | 15530.9 | 60 |  | 931854 | 935867.4295 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 935867.4295 | 898188.9867 | 37678.4427 | 4.1949 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 541205.3 | 559147.2 | 17941.9 | 60 |  | 1076514 | 1081150.4699 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1081150.4699 | 1065440.2479 | 15710.222 | 1.4745 | OK
25 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 872508.4 | 877493.5 | 4985.1 | 60 |  | 299106 | 300394.2285 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 300394.2285 | 217235.7079 | 83158.5205 | 38.2803 | OK
26 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538878 | 538934.5 | 56.5 | 60 |  | 3390 | 3404.6005 | Fatullah |  |  |  | 11 kV Dhaka Steel | 3404.6005 | 458632.0662 | -455227.4657 | -99.2577 | CHECK
27 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 1798728 | 2534578 | 735850 | 1 |  | 735850 | 739019.2541 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 739019.2541 | 764214.6584 | -25195.4043 | -3.2969 | OK
28 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 25554756 | 25882355 | 327599 | 1 |  | 327599 | 329009.9458 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 329009.9458 | 336317.7733 | -7307.8275 | -2.1729 | OK
29 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 15758208 | 16128427 | 370219 | 1 |  | 370219 | 371813.5071 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 371813.5071 | 231457.5089 | 140355.9982 | 60.6401 | FAULT
30 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 16913493 | 17649412 | 735919 | 1 |  | 735919 | 739088.5512 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 739088.5512 | 985608.2317 | -246519.6804 | -25.0119 | OK
35 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 8389302 | 10179956 | 1790654 | 1 |  | 1790654 | 1798366.2205 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1798366.2205 | 1947566.1648 | -149199.9443 | -7.6608 | OK
37 | 11 kV Spare Feeder |  | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 |  | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 12578322.6259 | 12524381 | 12578322.6259 | 0.43069
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 9660915.4436
[6 empty] | N.Gonj (West) | at 33 KV level |  | 1477564.4753
[6 empty] | Sytalakhya | at 33 KV level |  | 1439842.707
[6 empty] | Total = |  |  | 12578322.6259 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder |  | 132 | Export | 041808902770 | 1 | 126.96 | 126.96 | 0 | 1200000 |  | 0
|  |  | 132 |  | 041808904227 | 1 | 126.96 | 126.96 | 0 | 1200000 |  | 0
|  |  | 132 | Import | 041808902770 | 1 | 227 | 256.46 | 29.46 | 1200000 | 35352000
|  |  | 132 |  | 041808904227 | 1 | 226.97 | 256.42 | 29.45 | 1200000 | 35340000
3 | 132 kV Haripur Feeder |  | 132 | Export | 041808902766 | 1 | 64.54 | 91.34 | 26.8 | 1200000 |  | 32160000
|  |  | 132 |  | 041808904230 | 1 | 64.56 | 91.38 | 26.82 | 1200000 |  | 32184000
|  |  | 132 | Import | 041808902766 | 1 | 719.67 | 720.47 | 0.8 | 1200000 | 960000
|  |  | 132 |  | 041808904230 | 1 | 719.92 | 720.72 | 0.8 | 1200000 | 960000
4 | 132 kV Aggreko Feeder |  | 132 | Export | 041808902768 | 1 | 30.52 | 30.88 | 0.36 | 1200000 |  | 432000
|  |  | 132 |  | 041808904219 | 1 | 30.52 | 30.88 | 0.36 | 1200000 |  | 432000
|  |  | 132 | Import | 041808902768 | 1 | 257.68 | 259.55 | 1.87 | 1200000 | 2244000
|  |  | 132 |  | 041808904219 | 1 | 257.68 | 259.55 | 1.87 | 1200000 | 2244000
6 | 132 kV Shyampur-2 Feeder |  | 132 | Export | 041808902793 | 1 | 120.73 | 120.73 | 0 | 1200000 |  | 0
|  |  | 132 |  | 041808904278 | 1 | 120.74 | 120.74 | 0 | 1200000 |  | 0
|  |  | 132 | Import | 041808902793 | 1 | 218.97 | 248.72 | 29.75 | 1200000 | 35700000
|  |  | 132 |  | 041808904278 | 1 | 219.02 | 248.76 | 29.74 | 1200000 | 35688000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 74256000 | 32592000
|  |  | 7: 0; 8: 0; 10: Net Total | 41664000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| FATULLAH 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | Export | 041808902767 | 1 | 613.01 | 631.52 | 18.51 | 1200000 |  | 22212000
|  |  | 132 | Export | 041808904228 | 1 | 612.85 | 631.35 | 18.5 | 1200000 |  | 22200000
5 | 132/33 kV, 80/120 MVA GT-2 |  | 132 | Export | 041808902792 | 1 | 470.73 | 486.92 | 16.19 | 1200000 |  | 19428000
|  |  | 132 | Export | 041808904251 | 1 | 470.55 | 486.73 | 16.18 | 1200000 |  | 19416000
|  |  | 10: Total |  | 41640000
| 132 KV IMPORT |  | 4: KWH | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 4: 41664000 | 132 KV NET IMPORT |  | 41664000
| IMPORT-2 | [9 empty] | 132/33 KV GT LV Side |  | 41464800
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 199200
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.4781%
| 132 KV TOTAL IMPORT |  | 4: 41664000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902796 | 1 | 1016.88 | 1047.58 | 30.7 | 720000 | 22104000
|  |  | 33 | Backup | 041808904255 | 1 | 1016.88 | 1047.58 | 30.7 | 720000 | 22104000
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902802 | 1 | 781.17 | 808.06 | 26.89 | 720000 | 19360800
|  |  | 33 | Backup | 041808904281 | 1 | 780.98 | 807.86 | 26.88 | 720000 | 19353600
|  |  | 7: 0; 8: 0; 10: Total | 41464800 |  | 0
| FATULLAH 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902868 | 1 | 809.22 | 835.73 | 26.51 | 240000 |  | 6362400 | 6358719.5465 |  | 12832572.4533 | New Fatullah 33/11 kv ss | 0.22785 | 33/11 kV, 28/35 MVA T-1 (=H5) | 6358719.5465 | 6409629.0822 | -50909.5357 | -0.79427 | OK
|  |  | 33 | Backup | 041808904277 | 1 | 808.7 | 835.19 | 26.49 | 240000 |  | 6357600 | 6353922.3231 |  |  |  |  | 0 | 6353922.3231 | 6189020.8235 | 164901.4997 | 2.6644 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902824 | 1 | 710.71 | 737.7 | 26.99 | 240000 |  | 6477600 | 6473852.9068 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 6473852.9068 | 5894077.1732 | 579775.7336 | 9.8366 | OK
|  |  | 33 | Backup | 041808904267 | 1 | 710.6 | 737.58 | 26.98 | 240000 |  | 6475200 | 6471454.2951 |  |  |  |  | 0 | 6471454.2951 | 5891679.2574 | 579775.0378 | 9.8406 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 12840000 | 12832572.4533 |  |  |  |  | 33 KV Feeders | 12832572.4533 | 12303706.2554 | 528866.1979 | 4.2984 | OK
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 781.82 | 801.89 | 20.07 | 360000 |  | 7225200 | 7221020.4431 |  | 16053907.9308 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 7221020.4431 | 6459985.3152 | 761035.1279 | 11.7808 | OK
|  |  | 33 | Backup | 041808904220 | 1 | 781.47 | 801.49 | 20.02 | 360000 |  | 7207200 | 7203030.8556 |  |  |  |  | 0 | 7203030.8556 | 6474372.8103 | 728658.0453 | 11.2545 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) |  | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) |  | 33 | Main | 041808902828 | 1 | 739.8 | 763.72 | 23.92 | 360000 |  | 8611200 | 8606218.6846 |  | 12578319.6159 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 8606218.6846 | 9341081.2158 | -734862.5312 | -7.867 | OK
|  |  | 33 | Backup | 041808904262 | 1 | 739.81 | 763.74 | 23.93 | 360000 |  | 8614800 | 8609816.6021 |  |  |  |  | 0 | 8609816.6021 | 9341081.2158 | -731264.6137 | -7.8285 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 553.48 | 578.03 | 24.55 | 360000 |  | 8838000 | 8832887.4877 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 8832887.4877 | 7675728.654 | 1157158.8337 | 15.0756 | OK
|  |  | 33 | Backup | 041808904219 | 1 | 553.81 | 578.38 | 24.57 | 360000 |  | 8845200 | 8840083.3227 |  |  |  |  | 0 | 8840083.3227 | 7679325.5278 | 1160757.795 | 15.1154 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) |  | 33 | Main | 041808902873 | 1 | 510.23 | 521.27 | 11.04 | 360000 |  | 3974400 | 3972100.9313 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 3972100.9313 | 4258698.5597 | -286597.6283 | -6.7297 | OK
|  |  | 33 | Backup | 041808904258 | 1 | 510.42 | 521.47 | 11.05 | 360000 |  | 3978000 | 3975698.8488 |  |  |  |  | 0 | 3975698.8488 | 4258698.5597 | -282999.7108 | -6.6452 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) |  | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total |  | 28648800 | 28632227.5467 |  |  |  |  | 0 | 28632227.5467 | 27735493.7446 | 896733.8021 | 3.2332 | OK
|  |  | 9=8-7: Grand Total | 41464800 | 41488800 | 41464800 | -0.057847
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902832 | 1 | 774.68 | 800.08 | 25.4 | 250000 | 6350000 |  | 6359948.1037
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902765 | 1 | 680.28 | 706.13 | 25.85 | 250000 | 6462500 |  | 6472624.3496
|  |  | 7: 0; 8: 0; 10: Total | 12812500 |  | 12832572.4533
| FATULLAH 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) |  | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 959.96 | 999.44 | 39.48 | 60000 |  | 2368800 | 2374197.2935 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 2374197.2935 | 2139879.5383 | 234317.7552 | 10.95 | OK
7 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 471.37 | 497.96 | 26.59 | 60000 |  | 1595400 | 1599035.1072 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1599035.1072 | 1814088.8895 | -215053.7823 | -11.8546 | OK
8 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 553.03 | 563.73 | 10.7 | 60000 |  | 642000 | 643462.7923 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 643462.7923 | 673220.5289 | -29757.7366 | -4.4202 | OK
9 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1238.64 | 1267.53 | 28.89 | 60000 |  | 1733400 | 1737349.5392 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1737349.5392 | 1778023.504 | -40673.9648 | -2.2876 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) |  | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) |  | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 195.76 | 213.78 | 18.02 | 60000 |  | 1081200 | 1083663.5063 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 1083663.5063 | 1145075.9889 | -61412.4826 | -5.3632 | OK
16 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 88.69 | 98.21 | 9.52 | 60000 |  | 571200 | 572501.475 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 572501.475 | 611308.2838 | -38806.8088 | -6.3482 | OK
17 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1141.38 | 1178.03 | 36.65 | 60000 |  | 2199000 | 2204010.4054 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 2204010.4054 | 1471467.7275 | 732542.678 | 49.7831 | FAULT
18 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1408.64 | 1452.18 | 43.54 | 60000 |  | 2612400 | 2618352.3343 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2618352.3343 | 2670641.7946 | -52289.4603 | -1.9579 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 12832572.4533 | 12803400 | 12832572.4533 | 0.22785
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 12832572.4533
[6 empty] | Total = |  |  | 12832572.4533 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) |  | 33 | Main | 041808902822 | 1 | 781.82 | 801.89 | 20.07 | 360000 | 0 | 7225200 | 7221020.4431
0 | 0 |  | 33 | Backup | 041808904220 | 1 | 781.47 | 801.49 | 20.02 | 360000 | 0 | 7207200 | 7203030.8556
17 | 33 kV Dapa Circuit-2 (=H11) |  | 33 | Main | 041808902825 | 1 | 553.48 | 578.03 | 24.55 | 360000 | 0 | 8838000 | 8832887.4877
0 | 0 |  | 33 | Backup | 041808904219 | 1 | 553.81 | 578.38 | 24.57 | 360000 | 0 | 8845200 | 8840083.3227
| DAPA 33 KV SIDE (RECEIVING) |  | 10: Total | 0 | 16063200 | 16053907.9308
5 | 33 kV New Fatullah Incoming Circuit-2 |  | 33 | Import |  | 1 | 198883072 | 207699664 | 8816592 | 1 | 8816592
6 | 33 kV Shyampur Incoming Circuit |  | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder |  | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  |  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 |  | 33 | Import |  | 1 | 280967392 | 288178816 | 7211424 | 1 | 7211424
|  |  | 7: 0; 8: 0; 10: Total | 16028016 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| DAPA 33 KV SIDE |  | 7: 0; 8: 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) |  | 33 | Export | 00000135 | 1 | 290445824 | 299261760 | 8815936 | 1 |  | 8815936
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) |  | 33 | Export | 00000193 | 1 | 282640576 | 289843904 | 7203328 | 1 |  | 7203328
|  |  | 10: Total |  | 16019264 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 4: 16053907.9308; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 16053907.9308
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 16053907.9308 | 33 KV TX HV SIDE |  | 16019264
[11 empty] | LOSS UNITS=> |  | 34643.9308
[11 empty] | LOSS % IN => |  | 0.2158%
| TOTAL IMPORT |  | 4: 16053907.9308
11 KV SIDE of___DAPA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 00000035 | 1 | 81020736 | 81020736 | 0 | 1 | 0 |  | 0
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000143 | 1 | 289196544 | 297978560 | 8782016 | 1 | 8782016 |  | 16053907.9308
|  |  | 7: 0; 8: 0; 10: Total | 8782016 |  | 16053907.9308
| DAPA 11 KV SIDE |  | 7: 0; 8: 0
11 | 11 kV Katherpol Feeder | B8919 | 11 |  | 00000031 | 1 | 67326752 | 69331312 | 2004560 | 1 |  | 2004560 | 2017920.9065 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 2017920.9065 | 1907068.817 | 110852.0895 | 5.8127 | OK
12 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | B8918 | 11 |  | 00000032 | 1 | 67588392 | 69825752 | 2237360 | 1 |  | 2237360 | 2252272.5782 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 2252272.5782 | 1663620.755 | 588651.8232 | 35.3838 | OK
14 | 11 kV Shiachar Feeder | B891G | 11 |  | 00000030 | 1 | 69814874 | 71832544 | 2017670 | 1 |  | 2017670 | 2031118.288 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 2031118.288 | 2032383.0231 | -1264.735 | -0.062229 | OK
15 | 11 kV Sastapur Feeder | B8913 | 11 |  | 00000106 | 1 | 71305504 | 71818424 | 512920 | 1 |  | 512920 | 516338.7434 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 516338.7434 | 559825.9548 | -43487.2115 | -7.768 | OK
17 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | B891JA | 11 |  | 00000172 | 1 | 5241627 | 5637386 | 395759 | 1 |  | 395759 | 398396.8352 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 398396.8352 | 281983.6134 | 116413.2218 | 41.2837 | FAULT
19 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | B8911 | 11 |  | 00000044 | 1 | 81400280 | 84092032 | 2691752 | 1 |  | 2691752 | 2709693.2174 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 2709693.2174 | 2479807.3342 | 229885.8832 | 9.2703 | OK
23 | 11 kV Kotaler Bag Feeder | B8912 | 11 |  | 00000050 | 1 | 87316664 | 89610784 | 2294120 | 1 |  | 2294120 | 2309410.8982 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 2309410.8982 | 2305548.0804 | 3862.8178 | 0.16754 | OK
24 | 11 kV Idrakpur Feeder | B8915 | 11 |  | 00000021 | 1 | 77920088 | 79058888 | 1138800 | 1 |  | 1138800 | 1146390.3941 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 1146390.3941 | 1054879.9219 | 91510.4721 | 8.675 | OK
25 | 11 kV Isdair Feeder | B8914 | 11 |  | 00000029 | 1 | 41690220 | 42475456 | 785236 | 1 |  | 785236 | 790469.7993 | Fatullah |  |  |  | 11 kV Isdair Feeder | 790469.7993 | 829018.6896 | -38548.8902 | -4.6499 | OK
26 | 11 kV Shah Fateullah Express |  | 11 |  | 0000051 | 1 | 1009637 | 2873073 | 1863436 | 1 |  | 1863436 | 1875856.2789 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 1875856.2789 | 1015342.7418 | 860513.537 | 84.751 | FAULT
27 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 |  | 0.415 |  | DHKF 7522 | 1 | 3132 | 3192 | 60 | 100 |  | 6000 | 6039.9915 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 6039.9915 | 6235.0379 | -195.0464 | -3.1282 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 |  | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 16053907.9308 | 15947613 | 16053907.9308 | 0.66653
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 16053907.9308
[6 empty] | Total = |  |  | 16053907.9308 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 |  | 132 | IMPORT | 50501730 | 1 | 2905.949 | 2948.743 | 42.794 | 480000 | 0 | 20541120
2 | Tranformer 1 |  | 132 |  | 80505634 | 1 | 8501.42 | 8541.707 | 40.287 | 480000 | 0 | 19337760
3 | Tranformer 2 |  | 132 |  | 80505637 | 1 | 8454.115 | 8494.043 | 39.928 | 480000 | 0 | 19165440
4 | MI CEMENT |  | 132 |  | 38992489 (New) | 1 | 325.051 | 350.233 | 25.182 | 480000 | 0 | 12087360
|  |  | 9=8-7: Total Import/Export | 0 | 71131680
|  |  | 10: Net Total | 71131680
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 325.031 | 350.233 | 25.202 | 480000 |  | 12096960
|  |  | 132 | DPDC | 16402670 | 1 | 1850.027 | 1875.206 | 25.179 | 480000 |  | 12085920
|  |  | 10: Total |  | 12085920
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
| 132/33 KV GT-3 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 59045760
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 71131680; 6: EXPORT TO OTHER S/S; 9=8-7: 12085920 | 132 KV NET IMPORT |  | 59045760
| IMPORT-2 |  | 6: 132 KV NET IMPORT for Sitalakhya 33/11 KV; 9=8-7: 59045760 | GT (33 KV Side) |  | 58998813
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 46947
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.07951%
| 132 KV TOTAL IMPORT |  | 4: 71131680
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming |  | 33 | DPDC | H/A030701130-03 | 1 | 10779.032 | 30217.589 | 19438.557 | 1000 | 19438557
|  |  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming |  | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  |  | 33 | DPDC | BD001913 | 1 | 1808.9269 | 1848.6479 | 39.721 | 480000 | 19066080
18 | 132/33 KV Transformer, GT-3 Incoming |  | 33 | DPDC | BD001915 | 1 | 2898.6283 | 2941.3245 | 42.6962 | 480000 | 20494176
|  |  | 7: 0; 8: 0; 10: Total | 58998813 |  | 0
| SITALAKHYA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 |  | 33 | DPDC | H/A030701089-03 | 1 | 89322.461 | 98625.747 | 9303.286 | 1000 |  | 9303286 | 9301117.9185 |  | 14060795.4423 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 9301117.9185 | 9414215.8021 | -113097.8836 | -1.2014 | OK
|  |  | 33 | P. Cell | 08993597 | 1 | 5946.01 | 5984.717 | 38.707 | 240000 |  | 9289680 | 9287515.0893 |  |  |  |  | 0 | 9287515.0893 | 9414007.6427 | -126492.5534 | -1.3437 | OK
13 | 33/11 KV Transformer T-4 |  | 33 | DPDC | H/A030701087-03 | 1 | 81165.111 | 85925.898 | 4760.787 | 1000 |  | 4760787 | 4759677.5238 |  |  |  |  | 33/11 KV Transformer T-4 | 4759677.5238 | 4923659.6995 | -163982.1757 | -3.3305 | OK
|  |  | 33 | P. Cell | 08993925 | 1 | 5712.057 | 5738.492 | 26.435 | 180000 |  | 4758300 | 4757191.1034 |  |  |  |  | 0 | 4757191.1034 | 4925871.3928 | -168680.2894 | -3.4244 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 14064073 | 14060795.4423 |  |  |  |  | 33 KV Feeders | 14060795.4423 | 14337875.5016 | -277080.0592 | -1.9325 | OK
10 | 33 KV Char Syedpur Feeder (F1) |  | 33 | DPDC | H/A030701083-03 | 1 | 42622.667 | 42622.667 | 0 | 1000 |  | 0 | 0 |  | 2519.4127 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 0 | 1.0008 | -1.0008 | -100 | CHECK
| 34 KV Char Syedpur Feeder (F1) |  | 33 | P. Cell | 08993596 | 1 | 2186.817 | 2186.831 | 0.014 | 180000 |  | 2520 | 2519.4127 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 2519.4127 | 0 | 2519.4127 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 40179.341 | 52115.953 | 11936.612 | 1000 |  | 11936612 | 11933830.2359 |  | 11933830.2359 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 11933830.2359 | 10113465.1681 | 1820365.0678 | 17.9994 | OK
| 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9847.982 | 9914.297 | 66.315 | 180000 |  | 11936700 | 11933918.2153 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 11933918.2153 | 10118166.7678 | 1815751.4476 | 17.9455 | OK
14 | 33 KV Shah Cement Feeder (F2) |  | 33 | DPDC | H/A030800181-03 | 1 | 41084.318 | 41084.427 | 0.109 | 1000 |  | 109 | 108.9746 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 108.9746 | 64646.4953 | -64537.5207 | -99.8314 | CHECK
|  |  | 33 | P. Cell | 08993926 | 1 | 2303.686 | 2303.686 | 0 | 180000 |  | 0 | 0 |  | 17340684.9033 | Khanpur 33/11 kv ss |  | 0 | 0 | 64129.0991 | -64129.0991 | -100 | CHECK
16 | 33 KV Khanpur-02 (Old) Feeder (F4) |  | 33 | DPDC | H/A030800200-03 | 1 | 29336.973 | 38383.46 | 9046.487 | 1000 |  | 9046487 | 9044378.7642 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 9044378.7642 | 9243170.845 | -198792.0808 | -2.1507 | OK
|  |  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1649.9119 | 1692.0883 | 42.1764 | 180000 |  | 7591752 | 7589982.7824 |  | 15597588.2175 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 7589982.7824 | 7664544.2018 | -74561.4193 | -0.97281 | OK
19 | 33 kV Khanpur-01(New) Feeder |  | 33 | DPDC | BD001864 | 1 | 474.2031 | 508.7791 | 34.576 | 240000 |  | 8298240 | 8296306.1392 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 8296306.1392 | 8534958.6168 | -238652.4776 | -2.7962 | OK
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1358.4878 | 1391.8606 | 33.3728 | 240000 |  | 8009472 | 8007605.435 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 8007605.435 | 8027954.4394 | -20349.0044 | -0.25348 | OK
21 | 33/0.415 KV Transformer AT-1 |  | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6559.9 | 4 | 160 |  | 640 | 639.8509 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 639.8509 | 0 | 639.8509 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 |  | 0.415 | DPDC | 2001123043171 | 1 | 4763.3 | 4786.1 | 22.8 | 160 |  | 3648 | 3647.1499 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 3647.1499 | 6180.7322 | -2533.5823 | -40.9916 | CHECK
|  |  | 10: Total |  | 44889480 | 44879018.7447 |  |  |  |  | 0 | 44879018.7447 | 43654920.4984 | 1224098.2462 | 2.804 | OK
|  |  | 9=8-7: Grand Total | 58939814.187 | 58953553 | 58939814.187 | -0.023304
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 4395.9753
[6 empty] | Total = |  |  | 4395.9753
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | DHK 9372 | 1 | 75433.4419 | 126942.4609 | 51509.019 | 180 | 9271623.42 |  | 9303322.5104 |  |  |  |  | 33/11 kV Transformer, T-3 Incoming | 9303322.5104 | 9424397.1143 | -121074.6039 | -1.2847 | OK
10 | 33/11 kV Transformer, T-4 Incoming |  | 11 |  | DHK 9368 | 1 | 42850.2222 | 69190.5714 | 26340.3492 | 180 | 4741262.856 |  | 4757472.932 |  |  |  |  | 33/11 kV Transformer, T-4 Incoming | 4757472.932 | 4913478.3873 | -156005.4554 | -3.1751 | OK
|  |  | 7: 0; 8: 0; 10: Total | 14012886.276 |  | 14060795.4423
| SITALAKHYA 11 kV SIDE |  | 7: 0; 8: 0
3 | 11 kV Bholail Feeder (F-3) | E330V | 11 |  | DHK 9335 | 1 | 26613.8765 | 70399.8787 | 43786.0022 | 60 |  | 2627160.132 | 2632122.2753 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 2632122.2753 | 3204950.7718 | -572828.4965 | -17.8732 | OK
4 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 |  | DHK 9336 | 1 | 95805.2449 | 117372.339 | 21567.0941 | 60 |  | 1294025.646 | 1296469.7835 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1296469.7835 | 1414735.196 | -118265.4124 | -8.3595 | OK
5 | 11 kV Baburail Feeder (F-5) | A730R | 11 |  | DHK 9322 | 1 | 51769.6211 | 84762.3796 | 32992.7585 | 60 |  | 1979565.51 | 1983304.4857 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 1983304.4857 | 2103409.2909 | -120104.8052 | -5.71 | OK
6 | 11 kV Goghchar Feeder (F-1) | E330G | 11 |  | DHK 9323 | 1 | 56304.0611 | 76884.4867 | 20580.4256 | 60 |  | 1234825.536 | 1237157.8572 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1237157.8572 | 1317359.8624 | -80202.0052 | -6.0881 | OK
7 | 11 kV Norshinghopur (F-2) | E330N | 11 |  | DHK 9365 | 1 | 40357.6851 | 66325.1503 | 25967.4652 | 60 |  | 1558047.912 | 1560990.7311 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1560990.7311 | 1355613.7656 | 205376.9655 | 15.1501 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 |  | DHK 9367 | 1 | 6609.7103 | 15212.6093 | 8602.899 | 60 |  | 516173.94 | 517148.8821 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 517148.8821 | 0 | 517148.8821 | #DIV/0! | #DIV/0!
11 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 |  | H/A030701125-03 | 1 | 73556.451 | 73783.826 | 227.375 | 1000 |  | 227375 | 227804.4627 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 227804.4627 | 240354.077 | -12549.6143 | -5.2213 | OK
12 | 11 kV Kashipur Feeder (F-7) | E317K | 11 |  | H/A030800169-03 | 1 | 38456.292 | 40041.956 | 1585.664 | 1000 |  | 1585664 | 1588658.98 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1588658.98 | 1710138.4368 | -121479.4568 | -7.1035 | OK
13 | 11 kV Spare Feeder (F-6) |  | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | A730D | 11 |  | H/A030701098-03 | 1 | 80469.846 | 81538.063 | 1068.217 | 1000 |  | 1068217 | 1070234.6333 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 1070234.6333 | 1102912.6399 | -32678.0066 | -2.9629 | OK
15 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 |  | H/A030800205-03 | 1 | 96230.313 | 97166.397 | 936.084 | 1000 |  | 936084 | 937852.0624 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 937852.0624 | 845475.6866 | 92376.3758 | 10.926 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 |  | H/A030701091-03 | 1 | 55276.511 | 56283.66 | 1007.149 | 1000 |  | 1007149 | 1009051.2889 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 1009051.2889 | 1042925.7746 | -33874.4857 | -3.248 | OK
|  |  | 10: Total | 14060795.4423 | 14034287.676 | 14060795.4423 | 0.18888
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | N.Gonj (East) | at 33 KV level |  | 1165656.5251
[6 empty] | Sytalakhya | at 33 KV level |  | 9841599.7983
[6 empty] | N.Gonj (West) | at 33 KV level |  | 3053539.119
[6 empty] | Total = |  |  | 14060795.4423 | 0
MI CEMENT 132/33 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] |  | 132 | P. Cell | 08993599 | 1 | 325.031 | 350.233 | 25.202 | 480000 | 12096960 |  | 12087360
|  |  | 132 | DPDC | 16402670 | 1 | 1850.027 | 1875.206 | 25.179 | 480000 | 12085920
2 | 132/33 kV Transformer (132 kV Side) |  | 132 |  | 06502030 | 1 | 3680.475 | 3731.122 | 50.647 | 240000 |  | 12155280
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 12085920 | 12155280
[7 empty] | 0 | 0 |  | Net Total
[7 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) |  | 33 |  | 14718815 | 1 | 7263.684 | 7363.831 | 100.147 | 120000 | 12017640
4 | 33 kV Outgoing Feeder-1 |  | 33 |  | 11745824 | 1 | 3738.137 | 3776.316 | 38.179 | 120000 |  | 4581480
5 | 33 kV Outgoing Feeder-2 |  | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 7436160
|  |  | 9=8-7: Total Import/Export | 12017640 | 12017640
|  |  | 9=8-7: Net Total | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 12087360
[6 empty] | Total = |  |  | 12087360
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 |  | 33 | DPDC | BD001911 | 1 | 1649.9119 | 1692.0883 | 42.1764 | 180000 | 0 | 7591752 | 7589982.7824
20 | 33 kV Mondolpara-1 Feeder |  | 33 | DPDC | BD001823 | 1 | 1358.4878 | 1391.8606 | 33.3728 | 240000 | 0 | 8009472 | 8007605.435
|  |  | 10: Total | 0 | 15601224 | 15597588.2175
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder |  | 33 |  | 00000188 | 1 | 328323520 | 335898624 | 7575104 | 1 | 7575104
7 | 33 kV Shitalakhya-1 Feeder |  | 33 |  | 00000153 | 1 | 326468608 | 334500032 | 8031424 | 1 | 8031424
|  |  | 7: 0; 8: 0; 10: Total | 15606528 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer |  | 33 |  | 00000116 | 1 | 332932800 | 340581376 | 7648576 | 1 |  | 7648576
8 | 33/11 kV, 28/35 MVA T-1 Transformer |  | 33 |  | 00000194 | 1 | 321667904 | 329620544 | 7952640 | 1 |  | 7952640
|  |  | 10: Total |  | 15601216
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 15597588.2175; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 15597588.2175
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 15597588.2175 | 33 KV TX HV SIDE |  | 15601216
[11 empty] | LOSS UNITS=> |  | -3627.7825
[11 empty] | LOSS % IN => |  | -0.02326%
| TOTAL IMPORT |  | 4: 15597588.2175
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming |  | 11 |  | 00000055 | 1 | 320122560 | 328043776 | 7921216 | 1 | 7921216 |  | 7954239.4683
19 | 11 kV T-2 Incoming |  | 11 |  | 00000017 | 1 | 330414560 | 338026176 | 7611616 | 1 | 7611616 |  | 7643348.7491
|  |  | 7: 0; 8: 0; 10: Total | 15532832 |  | 15597588.2175
| MONDOLPARA 11 KV SIDE |  | 7: 0; 8: 0
9 | 11 kV River View | B793U | 11 |  | 00000061 | 1 | 8013364 | 8849520 | 836156 | 1 |  | 836156 | 838291.0284 | N.Gonj (East) |  |  |  | 11 kV River View | 838291.0284 | 794103.9859 | 44187.0425 | 5.5644 | OK
10 | 11 kV Railgate B.B. Road | B793F | 11 |  | 00000191 | 1 | 24086822 | 24783300 | 696478 | 1 |  | 696478 | 698256.3766 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 698256.3766 | 634632.2838 | 63624.0928 | 10.0253 | OK
11 | 11 kV DIT | A722D | 11 |  | 00000174 | 1 | 142723248 | 145783200 | 3059952 | 1 |  | 3059952 | 3067765.2362 | N.Gonj (West) |  |  |  | 11 kV DIT | 3067765.2362 | 3157724.5261 | -89959.2899 | -2.8489 | OK
12 | 11 kV Dalpatti | B7227 | 11 |  | 00000182 | 1 | 5095427 | 5882705 | 787278 | 1 |  | 787278 | 789288.224 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 789288.224 | 719006.8368 | 70281.3872 | 9.7748 | OK
13 | 11 kV South Chasara | A793S | 11 |  | 00000043 | 1 | 99667000 | 102195272 | 2528272 | 1 |  | 2528272 | 2534727.6524 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2534727.6524 | 2702179.486 | -167451.8337 | -6.1969 | OK
14 | 11 kV Spare |  | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | B7225 | 11 |  | 00000019 | 1 | 190279 | 213639 | 23360 | 1 |  | 23360 | 23419.6471 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 23419.6471 | 28768.3897 | -5348.7426 | -18.5924 | OK
17 | 11 kV Spare |  | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | B7229 | 11 |  | 00000173 | 1 | 7416422 | 8565979 | 1149557 | 1 |  | 1149557 | 1152492.2619 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1152492.2619 | 1058401.5124 | 94090.7495 | 8.8899 | OK
20 | 11 kV Nitaigonj | B722G | 11 |  | 00000189 | 1 | 59588816 | 60384252 | 795436 | 1 |  | 795436 | 797467.0545 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 797467.0545 | 710089.0378 | 87378.0168 | 12.3052 | OK
21 | 11 kV Shahid Nagar | E323T | 11 |  | 00000020 | 1 | 59699656 | 60968412 | 1268756 | 1 |  | 1268756 | 1271995.6228 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1271995.6228 | 1341667.6936 | -69672.0708 | -5.1929 | OK
22 | 11 kV Bangla Bazar | A793Z | 11 |  | 00000139 | 1 | 72583224 | 74210456 | 1627232 | 1 |  | 1627232 | 1631386.9501 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1631386.9501 | 1686165.1422 | -54778.1921 | -3.2487 | OK
23 | 11 kV Vogoban Gonj | B7228 | 11 |  | 00000181 | 1 | 3295232 | 3768630 | 473398 | 1 |  | 473398 | 474606.7675 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 474606.7675 | 456596.7336 | 18010.0339 | 3.9444 | OK
24 | 11 kV Tanbazar | B722I | 11 |  | 00000138 | 1 | 50648356 | 51622392 | 974036 | 1 |  | 974036 | 976523.0891 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 976523.0891 | 1000661.8275 | -24138.7383 | -2.4123 | OK
25 | 11 kV SS Road | A793O | 11 |  | 00000175 | 1 | 68058352 | 69392152 | 1333800 | 1 |  | 1333800 | 1337205.7052 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1337205.7052 | 1396187.0064 | -58981.3012 | -4.2245 | OK
26 | 11 kV Spare |  | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 |  | 0.415 |  |  | 1 | 2599.39 | 2640.91 | 41.52 | 100 |  | 4152 | 4162.6017 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 4162.6017 | 6314.1794 | -2151.5777 | -34.0753 | OK
28 | 33/0.415 kV Auxiliary-2 |  | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 15597588.2175 | 15557863 | 15597588.2175 | 0.25534
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 1271995.6228
[6 empty] | N.Gonj (East) | at 33 KV level |  | 5750344.4491
[6 empty] | N.Gonj (West) | at 33 KV level |  | 8575248.1456
[6 empty] | Total = |  |  | 15597588.2175 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | DPDC | H/A030701082-03 | 1 | 40179.341 | 52115.953 | 11936.612 | 1000 | 0 | 11936612 | 11933830.2359
0 | 33 KV Panchabati BSCIC Feeder (F3) |  | 33 | P. Cell | 08993594 | 1 | 9847.982 | 9914.297 | 66.315 | 180000 | 0 | 11936700 | 11933918.2153
| MATUAIL 33 KV SIDE |  | 10: Total |  | 11936612 | 11933830.2359
12 | 33 KV Panchabati Bscic (Feeder-2) |  | 33 | DPDC | H/A060300263-03 | 1 | 75609.32 | 82417.915 | 6808.595 | 1000 | 0 | 6808595 | 6831251.1517
0 | 0 |  | 33 | P. Cell | 08993580 | 1.5 | 1388.271 | 1413.422 | 25.151 | 180000 | 0 | 6790770 | 6813366.8376
|  |  | 10: Total | 0 | 6808595 | 6831251.1517
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) |  | 10: Total |  | 18745207 | 18765081.3875
3 | 33 kV Matuail Feeder |  | 33 | Digital | ABB03910 | 1 | 84171.54 | 85490.813 | 1319.2731 | 4000 | 5277092.36
6 | 33 kV Shitalakhya Feeder |  | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  |  | 33 | New | DHKA2199 | 1 | 4254.9898 | 4318.7162 | 63.7264 | 180000 | 11470752
|  |  | 7: 0; 8: 0; 10: Total | 16747844.36 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  | 7: 0; 8: 0
5 | 33/11 kV, 20/28 MVA Transformer-3 |  | 33 | Old | HA021100524-02 | 1 | 0 | 0 | 0 | 1000 |  | 0
|  |  | 33 | New | DHKA2200 | 1 | 4345.7595 | 4379.5301 | 33.7706 | 180000 |  | 6078708
7 | 33/11 kV, 10/14 MVA Transformer-2 |  | 33 | Old | HA030800199-03 | 1 | 49990.767 | 55897.14 | 5906.373 | 1000 |  | 5906373
|  |  | 33 | New | DHKA2195 | 1 | 4585.643 | 4648.3212 | 62.6782 | 90000 |  | 5641038
8 | 33/11 kV, 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03909 | 1 | 435834.3414 | 441660.8969 | 5826.5555 | 1000 |  | 5826555.51
|  |  | 10: Total |  | 17811636.51
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 4: 11933830.2359; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 18765081.3875
| MATUAIL 33 KV SIDE |  | 4: 6831251.1517; 6: 33 KV NET IMPORT; 9=8-7: 18765081.3875 | 33 KV TX HV SIDE |  | 17811636.51
[11 empty] | LOSS UNITS=> |  | 953444.8775
[11 empty] | LOSS % IN => |  | 5.081%
| TOTAL IMPORT |  | 4: 18765081.3875
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | 51426632 | 1 | 3845779 | 3910814 | 65035 | 90 | 5853150 |  | 5962240.0557
16 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | DHKA2192 | 1 | 3964.1745 | 4029.6985 | 65.524 | 90000 | 5897160 |  | 6007070.3069
22 | 33/11 kV Transformer, T-3 Incoming |  | 11 |  | 51426630 | 1 | 4143902 | 4218029 | 74127 | 90 | 6671430 |  | 6795771.025
|  |  | 7: 0; 8: 0; 10: Total | 18421740 |  | 18765081.3875
| NARAYANGONJ BSCIC 11 KV SIDE |  | 7: 0; 8: 0
10 | 11 kV Masdair Feeder (F-8) | A727M | 11 |  | XA575914 | 1 | 219192.9 | 222435 | 3242.1 | 1000 |  | 3242100 | 3291294.4584 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 3291294.4584 | 3221867.4125 | 69427.0459 | 2.1549 | OK
11 | 11 kV Narayangonj (F-7) | A727N | 11 |  | XA575915 | 1 | 168351.2 | 169847.6 | 1496.4 | 1000 |  | 1496400 | 1519105.835 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1519105.835 | 1446695.3457 | 72410.4892 | 5.0052 | OK
12 | 11 kV Nearest Feeder (F-6) | A727B | 11 |  | XA575927 | 1 | 107456.1 | 108569.7 | 1113.6 | 1000 |  | 1113600 | 1130497.3656 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 1130497.3656 | 1036613.3317 | 93884.0339 | 9.0568 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 |  | XA575916 | 1 | 118651.3 | 120037.9 | 1386.6 | 1000 |  | 1386600 | 1407639.7693 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1407639.7693 | 1294481.9465 | 113157.8227 | 8.7416 | OK
14 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 |  | XA575912 | 1 | 56646.1 | 57538.4 | 892.3 | 1000 |  | 892300 | 905839.439 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 905839.439 | 991802.3648 | -85962.9257 | -8.6673 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 |  | DHK66615 | 1 | 228.1138 | 246.1468 | 18.033 | 60000 |  | 1081978.68 | 1098396.235 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 1098396.235 | 953150.2952 | 145245.9398 | 15.2385 | OK
17 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 |  | XA575920 | 1 | 233276 | 234533.8 | 1257.8 | 1000 |  | 1257800 | 1276885.4045 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 1276885.4045 | 676995.0442 | 599890.3602 | 88.6107 | FAULT
18 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 |  | XA575929 | 1 | 22437.4 | 23731.9 | 1294.5 | 1000 |  | 1294500 | 1314142.277 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1314142.277 | 1121815.8354 | 192326.4417 | 17.1442 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 |  | HA021100913-02 | 1 | 42019.89 | 44435.628 | 2415.738 | 1000 |  | 2415738 | 2452393.5389 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 2452393.5389 | 1730245.9891 | 722147.5498 | 41.7367 | FAULT
20 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 |  | HA021100682-02 | 1 | 64204.485 | 66687.61 | 2483.125 | 1000 |  | 2483125 | 2520803.045 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2520803.045 | 2363695.2567 | 157107.7882 | 6.6467 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 |  | HA021100455-02 | 1 | 57860.6 | 59670.325 | 1809.725 | 1000 |  | 1809725 | 1837185.1157 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1837185.1157 | 1324011.9627 | 513173.1531 | 38.759 | OK
23 | 11/0.415 KV Transformer,AT-1 |  | 0.415 | Analog | 2001123043161 | 1 | 3930.2 | 3995.5 | 65.3 | 160 |  | 10448 | 10606.5342 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 10606.5342 | 9471.9695 | 1134.5647 | 11.9781 | OK
24 | 11/0.415 KV Transformer,AT-2 |  | 0.415 | Analog | 2001123043118 | 1 | 4106.3 | 4108.1 | 1.8 | 160 |  | 288 | 292.37 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 292.37 | 213.7771 | 78.5929 | 36.764 | OK
|  |  | 10: Grand Total | 18765081.3875 | 18484602.68 | 18765081.3875 | 1.5174
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 1276885.4045
[6 empty] | N.Gonj (West) | at 33 KV level |  | 17488195.9831
[6 empty] | Total = |  |  | 18765081.3875 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) |  | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  |  | IMPORT | 42627811 | 1 | 283.871 | 296.146 | 12.275 | 960000 | 0 | 11784000
| Madonganj to Charsyedpur-2 |  |  |  | 42627824 | 1 | 202.657 | 220.999 | 18.342 | 960000 | 0 | 17608320
|  |  | 9=8-7: Total Import/Export | 0 | 29392320 | 0
|  |  | 10: Net Total | 29392320
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 |  | 132 |  | 041808902821 | 1 | 234.57 | 244.39 | 9.82 | 1200000 | 11784000
|  |  | 132 |  | 041808904222 | 3 | 77.62 | 80.89 | 3.27 | 1200000 | 11772000
| 132 kV Madanganj Circuit-2 |  | 132 |  | 041808902865 | 1 | 162.12 | 176.79 | 14.67 | 1200000 | 17604000
|  |  | 132 |  | 041808904240 | 1 | 162.18 | 176.85 | 14.67 | 1200000 | 17604000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 29388000 | 0 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 29388000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 132 kV Shah Cement |  | 132 | EXPORT | 042003953369 | 1 | 8.92 | 21.5 | 12.58 | 1200000 |  | 15096000 |  | Sytalakhya | Main Meter
| 133 kV Shah Cement |  | 132 |  | 042003953379 | 1 | 8.93 | 21.52 | 12.59 | 1200000 |  | 15108000 |  |  | Check Meter
|  |  | 7: 0; 8: 0; 10: Total |  | 15096000
| CHAR SYEDPUR 132 KV SIDE |  | 7: 0; 8: 0
4 | 132/33 kV, 80/120 MVA GT-1 |  | 132 | EXPORT | 041808902864 | 1 | 184.86 | 194.68 | 9.82 | 1200000 | 11784000 | 11784000
|  |  | 132 |  | 041808904224 | 1 | 184.74 | 194.55 | 9.81 | 1200000 | 11772000 | 11772000
7 | 132/33 kV, 80/120 MVA GT-2 |  | 132 |  | 041808902848 | 1 | 202.89 | 204.95 | 2.06 | 1200000 | 2472000 | 2472000
|  |  | 132 |  | 041808904244 | 1 | 202.98 | 205.05 | 2.07 | 1200000 | 2484000 | 2484000
|  |  | 10: Total |  | 14256000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 4: 29392320; 6: Sytalakhya NOCS; 9=8-7: 15096000 | 132 KV NET IMPORT |  | 14256000
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 14256000 | 132/33 KV LV SIDE |  | 14148000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 108000
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.7576%
| 132 KV TOTAL IMPORT |  | 4: 29392320
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) |  | 33 | Main | 041808902859 | 1 | 306.1 | 322.37 | 16.27 | 720000 | 11714400 |  | 11803822.9008
|  |  | 33 | Backup | 041808904285 | 1 | 306.1 | 322.37 | 16.27 | 720000 | 11714400 |  | 11803822.9008
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) |  | 33 | Main | 041808902812 | 1 | 336.55 | 339.93 | 3.38 | 720000 | 2433600 |  | 2452177.0992
|  |  | 33 | Backup | 041808904276 | 1 | 336.57 | 339.96 | 3.39 | 720000 | 2440800 |  | 2459432.0611
|  |  | 7: 0; 8: 0; 10: Total | 14148000 |  | 14256000
| CHAR SYEDPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) |  | 33 | Main | 041808902875 | 1 | 231.38 | 241.33 | 9.95 | 240000 |  | 2388000 | 2390867.2743 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2390867.2743 | 2344006.2746 | 46860.9997 | 1.9992 | OK
|  |  | 33 | Backup | 041808904241 | 1 | 231.31 | 241.25 | 9.94 | 240000 |  | 2385600 | 2388464.3926 |  |  |  |  | 0 | 2388464.3926 | 2344006.2746 | 44458.118 | 1.8967 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) |  | 33 | Main | 041808902844 | 3 | 66.18 | 69.51 | 3.33 | 240000 |  | 2397600 | 2400478.801 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 2400478.801 | 2245336.606 | 155142.1951 | 6.9095 | OK
|  |  | 33 | Backup | 041808904259 | 3 | 66.18 | 69.51 | 3.33 | 240000 |  | 2397600 | 2400478.801 |  |  |  |  | 0 | 2400478.801 | 2245336.606 | 155142.1951 | 6.9095 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 4785600 | 4791346.0753 |  |  |  |  | 33 KV Feeders | 4791346.0753 | 4589342.8806 | 202003.1948 | 4.4016 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) |  | 33 | Main | 041808902866 | 1 | 343.51 | 361.28 | 17.77 | 360000 |  | 6397200 | 6404881.1253 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 6404881.1253 | 5779395.3475 | 625485.7778 | 10.8227 | OK
|  |  | 33 | Backup | 041808904221 | 1 | 343.67 | 361.46 | 17.79 | 360000 |  | 6404400 | 6412089.7703 |  |  |  |  | 0 | 6412089.7703 | 5783005.2134 | 629084.5569 | 10.8782 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) |  | 33 | Main | 041808902876 | 1 | 114.83 | 122.98 | 8.15 | 360000 |  | 2934000 | 2937522.8571 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2937522.8571 | 2682130.383 | 255392.4741 | 9.522 | OK
|  |  | 33 | Backup | 041808904237 | 1 | 114.83 | 122.98 | 8.15 | 360000 |  | 2934000 | 2937522.8571 |  |  |  |  | 0 | 2937522.8571 | 2682130.383 | 255392.4741 | 9.522 | OK
11 | 33 kV Outgoing Feeder-3 (=H3) |  | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) |  | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) |  | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 |  | 0 | 0 | Sytalakhya | Grid Has No Reading |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904232 | 1 | 43.8 | 43.8 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Outgoing Feeder-6 (=H12) |  | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) |  | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) |  | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 0 | 2277825.3993 | -2277825.3993 | -100 | CHECK
|  |  | 33 | Backup | 041808904242 | 1 | 499.7 | 499.7 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 2274215.5334 | -2274215.5334 | -100 | CHECK
| 33/0.415 kV Transformer AT-1 |  |  |  |  | 1 | 1814.62 | 1916.44 | 101.82 | 1 |  | 101.82 | 101.9423 | [5 empty] | 101.9423 | 105.9897
|  |  | 10: Total |  | 9331301.82 | 9342505.9247 |  |  |  |  | 0 | 9342505.9247 | 10739457.1194 | -1396951.1948 | -13.0077 | OK
|  |  | 9=8-7: Grand Total | 14133852 | 14116901.82 | 14133852 | 0.12007
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming |  | 11 |  | 041808902756 | 1 | 221.1 | 230.6 | 9.5 | 250000 | 2375000 |  | 1804771.7644
20 | 33/11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 041808902778 | 1.72 | 137.34 | 146.48 | 9.14 | 250000 | 3930200 |  | 2986574.3109
|  |  | 7: 0; 8: 0; 10: Total | 6305200 |  | 4791346.0753
| CHAR SYEDPUR 11 kV SIDE |  | 7: 0; 8: 0
4 | 11 kV Outgoing Feeder-1 (=F1) |  | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 |  | 041808902749 | 1 | 446.8 | 468.54 | 21.74 | 60000 |  | 1304400 | 1302048.296 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 1302048.296 | 1299547.0336 | 2501.2624 | 0.19247 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) |  | 11 |  | 041808902759 | 1 | 474.87 | 492.75 | 17.88 | 60000 |  | 1072800 | 1070865.8478 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1070865.8478 | 1018127.8829 | 52737.9649 | 5.1799 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) |  | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) |  | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) |  | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) |  | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 |  | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 |  | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 |  | 041808902786 | 1 | 330.24 | 356.76 | 26.52 | 60000 |  | 1591200 | 1588331.224 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1588331.224 | 1607255.8715 | -18924.6475 | -1.1775 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 |  | 041808902789 | 1 | 201.91 | 215.77 | 13.86 | 60000 |  | 831600 | 830100.7076 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 830100.7076 | 664412.0926 | 165688.615 | 24.9376 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) |  | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) |  | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) |  | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) |  | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) |  | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 |  | 0.415 |  | 041811907976 | 1 | 1814.62 | 1916.44 | 101.82 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 4791346.0753 | 4800000 | 4791346.0753 | -0.18029
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 14133750.0577
[6 empty] | Total = |  |  | 14133750.0577 | 9342403.9824
33 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia |  | 33 | Export | SIEM0505 | 1 | 38552 | 38986 | 434 | 6000 | 0 | 2604000 | 2606832.7173
FROM Kazla 33 KV SIDE
| 33 kV Amulia Feeder | 0 | 33 | Main | 41812909523 | 1 | 4.89 | 17.72 | 12.83 | 360000 | 0 | 4618800 | 4612723.7056
|  |  | 10: Total |  | 7222800 | 7219556.4229
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving |  | 33 |  |  | 1 | 1364.96 | 1379.37 | 14.41 | 180000 | 2593800
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total | 2593800 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| AMULIA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV Transformer, T-1 |  | 33 |  | DHKA2194 | 1 | 384.0364 | 398.8151 | 14.7787 | 240000 |  | 3546888
4 | 33/11 kV Transformer, T-2 |  | 33 |  | DHKA2198 | 1 | 561.101 | 576.0084 | 14.9074 | 240000 |  | 3577776
|  |  | 10: Total |  | 7124664 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 4: 7219556.4229; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7219556.4229
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 7219556.4229 | 33 KV TX HV SIDE |  | 7124664
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 94892.4229
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 1.314%
| TOTAL IMPORT |  | 4: 7219556.4229
11 KV SIDE of___AMULIA 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming |  | 11 |  | HA021100461-02 | 1 | 24256837 | 27840165 | 3583328 | 1 | 3583328 |  | 3627136.3623
11 | 33/11 kV Transformer, T-1 Incoming |  | 11 |  | HA021100478-02 | 1 | 92710119 | 96259150 | 3549031 | 1 | 3549031 |  | 3592420.0606
|  |  | 7: 0; 8: 0; 10: Total | 7132359 |  | 7219556.4229
| AMULIA 11 KV SIDE |  | 7: 0; 8: 0
5 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 71472942 | 72083645 | 610703 | 1 |  | 610703 | 618877.1744 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 618877.1744 | 747742.2401 | -128865.0656 | -17.2339 | OK
6 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 16734017 | 18045139 | 1311122 | 1 |  | 1311122 | 1328671.185 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1328671.185 | 1368274.6157 | -39603.4307 | -2.8944 | OK
8 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 1820347 | 2394570 | 574223 | 1 |  | 574223 | 581908.8947 | Demra |  |  |  | 11 kV Paity Feeder | 581908.8947 | 369688.6181 | 212220.2766 | 57.4051 | FAULT
9 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 68779188 | 71254185 | 2474997 | 1 |  | 2474997 | 2508124.4895 | Demra |  |  |  | 11 kV Bamuil Feeder | 2508124.4895 | 2591251.8147 | -83127.3252 | -3.208 | OK
12 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 15389909 | 16052331 | 662422 | 1 |  | 662422 | 671288.426 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 671288.426 | 654683.7051 | 16604.7209 | 2.5363 | OK
13 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra |  | 1 | 51992736 | 52158655 | 165919 | 1 |  | 165919 | 168139.8027 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 168139.8027 | 155971.1495 | 12168.6532 | 7.8019 | OK
14 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 13720036 | 15044850 | 1324814 | 1 |  | 1324814 | 1342546.4505 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1342546.4505 | 1461872.9578 | -119326.5073 | -8.1626 | OK
15 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 |  | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total | 7219556.4229 | 7124200 | 7219556.4229 | 1.3208
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Mugdapara | at 33 KV level |  | 1290165.6005
[6 empty] | Demra | at 33 KV level |  | 5929390.8224
[6 empty] | Total = |  |  | 7219556.4229 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MOGBAZAR T&T 11 KV SIDE | [9 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder |  | 33 |  | 8993 841 | 1 | 39462.866 | 39516.99 | 54.124 | 36000 | 0 | 1948464 | 1948464 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 1948464 | 817416 | 1131048 | 138.3687 | FAULT
13 | 33 kV Mondol Para (Premire cement) Feeder |  | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Grand Total |  | 1948464 | 1948464 | 0
[6 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[6 empty] | Sytalakhya | at 33 KV level |  | 1948464
[6 empty] | Total = |  |  | 1948464 | 0
Note on H481: User: Meter was faulty and New meter is installed properly in 12.07.23
Note on I481: User: Meter was faulty and New meter is installed properly in 12.07.23

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 |  | 132 | IMPORT | 50147584 | 1 | 3273.275 | 3318.886 | 45.611 | 1920000 | 0 | 87573120
| Maniknagar-2 |  | 132 |  | 50147585 | 1 | 3265.408 | 3311.084 | 45.676 | 1920000 | 0 | 87697920
|  |  | 9=8-7: Total Import/Export | 0 | 175271040
|  |  | 10: Net Total | 175271040
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 175271040
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 |  | 132 | EXPORT | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | From Downstream | 19540800 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 |  | 132 |  | 06604334 | 1 | 8968.84 | 9009.55 | 40.71 | 480000 |  | 19540800
| 132kV Motijheel Circuit-1 |  | 132 |  | 06604332 | 1 | 1847.38 | 1855.74 | 8.36 | 1440000 |  | 12038400
| 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1 | 1641.74 | 1651.74 | 10 | 1440000 |  | 14400000
| 132 kV Kazla Circuit-1 |  | 132 |  | ABB03905 | 1 | 814636.9 | 844535 | 29898.1 | 1000 |  | 29898100
| 132 kV Kazla Circuit-2 |  | 132 |  | ABB03904 | 1 | 611209.5 | 640950 | 29740.5 | 1000 |  | 29740500
|  |  | 7: 0; 8: 0; 10: Total |  | 125158600
| MANIKNAGAR 132 KV SIDE |  | 7: 0; 8: 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 24284000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) |  | 132 | Export | ABB03903 | 1 | 359033.9 | 383445 | 24411.1 | 1000 |  | 24411100 |  |  | 48695100
|  |  | 10: Total |  | 48695100
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 4: 175271040; 6: EXPORT TO OTHER S/S; 9=8-7: 125158600 | 132 KV NET IMPORT |  | 50112440
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 50112440 | 33 KV NET IMPORT |  | 49085000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1027440
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.05%
| 132 KV TOTAL IMPORT |  | 4: 175271040
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) |  | 33 | Digital | ABB03907 | 1 | 98028 | 122312 | 24284 | 1000 | 24284000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) |  | 33 | Digital | ABB03906 | 1 | 266188 | 290989 | 24801 | 1000 | 24801000
|  |  | 7: 0; 8: 0; 10: Total | 49085000 |  | 0
| Maniknagar 33 kV SIDE |  | 7: 0; 8: 0 |  |  |  |  | 4126429.8988
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 |  | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 10886789.1465 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 11 |  | DHK00121 | 2 | 10074.8 | 10495.1 | 420.3 | 4444 | Estimated | 3961409.94 | 3968474.087 |  |  |  |  | 0 | 3968474.087 | 3973995.7333 | -5521.6463 | -0.13894 | OK | 4161360.0577
7 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Digital | ABB03913 | 1 | 389465 | 392918 | 3453 | 2000 |  | 6906000 | 6918315.0595 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 6918315.0595 | 7521821.8916 | -603506.8321 | -8.0234 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 10867409.94 | 10886789.1465 |  |  |  |  | 33 KV Feeders | 10886789.1465 | 11495817.6249 | -609028.4783 | -5.2978 | OK
2 |  |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 12817716.3851 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder |  | 33 |  | DHK86054 | 1 | 2492.56 | 2516.03 | 23.47 | 270000 |  | 6336900 | 6348200.2173 |  |  |  |  | 33kV Motijheel-1 Feeder | 6348200.2173 | 6552050.5896 | -203850.3722 | -3.1112 | OK
3 | 33kV Mugdapara Hospital-1 Feeder |  | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 9073344 | 9089523.9553 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 9089523.9553 | 9371150.7854 | -281626.8301 | -3.0053 | OK
|  |  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 18348004.6649 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder |  | 33 | Digital | ABB03918 | 1 | 306967 | 311588 | 4621 | 2000 |  | 9242000 | 9258480.7096 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 9258480.7096 | 9405788.4843 | -147307.7748 | -1.5661 | OK
9 | 33kV Khilgaon Feeder |  | 33 | Digital | ABB03915 | 1 | 275583 | 278536 | 2953 | 2000 |  | 5906000 | 5916531.8189 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 5916531.8189 | 6516638.438 | -600106.619 | -9.2088 | OK
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 286975 | 290204 | 3229 | 2000 |  | 6458000 | 6469516.1677 |  | 5916531.8189 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 6469516.1677 | 6757400.9418 | -287884.7741 | -4.2603 | OK
12 | 33kV Water Treatment Plant |  | 33 | Digital | 80379618 | 1 | 21552 | 21815 | 263 | 2000 |  | 526000 | 526937.9846 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 526937.9846 | 686173.136 | -159235.1515 | -23.2063 | OK
|  |  | 10: Total |  | 37542244 | 37609190.8535 |  |  |  |  | 0 | 37609190.8535 | 39289202.3751 | -1680011.5217 | -4.276 | OK
|  |  | 9=8-7: Grand Total | 48495980 | 48409653.94 | 48495980 | 0.17832
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 526937.9846
[6 empty] | Total = |  |  | 526937.9846 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 |  | 11 | Import | 6604357 | 1 | 5518.75 | 5561.26 | 42.51 | 160000 | 6801600 |  | 7027236.7935
9 | 11kV 10/14 MVA Transformer T-1 |  | 11 | Import | DHK00121 | 2 | 10074.8 | 10495.1 | 420.3 | 4444 | 3735626.4 |  | 3859552.3531
|  |  | 7: 0; 8: 0; 10: Total | 10537226.4 |  | 10886789.1465
| MANIKNAGAR 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nearest Feeder | B2110N | 11 |  | HA021101060-02 | 1 | 78705271 | 80316933 | 1611662 | 1 |  | 1611662 | 1615577.819 | Maniknagar |  | 205 |  | 11 kV Nearest Feeder | 1615577.819 | 1668539.8072 | -52961.9883 | -3.1742 | OK
2 | 11kV Spare |  | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  | 130 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | B2110C | 11 |  | HA021100937-02 | 1 | 79002373 | 79831670 | 829297 | 1 |  | 829297 | 831311.9243 | Maniknagar |  | 75 |  | 11 kV City Palli Feeder | 831311.9243 | 885994.3441 | -54682.4198 | -6.1719 | OK
4 | 11 kV R K Mission Road Feeder | B2110R | 11 |  | HA021101035-02 | 1 | 17311553 | 18813697 | 1502144 | 1 |  | 1502144 | 1505793.7255 | Maniknagar |  | 25 |  | 11 kV R K Mission Road Feeder | 1505793.7255 | 1587170.4652 | -81376.7397 | -5.1272 | OK
5 | 11 kV Janapath Feeder | B2110J | 11 |  | HA021100864-02 | 1 | 31862091 | 33876168 | 2014077 | 1 |  | 2014077 | 2018970.5577 | Maniknagar |  | 155 |  | 11 kV Janapath Feeder | 2018970.5577 | 2145298.3795 | -126327.8219 | -5.8886 | OK
6 | 11 kV Dhalpur Feeder | B2110D | 11 |  | HA021100851-02 | 1 | 87890591 | 88732684 | 842093 | 1 |  | 842093 | 844139.0145 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 844139.0145 | 879803.8192 | -35664.8047 | -4.0537 | OK
7 | 11kV WTP | B2110O | 11 |  | X0599387 | 1 | 2253.4 | 2253.4 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11kV WTP | 0 | 285986.2262 | -285986.2262 | -100 | CHECK
10 | 11kV Kamalapur Water pumping | B2110F | 11 |  | HA021100474-02 | 1 | 7640348 | 7657094 | 16746 | 1 | Estimated | 97306.272 | 97542.6949 | Maniknagar | 8 |  |  | 11kV Kamalapur Water pumping | 97542.6949 | 82536.7668 | 15005.928 | 18.1809 | OK
11 | 11 kV Wasa Road Feeder | B2110A | 11 |  | HA021001011-02 | 1 | 25404116 | 26301986 | 897870 | 1 | Estimated | 2067758.28 | 2072782.2659 | Maniknagar | 170 |  |  | 11 kV Wasa Road Feeder | 2072782.2659 | 2063419.1707 | 9363.0952 | 0.45377 | OK
12 | 11kV Sutikhalpar Feeder | B2110K | 11 |  | HA021101047-02 | 1 | 79911027 | 80885566 | 974539 | 1 | Estimated | 1885309.02 | 1889889.713 | Maniknagar | 155 |  |  | 11kV Sutikhalpar Feeder | 1889889.713 | 1886554.6703 | 3335.0427 | 0.17678 | OK
13 | 11kV Spare |  | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare |  | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare |  | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare |  | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 |  | 0.415 |  | AH14044078 | 1 | 414749.8 | 420573.6 | 5823.8 | 1 |  | 5823.8 | 5837.95 | Maniknagar |  |  |  | Axuxilary -1 | 5837.95 | 5955.9261 | -117.9762 | -1.9808 | OK
| Axuxilary -2 |  | 0.415 |  | AH14044072 | 1 | 383501.3 | 388432.8 | 4931.5 | 1 |  | 4931.5 | 4943.482 | Maniknagar |  |  |  | Axuxilary -2 | 4943.482 | 4558.0495 | 385.4325 | 8.4561 | OK
13 | AT-1 |  | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 10886789.1465 | 10860401.872 | 10886789.1465 | 0.24297
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 10886789.1465
[6 empty] | Total = |  |  | 10886789.1465 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder |  | 33 | 0 | DHK86054 | 1 | 2492.56 | 2516.03 | 23.47 | 270000 | 0 | 6336900 | 6348200.2173
11 | 33kV Motijheel-2 Feeder |  | 33 | Digital | ABB03914 | 1 | 286975 | 290204 | 3229 | 2000 | 0 | 6458000 | 6469516.1677
|  |  | 10: Total | 0 | 12794900 | 12817716.3851
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 |  | 33 | Import | DHK86054 | 1 | 2492.56 | 2516.03 | 23.47 | 270000 | 6336900
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) |  | 33 | Import | DHK68120 | 1 | 2169.61 | 2193.32 | 23.71 | 270000 | 6401700 |  |  |  | From Upstream
|  |  | 7: 0; 8: 0; 10: Total | 12738600 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| 33kV Biddyut Bhaban Circuit |  | 33 | Export |  | 1 | 496351 | 503691 | 7340 | 600 |  | 4404000
|  |  | 7: 0; 8: 0; 10: Total |  | 4404000
[7 empty] | 0 | 0
| Motijheel 33 KV SIDE |  | 7: 0; 8: 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK86053 | 1 | 3013.67 | 3039.65 | 25.98 | 180000 |  | 4676400
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) |  | 33 | Export | DHK86055 | 1 | 2354.3 | 2374.62 | 20.32 | 180000 |  | 3657600
|  |  | 10: Total |  | 8334000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 4: 12738600; 6: EXPORT TO OTHER S/S; 9=8-7: 4404000 | 33 KV NET IMPORT |  | 8334600
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 8334600 | 33 KV TX HV SIDE |  | 8334000
[11 empty] | LOSS UNITS=> |  | 600
[11 empty] | LOSS % IN => |  | 0.007199%
| TOTAL IMPORT |  | 4: 12738600
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 |  | 11 | Import | DHK86059 | 1 | 3407.95 | 3437.35 | 29.4 | 160000 | 4704000 |  | 4681643.867 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 |  | 11 | Import | DHK86057 | 1 | 2640.38 | 2663.32 | 22.94 | 160000 | 3670400 |  | 3652956.133
|  |  | 7: 0; 8: 0; 10: Total | 8374400 |  | 8334600
| MOTIJHEEL 11 KV SIDE |  | 7: 0; 8: 0
6 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 |  | DHK86058 | 1 | 1731.8 | 1749.51 | 17.71 | 60000 |  | 1062600 | 1078290.2684 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 1078290.2684 | 1069121.0153 | 9169.253 | 0.85764 | OK
7 | 11kV Station Road Feeder | A175H | 11 |  | DHK86075 | 1 | 2379.78 | 2381.38 | 1.6 | 60000 |  | 96000 | 97417.5285 | Motijheel |  |  |  | 11kV Station Road Feeder | 97417.5285 | 97902.6548 | -485.1263 | -0.49552 | OK
8 | 11kV Box Culvert Road Feeder | A175F | 11 |  | DHK86071 | 1 | 3219.65 | 3251.61 | 31.96 | 60000 |  | 1917600 | 1945915.1314 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1945915.1314 | 1920213.4191 | 25701.7123 | 1.3385 | OK
9 | 11kV Mohamedan Club Feeder | A174V | 11 |  | DHK86062 | 1 | 1707.66 | 1722.37 | 14.71 | 60000 |  | 882600 | 895632.4025 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 895632.4025 | 840281.0677 | 55351.3348 | 6.5872 | OK
10 | 11kV Amina Ahmed Co. |  | 11 |  | DHK95754 | 1 | 115650 | 119456 | 3806 | 60 |  | 228360 | 231731.9459 | Motijheel |  | 267 |  | 11kV Amina Ahmed Co. | 231731.9459 | 212983.3214 | 18748.6245 | 8.8029 | OK
11 | 11kV Bangabhaban -1 |  | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  | 16 |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | A175SB | 11 |  | DHK95753 | 1 | 76280 | 84919 | 8639 | 60 |  | 518340 | 525993.7678 | Motijheel |  | 251 |  | 11kV Sonali Bank | 525993.7678 | 476719.8595 | 49273.9084 | 10.336 | OK
15 | 11kV NCC Bank Feeder | A133S | 11 |  | DHK68123 | 1 | 327.89 | 331.8 | 3.91 | 60000 |  | 234600 | 238064.0852 | Motijheel |  | 83.6667 |  | 11kV NCC Bank Feeder | 238064.0852 | 224635.5392 | 13428.546 | 5.9779 | OK
16 | 11kV IFIC BANK Feeder |  | 11 |  | DHK68116 | 1 | 412.05 | 419.59 | 7.54 | 60000 |  | 452400 | 459080.103 | Ramna |  | 99.6667 |  | 11kV IFIC BANK Feeder | 459080.103 | 425846.5168 | 33233.5862 | 7.8041 | OK
17 | 11kV Arambagh Feeder | A174X | 11 |  | DHK68117 | 1 | 3414.8 | 3437.26 | 22.46 | 60000 |  | 1347600 | 1367498.5561 | Motijheel |  |  |  | 11kV Arambagh Feeder | 1367498.5561 | 1397665.5071 | -30166.9511 | -2.1584 | OK
18 | 11kV Nikotborti Feeder | A175K | 11 |  | DHK68114 | 1 | 1435.2 | 1439.72 | 4.52 | 60000 |  | 271200 | 275204.518 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 275204.518 | 264277.1049 | 10927.413 | 4.1348 | OK
19 | 11kV Agrani Bank Feeder | A174O | 11 |  | DHK95756 | 1 | 374973 | 378789 | 3816 | 60 |  | 228960 | 232340.8054 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 232340.8054 | 213403.7622 | 18937.0432 | 8.8738 | OK
20 | 11kV Bangladesh Bank-2 | A133D | 11 |  | DHK95755 | 1 | 529 | 546 | 17 | 60000 | Estimated | 973062.72 | 987430.8879 | Motijheel | 80 |  |  | 11kV Bangladesh Bank-2 | 987430.8879 | 706996.5136 | 280434.3743 | 39.6656 | OK
21 | 11kV PDB Design Feeder 14 |  | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 |  | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT |  | 0.415 |  | ELIC5429 | 1 | 422280 | 422280 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT | 0 | 5453.7184 | -5453.7184 | -100 | CHECK
|  |  | 10: Grand Total | 8334600 | 8213322.72 | 8334600 | 1.4766
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 7875519.897
[6 empty] | Ramna | at 33 KV level |  | 459080.103
[6 empty] | Total = |  |  | 8334600 | 0
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 |  | 132 | 0 | 06604332 | 1 | 1847.38 | 1855.74 | 8.36 | 1440000 | 0 | 12038400
2 | 132kV Motijheel Circuit-2 |  | 132 |  | 06604330 | 1 | 1641.74 | 1651.74 | 10 | 1440000 | 0 | 14400000
|  |  | 9=8-7: Total Import/Export | 0 | 26438400
|  |  | 10: Net Total | 26438400
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 |  | 132 | Imp/Main | 41812909527 | 1 | 345.3 | 355.33 | 10.03 | 1200000 | 12036000
|  |  | 132 | Imp/Backup | 41812909575 | 1 | 345.39 | 355.42 | 10.03 | 1200000 | 12036000
5 | 132 kV Mniknagar Circuit-2 |  | 132 | Imp/Main | 41812909512 | 1 | 146.02 | 158.04 | 12.02 | 1200000 | 14424000
|  |  | 132 | Imp/Backup | 41812909591 | 1 | 146.05 | 158.07 | 12.02 | 1200000 | 14424000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 26460000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 26460000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1 | 39.34 | 40.51 | 1.17 | 1200000 |  | 1404000
|  |  | 132 | Exp/Backup | 41812909570 | 1 | 39.32 | 40.51 | 1.19 | 1200000 |  | 1428000
7 | 132 kV Bangabhaban Circuit-2 |  | 132 | Exp/Main | 41812909559 | 1 | 92.76 | 95.51 | 2.75 | 1200000 |  | 3300000
|  |  | 132 | Exp/Backup | 41812909569 | 1 | 92.76 | 95.51 | 2.75 | 1200000 |  | 3300000
|  |  | 7: 0; 8: 0; 10: Total |  | 4704000
| MOTIJHEEL 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41812909509 | 1 | 234.49 | 243.3 | 8.81 | 1200000 |  | 10572000
|  |  | 132 | Exp/Backup | 41812909594 | 1 | 234.49 | 243.3 | 8.81 | 1200000 |  | 10572000
6 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41812909508 | 1 | 124.79 | 134.07 | 9.28 | 1200000 |  | 11136000
|  |  | 132 | Exp/Backup | 41812909592 | 1 | 124.76 | 134.03 | 9.27 | 1200000 |  | 11124000
|  |  | 10: Total |  | 21708000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 4: 26438400; 6: EXPORT TO OTHER S/S; 9=8-7: 4704000 | 132 KV NET IMPORT |  | 21734400
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 21734400 | 33 KV NET IMPORT |  | 21549600
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 184800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.8503%
| 132 KV TOTAL IMPORT |  | 4: 26438400
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41812909543 | 1 | 388.2 | 402.78 | 14.58 | 720000 | 10497600
|  |  | 33 | Backup | 41812909617 | 1 | 388.47 | 403.06 | 14.59 | 720000 | 10504800
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41812909468 | 1 | 205.64 | 220.99 | 15.35 | 720000 | 11052000
|  |  | 33 | Backup | 41812909600 | 1 | 205.61 | 220.94 | 15.33 | 720000 | 11037600
|  |  | 7: 0; 8: 0; 10: Total | 21549600 |  | 0
| MOTIJHEEL 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) |  | 33 | Main | 41812909546 | 1 | 129.82 | 138.19 | 8.37 | 240000 |  | 2008800 | 2007905.5104 |  | 4788266.9042 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 2007905.5104 | 1928814.2523 | 79091.2581 | 4.1005 | OK
|  |  | 33 | Backup | 41812909616 | 1 | 129.78 | 138.24 | 8.46 | 240000 |  | 2030400 | 2029495.8922 |  |  |  |  | 0 | 2029495.8922 | 1928814.2523 | 100681.64 | 5.2199 | OK
17 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41812909482 | 1 | 221.08 | 232.67 | 11.59 | 240000 |  | 2781600 | 2780361.3937 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2780361.3937 | 2773270.2433 | 7091.1504 | 0.2557 | OK
|  |  | 33 | Backup | 42003953371 | 1 | 221.13 | 232.72 | 11.59 | 240000 |  | 2781600 | 2780361.3937 |  |  |  |  | 0 | 2780361.3937 | 2773270.2433 | 7091.1504 | 0.2557 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 4790400 | 4788266.9042 |  |  |  |  | 33 KV Feeders | 4788266.9042 | 4702084.4956 | 86182.4086 | 1.8329 | OK
10 | 33 kV Spare Feeder 1 |  | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 |  | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 446.88 | 459.45 | 12.57 | 360000 |  | 4525200 | 4523184.9939 |  | 8956410.0635 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 4523184.9939 | 4764459.0858 | -241274.0919 | -5.064 | OK
|  |  | 33 | Backup | 41812909610 | 1 | 447.05 | 459.63 | 12.58 | 360000 |  | 4528800 | 4526783.3908 |  |  |  |  | 0 | 4526783.3908 | 4768057.6199 | -241274.229 | -5.0602 | OK
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 267.82 | 278.65 | 10.83 | 360000 |  | 3898800 | 3897063.9207 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 3897063.9207 | 9043116.0745 | -5146052.1538 | -56.9057 | CHECK
|  |  | 33 | Backup | 41812909595 | 1 | 267.93 | 278.66 | 10.73 | 360000 |  | 3862800 | 3861079.951 |  | 7804923.0324 | Kamlapur Railway 33/11 kv ss |  | 0 | 3861079.951 | 9046714.6086 | -5185634.6576 | -57.3206 | CHECK
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 102.7 | 113.56 | 10.86 | 360000 |  | 3909600 | 3907859.1117 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 3907859.1117 | 4800444.4263 | -892585.3147 | -18.5938 | OK
|  |  | 33 | Backup | 41621865733 | 1 | 102.72 | 113.58 | 10.86 | 360000 |  | 3909600 | 3907859.1117 |  |  |  |  | 0 | 3907859.1117 | 4804042.9604 | -896183.8487 | -18.6548 | OK
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 136.79 | 149.11 | 12.32 | 360000 |  | 4435200 | 4433225.0696 |  |  |  |  | 33 kV P & T - 2 Feeder | 4433225.0696 | 255495.9177 | 4177729.1518 | 1635.1452 | FAULT
|  |  | 33 | Backup | 41812909598 | 1 | 136.75 | 149.07 | 12.32 | 360000 |  | 4435200 | 4433225.0696 |  |  |  |  | 0 | 4433225.0696 | 255495.9177 | 4177729.1518 | 1635.1452 | FAULT
20 | 33 kV Spare Feeder 9 |  | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 |  | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) |  | 0.415 |  |  | 1 | 1297.07 | 1382.5 | 85.43 | 300 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 16768800 | 16761333.0958 |  |  |  |  | 0 | 16761333.0958 | 18863515.5044 | -2102182.4086 | -11.1442 | OK
|  |  | 9=8-7: Grand Total | 21549600 | 21559200 | 21549600 | -0.044529
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) |  | 11 |  | 41812909493 | 1 | 123.43 | 131.66 | 8.23 | 250000 | 2057500 |  | 2009558.2163
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) |  | 11 |  | 41812909496 | 1 | 210.92 | 222.3 | 11.38 | 250000 | 2845000 |  | 2778708.6879
|  |  | 7: 0; 8: 0; 10: Total | 4902500 |  | 4788266.9042
| MOTIJHEEL 11 kV SIDE |  | 7: 0; 8: 0
2 | 11 kV Central Weman | A1111CW | 11 |  | 41812909492 | 1 | 166.18 | 179.49 | 13.31 | 60000 |  | 798600 | 780631.0755 | Motijheel |  |  |  | 11 kV Central Weman | 780631.0755 | 589767.3774 | 190863.6982 | 32.3625 | OK
3 | 11 kV Spare Feeder 2 |  | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len |  | 11 |  | 41812909499 | 1 | 282.85 | 297.27 | 14.42 | 60000 |  | 865200 | 845732.5401 | Swamibag |  |  |  | 11 kV K. M. Das Len | 845732.5401 | 957285.5746 | -111553.0345 | -11.6531 | OK
5 | 11 kV Gopibag | A1111GP | 11 |  | 41812909517 | 1 | 42.2 | 44.79 | 2.59 | 60000 |  | 155400 | 151903.4174 | Motijheel |  |  |  | 11 kV Gopibag | 151903.4174 | 162651.6346 | -10748.2172 | -6.6081 | OK
6 | 11kV SPICE TV | B1111E | 11 |  | 41812909518 | 1 | 22.22 | 26.14 | 3.92 | 60000 |  | 235200 | 229907.875 | Narinda |  |  |  | 11kV SPICE TV | 229907.875 | 224111.6034 | 5796.2716 | 2.5863 | OK
7 | 11 kV Spare Feeder 6 |  | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 |  | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 |  | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 |  | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 |  | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 |  | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | A1111SK | 11 |  | 41812909473 | 1 | 395.68 | 406.2 | 10.52 | 60000 |  | 631200 | 616997.6645 | Motijheel |  |  |  | 11 kV South Kamlapur | 616997.6645 | 555002.1425 | 61995.522 | 11.1703 | OK
14 | 11 kV Spare Feeder 11 |  | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | A1111AC | 11 |  | 41812909514 | 1 | 203.83 | 215.83 | 12 | 60000 |  | 720000 | 703799.6173 | Motijheel |  |  |  | 11 kV Answer Camp | 703799.6173 | 759868.7052 | -56069.0879 | -7.3788 | OK
16 | 11 kV Shapla Chattar | A1111SC | 11 |  | 41812909516 | 1 | 175.12 | 194.83 | 19.71 | 60000 |  | 1182600 | 1155990.8714 | Motijheel |  |  |  | 11 kV Shapla Chattar | 1155990.8714 | 1143527.9043 | 12462.9671 | 1.0899 | OK
17 | 11 kV Sayedabad |  | 11 |  | 41812909497 | 1 | 105.04 | 110.21 | 5.17 | 60000 |  | 310200 | 303220.3351 | Swamibag |  |  |  | 11 kV Sayedabad | 303220.3351 | 309783.0751 | -6562.7399 | -2.1185 | OK
22 | 33/0.4 kV Aux Transformer |  | 0.415 |  | 41901920686 | 1 | 1297.07 | 1382.5 | 85.43 | 1 |  | 85.43 | 83.5078 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 83.5078 | 86.4785 | -2.9707 | -3.4352 | OK
|  |  | 10: Total | 4788266.9042 | 4898485.43 | 4788266.9042 | -2.2501
[7 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[7 empty] | Motijheel | at 33 KV level |  | 3409406.1539
[7 empty] | Swamibag | at 33 KV level |  | 1148952.8752
[7 empty] | Narinda | at 33 KV level |  | 229907.875
|  |  | 7: Total =; 10: 4788266.9042 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 |  | 33 | Main | 41812909463 | 1 | 446.88 | 459.45 | 12.57 | 360000 | 0 | 4525200 | 4523184.9939
0 | 0 |  | 33 | Backup | 41812909610 | 1 | 447.05 | 459.63 | 12.58 | 360000 | 0 | 4528800 | 4526783.3908
19 | 33 kV P & T - 2 Feeder |  | 33 | Main | 42003953363 | 1 | 136.79 | 149.11 | 12.32 | 360000 | 0 | 4435200 | 4433225.0696
0 | 0 |  | 33 | Backup | 41812909598 | 1 | 136.75 | 149.07 | 12.32 | 360000 | 0 | 4435200 | 4433225.0696
|  |  | 10: Total | 0 | 8964000 | 8960008.4604
Kamalapur Railway 33 KV SIDE (Sending) | bar: 4
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 10: Total |  | 8960008.4604
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
5 | 33 kV Bidyut Bhaban Circuit |  | 33 | Import | BD017079 | 1 | 15806 | 15811 | 5 | 1000 | 5000
|  |  | 33 | Export | BD017079 | 1 | 0 | 0 | 0 | 1000 |  | 0
7 | 33 kV Motijheel Circuit-1 |  | 33 | Import | BD017081 | 1 | 60413 | 64921 | 4508 | 1000 | 4508000
8 | 33 kV Motijheel Circuit-2 |  | 33 | Import | BD017082 | 1 | 21372.33 | 21372.33 | 0 | 1000 | 4435200
11 | 33 kV Kamlapur Circuit |  | 33 | Import | BD017085 | 1 | 12870 | 12870 | 0 | 1000 | 0
|  |  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 8948200 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | BD017080 | 1 | 54230 | 59310 | 5080 | 888.88 |  | 4515510.4
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | BD017084 | 1 | 14678 | 19670 | 4992 | 888.88 |  | 4437288.96
|  |  | 10: Total |  | 8952799.36
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Sending Side |  | 4: 8960008.4604; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8960008.4604
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 8960008.4604 | 33 KV TX HV SIDE |  | 8952799.36
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 7209.1004
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.08046%
| TOTAL IMPORT |  | 4: 8960008.4604
11 KV SIDE of___P & T 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOGBAZAR T&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 |  | 11 | Import | BD014056 | 1 | 77488.94 | 77488.94 | 0 | 1000 | 4515510.4 |  | 8960008.4604 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | BD014057 | 1 | 101349 | 101349 | 0 | 1000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 4515510.4 |  | 8960008.4604
| MOGBAZAR T&T 11 KV SIDE |  | 7: 0; 8: 0
12 | Inner Circular Road Feeder | A161Z | 11 |  | BD014042 | 1 | 41532 | 42241 | 709 | 1000 |  | 709000 | 717359.185 | Motijheel |  |  |  | Inner Circular Road Feeder | 717359.185 | 740621.6003 | -23262.4153 | -3.1409 | OK
13 | NSI New Building Expres Feeder | D361NS | 11 |  | BD013982 | 1 | 10393 | 10797 | 404 | 1000 |  | 404000 | 408763.2027 | Ramna |  |  |  | NSI New Building Expres Feeder | 408763.2027 | 366793.6012 | 41969.6015 | 11.4423 | OK
14 | Police Hospital RMU Feeder | D661H | 11 |  | BD014044 | 1 | 3761 | 3920 | 159 | 1000 |  | 159000 | 160874.6268 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 160874.6268 | 178874.6877 | -18000.0609 | -10.0629 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder |  | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | D661J | 11 |  | BD014013 | 1 | 35526 | 36961 | 1435 | 1000 |  | 1435000 | 1451918.8017 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1451918.8017 | 1556611.7488 | -104692.947 | -6.7257 | OK
17 | Nayapalton Overhead Feeder | D361N | 11 |  | BD014014 | 1 | 25646 | 26556 | 910 | 1000 |  | 910000 | 920728.9962 | Ramna |  |  |  | Nayapalton Overhead Feeder | 920728.9962 | 1002904.148 | -82175.1518 | -8.1937 | OK
18 | Masjid Gali Over Head Feeder | D361MG | 11 |  | BD014016 | 1 | 15482 | 16316 | 834 | 1000 |  | 834000 | 843832.9482 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 843832.9482 | 902412.7504 | -58579.8022 | -6.4915 | OK
19 | Spare Feeder (Feeder-8) |  | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) |  | 11 |  | BD013988 | 1 | 13.18 | 13.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 1004.914 | -1004.914 | -100 | CHECK
23 | Mid Way Over Head Feeder | D361MW | 11 |  | BD014015 | 1 | 23839 | 24754 | 915 | 1000 |  | 915000 | 925787.9468 | Ramna |  |  |  | Mid Way Over Head Feeder | 925787.9468 | 990845.1803 | -65057.2335 | -6.5658 | OK
24 | Palton Thana Over Head Feeder | D661F | 11 |  | BD014033 | 1 | 25001 | 26289 | 1288 | 1000 |  | 1288000 | 1303185.6562 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1303185.6562 | 1382761.6309 | -79575.9747 | -5.7549 | OK
25 | Police Hospital (South) U/G Feeder 7 |  | 11 |  | BD014034 | 1 | 12571 | 12743 | 172 | 1000 |  | 172000 | 174027.8982 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 174027.8982 | 183899.2576 | -9871.3594 | -5.3678 | OK
26 | China Town Express Feeder | D361CT | 11 |  | BD013943 | 1 | 6660 | 6925 | 265 | 1000 |  | 265000 | 268124.378 | Ramna |  |  |  | China Town Express Feeder | 268124.378 | 282380.8272 | -14256.4492 | -5.0487 | OK
27 | Fakirapul Bazar O/H Feeder | A161FB | 11 |  | BD014032 | 1 | 30742 | 32179 | 1437 | 1000 |  | 1437000 | 1453942.382 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1453942.382 | 1464159.663 | -10217.281 | -0.69783 | OK
28 | PWD Ouarter (RMU) | A161PW | 11 |  | BD013937 | 1 | 2467 | 2615 | 148 | 1000 |  | 148000 | 149744.9357 | Motijheel |  |  |  | PWD Ouarter (RMU) | 149744.9357 | 156766.5803 | -7021.6446 | -4.479 | OK
29 | Postal Quarter RMU | A161PO | 11 |  | BD013945 | 1 | 3035 | 3209 | 174 | 1000 |  | 174000 | 176051.4784 | Motijheel |  |  |  | Postal Quarter RMU | 176051.4784 | 181889.4296 | -5837.9512 | -3.2096 | OK
30 | 11/0.4 kV AT-1 |  | 0.415 |  | DHKH4409 | 1 | 1476 | 1476 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 0 | 4220.6387 | -4220.6387 | -100 | CHECK
31 | 11/0.4 kV AT-2 |  | 0.415 |  | DHKH4411 | 1 | 522 | 578 | 56 | 100 |  | 5600 | 5666.0246 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 5666.0246 | 1406.8796 | 4259.145 | 302.737 | FAULT
|  |  | 10: Grand Total | 8960008.4604 | 8855600 | 8960008.4604 | 1.179
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 2497097.981
[6 empty] | Ramna | at 33 KV level |  | 3367237.4719
[6 empty] | Rajarbag | at 33 KV level |  | 3095673.0075
[6 empty] | Total = |  |  | 8960008.4604 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 |  | 33 | Main | 41812909530 | 1 | 267.82 | 278.65 | 10.83 | 360000 | 0 | 3898800 | 3897063.9207
0 | 0 |  | 33 | Backup | 41812909595 | 1 | 267.93 | 278.66 | 10.73 | 360000 | 0 | 3862800 | 3861079.951
18 | 33 kV Kamlapur- 2 Feeder |  | 33 | Main | 41812909552 | 1 | 102.7 | 113.56 | 10.86 | 360000 | 0 | 3909600 | 3907859.1117
0 | 0 |  | 33 | Backup | 41621865733 | 1 | 102.72 | 113.58 | 10.86 | 360000 | 0 | 3909600 | 3907859.1117
|  |  | 10: Total | 0 | 7772400 | 7768939.0627
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 |  | 33 | Import | 101 | 1 | 357.8 | 370.9 | 13.1 | 270000 | 3537000
6 | 33 kV Motijheel Circuit-2 |  | 33 | Import | 113 | 1 | 136.7 | 151.1 | 14.4 | 270000 | 3888000
|  |  | 7: 0; 8: 0; 10: Total | 7425000 | 0 | 0
[7 empty] | 0 | 0
1 | 33 kV P&T Circuit |  | 33 | Import | 102 | 1 | 47.7 | 47.7 | 0 | 270000 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 0 | 0
[7 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  | 7: 0; 8: 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) |  | 33 | Export | 103 | 1 | 340.1 | 356.3 | 16.2 | 240000 |  | 3888000
4 | 33 kV 28/35 MVA Transformer (T-2 ) |  | 33 | Export | 104 | 1 | 160.9 | 177.1 | 16.2 | 240000 |  | 3888000
|  |  | 10: Total |  | 7776000
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Kamalapur Railway 33 KV SIDE (Sending) |  | 4: 7768939.0627; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7768939.0627
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 7768939.0627 | 33 KV TX HV SIDE |  | 7776000
[11 empty] | LOSS UNITS=> |  | -7060.9373
[11 empty] | LOSS % IN => |  | -0.09089%
| TOTAL IMPORT |  | 4: 7768939.0627
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | 42 | 1 | 405 | 424.4 | 19.4 | 200000 | 3880000 |  | 3884469.5313
10 | 11 kV 20/28 MVA Transformer-2 |  | 11 | Import | 64 | 1 | 190.6 | 210 | 19.4 | 200000 | 3880000 |  | 3884469.5313
|  |  | 7: 0; 8: 0; 10: Total | 7760000 |  | 7768939.0627
| KAMALAPUR RAILWAY 11 KV SIDE |  | 7: 0; 8: 0
1 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 430.5 | 452 | 21.5 | 40000 |  | 860000 | 873041.3399 | Rajarbag |  |  |  | Amtola O/H Feeder | 873041.3399 | 948762.3589 | -75721.019 | -7.981 | OK
2 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 74 | 78.6 | 4.6 | 40000 |  | 184000 | 186790.2402 | Rajarbag |  |  |  | Police Telecom | 186790.2402 | 199525.1313 | -12734.8911 | -6.3826 | OK
3 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 305 | 324.1 | 19.1 | 40000 |  | 764000 | 775585.5625 | Rajarbag |  |  |  | Railway Colony O/H | 775585.5625 | 851035.764 | -75450.2015 | -8.8657 | OK
4 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 738.6 | 768.6 | 30 | 40000 |  | 1200000 | 1218197.2185 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 1218197.2185 | 1388532.036 | -170334.8175 | -12.2673 | OK
5 | 11 KV Majar Feeder |  | 11 |  | 96 | 1 | 62 | 71.1 | 9.1 | 40000 |  | 364000 | 369519.8229 | Motijheel |  |  |  | 11 KV Majar Feeder | 369519.8229 | 407194.1454 | -37674.3225 | -9.2522 | OK
7 | 11 kV Feeder-6 |  | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 343.4 | 355.6 | 12.2 | 40000 |  | 488000 | 495400.2022 | Rajarbag |  |  |  | Momenbagh O/H | 495400.2022 | 517136.5647 | -21736.3625 | -4.2032 | OK
9 | 11 kV Feeder-8 |  | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 224.2 | 232.7 | 8.5 | 40000 |  | 340000 | 345155.8786 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 345155.8786 | 354258.9065 | -9103.028 | -2.5696 | OK
12 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 330.7 | 363.8 | 33.1 | 40000 |  | 1324000 | 1344077.5978 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 1344077.5978 | 2296574.9803 | -952497.3826 | -41.4747 | CHECK
13 | 11 kV Feeder-11 |  | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway |  | 11 | Motijheel | 150 | 1 | 69.3 | 71.8 | 2.5 | 40000 |  | 100000 | 101516.4349 | Motijheel |  |  |  | Dhaka Railway | 101516.4349 | 199525.1313 | -98008.6964 | -49.121 | CHECK
15 | Jasimuddin Feeder-13 |  | 11 |  | 91 | 1 | 234.5 | 270.1 | 35.6 | 40000 |  | 1424000 | 1445594.0326 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1445594.0326 | 1653208.2305 | -207614.1979 | -12.5583 | OK
16 | Police Box Feeder-14 |  | 11 |  | 18 | 1 | 100.7 | 115.6 | 14.9 | 40000 |  | 596000 | 605037.9519 | Motijheel |  |  |  | Police Box Feeder-14 | 605037.9519 | 655582.5742 | -50544.6223 | -7.7099 | OK
17 | 11 kV Feeder-15 |  | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 |  | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) |  | 0.415 |  | DHKF 7632 | 1 | 948.92 | 1018.7 | 69.78 | 100 |  | 6978 | 7083.8168 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 7083.8168 | 0 | 7083.8168 | #DIV/0! | #DIV/0!
20 | Auxiliary -1 (AT-2 ) |  | 0.415 |  | DHKF 7733 | 1 | 137.5 | 156.6 | 19.1 | 100 |  | 1910 | 1938.9639 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 1938.9639 | 1823.2118 | 115.7521 | 6.3488 | OK
|  |  | 10: Grand Total | 7768939.0627 | 7652888 | 7768939.0627 | 1.5164
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Rajarbag | at 33 KV level |  | 5247270.8203
[6 empty] | Motijheel | at 33 KV level |  | 2521668.2423
[6 empty] | Total = |  |  | 7768939.0627 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 |  | 132 | Exp/Main | 41812909556 | 1 | 39.34 | 40.51 | 1.17 | 1200000 | 0 | 1404000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 |  | 132 |  | 41812909559 | 1 | 92.76 | 95.51 | 2.75 | 1200000 | 0 | 3300000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
|  |  | 10: Total | 0 | 4704000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
|  |  | 10: Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
BANGABHABAN 33 KV SIDE
|  |  | 3: 132; 4: NET IMPORT |  | 0
|  |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 4: 4704000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 4704000
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 4704000 | 33 KV TX HV SIDE |  | 4704000
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 4: 4704000
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) |  | 11 | Import | 4150744 | 1 | 1524064.4 | 1527376.9 | 3312.5 | 1000 | 3312500 |  | 3278902.4031
12 | 11 kV 28/35 MVA Transformer (GT-1) |  | 11 | Import | 4150742 | 1 | 1443276.5 | 1444716.2 | 1439.7 | 1000 | 1439700 |  | 1425097.5969
|  |  | 7: 0; 8: 0; 10: Total | 4752200 |  | 4704000
| BANGABHABAN 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV DIT S/S-1 Feeder |  | 11 | Motijheel | 4150750 | 1 | 217443.1 | 218543.72 | 1100.62 | 1000 | Estimated | 729797.04 | 730932.291 | Motijheel | 60 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 730932.291 | 825621.5358 | -94689.2448 | -11.4688 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 |  | 11 | Motijheel | 4150743 | 1 | 24265.4 | 24310.71 | 45.31 | 1000 |  | 45310 | 45380.4829 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 45380.4829 | 61964.371 | -16583.8881 | -26.7636 | OK
3 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder |  | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation |  | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder |  | 11 | Ramna | 4150754 | 1 | 33881.92 | 33902.7 | 20.78 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 668980.62 | 670021.2667 | Motijheel | 55 | Meter Bad |  | 11 kV Modhumita via Ovisar | 670021.2667 | 766648.569 | -96627.3023 | -12.6039 | OK
8 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 15953.16 | 16026.75 | 73.59 | 1000 |  | 73590 | 73704.4745 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 73704.4745 | 67064.6079 | 6639.8666 | 9.9007 | OK
9 | 11 kV Motijheel-1 Feeder |  | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 248922.27 | 250080.37 | 1158.1 | 1000 |  | 1158100 | 1159901.5065 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1159901.5065 | 1104426.7361 | 55474.7704 | 5.0229 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 |  | 11 | Motijheel | 4150737 | 1 | 14821.23 | 14984.45 | 163.22 | 1000 |  | 163220 | 163473.9003 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 163473.9003 | 173027.2895 | -9553.3893 | -5.5213 | OK
14 | 11 kV Motijheel-2 Feeder |  | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 243644.097 | 235891.8674 | 7752.2296 | 3.2863 | OK
16 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 164465.14 | 164831.63 | 366.49 | 1000 |  | 366490 | 367060.1011 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 367060.1011 | 339501.426 | 27558.6752 | 8.1174 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20709.49 | 20763.9 | 54.41 | 1000 | Estimated | 182449.26 | 182733.0727 | Motijheel | 15 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 182733.0727 | 235891.8674 | -53158.7946 | -22.5352 | OK
18 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | 20 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 243644.097 | 294864.8342 | -51220.7372 | -17.3709 | OK
19 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 123520.52 | 123820.22 | 299.7 | 1000 |  | 299700 | 300166.2046 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 300166.2046 | 298839.8125 | 1326.392 | 0.44385 | OK
20 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273191.92 | 273191.92 | 0 | 1000 |  | 0 | 0 | Motijheel | no reading |  |  | 11 kV DIT S/S RMU Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 81705.33 | 81979.59 | 274.26 | 1000 |  | 274260 | 274686.6308 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 274686.6308 | 474442.2708 | -199755.64 | -42.1033 | CHECK
22 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192767.86 | 192879.03 | 111.17 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | 20 | Meter Bad |  | 11 kV BCIC Feeder | 243644.097 | 294864.8342 | -51220.7372 | -17.3709 | OK
23 | 11/0.4 kV AT-1 |  | 0.415 |  | 63412931 | 1 | 78910 | 78910 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 0 | 5939.9222 | -5939.9222 | -100 | CHECK
24 | 11/0.4 kV AT-2 |  | 0.415 |  | 63403117 | 1 | 22885.4 | 22885.4 | 0 | 1 | Estimated | 5000 | 5007.7779 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5007.7779 | 5010.0559 | -2.278 | -0.045469 | OK
|  |  | 10: Grand Total | 4704000 | 4696693.96 | 4704000 | 0.15556
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Maniknagar | at 33 KV level |  | 0
[6 empty] | Ramna | at 33 KV level |  | 0
[6 empty] | Swamibag | at 33 KV level |  | 0
[6 empty] | Motijheel | at 33 KV level |  | 4704000
[6 empty] | Total = |  |  | 4704000 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
0 | 132 kV Narinda Circuit-1 | 0 | 132 | EXPORT | 06604331 | 1 | 8876.04 | 8876.04 | 0 | 480000 | From Downstream | 19540800 | 0 | 0 | Wrong Reading by Grid
0 | 132 kV Narinda Circuit-2 | 0 | 132 |  |  | 1 | 8968.84 | 9009.55 | 40.71 | 480000 | 0 | 19540800 | 0 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 39081600
|  |  | 10: Net Total | 39081600
NARINDA 132 KV SIDE (RECEIVING)
|  |  | 9=8-7: Total Import/Export | 0 | 0
|  |  | 9=8-7: Net Total | 39081600
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | 3: 132; 4: EXPORT |  | 0
| Feeder No.2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 |  | 3: 132; 4: NET IMPORT |  | 0
| 132/33 KV GT-2 |  | 3: 132 |  | 0
|  |  | 10: Total |  | 39081600
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 4: 39081600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 39081600
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 39081600 | 33 KV NET IMPORT |  | 39043200
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 38400
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.09826%
| 132 KV TOTAL IMPORT |  | 4: 39081600
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming |  | 33 | Import | 06604301 | 1 | 9335.02 | 9375.73 | 40.71 | 480000 | 19540800
7 | 132/33 kV 50/75 MVA GT-2 Incoming |  | 33 | Import | 06604304 | 1 | 9159 | 9199.63 | 40.63 | 480000 | 19502400
|  |  | 7: 0; 8: 0; 10: Total | 39043200 |  | 0
| NARINDA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 |  | 33 | Export | 06604300 | 1 | 9813.54 | 9862.03 | 48.49 | 180000 |  | 8728200 | 8741872.5494 |  | 17471125.3612 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 8741872.5494 | 8627081.218 | 114791.3315 | 1.3306 | OK
8 | 33 kV 20/28 MVA Transformer T-4 |  | 33 | Export | 06604303 | 1 | 9951.13 | 9999.55 | 48.42 | 180000 |  | 8715600 | 8729252.8118 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 8729252.8118 | 9121294.1081 | -392041.2963 | -4.2981 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 17443800 | 17471125.3612 |  |  |  |  | 33 KV Feeders | 17471125.3612 | 17748375.3261 | -277249.9649 | -1.5621 | OK
1 | 33 kV New Ramna Feeder |  | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 1648800 | 1651382.812 |  | 1651382.812 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1651382.812 | 1477227.5805 | 174155.2315 | 11.7893 | OK
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 8693968.6263 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5723.98 | 5750.32 | 26.34 | 180000 |  | 4741200 | 4748626.9943 |  |  |  |  | 33 kV Kumertully-1 Feeder | 4748626.9943 | 5062976.5793 | -314349.585 | -6.2088 | OK
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5614 | 5649.5 | 35.5 | 180000 |  | 6390000 | 6400009.8062 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 6400009.8062 | 7470911.6464 | -1070901.8402 | -14.3343 | OK
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder |  | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 8680371 | 8693968.6263 |  | 11148636.8005 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 8693968.6263 | 9217590.4677 | -523621.8414 | -5.6807 | OK
|  |  | 10: Total |  | 21460371 | 21493988.2388 |  |  |  |  | 0 | 21493988.2388 | 23228706.2739 | -1734718.0351 | -7.468 | OK
|  |  | 9=8-7: Grand Total | 38965113.6 | 38904171 | 38965113.6 | 0.15665
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 | Import | 06604351 | 1 | 11035.76 | 11090.85 | 55.09 | 160000 | 8814400 |  | 8745087.1902
9 | 33/11 kV 20/28 MVA T-4 Incoming |  | 11 | Import | 06604295 | 1 | 11375.94 | 11430.91 | 54.97 | 160000 | 8795200 |  | 8726038.1711
|  |  | 7: 0; 8: 0; 10: Total | 17609600 |  | 17471125.3612
| NARINDA 11 kV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bonogram Feeder | B124B | 11 |  | 06604467 | 1 | 25025.97 | 25159.72 | 133.75 | 8000 |  | 1070000 | 1081937.7982 | Narinda |  |  |  | 11 kV Bonogram Feeder | 1081937.7982 | 1068648.5129 | 13289.2853 | 1.2436 | OK
2 | 11 kV Sha Saheb Len Feeder | B524H | 11 |  | 06604469 | 1 | 16887.94 | 16969.66 | 81.72 | 8000 |  | 653760 | 661053.8831 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 661053.8831 | 660371.6402 | 682.243 | 0.10331 | OK
3 | 11 kV Sadiabad Water Treatment | B224W | 11 |  | 06604354 | 1 | 510.35 | 530.01 | 19.66 | 40000 |  | 786400 | 795173.7239 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 795173.7239 | 352381.8247 | 442791.8992 | 125.6568 | FAULT
4 | 11 kV Manashi Feeder | B124M | 11 |  | 06604353 | 1 | 5586.07 | 5614.2 | 28.13 | 40000 |  | 1125200 | 1137753.6547 | Narinda |  |  |  | 11 kV Manashi Feeder | 1137753.6547 | 1160429.802 | -22676.1473 | -1.9541 | OK
5 | 11 kV Jatrabari Feeder | B524E | 11 |  | 06604324 | 1 | 3530.9 | 3581.5 | 50.6 | 40000 |  | 2024000 | 2046581.4052 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 2046581.4052 | 2127657.1553 | -81075.75 | -3.8106 | OK
6 | 11 kV Wari Feeder | B124W | 11 |  | 06604291 | 1 | 8641.1 | 8679.86 | 38.76 | 40000 |  | 1550400 | 1567697.5349 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1567697.5349 | 1678876.6245 | -111179.0896 | -6.6222 | OK
7 | 11 kV Narinda Feeder | B124N | 11 |  | 06604348 | 1 | 7378.81 | 7414.52 | 35.71 | 40000 |  | 1428400 | 1444336.4028 | Narinda |  |  |  | 11 kV Narinda Feeder | 1444336.4028 | 1555745.5042 | -111409.1014 | -7.1611 | OK
10 | 11 kV Distillary Feeder | B524D | 11 |  | 06604347 | 1 | 6064.21 | 6095.73 | 31.52 | 40000 |  | 1260800 | 1274866.5196 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1274866.5196 | 1339455.9704 | -64589.4508 | -4.8221 | OK
11 | 11 kV Thatari Bazar Feeder | B124T | 11 |  | 06604296 | 1 | 5085.7 | 5110.49 | 24.79 | 40000 |  | 991600 | 1002663.1035 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 1002663.1035 | 1062005.913 | -59342.8095 | -5.5878 | OK
12 | 11 kV Swamibagh Feeder | B524C | 11 |  | 06604352 | 1 | 7861.81 | 7894.28 | 32.47 | 40000 |  | 1298800 | 1313290.4788 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 1313290.4788 | 1313533.6293 | -243.1504 | -0.018511 | OK
13 | 11 kV Tipu Sultan Feeder | B124S | 11 |  | 06604322 | 1 | 6432.11 | 6459.68 | 27.57 | 40000 |  | 1102800 | 1115103.7419 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 1115103.7419 | 1147873.668 | -32769.9261 | -2.8548 | OK
14 | 11 kV Spare |  | 11 |  | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | B124F | 11 |  | DHK00089 | 1 | 37642.3 | 41171.3 | 3529 | 444.44 |  | 1568428.76 | 1585927.4386 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1585927.4386 | 1742899.9791 | -156972.5405 | -9.0064 | OK
16 | 11 kV Bhajohari Feeder | B124V | 11 |  | DHK27842 | 1 | 414466 | 424175 | 9709 | 80 |  | 776720 | 785385.7258 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 785385.7258 | 835023.4135 | -49637.6877 | -5.9445 | OK
17 | 11 kV Lal mohon shaha Feeder | B124L | 11 |  | DHK00086 | 1 | 39197.2 | 41548.8 | 2351.6 | 444.44 |  | 1045145.104 | 1056805.6006 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 1056805.6006 | 1090752.6026 | -33947.002 | -3.1123 | OK
18 | 11 kV Dupkhola Feeder | B524A | 11 |  | 8838024/8838029 | 1 | 37971.7 | 38567.6 | 595.9 | 1000 |  | 595900 | 602548.3495 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 602548.3495 | 612719.0865 | -10170.737 | -1.6599 | OK
1 | 11/0.4 kV Aux Transformer-1 |  | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 |  | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 17471125.3612 | 17278353.864 | 17471125.3612 | 1.1157
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Narinda | at 33 KV level |  | 10777611.0011
[6 empty] | Maniknagar | at 33 KV level |  | 795173.7239
[6 empty] | Swamibag | at 33 KV level |  | 5898340.6363
[6 empty] | Total = |  |  | 17471125.3612 | 0
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder |  | 33 | Export | 06604318 | 1 | 5723.98 | 5750.32 | 26.34 | 180000 | 0 | 4741200 | 4748626.9943
9 | 33 kV Kumertully-2 Feeder |  | 33 | Export | 06604290 | 1 | 5614 | 5649.5 | 35.5 | 180000 | 0 | 6390000 | 6400009.8062
| MITFORD 33 KV SIDE | [10 empty] | 11131200 | 11148636.8005 | bar: 4
1 | Kumartuly Circuit-1 |  | 33 | 0 | DHK-66493 | 1 | 1290134 | 1291902 | 1768 | 180 | 0 | 318600 | 318600
6 | Kumartuly Circuit-2 |  | 33 | 0 | DHK-60914 | 1.1 | 774406 | 776528.4 | 2122.4 | 180 | 0 | 421740 | 421740
|  |  | 10: Total |  | 740340 | 740340
| KUMERTULY 33 KV SIDE (RECEIVING) | [11 empty] | 11888976.8005
5 | 33 kV Mitford Circuit-1 |  | 33 | Import | DHK60965 | 1 | 284476.7 | 286246.7 | 1770 | 180 | 318600
6 | 33 kV Narinda Circuit-1 |  | 33 | Import | DHK60959 | 1 | 1000840.4 | 1000840.4 | 0 | 540 | 0
9 | 33 kV Mitford Circuit-2 |  | 33 | Import | DHK86072 | 1 | 1775.47 | 1777.6 | 2.13 | 180000 | 383400
10 | 33 kV Narinda Circuit-2 |  | 33 | Import | DHK60957 | 1 | 917906.2 | 929717.4 | 11811.2 | 540 | 6378048
|  |  | 8: 0; 10: Total | 7080048 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
|  |  | 3: 33; 4: EXPORT; 8: 0 |  | 0
|  |  | 3: 33; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 702000
0
| KUMERTULY 33 KV SIDE |  | 8: 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) |  | 33 | Export | DHK60960 | 1 | 173640.5 | 200236.7 | 26596.2 | 180 |  | 4787316
8 | 33/11 kV 20/28 MVA Transformer (T-2) |  | 33 | Export | DHK60958 | 1 | 358200.1 | 391638.5 | 33438.4 | 180 |  | 6018912
|  |  | 10: Total |  | 10806228
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 11148636.8005; 6: EXPORT TO OTHER S/S; 9=8-7: 740340 | 33 KV NET IMPORT |  | 10408296.8005
| MITFORD 33 KV SIDE |  | 6: 33 KV NET IMPORT; 9=8-7: 10408296.8005 | 33 KV TX HV SIDE |  | 7080048
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 3328248.8005
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 31.98%
| TOTAL IMPORT |  | 4: 11148636.8005
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 | Import | 06604403 | 1 | 7287.33 | 7317.08 | 29.75 | 160000 | 4787316 |  | 4619110.6116 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 | Import | 06604410 | 1 | 6737.24 | 6774.74 | 37.5 | 160000 | 6000000 |  | 5789186.189
|  |  | 7: 0; 8: 0; 10: Total | 10787316 |  | 10408296.8005
| KUMERTULY 11 KV SIDE |  | 7: 0; 8: 0
11 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63208 | 63497.4 | 289.4 | 2222.22 |  | 643110.468 | 648124.404 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 648124.404 | 633672.3537 | 14452.0503 | 2.2807 | OK
12 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4655.85 | 4688.31 | 32.46 | 40000 |  | 1298400 | 1308522.8246 | Banglabazar |  |  |  | 11kV Islampur Feeder | 1308522.8246 | 1300047.3482 | 8475.4765 | 0.65194 | OK
13 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5168.65 | 5181.29 | 12.64 | 40000 |  | 505600 | 509541.8516 | Banglabazar |  | 120 |  | 11kV Majar O/H Feeder | 509541.8516 | 496023.0204 | 13518.8312 | 2.7254 | OK
15 | 11kV Spare |  | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  | 70 |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5499.06 | 5527.79 | 28.73 | 40000 |  | 1149200 | 1158159.6042 | Banglabazar |  | 50 |  | 11kV Sadarghat Feeder | 1158159.6042 | 1128130.2786 | 30029.3256 | 2.6619 | OK
17 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal |  | 16.6667 |  | 11kV Mitford Hospital Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4141.09 | 4169.95 | 28.86 | 40000 |  | 1154400 | 1163400.1454 | Banglabazar |  | 86.6667 |  | 11kV Zindabahar Feeder | 1163400.1454 | 1221939.8271 | -58539.6817 | -4.7907 | OK
21 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1070368.992 | 1078713.9994 | Banglabazar | 88 |  |  | 11kV Police fari Feeder | 1078713.9994 | 1184790.4407 | -106076.4413 | -8.9532 | OK
22 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 5956.75 | 5983.44 | 26.69 | 40000 |  | 1067600 | 1075923.4193 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 1075923.4193 | 1095518.3755 | -19594.9562 | -1.7886 | OK
23 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8287.89 | 8334.99 | 47.1 | 40000 |  | 1884000 | 1898688.3869 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1898688.3869 | 2041666.1823 | -142977.7953 | -7.003 | OK
24 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3780.65 | 3791.32 | 10.67 | 40000 |  | 426800 | 430127.4966 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 430127.4966 | 443280.3129 | -13152.8163 | -2.9672 | OK
25 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7270.69 | 7301.75 | 31.06 | 40000 |  | 1242400 | 1252086.2271 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 1252086.2271 | 586209.0241 | 665877.203 | 113.5904 | FAULT
26 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3600.06 | 3606.94 | 6.88 | 40000 |  | 275200 | 277345.5648 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 277345.5648 | 287870.5029 | -10524.9381 | -3.6561 | OK
27 | 11/0.4 kV AT-1 |  | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 |  | 0.415 |  | 05378636 | 1 | 173865.2 | 176640.6 | 2775.4 | 2 |  | 5550.8 | 5594.0762 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 5594.0762 | 5930.3337 | -336.2575 | -5.6701 | OK
|  |  | 10: Grand Total | 10806228 | 10722630.26 | 10806228 | 0.77964
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 0
[6 empty] | Banglabazar | at 33 KV level |  | 10806228
[6 empty] | Total = |  |  | 10806228 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder |  | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder |  | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 8680371 | 8693968.6263
|  |  | 10: Total | 0 | 8680371 | 8693968.6263
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 |  | 33 | Import | Mat-152447/1191738/007 | 1 | 123502200 | 126294600 | 2792400 | 1 | 2792400
5 | 33 kV Narinda Circuit-2 |  | 33 | Import | Mat-152447/1191738/002 | 1 | 248745800 | 254593400 | 5847600 | 1 | 5847600
|  |  | 7: 0; 8: 0; 10: Total | 8640000 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  | 7: 0; 8: 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) |  | 33 | Export | Mat-152447/1191738/009 | 1 | 130694300 | 133504800 | 2810500 | 1 |  | 2810500 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) |  | 33 | Export | Mat-152447/1191738/004 | 1 | 246273000 | 252121300 | 5848300 | 1 |  | 5848300 |  |  | #VALUE!
|  |  | 10: Total |  | 8658800
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 4: 8693968.6263; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8693968.6263
|  |  | 6: 33 KV NET IMPORT; 9=8-7: 8693968.6263 | 33 KV TX HV SIDE |  | 8658800
[11 empty] | LOSS UNITS=> |  | 35168.6263
[11 empty] | LOSS % IN => |  | 0.4045%
| TOTAL IMPORT |  | 4: 8693968.6263
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 |  | 11 | Import | 340180016886 | 1 | 130725818 | 133533495 | 2807677 | 1 | 2807677 |  | 2812075.1694 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 |  | 11 | Import | 340180012685 | 1 | 249636430 | 255509124 | 5872694 | 1 | 5872694 |  | 5881893.4568
|  |  | 7: 0; 8: 0; 10: Total | 8680371 |  | 8693968.6263
| BANGSHAL 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 39891564 | 40639116 | 747552 | 1 |  | 747552 | 748100.1808 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 748100.1808 | 769760.338 | -21660.1572 | -2.8139 | OK
2 | 11 kV Spare Feeder |  | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder |  | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 52546725 | 53863751 | 1317026 | 1 |  | 1317026 | 1317991.7768 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1317991.7768 | 1424094.0148 | -106102.238 | -7.4505 | OK
5 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 22130205 | 22867036 | 736831 | 1 |  | 736831 | 737371.3191 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 737371.3191 | 742977.1081 | -5605.7891 | -0.7545 | OK
8 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 49587871 | 51129746 | 1541875 | 1 |  | 1541875 | 1543005.6588 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1543005.6588 | 1634853.1578 | -91847.499 | -5.6181 | OK
9 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 64655261 | 65782506 | 1127245 | 1 |  | 1127245 | 1128071.6101 | Bangshal |  |  |  | 11 kV French Road Feeder | 1128071.6101 | 1204002.0348 | -75930.4246 | -6.3065 | OK
10 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 32104912 | 32609799 | 504887 | 1 |  | 504887 | 505257.2343 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 505257.2343 | 581501.911 | -76244.6768 | -13.1117 | OK
11 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 65935153 | 67416873 | 1481720 | 1 |  | 1481720 | 1482806.5471 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1482806.5471 | 1592214.2158 | -109407.6687 | -6.8714 | OK
12 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 52819246 | 54042708 | 1223462 | 1 |  | 1223462 | 1224359.1662 | Narinda |  |  |  | 11 kV Suritolla Feeder | 1224359.1662 | 1261180.3015 | -36821.1353 | -2.9196 | OK
13 | AT-1 |  | 0.415 |  | DHK-4415 | 1 | 734.14 | 764.01 | 29.87 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 |  | 0.415 |  | DHK-4410 | 1 | 764.83 | 771.03 | 6.2 | 100 |  | 7000 | 7005.1331 | Bangshal |  |  |  | AT-2 | 7005.1331 | 7007.3859 | -2.2528 | -0.032149 | OK
|  |  | 10: Grand Total | 8693968.6263 | 8687598 | 8693968.6263 | 0.07333
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Bangshal | at 33 KV level |  | 6151617.6833
[6 empty] | Banglabazar | at 33 KV level |  | 1317991.7768
[6 empty] | Narinda | at 33 KV level |  | 1224359.1662
[6 empty] | Total = |  |  | 8693968.6263 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING) Maniknagar 132
0 | 132 kV Kazla Circuit-1 | 0 | 132 | 0 | ABB03905 | 1 | 814636.9 | 844535 | 29898.1 | 1000 | 0 | 29898100
0 | 132 kV Kazla Circuit-2 | 0 | 132 |  |  | 1 | 611209.5 | 640950 | 29740.5 | 1000 | 0 | 29740500
|  |  | 9=8-7: Total Import/Export | 0 | 59638600
|  |  | 10: Net Total | 59638600
KAZLA 132 KV SIDE (RECEIVING)
3 | 132kV Maniknagar Circuit-1 |  | 132 | Main | 41812909505 | 1 | 679.22 | 705.51 | 26.29 | 1200000 | 31548000
|  |  | 132 | Backup | 41812909603 | 1 | 679.19 | 705.48 | 26.29 | 1200000 | 31548000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 |  | 132 | Main | 41812909540 | 1 | 508.32 | 533.06 | 24.74 | 1200000 | 29688000
|  |  | 132 | Backup | 41812909587 | 1 | 508.33 | 533.08 | 24.75 | 1200000 | 29700000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
|  |  | 8: 0; 9=8-7: Total Import/Export | 61236000 | 0
|  |  | 8: 0; 9=8-7: Net Total | 61236000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 8: 0; 10: Total |  | 0
| KAZLA 132 KV SIDE |  | 8: 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Main | 41812909542 | 1 | 679.85 | 706.4 | 26.55 | 1200000 |  | 31860000 |  |  | #DIV/0!
|  |  | 132 | Backup | 41812909589 | 1 | 680.25 | 706.81 | 26.56 | 1200000 |  | 31872000
7 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Main | 41812909501 | 1 | 507.93 | 532.43 | 24.5 | 1200000 |  | 29400000 |  |  | 100
|  |  | 132 | Backup | 41812909606 | 1 | 507.87 | 532.36 | 24.49 | 1200000 |  | 29388000
|  |  | 10: Total |  | 61260000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) Maniknagar 132 |  | 4: 59638600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 59638600
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 59638600 | 33 KV NET IMPORT |  | 61034400
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -1395800
| IMPORT-4 | [9 empty] | LOSS % IN => |  | -2.34%
| 132 KV TOTAL IMPORT |  | 4: 59638600
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder |  | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder |  | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder |  | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder |  | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) |  | 33 | Main | 41812909533 | 1 | 1128.56 | 1172.62 | 44.06 | 720000 | 31723200
|  |  | 33 | Backup | 41812909582 | 1 | 1128.65 | 1172.72 | 44.07 | 720000 | 31730400
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) |  | 33 | Main | 41812909479 | 1 | 843.81 | 884.52 | 40.71 | 720000 | 29311200
|  |  | 33 | Backup | 41812909622 | 1 | 843.69 | 884.39 | 40.7 | 720000 | 29304000
|  |  | 7: 0; 8: 0; 10: Total | 61034400 |  | 0
| KAZLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 |  | 33 | Main | 41812909465 | 1 | 1142.17 | 1190.68 | 48.51 | 240000 |  | 11642400 | 11627083.7597 |  | 38211664.1599 | Kazla 33/11 kv ss | 1.3565 | 33/11 kV 20/28 MVA T-1 | 11627083.7597 | 12234320.1984 | -607236.4387 | -4.9634 | OK
|  |  | 33 | Backup | 41812909596 | 1 | 1141.87 | 1190.366 | 48.496 | 240000 |  | 11639040 | 11623728.18 |  |  |  |  | 0 | 11623728.18 | 12229540.2335 | -605812.0535 | -4.9537 | OK
13 | 33/11 kV 28/35 MVA T-5 |  | 33 | Main | 41812909536 | 1 | 137.26 | 148.15 | 10.89 | 360000 |  | 3920400 | 3915242.4905 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 3915242.4905 | 3904036.3438 | 11206.1467 | 0.28704 | OK
|  |  | 33 | Backup | 41812909578 | 1 | 129.78 | 138.24 | 8.46 | 360000 |  | 3045600 | 3041593.3397 |  |  |  |  | 0 | 3041593.3397 | 2882318.8434 | 159274.4964 | 5.5259 | OK
14 | 33/11 kV 20/28 MVA T-2 |  | 33 | Main | 41812909554 | 1 | 1122.03 | 1160.82 | 38.79 | 240000 |  | 9309600 | 9297352.691 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 9297352.691 | 10085725.9694 | -788373.2784 | -7.8167 | OK
|  |  | 33 | Backup | 41812909613 | 1 | 1120.93 | 1159.68 | 38.75 | 240000 |  | 9300000 | 9287765.3203 |  |  |  |  | 0 | 9287765.3203 | 10076166.0396 | -788400.7192 | -7.8244 | OK
17 | 33/11 kV 20/28 MVA T-3 |  | 33 | Main | 41812909544 | 1 | 973.4 | 1008.77 | 35.37 | 240000 |  | 8488800 | 8477632.5001 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 8477632.5001 | 8417518.2143 | 60114.2859 | 0.71416 | OK
|  |  | 33 | Backup | 41812909614 | 1 | 973.43 | 1008.8 | 35.37 | 240000 |  | 8488800 | 8477632.5001 |  |  |  |  | 0 | 8477632.5001 | 8417518.2143 | 60114.2859 | 0.71416 | OK
22 | 33/11 kV 10/14 MVA T-4 |  | 33 | Main | 41812909506 | 1 | 512.96 | 533.38 | 20.42 | 240000 |  | 4900800 | 4894352.7185 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 4894352.7185 | 5069152.7917 | -174800.0732 | -3.4483 | OK
|  |  | 33 | Backup | 41812909602 | 1 | 513.11 | 533.54 | 20.43 | 240000 |  | 4903200 | 4896749.5612 |  |  |  |  | 0 | 4896749.5612 | 5071542.7742 | -174793.213 | -3.4465 | OK
| 33 KV Feeders |  | 8: 0; 10: Total |  | 38262000 | 38211664.1599 |  |  |  |  | 33 KV Feeders | 38211664.1599 | 39710753.5176 | -1499089.3577 | -3.775 | OK
10 | 33 kV Shahriar Steel Feeder |  | 33 | Main | 41812909534 | 1 | 613.69 | 633.58 | 19.89 | 360000 |  | 7160400 | 7150980.086 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 7150980.086 | 7435235.4244 | -284255.3384 | -3.8231 | OK
|  |  | 33 | Backup | 41812909580 | 1 | 613.63 | 633.52 | 19.89 | 360000 |  | 7160400 | 7150980.086 |  |  |  |  | 0 | 7150980.086 | 7431650.4507 | -280670.3647 | -3.7767 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | A418S | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 |  | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 |  | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 |  | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Amulia Feeder |  | 33 | Main | 41812909523 | 1 | 4.89 | 17.72 | 12.83 | 360000 |  | 4618800 | 4612723.7056 |  |  |  |  | 33 kV Amulia Feeder | 4612723.7056 | 1498519.0007 | 3114204.7049 | 207.8188 | FAULT
|  |  | 33 | Backup | 41812909565 | 1 | 4.88 | 17.71 | 12.83 | 360000 |  | 4618800 | 4612723.7056 |  |  |  |  | 0 | 4612723.7056 | 1494934.027 | 3117789.6786 | 208.557 | FAULT
21 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 691.06 | 721.82 | 30.76 | 360000 |  | 11073600 | 11059032.0485 | Kazla |  |  |  | 33 kV Zahir Steel | 11059032.0485 | 10618692.0573 | 440339.9912 | 4.1468 | OK
|  |  | 33 | Backup | 41812909563 | 1 | 691.31 | 722.09 | 30.78 | 360000 |  | 11080800 | 11066222.5765 |  |  |  |  | 0 | 11066222.5765 | 10622277.031 | 443945.5455 | 4.1794 | OK
| Auxiliary Transformer-3 (AT-3) |  | 0.415 |  |  | 1 | 2645.13 | 2767.96 | 122.83 | 160 |  |  | 0 | [5 empty] | 0 | 0
|  |  | 10: Total |  | 22852800 | 22822735.8401 |  |  |  |  | 0 | 22822735.8401 | 19552446.4824 | 3270289.3577 | 16.7257 | OK
|  |  | 9=8-7: Grand Total | 61034400 | 61114800 | 61034400 | -0.13156
|  |  | 7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[7 empty] | KAZLA at 33 KV level |  |  | 18210012.1345
[7 empty] | Kazla 33/11 KV Substation |  |  | 42824387.8655
|  |  | 9=8-7: Total =; 10: 61034400 | 0
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK-61009 | 1 | 7965905 | 8029363 | 63458 | 180 | 11422440 |  | 11627083.7597
30 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK-61124 | 1 | 913432.2 | 963697.2 | 50265 | 180 | 9047700 |  | 9297352.691
24 | 33/11 kV 20/28 MVA T-3 Incoming |  | 11 |  | DHK-61015 | 1 | 532047.8 | 579080.9 | 47033.1 | 180 | 8465958 |  | 8477632.5001
39 | 33/11 kV 10/14 MVA T-4 Incoming |  | 11 |  | 8L55984 | 1 | 30493.8 | 31703 | 1209.2 | 4000 | 4836800 |  | 4894352.7185
42 | 33/11 kv 28/35 MVA T-5 Incomer |  | 11 |  | DHK00112 | 1 | 13959.7 | 18380.8 | 4421.1 | 888.8 | 3929473.68 |  | 3915242.4905
|  |  | 7: 0; 8: 0; 10: Total | 37702371.68 |  | 38211664.1599
| KAZLA 11 kV SIDE |  | 7: 0; 8: 0
17 | 11 kV Nayanagor Feeder | A418N | 11 |  | DHK-61125 | 1 | 904496 | 933689.8 | 29193.8 | 60 |  | 1751628 | 1775388.4538 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1775388.4538 | 1866468.623 | -91080.1692 | -4.8798 | OK
18 | 11 kV Madrasa Bazar Feeder | A418B | 11 |  | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1581226.92 | 1602675.9202 | Kazla | 130 | 180 |  | 11 kV Madrasa Bazar Feeder | 1602675.9202 | 1563148.5482 | 39527.372 | 2.5287 | OK
19 | 11 kV Kazla Feeder | A418K | 11 |  | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2675922.48 | 2712220.788 | Kazla | 220 | 120 |  | 11 kV Kazla Feeder | 2712220.788 | 2825691.6063 | -113470.8183 | -4.0157 | OK
20 | 11 kV Sayedabad Feeder | B218S | 11 |  | HA021101239-02 | 1 | 36964646 | 36964648 | 2 | 1000 | Estimated | 1216328.4 | 1232827.6309 | Maniknagar | 100 | 140 |  | 11 kV Sayedabad Feeder | 1232827.6309 | 1202421.9601 | 30405.6708 | 2.5287 | OK
21 | 11 kV Zenith Feeder | old | 11 |  | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | B318P | 11 |  | HA-021200060 | 1 | 118988.3 | 120971.5 | 1983.2 | 1000 |  | 1983200 | 2010101.6778 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 2010101.6778 | 2308939.6211 | -298837.9433 | -12.9426 | OK
23 | 11 kV Matuail Feeder | A418M | 11 |  | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1824492.6 | 1849241.4463 | Kazla | 150 |  |  | 11 kV Matuail Feeder | 1849241.4463 | 1803632.9402 | 45608.5061 | 2.5287 | OK
25 | 11 kV Kutubkhali Feeder | B326C | 11 |  | DHK-61117 | 1 | 798597.4 | 838596.4 | 39999 | 60 |  | 2399940 | 2432494.6655 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2432494.6655 | 2317847.2676 | 114647.3978 | 4.9463 | OK
26 | 11 kV Mridhabari Feeder | A418R | 11 |  | DHK-61118 | 1 | 674765.1 | 699957.1 | 25192 | 60 |  | 1511520 | 1532023.4409 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1532023.4409 | 1493309.739 | 38713.7019 | 2.5925 | OK
27 | 11 kV Muslim Nagar Feeder | A418U | 11 |  | DHK-61011 | 1 | 111124.4 | 154325.8 | 43201.4 | 60 |  | 2592084 | 2627245.0572 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2627245.0572 | 2655800.5175 | -28555.4603 | -1.0752 | OK
28 | 11 kV Jatrabari Thana Feeder | A418H | 11 |  | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | B518D | 11 |  | DHK-61008 | 1 | 316031.7 | 348875.3 | 32843.6 | 60 |  | 1970616 | 1997346.9786 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 1997346.9786 | 2119778.8003 | -122431.8217 | -5.7757 | OK
31 | 11 kV Mukti Sharani Feeder | B318T | 11 |  | DHK-61014 | 1 | 193957.2 | 213216.9 | 19259.7 | 60 |  | 1155582 | 1171257.2192 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 1171257.2192 | 2474942.6039 | -1303685.3848 | -52.6754 | CHECK
32 | 11 kV Kadamtali Feeder | B418K | 11 |  | DHK-61006 | 1 | 415256.6 | 452013.2 | 36756.6 | 60 |  | 2205396 | 2235311.7183 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 2235311.7183 | 2567504.4926 | -332192.7742 | -12.9384 | OK
33 | 11kV Rayerbagh Feeder | E218R | 11 |  | DHK-61012 | 1 | 424206.8 | 448270.6 | 24063.8 | 60 |  | 1443828 | 1463413.2136 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 1463413.2136 | 898785.6229 | 564627.5907 | 62.8212 | FAULT
34 | 11 kV Donia Feeder | B318D | 11 |  | DHK-61013 | 1 | 2047373 | 2084796 | 37423 | 60 | 351948 | 2245380 | 2275838.0926 | Jurain | Import from Matuail |  |  | 11 kV Donia Feeder | 2275838.0926 | 2097995.927 | 177842.1656 | 8.4768 | OK
35 | 11 kV Nimtoli Feeder | A418T | 11 |  | HA-021100855-02 | 1 | 32429125 | 34003353 | 1574228 | 1 |  | 1574228 | 1595582.0613 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1595582.0613 | 1529815.767 | 65766.2943 | 4.299 | OK
36 | 11 kV Gobindapur Feeder | A441G | 11 |  | HA-021101057-02 | 1 | 28077525 | 28747928 | 670403 | 1 |  | 670403 | 679496.8713 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 679496.8713 | 715534.2901 | -36037.4188 | -5.0364 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 |  | 9A56136 | 1 | 3626 | 3801 | 175 | 10000 |  | 1750000 | 1773738.3704 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1773738.3704 | 1822390.0739 | -48651.7035 | -2.6697 | OK
38 | 11 kV Samad Nagar Gate (Old) | old | 11 |  | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | A418D | 11 |  | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Dharmik Para | 0 | 0 | 0 | #DIV/0! | #DIV/0!
41 | 11 kV Sheikhdi Feeder | A418I | 11 |  | 9A56133 | 1 | 15959.8 | 16766 | 806.2 | 4000 |  | 3224800 | 3268543.7125 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 3268543.7125 | 3436798.8591 | -168255.1466 | -4.8957 | OK
43 | 11 kV Spare Feeder |  | 11 |  |  | 1 | 0 | 0 | 0 |  | T-5 Sum | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | A418Z | 11 |  | 61903661 | 1 | 22062 | 22659 | 597 | 2000 | 3898000 | 1194000 | 1210196.351 | Kazla | OMF Corrected |  |  | 11 kV Jenith Feeder | 1210196.351 | 1200080.6383 | 10115.7126 | 0.84292 | OK
45 | 11 KV Samad Nagor Gate | A418A | 11 |  | 61903675 | 1 | 19029 | 19683 | 654 | 2000 |  | 1308000 | 1325742.7363 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1325742.7363 | 1296103.4337 | 29639.3025 | 2.2868 | OK
46 | 11 KV Bibir Bagicha | B218I | 11 |  | 61903557 | 1 | 37768 | 38466 | 698 | 2000 |  | 1396000 | 1414936.4372 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 1414936.4372 | 1478955.3526 | -64018.9154 | -4.3287 | OK
47 | 33/0.4 kV AT-1 |  | 0.415 |  | 503043 | 1 | 96204 | 96204 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 |  | 0.415 |  | 503044 | 1 | 95386 | 95990 | 604 | 10 |  | 6040 | 6121.9313 | Kazla |  |  |  | 33/0.4 kV AT-2 | 6121.9313 | 14219.5459 | -8097.6146 | -56.9471 | CHECK
23 | Auxiliary Transformer |  | 0.415 |  | 41901920685 | 1 | 2645.13 | 2767.96 | 122.83 | 160 |  | 19652.8 | 19919.386 | Kazla |  |  |  | Auxiliary Transformer | 19919.386 | 20587.2873 | -667.9014 | -3.2442 | OK
|  |  | 10: Total | 38211664.1599 | 37700268.2 | 38211664.1599 | 1.3565
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Matuail | at 33 KV level |  | 1111465.2136
[6 empty] | Jurain | at 33 KV level |  | 8241639.655
[6 empty] | Swamibag | at 33 KV level |  | 1997346.9786
[6 empty] | Maniknagar | at 33 KV level |  | 2647764.0681
[6 empty] | Shyampur | at 33 KV level |  | 2235311.7183
[6 empty] | Kazla | at 33 KV level |  | 21978136.5263
[6 empty] | Total = |  |  | 38211664.1599 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT |  | 132 |  | 8993532 | 1 | 2227.617 | 2229.915 | 2.298 | 960000 | 0 | 2206080
|  |  | 132 |  |  | 1 | 666.689 | 667.19 | 0.501 | 960000 | 480960 | 0
1 | Tranformer - 1 at Shyampur 230/132 |  | 132 |  | 38992560 | 1 | 1511.889 | 1553.392 | 41.503 | 1920000 | 0 | 79685760
|  |  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 |  | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  |  | 132 |  | 38992559 | 1 | 1602.462 | 1643.73 | 41.268 | 1920000 | 0 | 79234560
| Aggrekko 100 MW (Brammhongao) |  | 132 |  | PN-1711A04601 | 1 | 363.871 | 363.871 | 0 | 960000 | 0 | 0
|  |  | 132 |  |  | 1 | 5.419 | 5.419 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Exp |  | 132 |  | 38992544 | 1 | 32.492 | 33.497 | 1.005 | 960000 | 0 | 964800
| Madanganj-Fatullah Imp |  | 132 |  | 38992544 | 1 | 33.196 | 66.461 | 33.265 | 960000 | 31934400 | 0
|  |  | 9=8-7: Total Import/Export | 32415360 | 162091200
|  |  | 10: Net Total | 129675840
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) |  | 132 | Import | 08993727 | 1 | 9201.93 | 9268.339 | 66.409 | 720000 | 47814480
|  |  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) |  | 132 | Import | 08993726 | 1 | 6935.786 | 6991.138 | 55.352 | 720000 | 39853440
|  |  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 87667920 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 87667920
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
|  |  | 132 |  |  |  | 0 | 0
|  |  | 132 |  |  |  | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 41640000
| SHYAMPUR 132 KV SIDE |  | 7: 0; 8: 0
5 | 132 kV 80/120 MVA ( GT-1) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) |  | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) |  | 132 | Export | ABB3902 | 1 | 2333384.4 | 2486388.1 | 153003.7 | 1300 |  | 198904810
|  |  | 10: Total |  | 46027920
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 4: 129675840; 6: EXPORT TO OTHER S/S; 9=8-7: 41640000 | 132 KV NET IMPORT |  | 88035840
| IMPORT-2 |  | 6: 132 KV NET IMPORT; 9=8-7: 88035840 | 33 KV NET IMPORT |  | 87743472
| IMPORT-3 | [9 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 292368
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.3321%
| 132 KV TOTAL IMPORT |  | 4: 129675840
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) |  | 33 | Import | BD001826 | 1 | 3465.632 | 3507.3328 | 41.7008 | 480000 | 20016384
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) |  | 33 | Import | BD001850 | 1 | 3520.739 | 3562.5122 | 41.7732 | 480000 | 20051136
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) |  | 33 | Import | BD001835 | 1 | 3023.939 | 3073.5188 | 49.5798 | 480000 | 23798304
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) |  | 33 | Import | BD001831 | 1 | 3907.135 | 3956.8801 | 49.7451 | 480000 | 23877648
|  |  | 7: 0; 8: 0; 10: Total | 87743472
| SHYAMPUR 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) |  | 33 | Export | BD001808 | 1 | 2177.041 | 2208.0439 | 31.0029 | 240000 |  | 7440696 | 7438340.1673 |  | 25685545.0066 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7438340.1673 | 6814502.8244 | 623837.3429 | 9.1546 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) |  | 33 | Export | BD001834 | 1 | 1989.027 | 2019.887 | 30.86 | 240000 |  | 7406400 | 7404055.0259 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7404055.0259 | 6785468.1808 | 618586.8451 | 9.1163 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) |  | 33 | Export | BD001846 | 1 | 1473.18 | 1500.2162 | 27.0362 | 240000 |  | 6488688 | 6486633.5869 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 6486633.5869 | 5855159.809 | 631473.7778 | 10.7849 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) |  | 33 | Export | BD001847 | 1 | 1321.957 | 1340.1149 | 18.1579 | 240000 |  | 4357896 | 4356516.2266 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 4356516.2266 | 4666659.07 | -310142.8433 | -6.6459 | OK
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 25693680 | 25685545.0066 |  |  |  |  | 33 KV Feeders | 25685545.0066 | 24121789.8842 | 1563755.1224 | 6.4827 | OK
1 | 33 kV Rani RRM Feeder |  | 33 | Export | BD001809 | 1 | 749.791 | 760.393 | 10.602 | 240000 |  | 2544480 | 2543674.3806 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 2543674.3806 | 3093749.2487 | -550074.8682 | -17.7802 | OK
2 | 33 kV Postogola Feeder-1. |  | 33 | Export | BD001804 | 1 | 1564.542 | 1564.544 | 0.002 | 240000 |  | 480 | 479.848 |  | 479.848 | Postogola 33/11 kv s/s | Grid Has No Reading | 33 kV Postogola Feeder-1. | 479.848 | 23.9956 | 455.8525 | 1899.7356 | FAULT
5 | 33 kV Prime Textile Feeder. |  | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1337.202 | 1366.304 | 29.102 | 240000 | From Downstream | 6984480 | 6982268.6119 |  | 12774154.2357 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 6982268.6119 | 7055178.4232 | -72909.8114 | -1.0334 | OK
7 | 33 kV Nondolalpur -2 feeder |  | 33 | Export | BD001807 | 1 | 1156.66 | 1180.8005 | 24.1405 | 240000 |  | 5793720 | 5791885.6239 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 5791885.6239 | 5586913.2966 | 204972.3273 | 3.6688 | OK
8 | 33 kV Postogola Feeder-2. |  | 33 | Export | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Postogola Feeder-2. | 0 | 23.9956 | -23.9956 | -100 | CHECK
11 | 33 kV Rahima Steel feeder |  | 33 | Export | BD001803 | 1 | 654.799 | 656.416 | 1.617 | 240000 |  | 388080 | 387957.1282 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 387957.1282 | 1848762.9304 | -1460805.8022 | -79.0153 | CHECK
12 | 33 kV Salam Steel Feeder |  | 33 | Export | BD001849 | 1 | 1212.322 | 1251.608 | 39.286 | 240000 |  | 9428640 | 9425654.7552 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 9425654.7552 | 6942639.1851 | 2483015.5702 | 35.7647 | OK
13 | 33 kV Fatullah Feeder-2. |  | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 1073036.1535 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2608.969 | 2644.437 | 35.468 | 240000 |  | 8682566.4 | 8679817.373 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8679817.373 | 7598658.9591 | 1081158.4139 | 14.2283 | OK
17 | 33 kV Akhter Steel Feeder |  | 33 | Export | BD001828 | 1 | 686.506 | 690.9784 | 4.4724 | 240000 | Prime Textile | 1073376 | 1073036.1535 | Fatullah | 19563778.261 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 1073036.1535 | 1039008.3182 | 34027.8353 | 3.275 | OK
18 | 33 kV Steel Famus feeder |  | 33 | Export | BD001806 | 1 | 145.878 | 153.6104 | 7.7324 | 240000 |  | 1855776 | 1855188.4343 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1855188.4343 | 668060.7526 | 1187127.6817 | 177.6976 | FAULT
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.896 | 1544.8992 | 0.0032 | 240000 |  | 768 | 767.7568 |  | 767.7568 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 767.7568 | 1439.7344 | -671.9776 | -46.6737 | CHECK
20 | 33 kV Rani Kamal Steel Feeder |  | 33 | Export | BD001829 | 1 | 1569.566 | 1593.2569 | 23.6909 | 240000 |  | 5685816 | 5684015.7878 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 5684015.7878 | 6636959.5785 | -952943.7906 | -14.3581 | OK
23 | 33 kV Shyampur BSCIC-2. |  | 33 | Export | BD001827 | 1 | 2544.947 | 2590.3112 | 45.3642 | 240000 |  | 10887408 | 10883960.888 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 10883960.888 | 9771237.3503 | 1112723.5378 | 11.3877 | OK
24 | 33 kV Chakda Steel Feeder |  | 33 | Export | BD001832 | 1 | 2441.53 | 2477.8933 | 36.3633 | 240000 |  | 8727192 | 8724428.8439 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 8724428.8439 | 9042995.7002 | -318566.8563 | -3.5228 | OK
23 | Aux Tr-1 |  | 0.44kv | Export | DHKG9742 | 1.025 | 347.544 | 349.667 | 2.123 | 2400 |  | 5222.58 | 5222.58 | Fatullah
24 | Aux Tr-2 |  | 0.44kv | Export | DHKG9743 | 1.025 | 109.988 | 117.946 | 7.958 | 2400 |  | 19576.68 | 19576.68 | Fatullah
|  |  | 10: Total |  | 62077581.66 | 62057934.8452 |  |  |  |  | 0 | 62057934.8452 | 59308598.3484 | 2749336.4968 | 4.6356 | OK
|  |  | 9=8-7: Grand Total | 87743472 | 87771261.66 | 87743479.8518 | -0.031653
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 28620919.33
[6 empty] | Fatullah | at 33 KV level |  | 1097835.4135
[7 empty] | Export to Other SS |  | 58024725.1083
[6 empty] | Total = |  |  | 87743479.8518 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 |  | 11 | Import | BD001926 | 1 | 2954.76 | 3001.13 | 46.37 | 160000 | 7419200 |  | 7443992.0122 |  | 7419200
16 | 11 kV 20/28 MVA Transformer-2 |  | 11 |  | BD001952 | 1 | 2966.78 | 3012.88 | 46.1 | 160000 | 7376000 |  | 7400647.655
27 | 11 kV20/28 MVA Transformer-3 |  | 11 |  | BD001927 | 1 | 2074.33 | 2114.71 | 40.38 | 160000 | 6460800 |  | 6482389.421 |  | 1800000
36 | 11 kV 20/28 MVA Transformer-4 |  | 11 |  | BD001927 | 1 | 1978.21 | 2005.36 | 27.15 | 160000 | 4344000 |  | 4358515.9183 |  | 1800000
|  |  | 7: 0; 8: 0; 10: Total | 25600000 |  | 25685545.0066
| SHYAMPUR 11 kV SIDE |  | 7: 0; 8: 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur |  | 1 | 707.49 | 752.49 | 45 | 40000 |  | 1800000 | 1814264.1154 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1814264.1154 | 1610415.5328 | 203848.5826 | 12.6581 | OK
6 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | B426E | 11 |  | BD001943 | 1 | 1071.17 | 1085.02 | 13.85 | 40000 |  | 554000 | 558390.1777 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 558390.1777 | 490213.532 | 68176.6458 | 13.9075 | OK
8 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1561.8 | 1583.91 | 22.11 | 40000 |  | 884400 | 891408.4354 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 891408.4354 | 575920.7998 | 315487.6355 | 54.7797 | FAULT
10 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1454.49 | 1473.51 | 19.02 | 40000 |  | 760800 | 766828.9661 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 766828.9661 | 770964.9094 | -4135.9433 | -0.53646 | OK
11 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1365.13 | 1390.8 | 25.67 | 40000 |  | 1026800 | 1034936.8854 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 1034936.8854 | 1058124.3068 | -23187.4214 | -2.1914 | OK
12 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3398.03 | 3458.08 | 60.05 | 40000 |  | 2402000 | 2421034.6696 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2421034.6696 | 2293670.6681 | 127364.0015 | 5.5528 | OK
13 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2212.37 | 2255.93 | 43.56 | 40000 |  | 1742400 | 1756207.6637 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1756207.6637 | 1462630.5709 | 293577.0928 | 20.0719 | OK
15 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 492.99 | 496.84 | 3.85 | 40000 |  | 154000 | 155220.3743 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 155220.3743 | 135769.9243 | 19450.45 | 14.326 | OK
17 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3222.54 | 3269.99 | 47.45 | 40000 |  | 1898000 | 1913040.7173 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1913040.7173 | 1822681.1962 | 90359.5211 | 4.9575 | OK
18 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2013.89 | 2051.33 | 37.44 | 40000 |  | 1497600 | 1509467.744 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1509467.744 | 1396147.3632 | 113320.3809 | 8.1166 | OK
19 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1509.68 | 1523.24 | 13.56 | 40000 |  | 542400 | 546698.2534 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 546698.2534 | 888712.2774 | -342014.0239 | -38.4842 | OK
20 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 845.91 | 864.46 | 18.55 | 40000 |  | 742000 | 747879.9854 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 747879.9854 | 273141.8536 | 474738.1318 | 173.8064 | FAULT
22 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1352.04 | 1370.29 | 18.25 | 40000 |  | 730000 | 735784.8913 | Shyampur |  |  |  | 11 kV Delpara Feeder | 735784.8913 | 764156.3881 | -28371.4968 | -3.7128 | OK
23 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3136.88 | 3205.07 | 68.19 | 40000 |  | 2727600 | 2749214.8896 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2749214.8896 | 3128315.2765 | -379100.3869 | -12.1184 | OK
24 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1114.7 | 1121.46 | 6.76 | 40000 |  | 270400 | 272542.7871 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 272542.7871 | 255119.2973 | 17423.4898 | 6.8295 | OK
26 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2017.21 | 2055.4 | 38.19 | 40000 |  | 1527600 | 1539705.4793 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1539705.4793 | 1292017.0377 | 247688.4415 | 19.1707 | OK
28 | 11 kV Spare Feeder | spare | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1390.26 | 1411.57 | 21.31 | 40000 |  | 852400 | 859154.8511 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 859154.8511 | 801803.5058 | 57351.3454 | 7.1528 | OK
30 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1358.68 | 1384.37 | 25.69 | 40000 |  | 1027600 | 1035743.225 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 1035743.225 | 446558.8956 | 589184.3294 | 131.9388 | FAULT
31 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2314.14 | 2351.37 | 37.23 | 40000 |  | 1489200 | 1501001.1782 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1501001.1782 | 1526310.2699 | -25309.0918 | -1.6582 | OK
35 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 174.8 | 175.82 | 1.02 | 40000 |  | 40800 | 41123.3199 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 41123.3199 | 3604.5113 | 37518.8087 | 1040.8848 | FAULT
37 | 11 kV Spare Feeder | spare | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1234.74 | 1256.25 | 21.51 | 40000 |  | 860400 | 867218.2472 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 867218.2472 | 889112.7786 | -21894.5314 | -2.4625 | OK
39 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3772.66 | 3812.96 | 40.3 | 40000 |  | 1612000 | 1624774.3078 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 1624774.3078 | 1797850.1185 | -173075.8107 | -9.6268 | OK
40 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1119.74 | 1128.27 | 8.53 | 40000 |  | 341200 | 343903.8423 | Shyampur |  |  |  | 11 kV Igloo Feeder | 343903.8423 | 438548.8705 | -94645.0282 | -21.5814 | OK
41 | 11/0.4 kV Aux Transformer, T-1 |  | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) |  | 0.415 | DPDC | DHK26108 | 1 | 64792.6 | 65260.8 | 468.2 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) |  | 0.415 |  |  | 1 | 611666 | 619265 | 7599 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 |  | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 10: Total | 25685545.0066 | 25483600 | 25685545.0066 | 0.79245
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Fatullah | at 33 KV level |  | 1190157.2597
[6 empty] | Shyampur | at 33 KV level |  | 24495387.7469
[6 empty] | Total = |  |  | 25685545.0066 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. |  | 33 | Export | BD001805 | 1.02 | 2608.969 | 2644.437 | 35.468 | 240000 | 0 | 8682566.4 | 8679817.373
23 | 33 kV Shyampur BSCIC-2. |  | 33 |  | BD001827 | 1 | 2544.947 | 2590.3112 | 45.3642 | 240000 | 0 | 10887408 | 10883960.888
|  |  | 10: Total | 0 | 19569974.4 | 19563778.261
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 |  | 33 | Import | DHK61071 | 1 | 975540.8 | 1006470.9 | 30930.1 | 270 | 8351127
5 | 33 kV Shyampur Circuit-2 |  | 33 | Import | DHK61067 | 1 | 784722.4 | 824440.7 | 39718.3 | 270 | 10723941
|  |  | 7: 0; 8: 0; 10: Total | 19075068 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  | 7: 0; 8: 0
2 | 33 kV 20/28 MVA Transformer-1 |  | 33 | Export | DHK61068 | 1 | 977870.5 | 1024311.6 | 46441.1 | 180 |  | 8359398
3 | 33 kV 20/28 MVA Transformer-2 |  | 33 | Export | DHK61066 | 1 | 670460.2 | 730036.7 | 59576.5 | 180 |  | 10723770
|  |  | 10: Total |  | 19083168 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| 33 KV SIDE |  | 4: 19563778.261; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 19563778.261
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 19563778.261 | 33 KV TX HV SIDE |  | 19083168
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 480610.261
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 2.457%
| TOTAL IMPORT |  | 4: 19563778.261
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming |  | 11 |  | DHK61019 | 1.05 | 1048255.9 | 1048255.9 | 0 | 180 | 0 |  | 0 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK61018 | 1 | 791013.6 | 849520.6 | 58507 | 180 | 10531260 |  | 19563778.261
|  |  | 7: 0; 8: 0; 10: Total | 10531260 |  | 19563778.261
| SHYAMPUR BISIC 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Nama shyampur Feeder |  | 11 | Shympur | HA-021101066-02 | 1 | 42309350 | 44443826 | 2134476 | 1 |  | 2134476 | 2124178.3588 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 2124178.3588 | 2141060 | -16881.6412 | -0.78847 | OK
2 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 22873022 | 23612106 | 739084 | 1 |  | 739084 | 735518.3371 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 735518.3371 | 786111 | -50592.6629 | -6.4358 | OK
3 | 11 kV H. R Steel |  | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) |  | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 498635.8 | 528325.7 | 29689.9 | 60 |  | 1781394 | 1772799.78 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1772799.78 | 1740318 | 32481.78 | 1.8664 | OK
6 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 642966.5 | 668712.2 | 25745.7 | 60 |  | 1544742 | 1537289.4923 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1537289.4923 | 1379322 | 157967.4923 | 11.4525 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 661715.4 | 685766.2 | 24050.8 | 60 |  | 1443048 | 1436086.1084 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1436086.1084 | 1338426 | 97660.1084 | 7.2966 | OK
8 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 385320 | 403627.9 | 18307.9 | 60 |  | 1098474 | 1093174.4833 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1093174.4833 | 818646 | 274528.4833 | 33.5345 | OK
9 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 518062.2 | 521552.7 | 3490.5 | 60 |  | 209430 | 208419.6185 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 208419.6185 | 288 | 208131.6185 | 72267.9231 | FAULT
12 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 967640.9 | 1012323.7 | 44682.8 | 60 |  | 2680968 | 2668033.8435 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2668033.8435 | 2872542 | -204508.1565 | -7.1194 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 304035.4 | 328026.8 | 23991.4 | 60 |  | 1439484 | 1432539.3027 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1432539.3027 | 1270602 | 161937.3027 | 12.7449 | OK
14 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 475560.2 | 498710.3 | 23150.1 | 60 |  | 1389006 | 1382304.8305 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 1382304.8305 | 530982 | 851322.8305 | 160.3299 | FAULT
15 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 617165.5 | 659724.2 | 42558.7 | 60 |  | 2553522 | 2541202.6985 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2541202.6985 | 2715606 | -174403.3015 | -6.4223 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 881811.3 | 894406.3 | 12595 | 60 |  | 755700 | 752054.1743 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 752054.1743 | 714972 | 37082.1743 | 5.1865 | OK
17 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 8046.7 | 38811.9 | 30765.2 | 60 |  | 1845912 | 1837006.5171 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1837006.5171 | 1401510 | 435496.5171 | 31.0734 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB7380 | 1 | 615780 | 659160 | 43380 | 1 |  | 43380 | 43170.716 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 43170.716 | 3507 | 39663.716 | 1130.9871 | FAULT
| SUB-Station not match |  | 10: Grand Total | 19563778.261 | 19658620 | 19563778.261 | -0.48244 |  |  |  | SUB-Station not match
| bscic 33/11 kv ss | [16 empty] | bscic 33/11 kv ss
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 6530069.3779
[6 empty] | Jurain | at 33 KV level |  | 13033708.8831
[6 empty] | Total = |  |  | 19563778.261 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder |  | 33 | Export | BD001801 | 1 | 1337.202 | 1366.304 | 29.102 | 240000 | From Downstream | 6984480 | 6982268.6119
7 | 33 kV Nondolalpur -2 feeder |  | 33 |  | BD001807 | 1 | 1156.66 | 1180.8005 | 24.1405 | 240000 | 0 | 5793720 | 5791885.6239
|  |  | 10: Total | 0 | 12778200 | 12774154.2357
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) |  | 33 | Import | 00000084 | 1 | 320910976 | 327871524 | 6960548 | 1 | 6960548
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) |  | 33 | Import | 00000070 | 1 | 298144800 | 303934336 | 5789536 | 1 | 5789536
|  |  | 7: 0; 8: 0; 10: Total | 12750084 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| NANDALALPUR 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 28/35 MVA T-1 |  | 33 | Export | 00000086 | 1 | 321100736 | 328057280 | 6956544 | 1 |  | 6956544
5 | 33 kV, 28/35 MVA T-2 |  | 33 | Export | 00000083 | 1 | 297584832 | 303371200 | 5786368 | 1 |  | 5786368
|  |  | 10: Total |  | 12742912 | 0
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 4: 12774154.2357; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 12774154.2357
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 12774154.2357 | 33 KV TX HV SIDE |  | 12742912
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 31242.2357
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 0.2446%
| TOTAL IMPORT |  | 4: 12774154.2357
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. |  | 11 |  | 00000036 | 1 | 319187360 | 326114944 | 6927584 | 1 | 6927584 |  | 6973427.8309 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming |  | 11 |  | 00000033 | 1 | 296293152 | 302055744 | 5762592 | 1 | 5762592 |  | 5800726.4049
|  |  | 7: 0; 8: 0; 10: Total | 12690176 |  | 12774154.2357
| NANDALALPUR 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV Spare | spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | B889Z | 11 |  | 00000026 | 1 | 6767583 | 7422622 | 655039 | 1 |  | 655039 | 656635.1076 | Fatullah |  |  |  | 11 kV Khaza Moinuddin | 656635.1076 | 680847.6789 | -24212.5713 | -3.5562 | OK
10 | 11 kV Chitashal | B489Q | 11 |  | 00000027 | 1 | 34722676 | 35456592 | 733916 | 1 |  | 733916 | 735704.304 | Shyampur |  |  |  | 11 kV Chitashal | 735704.304 | 743621.9237 | -7917.6197 | -1.0647 | OK
11 | 11 kV Local Feeder | B489G | 11 |  | 00000157 | 1.5 | 18844474 | 19031274 | 186800 | 1 | Estimated | 668980.62 | 670610.6986 | Shyampur | 55 |  |  | 11 kV Local Feeder | 670610.6986 | 650428.6635 | 20182.035 | 3.1029 | OK
12 | 11 kV Rasel Germants |  | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 |  | 00000121 | 1 | 78230880 | 80634160 | 2403280 | 1 |  | 2403280 | 2409135.9772 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2409135.9772 | 2474142.3426 | -65006.3655 | -2.6274 | OK
14 | 11 kV Nandalalpur | B890X | 11 |  | 00000010 | 1 | 85321072 | 86136912 | 815840 | 1 |  | 815840 | 817827.925 | Fatullah |  |  |  | 11 kV Nandalalpur | 817827.925 | 726019.9781 | 91807.9469 | 12.6454 | OK
15 | 11 kV Sharif Bagh | B489SB | 11 |  | 00000132 | 1 | 75334576 | 77028008 | 1693432 | 1 |  | 1693432 | 1697558.3187 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1697558.3187 | 1769871.618 | -72313.2993 | -4.0858 | OK
18 | 11 kV Spare | spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | B890Y | 11 |  | 00000158 | 1 | 67337432 | 68472832 | 1135400 | 1 |  | 1135400 | 1138166.5842 | Fatullah |  |  |  | 11 KV Nayamati | 1138166.5842 | 1094447.1869 | 43719.3973 | 3.9947 | OK
20 | 11 kV Pulpar | B889S | 11 |  | 00000160 | 1 | 9343257 | 10315015 | 971758 | 1 |  | 971758 | 974125.8442 | Fatullah |  |  |  | 11 kV Pulpar | 974125.8442 | 814027.697 | 160098.1472 | 19.6674 | OK
21 | 11 kV Shahi Bazar | B489X | 11 |  | 00000170 | 1 | 42551376 | 43318576 | 767200 | 1 |  | 767200 | 769069.4058 | Shyampur |  |  |  | 11 kV Shahi Bazar | 769069.4058 | 789833.0592 | -20763.6533 | -2.6289 | OK
22 | 11 kV Pagla Bazar | B890G | 11 |  | 00000060 | 1 | 51571436 | 52221152 | 649716 | 1 |  | 649716 | 651299.1372 | Fatullah |  |  |  | 11 kV Pagla Bazar | 651299.1372 | 675946.8632 | -24647.726 | -3.6464 | OK
23 | 11 kV Delpara bazar | B489M | 11 |  | 00000063 | 1 | 82332920 | 83841392 | 1508472 | 1 |  | 1508472 | 1512147.634 | Shyampur |  |  |  | 11 kV Delpara bazar | 1512147.634 | 1531851.518 | -19703.884 | -1.2863 | OK
24 | 11 kV Bhuighor (Board mill) | E289C | 11 |  | 00000146 | 1 | 45140688 | 45875048 | 734360 | 1 |  | 734360 | 736149.3859 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 736149.3859 | 684221.3852 | 51928.0007 | 7.5894 | OK
25 | 11 kV Spare |  | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 |  | 11 |  | 7803 | 1 | 2552 | 2600 | 48 | 100 |  | 4800 | 4811.696 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 4811.696 | 5827.1281 | -1015.4322 | -17.4259 | OK
27 | 33/0.415 kV, 200 kVA AT-2 |  | 11 |  | 7805 | 1 | 62 | 71.1 | 9.1 | 100 |  | 910 | 912.2174 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 912.2174 | 1004.6773 | -92.4599 | -9.2029 | OK
|  |  | 10: Grand Total | 12774154.2357 | 12743103.62 | 12774154.2357 | 0.24367
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Shyampur | at 33 KV level |  | 5390814.2744
[6 empty] | Fatullah | at 33 KV level |  | 4238054.5982
[6 empty] | Matuail | at 33 KV level |  | 3145285.3631
[6 empty] | Total = |  |  | 12774154.2357 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 |  | 132 | Import | 4262 7826 | 1 | 349.978 | 378.796 | 28.818 | 960000 | 0 | 27665280
[6 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 |  | 132 |  | 4262 7815 | 1 | 150.919 | 159.248 | 8.329 | 960000 | 0 | 7995840
2 | [5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
|  |  | 9=8-7: Total Import/Export | 0 | 35661120
|  |  | 10: Net Total | 35661120
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 |  | 132 | Main | 41808902823 | 1 | 279.79 | 302.81 | 23.02 | 1200000 | 27624000
|  |  | 132 | Backup | 41808904269 | 1 | 279.79 | 302.81 | 23.02 | 1200000 | 27624000
4 | 132kV Hasnabad Circuit-2 |  | 132 | Imp/Main | 41808902845 | 1 | 120.64 | 127.29 | 6.65 | 1200000 | 7980000
|  |  | 132 | Imp/Backup | 41808904256 | 1 | 120.64 | 127.29 | 6.65 | 1200000 | 7980000
|  |  | 7: 0; 8: 0; 9=8-7: Total Import/Export | 35604000 | 0
|  |  | 7: 0; 8: 0; 9=8-7: Net Total | 35604000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 132; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
| POSTOGOLA 132 KV SIDE |  | 7: 0; 8: 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) |  | 132 | Exp/Main | 41808902871 | 1 | 290.91 | 313.92 | 23.01 | 1200000 |  | 27612000
|  |  | 132 | Exp/Backup | 41808904257 | 1 | 290.91 | 313.92 | 23.01 | 1200000 |  | 27612000
5 | 132/33 kV 80/120 MVA GT-2 (HV) |  | 132 | Exp/Main | 41808902846 | 1 | 109.36 | 116.02 | 6.66 | 1200000 |  | 7992000
|  |  | 132 | Exp/Backup | 41808904243 | 1 | 109.36 | 116.02 | 6.66 | 1200000 |  | 7992000
|  |  | 10: Total |  | 35604000
| 132 KV IMPORT |  | 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 4: 35661120; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 35661120
|  |  | 6: 132 KV NET IMPORT; 9=8-7: 35661120 | 33 KV NET IMPORT |  | 35496000
[11 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 165120
[11 empty] | LOSS % IN => |  | 0.463%
| 132 KV TOTAL IMPORT |  | 4: 35661120
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE |  | 10: Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) |  | 33 | Main | 41808902807 | 1 | 483.17 | 521.43 | 38.26 | 720000 | 27547200
|  |  | 33 | Backup | 41808904286 | 1 | 483.17 | 521.43 | 38.26 | 720000 | 27547200
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) |  | 33 | Main | 41808902869 | 1 | 181.04 | 192.08 | 11.04 | 720000 | 7948800
|  |  | 33 | Backup | 41808904268 | 1 | 181.04 | 192.08 | 11.04 | 720000 | 7948800
|  |  | 7: 0; 8: 0; 10: Total | 35496000 |  | 0
| POSTOGOLA 33 kV SIDE |  | 7: 0; 8: 0
| 33/11 KV Transforfers |  | 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 |  | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss |  | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 |  | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders |  | 7: 0; 8: 0; 10: Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 449 | 475.3 | 26.3 | 360000 |  | 9468000 | 9468000 |  | 17049600 | IG Gate 33/11 kv ss |  | 33 kV IG Gate Ckt-2 | 9468000 | 10632838.4279 | -1164838.4279 | -10.9551 | OK
|  |  | 33 | Backup | 41808904225 | 1 | 449 | 475.3 | 26.3 | 360000 |  | 9468000 | 9468000 |  |  |  |  | 0 | 9468000 | 10632838.4279 | -1164838.4279 | -10.9551 | OK
8 | 33 kV Spare Feeder 2 |  | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 |  | 33 | Main | 41808902810 | 1 | 518.06 | 569.3 | 51.24 | 360000 |  | 18446400 | 18446400 |  |  |  |  | 33kV Postogola circuit-1 | 18446400 | 18437449.7817 | 8950.2183 | 0.048544 | OK
|  |  | 33 | Backup | 41808904252 | 1 | 518.06 | 569.3 | 51.24 | 360000 |  | 18446400 | 18446400 |  |  |  |  | 0 | 18446400 | 18437449.7817 | 8950.2183 | 0.048544 | OK
14 | 31 kV Spare Feeder 4 |  | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 |  | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 |  | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1 | 361.64 | 382.7 | 21.06 | 360000 |  | 7581600 | 7581600 |  |  |  |  | 33 kV IG Gate Ckt-1 | 7581600 | 8009711.7904 | -428111.7904 | -5.3449 | OK
|  |  | 33 | Backup | 41812909573 | 1 | 361.64 | 382.7 | 21.06 | 360000 |  | 7581600 | 7581600 |  |  |  |  | 0 | 7581600 | 8009711.7904 | -428111.7904 | -5.3449 | OK
|  |  | 10: Total |  | 35496000 | 35496000 |  |  |  |  | 0 | 35496000 | 37080000 | -1584000 | -4.2718 | OK
|  |  | 9=8-7: Grand Total | 35496000 | 35496000 | 35496000 | -1.0495e-13
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola |  | 33 | Import | BD001804 | 1 | 518.06 | 569.3 | 51.24 | 360000 | 18446400 |  | 18446400
2 | 33 kV Postogola Circuit-2 at Shyampur |  | 33 | Import | BD001830 | 1 | 2131.896 | 2131.896 | 0 | 240000 | 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total | 18446400 |  | 18446400
| POSTOGOLA 33 KV SIDE (RECEIVING) |  | 7: 0; 8: 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) |  | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) |  | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
|  |  | 7: 0; 8: 0; 10: Total | 0
| POSTOGOLA 33 KV SIDE |  | 7: 0; 8: 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK61027 | 1 | 333819 | 376993.6 | 43174.6 | 180 |  | 7771428 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60870 | 1 | 787296.8 | 846711.4 | 59414.6 | 180 |  | 10694628
|  |  | 7: 0; 8: 0; 10: Total |  | 18466056
| POSTOGOLA 11 KV SIDE |  | 7: 0; 8: 0
8 | 11 kV 20/28 MVA T-1 Incoming. |  | 11 |  | DHK61005 | 1.165 | 916064.8 | 954321.5 | 38256.7 | 180 | 8022429.99 |  | 7953233.829 |  | 36932112
9 | 11 kV 20/28 MVA T-2 Incoming |  | 11 |  | DHK60861 | 1.165 | 988005.6 | 1038479.9 | 50474.3 | 180 | 10584460.71 |  | 10493166.171
|  |  | 7: 0; 8: 0; 10: Total | 18606890.7 |  | 18446400
| POSTOGOLA 11 kV SIDE |  | 7: 0; 8: 0 | [5 empty] | 70
1 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 64899212 | 66131524 | 1232312 | 1 |  | 1232312 | 1255334.9139 | Postogola |  | 10 |  | 11 kV Station Road Feeder | 1255334.9139 | 1334586.3999 | -79251.486 | -5.9383 | OK
2 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | HA021100501-02 | 1 | 10944921 | 10944921 | 0 | 1 | Estimated | 1216328.4 | 1239052.6971 | Jurain | 100 | 60 |  | 11 kV Samon & Sons Feeder. | 1239052.6971 | 1255387.5265 | -16334.8293 | -1.3012 | OK
3 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 25117608 | 25644920 | 527312 | 1 |  | 527312 | 537163.6113 | Jurain |  | 20 |  | 11 kV Alam Bagh Feeder. | 537163.6113 | 519931.6597 | 17231.9516 | 3.3143 | OK
4 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 77506907 | 79011228 | 1504321 | 1 |  | 1504321 | 1532425.7761 | Postogola |  | 30 |  | 11 kV Majar O/H Feeder | 1532425.7761 | 1609308.7492 | -76882.973 | -4.7774 | OK
5 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 450849.6 | 461916 | 11066.4 | 60 |  | 663984 | 676389.0131 | Postogola |  |  |  | 11 kV Cyca Feeder | 676389.0131 | 678803.9555 | -2414.9424 | -0.35576 | OK
6 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 906382.3 | 925873.2 | 19490.9 | 60 |  | 1169454 | 1191302.5568 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 1191302.5568 | 1270287.67 | -78985.1132 | -6.2179 | OK
7 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 794197.3 | 814922.6 | 20725.3 | 60 |  | 1243518 | 1266750.2722 | Postogola |  |  |  | 11 kV Munshi Bari | 1266750.2722 | 1384014.8487 | -117264.5764 | -8.4728 | OK
8 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 524334.2 | 526393.2 | 2059 | 60 |  | 123540 | 125848.0606 | Postogola |  |  |  | 11 kV Cantonment Feeder | 125848.0606 | 126732.5803 | -884.5196 | -0.69794 | OK
9 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 881725.3 | 905082.3 | 23357 | 60 |  | 1401420 | 1427602.3077 | Postogola |  |  |  | 11 kV DIT Feeder. | 1427602.3077 | 1330189.3065 | 97413.0012 | 7.3232 | OK
10 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 405545.3 | 445618.9 | 40073.6 | 60 |  | 2404416 | 2449336.9799 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 2449336.9799 | 2475377.6895 | -26040.7096 | -1.052 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 42901124 | 45310492 | 2409368 | 1 |  | 2409368 | 2454381.4966 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 2454381.4966 | 2115704.7964 | 338676.7002 | 16.0077 | OK
12 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 13201.1 | 15592.1 | 2391 | 1000 |  | 2391000 | 2435670.3328 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2435670.3328 | 2485795.0121 | -50124.6793 | -2.0164 | OK
13 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 59377915 | 60970541 | 1592626 | 1 |  | 1592626 | 1622380.5518 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1622380.5518 | 1682719.5891 | -60339.0373 | -3.5858 | OK
14 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | HA021100681-02 | 1 | 53444745 | 53444745 | 0 | 1 | Estimated | 243265.68 | 247810.5394 | Postogola | 20 |  |  | 11 kV Rajabari Feeder. | 247810.5394 | 239121.4336 | 8689.1058 | 3.6338 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 |  | 11 |  | ELIB67385 | 1 | 483.1 | 539.63 | 56.53 | 80 |  | 4522.4 | 4606.8906 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 4606.8906 | 4570.7831 | 36.1075 | 0.78996 | OK
|  |  | 10: Total | 18466056 | 18127387.48 | 18466056 | 1.8683
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Postogola | at 33 KV level |  | 9350450.8824
[6 empty] | Jurain | at 33 KV level |  | 9115605.1176
[6 empty] | Total = |  |  | 18466056 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. |  | 33 | Export | BD001802 | 1 | 1544.896 | 1544.8992 | 0.0032 | 240000 | 0 | 768 | 767.7568
| Postogola 33 KV SIDE |  | 10: Total | 0 | 768 | 767.7568
7 | 33 kV IG Gate Ckt-2 |  | 33 | Main | 41808902815 | 1 | 449 | 475.3 | 26.3 | 360000 | 0 | 9468000 | 9468000
17 | 33 kV IG Gate Ckt-1 |  | 33 | Main | 41812909470 | 1 | 361.64 | 382.7 | 21.06 | 360000 | 0 | 7581600 | 7581600
|  |  | 10: Total | 0 | 17049600 | 17049600
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 |  | 33 | Import | DHK60973 | 1 | 295159.8 | 309189.6 | 14029.8 | 540 | 7576092
6 | 33 kV Postogola Incoming Feeder-2 |  | 33 | Import | DHK60966 | 1 | 482124.7 | 502284.8 | 20160.1 | 540 | 10886454
|  |  | 7: 0; 8: 0; 10: Total | 18462546 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  | 7: 0; 8: 0
| Feeder No.1 |  | 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
| Feeder No.2 |  | 3: 33; 7: 0; 8: 0 |  | 0
|  |  | 7: 0; 8: 0; 10: Total |  | 0
[7 empty] | 0 | 0
| IG GATE 33 KV SIDE |  | 7: 0; 8: 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) |  | 33 | Export | DHK60893 | 1 | 850100.2 | 892147.6 | 42047.4 | 180 |  | 7568532
5 | 33 kV, 20/28 MVA T-2 (HV Side) |  | 33 | Export | DHK60975 | 1 | 480036.4 | 518056.2 | 38019.8 | 180 |  | 6843564
|  |  | 10: Total |  | 14412096
| 33 KV IMPORT |  | 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 4: 17049600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 17049600
| IMPORT-2 |  | 6: 33 KV NET IMPORT; 9=8-7: 17049600 | 33 KV TX HV SIDE |  | 14412096
| IMPORT-3 | [9 empty] | LOSS UNITS=> |  | 2637504
| IMPORT-4 | [9 empty] | LOSS % IN => |  | 15.47%
| TOTAL IMPORT |  | 4: 17049600
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [14 empty] | Month October-2023 |  |  | Name of Feeders. | Month October-2023 | Month September-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. |  | 3: Meter; 6: CF; 7: Active Energy Reading at 00:00 Hr. on; 10: OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  |  | Possition |  | Number |  | Reading at 00.00hr 01.10.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. |  | 11 |  | DHK68139 | 1 | 3788.85 | 3829.57 | 40.72 | 180000 | 7329600 |  | 7688368.9037 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming |  | 11 |  | DHK68137 | 1 | 4430.39 | 4479.97 | 49.58 | 180000 | 8924400 |  | 9361231.0963
|  |  | 7: 0; 8: 0; 10: Total | 16254000 |  | 17049600
| IG GATE 11 KV SIDE |  | 7: 0; 8: 0
1 | 11 kV Feeder-1 |  | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 |  | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | A619R | 11 |  | DHK60970 | 1 | 294537.9 | 325962.4 | 31424.5 | 60 |  | 1885470 | 1912589.3597 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 1912589.3597 | 2044107.1526 | -131517.7929 | -6.434 | OK
4 | 11 kV Alom Gonj | A581A | 11 |  | DHK60894 | 1 | 501244.8 | 511135.3 | 9890.5 | 60 |  | 593430 | 601965.5066 | Postogola |  |  |  | 11 kV Alom Gonj | 601965.5066 | 622652.7534 | -20687.2468 | -3.3224 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 |  | DHK60895 | 1 | 599147 | 625193.4 | 26046.4 | 60 |  | 1562784 | 1585262.0566 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1585262.0566 | 1935090.8799 | -349828.8233 | -18.0782 | OK
6 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 |  | DHK68133 | 1 | 3653.37 | 3683.69 | 30.32 | 60000 |  | 1819200 | 1845366.1756 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1845366.1756 | 1846529.6992 | -1163.5236 | -0.063011 | OK
7 | 11 kV Doyaganj | B587Y | 11 |  | DHK68134 | 1 | 2436.85 | 2463.08 | 26.23 | 60000 |  | 1573800 | 1596436.5035 | Swamibag |  |  |  | 11 kV Doyaganj | 1596436.5035 | 1387958.4974 | 208478.0061 | 15.0205 | OK
10 | 11 kV Faridabad | A587F | 11 |  | DHK68140 | 1 | 818.15 | 838.74 | 20.59 | 60000 |  | 1235400 | 1253169.1806 | Postogola |  |  |  | 11 kV Faridabad | 1253169.1806 | 1329183.0163 | -76013.8357 | -5.7188 | OK
11 | 11 kV Gandaria | A524D | 11 |  | DHK60969 | 1 | 441701.8 | 473557.9 | 31856.1 | 60 |  | 1911366 | 1938857.8307 | Postogola |  |  |  | 11 kV Gandaria | 1938857.8307 | 2106445.8973 | -167588.0666 | -7.956 | OK
12 | 11 kV Walter Road | A687W | 11 |  | DHK68136 | 1 | 1032.13 | 1054.29 | 22.16 | 60000 |  | 1329600 | 1348724.0914 | Banglabazar |  |  |  | 11 kV Walter Road | 1348724.0914 | 2063264.286 | -714540.1946 | -34.6315 | OK
13 | 11 kV Murgitola Feeder (F-11) | B587G | 11 |  | DHK68138 | 1 | 3970.36 | 4009.01 | 38.65 | 60000 |  | 2319000 | 2352354.9699 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2352354.9699 | 2412855.9498 | -60500.98 | -2.5074 | OK
14 | 11 kV Feeder-12 |  | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 |  | DHK60899 | 1 | 724879 | 752453.5 | 27574.5 | 60 |  | 1654470 | 1678266.8077 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1678266.8077 | 1754827.7038 | -76560.8961 | -4.3629 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 |  | DHK60967 | 1 | 199239 | 214602.5 | 15363.5 | 60 |  | 921810 | 935068.7084 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 935068.7084 | 1005323.9927 | -70255.2843 | -6.9883 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 |  | 0.415 |  | ELIB2774 | 1 | 282863.01 | 284380 | 1516.99 | 1 |  | 1516.99 | 1538.8094 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1538.8094 | 3608.1717 | -2069.3623 | -57.3521 | CHECK
|  |  | 10: Grand Total | 17049600 | 16807846.99 | 17049600 | 1.4383
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Swamibag | at 33 KV level |  | 5627058.2811
[6 empty] | Banglabazar | at 33 KV level |  | 5106679.6267
[6 empty] | Postogola | at 33 KV level |  | 6315862.0923
[6 empty] | Total = |  |  | 17049600 | 0
Note on J387: No Reading Due to PT Out
Note on L387: Reading From Higher Side
Note on J644: No Reading due to PT Open
Note on M644: Energy From Bangshal SS End
Note on M649: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [12 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month October-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month October-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.09.2023 | [6 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 9098920.785 | 20151872.4546 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 8278663.3996 |  | North | 290619205.9854 | Tejgaon | 58791192.4917 | Tejgaon | 33018095.2472 | 34107405.5145 | -1089310.2673 | -3.1938 | North | 290619205.9854 | 303699254.015 | -4.5008 | Tejgaon | 58791192.4917 | 59346933 | -0.94528 | Tejgaon | 33018095.2472 | 31468806 | 4.6922 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 154587.5799 | [5 empty] | Kakrail | 25773097.2445 | 27317341.3597 | -1544244.1152 | -5.653 | [8 empty] | Kakrail | 25773097.2445 | 27878127 | -8.1675 | 2 | Tejgaon | 31468806 | 196426 | 31665232 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | 240513.9162
|  |  |  | Maghbazar | 2619700.69 |  |  |  | Moghbazar | 35131326.2934 | Moghbazar | 19456170.4445 | 20961176.334 | -1505005.8894 | -7.18 |  |  |  |  | Moghbazar | 35131326.2934 | 36894933 | -5.02 | Moghbazar | 19456170.4445 | 20573106 | -5.7408 | 3 | Kakrail | 27878127 | 134050 | 28012177 | A1 | Motijheel | 22865869 | 164088 | 23029957
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 13422148.4753 |  |  |  |  | Khilgaon | 15675155.8489 | 16875886.2941 | -1200730.4452 | -7.1151 | [8 empty] | Khilgaon | 15675155.8489 | 16321827 | -4.1255 | 4 | Moghbazar | 20573106 | 63535 | 20636641 | A2 | Khilgaon | 16321827 | 59703 | 16381530
|  |  |  | Jigatola | 2555681.0055 |  |  |  | Satmasjid | 45255504.4397 | Satmosjid | 21777495.0822 | 23412446.5748 | -1634951.4925 | -6.9833 |  |  |  |  | Satmasjid | 45255504.4397 | 46167247 | -2.0147 | Satmosjid | 21777495.0822 | 22160943 | -1.7608 | 5 | Khilgaon | 16321827 | 59703 | 16381530 | A3 | Lalbag | 32204138 | 464799 | 32668937
|  |  |  | Paribagh | 10866467.4697 | [5 empty] | Sherebanglanagar | 23478009.3575 | 24960323.2814 | -1482313.9239 | -5.9387 | [8 empty] | Sherebangla nagar | 23478009.3575 | 24006304 | -2.2502 | 6 | Satmosjid | 22160943 | 83495 | 22244438 | A4 | Kazla | 38390804 | 86446 | 38477250
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 13778010 |  |  | Dhanmondi | 49840958.1564 | Dhanmondi | 22296608.5062 | 23862105.7271 | -1565497.2209 | -6.5606 |  |  |  |  | Dhanmondi | 49840958.1564 | 53818759.15 | -7.981 | Dhanmondi | 22296608.5062 | 24555384 | -10.1306 | 7 | Sherebanglanagar | 24006304 | 57477 | 24063781 | A5 | Postogola | 15925283 | 139839 | 16065122
[11 empty] | Jhigatala | 27544349.6502 | 28839402.8735 | -1295053.2233 | -4.4906 | [8 empty] | Jhigatala | 27544349.6502 | 29263375.15 | -6.2409 | 8 | Dhanmondi | 24555384 | 124825 | 24680209 | A6 | Banglabazar | 16227586 | 65470 | 16293056
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 52205900.6732 | Azimpur | 18790675.4911 | 20220711.3559 | -1430035.8648 | -7.0721 |  |  |  |  | Azimpur | 52205900.6732 | 54252662.865 | -3.9206 | Azimpur | 18790675.4911 | 19587741 | -4.2418 | 9 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274 | A7 | N.Gonj (West) | 28707452 | 196212 | 28903664
|  |  |  | Dhanmondi | 13778010 | [5 empty] | Paribagh | 33415225.182 | 36167293.3587 | -2752068.1766 | -7.6093 | [8 empty] | Paribagh | 33415225.182 | 34664921.865 | -3.7399 | 10 | Azimpur | 19587741 | 236081 | 19823822 | A8 | Siddirgonj | 49639472 | 532212 | 50171684
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 20863294.4968 | 20863294.4968 |  |  | Shamoly | 49394323.931 | Shyamoli | 17460263.4212 | 18613818.2819 | -1153554.8607 | -6.1973 |  |  |  |  | Shamoly | 49394323.931 | 53218719 | -7.7426 | Shyamoli | 17460263.4212 | 19516523 | -11.7768 | 11 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448 | A9 | Bashabo | 14583022 | 53363 | 14636385
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 13115973.2841 |  |  |  |  | Adabor | 31934060.5098 | 34402560.007 | -2468499.4973 | -7.1753 | [8 empty] | Adabor | 31934060.5098 | 33702196 | -5.5368 | 12 | Shyamoli | 19516523 | 64518 | 19581041 | B1 | Narinda | 13978240 | 38770 | 14017010
|  |  |  | RAMNA | 1015696.7461 |  | Central | 269239151.9106 | Lalbagh | 78770442.9438 | Lalbagh | 36837631.6772 | 35407892.3412 | 1429739.336 | 4.0379 | Central | 269239151.9106 | 262953550.91 | 2.3346 | Lalbagh | 78770442.9438 | 70781931 | 10.1415 | Lalbagh | 36837631.6772 | 32204138 | 12.5782 | 13 | Adabor | 33702196 | 255452 | 33957648 | B2 | Maniknagar | 20970662 | 109760 | 21080422
|  |  |  | Kakrail | 1719829.4795 | [5 empty] | Kamrangirchar | 41932811.2666 | 41771703.2476 | 161108.0189 | 0.38569 | [8 empty] | Kamrangirchar | 41932811.2666 | 38577793 | 8.0009 | 14 | Lalbagh | 32204138 | 464799 | 32668937 | B3 | Jurain | 27684985 | 453096 | 28138081
|  |  |  | Paribagh | 10380447.0584 |  |  |  | Ramna | 45398707.1559 | Ramna | 27563948.3663 | 28911229.1877 | -1347280.8214 | -4.6601 |  |  |  |  | Ramna | 45398707.1559 | 47932700 | -5.5816 | Ramna | 27563948.3663 | 28702610 | -4.131 | 15 | Kamrangirchar | 38577793 | 101944 | 38679737 | B4 | Shyampur | 66519316 | 426920 | 66946236
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 3949533.4562 |  |  |  |  | Rajarbagh | 17834758.7896 | 19622794.8267 | -1788036.0371 | -9.112 | [8 empty] | Rajarbagh | 17834758.7896 | 19230090 | -7.8237 | 16 | Ramna | 28702610 | 211333 | 28913943 | B5 | Swamibag | 13880852 | 46920 | 13927772
|  |  |  | Kakrail | 236270.9269 |  |  |  | Bashabo | 38349981.2223 | Bashabo | 14160522.2761 | 15171853.2974 | -1011331.0213 | -6.6658 |  |  |  |  | Bashabo | 38349981.2223 | 39590401.91 | -3.2345 | Bashabo | 14160522.2761 | 14583022 | -2.9836 | 17 | Rajarbagh | 19230090 | 88052 | 19318142 | B6 | Bangshal | 19038085 | 79495 | 19117580
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 24189458.9462 | 26442699.188 | -2253240.2419 | -8.5212 | [8 empty] | Bonossri | 24189458.9462 | 25007379.91 | -3.3813 | 18 | Bashabo | 14583022 | 53363 | 14636385 | B7 | N.Gonj (East) | 30757520 | 509964 | 31267484
|  |  |  | Shere Bangla Nagar | 3713262.5293 |  |  |  | Motijheel | 40501924.2604 | Motijheel | 21462622.2777 | 21726576.266 | -263953.9883 | -1.2149 |  |  |  |  | Motijheel | 40501924.2604 | 41523755 | -2.5229 | Motijheel | 21462622.2777 | 22865869 | -6.5381 | 19 | Bnossri | 25007379.91 | 102145 | 25109524.91 | B8 | Fateullah | 32245904 | 463782 | 32709686
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 2296031.146 | 9090800 |  |  |  |  | Mughdapara | 19039301.9827 | 20328273.2401 | -1288971.2574 | -6.3408 | [8 empty] | Mughdapara | 19039301.9827 | 18657886 | 2.0033 | 20 | Motijheel | 22865869 | 164088 | 23029957 | B9 | Mugdapara | 18657886 | 36172 | 18694058
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 36838241.2053 | Banglabazar | 17230899.4035 | 17803073.1525 | -572173.7491 | -3.2139 |  |  |  |  | Banglabazar | 36838241.2053 | 35265671 | 4.2689 | Banglabazar | 17230899.4035 | 16227586 | 5.8228 | 21 | Mughdapara | 18657886 | 36172 | 18694058 | C1 | Tejgaon | 31468806 | 196426 | 31665232
|  |  |  | Narinda | 419318.091 | [5 empty] | Bongshal | 19607341.8018 | 20066558.571 | -459216.7692 | -2.2885 | [8 empty] | Bongshal | 19607341.8018 | 19038085 | 2.9033 | 22 | Banglabazar | 16227586 | 65470 | 16293056 | C2 | Satmasjid | 22160943 | 83495 | 22244438
|  |  |  | Motijheel | 454930.0034 |  |  |  | Narinda | 29379855.123 | Narinda | 14708156.3518 | 15407227.6581 | -699071.3063 | -4.5373 |  |  |  |  | Narinda | 29379855.123 | 27859092 | 5.1762 | Narinda | 14708156.3518 | 13978240 | 4.9627 | 23 | Bongshal | 19038085 | 79495 | 19117580 | C3 | Paribagh | 34664921.865 | 199185.0798 | 34864106.9448
|  |  |  | RAMNA | 5920520.7596 | [5 empty] | Swamibagh | 14671698.7712 | 14996227.0826 | -324528.3114 | -2.1641 | [8 empty] | Swamibagh | 14671698.7712 | 13880852 | 5.3903 | 24 | Narinda | 13978240 | 38770 | 14017010 | C6 | Kakrail | 27878127 | 134050 | 28012177
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 447523863.3417 | Kazla | 61048228.1998 | Kazla | 40188148.6608 | 40297509.3512 | -109360.6904 | -0.27138 | South | 447523863.3417 | 418742139 | 6.4313 | Kazla | 61048228.1998 | 59361466 | 2.763 | Kazla | 40188148.6608 | 38390804 | 4.4723 | 25 | Swamibagh | 13880852 | 46920 | 13927772 | D1 | Moghbazar | 20573106 | 63535 | 20636641
|  | Khillgaon 33/11KV S/S |  | Kakrail | 61390.4591 | 6838730.1823 |  |  |  |  | Maniknagar | 20860079.5389 | 21375615.4926 | -515535.9537 | -2.4118 | [8 empty] | Maniknagar | 20860079.5389 | 20970662 | -0.53012 | 26 | Kazla | 38390804 | 86446 | 38477250 | D2 | Dhanmondi | 24555384 | 124825 | 24680209
|  |  |  | Khilgaon | 0 |  |  |  | Shyampur | 91688498.606 | Shyampur | 67619215.2097 | 65117524.5991 | 2501690.6107 | 3.8418 |  |  |  |  | Shyampur | 91688498.606 | 88513636 | 3.4627 | Shyampur | 67619215.2097 | 66519316 | 1.6266 | 27 | Maniknagar | 20970662 | 109760 | 21080422 | D3 | Ramna | 28702610 | 211333 | 28913943
| 9 |  |  | Maghbazaar | 122203.1256 | [5 empty] | Matuail | 24069283.3962 | 24578480.5301 | -509197.1338 | -2.0717 | [8 empty] | Matuail | 24069283.3962 | 21994320 | 8.6208 | 28 | Shyampur | 66519316 | 426920 | 66946236 | D4 | Shyamoli | 19516523 | 64518 | 19581041
|  |  |  | Rajarbagh | 6655136.5976 |  |  |  | Postogola | 46057266.6304 | Postogola | 15666312.9746 | 16662640.0271 | -996327.0525 | -5.9794 |  |  |  |  | Postogola | 46057266.6304 | 43610268 | 5.3129 | Postogola | 15666312.9746 | 15925283 | -1.653 | 29 | Matuail | 21994320 | 179400 | 22173720 | D5 | Shere b.nagar | 24006304 | 57477 | 24063781
| 10 | Goran 33/11KV S/S |  | Bashabo | 1194417.5741 | 9890611 |  |  |  |  | Jurain | 30390953.6558 | 30130489.1038 | 260464.5521 | 0.86446 | [8 empty] | Jurain | 30390953.6558 | 27684985 | 8.9039 | 30 | Postogola | 15925283 | 139839 | 16065122 | D6 | Rajarbag | 19230090 | 88052 | 19318142
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 68264380.38 | Narayangonj-West | 34400925.3767 | 33152990.0775 | 1247935.2993 | 3.7642 |  |  |  |  | Narayangonj | 68264380.38 | 59464972 | 12.8902 | Narayangonj- West | 34400925.3767 | 28707452 | 16.5503 | 31 | Jurain | 27684985 | 453096 | 28138081 | D8 | Jhigatala | 29263375.15 | 214733.3774 | 29478108.5274
|  |  |  | Banosree | 8696193.4259 | [5 empty] | Narayangonj-East | 33863455.0033 | 32340650.3155 | 1522804.6878 | 4.7086 | [8 empty] | Narayangonj- East | 33863455.0033 | 30757520 | 9.1719 | 32 | Narayangonj-West | 28707452 | 196212 | 28903664 | D9 | Azimpur | 19587741 | 236081 | 19823822
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 8270943.4744 | 12070400 |  |  | Demra | 74129133.2176 | Demra | 24012632.971 | 25117614.5091 | -1104981.5381 | -4.3992 |  |  |  |  | Demra | 74129133.2176 | 71702210 | 3.2739 | Demra | 24012632.971 | 22062738 | 8.1203 | 33 | Narayangonj-East | 30757520 | 509964 | 31267484 | E1 | Demra | 22062738 | 533151 | 22595889
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 50116500.2466 | 50307426.9765 | -190926.7299 | -0.37952 | [8 empty] | Siddhirgonj | 50116500.2466 | 49639472 | 0.95184 | 34 | Damra | 22062738 | 533151 | 22595889 | E2 | Matuail | 21994320 | 179400 | 22173720
|  |  |  | Bashabo | 3799456.5256 |  |  |  | Fatullah | 106336356.3079 | Fatulla | 36403490.2891 | 35130226.3657 | 1273263.9233 | 3.6244 |  |  |  |  | Fatullah | 106336356.3079 | 96089587 | 9.6362 | Fatulla | 36403490.2891 | 32245904 | 11.4208 | 35 | Siddhirgonj | 49639472 | 532212 | 50171684 | E3 | Sytalakha | 63843683 | 329125 | 64172808
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 18649800 |  |  |  |  | Shitalakha | 69932866.0189 | 64490939.9788 | 5441926.0401 | 8.4383 | [8 empty] | Sytalakhya | 69932866.0189 | 63843683 | 8.7072 | 36 | Fatulla | 32245904 | 463782 | 32709686 | F1 | Kamrangirchar | 38577793 | 101944 | 38679737
|  |  |  | Shyamoli | 2805597.1844 |  | TOTAL=> | 1007382221.2377 | TOTAL=> | 1007382221.2377 | TOTAL=> | 1007382221.2377 | 1026098686.3486 | -18716465.1109 | -1.824 |  | 1007382221.2377 | 985394943.925 |  | TOTAL=> | 1007382221.2377 | 985394943.925 |  | Total=> | 1007382221.2377 | 985394943.925 | 2.1826 | 37 | Shitalokko | 63843683 | 329125 | 64172808 | F2 | Banosree | 25007379.91 | 102145 | 25109524.91
|  |  |  | Shere Bangla Nagar | 0 | [23 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823 | G1 | Adabor | 33702196 | 255452 | 33957648
|  |  |  | Satmosjid | 9934656.5459 | [14 empty] | 132KV Import => |  |  |  |  | 1013291785.8784 | [8 empty] | Total => | 985394943.925 | 7101938.4573 | 992496882.3823
|  |  |  | Dhanmondi NOCS | 5909546.2697 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 1013291785.8784 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 1007382221.2377
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 1007382221.2377 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.5832
| 13 | Japan garden Building |  | Adabor | 1459800 | 1459800 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.5832 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 985394943.925
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 5909564.6407 | [8 empty] | System loss at 132kv level => |  |  |  |  | 2.7531
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 1932000 | 1932000
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 11394474 | 12130424
| 16 |  |  | Shere Bangla Nagar | 735950
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 25776000 | 25776000
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1328075.3488 | 11093243.9295
|  |  |  | Lalbagh | 9765168.5807
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 8183826.3867
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 8183826.3867
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 2386091.1622 | 9667826.4596
|  |  |  | Rajarbaghl | 2836678.3641
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 4445056.9333 | 4445056.9333
|  | Banshal 33/11 KV S/S |  | Bangshal | 6151617.6833 | 8693968.6263
|  |  |  | Banglabazar | 1317991.7768
|  |  |  | Narinda | 1224359.1662
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 11085248.5802 | 16196800
|  |  |  | Shamoly | 4044620.7644
|  |  |  | Satmosjit | 1066930.6554
|  | Azimpur 33/11 KV |  | jigatola | 715312.2841 | 16038304.0679
|  |  |  | Azimpur | 13261159.345
|  |  |  | RAMNA | 1401982.9497
|  |  |  | Paribagh | 659849.4891
|  | T&T 33/11 KV |  | Kakrail | 2198026.4014 | 9369331.9415
|  |  |  | Mogbazar | 5549586.2622
|  |  |  | Khilgaon | 1621719.2778
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 3538409.374 | 6274894.179
|  |  |  | Shamoly | 2071055.8024
|  |  |  | Tejgaon | 658608.2649
|  |  |  | Satmosjit | 6820.7377
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 24374740.8108 | 26822800
|  |  |  | Kamrangirchar | 2448059.1892
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 4072688.3333 | 6285845.7
|  |  |  | Kakrail | 2213157.3667
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1072911.2814
|  |  |  | Shere Bangla Nagar | 1384669.6932
|  |  |  | Shamoly | 8538989.67
|  |  |  | Satmosjit | 4819354.8526
|  | Banasree 33/11SS |  | Khilgaon | 4584489.0151
|  |  |  | Bansree | 11294766.1931 | 11294766.1931
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 1198004.0816 | 18348004.6649
|  |  |  | Bashabo | 7341637.2615
|  |  |  | Mugdapara | 4064272.8038
|  |  |  | Maniknagor | 5744090.518
|  | DMC |  | Bangshal | 2855744.386
|  |  |  | RAMNA | 1654716.4315 | 3828040.0025
|  |  |  | Lalbagh | 2173323.571
|  | Green Road Dormatory |  | Paribagh | 8619757.3503
|  |  |  | Shere Bangla Nagar | 5431546.5766
|  | BSMMU 33/11KV S/S |  | Kakrail | 2019898.7787
|  |  |  | Paribagh | 2888703.8145
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 7994537.9296
|  |  |  | Satmasjid | 5949732.2906
|  | Dhaka University 33/11 KV SS |  | RAMNA | 2195000
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 6328106.6193
|  |  |  | Kakrail | 987318.9359
|  |  |  | Tejgaon | 3217529.0858
|  | BGB 33/11 KV SS |  | Kamrangirchar | 7257640.057
|  |  |  | Jigatola | 5498539.1457
|  |  |  | Azimpur | 4201440.7973
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2191476.9852
|  | BB Avenue 33/11 KV SS |  | Narinda | 2056960.2186
|  |  |  | Ramna | 5090934.409
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 16842817.2149
|  |  |  | Dhanmondi | 1536140.9551
|  | Ispahani 33/11 KV SS |  | Moghbazar | 2980853.9799
|  |  |  | Kakrail | 2793227.178
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 6451112.0203
|  |  |  | Total=> | 461006482.7408 | 299905449.873
NORTH ZONE TOTAL=>
|  | NOCS |  | 461006482.7408 |  | 200857461
|  | diff |  |  | -461006482.7408
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 4704000
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 4704000
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 795173.7239 | 17471125.3612
|  |  |  | Swamibagh | 5898340.6363
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 10777611.0011
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 10806228
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 10806228
| 4 | Maderteck 33/11KV S/S |  | Banosree | 4198499.3272 | 19967697.9184
|  |  |  | Bashabo | 1825010.9149
|  |  |  | Maniknagar | 259324.0979
|  |  |  | Mugdapara | 13684863.5785
| 5 | Kazla 33/11KV S/S |  | Matual | 1111465.2136 | 38211664.1599
|  |  |  | Jurain | 8241639.655
|  |  |  | Swamibagh | 1997346.9786
|  |  |  | Maniknagar | 2647764.0681
|  |  |  | Shyampur | 2235311.7183
|  |  |  | Kazla | 21978136.5263
|  | Shyampur 132/11KV S/S |  | Shyampur | 28620919.33 | 29718754.7435
|  |  |  | Fatullah. | 1097835.4135
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 25685545.0066
|  |  |  | Fatullah | 1190157.2597
|  |  |  | Shyampur | 24495387.7469
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 6530069.3779 | 19563778.261
|  |  |  | Jurain | 13033708.8831
| 8 | Postogola 33/11KV S/S |  | Jurain | 9115605.1176 | 18466056
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 9350450.8824
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 9660915.4436 | 11100758.1506
|  |  |  | Narayanganj (West) | 1477564.4753
|  |  |  | Shitalakhy | 1439842.707
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 1165656.5251 | 14065191.4176
|  |  |  | Shitalakhy | 9841599.7983
|  |  |  | Narayanganj (West) | 3053539.119
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 4395.9753
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 1276885.4045
| 11 |  |  | Narayanganj (West) | 17488195.9831 | 18765081.3875
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 15180009.9325 | 15180009.9325
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 13280455.8512 | 13280455.8512
|  |  |  | Matuail | 283444.1488
| 14 | Sarulia 33/11KV S/S |  | Demra | 15656351.089 | 18158692.8129
|  |  |  | Matuail | 2502341.7238
|  | Demra 33/11KV S/S |  | Matuail | 7718156.9441 | 23150864
| 15 |  |  | Demra | 2426891.0596
|  |  |  | Siddhirganj | 13005815.9963
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1271995.6228
| 16 |  |  | Narayanganj (East) | 5750344.4491 | 14325592.5946
|  |  |  | Narayanganj (West) | 8575248.1456
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 3806377.6538 | 17340684.9033
|  |  |  | Narayanganj (East) | 13534307.2495
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 5921670.5899 | 19739592.998
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 346712.7622
|  |  |  | Fatullah | 4162619.6431
|  |  |  | Matuail | 9308590.0027
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 1948464 | 1948464
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 526937.9846
|  |  |  | Maniknagar | 10886789.1465 | 10886789.1465
|  | IG Gate 33/11 kv |  | Swamibagh | 5627058.2811 | 17049600
|  |  |  | Banglabazr | 5106679.6267
|  |  |  | Postogola | 6315862.0923
|  | Motijil 33/11kv |  | kamlapur | 7875519.897 | 8334600
|  |  |  | RAMNA | 459080.103
|  | Mitford 33/11kv |  | Banshal | 8303948.5866 | 8828347.3012
|  |  |  | Lalbagh | 524398.7147
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 5390814.2744 | 12774154.2357
|  |  |  | Fatullah | 4238054.5982
|  |  |  | Matuail | 3145285.3631
|  | MI CEMENT |  | Shitalakhy | 12087360 | 12087360
|  | Dapa 33/11 kV |  | Fatullah | 16053907.9308 | 16053907.9308
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7491476.1897 | 16141694.6563
|  |  |  | Siddhirganj | 8650218.4666
|  | Amulia 33/11 KV SS |  | Mugdapara | 1290165.6005 | 7219556.4229
|  |  |  | Demra | 5929390.8224
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 12832572.4533
|  | P&T 33/11 KV SS |  | Motijeel | 2497097.981
|  |  |  | RAMNA | 3367237.4719
|  |  |  | Rajarbagh | 3095673.0075
|  | Kazla 132/33 KV SS |  | Kazla | 18210012.1345
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 5247270.8203
|  |  |  | Motijeel | 2521668.2423
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 14133750.0577
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 3409406.1539
|  |  |  | Swamibagh | 1148952.8752
|  |  |  | Narinda | 229907.875
|  | 132 KV Shah Cement |  | Sitalakhya | 15096000
|  |  |  | Total=> | 546375738.4969 | 421611088.1826
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 546375738.4969
| Diff zone&Nocs |  |  |  | -33776496.1717
|  |  |  | Diff= | 0

## Forwarding (hidden)
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 33164537.2467 | 33018095.2472 | -146441.9995 | -0.44352
Kakrail | 25723127.9287 | 25773097.2445 | 49969.3158 | 0.19388
Moghbazar | 19528895.2116 | 19456170.4445 | -72724.767 | -0.37379
Khilgaon | 15686298.6946 | 15675155.8489 | -11142.8457 | -0.071086
Satmosjid | 21777495.0822 | 21777495.0822 | 0 | 0
Sherebanglanagar | 23445835.7557 | 23478009.3575 | 32173.6018 | 0.13704
Dhanmondi | 22296608.5062 | 22296608.5062 | 0 | 0
Jhigatala | 27526386.5537 | 27544349.6502 | 17963.0965 | 0.065215
Azimpur | 18716546.4471 | 18790675.4911 | 74129.044 | 0.3945
Paribagh | 33055516.0236 | 33415225.182 | 359709.1585 | 1.0765
Shyamoli | 17460263.4212 | 17460263.4212 | 0 | 0
Adabor | 31934060.5098 | 31934060.5098 | 0 | 0
Lalbagh | 36810896.9275 | 36837631.6772 | 26734.7497 | 0.072575
Kamrangirchar | 41932811.2666 | 41932811.2666 | 0 | 0
Ramna | 27492222.7413 | 27563948.3663 | 71725.6251 | 0.26022
Rajarbagh | 17625285.4915 | 17834758.7896 | 209473.2981 | 1.1745
Bashabo | 14259885.2463 | 14160522.2761 | -99362.9702 | -0.70169
Bonoseeri | 24153463.8028 | 24189458.9462 | 35995.1434 | 0.14881
Motijheel | 21464015.4727 | 21462622.2777 | -1393.195 | -0.0064913
Mughdapara | 19034948.4193 | 19039301.9827 | 4353.5635 | 0.022866
Banglabazar | 17230899.4035 | 17230899.4035 | 0 | 0
Bongshal | 19727027.4876 | 19607341.8018 | -119685.6858 | -0.61041
Narinda | 14689247.3555 | 14708156.3518 | 18908.9962 | 0.12856
Swamibagh | 14671698.7712 | 14671698.7712 | 0 | 0
Kazla | 40188148.6608 | 40188148.6608 | 0 | 0
Maniknagar | 20875545.1569 | 20860079.5389 | -15465.618 | -0.07414
Shyampur | 67652691.0714 | 67619215.2097 | -33475.8616 | -0.049506
Matuail | 24595658.9541 | 24069283.3962 | -526375.5579 | -2.1869
Postogola | 15664758.0513 | 15666312.9746 | 1554.9233 | 0.0099253
Jurain | 30103745.696 | 30390953.6558 | 287207.9598 | 0.94504
Narayangonj-West | 34453478.677 | 34400925.3767 | -52553.3003 | -0.15277
Narayangonj-East | 33944804.93 | 33863455.0033 | -81349.9267 | -0.24023
Damra | 24062056.9221 | 24012632.971 | -49423.9511 | -0.20582
Siddhirgonj | 50388091.1787 | 50116500.2466 | -271590.9321 | -0.54192
Fatulla | 36425332.0158 | 36403490.2891 | -21841.7268 | -0.059999
Shitalakha | 69960826.8475 | 69932866.0189 | -27960.8286 | -0.039982
TOTAL=> | 1007723111.9281 | 1007382221.2377 | -340890.6904 | -0.033839

## Linked_11KV
SL | Feeder_Name | FEEDER_NO | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | SUBSTN_CODE | September23_Consumption | August23_Consumption | July23_Consumption | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | C301B | 11 | EXPORT | HA021100901-02 | 1 | 9200644 | 10517508 | 1316864 | 1 | 0 | 1316864 | 1327224.0724 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1457854.4301 | 1314371.1616 | 1273734.3863 | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | C301M | 11 | 0 | HA021100463-02 | 1 | 50840272 | 52334628 | 1494356 | 1 | 0 | 1494356 | 1506112.4428 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1598079.2811 | 1562022.8871 | 1571851.4764 | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | C3011 | 11 | 0 | HA021101078-02 | 1 | 65548276 | 66739049 | 1190773 | 1 | 0 | 1190773 | 1200141.0854 | Paribag | Dhanmondi 33/11KV S/S | 1 | 2105982.2036 | 2198394.2713 | 2202528.7234 | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | C301U | 11 | 0 | DHK60882 | 1 | 229747.82 | 236770.81 | 7022.99 | 60 | 0 | 421379.4 | 424694.4888 | Paribag | Dhanmondi 33/11KV S/S | 1 | 424650.6487 | 429515.8245 | 406161.3393 | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | C301P | 11 | 0 | DHK60889 | 1 | 290812.76 | 294533.1518 | 3720.3918 | 60 | 0 | 223223.5099 | 224979.6606 | Paribag | Dhanmondi 33/11KV S/S | 1 | 224715.2737 | 240975.4757 | 236479.8549 | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 0 | 11 | 0 | DHK60890 | 1 | 713.79 | 720.79 | 7 | 60000 | 0 | 420000 | 423304.2367 | Paribag | Dhanmondi 33/11KV S/S | 1 | 422384.6367 | 444161.7425 | 451511.4107 | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | D301H | 11 | 0 | DHK60880 | 1 | 570802.23 | 576270.3 | 5468.07 | 60 | 0 | 328084.2 | 330665.314 | Ramna | Dhanmondi 33/11KV S/S | 1 | 381236.2759 | 740264.9629 | 797710.3468 | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 0 | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0
9 | 11 kV TSC Feeder | D301U | 11 | 0 | DHK60873 | 1 | 947497.59 | 956639.98 | 9142.39 | 60 | 0 | 548543.4 | 552858.9173 | Ramna | Dhanmondi 33/11KV S/S | 1 | 527789.8466 | 622520.63 | 596411.0072 | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | C301S | 11 | 0 | DHK60883 | 1 | 28547.18 | 28791.31 | 244.13 | 60 | 0 | 14647.8 | 14763.0376 | Paribag | Dhanmondi 33/11KV S/S | 1 | 14899.4821 | 7435.3517 | 6184.9227 | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 0 | 11 | 0 | DHK60871 | 1 | 532788.31 | 549657.1 | 16868.79 | 60 | 0 | 1012127.4 | 1020090.0393 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1178402.3777 | 1167367.0478 | 1168612.8044 | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | C301E | 11 | 0 | DHK60981 | 1 | 116390.67 | 131190.1 | 14799.43 | 60 | 0 | 887965.8 | 894951.6314 | Paribag | Dhanmondi 33/11KV S/S | 1 | 961999.4403 | 1097238.176 | 1271574.285 | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | C301D | 11 | 0 | DHK61110 | 1 | 456146.54 | 480431.1 | 24284.56 | 60 | 0 | 1457073.6 | 1468536.7336 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1572278.7706 | 1519703.9096 | 1444426.5973 | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 0 | 11 | 0 | DHK61115 | 1 | 399272.59 | 426855.1 | 27582.51 | 60 | 0 | 1654950.6 | 1667970.4775 | Paribag | Dhanmondi 33/11KV S/S | 1 | 1771267.2548 | 1745625.9685 | 1732224.4313 | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | D301M | 11 | 0 | DHK61107 | 1 | 552119.57 | 554305.25 | 2185.68 | 60 | 0 | 131140.8 | 132172.5149 | Ramna | Dhanmondi 33/11KV S/S | 1 | 123208.813 | 139745.6654 | 147111.9421 | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 0 | 11 | 0 | DHK61112 | 1 | 348994.41 | 352032.55 | 3038.14 | 60 | 0 | 182288.4 | 183722.5048 | Paribag | Dhanmondi 33/11KV S/S | 1 | 209615.174 | 205991.8784 | 207014.0635 | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | C601R | 11 | 0 | DHK61108 | 1 | 732231.99 | 746291.96 | 14059.97 | 60 | 0 | 843598.2 | 850234.9813 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 921150.1931 | 935875.2367 | 955769.4815 | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 0 | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 1 | 0 | 0 | 0 | 0 | 0
19 | 11 kV DPH Sw/S-1 | 0 | 11 | 0 | DHK60978 | 1 | 812155.99 | 826536.1 | 14380.11 | 60 | 0 | 862806.6 | 869594.4982 | Kakrail | Dhanmondi 33/11KV S/S | 1 | 880434.4894 | 909712.3671 | 894673.7786 | 964542.5031 | 717844.627
20 | WASA Bhaban | C605M | 11 | 0 | 8536188 | 1.11 | 271216 | 271216 | 0 | 1000 | 1121880 | 1121880 | 1122893.6635 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1128091.0061 | 1031848.2658 | 1051553.1772 | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 0 | 11 | 0 | 8536178 | 1.11 | 577180 | 581779 | 4599 | 44 | 0 | 224615.16 | 224818.1088 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 56030.9835 | 205730.3432 | 203697.4272 | 26163.5003 | 291323.9838
22 | Air Port Road (West) | D505A | 11 | 0 | 8536182 | 1.11 | 3219.3 | 4157.6 | 938.3 | 1000 | 0 | 1041513 | 1042454.0487 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 996313.4361 | 1009777.8086 | 1128128.4372 | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | C172C | 11 | 0 | 8536193 | 1.11 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0
24 | (UTC) Tower | D505U | 11 | 0 | DHK00183 | 1.11 | 16986.2 | 17563.9 | 577.7 | 444.44 | 0 | 284995.8167 | 285253.3218 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 290292.9413 | 349161.1513 | 363430.7232 | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | C605O | 11 | 0 | 8536190 | 1.11 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 0 | 110790.7123 | 63163.9823 | 0 | 0
26 | Panthopath | D505P | 11 | 0 | 8536184 | 1.11 | 37334.9 | 38266.9 | 932 | 1000 | 0 | 1034520 | 1035454.7302 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 1172086.0871 | 1196734.0813 | 1204221.3334 | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | C605N | 11 | 0 | DHK00190 | 1.11 | 56600.9 | 57079.4 | 478.5 | 444.44 | 0 | 236057.6394 | 236270.9269 | Kakrail | Kawranbazar 33/11KV S/S | 5 | 238706.8937 | 200780.8678 | 155748.3677 | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 0 | 11 | 0 | DHK00021 | 1.11 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0
29 | Aux. Transformer, AT-1 | 0 | 11 | 0 | 85-12906 | 1.11 | 69061 | 69276 | 215 | 10 | 0 | 2386.5 | 2388.6563 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 2990.8959 | 2900.021 | 3641.847 | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 0 | 11 | 0 | 85-12909 | 1.11 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 5 | 0 | 0 | 0 | 0 | 0
31 | Police Bhaban | D315I | 11 | 0 | DHK 00005 | 1 | 73880.1 | 74130.7 | 250.6 | 444.44 | 0 | 111376.664 | 113280.4639 | Ramna | New Ramna 33/11KV S/S | 15 | 112636.0604 | 117855.6107 | 121266.9463 | 121013.0538 | 111715.2077
32 | Water Works | 0 | 11 | 0 | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Lalbag | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0
33 | GPO | D3157 | 11 | 0 | DHK 00060 | 1 | 99521.1 | 100084.7 | 563.6 | 444.44 | 0 | 250486.384 | 254768.0345 | Ramna | New Ramna 33/11KV S/S | 15 | 252148.1113 | 248107.5506 | 224260.1714 | 278965.4908 | 233730.721
34 | Culvert Road | D315C | 11 | 0 | 8536184 | 1 | 39940.4 | 40096.9 | 156.5 | 444.44 | 95 | 1155511.98 | 1175263.5465 | Ramna | New Ramna 33/11KV S/S | 15 | 1013459.3684 | 1052444.418 | 990314.9211 | 787025.6832 | 769934.2629
35 | Secretariat (East) | D315E | 11 | 0 | DHK00059 | 1 | 81726.9 | 81730.6 | 3.7 | 444.44 | 0 | 1644.428 | 1672.5368 | Ramna | New Ramna 33/11KV S/S | 15 | 765.313 | 950.0836 | 1673.5834 | 2240.1359 | 29358.1395
36 | Siddik Bazar | B615S | 11 | 0 | DHK00076 | 1 | 37647.7 | 41750.6 | 4102.9 | 444.44 | 0 | 1823492.876 | 1854662.4712 | Bangshal | New Ramna 33/11KV S/S | 15 | 1902703.0751 | 1396125.2558 | 499406.3237 | 894134.2296 | 765262.7858
37 | Bokshi Bazar | D315X | 11 | 0 | DHK 00206 | 1 | 89013.4 | 90253.3 | 1239.9 | 444.44 | 0 | 551061.156 | 560480.6352 | Ramna | New Ramna 33/11KV S/S | 15 | 561829.7499 | 563173.3752 | 477921.1318 | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 0 | 11 | 0 | DHK00198 | 1 | 48942.9 | 50244.2 | 1301.3 | 444.44 | 0 | 578349.772 | 588235.7049 | Ramna | New Ramna 33/11KV S/S | 15 | 500739.7682 | 521233.9697 | 36728.3702 | 1058898.5083 | 1085933.5304
39 | TNT RMU | D315Z | 11 | 0 | DHK 00207 | 1 | 63163 | 64037.1 | 874.1 | 444.44 | 0 | 388485.004 | 395125.5127 | Ramna | New Ramna 33/11KV S/S | 15 | 407146.495 | 424144.4724 | 438569.3066 | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 0 | 11 | 0 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 35665.375
41 | Secretariat (West) | D315W | 11 | 0 | DHK 00006 | 1 | 71279 | 72394.3 | 1115.3 | 444.44 | 0 | 495683.932 | 504156.8291 | Ramna | New Ramna 33/11KV S/S | 15 | 472288.1335 | 522274.5375 | 534325.4145 | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 0 | 11 | 0 | DHK00197 | 1 | 89195.8 | 89224 | 28.2 | 444.44 | 0 | 12533.208 | 12747.4425 | Ramna | New Ramna 33/11KV S/S | 15 | 1125.4602 | 1246464.4649 | 757545.2503 | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | D315A | 11 | 0 | DHK00186 | 1 | 33393.1 | 36023.9 | 2630.8 | 444.44 | 0 | 1169232.752 | 1189218.8524 | Ramna | New Ramna 33/11KV S/S | 15 | 1357169.9895 | 1293561.4671 | 1334026.873 | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | D3153 | 11 | 0 | DHK00030 | 1 | 55912.3 | 56404.5 | 492.2 | 444.44 | 0 | 218753.368 | 222492.5951 | Ramna | New Ramna 33/11KV S/S | 15 | 223201.274 | 228427.247 | 210464.4166 | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | D3152 | 11 | 0 | DHK 00008 | 1 | 308.7 | 443.7 | 135 | 444.44 | 0 | 59999.4 | 61024.9905 | Ramna | New Ramna 33/11KV S/S | 15 | 71264.1421 | 71075.3031 | 68978.774 | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 0 | 11 | 0 | DHK00196 | 1 | 28080.3 | 29086.7 | 1006.4 | 444.44 | 0 | 447284.416 | 454930.0034 | Motijheel | New Ramna 33/11KV S/S | 15 | 443071.1857 | 477711.0916 | 494476.0375 | 481492.0598 | 701782.0483
47 | Jail | B678Z | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 0
48 | Kosturi Bazar | D315K | 11 | 0 | HA021100713-02 | 1 | 76948472 | 77199099 | 250627 | 1 | 0 | 250627 | 254911.0541 | Ramna | New Ramna 33/11KV S/S | 15 | 109455.5914 | 110597.9648 | 782852.0054 | 108530.1819 | 101993.6695
49 | Kaptan Bazar | B124K | 11 | 0 | HA021101251-02 | 1 | 7518514 | 7930785 | 412271 | 1 | 0 | 412271 | 419318.091 | Narinda | New Ramna 33/11KV S/S | 15 | 424171.1844 | 443349.7565 | 434935.9868 | 427872.7434 | 409490.3581
50 | G.T.V | D315G | 11 | 0 | HA-021101054-02 | 1 | 72973784 | 73543399 | 569615 | 1 | 0 | 569615 | 579351.6265 | Ramna | New Ramna 33/11KV S/S | 15 | 620088.9847 | 609639.126 | 653967.7221 | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | B615K | 11 | 0 | HA021100951-02 | 1 | 7403768 | 7837719 | 433951 | 1 | 0 | 433951 | 441368.6747 | Bangshal | New Ramna 33/11KV S/S | 15 | 366764.7103 | 373997.3699 | 641935.1027 | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.4 | 0 | 2436 | 1 | 67423 | 67703 | 280 | 10 | 0 | 2800 | 2847.8614 | Ramna | New Ramna 33/11KV S/S | 15 | 0 | 0 | 0 | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.4 | 0 | 2437 | 1 | 89514 | 90000 | 486 | 10 | 0 | 4860 | 4943.0737 | Ramna | New Ramna 33/11KV S/S | 15 | 3443.9428 | 3735.9019 | 3663.8273 | 3672.2594 | 3624.4279
54 | Pioneer | D304P | 11 | 0 | 06604395 | 1 | 24062.02 | 24160.1 | 98.08 | 8000 | 0 | 784640 | 784360.9682 | Ramna | Kakrail 33/11KV S/S | 4 | 828175.4667 | 850072.0555 | 872559.2 | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | D604L | 11 | 0 | DHK-00102 | 1 | 89807.9 | 92942.8 | 3134.9 | 444.444 | 0 | 1393287.4956 | 1392792.0181 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1485476.6819 | 1494821.3647 | 1589289.5218 | 1570646.0565 | 1456807.534
56 | Montri Para | C604B | 11 | 0 | DHK-00110 | 1 | 12875.3 | 12950.5 | 75.2 | 2222.22 | 0 | 167110.944 | 167051.5164 | Kakrail | Kakrail 33/11KV S/S | 4 | 197223.0332 | 196663.3629 | 206488.6824 | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 0 | 11 | 0 | 9119865 | 1 | 70152.8 | 72383.6 | 2230.8 | 1000 | 0 | 2230800 | 2230006.6883 | Kakrail | Kakrail 33/11KV S/S | 4 | 2380457.3749 | 2409184.7946 | 2711345 | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | C604T | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0
59 | High Court | D3046 | 11 | 0 | 1025651 | 1 | 29759.6 | 30010.8 | 251.2 | 1000 | 0 | 251200 | 251110.6689 | Ramna | Kakrail 33/11KV S/S | 4 | 202322.6667 | 325169.1484 | 265125 | 281963.0422 | 304725.5352
60 | Secretaiat | 0 | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0
61 | Shanti Nagar Bazar | D604N | 11 | 0 | 06604402 | 1 | 5747.72 | 5783.83 | 36.11 | 40000 | 0 | 1444400 | 1443886.346 | Rajarbag | Kakrail 33/11KV S/S | 4 | 1590213.609 | 1510645.8477 | 1601052 | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 0 | 11 | 0 | 9119867 | 1 | 32771.1 | 32987.8 | 216.7 | 1000 | 0 | 216700 | 216622.9377 | Kakrail | Kakrail 33/11KV S/S | 4 | 242037.4816 | 236872.8291 | 224220 | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 0 | 11 | 0 | DHK00199 | 1 | 79303.3 | 79591.4 | 288.1 | 2222.22 | 0 | 640221.582 | 639993.908 | Kakrail | Kakrail 33/11KV S/S | 4 | 715946.6275 | 682140.9217 | 703183.7413 | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 0 | 11 | 0 | DHK00027 | 1 | 56972.7 | 57453.2 | 480.5 | 2222.22 | 0 | 1067776.71 | 1067396.9898 | Kakrail | Kakrail 33/11KV S/S | 4 | 1227916.0084 | 1208524.4599 | 1467416.3104 | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | D304B | 11 | 0 | D1025656 | 1 | 68966.3 | 69884.3 | 918 | 1000 | 0 | 918000 | 917673.5431 | Ramna | Kakrail 33/11KV S/S | 4 | 1028330.0287 | 1027534.5089 | 1059146.6 | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | D304F | 11 | 0 | D0086137 | 1 | 26942.9 | 27376 | 433.1 | 1000 | 0 | 433100 | 432945.982 | Ramna | Kakrail 33/11KV S/S | 4 | 472221.3068 | 517539.8234 | 576508 | 916863.5723 | 907912.3538
67 | Judges Complex | C604JC | 11 | 0 | 06604344 | 1 | 681.42 | 684.38 | 2.96 | 40000 | 0 | 118400 | 118357.8949 | Kakrail | Kakrail 33/11KV S/S | 4 | 136165.0797 | 135933.8524 | 151904 | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 0 | 11 | 0 | 39333 | 1 | 492441 | 496195 | 3754 | 1 | 0 | 3754 | 3752.665 | Kakrail | Kakrail 33/11KV S/S | 4 | 0 | 0 | 0 | 0 | 0
69 | Auxiliary Transformer, AT-2 | 0 | 11 | 0 | 39254 | 1 | 1226887 | 1228762 | 1875 | 1 | 0 | 1875 | 1874.3332 | Kakrail | Kakrail 33/11KV S/S | 4 | 6333.0946 | 25918.4591 | 0 | 0 | 0
70 | 11 kV Jamuna (F1) | C6101JG | 11 | 0 | BD017073 | 1 | 0.39 | 0.4073 | 0.0173 | 2000 | 0 | 34.6 | 34.3292 | Kakrail | BSMMU 33/11KV S/S | 101 | 8.7511 | 22.0654 | 24.7258 | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | C6101PP | 11 | 0 | BD017074 | 1 | 2970.98 | 2992.52 | 21.54 | 2000 | 0 | 43080 | 42742.7844 | Kakrail | BSMMU 33/11KV S/S | 101 | 43083.9288 | 43219.8277 | 44627.1399 | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | C6101BC | 11 | 0 | BD017075 | 1 | 1810.65 | 1854.6 | 43.95 | 2000 | 0 | 87900 | 87211.9487 | Kakrail | BSMMU 33/11KV S/S | 101 | 84458.3395 | 31822.749 | 77353.7092 | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | C6101UH | 11 | 0 | BD017076 | 1 | 3190.68 | 3278.62 | 87.94 | 2000 | 0 | 175880 | 174503.2711 | Kakrail | BSMMU 33/11KV S/S | 101 | 172111.8499 | 179215.5198 | 177543.6485 | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | C6101HF | 11 | 0 | BD017077 | 1 | 15095.74 | 15411.85 | 316.11 | 2000 | 0 | 632220 | 627271.1967 | Kakrail | BSMMU 33/11KV S/S | 101 | 702896.8986 | 697529.5567 | 750881.7825 | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | C6101NH | 11 | 0 | BD017078 | 1 | 27279.48 | 27649.1 | 369.62 | 2000 | 0 | 739240 | 733453.4805 | Kakrail | BSMMU 33/11KV S/S | 101 | 641089.6752 | 636961.0675 | 681006.1346 | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | C31016 | 11 | 0 | BD017079 | 1 | 33539.9 | 34271.31 | 731.41 | 2000 | 0 | 1462820 | 1451369.5422 | Paribag | BSMMU 33/11KV S/S | 101 | 1603019.2834 | 1597412.9298 | 1675286.7504 | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | C3101CB | 11 | 0 | BD017080 | 1 | 6815.21 | 7006.17 | 190.96 | 2000 | 0 | 381920 | 378930.46 | Paribag | BSMMU 33/11KV S/S | 101 | 414273.243 | 428837.8596 | 457910.6397 | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | C3101OC | 11 | 0 | BD017083 | 1 | 2433.64 | 2501.72 | 68.08 | 2000 | 0 | 136160 | 135094.1858 | Paribag | BSMMU 33/11KV S/S | 101 | 140648.5745 | 143344.075 | 137962.1897 | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | C6101RT | 11 | 0 | BD017084 | 1 | 1489.37 | 1616.91 | 127.54 | 2000 | 0 | 255080 | 253083.3205 | Kakrail | BSMMU 33/11KV S/S | 101 | 267336.0837 | 281930.9324 | 302057.3893 | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | C6101SN | 11 | 0 | BD017085 | 1 | 2231.75 | 2282.95 | 51.2 | 2000 | 0 | 102400 | 101598.4476 | Kakrail | BSMMU 33/11KV S/S | 101 | 113805.0685 | 114841.2565 | 122402.9977 | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | C3101RM | 11 | 0 | BD017086 | 1 | 2219.41 | 2299.99 | 80.58 | 2000 | 0 | 161160 | 159898.4943 | Paribag | BSMMU 33/11KV S/S | 101 | 165660.4538 | 173668.8065 | 174287.0734 | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | C3101DB | 11 | 0 | BD017087 | 1 | 4386.63 | 4503.32 | 116.69 | 2000 | 0 | 233380 | 231553.1807 | Paribag | BSMMU 33/11KV S/S | 101 | 239475.0074 | 241970.3048 | 234654.3262 | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | C3101BA | 11 | 0 | BD017088 | 1 | 1086.59 | 1117.1 | 30.51 | 2000 | 0 | 61020 | 60542.3562 | Paribag | BSMMU 33/11KV S/S | 101 | 62295.6571 | 66843.9677 | 56065.3573 | 59004.3933 | 75292.0174
84 | Spare | 0 | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 0 | 0 | 0 | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | C310113 | 11 | 0 | BD017090 | 1 | 1923.81 | 2155.2 | 231.39 | 2000 | 0 | 462780 | 459157.5154 | Paribag | BSMMU 33/11KV S/S | 101 | 528668.5024 | 530318.42 | 510819.9335 | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKD4418 | 1 | 2965 | 2965 | 0 | 100 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 101 | 6033.1746 | 14842.5188 | 15407.4195 | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 1754.5 | 1877.04 | 122.54 | 100 | 0 | 12254 | 12158.0799 | Paribag | BSMMU 33/11KV S/S | 101 | 8446.8515 | 487.8678 | 0 | 0 | 0
88 | Chata Mosjid | 0 | 11 | 0 | 0 | 1 | 176550.2 | 178961 | 2410.8 | 1000 | 0 | 2410800 | 2448059.1892 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 109 | 2307606.3907 | 2543835.8742 | 2199148.6226 | 2319503.7751 | 2426211.3577
89 | AC mosjid | A3109X | 11 | 0 | 0 | 1 | 9113.5192 | 10394.041 | 1280.5218 | 1000 | 0 | 1280521.8 | 1300312.4106 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1258989.8828 | 1405178.1975 | 1152835.6866 | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | A3109K | 11 | 0 | 0 | 1 | 25413.274 | 27738.754 | 2325.48 | 1000 | 0 | 2325480 | 2361420.5589 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2255488.3746 | 2390177.1556 | 2000565.9387 | 2224217.61 | 2267338.6868
91 | Nazimuddin | A3109M | 11 | 0 | 0 | 1 | 6536.8212 | 7287.9168 | 751.0956 | 1000 | 0 | 751095.6 | 762703.8683 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 950975.5456 | 925339.67 | 477977.0793 | 0 | 0
92 | Kamal Bagh | A3109U | 11 | 0 | 0 | 1 | 18105.986 | 20174.008 | 2068.022 | 1000 | 0 | 2068022 | 2099983.5161 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1567737.0505 | 1686096.534 | 1618577.1268 | 1589844.4629 | 1583845.5588
93 | Rahamatganj | A3109B | 11 | 0 | 0 | 1 | 15585.779 | 18036.49 | 2450.711 | 1000 | 0 | 2450711 | 2488587.0183 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2323808.6258 | 2495628.7814 | 2157043.5386 | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 0 | 11 | 0 | 0 | 1 | 2538.9734 | 4448.2884 | 1909.315 | 1000 | Estimated | 1824492.6 | 1852690.3414 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1787173.2312 | 1980277.4376 | 1747210.9883 | 1862323.276 | 1854345.8684
95 | City Colony | A3109J | 11 | 0 | 0 | 1 | 28562.332 | 1465.432 | -27096.9 | 1000 | Meter Reset | 2166842 | 2200330.7905 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2079469.3659 | 2219309.3581 | 1859682.1079 | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 0 | 11 | 0 | 0 | 1 | 4678.0648 | 7701.988 | 3023.9232 | 1000 | Estimated | 2675922.48 | 2717279.1674 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2859477.1699 | 2599114.1368 | 2790703.3917 | 2997202.1128 | 3092062.2371
97 | Chun Goli | A3109H | 11 | 0 | 0 | 1 | 716.9223 | 1678.5962 | 961.6739 | 1000 | 0 | 961673.88 | 976536.6596 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 927964.1813 | 983357.245 | 754718.4448 | 841380.8401 | 894878.3402
98 | Alir Ghat | A3109L | 11 | 0 | 0 | 1 | 125330.2 | 127347 | 2016.8 | 1000 | 0 | 2016800 | 2047969.8743 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 1928133.7897 | 2137361.0725 | 1734165.991 | 1904122.5273 | 2096766.6729
99 | Club Ghat | A3109C | 11 | 0 | 0 | 1 | 21816.792 | 24630.07 | 2813.278 | 1000 | 0 | 2813278 | 2856757.5327 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2651623.7603 | 2977501.1852 | 2317579.0304 | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | A3109V | 11 | 0 | 0 | 1 | 34120.9 | 1744.5846 | -32376.3154 | 1000 | Meter Reset | 2668920.6 | 2710169.0726 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 2405552.6316 | 2718263.3522 | 2261609.1864 | 2437761.5097 | 2619436.8857
101 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 109 | 0 | 0 | 0 | 0 | 0
102 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
103 | Sowari Ghat | A319R | 11 | 0 | 8838019 | 1 | 82662.7 | 83080.1 | 417.4 | 1000 | Estimated | 2797555.32 | 2802102.8851 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 2638720.3862 | 2802348.4469 | 2329233.6447 | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | A3202 | 11 | 0 | 8838014 | 1 | 82451 | 82569.1 | 118.1 | 1000 | Estimated | 621678.96 | 622689.53 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 658473.4491 | 560200.422 | 121854.324 | 118483.0867 | 132959.886
105 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
106 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
107 | Eidgah | A320A | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1367693.712 | 1369916.966 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1376808.1209 | 1431623.3008 | 1096688.9157 | 1303313.9541 | 1329598.8604
108 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
109 | Modumoti | A3201 | 11 | 0 | 0 | 1 | 101250 | 101250 | 0 | 444.44 | Estimated | 2238044.256 | 2241682.3081 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1975420.3474 | 2116312.7055 | 1584106.2116 | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | A320Y | 11 | 0 | 61389152 | 1 | 442226 | 442711 | 485 | 1000 | Estimated | 1119022.128 | 1120841.154 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 1197224.4529 | 1244889.8267 | 1181986.9425 | 1066347.7806 | 1087853.6131
111 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
112 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
113 | Water Works 11 kV Sw/S-2 | A320G | 11 | 0 | 61389109 | 1 | 403760 | 404617 | 857 | 1000 | 0 | 857000 | 858393.0961 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 972107.7743 | 1045286.2834 | 874589.6653 | 951212.9635 | 980831.1601
114 | Islambagh | A320D | 11 | 0 | 61389186 | 1 | 501801 | 502493 | 692 | 1000 | 0 | 692000 | 693124.8804 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 855693.6396 | 941158.1479 | 774407.5731 | 861627.8273 | 876487.4197
115 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
116 | WASA Low Lift Pump | A320F | 11 | 0 | 61389202 | 1 | 15646 | 15689 | 43 | 1000 | 0 | 43000 | 43069.8986 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 55719.5858 | 56068.996 | 57103.7926 | 61401.0484 | 45712.4958
117 | Shahi Mosjid | D920M | 11 | 0 | 06604459 | 1 | 36252.8 | 36418.54 | 165.74 | 8000 | 0 | 1325920 | 1328075.3488 | Azimpur | Lalbagh Old 33/11KV S/S | 20 | 1734152.7099 | 1661564.6485 | 1773623.7611 | 1752245.002 | 1250534.8854
118 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 0 | 0 | 0 | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | 5395822 | 1 | 47309.6 | 60635.8 | 13326.2 | 1 | 0 | 13326.2 | 13347.8624 | Lalbag | Lalbagh Old 33/11KV S/S | 20 | 8792.8491 | 9867.6427 | 0 | 0 | 0
120 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0
121 | Spare | 0 | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0
122 | Chawk Bazar | A319Z | 11 | 0 | DHK-60904 | 1 | 988642.8 | 997275.1 | 8632.3 | 60 | 0 | 517938 | 524398.7147 | Lalbag | Mitford 33/11 kV | 88 | 501841.8638 | 526171.1474 | 480516.9276 | 522405.3875 | 508276.2976
123 | Spare | 0 | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0
124 | Chatrabas | B688D | 11 | 0 | DHK-66485 | 1 | 857675 | 863260 | 5585 | 60 | 0 | 335100 | 339280.009 | Bangshal | Mitford 33/11 kV | 88 | 1110389.3159 | 1353014.9285 | 1237900.3837 | 762976.1234 | 353557.5482
125 | Begum Bazar | B678G | 11 | 0 | DHK-66481 | 1 | 3748981 | 3787572 | 38591 | 60 | 0 | 2315460 | 2344342.8516 | Bangshal | Mitford 33/11 kV | 88 | 2422961.4211 | 2446646.3554 | 2397460.098 | 2421237.7604 | 2357293.0663
126 | SCC ROAD | B688R | 11 | 0 | DHK-60901 | 1 | 130309.7 | 157171.5 | 26861.8 | 60 | 0 | 1611708 | 1631812.3089 | Bangshal | Mitford 33/11 kV | 88 | 1626362.4279 | 1682445.687 | 1526989.2348 | 1650255.6547 | 1574186.7645
127 | Spare | 0 | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0
128 | Armanitola | B619A | 11 | 0 | DHK-61104 | 1 | 717808.9 | 733048.2 | 15239.3 | 60 | 0 | 914358 | 925763.6241 | Bangshal | Mitford 33/11 kV | 88 | 975265.6139 | 991422.0466 | 974917.2355 | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 0 | 11 | 0 | DHK-61101 | 1 | 410380.5 | 418515.6 | 8135.1 | 60 | 0 | 488106 | 494194.5928 | Bangshal | Mitford 33/11 kV | 88 | 534862.6587 | 551030.4718 | 539101.6117 | 513839.5885 | 528540.0121
130 | Emamganj | B688I | 11 | 0 | DHK-68130 | 1 | 1459.36 | 1478.28 | 18.92 | 60000 | 0 | 1135200 | 1149360.3885 | Bangshal | Mitford 33/11 kV | 88 | 350737.4618 | 168709.5633 | 161982.5873 | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | A319T | 11 | 0 | DHK-68129 | 1 | 1226.82 | 1226.82 | 0 | 60000 | 0 | 0 | 0 | Lalbag | Mitford 33/11 kV | 88 | 0 | 84652.8551 | 538371.2175 | 628439.5052 | 594724.3345
132 | Spare | 0 | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 88 | 0 | 0 | 0 | 0 | 0
133 | Panghat | B688P | 11 | 0 | DHK-68127 | 1 | 1573.97 | 1597.26 | 23.29 | 60000 | 0 | 1397400 | 1414831.0491 | Bangshal | Mitford 33/11 kV | 88 | 1293419.2063 | 1420021.8363 | 1363598.8715 | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | U0004460 | 1 | 5674.73 | 5717.83 | 43.1 | 100 | 0 | 4310 | 4363.7626 | Bangshal | Mitford 33/11 kV | 88 | 4064.0057 | 3905.7556 | 3927.8323 | 4152.4762 | 4434.1352
135 | Chadni chwok | 0 | 11 | 0 | DHK60916 | 1 | 433697 | 444571 | 10874 | 60 | 0 | 652440 | 659849.4891 | Paribag | Azimpur 33/11 KV | 66 | 735121.5421 | 735452.5478 | 623153.8648 | 792142.0147 | 648152.1238
136 | BGB | 0 | 11 | 0 | DHK61090 | 1 | 702252 | 714040 | 11788 | 60 | 0 | 707280 | 715312.2841 | Jigatola | Azimpur 33/11 KV | 66 | 771727.6444 | 791117.6745 | 677536.8748 | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | D920P | 11 | 0 | DHK61091 | 1 | 852708 | 888592 | 35884 | 60 | 0 | 2153040 | 2177491.1776 | Azimpur | Azimpur 33/11 KV | 66 | 2180695.2965 | 2262756.8158 | 2133225.2763 | 2225341.7622 | 2144033.6462
138 | Azimpur | D901P | 11 | 0 | DHK61086 | 1 | 339578 | 356695 | 17117 | 60 | 0 | 1027020 | 1038683.4379 | Azimpur | Azimpur 33/11 KV | 66 | 1153765.578 | 1156672.3968 | 1153479.4596 | 1136633.6642 | 1104066.6214
139 | Aazd | D901Z | 11 | 0 | DHK61089 | 1 | 26709 | 47477 | 20768 | 60 | 0 | 1246080 | 1260231.211 | Azimpur | Azimpur 33/11 KV | 66 | 1354793.0694 | 1347891.2826 | 1333174.551 | 1318714.278 | 1257709.9294
140 | Dayra Sharif | D966D | 11 | 0 | DHK61088 | 1 | 549813 | 566604 | 16791 | 60 | 0 | 1007460 | 1018901.3032 | Azimpur | Azimpur 33/11 KV | 66 | 1035744.5659 | 1040264.9944 | 1036318.7466 | 1007533.0284 | 980271.2172
141 | Naya palton | D966U | 11 | 0 | DHK86065 | 1 | 1957.04 | 1983.32 | 26.28 | 60000 | 0 | 1576800 | 1594707.0602 | Azimpur | Azimpur 33/11 KV | 66 | 1776436.6019 | 1764768.0283 | 1711787.3638 | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | D966V | 11 | 0 | DHK66477 | 1 | 1657953 | 1680319 | 22366 | 60 | 0 | 1341960 | 1357200.0802 | Azimpur | Azimpur 33/11 KV | 66 | 1489035.8491 | 1488032.8269 | 1499973.4477 | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | D966W | 11 | 0 | DHK66480 | 1 | 4056431 | 4079743 | 23312 | 60 | 0 | 1398720 | 1414604.6799 | Azimpur | Azimpur 33/11 KV | 66 | 1497238.5543 | 1598200.8415 | 1506117.3895 | 1034936.4652 | 1287496.6695
144 | Lalbagh | D920L | 11 | 0 | DHK61093 | 1 | 806952 | 844380 | 37428 | 60 | 0 | 2245680 | 2271183.2515 | Azimpur | Azimpur 33/11 KV | 66 | 2469993.6901 | 2465781.6021 | 2471750.3893 | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | D366J | 11 | 0 | DHK66497 | 1 | 1263879 | 1273675 | 9796 | 60 | 0 | 587760 | 594434.9453 | Ramna | Azimpur 33/11 KV | 66 | 771237.9306 | 746279.7208 | 668533.8709 | 616760.0188 | 675859.2968
146 | Eden College | D966E | 11 | 0 | DHK60917 | 1 | 949453 | 957512 | 8059 | 60 | 0 | 483540 | 489031.3622 | Azimpur | Azimpur 33/11 KV | 66 | 487693.6736 | 503127.1069 | 450271.8574 | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | D902N | 11 | 0 | DHK60918 | 1 | 500487 | 510949 | 10462 | 60 | 0 | 627720 | 634848.7543 | Azimpur | Azimpur 33/11 KV | 66 | 693863.1593 | 681133.1714 | 683984.9722 | 653358.8311 | 648152.1238
148 | BUET | D366BU | 11 | 0 | DHK66496 | 1 | 995361 | 1008669 | 13308 | 60 | 0 | 798480 | 807548.0045 | Ramna | Azimpur 33/11 KV | 66 | 1180516.1912 | 815830.544 | 798043.2987 | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIG2780 | 1 | 397640 | 401869 | 4229 | 1 | 0 | 4229 | 4277.027 | Azimpur | Azimpur 33/11 KV | 66 | 4444.1522 | 3986.2756 | 4092.9197 | 4399.774 | 2203.9333
150 | Rasulpur | F120R | 11 | 0 | HA-021101042-02 | 1 | 94974148 | 96619539 | 1645391 | 1 | 0 | 1645391 | 1665082.8173 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1532049.0872 | 1584215.5272 | 1403442.4135 | 1475786.882 | 1248201.2259
151 | Bheribadh | F120B | 11 | 0 | HA-021101105-02 | 1 | 69430726 | 71909539 | 2478813 | 1 | 0 | 2478813 | 2508479.0993 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2458320.6942 | 2620926.9562 | 2327005.5404 | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | F140F | 11 | 0 | 30799521 | 1 | 2647.1 | 2651.27 | 4.17 | 60000 | 0 | 250200 | 253194.3598 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 408741.1592 | 362911.631 | 314576.4303 | 364934.8739 | 488122.7019
153 | Panna Battery Express | F140E | 11 | 0 | DHK15431 | 1 | 5316.56 | 5329.54 | 12.98 | 60000 | 0 | 778800 | 788120.5732 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1093857.5249 | 1220535.5698 | 1068349.9537 | 1060687.1709 | 1118589.0702
154 | Eidgah | F140I | 11 | 0 | 30799460 | 1 | 5447.79 | 5487.62 | 39.83 | 60000 | 0 | 2389800 | 2418400.8037 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2321919.4185 | 2480917.8558 | 2121576.0406 | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | D840L | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 40 | 0 | 0 | 0 | 0 | 0
156 | Huzur Para | F140H | 11 | 0 | HA-021101055-02 | 1 | 5268360 | 7396376 | 2128016 | 1 | 0 | 2128016 | 2153483.8082 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1914978.8856 | 2163917.8156 | 1832748.4977 | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | F103K | 11 | 0 | HA-021101015-02 | 1 | 24970453 | 27010939 | 2040486 | 1 | 0 | 2040486 | 2064906.2609 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1863929.1371 | 2041804.9994 | 1873617.2189 | 1726065.7983 | 1737567.1439
158 | Munshihati | F140T | 11 | 0 | HA-021100854-02 | 1 | 54153098 | 55432498 | 1279400 | 1 | 0 | 1279400 | 1294711.6864 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1345431.4782 | 1376742.8712 | 1392932.3343 | 1212171.698 | 1205376.9608
159 | Jhawchar | F140J | 11 | 0 | HA-021101028-02 | 1 | 3313797 | 4801619 | 1487822 | 1 | 0 | 1487822 | 1505628.0528 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1566579.6466 | 1562224.2267 | 1438582.214 | 1425641.3374 | 1328999.0751
160 | RMU Express | F140D | 11 | 0 | HA-021101248-02 | 1 | 7266805 | 7971838 | 705033 | 1 | 0 | 705033 | 713470.7397 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 717231.4507 | 658611.0471 | 606779.6203 | 633839.2782 | 704501.3661
161 | Koyla Ghat | F140C | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 1885309.02 | 1907872.1438 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2053915.4269 | 2183072.3937 | 1900877.505 | 2223108.4368 | 1816011.9444
162 | Muslimbagh | F140M | 11 | 0 | HA-021100908-02 | 1 | 29521497 | 31186206 | 1664709 | 1 | 0 | 1664709 | 1684632.0125 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 1681378.5129 | 1753494.5949 | 1596522.772 | 1696945.1326 | 1737474.4882
163 | Noyagaon | F140Y | 11 | 0 | HA-021101087-02 | 1 | 11442008 | 13945688 | 2503680 | 1 | 0 | 2503680 | 2533643.7042 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2800404.9743 | 2891878.4964 | 2674100.301 | 2742632.8101 | 2660587.4202
164 | Nurbagh | F140N | 11 | 0 | HA-021100982-02 | 1 | 27383988 | 27383988 | 0 | 1 | ESTIMATED | 2073839.922 | 2098659.3582 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2062025.6114 | 2315958.5809 | 1868573.9135 | 2159293.4513 | 2300317.433
165 | Ali Nagar | F140A | 11 | 0 | HA-021101022-02 | 1 | 26869929 | 29006769 | 2136840 | 1 | 0 | 2136840 | 2162413.4126 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 40 | 2438442.3104 | 2505512.4752 | 2290198.0816 | 2360084.8023 | 2402380.2856
166 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
167 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
168 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
169 | Nababgonj Park | D920K | 11 | 0 | 0 | 1 | 11240690 | 12267110 | 1026420 | 1 | 0 | 1026420 | 1028840.1279 | Azimpur | BGB 33/11 KV S/S | 104 | 1022665.2071 | 1042273.5833 | 1021134.2367 | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | F1104O | 11 | 0 | 0 | 1 | 82820712 | 85905840 | 3085128 | 1 | 0 | 3085128 | 3092402.2195 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2773618.4692 | 2851658.6512 | 2502740.2728 | 2762472.0542 | 2841690.4191
171 | Khalpar | F1104L | 11 | 0 | 0 | 1 | 87460992 | 89399920 | 1938928 | 1 | 0 | 1938928 | 1943499.6703 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 1539343.6525 | 1698814.3914 | 1298185.7875 | 1375644.1828 | 1437529.7992
172 | Shahidnagar | D920S | 11 | 0 | 0 | 1 | 19879410 | 21734350 | 1854940 | 1 | 0 | 1854940 | 1859313.6405 | Azimpur | BGB 33/11 KV S/S | 104 | 1906528.5825 | 1984753.7699 | 1856790.3941 | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | D9104G | 11 | 0 | 0 | 1 | 35499580 | 36808688 | 1309108 | 1 | 0 | 1309108 | 1312194.6593 | Azimpur | BGB 33/11 KV S/S | 104 | 1412422.3679 | 1466652.5091 | 1458588.073 | 1375749.2129 | 1318685.5995
174 | Ganaktuli | D8104J | 11 | 0 | 0 | 1 | 25294590 | 26164070 | 869480 | 1 | 0 | 869480 | 871530.0895 | Jigatola | BGB 33/11 KV S/S | 104 | 914191.5251 | 939625.3117 | 882817.4598 | 725654.1445 | 693078.4919
175 | Thana | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
176 | Bot Tola Mazar | D8104L | 11 | 0 | 0 | 1 | 36479882 | 38561747 | 2081865 | 1 | 0 | 2081865 | 2086773.692 | Jigatola | BGB 33/11 KV S/S | 104 | 2120352.147 | 2064384.9311 | 2207948.9744 | 2074198.5352 | 1909183.4664
177 | Sikder Medical | D8104K | 11 | 0 | 0 | 1 | 38097980 | 39247632 | 1149652 | 1 | 0 | 1149652 | 1152362.6885 | Jigatola | BGB 33/11 KV S/S | 104 | 1220473.4868 | 1221157.6998 | 1181050.1989 | 1134381.9061 | 1138392.2283
178 | Gas Field | F1104G | 11 | 0 | 0 | 1 | 58228168 | 60444680 | 2216512 | 1 | 0 | 2216512 | 2221738.1672 | Kamrangirchar | BGB 33/11 KV S/S | 104 | 2114640.3455 | 2213538.6558 | 2063276.8361 | 2061072.7993 | 1985612.1672
179 | Hazaribagh | D8104H | 11 | 0 | 0 | 1 | 42939672 | 44324280 | 1384608 | 1 | 0 | 1384608 | 1387872.6757 | Jigatola | BGB 33/11 KV S/S | 104 | 1512565.9182 | 1534113.0489 | 1525507.7666 | 1485016.8997 | 1465699.7946
180 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
181 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 104 | 0 | 0 | 0 | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 0 | 1 | 2240.9 | 2295.89 | 54.99 | 10 | 0 | 549.9 | 551.1966 | Azimpur | BGB 33/11 KV S/S | 104 | 644.3721 | 611.8898 | 0 | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 1812.98 | 1866.97 | 53.99 | 10 | 0 | 539.9 | 541.173 | Azimpur | BGB 33/11 KV S/S | 104 | 593.9263 | 558.558 | 0 | 0 | 0
184 | Salek Garden | 0 | 11 | 0 | 2761 | 1 | 678.24 | 718.18 | 39.94 | 60000 | 0 | 2396400 | 2402250.1859 | Jigatola | Jigatola New 33/11 KV S/S |  | 2551916.8348 | 2553649.2193 | 2650896.5462 | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 0 | 11 | 0 | 2850 | 1 | 529.26 | 557.19 | 27.93 | 60000 | 0 | 1675800 | 1679891.0289 | Jigatola | Jigatola New 33/11 KV S/S |  | 1793125.2848 | 1780723.9511 | 1886527.6034 | 1807426.7227 | 1737565.9216
186 | Modina Rayer Bazar | 0 | 11 | 0 | 2851 | 1 | 628.51 | 628.51 | 0 | 60000 | 0 | 0 | 0 | Switching | Jigatola New 33/11 KV S/S |  | 0 | 0
187 | City College | 0 | 11 | 0 | 2784 | 1 | 568.46 | 596.23 | 27.77 | 60000 | 0 | 1666200 | 1670267.593 | Jigatola | Jigatola New 33/11 KV S/S |  | 1742699.2641 | 1753162.2749 | 1830510.0213 | 1777383.0604 | 2346194.6487
188 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0
189 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0
190 | Post Office | 0 | 11 | 0 | 2836 | 1 | 441.51 | 467.42 | 25.91 | 60000 | 0 | 1554600 | 1558395.1507 | Jigatola | Jigatola New 33/11 KV S/S |  | 1658055.5864 | 1646510.5712 | 1676311.0857 | 1671629.3692 | 1589764.671
191 | Leather Institute | 0 | 11 | 0 | 2835 | 1 | 58.33 | 58.33 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 57222.2613 | 189875.9456 | 195265.8799
192 | Mina Bazar | 0 | 11 | 0 | 2853 | 1 | 218 | 229 | 11 | 60000 | 0 | 660000 | 661611.218 | Jigatola | Jigatola New 33/11 KV S/S |  | 704163.3609 | 701025.2432 | 763766.6032 | 746284.571 | 706562.076
193 | Mitali | 0 | 11 | 0 | 2852 | 1 | 470.64 | 519.49 | 48.85 | 60000 | 0 | 2931000 | 2938155.2725 | Switching | Jigatola New 33/11 KV S/S |  | 3066382.3082 | 3083312.7364
194 | Road-2 | 0 | 11 | 0 | 2839 | 1 | 702.58 | 742.81 | 40.23 | 60000 | 0 | 2413800 | 2419692.6635 | Jigatola | Jigatola New 33/11 KV S/S |  | 2344809.964 | 2360717.4857 | 2376832.0316 | 2301945.4038 | 2450136.1786
195 | SS-2 | 0 | 11 | 0 | 2838 | 1 | 332.13 | 352.5 | 20.37 | 60000 | 0 | 1222200 | 1225183.6827 | Jigatola | Jigatola New 33/11 KV S/S |  | 1208423.5682 | 1244469.5984 | 1139024.1692 | 1127238.2087 | 1112715.1061
196 | Spare | 0 | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S |  | 0 | 0 | 0 | 0 | 0
197 | Bou Bazar | 0 | 11 | 0 | 2843 | 1 | 566.17 | 596.66 | 30.49 | 60000 | 0 | 1829400 | 1833866.0032 | Jigatola | Jigatola New 33/11 KV S/S |  | 1887974.2286 | 1919131.4991 | 1882311.2263 | 1850088.7231 | 1774816.6433
198 | BGB | 0 | 11 | 0 | 2764 | 1 | 194.41 | 201.95 | 7.54 | 60000 | 0 | 452400 | 453504.4167 | Jigatola | Jigatola New 33/11 KV S/S |  | 461638.2136 | 445780.1547 | 580655.3671 | 1007063.5596 | 934872.9509
199 | Dhamondi-12 | 0 | 11 | 0 | 2763 | 1 | 461.94 | 487.48 | 25.54 | 60000 | 0 | 1532400 | 1536140.9551 | Dhanmondi | Jigatola New 33/11 KV S/S |  | 2054260.035 | 1641717.2362 | 1520907.4708 | 1213163.0828 | 1602982.669
200 | Lalmatia Sw/S(Dhanmondi Road 12A) | D203T | 11 | 0 | DHK60907 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
201 | Mitali Road | D803D | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
202 | Bou Bazar | D803E | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
203 | Mina Bazar | D803I | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
204 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
205 | Simanto Square | D803R | 11 | 0 | DHK60946 | 1 | 1172.18 | 1187.02 | 14.84 | 60000 | 0 | 890400 | 891294.9856 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 910570.4517 | 922404.6994 | 967800 | 852145.3731 | 901151.3428
206 | Post Office | D803P | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
207 | Hazaribagh Sw/S-2 | D803S | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
208 | Green Road Via Park | D803G | 11 | 0 | DHK61070 | 1 | 3477.14 | 3493.18 | 16.04 | 60000 | 0 | 962400 | 963367.3565 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 1108520.5499 | 1276574.4307 | 1342800 | 1229862.9154 | 476757.7712
209 | PWD Quarters 11 kV Saleq Grand | D803A | 11 | 0 | DHK61028 | 1 | 3633.07 | 3634.3 | 1.23 | 60000 | 0 | 73800 | 73874.1801 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 78580.1905 | 73359.435 | 68400 | 74813.6195 | 63933.0345
210 | Road No.-2 | D803T | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
211 | Hzaribagh O/H | D803H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
212 | B.G.B | D803B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
213 | 11 kV City College | D803C | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
214 | Jigatala Local | D803Z | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 0 | 0 | 0 | 0 | 0
215 | 33/0.4 kV Aux. Transformer AT-1 | 0 | 0.415 | 0 | 243284 | 1 | 85079 | 85276 | 197 | 10 | 0 | 1970 | 1971.9801 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 3959.002 | 5251.4131 | 3680 | 2585.0234 | 3440.2061
216 | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0.415 | 0 | 412277 | 1 | 39741 | 39890 | 149 | 10 | 0 | 1490 | 1491.4977 | Jigatola | Jigatola Old 33/11KV S/S | 3 | 769.8059 | 10.0218 | 1650 | 5393.0685 | 0
217 | Spare | 0 | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0
218 | D Block dhaka uddyan | G1103L | 11 | 0 | BD014031 | 1 | 49744.35 | 50107.2 | 362.85 | 1000 | 0 | 362850 | 367241.8104 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 387945.2586 | 382937.2777 | 364723.8055 | 376392.0985 | 356370.9019
219 | Dill Mohammad O/H | G1103DM | 11 | 0 | BD014027 | 1 | 21821.33 | 23726.2 | 1904.87 | 1000 | 0 | 1904870 | 1927925.8849 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1986501.3323 | 2019494.4174 | 1931376.746 | 1945233.0858 | 1925614.3584
220 | Turag O/H | G1103U | 11 | 0 | BD014028 | 1 | 27579.27 | 28276.4 | 697.13 | 1000 | 0 | 697130 | 705567.8194 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 641819.4994 | 770193.2072 | 703573.3851 | 725059.1327 | 419185.0275
221 | Nabadoy O/H | G1103N | 11 | 0 | BD014025 | 1 | 37467.87 | 38453.6 | 985.73 | 1000 | 0 | 985730 | 997660.9336 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 848979.0298 | 846778.6447 | 874784.3247 | 873886.7957 | 1264712.0241
222 | Chandrima O/H | G1103CH | 11 | 0 | BD014024 | 1 | 6934.23 | 7893.5 | 959.27 | 1000 | 0 | 959270 | 970880.6709 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1055645.8739 | 1037828.5358 | 998647.327 | 974655.0029 | 879754.0777
223 | Shyamoli Housing Project-2 | G1103SH | 11 | 0 | BD014029 | 1 | 29921.69 | 31072.7 | 1151.01 | 1000 | 0 | 1151010 | 1164941.4253 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 2147810.8671 | 1346057.1733 | 1686564.4606 | 1305126.5223 | 2226602.9518
224 | Spare | 0 | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0
225 | Spare | 0 | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0
226 | Spare | 0 | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 0 | 0 | 0 | 0 | 0
227 | U Lab | C2103U | 11 | 0 | BD013959 | 1 | 42134.47 | 44808.9 | 2674.43 | 1000 | 0 | 2674430 | 2706800.3719 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 2673135.1804 | 1523999.7543 | 2168216.2175 | 2766170.13 | 2585824.4138
228 | Akota | G1103AK | 11 | 0 | BD014020 | 1 | 7179.56 | 7699.4 | 519.84 | 1000 | 0 | 519840 | 526131.9628 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 548510.7365 | 553675.3788 | 518552.2147 | 529306.7232 | 494561.9781
229 | Burigonga O/H | G1103BU | 11 | 0 | BD014019 | 1 | 5489.2 | 5871.8 | 382.6 | 1000 | 0 | 382600 | 387230.8575 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 410809.9274 | 413097.2082 | 391376.3535 | 420977.1349 | 372374.7602
230 | Garden City | C2103G | 11 | 0 | BD014021 | 1 | 89647.99 | 92171 | 2523.01 | 1000 | 0 | 2523010 | 2553547.6368 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 3028251.44 | 2810059.9564 | 2804225.2436 | 2395190.4943 | 2278829.2831
231 | Avenue O/H | G1103AV | 11 | 0 | BD014017 | 1 | 15004.61 | 15936.5 | 931.89 | 1000 | 0 | 931890 | 943169.2729 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1027773.9029 | 1034448.2826 | 977183.594 | 966250.121 | 894892.5874
232 | Chand Uddyan | C2103D | 11 | 0 | BD014018 | 1 | 9747.36 | 10428.5 | 681.14 | 1000 | 0 | 681140 | 689384.282 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 103 | 764257.0863 | 760476.2406 | 759432.9748 | 732469.8888 | 645275.1572
233 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4416 | 1 | 1851.08 | 1888.5 | 37.42 | 100 | 0 | 3742 | 3787.2919 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 1595.7005 | 3776.8023 | 3734.949 | 3966.4616 | 1513.851
234 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4412 | 1 | 283.05 | 283.05 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 103 | 3189.39 | 0 | 0 | 0 | 2409.7413
235 | Lalmatia O/H | C209M | 11 | 0 | DHK61042 | 1 | 3189.06 | 3204.12 | 15.06 | 60000 | 0 | 903600 | 911395.4616 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1251951.9192 | 1243685.3152 | 1300189.4979 | 1240075.1783 | 1343819.1874
236 | Asad Avenue (South) | C209C | 11 | 0 | DHK 60999 | 1 | 2921.88 | 2936 | 14.12 | 60000 | 0 | 847200 | 854508.8922 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1448736.6599 | 0 | 99461.5008 | 201384.8525 | 143036.2105
237 | Madrasha Road | 0 | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0
238 | Bashbari | C209H | 11 | 0 | DHK61002 | 1 | 2421.28 | 2441.86 | 20.58 | 60000 | 0 | 1234800 | 1245452.7622 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1339544.3993 | 1690928.3933 | 1784914.5226 | 1599091.6268 | 1533732.8114
239 | Road-27 | C209A | 11 | 0 | DHK61001 | 1 | 1467.19 | 1474.17 | 6.98 | 60000 | 0 | 418800 | 422413.036 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1160540.6933 | 560250.965 | 379271.8673 | 89903.952 | 435118.5562
240 | Boishakhi O/H | D209O | 11 | 0 | DHK61024 | 1 | 4186.05 | 4226.72 | 40.67 | 60000 | 0 | 2440200 | 2461251.8872 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 2676105.4034 | 2946106.036 | 2918535.965 | 3026167.0253 | 2814447.7883
241 | Katasur O/H | C209K | 11 | 0 | DHK61003 | 1 | 3653.23 | 3674.52 | 21.29 | 60000 | 0 | 1277400 | 1288420.2773 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 1430239.6103 | 1419182.7329 | 1436799.27 | 1431270.9163 | 1334804.3002
242 | Nurjahan Road | D409I | 11 | 0 | DHK61000 | 1 | 1865.6 | 1885.68 | 20.08 | 60000 | 0 | 1204800 | 1215193.9487 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1433819.6844 | 1423372.644 | 1464960.0563 | 1437863.8728 | 1376873.7739
243 | polpar over head | D209W | 11 | 0 | DHK61003 | 1 | 1869.15 | 1902.19 | 33.04 | 60000 | 0 | 1982400 | 1999502.3937 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 2133127.4955 | 2142241.6706 | 2168380.5497 | 2135518.5405 | 2016930.7661
244 | Satmosjid Housing | C209S | 11 | 0 | DHK61043 | 1 | 2828.71 | 2828.71 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 189147.2492 | 1377283.6223 | 608153.1522 | 0 | 0
245 | Physical College | C209P | 11 | 0 | DHK61041 | 1 | 3350.32 | 3391.12 | 40.8 | 60000 | 0 | 2448000 | 2469119.1787 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 2662381.786 | 2653410.8203 | 2677671.3668 | 2636583.2332 | 2184607.6683
246 | Asad Avenue (North) | D409V | 11 | 0 | DHK61022 | 1 | 2730.21 | 2730.21 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 288792.6455 | 0 | 3594.994 | 0 | 0
247 | Spare Feeder | 0 | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 0 | 0 | 0 | 0 | 0
248 | Ghraphic artch college | D209Z | 11 | 0 | DHK61023 | 1 | 1124.27 | 1148.21 | 23.94 | 60000 | 0 | 1436400 | 1448791.9887 | Dhanmondi | Satmasjid 33/11KV S/S | 9 | 1578216.0071 | 1715469.3009 | 1620743.1298 | 1570921.7218 | 1701409.7136
249 | Mohammadpur O/H | D409W | 11 | 0 | DHK61025 | 1 | 2215.45 | 2241.73 | 26.28 | 60000 | 0 | 1576800 | 1590403.2357 | Shyamoli | Satmasjid 33/11KV S/S | 9 | 1624160.2917 | 1649627.8414 | 1683655.5249 | 1660825.6738 | 1343218.1949
250 | Bosila Feeder | C209V | 11 | 0 | DHK60997 | 1 | 4147.07 | 4192.28 | 45.21 | 60000 | 0 | 2712600 | 2736001.9135 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 2540659.2659 | 2707281.1054 | 2444595.9223 | 2900301.4925 | 3015179.277
251 | 11/0.4 kV Auxiliary Transformer | 0 | 0.415 | 0 | ELIB 7375 | 1 | 5971.73 | 6093.1 | 121.37 | 60 | 0 | 7282.2 | 7345.0244 | Satmasjid | Satmasjid 33/11KV S/S | 9 | 8176.8893 | 8159.5525 | 8272.6804 | 8691.9141 | 0
252 | Dhaka Uddyan | G186D | 11 | 0 | DHK86067 | 1 | 3252.11 | 3252.83 | 0.72 | 60000 | 0 | 43200 | 43181.0046 | Adabor | Japan Garden 33/11 KV | 86 | 44366.4049 | 46170.0157 | 47362.5115 | 34177.6075 | 0
253 | Shia Mosjid | D409H | 11 | 0 | DHK60950 | 1 | 3509.16 | 3541.94 | 32.78 | 60000 | 0 | 1966800 | 1965935.1818 | Shyamoli | Japan Garden 33/11 KV | 86 | 2358614.0108 | 2312098.4465 | 2316566.3838 | 2321079.2736 | 1677029.4105
254 | Shekhar Tek | G186S | 11 | 0 | DHK60977 | 1 | 2414.59 | 2443.6 | 29.01 | 60000 | 0 | 1740600 | 1739834.6438 | Adabor | Japan Garden 33/11 KV | 86 | 2042053.7165 | 2050068.6174 | 2089945.7593 | 2160384.5576 | 1966584.1503
255 | Madrasha Road | D434D | 11 | 0 | DHK61083 | 1 | 2033.33 | 2064.99 | 31.66 | 60000 | 0 | 1899600 | 1898764.7302 | Shyamoli | Japan Garden 33/11 KV | 86 | 2311849.4219 | 1518214.0214 | 1459844.4991 | 1147648.0831 | 1148666.6379
256 | Baitul Aman Housing | G186B | 11 | 0 | DHK668115 | 1 | 4165.49 | 4208.5 | 43.01 | 60000 | 0 | 2580600 | 2579465.2888 | Adabor | Japan Garden 33/11 KV | 86 | 2865829.9369 | 2799581.8586 | 2963454.3569 | 2980047.5303 | 2714650.3131
257 | Shyamoli Square | D486G | 11 | 0 | DHK86063 | 1 | 469.86 | 475.86 | 6 | 30000 | 0 | 180000 | 179920.8525 | Shyamoli | Japan Garden 33/11 KV | 86 | 180163.5766 | 172388.0455 | 167267.6038 | 170888.0374 | 163284.9924
258 | Mohammadi Housing | G186E | 11 | 0 | DHK60948 | 1 | 3848.65 | 3873.73 | 25.08 | 60000 | 0 | 1504800 | 1504138.327 | Adabor | Japan Garden 33/11 KV | 86 | 1937732.7104 | 1867187.3865 | 2007211.2456 | 1954719.3056 | 1343295.1846
259 | Chand Housing | C286H | 11 | 0 | DHK60867 | 1 | 2195.59 | 2213.38 | 17.79 | 60000 | 0 | 1067400 | 1066930.6554 | Satmasjid | Japan Garden 33/11 KV | 86 | 1224872.5023 | 796282.8675 | 850127.1046 | 960570.6526 | 891350.9825
260 | PC Culture Housing | 0 | 11 | 0 | DHK60979 | 1 | 4153.53 | 4192.75 | 39.22 | 60000 | 0 | 2353200 | 2352165.2785 | Adabor | Japan Garden 33/11 KV | 86 | 2602029.6916 | 2565134.1168 | 2719447.494 | 2646665.9554 | 2456140.6176
261 | Mehedibagh | G186H | 11 | 0 | DHK68121 | 1 | 2360.8 | 2408.52 | 47.72 | 60000 | 0 | 2863200 | 2861941.0273 | Adabor | Japan Garden 33/11 KV | 86 | 3070874.6729 | 3016640.8933 | 3040793.1415 | 3013625.5306 | 2845397.7111
262 | 33/11 kV Incoming (Spare) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 86 | 0 | 0 | 0 | 0 | 0
263 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | 0 | 1 | 657401 | 661926 | 4525 | 1 | 0 | 4525 | 4523.0103 | Adabor | Japan Garden 33/11 KV | 86 | 4813.3552 | 5033.7309 | 5179.9 | 5393.4663 | 0
264 | Mokarom Bhabon | D3108MB | 11 | 0 | 2761 | 1 | 57.23 | 60.6 | 3.37 | 60000 | 0 | 202200 | 202329.0481 | Ramna | Dhaka University 33/11 KV S/S | 108 | 226720.401 | 207689.3161 | 186304.8566 | 168036.2342 | 191876.7922
265 | 11 kV Shaid Minar RMU | D3108SM | 11 | 0 | 2850 | 1 | 133.38 | 143.49 | 10.11 | 60000 | 0 | 606600 | 606987.1444 | Ramna | Dhaka University 33/11 KV S/S | 108 | 637120.699 | 361224.6845 | 367165.7402 | 336672.5979 | 339844.4752
266 | 11 kV Shaidulla Hall | D3108SH | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
267 | Spare | 0 | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
268 | Spare | 0 | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
269 | Spare | 0 | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
270 | MBA Bhabon | D3108MA | 11 | 0 | 2836 | 1 | 99.81 | 103.68 | 3.87 | 60000 | 0 | 232200 | 232348.1947 | Ramna | Dhaka University 33/11 KV S/S | 108 | 278853.9691 | 280291.312 | 263125.3657 | 250253.9631 | 301348.8178
271 | Suprime Court | 0 | 11 | 0 | 2835 | 1 | 60.62 | 66 | 5.38 | 60000 | 0 | 322800 | 323006.0175 | Ramna | Dhaka University 33/11 KV S/S | 108 | 284309.8076 | 352893.3079 | 353253.3645 | 298264.3158 | 306762.2696
272 | Karjon Hall | D3108KH | 11 | 0 | 2853 | 1 | 67.57 | 72.86 | 5.29 | 60000 | 0 | 317400 | 317602.5711 | Ramna | Dhaka University 33/11 KV S/S | 108 | 349779.87 | 351108.0129 | 342970.3043 | 313267.551 | 333228.0341
273 | Spare | 0 | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
274 | Swimming Pool | D3108SP | 11 | 0 | 2839 | 1 | 1.56 | 2.33 | 0.77 | 60000 | 0 | 46200 | 46229.4858 | Ramna | Dhaka University 33/11 KV S/S | 108 | 46071.5253 | 0 | 0 | 0 | 0
275 | Spare | 0 | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
276 | Police Head Quarter RMU | 0 | 11 | 0 | 2772 | 1 | 86.91 | 93.56 | 6.65 | 60000 | 0 | 399000 | 399254.6499 | Ramna | Dhaka University 33/11 KV S/S | 108 | 414643.728 | 474293.3666 | 554680.3686 | 488505.3381 | 444504.5437
277 | Spare | 0 | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
278 | Spare | 0 | 11 | 0 | 2764 | 1 | 0.36 | 1.48 | 1.12 | 60000 | Cheek Nocs & Feeder | 67200 | 67242.8884 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
279 | Spare | 0 | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 108 | 0 | 0 | 0 | 0 | 0
280 | Segunbagicha | D394S | 11 | 0 | DHK-C9360 | 1 | 3594.58 | 13326.33 | 9731.75 | 60 | 0 | 583905 | 585591.0985 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 595887.9152 | 652730.1844 | 660791.8145 | 648570.0837 | 628132.1417
281 | Secretariat RMU | D394FB | 11 | 0 | DHK-C9379 | 1 | 77044.89 | 79602.83 | 2557.94 | 60 | 0 | 153476.4 | 153919.5822 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 147122.5127 | 169088.4911 | 173479.2405 | 157347.3651 | 189151.3106
282 | NBR RMU | D394NR | 11 | 0 | DHK-C9319 | 1 | 66156.55 | 73234.86 | 7078.31 | 60 | 0 | 424698.6 | 425924.9701 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 412789.7325 | 468220.1905 | 479026.3146 | 471677.0943 | 454185.7713
283 | Ramna 11 kV Sw/S-2 | 0 | 11 | 0 | DHK-C9364 | 1 | 30272.44 | 50263.55 | 19991.11 | 60 | 0 | 1199466.6 | 1202930.2093 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 1229384.6711 | 70113.1256 | 552257.97 | 1047973.9631 | 1309281.295
284 | Ramna 11 kV Sw/S-1 | 0 | 11 | 0 | DHK-C9375 | 1 | 55044.47 | 55956.29 | 911.82 | 60 | 0 | 54709.2 | 54867.1796 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 213365.2082 | 295845.9008 | 960645.5509 | 37569.2064 | 3932.094
285 | Family Planning | D394FP | 11 | 0 | DHK-C9378 | 1 | 64525.07 | 71774.93 | 7249.86 | 60 | 0 | 434991.6 | 436247.6925 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 440914.9728 | 477616.3037 | 472965.3149 | 459978.3897 | 450311.5022
286 | Muktijuddho Montranalaya | D394MJ | 11 | 0 | DHK-C9376 | 1 | 74251.93 | 88559.61 | 14307.68 | 60 | 0 | 858460.8 | 860939.7125 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 912278.2358 | 979522.345 | 1003580.0431 | 989924.3443 | 925250.3935
287 | Purana Palton | D394R | 11 | 0 | DHK-C9318 | 1 | 60052.08 | 65821.54 | 5769.46 | 60 | 0 | 346167.6 | 347167.2021 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 309416.4011 | 349193.9997 | 350733.9486 | 318744.0733 | 328976.7665
288 | Tip Top Feeder | 0 | 11 | 0 | DHK-C9318 | 1 | 33459.86 | 70239.61 | 36779.75 | 60 | 0 | 2206785 | 2213157.3667 | Kakrail | Biddyut Bhaban 33/11 KV | 94 | 1322789.6384 | 1326276.1291 | 1389761.4375 | 1427034.1549 | 1299449.2529
289 | 11/0.4 kV Auxiliary Transformer, AT | 0 | 0.415 | 0 | DHKD3784 | 1 | 350107 | 355193 | 5086 | 1 | 0 | 5086 | 5100.6865 | Ramna | Biddyut Bhaban 33/11 KV | 94 | 4311.9923 | 4669.8501 | 4947.3654 | 4696.0253 | 4800.6724
290 | Nearest O/H | D398NE | 11 | 0 | 00000126 | 1 | 7743381 | 7943260.5 | 199879.5 | 1 | 0 | 199879.5 | 200195.8311 | Ramna | DMC 33/11 KV SS | 98 | 223877.2462 | 227289.0317 | 224820.1739 | 210729.7741 | 229906.9253
291 | Jagannath Hall | D398JA | 11 | 0 | 00000002 | 1 | 2867233 | 2968112.8 | 100879.8 | 1 | 0 | 100879.8 | 101039.4533 | Ramna | DMC 33/11 KV SS | 98 | 107985.9597 | 106229.8836 | 110593.2428 | 113276.1711 | 96242.8599
292 | Samsun Nahar Hall | D398SN | 11 | 0 | 00000024 | 1 | 10018216 | 10295055 | 276839 | 1 | 0 | 276839 | 277277.1279 | Ramna | DMC 33/11 KV SS | 98 | 321630.4227 | 329771.0476 | 322680.6125 | 293593.2672 | 312413.2678
293 | Spare, 4L | 0 | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0
294 | Board Office O/H, (5L) | A3983 | 11 | 0 | 00000023 | 1 | 22339026 | 22742504 | 403478 | 1 | 0 | 403478 | 404116.548 | Lalbag | DMC 33/11 KV SS | 98 | 474520.243 | 554924.1978 | 600144.1706 | 492983.2953 | 466712.6927
295 | OT- Complex | D398OT | 11 | 0 | 00000167 | 1 | 6728543 | 6834903.5 | 106360.5 | 1 | 0 | 106360.5 | 106528.8271 | Ramna | DMC 33/11 KV SS | 98 | 336918.4015 | 246189.5687 | 446170.5101 | 427837.7768 | 405707.0733
296 | Alia Mdrasha O/H, (7L) | A3984 | 11 | 0 | 00000148 | 1 | 9609897 | 9674696 | 64799 | 1 | 0 | 64799 | 64901.5515 | Lalbag | DMC 33/11 KV SS | 98 | 73635.9109 | 143184.6648 | 77701.5086 | 75154.3226 | 71193.4446
297 | Majed Sordar Road | B698J | 11 | 0 | 00000164 | 1 | 58563616 | 60280212 | 1716596 | 1 | 0 | 1716596 | 1719312.7006 | Bangshal | DMC 33/11 KV SS | 98 | 1747073.1814 | 1774470.2621 | 1602752.7729 | 1759301.3409 | 1689289.8138
298 | Chankharpool, 9L | B698Q | 11 | 0 | 00000001 | 1 | 49199160 | 50333796 | 1134636 | 1 | 0 | 1134636 | 1136431.6854 | Bangshal | DMC 33/11 KV SS | 98 | 1199639.3416 | 1210601.5564 | 1176945.2408 | 1201456.0712 | 1157798.1959
299 | Shahidullah College O/H, (10L) | A3986 | 11 | 0 | 00000003 | 1 | 13359607 | 13594687 | 235080 | 1 | 0 | 235080 | 235452.0398 | Lalbag | DMC 33/11 KV SS | 98 | 255337.0354 | 264888.6074 | 263222.0224 | 263967.4494 | 265403.8751
300 | Ananda Bazar | D398AB | 11 | 0 | 00000111 | 1 | 15136523 | 15255803 | 119280 | 1 | 0 | 119280 | 119468.7736 | Ramna | DMC 33/11 KV SS | 98 | 114687.4296 | 145238.9396 | 167074.5674 | 216784.0965 | 169141.9631
301 | Hosseni Dalan O/H, (12L) | A3985 | 11 | 0 | 0 | 1 | 58.94 | 62.84 | 3.9 | 60000 | Estimated | 997814.484 | 999393.6344 | Lalbag | DMC 33/11 KV SS | 98 | 862949.5725 | 1039954.5727 | 1170127.1783 | 1629339.2554 | 1651805.4359
302 | Badrun Nessa College | A398W | 11 | 0 | 00000006 | 1 | 20531070 | 20999788 | 468718 | 1 | 0 | 468718 | 469459.7974 | Lalbag | DMC 33/11 KV SS | 98 | 504253.5009 | 510636.8949 | 522687.5196 | 511348.0734 | 487810.3149
303 | Dhaka Medical College, Unit-II | D398DM | 11 | 0 | 00000125 | 1 | 12313610 | 12612529 | 298919 | 1 | 0 | 298919 | 299392.072 | Ramna | DMC 33/11 KV SS | 98 | 310172.7151 | 327495.1248 | 332597.3491 | 314783.3957 | 318669.3545
304 | Spare, 15L | 0 | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0
305 | Sheikh Hasina National Burn Institute | D398SH | 11 | 0 | 00000127 | 1 | 21432388 | 21974666 | 542278 | 1 | 0 | 542278 | 543136.2141 | Ramna | DMC 33/11 KV SS | 98 | 551404.561 | 585271.851 | 637362.5402 | 594088.462 | 527600.9918
306 | Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKF-7804 | 1 | 2796.2 | 2872.86 | 76.66 | 100 | 0 | 7666 | 7678.1323 | Ramna | DMC 33/11 KV SS | 98 | 7994.6127 | 7937.0165 | 8829.1604 | 8254.0596 | 7320.9952
307 | Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 98 | 0 | 0 | 0 | 0 | 0
308 | Secratariet East | D363BS | 11 | 0 | BD 013966 | 1 | 4125.4 | 4367.4 | 242 | 1000 | 0 | 242000 | 242760.0671 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 221126.0937 | 241216.6768 | 260076.7434 | 245293.0009 | 245463.3743
309 | Taher Bag O/H | B163G | 11 | 0 | BD 014045 | 1 | 19951.23 | 20674.71 | 723.48 | 1000 | 0 | 723480 | 725752.2867 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 829864.029 | 794329.1648 | 678707.287 | 744464.9674 | 740283.3012
310 | Al Raji Complex | D363AR | 11 | 0 | BD 013983 | 1 | 15315.66 | 16069.61 | 753.95 | 1000 | 0 | 753950 | 756317.9861 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 777798.4115 | 793783.38 | 773675.1898 | 784809.8778 | 793405.3649
311 | Raduni | D363RI | 11 | 0 | BD 013999 | 1 | 29678.37 | 30757.71 | 1079.34 | 1000 | 0 | 1079340 | 1082729.9623 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 1265333.7606 | 1301100.4786 | 623159.8339 | 1293358.488 | 1280815.0384
312 | Sundor Bon Square O/H | B163D | 11 | 0 | BD 013954 | 1 | 13692.68 | 14187.74 | 495.06 | 1000 | 0 | 495060 | 496614.8713 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 482395.9106 | 519829.721 | 434096.0289 | 473931.0551 | 515871.5523
313 | Shromo Bhobon O/H | D363SB | 11 | 0 | BD 013985 | 1 | 13642.15 | 14129.96 | 487.81 | 1000 | 0 | 487810 | 489342.1006 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 495640.2335 | 516585.3335 | 525134.9167 | 505142.6077 | 521299.6391
314 | Nawabpur Road | B163P | 11 | 0 | BD 013953 | 1 | 21092.3 | 21924.28 | 831.98 | 1000 | 0 | 831980 | 834593.0606 | Narinda | BB Aveneu 33/11 KV S/S | 63 | 843248.6095 | 904941.5553 | 800366.4326 | 843066.7121 | 849749.7199
315 | Spair | 0 | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0
316 | Spare | 0 | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0
317 | Ahad Police Box | D363AP | 11 | 0 | BD 013984 | 1 | 11563.76 | 12043.51 | 479.75 | 1000 | 0 | 479750 | 481256.786 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 438024.4232 | 458924.1778 | 366641.2546 | 470281.7667 | 423970.1788
318 | Nearest O/H | D363NE | 11 | 0 | BD 013997 | 1 | 2742.58 | 2866.83 | 124.25 | 1000 | 0 | 124250 | 124640.2411 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 121402.9541 | 117384.1651 | 114763.3233 | 117912.5625 | 115595.8875
319 | Natab Bhaban | D363NB | 11 | 0 | BD 014000 | 1 | 5167.31 | 5346.21 | 178.9 | 1000 | 0 | 178900 | 179461.8844 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 187424.2009 | 177268.8886 | 180013.0381 | 185708.2311 | 177165.0302
320 | Spare | 0 | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 63 | 0 | 0 | 0 | 0 | 0
321 | Awami League Party Office | D363AO | 11 | 0 | BD 013956 | 1 | 1423.72 | 1434.02 | 10.3 | 1000 | 0 | 10300 | 10332.35 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 10118.5826 | 5579.1337 | 3568.1872 | 9417.1914 | 9250.1106
322 | Khaddar Bazar | D363KB | 11 | 0 | BD 014012 | 1 | 10515.7 | 10910.83 | 395.13 | 1000 | 0 | 395130 | 396371.0138 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 401687.6915 | 409449.7945 | 392931.5775 | 394275.1992 | 392631.6173
323 | Bangobondu National Stidium | D363NS | 11 | 0 | BD 014008 | 1 | 9133.78 | 10449.23 | 1315.45 | 1000 | 0 | 1315450 | 1319581.5303 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 1315375.6615 | 1298280.5904 | 390265.4601 | 288658.7112 | 290128.194
324 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKH4418 | 1 | 1326.39 | 1407.54 | 81.15 | 100 | 0 | 8115 | 8140.4874 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 6640.1946 | 13693.1347 | 0 | 0 | 1718.8942
325 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHKH4413 | 1 | 48.11 | 48.11 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 63 | 30.0552 | 597.3312 | 0 | 0 | 387.2849
326 | 11 KV Ring Road Feeder | G134R | 11 | 0 | 77816675 | 1 | 42213.06 | 42349.9 | 136.84 | 8000 | 0 | 1094720 | 1122088 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1191132 | 1186458 | 1209910 | 1172682 | 1124384
327 | 11 KV Gano Bhavan RMU | D534T | 11 | 0 | DHK14997 | 1 | 995.82 | 995.87 | 0.05 | 40000 | 0 | 2000 | 2050 | Shere b.nagar | Kallyanpur 33/11KV S/S | 34 | 2050 | 1230 | 1230 | 1230 | 1230
328 | 11 KV Adabor O/H | D434A | 11 | 0 | DHK14957 | 1 | 4531.62 | 4583.3 | 51.68 | 40000 | 0 | 2067200 | 2118880 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2481320 | 2098790 | 1976610 | 2150040 | 2995460
329 | 11 KV Goidertek (DPDC) | G134G | 11 | 0 | DHK14996 | 1 | 9399.97 | 9414.91 | 14.94 | 40000 | 0 | 597600 | 612540 | Adabor | Kallyanpur 33/11KV S/S | 34 | 617460 | 614590 | 586300 | 591220 | 558420
330 | 11 KV Beribandh Feeder. | G134K | 11 | 0 | DHK14960 | 1 | 9660.49 | 9667.45 | 6.96 | 40000 | 0 | 278400 | 285360 | Adabor | Kallyanpur 33/11KV S/S | 34 | 348090 | 239440 | 234930 | 301350 | 184500
331 | 11 KV Sewarage Pump | G134P | 11 | 0 | DHK14959 | 1 | 2228.14 | 2296.25 | 68.11 | 40000 | 0 | 2724400 | 2792510 | Adabor | Kallyanpur 33/11KV S/S | 34 | 1776530 | 2952000 | 2380460 | 2601450 | 535870
332 | 11 KV Technical School (DPDC) | G134T | 11 | 0 | DHK15019 | 1 | 8308.18 | 8361.96 | 53.78 | 40000 | 0 | 2151200 | 2204980 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2398910 | 2363240 | 2400960 | 2347660 | 2184890
333 | 11 KV Mansurabad | G134M | 11 | 0 | 77816681 | 1 | 52493.68 | 52769.06 | 275.38 | 8000 | 0 | 2203040 | 2258116 | Adabor | Kallyanpur 33/11KV S/S | 34 | 2458196 | 2422936 | 2313630 | 2379804 | 2220888
334 | 11 kV Doctor's Lane | D108D | 11 | T-1 | 21100462 | 1 | 40800.1 | 40966.6 | 166.5 | 1000 | 0 | 166500 | 170232.3057 | Kakrail | Moghbazar 33/11KV S/S | 8 | 173300.7767 | 177316.5531 | 65016.8533 | 1691.4448 | 1119.369
335 | 11 kV T&T O/H Feeder | C108S | 11 | T-1 | 21100473 | 1 | 80823.9 | 80957.2 | 133.3 | 1000 | 0 | 133300 | 136288.0862 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 107803.7381 | 78656.0729 | 96666.9717 | 802696.2793 | 1023306.7911
336 | 11 kV Acore Ice Feeder (TEJ) | C108Q | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 1589911.0287
337 | 11 kV Tejgaon S/S-1 | 0 | 11 | T-1 | 30/11004-1101 | 1 | 120284.8 | 120741.7 | 456.9 | 1000 | 0 | 456900 | 467141.9849 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 391310.8557 | 416531.5604 | 434303.9973 | 326660.2796 | 342221.6327
338 | 11 kV Madhubagh | D108U | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0
339 | 11 kV Iskaton | C608G | 11 | T-3 | 30/11006-1101 | 1 | 122629 | 123990 | 1361 | 1000 | Estimated | 1763676.18 | 1803211.1873 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1782922.7783 | 2012798.2977 | 1909092.2251 | 1919578.4326 | 1819483.4353
340 | 11KV Ambagan | D108A | 11 | T-1 | 21101054 | 1 | 129935.9 | 132139.2 | 2203.3 | 1000 | 0 | 2203300 | 2252689.725 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 2523568.5136 | 2372564.6062 | 2579216.4264 | 2455343.5773 | 1989016.959
341 | 11 kV Moghbazar Nearest | C108A | 11 | T-2 | 30/11005-1101 | 1 | 147394.9 | 148899.1 | 1504.2 | 1000 | 0 | 1504200 | 1537918.5242 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1644738.2335 | 1666230.9769 | 1593234.7726 | 1205154.4296 | 1055666.7314
342 | 11 kV Vumi Bhaban | 0 | 11 | T-3 | 21101039 | 1 | 8856.8 | 8997.2 | 140.4 | 1000 | 0 | 140400 | 143547.2416 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 140604.4879 | 151132.7739 | 165331.6353 | 136267.0228 | 122011.2214
343 | 11 kV MP Suite Feeder | C108D | 11 | T-2 | 30/11010-1101 | 1 | 9978.1 | 10125.5 | 147.4 | 1000 | 0 | 147400 | 150704.1553 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 173927.5426 | 164434.1337 | 177991.6827 | 170095.919 | 154167.6401
344 | 11 kV Bangla Motor | C608H | 11 | T-2 | 202006983 | 1 | 126688.8 | 128558 | 1869.2 | 1000 | 0 | 1869200 | 1911100.4557 | Kakrail | Moghbazar 33/11KV S/S | 8 | 2221153.9574 | 2075012.1387 | 2269581.709 | 2138303.3901 | 1962152.1029
345 | 11 kV Ispahani Feeder | D108S | 11 | T-3 | 21101021 | 1 | 87567.7 | 89088.7 | 1521 | 1000 | 0 | 1521000 | 1555095.1172 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1652781.7295 | 1586003.8772 | 1603212.6065 | 1595983.8968 | 78254.0694
346 | 11 kV Kunipara Feeder | C108T | 11 | T-2 | 30/11007-1102 | 1 | 176601.2 | 178896.5 | 2295.3 | 1000 | 0 | 2295300 | 2346752.0201 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 2390485.2167 | 1095738.7944 | 1085008.9734 | 952812.0065 | 1869447.9972
347 | 11 kV Nayatola Feeder | D108N | 11 | T-3 | 2110137 | 1 | 123893.2 | 124248.6 | 355.4 | 1000 | 0 | 355400 | 363366.7355 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 399563.2736 | 370867.0494 | 398147.7603 | 399920.9831 | 690345.3929
348 | 11 kV Garden Feeder (KAK) | C608I | 11 | T-3 | 21101000 | 1 | 115143.1 | 116054.5 | 911.4 | 1000 | 0 | 911400 | 931830.1708 | Kakrail | Moghbazar 33/11KV S/S | 8 | 991857.0675 | 900407.8011 | 994564.7368 | 950591.9851 | 944645.6784
349 | 11 kV BSRS Feeder | C608J | 11 | T-3 | 21100870 | 1 | 44147 | 44614.9 | 467.9 | 1000 | 0 | 467900 | 478388.5637 | Kakrail | Moghbazar 33/11KV S/S | 8 | 514783.7418 | 344054.8595 | 0 | 0 | 323294.1205
350 | 11kV Moghbazar(old.buil) | D108T | 11 | T-3 | 21101247 | 1 | 19577.5 | 19577.5 | 0 | 1000 | 14248266.2732 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 1357.9928 | 0 | 0 | 0 | 0
351 | 11 kV TCB Feeder | C608P | 11 | T-4 | 0 | 1 | 36560.7 | 36868.9 | 308.2 | 1000 | 0 | 308200 | 327449.4305 | Kakrail | Moghbazar 33/11KV S/S | 8 | 337617.6819 | 593608.4852 | 1091208.9552 | 1058026.2525 | 587067.814
352 | 11 kV Tejgaon SS-2 | 0 | 11 | T-4 | 0 | 1 | 32855.5 | 34285.7 | 1430.2 | 1000 | 0 | 1430200 | 1519526.851 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 1537848.541 | 1385049.7687 | 1574127.4074 | 1532552.8114 | 1481122.0985
353 | Holy Day Inn | C108HY | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 396900 | 421689.4191 | Tejgaon | Moghbazar 33/11KV S/S | 8 | 437235.9991 | 578900.3818 | 542740.3295 | 522630.1141 | 493817.3233
354 | Polly Bhabon-2 | C608PB | 11 | T-4 | 0 | 1 | 18384.8 | 18384.8 | 0 | 1000 | According to AMR meter reading | 21927 | 23296.5077 | Kakrail | Moghbazar 33/11KV S/S | 8 | 25096.5994 | 28135.8532 | 27898.691 | 30058.9479 | 29444.1053
355 | Polly Bhabon-1 / ambarsaha mosjid | C608AS | 11 | T-4 | 0 | 1 | 18495.9 | 20174.3 | 1678.4 | 1000 | 0 | 1678400 | 1783228.8258 | Kakrail | Moghbazar 33/11KV S/S | 8 | 1839066.8165 | 1861301.6803 | 1854771.9565 | 1842884.7823 | 1860061.7445
356 | 11 kV Tejturibazar | C608X | 11 | T-4 | 0 | 1 | 132188.2 | 132923.9 | 735.7 | 1000 | 0 | 735700 | 781650.0519 | Kakrail | Moghbazar 33/11KV S/S | 8 | 797094.2458 | 844174.6782 | 788742.3253 | 776669.7972 | 731592.6735
357 | Songsad | 0 | 11 | T-4 | 0 | 1 | 3719.3 | 3864.8 | 145.5 | 1000 | 0 | 145500 | 154587.5799 | Shere b.nagar | Moghbazar 33/11KV S/S | 8 | 443228.713 | 416692.9 | 475259.7411 | 544550.7215 | 126381.9385
358 | Chennel 24 | 0 | 11 | T-4 | 0 | 1 | 7324.01 | 7327.44 | 3.43 | 1000 | 0 | 3430 | 3644.2295 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 5053.7147 | 7574.2329 | 3766.4072 | 1700.7368 | 1164.858
359 | Sonargaon | C608K | 11 | T-4 | 0 | 1 | 41121.6 | 41957.9 | 836.3 | 1000 | 0 | 836300 | 888533.2859 | Kakrail | Moghbazar 33/11KV S/S | 8 | 916526.5008 | 698965.1841 | 733347.8124 | 844174.3497 | 839625.5215
360 | AT -1 | 0 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 7215.9345
361 | AT -2 | 0 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 5903606.1813 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 8 | 0 | 0 | 0 | 0 | 0
362 | 11 kV post office | C6105Z | 11 | Kakril | DHK60950 | 1 | 202609 | 208557 | 5948 | 60 | 0 | 356880 | 350929.0306 | Kakrail | T&T 33/11 KV | 105 | 1384212.3787 | 1354639.697 | 1410640.1386 | 1413099.3422 | 1314936.3633
363 | 11 kV anarkoli | C6105Y | 11 | Kakril | DHK60977 | 1 | 470715 | 491607 | 20892 | 60 | 0 | 1253520 | 1232617.5702 | Kakrail | T&T 33/11 KV | 105 | 1434115.4167 | 1367760.1292 | 1475917.0544 | 1466512.1688 | 1363050.3594
364 | 11 kV sonalibagh | D1105O | 11 | Mogbazar | DHK61083 | 1 | 957585 | 963754 | 6169 | 60 | 0 | 370140 | 363967.9203 | Moghbazar | T&T 33/11 KV | 105 | 383823.6058 | 382050.2122 | 390823.0756 | 376350.3769 | 416269.8468
365 | 11 Kv desh tv | D1105E | 11 | Mogbazar | DHK60948 | 1 | 1974036 | 1987746 | 13710 | 60 | 0 | 822600 | 808883.1556 | Moghbazar | T&T 33/11 KV | 105 | 925176.0601 | 915135.1719 | 946635.0529 | 901476.4809 | 862940.0791
366 | 11 Kv Btcl | D1105T | 11 | Mogbazar | DHK86070 | 1 | 646 | 670.9 | 24.9 | 60000 | 0 | 1494000 | 1469087.5693 | Moghbazar | T&T 33/11 KV | 105 | 1653485.829 | 1672106.229 | 1759482.372 | 1708010.1623 | 1630130.9123
367 | 11 kV century | C6105S | 11 | Kakril | DHK60867 | 1 | 905645 | 916060 | 10415 | 60 | 0 | 624900 | 614479.8006 | Kakrail | T&T 33/11 KV | 105 | 616445.7818 | 601742.5641 | 617435.7813 | 612807.1598 | 591251.5937
368 | 11 kV cinema hall | 0 | 11 | Mogbazar | DHK60979 | 1 | 506046 | 522676 | 16630 | 60 | 0 | 997800 | 981161.6979 | Moghbazar | T&T 33/11 KV | 105 | 1071064.8459 | 1069584.8264 | 1086052.1721 | 1077858.8375 | 1046359.7284
369 | 11 kV malibagh bazar | 0 | 11 | Khailgaon | DHK61106 | 1 | 755000 | 782487 | 27487 | 60 | 0 | 1649220 | 1621719.2778 | Khilgaon | T&T 33/11 KV | 105 | 1701657.7808 | 1728362.3289 | 1686240.4748 | 1646555.4045 | 1662984.8723
370 | 11 kv Sherebangla | D1105G | 11 | 0 | DHK60915 | 1 | 743499 | 765116 | 21617 | 60 | 0 | 1297020 | 1275392.2083 | Moghbazar | T&T 33/11 KV | 105 | 1525385.4467 | 1396637.0623 | 1544547.6466 | 1416880.2502 | 1438632.4204
371 | 11 kV Nur Mosjid | D1105Z | 11 | Khailgaon | DHK60913 | 1 | 344109 | 355079 | 10970 | 60 | 0 | 658200 | 647224.5235 | Moghbazar | T&T 33/11 KV | 105 | 706402.574 | 705627.6304 | 690498.0173 | 692746.3564 | 708065.6738
372 | Auxiliary | 0 | 0 | Export | U0004461 | 1 | 8223.3 | 8288.88 | 65.58 | 60 | 0 | 3934.8 | 3869.1873 | Moghbazar | T&T 33/11 KV | 105 | 7599.4686 | 0 | 4061.5417 | 3583.4605 | 3045.4245
373 | West Malibagh | D192M | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 973062.72 | 977173.2999 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1007307.2369 | 980334.5269 | 1038100.3806 | 1138226.0536 | 978294.9507
374 | Ullon | D192L | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1824492.6 | 1832199.9373 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1836854.3731 | 1838127.2379 | 1648747.6632 | 1617479.1288 | 1406298.9916
375 | Mohanagar | D192P | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1520410.5 | 1526833.2811 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1659094.2725 | 1654314.5141 | 1770877.1198 | 1677385.7633 | 1345155.5572
376 | Bagichartek | D192B | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1033879.14 | 1038246.6311 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1125813.9706 | 1102876.3427 | 1282359.2936 | 1317945.9568 | 1100581.8195
377 | Mirbagh | D192V | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1702859.76 | 1710053.2748 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1718347.6394 | 1715585.422 | 1648747.6632 | 1557572.4944 | 1345155.5572
378 | West Rampura | D192R | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1094695.56 | 1099319.9624 | Moghbazar | Ullon local 33/11KV S/S | 92 | 1149515.3174 | 1225418.1586 | 1282359.2936 | 1377852.5912 | 1222868.6883
379 | Jilkanon | D192J | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0
380 | AT-1 | 0 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0
381 | AT-2 | 0 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 92 | 0 | 0 | 0 | 0 | 0
382 | Sobujbagh | B921S | 11 | Mugdapara | 34140453696 | 1 | 14.0602 | 15.7858 | 1.7256 | 1000000 | 0 | 1725578 | 1733090.4653 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1860379.5125 | 1839023.3133 | 1914129.2674 | 1830321.6533 | 1753548.1446
383 | Madertek | A921K | 11 | Mugdapara | D0086134 | 1 | 103409.1 | 105215.6 | 1806.5 | 1000 | 0 | 1806500 | 1814364.7668 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1995837.5311 | 1955619.6426 | 2015001.2811 | 1947058.9925 | 1858521.5132
384 | Rajarbagh | B921R | 11 | Mugdapara | DHKD9104 | 1 | 4101.6 | 6227.8 | 2126.2 | 1000 | 0 | 2126200 | 2135456.6106 | Mugdapara | Madarteck 33/11KV S/S | 21 | 2140470.7173 | 2127980.2733 | 2037129.655 | 2033626.6462 | 1264456.5681
385 | Goran | A921G | 11 | 0 | X1390296 | 1 | 32509.3 | 34326.4 | 1817.1 | 1000 | 0 | 1817100 | 1825010.9149 | Bashabo | Madarteck 33/11KV S/S | 21 | 1949936.5823 | 1924894.1079 | 2047460.5279 | 1968306.9598 | 1851494.7743
386 | Dhakhingaon | B921D | 11 | Mugdapara | 34140313075 | 1 | 12785.006 | 14225.436 | 1440.43 | 1000 | 0 | 1440430 | 1446701.0468 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1502775.9682 | 1533961.2033 | 1583000.8619 | 1493157.2972 | 2039169.8043
387 | Manda | B221E | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 21 | 0 | 0 | 0 | 373198.8946 | 881499.2996
388 | Green Model Town | B921G | 11 | Mugdapara | 34140453695 | 1 | 1236.0474 | 1479.3345 | 243.2871 | 1000 | 0 | 243287.1 | 244346.2732 | Mugdapara | Madarteck 33/11KV S/S | 21 | 252299.2953 | 242642.782 | 236939.3158 | 229733.5056 | 209712.5124
389 | Biswa Road | B921B | 11 | Mugdapara | 34140313080 | 1 | 4394.6776 | 4970.5368 | 575.8592 | 1000 | 0 | 575859.2 | 578366.2569 | Mugdapara | Madarteck 33/11KV S/S | 21 | 687579.7395 | 671883.3535 | 576962.6065 | 679941.1966 | 331641.7074
390 | Mugdapara | B921P | 11 | 0 | X0854272 | 1 | 4423.5 | 4681.7 | 258.2 | 1000 | 0 | 258200 | 259324.0979 | Maniknagar | Madarteck 33/11KV S/S | 21 | 280126.3587 | 262278.8244 | 99804.6 | 280453.0279 | 256934.2344
391 | Singapur | F221S | 11 | 0 | X1390302 (N) | 1 | 38272.3 | 40431.5 | 2159.2 | 1000 | 0 | 2159200 | 2168600.2792 | Banosree | Madarteck 33/11KV S/S | 21 | 2400509.1335 | 2332917.0805 | 2449510.2642 | 2359732.7837 | 2200082.1244
392 | Trimohony | F221T | 11 | 0 | X1390308 | 1 | 30823 | 32844.1 | 2021.1 | 1000 | 0 | 2021100 | 2029899.048 | Banosree | Madarteck 33/11KV S/S | 21 | 2144287.4264 | 2101565.9326 | 2104795.0854 | 2021980.735 | 1604947.893
393 | Mayakanon | B921K | 11 | Mugdapara | 34140313073 | 1 | 16162.476 | 17776.286 | 1613.81 | 1000 | 0 | 1613810 | 1620835.8728 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1884688.9362 | 1948965.1387 | 1816135.3069 | 1942171.9601 | 1839386.3794
394 | Ahmedbagh | B921A | 11 | Mugdapara | 34140453691 | 1 | 6360.944 | 7166.0944 | 805.1504 | 1000 | 0 | 805150.4 | 808655.6976 | Mugdapara | Madarteck 33/11KV S/S | 21 | 863662.2068 | 854936.3865 | 710891.4812 | 850151.1099 | 596386.824
395 | Wasa Road | B921W | 11 | Mugdapara | 61903686 | 1 | 739814 | 748752 | 8938 | 200 | 0 | 1787600 | 1795382.4839 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1921009.9451 | 1954912.1468 | 1661387.6173 | 1892982.4123 | 480873.3471
396 | Nandipara | B921E | 11 | Mugdapara | 61903558 | 1 | 769845 | 777256 | 7411 | 200 | 0 | 1482200 | 1488652.8964 | Mugdapara | Madarteck 33/11KV S/S | 21 | 1652835.9122 | 1533042.4693 | 1508090.9874 | 1450702.4488 | 298789.1572
397 | Nakhal Para Feeder | C110U | 11 | 0 | DHK60950 | 1 | 280751.8 | 305498.9 | 24747.1 | 60 | 0 | 1484826 | 1500089.328 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1599409.3479 | 1587033.6595 | 1590100.5899 | 1545202.0376 | 1536369.5556
398 | Badda-Meghna Feeder | C110N | 11 | 0 | DHK60979 | 1 | 927571.6 | 940674.7 | 13103.1 | 60 | 0 | 786186 | 794267.6303 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 812324.781 | 768867.2754 | 797427.1133 | 711868.0468 | 842649.7133
399 | Rasulbagh Feeder | C110K | 11 | 0 | DHK60948 | 1 | 52268.2 | 82062.5 | 29794.3 | 60 | 0 | 1787658 | 1806034.3017 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1726738.2372 | 1932163.7903 | 1821935.9992 | 1845073.9247 | 1902151.6741
400 | Lukas | C171V | 11 | 0 | 8A021100948-02 | 1 | 71541234 | 73546915 | 2005681 | 1 | 0 | 2005681 | 2026298.4778 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2352263.3192 | 2382018.4101 | 2450636.3287 | 2356930.5125 | 2345545.782
401 | PWD RMU | 0 | 11 | 0 | 0 | 1 | 658258.5 | 660047.1 | 1788.6 | 1 | 0 | 1788.6 | 1806.986 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1917.0903 | 1854.955 | 1876.4622 | 1825.2484 | 1757.0539
402 | Civil Aviation Feeder | 0 | 11 | 0 | DHK60977 | 1 | 936848.6 | 984210.7 | 47362.1 | 60 | 0 | 2841726 | 2870937.6357 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 3006456.2987 | 2816826.0828 | 2972868.5519 | 2843930.4649 | 2795399.6317
403 | Ahasanullah Eng. | C171L | 11 | 0 | DHK60867 | 1 | 891167.4 | 900589.8 | 9422.4 | 60 | 0 | 565344 | 571155.4762 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 575802.5636 | 668050.5071 | 681476.0179 | 638085.1899 | 673101.4258
404 | New GMG Feeder | C110M | 11 | 0 | DHK61106 | 1 | 120977.6 | 151809.7 | 30832.1 | 60 | 0 | 1849926 | 1868942.3881 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2083647.5312 | 2435471.7452 | 2366892.1845 | 2233355.6797 | 2281871.6214
405 | Shikajo | C171Z | 11 | 0 | HA021101036-02 | 1 | 65204937 | 66059038 | 854101 | 1 | 0 | 854101 | 862880.7653 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 832111.8625 | 813808.0835 | 877169.4199 | 833321.8823 | 756034.1648
406 | Kahinur | 0 | 11 | 0 | 0 | 1 | 563203.8 | 584798.7 | 21594.9 | 60 | 0 | 1295694 | 1309013.1381 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1330662.8857 | 1351230.8033 | 1347009.4431 | 1251045.3402 | 1294083.2246
407 | Link road | C171X | 11 | 0 | 8A021100380-02 | 1 | 65396105 | 66112857 | 716752 | 1 | 0 | 716752 | 724119.8808 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 647867.3456 | 425896.0895 | 415317.8944 | 416737.628 | 435428.3198
408 | Shanta | C110E | 11 | 0 | 0 | 1 | 331155.2 | 341520.5 | 10365.3 | 60 | 0 | 621918 | 628311.0309 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 599004.2611 | 643052.4099 | 671568.0547 | 608607.1616 | 630895.3248
409 | Karnafuly Feeder | C110Y | 11 | 0 | DHK61084 | 1 | 35882.9 | 36682 | 799.1 | 1000 | 0 | 799100 | 807314.3803 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 766856.2088 | 716684.8588 | 722759.1976 | 686952.8872 | 738300.0364
410 | Butex | C110BT | 11 | 0 | 0 | 1 | 1193.8 | 1299 | 105.2 | 1000 | 0 | 105200 | 106281.4076 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 100920.6493 | 102946.4154 | 100374.7899 | 90006.1656 | 91610.1416
411 | OriON LAB | C171A | 11 | 0 | 0 | 1 | 8288014 | 8377954 | 89940 | 1 | 0 | 89940 | 90864.5418 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 93311.3932 | 93876.22 | 95833.6401 | 88588.4676 | 248723.2522
412 | Nina kabbo | C171Y | 11 | 0 | 201101025-2 | 1 | 17388563 | 17647767 | 259204 | 1 | 0 | 259204 | 261868.4978 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 264819.2014 | 285983.9298 | 281438.971 | 283127.915 | 99489.3009
413 | Satrong | C171S | 11 | 0 | HA021100515-2 | 1 | 95302967 | 97172731 | 1869764 | 1 | 0 | 1869764 | 1888984.3136 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 2007795.2093 | 1899691.7228 | 1806807.9399 | 1563100.3489 | 1367977.887
414 | South East RMU | 0 | 11 | 0 | 0 | 1 | 994.7 | 1108.7 | 114 | 1000 | 0 | 114000 | 115171.8675 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 137308.3735 | 130223.6796 | 128807.568 | 139045.3993 | 149070.967
415 | Rangs Bhaban | 0 | 11 | 0 | HA021100939-2 | 1 | 731159 | 881462 | 150303 | 1 | 0 | 150303 | 151848.0457 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 148545.345 | 152471.8244 | 163396.3968 | 151255.7649 | 161670.1139
416 | Babli | C171R | 11 | 0 | 0 | 1 | 59368.5 | 60405.4 | 1036.9 | 1000 | 0 | 1036900 | 1047558.8549 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1066401.5624 | 2240675.7095 | 2109084.7983 | 2111815.0669 | 1541422.4274
417 | SPL | 0 | 11 | 0 | 0 | 1 | 4841.1 | 5307 | 465.9 | 1000 | 0 | 465900 | 470689.2376 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 471130.5611 | 465633.0017 | 455733.9249 | 408962.9923 | 372268.4438
418 | DNCC Hospital | 0 | 11 | 0 | 0 | 1 | 16588.9 | 17538 | 949.1 | 1000 | 0 | 949100 | 958856.3113 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 1039161.0285 | 1028453.8853 | 1058083.8484 | 992388.6083 | 965076.0343
419 | 11/.415 kv Local transformer | 0 | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 10 | 0 | 0 | 0 | 6054.2264 | 6134.6077
420 | Gonobhaban | D570T | 11 | 0 | DHKC9332 | 1 | 79412.59 | 82497.17 | 3084.58 | 60 | 0 | 185074.8 | 186647.9358 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 199883.04 | 203554.794 | 226219.392 | 216875.2359 | 216836.1836
421 | Rapa Plaza Feeder | D270R | 11 | 0 | DHKC9339 | 1 | 13619.17 | 31044.61 | 17425.44 | 60 | 0 | 1045526.4 | 1054413.3744 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 1089910.392 | 1159561.608 | 1233509.5584 | 1199461.0668 | 1170856.0696
422 | Shukrabad/ South Plaza | D570S | 11 | 0 | DHKC9324 | 1 | 53201.34 | 71432.99 | 18231.65 | 60 | 0 | 1093899 | 1103197.1415 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 1099590.636 | 1169672.112 | 1195401.7152 | 1120705.5276 | 1130327.1946
423 | Wasa O/H | C270W | 11 | 0 | DHKC9333 | 1 | 46540.01 | 58765.81 | 12225.8 | 60 | 0 | 733548 | 739783.158 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1806723.552 | 986766.768 | 1324483.5744 | 2118683.8855 | 1049087.4751
424 | Bangabandhu Memorial Museum | 0 | 11 | 0 | DHKC9334 | 1 | 16026.67 | 16332.37 | 305.7 | 60 | 0 | 18342 | 18497.907 | Dhanmondi | Asad Gate 33/11 KV S/S | 70 | 17876.394 | 21495.426 | 21201.264 | 20854.3329 | 20897.995
425 | Iqbal Road O/H | D470Q | 11 | 0 | DHKC9330 | 1 | 24076.29 | 48276.24 | 24199.95 | 60 | 0 | 1451997 | 1464338.9745 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1539511.488 | 1602882.12 | 1776423.3984 | 1626760.4818 | 1601413.1174
426 | Town Hall | D470W | 11 | 0 | DHKC9351 | 1 | 70678.83 | 103102.61 | 32423.78 | 60 | 0 | 1945426.8 | 1961962.9278 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 2111520.342 | 2123219.172 | 2353752.1728 | 1991480.522 | 2338946.2013
427 | Post Office | D470P | 11 | 0 | DHKC9331 | 1 | 9701.3 | 33036.5 | 23335.2 | 60 | 0 | 1400112 | 1412012.952 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1209158.466 | 1512426.318 | 1672604.0352 | 1378440.8932 | 1492441.2314
428 | Shangshad Bhaban | 0 | 11 | 0 | DHKC9370 | 1 | 22456.58 | 24023.67 | 1567.09 | 60 | 0 | 94025.4 | 94824.6159 | Shere b.nagar | Asad Gate 33/11 KV S/S | 70 | 417958.806 | 245083.974 | 292942.1376 | 474363.1372 | 422562.5169
429 | Jakir Hossain Road | C270J | 11 | 0 | DHKC9373 | 1 | 43058.44 | 67793.29 | 24734.85 | 60 | 0 | 1484091 | 1496705.7735 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 741916.104 | 1368356.484 | 1603359.2736 | 1792634.4006 | 1277863.2905
430 | New Colony O/H Feeder | C270N | 11 | 0 | DHKC9369 | 1 | 14193.96 | 31606.58 | 17412.62 | 60 | 0 | 1044757.2 | 1053637.6362 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 236025.486 | 1443709.554 | 1041715.3824 | 0 | 1328527.8719
431 | Aurangzeb Feeder | D470M | 11 | 0 | DHKC9321 | 1 | 7329.59 | 34889.71 | 27560.12 | 60 | 0 | 1653607.2 | 1667662.8612 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 711485.208 | 1577029.554 | 1636123.104 | 1847282.7847 | 2012075.4293
432 | Asadgate Local Feeder | C270E | 11 | 0 | DHKC9338 | 1 | 17111.13 | 42257.12 | 25145.99 | 60 | 0 | 1508759.4 | 1521583.8549 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 1037091.432 | 1943325.648 | 2129079.8592 | 2381609.9379 | 1832840.2298
433 | Sonarbangla Road | D470R | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 0 | 0 | 0 | 0 | 0
434 | Humayun Road | D470H | 11 | 0 | DHKC9366 | 1 | 27223.31 | 57194.89 | 29971.58 | 60 | 0 | 1798294.8 | 1813580.3058 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 1032128.898 | 1903127.244 | 1920389.3856 | 263604.1533 | 1670349.266
435 | NHA | D470B | 11 | 0 | DHKC9374 | 1 | 62223.75 | 65850.12 | 3626.37 | 60 | 0 | 217582.2 | 219431.6487 | Shyamoli | Asad Gate 33/11 KV S/S | 70 | 72214.596 | 237352.02 | 264138.5376 | 26450.7883 | 221861.5773
436 | Auxiliary transformer | 0 | 0.415 | 0 | 0 | 1 | 659515 | 667095 | 7580 | 1 | 0 | 7580 | 7644.43 | Satmasjid | Asad Gate 33/11 KV S/S | 70 | 8345.63 | 17430.58 | 0 | 7372.3763 | 6148.5505
437 | Angur Jora | F292A | 11 | 0 | 141 | 1 | 391040 | 2417760 | 2026720 | 1 | 0 | 2026720 | 2051370.0659 | Banosree | Banasree 33/11 SS | 99 | 2226512.8044 | 2196051.2126 | 2182461.1184 | 2168323.5267 | 1879685.8324
438 | Block F-G Avenue | F299G | 11 | 0 | 68 | 1 | 3403100 | 5525600 | 2122500 | 1 | 0 | 2122500 | 2148314.9942 | Banosree | Banasree 33/11 SS | 99 | 2658158.1289 | 2630613.5558 | 2686465.1418 | 2772883.9436 | 2653782.5782
439 | Banasree Main Road(Monpura) | F292P | 11 | 0 | 168 | 1 | 9274200 | 10276520 | 1002320 | 1 | 0 | 1002320 | 1014510.7585 | Banosree | Banasree 33/11 SS | 99 | 1233831.441 | 1794844.8609 | 1857089.8973 | 1771391.1453 | 1640446.1666
440 | Baitul Kuddus | F292Q | 11 | 0 | 62 | 1 | 4111160 | 6205400 | 2094240 | 1 | 0 | 2094240 | 2119711.2807 | Banosree | Banasree 33/11 SS | 99 | 2318179.6901 | 2240905.0671 | 2321761.5567 | 2248090.2296 | 2090165.4312
441 | Ideal | F214I | 11 | 0 | 0 | 1 | 9849120 | 10538960 | 689840 | 1 | 0 | 689840 | 698230.2076 | Banosree | Banasree 33/11 SS | 99 | 798010.2701 | 777466.8098 | 813387.6289 | 785714.1589 | 730886.4987
442 | Central Mosque | F292C | 11 | 0 | 46 | 1 | 4361840 | 6352040 | 1990200 | 1 | #REF! | 1990200 | 2014405.8899 | Banosree | Banasree 33/11 SS | 99 | 2216426.2192 | 2155463.3498 | 2252151.7613 | 2213991.1776 | 2027033.5767
443 | Larive | F299L | 11 | 0 | 47 | 1 | 1887400 | 3120560 | 1233160 | 1 | 0 | 1233160 | 1248158.3596 | Banosree | Banasree 33/11 SS | 99 | 1177386.9105 | 1133778.6787 | 1209136.6977 | 1154817.1834 | 1075325.8802
444 | Bank Colony | A299K | 11 | 0 | 0 | 1 | 6193200 | 8053280 | 1860080 | 1 | 0 | 1860080 | 1882703.3 | Khilgaon | Banasree 33/11 SS | 99 | 767992.5927 | 745817.2151 | 791659.8328 | 743707.201 | 684269.1356
445 | Salambagh | A299G | 11 | 0 | 0 | 1 | 5088040 | 6381080 | 1293040 | 1 | 0 | 1293040 | 1308766.6526 | Khilgaon | Banasree 33/11 SS | 99 | 927562.3697 | 1031151.1096 | 794065.0493 | 937481.2326 | 1234217.735
446 | Titas Road | A299T | 11 | 0 | 0 | 1 | 3258920 | 4635200 | 1376280 | 1 | 0 | 1376280 | 1393019.0625 | Khilgaon | Banasree 33/11 SS | 99 | 401204.0106 | 522157.3704 | 387724.9431 | 442215.7606 | 461564.0031
447 | AT-1 | 0 | 0.415 | 0 | 7734 | 1 | 3471 | 3534.86 | 63.86 | 1 | 0 | 63.86 | 64.6367 | Banosree | Banasree 33/11 SS | 99 | 66.5715 | 73.8423 | 76.0089 | 145.5702 | 0
448 | AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 99 | 0 | 0 | 0 | 0 | 0
449 | Meradia | F214M | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 160 | 376669.44 | 378160.5224 | Banosree | Goran 33/11KV S/S | 14 | 0 | 0 | 0 | 0 | 0
450 | Shipahibagh | A914S | 11 | 0 | HA-021001030-02 | 1 | 40881162 | 42070870 | 1189708 | 1 | 0 | 1189708 | 1194417.5741 | Bashabo | Goran 33/11KV S/S | 14 | 1488941.4076 | 1499139.6523 | 1654071.9922 | 1292900.8718 | 1411235.5236
451 | Farazi Hospital | F214F | 11 | 0 | HA-030701081-03 | 1 | 51063880 | 51724280 | 660400 | 1 | 0 | 660400 | 663014.2572 | Banosree | Goran 33/11KV S/S | 14 | 614880.5841 | 0 | 0 | 0 | 0
452 | West Bansree | F214W | 11 | 0 | New Meter | 1 | 96909074 | 98404140 | 1495066 | 1 | 0 | 1495066 | 1500984.3633 | Banosree | Goran 33/11KV S/S | 14 | 1948580.2361 | 1917412.8456 | 1975561.8751 | 1966878.4605 | 1837316.4777
453 | Model School(Nearest) | F214D | 11 | 0 | HA-030701099-03 | 1 | 22464572 | 24729160 | 2264588 | 1 | 0 | 2264588 | 2273552.5905 | Banosree | Goran 33/11KV S/S | 14 | 2474165.667 | 2481856.1691 | 2525253.4223 | 2475694.1412 | 2316464.2537
454 | Bhuiyan Para | F214V | 11 | 0 | HA-021100508-02 | 1 | 60667692 | 63138610 | 2470918 | 1 | 0 | 2470918 | 2480699.3677 | Banosree | Goran 33/11KV S/S | 14 | 2656699.6806 | 2382096.4852 | 2607870.9453 | 2554505.4549 | 2408712.741
455 | Bonobithi (Ideal) School | F214B | 11 | 0 | HA-021100879-02 | 1 | 18782519 | 20164310 | 1381791 | 1 | 0 | 1381791 | 1387260.9532 | Banosree | Goran 33/11KV S/S | 14 | 1569496.2633 | 1543598.2091 | 1587554.1504 | 1568260.1835 | 1428642.8767
456 | AT-01 | 0 | 0.415 | 0 | 3043122 | 1 | 7023.2 | 7030.2 | 7 | 80 | 0 | 560 | 562.2168 | Banosree | Goran 33/11KV S/S | 14 | 0 | 0 | 0 | 0 | 0
457 | AT-02 | 0 | 0.415 | 0 | 3043146 | 1 | 4935.3 | 5084.2 | 148.9 | 80 | 0 | 11912 | 11959.1548 | Banosree | Goran 33/11KV S/S | 14 | 5508.1614 | 6933.6386 | 6257.2038 | 5424.4075 | 4669.3803
458 | Shankor O/H | D207S | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 120 | 1459594.08 | 1468016.3082 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1541495.5501 | 1473463.6679 | 1695740.7049 | 1418643.1678 | 1399733.2864
459 | Bangabobondhu museum | D207B | 11 | Export | 0 | 1 | 629342 | 629342 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1906.9492 | 0 | 0 | 0 | 0
460 | Road No-13/A | D207M | 11 | Export | 202006950 | 1 | 84603836 | 86479670 | 1875834 | 1 | 0 | 1875834 | 1886658.0381 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1858256.0346 | 2288167.324 | 2330507.8061 | 2062161.6863 | 2160918.3029
461 | Jaforabad | D234K | 11 | Export | DHK00163 | 1 | 5564310 | 7608679 | 2044369 | 1 | 0 | 2044369 | 2056165.5278 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 2227970.4742 | 2396456.6421 | 1846222.5257 | 2324395.3174 | 2181617.4346
462 | Asadgate U/G | D207G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 0 | 0 | 0 | 0 | 0
463 | Road 32 ( Lalmatia 11 kV S/S) | D207A | 11 | Export | DHK00175 | 1 | 26012.1 | 26183.9 | 171.8 | 3333.33 | 0 | 572666.094 | 575970.5227 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 619531.2198 | 632620.8461 | 655652.5794 | 676925.663 | 643438.6457
464 | Road No -15 | D207L | 11 | Export | DHK00162 | 1 | 70587.5 | 71012.2 | 424.7 | 3333.33 | 0 | 1415665.251 | 1423833.9987 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1532206.4801 | 1409263.8848 | 1205565.6057 | 1637075.4163 | 1478674.7103
465 | Road No-27 South | D207P | 11 | Export | DHK00161 | 1 | 78600.4 | 79007.3 | 406.9 | 3333.33 | 0 | 1356331.977 | 1364158.3566 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1534221.2158 | 1535115.0531 | 1547367.0274 | 1547019.5294 | 1459995.3095
466 | Road 25 | D207C | 11 | Export | 0 | 1 | 71004.7 | 71389.6 | 384.9 | 3333.3 | 0 | 1282987.17 | 1290390.3315 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 1318296.8446 | 1268595.2792 | 1429491.6026 | 1320696.1949 | 1108412.3257
467 | Ibne Sina | D207I | 11 | Export | DHK00165 | 1 | 38100.5 | 38220.6 | 120.1 | 3333.33 | 0 | 400332.933 | 402642.9556 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 432160.8021 | 453939.1071 | 448887.9755 | 428853.4986 | 403274.921
468 | Road No-31 (PARI) | C307R | 11 | Export | HA-021100490-02 | 1 | 62122937 | 63193708 | 1070771 | 1 | 0 | 1070771 | 1076949.6203 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 939422.8232 | 963337.8167 | 1202715.5447 | 1761856.4725 | 924073.8841
469 | Satmoszid Road West | D207D | 11 | Export | HA-021101031-02 | 1 | 73910799 | 76131211 | 2220412 | 1 | 0 | 2220412 | 2233224.3406 | Dhanmondi | Lalmatia 33/11KV S/S | 7 | 2307141.6064 | 2239410.379 | 2263478.6281 | 2215613.0537 | 2070071.1797
470 | Lab aid/local RMU | C302L | 11 | 0 | 3C65883 | 1 | 68698 | 73195 | 4497 | 300 | 0 | 1349100 | 1368745.9116 | Paribag | Green Road 33/11KV S/S | 2 | 1391721.2231 | 1482077.1317 | 1556841.7376 | 1536617.643 | 1422394.5672
471 | Green View | C302V | 11 | 0 | DHK000151 | 1 | 67971.6 | 68313.2 | 341.6 | 3333.33 | 0 | 1138665.528 | 1155247.0433 | Paribag | Green Road 33/11KV S/S | 2 | 1226741.8962 | 1226475.691 | 1233531.7182 | 1202336.4681 | 1154869.3417
472 | Central Road | C302C | 11 | 0 | 65943 | 1 | 32548 | 37616 | 5068 | 300 | 0 | 1520400 | 1542540.4225 | Paribag | Green Road 33/11KV S/S | 2 | 1699791.5522 | 1668170.2521 | 1747192.6716 | 1761466.4931 | 1692090.5953
473 | New Market | D802N | 11 | 0 | DHK000194 | 1 | 47323.8 | 47697.9 | 374.1 | 3333.33 | 0 | 1246998.753 | 1265157.8423 | Jigatola | Green Road 33/11KV S/S | 2 | 1241755.0551 | 1233547.6266 | 1104020.9274 | 1190965.2748 | 1011316.673
474 | DPH Feeder | 0 | 11 | 0 | HA-021100459 | 1 | 41862.9 | 41984 | 121.1 | 1 | 25 | 304082.1 | 308510.2151 | Paribag | Green Road 33/11KV S/S | 2 | 353437.7385 | 245765.8495 | 244229.1636 | 236205.0715 | 247670.0176
475 | Dhanmondi Rd 4(md Banglo | D802F | 11 | 0 | 6604464 | 1 | 4552.33 | 4573.53 | 21.2 | 60000 | 0 | 1272000 | 1290523.1633 | Jigatola | Green Road 33/11KV S/S | 2 | 1536748.4833 | 1456011.9715 | 1566178.5714 | 1573640.9477 | 1319464.1465
476 | Green Road East | C302X | 11 | 0 | HA-021101050 | 1 | 98378742 | 99752905 | 1374163 | 1 | 0 | 1374163 | 1394173.8849 | Paribag | Green Road 33/11KV S/S | 2 | 1544603.3759 | 1523648.0314 | 1576340.6608 | 1533242.4019 | 1471624.0188
477 | North Road | C302Z | 11 | 0 | HA-021100884 | 1 | 83668870 | 85256362 | 1587492 | 1 | 0 | 1587492 | 1610609.432 | Paribag | Green Road 33/11KV S/S | 2 | 1705708.7444 | 1708178.2525 | 1755468.3191 | 1721328.8161 | 1634915.8518
478 | Green road SS | C302W | 11 | 0 | DHK00135 | 1 | 21043782 | 22261302 | 1217520 | 1 | 0 | 1217520 | 1235249.8127 | Paribag | Green Road 33/11KV S/S | 2 | 1304162.391 | 1263700.5929 | 1250797.3933 | 1224610.5159 | 1315498.6273
479 | Plane Moszid | C302A | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 60 | 729797.04 | 740424.5162 | Paribag | Green Road 33/11KV S/S | 2 | 1001406.9258 | 1044504.8605 | 976916.6543 | 944820.2858 | 990680.0705
480 | Malancha | C302H | 11 | 0 | HA-021100953 | 1 | 36299925 | 37784204 | 1484279 | 1 | 0 | 1484279 | 1505893.42 | Paribag | Green Road 33/11KV S/S | 2 | 1581374.6424 | 1473084.6514 | 1290839.3587 | 1378192.0129 | 1148505.9825
481 | AT -1 | 0 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5072.8112 | Paribag | Green Road 33/11KV S/S | 2 | 5004.3913 | 5051.3876 | 5019.8031 | 5016.7079 | 5090.5253
482 | North Dhanmondi | C31002 | 11 | 0 | BD 014039 | 1 | 22691.77 | 23293.96 | 602.19 | 2000 | 0 | 1204380 | 1220415.3715 | Paribag | Green Road Dormatory 33/11 SS | 100 | 539516.6063 | 454897.5939 | 484039.8994 | 504079.3978 | 452285.2955
483 | Lake circus | C31004 | 11 | 0 | BD 014047 | 1 | 37594.03 | 38490.6 | 896.57 | 2000 | 0 | 1793140 | 1817014.2474 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1989795.0818 | 1922931.395 | 2034236.8602 | 2046787.3073 | 1887308.9386
484 | Bashir Uddin | C31003 | 11 | 0 | BD 014037 | 1 | 15223.59 | 15568.84 | 345.25 | 2000 | 0 | 690500 | 699693.4639 | Paribag | Green Road Dormatory 33/11 SS | 100 | 775365.5929 | 750942.0597 | 792213.6477 | 798302.5936 | 740604.9957
485 | Raza Bazar | D5100R | 11 | 0 | BD 013939 | 1 | 22591.2 | 23208.95 | 617.75 | 2000 | 0 | 1235500 | 1251949.7098 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1335486.8536 | 1305339.0743 | 1333290.6732 | 1329360.3858 | 1277085.001
486 | Rasel Squar | D5100RS | 11 | 0 | BD 013970 | 1 | 34305.82 | 35203.1 | 897.28 | 2000 | 0 | 1794560 | 1818453.1535 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1979472.6721 | 1896362.0126 | 1946515.3317 | 1986224.7792 | 1860400.7233
487 | Bow Bazar | D5100O | 11 | 0 | BD 013967 | 1 | 25458.37 | 26056.32 | 597.95 | 2000 | 0 | 1195900 | 1211822.467 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 1271865.4648 | 1228245.6279 | 1315379.6859 | 1361417.0663 | 1195690.6937
488 | BRB Hospital | D5100S | 11 | 0 | BD 014003 | 1 | 13677.42 | 14075.99 | 398.57 | 2000 | 0 | 797140 | 807753.2915 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 817558.9445 | 861081.3012 | 841735.8151 | 735319.9448 | 733624.2823
489 | Green Road North | C31008 | 11 | 0 | BD 013969 | 1 | 16578.98 | 17173.89 | 594.91 | 2000 | 0 | 1189820 | 1205661.5166 | Paribag | Green Road Dormatory 33/11 SS | 100 | 1207219.8681 | 1206463.1592 | 1244662.5143 | 1225136.5003 | 1163648.4072
490 | Water Bhaban | D5100PB | 11 | 0 | BD 014004 | 1 | 5421.06 | 5589.6 | 168.54 | 2000 | 0 | 337080 | 341567.9548 | Shere b.nagar | Green Road Dormatory 33/11 SS | 100 | 321038.9901 | 360889.0448 | 369844.7631 | 332111.9703 | 301428.8307
491 | Alamin Road | C31007 | 11 | 0 | BD 014006 | 1 | 19151.62 | 19439.5 | 287.88 | 2000 | 0 | 575760 | 583425.7911 | Paribag | Green Road Dormatory 33/11 SS | 100 | 637499.1681 | 607978.2671 | 645158.196 | 644406.723 | 578607.7993
492 | Katal Bagan | C3100K | 11 | 0 | 0 | 1 | 9924.75 | 10936.14 | 1011.39 | 2000 | 0 | 2022780 | 2049711.7232 | Paribag | Green Road Dormatory 33/11 SS | 100 | 2213293.3253 | 2170885.4799 | 2232426.2667 | 2461917.3517 | 1880307.9323
493 | Eastern Pantho chaya | C310010 | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 100 | 0 | 0 | 0 | 0 | 0
494 | Kalabagan | 0 | 11 | 0 | BD 014005 | 1 | 6072.12 | 6224.11 | 151.99 | 2000 | 0 | 303980 | 308027.2544 | Paribag | Green Road Dormatory 33/11 SS | 100 | 333048.3305 | 321346.724 | 343995.7229 | 360201.2398 | 320179.3518
495 | Univer Hospital | C310012 | 11 | 0 | BD 013963 | 1 | 1154.01 | 1281.57 | 127.56 | 2000 | 0 | 255120 | 258516.7219 | Paribag | Green Road Dormatory 33/11 SS | 100 | 265852.2552 | 274362.5626 | 281740.4351 | 275219.2974 | 258266.1053
496 | Green Road Staff Quarter(Anowar Khan Medical) | C31009 | 11 | 0 | BD 013971 | 1 | 10293.69 | 10529.2 | 235.51 | 2000 | 0 | 471020 | 477291.2605 | Paribag | Green Road Dormatory 33/11 SS | 100 | 521121.028 | 519641.6074 | 508095.8262 | 507213.6524 | 520651.6433
497 | Matir Masjid | A229S | 11 | 0 | DHK00170 | 1 | 27323.3 | 29471.9 | 2148.6 | 888.8889 | 0 | 1909866.6667 | 1914137.6974 | Khilgaon | Taltola 33/11KV S/S | 29 | 2132185.0742 | 2085431.7227 | 2167154.5553 | 2177028.2382 | 2023352.6919
498 | Hajipara | A229P | 11 | 0 | DHK-00108 | 1 | 5735.6 | 6219.3 | 483.7 | 2222.2222 | 0 | 1074888.8889 | 1077292.6606 | Khilgaon | Taltola 33/11KV S/S | 29 | 2330316.32 | 2323985.9847 | 2257545.6108 | 2323390.6234 | 1505682.5673
499 | Nearest Feeder | A929N | 11 | 0 | DHK-00106 | 1 | 91286.8 | 91617.7 | 330.9 | 2222.222 | 0 | 735333.2598 | 736977.684 | Bashabo | Taltola 33/11KV S/S | 29 | 448845.991 | 661064.6612 | 0 | 0 | 102528.7436
500 | Reazbagh | A229C | 11 | 0 | DHK-00109 | 1 | 97567.1 | 98320.2 | 753.1 | 2222.222 | 0 | 1673555.3882 | 1677297.9566 | Khilgaon | Taltola 33/11KV S/S | 29 | 1831327.1429 | 1773544.5971 | 1831021.0001 | 1850181.9906 | 1693614.7124
501 | Chowdhury Para | A229F | 11 | 0 | DHK-00107 | 1 | 53017.5 | 53269.4 | 251.9 | 2222.222 | 0 | 559777.7218 | 561029.5515 | Khilgaon | Taltola 33/11KV S/S | 29 | 662951.963 | 585903.1258 | 625509.6106 | 653692.0598 | 575139.5465
502 | Model Colleg | A229D | 11 | 0 | 9122392 | 1 | 2570.74 | 2584.74 | 14 | 40000 | 0 | 560000 | 561252.3268 | Khilgaon | Taltola 33/11KV S/S | 29 | 1334690.1699 | 1248930.587 | 1283320.9871 | 723685.6707 | 1038453.9207
503 | East Rampura | A229B | 11 | 0 | DHK-00181 | 1 | 99303.7 | 99587.6 | 283.9 | 2222.222 | 0 | 630888.8258 | 632299.6811 | Khilgaon | Taltola 33/11KV S/S | 29 | 1183684.3115 | 1041555.9945 | 1373711.9053 | 1177184.4648 | 1381135.5698
504 | Adarshabagh | A929A | 11 | 0 | DHK-00090 | 1 | 51475.5 | 52389.5 | 914 | 2222.222 | 0 | 2031110.908 | 2035653.077 | Bashabo | Taltola 33/11KV S/S | 29 | 2182105.9426 | 2139761.9297 | 2323799.4344 | 2249760.2414 | 2012766.0076
505 | Khailgaon Govt Colony | A229K | 11 | 0 | DHK00167 | 1 | 76520.9 | 77198.2 | 677.3 | 2222.222 | 0 | 1505110.9606 | 1508476.8371 | Khilgaon | Taltola 33/11KV S/S | 29 | 1632974.0455 | 1590881.9934 | 1651220.4486 | 1644511.4325 | 1548206.2687
506 | TV Road | A214T | 11 | 0 | 6604434 | 1 | 5138.95 | 5147.41 | 8.46 | 40000 | 0 | 338400 | 339156.7632 | Khilgaon | Taltola 33/11KV S/S | 29 | 1446513.4037 | 1300316.995 | 1457589.2313 | 1435653.3713 | 1278251.1059
507 | Post Office | 0 | 11 | 0 | 06604476 | 1 | 6610.69 | 6635.86 | 25.17 | 40000 | 0 | 1006800 | 1009051.5047 | Bashabo | Taltola 33/11KV S/S | 29 | 850255.946 | 1067472.334 | 544086.3384 | 925315.57 | 631719.4629
508 | Navana | A929V | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 0
509 | Shantipur | A929P | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 29 | 0 | 0 | 0 | 0 | 232625.2878
510 | AT-01 | 0 | 0.415 | 0 | 9187958 | 1 | 568.08 | 787.71 | 219.63 | 80 | 0 | 17570.4 | 17609.6926 | Bashabo | Taltola 33/11KV S/S | 29 | 22368.6405 | 0 | 0 | 388.7134 | 5004.1149
511 | AT-02 | 0 | 0.415 | 0 | 9187959 | 1 | 221.34 | 237.76 | 16.42 | 10 | 0 | 164.2 | 164.5672 | Bashabo | Taltola 33/11KV S/S | 29 | 981.0492 | 0 | 0 | 1243.317 | 0
512 | Sher-e-Banglanagar Local | 0 | 11 | 0 | DHK 66503 | 1.45 | 82897 | 84325 | 1428 | 60 | 11 kv bus-1 R Phase PT missing | 124236 | 124871.9678 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 133378.1778 | 145611.0642 | 127632.9783 | 130259.0089 | 137740.1655
513 | Mirpur Road East | D550F | 11 | 0 | DHK 60961 | 1.45 | 843723 | 849497 | 5774 | 60 | 0 | 502338 | 504909.4833 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 511825.2027 | 595499.8531 | 565408.7832 | 579726.769 | 591320.8565
514 | Gonobhaban school | D550E | 11 | 0 | DHK 66492 | 1.45 | 532652 | 534506 | 1854 | 60 | 0 | 161298 | 162123.6893 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 177174.8965 | 204772.9102 | 187053.4171 | 201293.1928 | 178100.36
515 | Babor Road | D450B | 11 | 0 | DHK 66489 | 1.45 | 783040 | 791315 | 8275 | 60 | 0 | 719925 | 723610.3177 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 1641262.4555 | 827030.8546 | 821146.7988 | 2355047.2749 | 1531864.2685
516 | College Gate | D450K | 11 | 0 | DHK 66487 | 1.45 | 2689618 | 2705027 | 15409 | 60 | 0 | 1340583 | 1347445.4847 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 1954707.1976 | 2003387.1217 | 2118896.2632 | 2029429.4244 | 1693179.314
517 | Parade ground | 0 | 11 | 0 | DHK 66490 | 1.45 | 938348 | 938426 | 78 | 60 | 0 | 6786 | 6820.7377 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 4879.6894 | 117.618 | 1062.133 | 1780.3054
518 | Hospital RMU | D550H | 11 | 0 | DHK 66491 | 1.45 | 914941 | 921595 | 6654 | 60 | 0 | 578898 | 581861.3963 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 629901.6383 | 661895.205 | 606359.9098 | 560499.4711 | 544171.0965
519 | Shamoly Square | 0 | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 0 | 0 | 0 | 0 | 0
520 | Gonobhaban RMU | D550D | 11 | 0 | DHK 60964 | 1 | 195915.8 | 197469.2 | 1553.4 | 60 | 0 | 93204 | 93681.1141 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 88021.1633 | 97246.5492 | 98796.0682 | 102753.2911 | 81921.1363
521 | Krishi University | D550V | 11 | 0 | DHK 60963 | 1 | 370114.7 | 378971.9 | 8857.2 | 60 | 0 | 531432 | 534152.4164 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 582966.2552 | 608461.3549 | 589560.5067 | 563852.3796 | 574020.0379
522 | NEC | D550X | 11 | 0 | DHK 86073 | 1 | 43.55 | 47.94 | 4.39 | 60000 | 0 | 263400 | 264748.3525 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 251816.0719 | 276990.3524 | 279104.941 | 274760.4607 | 284784.5503
523 | Novo Theater/Army Musium (41%) | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 399.36 | 417.87 | 18.51 | 60000 | 0 | 455346 | 457676.9299 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 439900.9902 | 454264.1779 | 491118.4828 | 467152.1267 | 453385.8053
524 | Novo Theater/Army Musium (59%) | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 399.36 | 417.87 | 18.51 | 60000 | 0 | 655254 | 658608.2649 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 633028.2541 | 653697.2316 | 706731.4752 | 672243.3043 | 652433.232
525 | Netor | 0 | 11 | 0 | DHK 60962 | 1 | 134307.8 | 143367.9 | 9060.1 | 60 | 0 | 543606 | 546388.7354 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 587213.3923 | 617847.27 | 628517.1836 | 620062.5542 | 596532.4766
526 | BICC | D550VV | 11 | 0 | 0 | 1 | 43.55 | 47.94 | 4.39 | 60000 | 0 | 263400 | 264748.3525 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 251816.0719 | 276990.3524 | 279104.941 | 193459.8492 | 69152.9813
527 | Auxiliary | 0 | 0.415 | 0 | 0 | 1 | 5342.83 | 5396.67 | 53.84 | 60 | 0 | 3230.4 | 3246.9365 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 50 | 3802.5432 | 2988.0849 | 4296.3279 | 3895.3081 | 5642.8833
528 | City Corporation | A997Y | 11 | 0 | 93 | 1 | 43022376 | 44005332 | 982956 | 1 | 0 | 982956 | 996604.0058 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1085361.1698 | 1583920.0344 | 672002.1574 | 951549.8845 | 660250.7383
529 | Bot tola | B297L | 11 | 0 | 0 | 1 | 58423616 | 60692692 | 2269076 | 1 | 0 | 2269076 | 2300581.3394 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 2406944.4276 | 2386526.2912 | 2395209.9678 | 2298336.7826 | 2240795.0697
530 | Jhilpar | B997J | 11 | 0 | 145 | 1 | 36824472 | 37775588 | 951116 | 1 | 0 | 951116 | 964321.9183 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 1048862.0833 | 1018967.1456 | 1203846.2525 | 1011093.8025 | 1160185.3486
531 | Central Bashaboo | A997C | 11 | 0 | 128 | 1 | 40716380 | 42422256 | 1705876 | 1 | 0 | 1705876 | 1729561.5012 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1906586.5613 | 1065915.018 | 2018436.7723 | 1763582.1465 | 1733572.9987
532 | Kadamtala | B997L | 11 | 0 | 8 | 1.5 | 19491432 | 20022992 | 531560 | 1 | 0 | 797340 | 808410.7915 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 737461.0018 | 659233.1205 | 895857.2066 | 680353.9053 | 1958904.8441
533 | Ansar VDP | A297A | 11 | 0 | 119 | 1 | 20098870 | 21280468 | 1181598 | 1 | 0 | 1181598 | 1198004.0816 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 97 | 522827.1096 | 571466.9061 | 611327.4182 | 1128730.4864 | 727503.1317
534 | Mugda Hospital Express-01 | B997H | 11 | 0 | 0 | 1 | 6519544 | 6811903 | 292359 | 1 | 0 | 292359 | 296418.3041 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 309430.1308 | 314267.439 | 307500.5637 | 293639.1125 | 272764.3875
535 | Boro Masjid | B997Z | 11 | 0 | 7 | 1.22 | 50253036 | 51357956 | 1104920 | 1 | 0 | 1348002.4 | 1366718.9494 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 1456683.3289 | 1401094.4155 | 1717015.7129 | 1405726.812 | 1342757.2732
536 | Anandodhara | B297B | 11 | 0 | 120 | 1 | 48863040 | 49877200 | 1014160 | 1 | 0 | 1014160 | 1028241.2626 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 986769.0262 | 991611.9155 | 1008287.8477 | 964251.0175 | 915566.0508
537 | Culvert | A997L | 11 | 0 | 117 | 1 | 42511816 | 44077932 | 1566116 | 1 | 0 | 1566116 | 1587860.9817 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1735000.3001 | 1917088.0393 | 2175998.5274 | 1824104.3237 | 1912589.1389
538 | Mugda Hospital Express-02 | 0 | 11 | 0 | 97 | 1 | 4845548 | 4845548 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0 | 0 | 0
539 | Jhor Pukur | A997J | 11 | 0 | 98 | 1 | 28559450 | 29356208 | 796758 | 1 | 0 | 796758 | 807820.7106 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 1233989.5056 | 952311.2849 | 1695311.8425 | 1643349.6255 | 1429146.8866
540 | T&T | B997T | 11 | 0 | 99 | 1 | 24519980 | 25139698 | 619718 | 1 | 0 | 619718 | 628322.5712 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 593432.5647 | 596600.2068 | 721459.9725 | 567104.166 | 852556.8368
541 | Haider Ali | B297H | 11 | 0 | 9 | 1 | 72359744 | 74741936 | 2382192 | 1 | 0 | 2382192 | 2415267.9161 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 97 | 2486025.7818 | 2500945.5412 | 2687168.9248 | 2028073.3969 | 1439434.5953
542 | 11kv Tilpapara | A929T | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 2189391.12 | 2219790.0622 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 97 | 2267480.2014 | 2153708.0482 | 2169910.6664 | 2181802.1625 | 2151612.2434
543 | AT-01 | 0 | 11 | 0 | 0 | 1 | 3127.9 | 3207.07 | 79.17 | 1 | 0 | 79.17 | 80.2692 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 86.077 | 79.9328 | 89.8242 | 94.3756 | 0
544 | AT-02 | 0 | 11 | 0 | 0 | 1 | 17.34 | 17.34 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 97 | 0 | 0 | 0.34315 | 0 | 8.4563
545 | Shantinagar s/s-1 | 0 | 11 | 0 | DHK60932 | 1 | 365765 | 397140 | 31375 | 60 | 0 | 1882500 | 1888358.4836 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1327460.0638 | 1164408 | 2916346.3506 | 2755360.6206 | 2616486.0095
546 | Gulbagh | D606G | 11 | 0 | DHK60934 | 1 | 158531 | 175960 | 17429 | 60 | 0 | 1045740 | 1048994.4227 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1110222.7304 | 1081462.2 | 329175.3109 | 325114.8574 | 314880.9114
547 | Rampura BTV | A206H | 11 | 0 | DHK60933 | 1 | 14073 | 14073 | 0 | 60 | 0 | 0 | 0 | Khilgaon | Khillgaon 33/11KV S/S | 6 | 0 | 0 | 0 | 1220.4011 | 241.3343
548 | West Shantibag | D606W | 11 | 0 | DHK60926 | 1 | 551556 | 551556 | 0 | 60 | Estimated | 1094695.56 | 1098102.3361 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1003916.3939 | 885668.7 | 934072.7507 | 932020.3326 | 912726.2746
549 | East Malibagh | D606E | 11 | 0 | DHK60929 | 1 | 628367 | 648732 | 20365 | 60 | 0 | 1221900 | 1225702.646 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 1396586.5654 | 1214224.2 | 1558104.7013 | 1377100.6198 | 1289630.0978
550 | Police Line | D606S | 11 | 0 | DHK60930 | 1 | 584758 | 594185 | 9427 | 60 | 0 | 565620 | 567380.2526 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 593599.4922 | 600534.9 | 624772.6414 | 596226.9654 | 576125.2774
551 | PWD RMU 11 KV Sajanpur Feeder. | D606D | 11 | 0 | DHK61017 | 1 | 197716 | 199938 | 2222 | 60 | 0 | 133320 | 133734.902 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 145615.9492 | 150301.2 | 152458.8445 | 149621.1769 | 146188.2445
552 | Benjir Bagan | D662R | 11 | 0 | DHK60985 | 1 | 170493 | 173708 | 3215 | 60 | 0 | 192900 | 193500.3195 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 197704.2286 | 195610.8 | 195480.6318 | 194653.9781 | 180699.0476
553 | AT-1 & AT-2 | 0 | 0.415 | 0 | ELIB 7374 | 1 | 2209.9 | 2332.2 | 122.3 | 60 | 0 | 7338 | 7360.8364 | Rajarbag | Khillgaon 33/11KV S/S | 6 | 7097.6366 | 6669.159 | 7349.5039 | 14431.2432 | 0
554 | Spare | 0 | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0
555 | Monipuripara west | D572W | 11 | 0 | BD013947 | 1 | 31973.6 | 32779.66 | 806.06 | 1000 | 0 | 806060 | 814448.4485 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 843758.793 | 830035.6978 | 847623.509 | 861249.4503 | 873090.4062
556 | Biggan College | C672BC | 11 | 0 | BD013949 | 1 | 19907.7 | 20808.54 | 900.84 | 1000 | 0 | 900840 | 910214.7983 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 898340.4903 | 876599.5577 | 835521.2072 | 819870.1443 | 853994.1863
557 | Green Road South | D572G | 11 | 0 | BD013948 | 1 | 30606.05 | 31642.23 | 1036.18 | 1000 | 0 | 1036180 | 1046963.2451 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 997691.2194 | 972408.44 | 975210.3173 | 1037302.1428 | 986346.7996
558 | BARC Building O/H | D572B | 11 | 0 | BD014010 | 1 | 14027.2 | 14574.54 | 547.34 | 1000 | 0 | 547340 | 553036.0194 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 605164.5353 | 601022.2433 | 634425.9824 | 629218.3029 | 632910.7169
559 | Green Road North | D572NN | 11 | 0 | BD014036 | 1 | 60825.6 | 62546.1 | 1720.5 | 1000 | 0 | 1720500 | 1738404.7784 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 1930586.7401 | 1889476.4806 | 1966221.9789 | 1919532.2257 | 1871294.3358
560 | Chundrima Uddan | D572C | 11 | 0 | BD014035 | 1 | 31059.28 | 32013.76 | 954.48 | 1000 | 0 | 954480 | 964413.0153 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 995724.673 | 1002061.8966 | 1070591.3324 | 1032887.2799 | 1015615.1889
561 | RMU-1 Feeder | 0 | 11 | 0 | BD013940 | 1 | 799.47 | 1047.79 | 248.32 | 1000 | 0 | 248320 | 250904.1991 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 255319.9358 | 263025.0554 | 137015.3458 | 147255.7457 | 0
562 | Spare-03 | 0 | 11 | 0 | BD013946 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0
563 | kawran Bazar North | C672K | 11 | 0 | BD013964 | 1 | 40380.21 | 40456.52 | 76.31 | 1000 | 0 | 76310 | 77104.1375 | Kakrail | Monipuripara 33/11 KV S/S | 72 | 81762.1785 | 77492.626 | 79448.9981 | 30221.7434 | 0
564 | NAM Bhanan RMU | D572NM | 11 | 0 | BD013950 | 1 | 17250.82 | 18200.87 | 950.05 | 1000 | 0 | 950050 | 959936.9135 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 1011015.5749 | 965308.8823 | 1005888.2452 | 1030950.7605 | 1013545.3917
565 | Novo Theater | 0 | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0
566 | Monipuripara Nearest | C172I | 11 | 0 | BD013962 | 1 | 38929.72 | 39654.38 | 724.66 | 1000 | 0 | 724660 | 732201.3407 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 808641.8922 | 823257.478 | 844317.6909 | 794156.578 | 733061.8614
567 | Holy Cross | C172HC | 11 | 0 | BD013965 | 1 | 38607.3 | 39906.37 | 1299.07 | 1000 | 0 | 1299070 | 1312589.0703 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 1258529.5254 | 1242673.6384 | 1267377.9768 | 1286005.418 | 1126874.592
568 | Honda Goli | C172HG | 11 | 0 | BD014011 | 1 | 15366.23 | 16352.73 | 986.5 | 1000 | 0 | 986500 | 996766.2388 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 1069470.1647 | 1059189.7376 | 1074102.0051 | 1068926.6085 | 953126.0337
569 | Navy Quarter | C172NQ | 11 | 0 | BD013941 | 1 | 5549.43 | 5723.59 | 174.16 | 1000 | 0 | 174160 | 175972.436 | Tejgaon | Monipuripara 33/11 KV S/S | 72 | 196544.2773 | 221522.2664 | 200143.5254 | 202962.2853 | 175339.91
570 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 2063.78 | 2141.19 | 77.41 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0
571 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 585.48 | 585.48 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 72 | 0 | 0 | 0 | 0 | 0
572 | Doctor Goli | D1113D | 11 | 0 | BD013944 | 1 | 9640.93 | 10546.84 | 905.91 | 1000 | 0 | 905910 | 917384.4784 | Moghbazar | Ispahani 33/11 KV SS | 113 | 958125.7556 | 963950.8063 | 948233.0953 | 958270.3835 | 898591.0283
573 | Ispahani | D1113S | 11 | 0 | BD013947 | 1 | 10792.27 | 11780.12 | 987.85 | 1000 | 0 | 987850 | 1000362.3505 | Moghbazar | Ispahani 33/11 KV SS | 113 | 1092016.0616 | 1087721.0462 | 1055882.4039 | 1058199.8531 | 999582.0108
574 | BTCL | C6113BT | 11 | 0 | BD013949 | 1 | 5553.52 | 6098.75 | 545.23 | 1000 | 0 | 545230 | 552136.017 | Kakrail | Ispahani 33/11 KV SS | 113 | 523407.6855 | 549951.6967 | 529591.2713 | 523726.617 | 532492.3633
575 | Vikarunnesa | C6113VQ | 11 | 0 | BD013948 | 1 | 7515.66 | 8561.61 | 1045.95 | 1000 | 0 | 1045950 | 1059198.2594 | Kakrail | Ispahani 33/11 KV SS | 113 | 1138092.7736 | 1152044.6426 | 1148347.0254 | 1136233.5895 | 1092064.7445
576 | OASIS | 0 | 11 | 0 | 0 | 1 | 202.8 | 310.99 | 108.19 | 1000 | 0 | 108190 | 109560.3611 | Kakrail | Ispahani 33/11 KV SS | 113 | 90109.3741 | 109400.2883 | 4342.8205 | 0 | 0
577 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
578 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
579 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
580 | Wireless | D1113W | 11 | 0 | 0 | 1 | 8932.63 | 9982.44 | 1049.81 | 1000 | 0 | 1049810 | 1063107.1511 | Moghbazar | Ispahani 33/11 KV SS | 113 | 1088068.9306 | 1084178.7327 | 1047125.901 | 1048087.1638 | 896344.5253
581 | Kazir Goli | C6113KG | 11 | 0 | 0 | 1 | 8472.69 | 9531.61 | 1058.92 | 1000 | 0 | 1058920 | 1072332.5406 | Kakrail | Ispahani 33/11 KV SS | 113 | 1195416.795 | 1197081.1949 | 1203659.779 | 1263311.3532 | 1182067.1763
582 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
583 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
584 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
585 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
586 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
587 | Spare | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
588 | AT-01 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
589 | AT-02 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 113 | 0 | 0 | 0 | 0 | 0
590 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | A828D | 11 | New | XA587377 | 1 | 217862.8 | 220112.5 | 2249.7 | 1000 | 0 | 2249700 | 2264304.2356 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2396448.119 | 2486440.3485 | 2725888.0748 | 2549641.8301 | 2438789.3271
591 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | A828K | 11 | New | XA587359 | 1 | 17125.2 | 17238.9 | 113.7 | 1000 | 0 | 113700 | 114438.0991 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 122268.7906 | 127832.1205 | 148265.7961 | 145583.9006 | 138711.8093
592 | 11 kV Narayangonj Direct Feeder (F-3) | A828F | 11 | New | XA586385 | 1 | 111187.4 | 112545.1 | 1357.7 | 1000 | 0 | 1357700 | 1366513.6955 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1396305.5531 | 1491140.0618 | 1611243.3589 | 1535819.0344 | 1523513.0022
593 | 11 kV Ekata Steel Feeder (F-4) | A828T | 11 | New | XA587376 | 1 | 174800.7 | 177164.8 | 2364.1 | 1000 | 0 | 2364100 | 2379446.8789 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2449713.7307 | 2507460.7365 | 2663481.8388 | 2529191.2405 | 2405949.7847
594 | 11 kV Silo+Titas Feeder (F-5) | A828I | 11 | New | XA575929 | 1 | 7125.2 | 7210.5 | 85.3 | 1000 | 0 | 85300 | 85853.7366 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 56292.0669 | 68291.1171 | 54248.5581 | 41407.382 | 36566.7297
595 | 11 kV Monowar Feeder (F-6) | A828L | 11 | New | XA587363 | 1 | 77339.6 | 78690 | 1350.4 | 1000 | 0 | 1350400 | 1359166.3065 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 1319938 | 1387647.3379 | 1431264.5899 | 1311672.4727 | 1337959.5143
596 | 11 kV Era Steel Feeder (F-7) | A828G | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0
597 | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 11 | New | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0
598 | 11 kV Mizmizi Feeder (F-9) | A828M | 11 | New | XA587358 | 1 | 151130.8 | 153390.8 | 2260 | 1000 | 0 | 2260000 | 2274671.0995 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2350345.1179 | 2375002.1192 | 2446793.5192 | 2328937.4468 | 2238024.8856
599 | 11 KV Jhilpar (F-10) | E228Z | 11 | New | XA587369 | 1 | 94.7878 | 101.8282 | 7.0404 | 40000 | 0 | 281616 | 283444.1488 | Matuail | Siddhirganj 33/11KV S/S | 28 | 297629.6761 | 330706.0205 | 314747.6869 | 291293.3394 | 424399.7103
600 | 11 kV Madrasha Road Feeder (F-11) | 0 | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0
601 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | A8281H | 11 | New | XA587383 | 1 | 15601.7 | 16306.6 | 704.9 | 1000 | 0 | 704900 | 709475.9549 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 663499.8644 | 692465.8927 | 722974.2051 | 681450.0937 | 758130.0486
602 | Seven Horse Feeder (F-13) | A828H | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 0 | 0 | 0 | 0 | 0
603 | 11 kV Shanti Nagar (F-14) | A828N | 11 | New | XA587371 | 1 | 152087.1 | 154796.1 | 2709 | 1000 | 0 | 2709000 | 2726585.8445 | Siddirgonj | Siddhirganj 33/11KV S/S | 28 | 2843859.0812 | 2866014.2453 | 2915044.2314 | 2806489.0873 | 2820775.6603
604 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | E216W | 11 | 0 | HA021101013-02 | 1 | 51773300 | 54945696 | 3172396 | 1 | 0 | 3172396 | 3182659.205 | Matuail | Demra 33/11KV S/S | 16 | 3242375.7883 | 2482601.3667 | 2346002.1943 | 2312393.5546 | 2206583.7096
605 | 11 kV DND (WASA) Feeder. | A816B | 11 | 0 | HA021100992-02 | 1 | 6258120 | 6447792 | 189672 | 1 | 0 | 189672 | 190285.6191 | Siddirgonj | Demra 33/11KV S/S | 16 | 296942.4232 | 349346.3885 | 251256.153 | 80170.7162 | 6927.7253
606 | 11 kV Local Feeder | A816D | 11 | 0 | HA021100794-02 | 1 | 12242460 | 13337258 | 1094798 | 1 | 0 | 1094798 | 1098339.8454 | Siddirgonj | Demra 33/11KV S/S | 16 | 1209825.1625 | 1190157.3614 | 1182388.6301 | 2088621.9879 | 1417684.9395
607 | 11 kV Mouchak Feeder | A816A | 11 | 0 | DHK60888 | 1 | 974230.4 | 1013189.5 | 38959.1 | 60 | 0 | 2337546 | 2345108.3326 | Siddirgonj | Demra 33/11KV S/S | 16 | 2403503.8665 | 2439051.751 | 2339275.7144 | 2308639.9015 | 2074135.4747
608 | 11 kV Overhead-1 Feeder | A816C | 11 | 0 | HA021100829-02 | 1 | 79132380 | 79563317 | 430937 | 1 | 0 | 430937 | 432331.1497 | Siddirgonj | Demra 33/11KV S/S | 16 | 507759.6491 | 490206.9454 | 1190489.8427 | 1095153.438 | 1095304.9401
609 | 11 kV Provati Steel Feeder | A816Z | 11 | 0 | DHK60874 | 1 | 591968.1 | 601475.9 | 9507.8 | 60 | 0 | 570468 | 572313.5546 | Siddirgonj | Demra 33/11KV S/S | 16 | 603535.6264 | 2095360.2501 | 124835.9443 | 0 | 0
610 | 11 kV Islambagh Feeder. | E116I | 11 | 0 | DHKA2190 | 1 | 1140.165 | 1179.7411 | 39.5761 | 60000 | 0 | 2374566 | 2382248.0982 | Matuail | Demra 33/11KV S/S | 16 | 2479849.2574 | 3031414.6894 | 2979112.0563 | 3002442.9965 | 2983539.0327
611 | 11 kV Taj Jute Feeder. | A816E | 11 | 0 | DHK61062 | 1 | 653180.2 | 679906.6 | 26726.4 | 60 | 0 | 1603584 | 1608771.849 | Siddirgonj | Demra 33/11KV S/S | 16 | 1850699.8521 | 525126.6242 | 1404410.5059 | 1676660.8446 | 1675376.4941
612 | 11 kV Al-Aksa Steel Feeder | A816S | 11 | 0 | DHK61061 | 1 | 819260.3 | 848208.6 | 28948.3 | 60 | 0 | 1736898 | 1742517.141 | Siddirgonj | Demra 33/11KV S/S | 16 | 1948104.7891 | 1679729.0047 | 1595509.5853 | 1474597.4818 | 1597579.1906
613 | 11 kV Sahebpara O/H (Old Spare Feeder) | A816W | 11 | 0 | DHKA2189 | 1 | 1074.576 | 1116.5269 | 41.9509 | 60000 | 0 | 2517054 | 2525197.0695 | Siddirgonj | Demra 33/11KV S/S | 16 | 2620588.9584 | 2664152.1809 | 2514049.716 | 2467512.3805 | 2370283.5934
614 | 11 kV Over Head Feeder-2. | E116V | 11 | 0 | HA021100488-02 | 1 | 31329630 | 33418808 | 2089178 | 1 | 0 | 2089178 | 2095936.8227 | Demra | Demra 33/11KV S/S | 16 | 2186616.3464 | 2197276.8827 | 2204224.8423 | 2131027.6013 | 2071443.4949
615 | 11 kV Shimrail Express Feeder. | A8164 | 11 | 0 | HA021100511-02 | 1 | 8223928 | 8254376 | 30448 | 1 | 0 | 30448 | 30546.5041 | Siddirgonj | Demra 33/11KV S/S | 16 | 1269.0967 | 53083.1379 | 75076.7556 | 29225.6688 | 0
616 | 11 kV Sarder & Khadem Steel Feeder | E116SK | 11 | 0 | HA021100413-02 | 1 | 81824770 | 82154657 | 329887 | 1 | 0 | 329887 | 330954.2369 | Demra | Demra 33/11KV S/S | 16 | 688064.1207 | 409117.6527 | 331227.7744 | 650733.1002 | 409613.9007
617 | 11 kV Siddhirgonj Mazar Feeder | 0 | 11 | 0 | HA021100393-02 | 1 | 24945.09 | 26069.366 | 1124.276 | 1000 | 0 | 1124276 | 1127913.2115 | Siddirgonj | Demra 33/11KV S/S | 16 | 1241829.7858 | 1214207.0897 | 1262090.4156 | 281800.301 | 832832.3648
618 | 11 kV AST Beverage Feeder | A816J | 11 | 0 | 0 | 1 | 22532950 | 23064522 | 531572 | 1 | 0 | 531572 | 533291.7199 | Siddirgonj | Demra 33/11KV S/S | 16 | 269111.0012 | 890478.2395 | 1164572.2996 | 1051751.2525 | 1163750.6238
619 | 11 kV Karim Market Feeder | E216K | 11 | 0 | 0 | 1 | 60540.91 | 62687.216 | 2146.306 | 1000 | 0 | 2146306 | 2153249.6409 | Matuail | Demra 33/11KV S/S | 16 | 2251573.1315 | 2292212.1727 | 2119617.9699 | 2072299.946 | 2089377.8867
620 | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 16 | 0 | 0 | 0 | 0 | 0
621 | 11 kV Dayagonj Feeder (=L11) | E116G | 11 | 0 | 2007755114 | 1 | 5865.74 | 5918.8 | 53.06 | 60000 | 0 | 3183600 | 3219680.3589 | Demra | Sarulia 33/11KV S/S | 83 | 3402160.7226 | 2567812.3685 | 2674737.7934 | 2648546.8605 | 3036942.6611
622 | 11 kV Karim Jute Feeder (=L12) | E183J | 11 | 0 | 30799484 | 1 | 21.8339 | 22.0742 | 0.2403 | 60000 | 0 | 14418 | 14581.402 | Demra | Sarulia 33/11KV S/S | 83 | 14754.6723 | 14656.6857 | 14157.8637 | 13577.9934 | 12817.0467
623 | 11 kV Konapara (=L13) **** | E183KL | 11 | 0 | DHKA2191 | 1 | 2165.8271 | 2208.3613 | 42.5342 | 60000 | 0 | 2552052 | 2580974.9024 | Demra | Sarulia 33/11KV S/S | 83 | 2723567.5839 | 3439291.4731 | 3588042.0557 | 3482255.5223 | 2467003.1131
624 | 11 kV Sanarpar Feeder (=L14) | E183S | 11 | 0 | 575926 | 1 | 56099.9 | 58574.2 | 2474.3 | 1000 | 0 | 2474300 | 2502341.7238 | Matuail | Sarulia 33/11KV S/S | 83 | 2566996.3354 | 2566696.0166 | 2627544.9143 | 2556143.6589 | 2386518.0767
625 | 11 kV Latif Bawani Feeder (=L15) | E183L | 11 | 0 | 30799450 | 1 | 1819.9 | 1825.25 | 5.35 | 60000 | 0 | 321000 | 324637.9555 | Demra | Sarulia 33/11KV S/S | 83 | 325784.1394 | 326380.7042 | 261798.4288 | 295524.6849 | 302404.9427
626 | 11 kV Tengra Feeder (=L16) | E183T | 11 | 0 | 30799145 | 1 | 5565.59 | 5610.1 | 44.51 | 60000 | 0 | 2670600 | 2700866.43 | Demra | Sarulia 33/11KV S/S | 83 | 2803570.4254 | 2888103.8805 | 2785803.7935 | 2203397.2826 | 3315319.3041
627 | 11 kV Police Line Feeder (=L17) | E183PL | 11 | 0 | 30799480 | 1 | 3358.77 | 3379.8 | 21.03 | 60000 | 0 | 1261800 | 1276100.2252 | Demra | Sarulia 33/11KV S/S | 83 | 1292175.5957 | 1231843.5906 | 1213792.7153 | 1297576.8726 | 1183247.2468
628 | 11 kV Demra Bazar Feeder (=L18) | E183D | 11 | 0 | 30799119 | 1 | 1655.95 | 1664.08 | 8.13 | 60000 | 0 | 487800 | 493328.3324 | Demra | Sarulia 33/11KV S/S | 83 | 441483.1795 | 534022.1596 | 561432.5279 | 558765.1604 | 495803.4526
629 | 11 kV Spare Feeder (=F9) | 0 | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0
630 | 11 kV Boxnagar Feeder (=F10) | E183N | 11 | 0 | HA021100493-02 | 1 | 86640496 | 89482972 | 2842476 | 1 | 0 | 2842476 | 2874690.3342 | Demra | Sarulia 33/11KV S/S | 83 | 3063617.2119 | 3062145.1731 | 3047117.0714 | 3001937.8862 | 2753359.8865
631 | 11 kV Baser Pool Feeder (=L11) | E118B | 11 | 0 | HA021100518-02 | 1 | 50869565 | 50895377 | 25812 | 1 | 0 | 25812 | 26104.5324 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 1592.7597 | 158210.2162 | 30254.1689
632 | 11 kV Dip-Pur Feeder (=L12) | E183P | 11 | 0 | HA021100697-02 | 1 | 27201550 | 29322895 | 2121345 | 1 | 0 | 2121345 | 2145386.6161 | Demra | Sarulia 33/11KV S/S | 83 | 2228761.3555 | 2265661.5752 | 2324189.2905 | 2304863.862 | 2171918.011
633 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0
634 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 83 | 0 | 0 | 0 | 0 | 0
635 | 11 kV Khanpur Feeder | B723B | 11 | 0 | DHKC 9348 | 1 | 5240.9 | 32799.1 | 27558.2 | 60 | 0 | 1653492 | 1671397.6523 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1767813.7522 | 1753296.6737 | 1849730.4598 | 1858439.2031 | 1689432.0922
636 | 11 kV Mission Para Feeder. | B723T | 11 | 0 | DHKC 9347 | 1 | 87209.98 | 112889.86 | 25679.88 | 60 | 0 | 1540792.8 | 1557478.0335 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1662446.9196 | 1652830.7535 | 1736094.2229 | 1666330.9001 | 1591097.4109
637 | 11 kV Esha Kha Feeder | B723M | 11 | 0 | DHKC 9311 | 1 | 12466.88 | 29602.88 | 17136 | 60 | 0 | 1028160 | 1039293.9368 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1004043.7507 | 968513.5517 | 939733.5453 | 917602.1317 | 1040108.3114
638 | 11 kV New Hazigonj Feeder | B723F | 11 | 0 | DHKC 9314 | 1 | 241.31 | 275.24 | 33.93 | 60000 | 0 | 2035800 | 2057845.6627 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 2170066.5597 | 2135314.0661 | 2193735.673 | 2054393.8757 | 2135156.6373
639 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
640 | 11 kV Hospital RMU Feeder. | B723H | 11 | 0 | 6604412 | 1 | 7.01 | 8.03 | 1.02 | 60000 | 0 | 61200 | 61862.7343 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 64307.2562 | 63695.448 | 65004.0756 | 61352.3895 | 59949.0945
641 | 11 kV Old Hajiganj Feeder. | B723E | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
642 | 11 kV Siraj-ud-daullah Feeder. | B723D | 11 | 0 | 06604389 | 1 | 49646.85 | 70259.15 | 20612.3 | 60 | 0 | 1236738 | 1250130.6264 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1328944.0291 | 1304005.3624 | 1304824.3795 | 1324560.4284 | 1260578.6756
643 | 11 kV Spare Feeder. | 0 | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
644 | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
645 | 11 kV B. B. Road West Feeder. | A723A | 11 | 0 | 6604415 | 1 | 329.61 | 375.72 | 46.11 | 40000 | 0 | 1844400 | 1864372.9936 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 1918297.585 | 1915716.4264 | 1976042.8964 | 1840166.7201 | 1800087.6245
646 | 11 kV Mondalpara Feeder. | 0 | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
647 | 11 kV B. B. Road East Feeder. | B723C | 11 | 0 | 06604392 | 1 | 257.82 | 293.14 | 35.32 | 40000 | 0 | 1412800 | 1428099.2005 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1517085.0182 | 1504830.2349 | 1509066.5776 | 1463548.0912 | 1396793.7162
648 | 11 kV Bishaw Road Feeder. | B723A | 11 | 0 | 06604393 | 1 | 281.34 | 308.98 | 27.64 | 40000 | 0 | 1105600 | 1117572.534 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1216580.0413 | 1210820.1352 | 1222724.6371 | 1779421.78 | 1969640.6189
649 | 11 kV Chasara Feeder. | A723B | 11 | 0 | 06604391 | 1 | 362.61 | 410.64 | 48.03 | 40000 | 0 | 1921200 | 1942004.6602 | N.Gonj (West) | Khanpur 33/11KV S/S | 23 | 2118903.8684 | 2081122.3834 | 2195963.227 | 2115948.7484 | 2048765.3497
650 | 11 kV Pathan Tully Feeder. | B723G | 11 | 0 | 06604388 | 1 | 50.76 | 65.03 | 14.27 | 40000 | 0 | 570800 | 576981.1889 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 529827.0791 | 160552.9705 | 39690.9621 | 0 | 0
651 | 11 kV Spare Feeder. | 0 | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
652 | 11 kV Nayamati Feeder. | B722J | 11 | 0 | 6604289 | 1 | 233.78 | 266.66 | 32.88 | 40000 | 0 | 1315200 | 1329442.2908 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 1269562.7492 | 1343468.4333 | 1193968.9401 | 1316545.3361 | 1343505.6323
653 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
654 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
655 | 11 kV Spare Feeder. | 0 | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 23 | 0 | 0 | 0 | 0 | 0
656 | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0.415 | 0 | 412109 | 1 | 9177.2 | 9204 | 26.8 | 10 | 0 | 268 | 270.9022 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 317.4918 | 324.5435 | 42.526 | 0 | 0
657 | 33/0.415 kV Auxiliary Transformer-2 | 0 | 0.415 | 0 | 243285 | 1 | 6433.2 | 6433.2 | 0 | 10 | 0 | 3000 | 3032.487 | N.Gonj (East) | Khanpur 33/11KV S/S | 23 | 3033.3611 | 3033.1166 | 3037.5736 | 3037.247 | 3027.732
658 | 11 kV Link Road Feeder | B741N | 11 | 0 | HA021100475-02 | 1 | 94015.775 | 97092.756 | 3076.981 | 1000 | 0 | 3076981 | 3109326.5102 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 2934230.0248 | 2975929.581 | 2607402.2302 | 1951841.3049 | 1877540.2045
659 | 11 kV Lamapara Express Feeder | B723L | 11 | 0 | HA021100928-03 | 1 | 79149.036 | 80182.444 | 1033.408 | 1000 | 0 | 1033408 | 1044271.2809 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 777935.2019 | 1101665.3091 | 726895.7131 | 1017580.9915 | 1063497.0225
660 | 11 kV Kutubpur Feeder*** | B741Q | 11 | 0 | DHK66616 | 1 | 18071.3 | 18290.01 | 218.71 | 8000 | 0 | 1749680 | 1768072.7988 | N.Gonj (East) | Matuail 33/11KV S/S | 41 | 1341995.221 | 1569417.834 | 1641482.3695 | 1554956.8642 | 1703285.4205
661 | 11 kV Ramarbagh Feeder (F1) | B841M | 11 | 0 | DHK66625 | 1 | 3557.19 | 3580.6 | 23.41 | 60000 | 0 | 1404600 | 1419365.2857 | Fatullah | Matuail 33/11KV S/S | 41 | 1418275.2675 | 1534196.2033 | 1364062.3916 | 1338941.0426 | 835792.1765
662 | 11 kV Tushardhara Feeder (F2) | E241T | 11 | 0 | DHK66623 | 1 | 3887.45 | 3931.53 | 44.08 | 60000 | 0 | 2644800 | 2672602.3834 | Matuail | Matuail 33/11KV S/S | 41 | 2999054.9265 | 2829014.2755 | 2689931.0362 | 2755784.1096 | 2760297.6743
663 | 11 kV Matuail Medical Feeder (F3) | E227M | 11 | 0 | DHK66627 | 1 | 3316.68 | 3332.15 | 15.47 | 60000 | 0 | 928200 | 937957.3247 | Matuail | Matuail 33/11KV S/S | 41 | 903475.9079 | 1019170.5275 | 792368.687 | 795452.7012 | 696897.8308
664 | 11 kV Rupayan Town Feeder (F4) | E241R | 11 | 0 | HA021101044-02 | 1 | 66232.154 | 66528.706 | 296.552 | 1000 | 0 | 296552 | 299669.3822 | Matuail | Matuail 33/11KV S/S | 41 | 351957.4279 | 332319.5113 | 349545.5347 | 361905.6203 | 323912.9361
665 | 11 kV Shibu Market Feeder (F7) | B841B | 11 | 0 | DHK66624 | 1 | 2383.91 | 2390.92 | 7.01 | 60000 | 0 | 420600 | 425021.3863 | Fatullah | Matuail 33/11KV S/S | 41 | 388070.1886 | 515025.6758 | 398306.2183 | 387075.6832 | 615623.4101
666 | 11 kV Soma-Sagar Steel (F6) | B841C | 11 | 0 | HA060300286-03 | 1 | 3583.649 | 5075.064 | 1491.415 | 1000 | 0 | 1491415 | 1507092.8931 | Fatullah | Matuail 33/11KV S/S | 41 | 1340202.4176 | 1497969.2549 | 1502329.9696 | 1201993.7471 | 1110650.3388
667 | 11 kV Jhalkuri Feeder (F8) | E241J | 11 | 0 | DHK66626 | 1 | 4466.06 | 4509.48 | 43.42 | 60000 | 0 | 2605200 | 2632586.1045 | Matuail | Matuail 33/11KV S/S | 41 | 2681928.8192 | 2638599.8531 | 2625668.5413 | 2669361.5514 | 2690547.2387
668 | 11 kV Madani Nagar Feeder (F9) | E241N | 11 | 0 | DHK6622 | 1 | 4234.09 | 4256.29 | 22.2 | 60000 | 0 | 1332000 | 1346002.1078 | Matuail | Matuail 33/11KV S/S | 41 | 1350362.9845 | 1363125.4682 | 1274337.3987 | 1416234.4574 | 1374993.3702
669 | 11 kV Rajmahal Feeder (F10) | B4413 | 11 | 0 | DHKA2187 | 1 | 120.5913 | 126.118 | 5.5267 | 60000 | 0 | 331602 | 335087.831 | Shyampur | Matuail 33/11KV S/S | 41 | 248953.0896 | 243349.6318 | 240620.6059 | 244740.1643 | 218634.2568
670 | 11 kV Bhuighor Bazar | 0 | 11 | 0 | HA021100861-02 | 1 | 869.686 | 2266.614 | 1396.928 | 1000 | 0 | 1396928 | 1411612.637 | Matuail | Matuail 33/11KV S/S | 41 | 1387743.4624 | 1286702.6096 | 1290448.3093 | 1462145.9342 | 1034107.8281
671 | 11 kV Tokkar Math Feeder | B8416 | 11 | 0 | HA021200298-02 | 1 | 81846.959 | 82630.261 | 783.302 | 1000 | 0 | 783302 | 791536.1434 | Fatullah | Matuail 33/11KV S/S | 41 | 789253.9157 | 797388.0996 | 771061.022 | 778486.6953 | 733095.2742
672 | 11 kV Osmani Stadium Feeder***** | B841OS | 11 | 0 | XA575922 | 1 | 213.4 | 232.8 | 19.4 | 1000 | 0 | 19400 | 19603.9346 | Fatullah | Matuail 33/11KV S/S | 41 | 10611.2942 | 9873.3404 | 9194.7909 | 13287.9755 | 64493.8811
673 | 33/0.415 KV Transformer, AT-1 | 0 | 0.415 | 0 | 2001123043119 | 1 | 7506.3 | 7578.2 | 71.9 | 160 | 0 | 11504 | 11624.9311 | Shyampur | Matuail 33/11KV S/S | 41 | 12240.3805 | 12799.0731 | 12965.6656 | 12496.7831 | 11807.0303
674 | 33/0.415 KV Transformer, AT-2 | 0 | 0.415 | 0 | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 41 | 0 | 0 | 0 | 0 | 129.3921
675 | 11 kV Godnail (F16) | A8963 | 11 | 0 | 00000109 | 1 | 28743610 | 30618406 | 1874796 | 1 | 0 | 1874796 | 1902311.4075 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2038403.821 | 2022169.7421 | 1902174.2906 | 1848814.9706 | 1869406.9017
676 | 11 kV M. Circus (F15) | B796C | 11 | 0 | 00000123 | 1 | 110692328 | 112349288 | 1656960 | 1 | 0 | 1656960 | 1681278.3417 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1521029.259 | 1828274.6635 | 1936785.1498 | 1975646.3394 | 2135882.0516
677 | 11 kV Wapderpool (F14) | B723W | 11 | 0 | 00000190 | 1 | 57555940 | 58342616 | 786676 | 1 | 0 | 786676 | 798221.6352 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 482340.828 | 822312.035 | 474935.0147 | 619875.2088 | 595303.4365
678 | 11 kV Chowdhury Bari (F13) | A896C | 11 | 0 | 00000191 | 1 | 102995352 | 105146864 | 2151512 | 1 | 0 | 2151512 | 2183088.6246 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2226891.1005 | 2193767.4037 | 2204031.0267 | 2287431.9192 | 2194488.2982
679 | 11 kV Ailpara (F12) | B7966 | 1 | 0 | 00000192 | 1 | 56582940 | 58996976 | 2414036 | 1 | 0 | 2414036 | 2449465.553 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 2507772.6658 | 2664936.682 | 2385423.2662 | 2312455.9158 | 2506620.5244
680 | 11 kV Spare (F11) | 0 | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0
681 | 11 kV Spare (F10) | 0 | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0
682 | 11 kV Spare (F9) | 0 | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0
683 | 11 kV Spare (F8) | 0 | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0
684 | 11 kV Zulfiqur Steel | A8962H | 11 | 0 | 00000197 | 1 | 17476638 | 18664354 | 1187716 | 1 | 0 | 1187716 | 1205147.4911 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 881898.0967 | 1269192.9831 | 1109871.8066 | 1233882.0915 | 1248729.4855
685 | 11 kV New Laxmi Narayan Cotton Mill (F6) | B796X | 11 | 0 | 00000198 | 1 | 4203789 | 4241549 | 37760 | 1 | 0 | 37760 | 38314.1839 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 81476.5739 | 45981.5802 | 80821.2927 | 12574.267 | 42071.0581
686 | 11 kV Lucky Bazar (F5) | B796Z | 11 | 0 | 00000199 | 1 | 91070136 | 92459576 | 1389440 | 1 | 0 | 1389440 | 1409832.0895 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1363293.8581 | 1360268.1394 | 1265880.4844 | 1332623.2308 | 1392661.9878
687 | 11 kV Enayetnagar (F4) | A896Y | 11 | 0 | 00000200 | 1 | 34021796 | 35538712 | 1516916 | 1 | 0 | 1516916 | 1539178.9886 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1637703.7047 | 1666199.7304 | 1606948.7378 | 1544300.7721 | 1576051.8888
688 | 11 kV Bhuiyapara (F3) | A896V | 11 | 0 | 00000201 | 1 | 67505552 | 69299712 | 1794160 | 1 | 0 | 1794160 | 1820491.9548 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1638474.4387 | 1895985.9869 | 1703398.6781 | 2021560.4921 | 1949356.1666
689 | 11 kV Arambagh (F2) | B796D | 11 | 0 | 00000202 | 1 | 10097575 | 11191773 | 1094198 | 1 | 0 | 1094198 | 1110256.976 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 1096967.543 | 1072171.1368 | 1011302.9055 | 1033739.3311 | 1073358.7436
690 | 11 kV Spare (F1) | 0 | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0 | 0 | 0
691 | 11/0.415 kV Aux. Transformer-1 | 0 | 0.415 | 0 | 00000204 | 1 | 1713.27 | 1753.31 | 40.04 | 100 | 0 | 4004 | 4062.7646 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 4590.7608 | 4148.0738 | 5028.3475 | 4509.4616 | 4713.1396
692 | 11/0.415 kV Aux. Transformer-2 | 0 | 0.415 | 0 | 00000205 | 1 | 60.72 | 61.16 | 0.44 | 100 | 0 | 44 | 44.6458 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 96 | 0 | 0 | 0.99927 | 0 | 0
693 | 11 kV Minan Steel Feeder | A717R | 11 | New | 0 | 1 | 76821856 | 77458900 | 637044 | 1 | 0 | 637044 | 639787.7036 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 668682.8226 | 690626.9008 | 493276.6302 | 608736.535 | 686221.5647
694 | 11 kV Shovon Garments | A717V | 11 | New | HA021100480-02 | 1 | 89548428 | 90382612 | 834184 | 1 | 0 | 834184 | 837776.7717 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 17 | 798148.0435 | 798255.2776 | 675313.5877 | 687996.4568 | 904286.638
695 | 11 kV Mazar O/H Feeder | B817M | 11 | New | DHK61059 | 1 | 186054.2 | 205819 | 19764.8 | 60 | 0 | 1185888 | 1190995.536 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1654746.3681 | 1713127.7082 | 1429973.3518 | 1348752.6633 | 1520277.0648
696 | 11 kV Shahjahan Steel. | B817S | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
697 | 11 kV Pilkuni O/H Feeder. | B817I | 11 | New | DHK61058 | 1 | 342116.1 | 358618.1 | 16502 | 60 | 0 | 990120 | 994384.377 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1017275.0549 | 998917.0422 | 983661.4804 | 966418.4358 | 973413.7301
698 | 11 kV Narayangonj Express Feeder. | B817N | 11 | New | DHK61052 | 1 | 36070.8 | 67878.2 | 31807.4 | 60 | 0 | 1908444 | 1916663.5337 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1932341.6728 | 1605143.4286 | 2269442.86 | 1903765.6601 | 1898489.4903
699 | 11 kV Post Office Road Feeder. | B817P | 11 | New | DHK61053 | 1 | 80146 | 91772.6 | 11626.6 | 60 | 0 | 697596 | 700600.4968 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 623925.9784 | 637276.1792 | 646164.6825 | 667510.2274 | 661387.5474
700 | 11 kV Fatullah Feeder. | B817F | 11 | New | DHK61056 | 1 | 646090.6 | 661621.5 | 15530.9 | 60 | 0 | 931854 | 935867.4295 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 898188.9867 | 879720.3375 | 817413.76 | 827156.9088 | 863427.9271
701 | 11 kV Al-baraka & Shah Fatullah. | B817L | 11 | New | DHK61114 | 1 | 541205.3 | 559147.2 | 17941.9 | 60 | 0 | 1076514 | 1081150.4699 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1065440.2479 | 1123770.5196 | 1043132.595 | 1256184.2479 | 1130265.9765
702 | 11 kV Haque Steel & Shilpi Steel | B817Q | 11 | New | DHK61111 | 1 | 872508.4 | 877493.5 | 4985.1 | 60 | 0 | 299106 | 300394.2285 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 217235.7079 | 274279.1183 | 230613.5281 | 268951.939 | 461817.7457
703 | 11 kV Dhaka Steel | B817W | 11 | New | DHK60923 | 1 | 538878 | 538934.5 | 56.5 | 60 | 0 | 3390 | 3404.6005 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 458632.0662 | 1006566.474 | 739323.8488 | 888156.2557 | 505747.1466
704 | 11 kV Panchabati O/H Feeder | E317Z | 11 | New | HA021100891-02 | 1 | 1798728 | 2534578 | 735850 | 1 | 0 | 735850 | 739019.2541 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 764214.6584 | 798862.9891 | 731731.9387 | 686782.5544 | 645276.6941
705 | 11 kV Dharmagonj Feeder. | E317D | 11 | New | HA021101231-02 | 1 | 25554756 | 25882355 | 327599 | 1 | 0 | 327599 | 329009.9458 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 336317.7733 | 326230.0217 | 318326.9039 | 335635.5116 | 326421.8579
706 | 11 kV Sena Edible Oil Feeder. | E317SK | 11 | New | HA021101108-02 | 1 | 15758208 | 16128427 | 370219 | 1 | 0 | 370219 | 371813.5071 | Sytalakhya | Fatullah OLD 33/11KV S/S | 17 | 231457.5089 | 350113.1813 | 373857.3757 | 329133.6781 | 311868.8913
707 | 11 kV Kutubail Feeder | B817U | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
708 | 11 kV Aligonj Feeder | B817A | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 123409.7429 | 535601.4665
709 | 11 kV Gabtoli Feeder | B817T | 11 | New | HA021101005-02 | 1 | 16913493 | 17649412 | 735919 | 1 | 0 | 735919 | 739088.5512 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 985608.2317 | 2067941.9788 | 1957359.7515 | 2145386.8814 | 2599917.6327
710 | 11 kV Jamuna Steel Feeder. | B817J | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
711 | 0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
712 | 11 kV Bishwa Road Feeder | B826B | 11 | New | HA021100705-02 | 1 | 8389302 | 10179956 | 1790654 | 1 | 0 | 1790654 | 1798366.2205 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 1947566.1648 | 1839951.043 | 1845653.8856 | 1844325.072 | 1788794.6263
713 | 11 kV Spare Feeder | 0 | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
714 | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 17 | 0 | 0 | 0 | 0 | 0
715 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
716 | 11 kV Outgoing Feeder-2 (=F2) | 0 | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
717 | 11 kV Morakhalpar (=F3) | E3107X | 11 | Shitalakhya | 041808902797 | 1 | 959.96 | 999.44 | 39.48 | 60000 | 0 | 2368800 | 2374197.2935 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2139879.5383 | 2225117.9731 | 1919103.2774 | 1925513.8961 | 2018573.5941
718 | 11 kV Achimtola (=F4) | E3107L | 11 | Shitalakhya | 041808902780 | 1 | 471.37 | 497.96 | 26.59 | 60000 | 0 | 1595400 | 1599035.1072 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1814088.8895 | 1616939.3533 | 1431521.3433 | 1476167.1668 | 1492878.3256
719 | 11 kV Horihorpara (=F5) | E3107R | 11 | Shitalakhya | 041808902782 | 1 | 553.03 | 563.73 | 10.7 | 60000 | 0 | 642000 | 643462.7923 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 673220.5289 | 698887.9434 | 713358.7902 | 702593.0118 | 691704.3007
720 | 11 kV Amtola Feeder (=F6) | E3107A | 11 | Shitalakhya | 041808902773 | 1 | 1238.64 | 1267.53 | 28.89 | 60000 | 0 | 1733400 | 1737349.5392 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1778023.504 | 1913418.8206 | 1823628.4898 | 1708359.7204 | 1811062.3039
721 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
722 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
723 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
724 | 11 kV Outgoing Feeder-10 (=F8) | 0 | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
725 | 11 kV Outgoing Feeder-11 (=F9) | 0 | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
726 | 11 kV Nabinagar (=F10) | E3107I | 11 | Shitalakhya | 041808902841 | 1 | 195.76 | 213.78 | 18.02 | 60000 | 0 | 1081200 | 1083663.5063 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1145075.9889 | 1196876.0424 | 1264590.5826 | 1201867.1554 | 1168078.0452
727 | 11 kV Dhalipara (=F11) | E3107F | 11 | Shitalakhya | 041808902842 | 1 | 88.69 | 98.21 | 9.52 | 60000 | 0 | 571200 | 572501.475 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 611308.2838 | 620963.1553 | 614881.6508 | 573262.9625 | 566596.0446
728 | 11 kV Etimkhana (=F12) | E3107Y | 11 | Shitalakhya | 041808902840 | 1 | 1141.38 | 1178.03 | 36.65 | 60000 | 0 | 2199000 | 2204010.4054 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 1471467.7275 | 1601110.8808 | 1579237.0524 | 1146525.925 | 1680540.7098
729 | 11 kV Premroad (=F13) | E3107P | 11 | Shitalakhya | 041808902798 | 1 | 1408.64 | 1452.18 | 43.54 | 60000 | 0 | 2612400 | 2618352.3343 | Sytalakhya | Fatullah New 33/11 KV SS | 107 | 2670641.7946 | 2813206.6084 | 2526178.8135 | 2500581.4639 | 2536449.5967
730 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 107 | 0 | 0 | 0 | 0 | 0
731 | 11 kV Katherpol Feeder | B8919 | 11 | 0 | 00000031 | 1 | 67326752 | 69331312 | 2004560 | 1 | 0 | 2004560 | 2017920.9065 | Fatullah | Dapa 33/11 kV | 91 | 1907068.817 | 2019617.347 | 1872668.2415 | 1825325.1091 | 2095256.7912
732 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
733 | 11 kV Union Parishad Feeder | B8918 | 11 | 0 | 00000032 | 1 | 67588392 | 69825752 | 2237360 | 1 | 0 | 2237360 | 2252272.5782 | Fatullah | Dapa 33/11 kV | 91 | 1663620.755 | 1557194.9668 | 1351133.0591 | 1174339.0851 | 1364658.7564
734 | 11 kV Shiachar Feeder | B891G | 11 | 0 | 00000030 | 1 | 69814874 | 71832544 | 2017670 | 1 | 0 | 2017670 | 2031118.288 | Fatullah | Dapa 33/11 kV | 91 | 2032383.0231 | 2001560.8541 | 1924678.9852 | 1907532.8668 | 1901950.2285
735 | 11 kV Sastapur Feeder | B8913 | 11 | 0 | 00000106 | 1 | 71305504 | 71818424 | 512920 | 1 | 0 | 512920 | 516338.7434 | Fatullah | Dapa 33/11 kV | 91 | 559825.9548 | 395679.6151 | 1143053.371 | 1344939.9892 | 1492863.3157
736 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
737 | 11 kV Jalal Ahmed Express | B891JA | 11 | 0 | 00000172 | 1 | 5241627 | 5637386 | 395759 | 1 | 0 | 395759 | 398396.8352 | Fatullah | Dapa 33/11 kV | 91 | 281983.6134 | 872.8694 | 163.171 | 71453.7073 | 791901.0884
738 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
739 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
740 | 11 kV Lalpur Feeder | B8911 | 11 | 0 | 00000044 | 1 | 81400280 | 84092032 | 2691752 | 1 | 0 | 2691752 | 2709693.2174 | Fatullah | Dapa 33/11 kV | 91 | 2479807.3342 | 1402820.0857 | 1449235.5198 | 1159780.4978 | 373576.7292
741 | 11 kV Kotaler Bag Feeder | B8912 | 11 | 0 | 00000050 | 1 | 87316664 | 89610784 | 2294120 | 1 | 0 | 2294120 | 2309410.8982 | Fatullah | Dapa 33/11 kV | 91 | 2305548.0804 | 2521037.1496 | 1462297.3552 | 1401235.8745 | 1515181.1462
742 | 11 kV Idrakpur Feeder | B8915 | 11 | 0 | 00000021 | 1 | 77920088 | 79058888 | 1138800 | 1 | 0 | 1138800 | 1146390.3941 | Fatullah | Dapa 33/11 kV | 91 | 1054879.9219 | 1213883.5456 | 1042540.0593 | 1114166.2721 | 1068664.5804
743 | 11 kV Isdair Feeder | B8914 | 11 | 0 | 00000029 | 1 | 41690220 | 42475456 | 785236 | 1 | 0 | 785236 | 790469.7993 | Fatullah | Dapa 33/11 kV | 91 | 829018.6896 | 795100.6656 | 849835.155 | 794122.676 | 792940.801
744 | 11 kV Shah Fateullah Express | 0 | 11 | 0 | 0000051 | 1 | 1009637 | 2873073 | 1863436 | 1 | 0 | 1863436 | 1875856.2789 | Fatullah | Dapa 33/11 kV | 91 | 1015342.7418 | 0 | 0 | 0 | 0
745 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
746 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
747 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0 | 0.415 | 0 | DHKF 7522 | 1 | 3132 | 3192 | 60 | 100 | 0 | 6000 | 6039.9915 | Fatullah | Dapa 33/11 kV | 91 | 6235.0379 | 5653.8129 | 5914.9473 | 5529.8501 | 5198.5629
748 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 91 | 0 | 0 | 0 | 0 | 0
749 | 11 kV Bholail Feeder (F-3) | E330V | 11 | 0 | DHK 9335 | 1 | 26613.8765 | 70399.8787 | 43786.0022 | 60 | 0 | 2627160.132 | 2632122.2753 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 3204950.7718 | 3202295.2627 | 3113891.785 | 3046734.2178 | 2464743.5384
750 | 11 kV Crony Apparels (F-2) | E330CC1 | 11 | 0 | DHK 9336 | 1 | 95805.2449 | 117372.339 | 21567.0941 | 60 | 0 | 1294025.646 | 1296469.7835 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1414735.196 | 1450857.7553 | 1198137.3888 | 1083589.5043 | 1409860.9795
751 | 11 kV Baburail Feeder (F-5) | A730R | 11 | 0 | DHK 9322 | 1 | 51769.6211 | 84762.3796 | 32992.7585 | 60 | 0 | 1979565.51 | 1983304.4857 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 2103409.2909 | 2067517.7824 | 2058052.5984 | 2038840.2789 | 1960329.6227
752 | 11 kV Goghchar Feeder (F-1) | E330G | 11 | 0 | DHK 9323 | 1 | 56304.0611 | 76884.4867 | 20580.4256 | 60 | 0 | 1234825.536 | 1237157.8572 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1317359.8624 | 1330855.5581 | 1324242.6499 | 1303267.9767 | 1261095.5642
753 | 11 kV Norshinghopur (F-2) | E330N | 11 | 0 | DHK 9365 | 1 | 40357.6851 | 66325.1503 | 25967.4652 | 60 | 0 | 1558047.912 | 1560990.7311 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1355613.7656 | 1460780.2783 | 1404336.8639 | 1352601.3966 | 1471201.0567
754 | 11 kV Geddar Bazar Feeder (F-4) | E330B | 11 | 0 | DHK 9367 | 1 | 6609.7103 | 15212.6093 | 8602.899 | 60 | 0 | 516173.94 | 517148.8821 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 0 | 0 | 0 | 0 | 554462.5713
755 | 11 kV Noluyapara Feeder (F-6)*** | B730A | 11 | 0 | H/A030701125-03 | 1 | 73556.451 | 73783.826 | 227.375 | 1000 | 0 | 227375 | 227804.4627 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 240354.077 | 235334.8005 | 246133.1449 | 234255.9876 | 224598.6372
756 | 11 kV Kashipur Feeder (F-7) | E317K | 11 | 0 | H/A030800169-03 | 1 | 38456.292 | 40041.956 | 1585.664 | 1000 | 0 | 1585664 | 1588658.98 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1710138.4368 | 1760370.7558 | 1741847.8978 | 1664580.229 | 1652181.4751
757 | 11 kV Spare Feeder (F-6) | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 0 | 0 | 0 | 0 | 0
758 | 11 kV Paikpara Feeder (F-8) | A730D | 11 | 0 | H/A030701098-03 | 1 | 80469.846 | 81538.063 | 1068.217 | 1000 | 0 | 1068217 | 1070234.6333 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 30 | 1102912.6399 | 1118443.5796 | 1135381.2606 | 1090515.7468 | 1082731.082
759 | 11 kV B. K. Road Feeder (F-9) | B730K | 11 | 0 | H/A030800205-03 | 1 | 96230.313 | 97166.397 | 936.084 | 1000 | 0 | 936084 | 937852.0624 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 30 | 845475.6866 | 838157.9765 | 729788.4502 | 786055.2221 | 765048.1281
760 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | E322T | 11 | 0 | H/A030701091-03 | 1 | 55276.511 | 56283.66 | 1007.149 | 1000 | 0 | 1007149 | 1009051.2889 | Sytalakhya | Sitalakhya 33/11KV S/S | 30 | 1042925.7746 | 1035234.9191 | 1075488.4842 | 1015821.5301 | 958950.0681
761 | 11 kV River View | B793U | 11 | 0 | 00000061 | 1 | 8013364 | 8849520 | 836156 | 1 | 0 | 836156 | 838291.0284 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 794103.9859 | 844731.2094 | 841728.9793 | 838140.6773 | 803073.4017
762 | 11 kV Railgate B.B. Road | B793F | 11 | 0 | 00000191 | 1 | 24086822 | 24783300 | 696478 | 1 | 0 | 696478 | 698256.3766 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 634632.2838 | 651403.112 | 672012.4136 | 662899.4007 | 611819.3181
763 | 11 kV DIT | A722D | 11 | 0 | 00000174 | 1 | 142723248 | 145783200 | 3059952 | 1 | 0 | 3059952 | 3067765.2362 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 3157724.5261 | 3006495.8053 | 3105959.8639 | 3165323.9759 | 2992837.0935
764 | 11 kV Dalpatti | B7227 | 11 | 0 | 00000182 | 1 | 5095427 | 5882705 | 787278 | 1 | 0 | 787278 | 789288.224 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 719006.8368 | 711194.3901 | 640949.3228 | 661646.5082 | 714092.6513
765 | 11 kV South Chasara | A793S | 11 | 0 | 00000043 | 1 | 99667000 | 102195272 | 2528272 | 1 | 0 | 2528272 | 2534727.6524 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 2702179.486 | 2680027.0984 | 2791666.2107 | 2659640.365 | 2565218.7341
766 | 11 kV Spare | 0 | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0
767 | 11 kV NCC Express | B7225 | 11 | 0 | 00000019 | 1 | 190279 | 213639 | 23360 | 1 | 0 | 23360 | 23419.6471 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 28768.3897 | 31678.5827 | 33494.5516 | 30069.4219 | 22516.8296
768 | 11 kV Spare | 0 | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0
769 | 11 kV Masuya Bazar | B7229 | 11 | 0 | 00000173 | 1 | 7416422 | 8565979 | 1149557 | 1 | 0 | 1149557 | 1152492.2619 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 1058401.5124 | 1053995.629 | 1019425.3124 | 1009868.8027 | 967617.4501
770 | 11 kV Nitaigonj | B722G | 11 | 0 | 00000189 | 1 | 59588816 | 60384252 | 795436 | 1 | 0 | 795436 | 797467.0545 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 710089.0378 | 797549.9114 | 692971.3447 | 773236.8002 | 671875.6098
771 | 11 kV Shahid Nagar | E323T | 11 | 0 | 00000020 | 1 | 59699656 | 60968412 | 1268756 | 1 | 0 | 1268756 | 1271995.6228 | Sytalakhya | Mondalpara 33/11KV S/S | 22 | 1341667.6936 | 1338376.1519 | 1319788.4916 | 1324869.236 | 1256708.9709
772 | 11 kV Bangla Bazar | A793Z | 11 | 0 | 00000139 | 1 | 72583224 | 74210456 | 1627232 | 1 | 0 | 1627232 | 1631386.9501 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1686165.1422 | 1670015.7997 | 1659253.7348 | 1635218.8108 | 1605498.2865
773 | 11 kV Vogoban Gonj | B7228 | 11 | 0 | 00000181 | 1 | 3295232 | 3768630 | 473398 | 1 | 0 | 473398 | 474606.7675 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 456596.7336 | 480180.888 | 455263.1874 | 451404.0608 | 442440.5963
774 | 11 kV Tanbazar | B722I | 11 | 0 | 00000138 | 1 | 50648356 | 51622392 | 974036 | 1 | 0 | 974036 | 976523.0891 | N.Gonj (East) | Mondalpara 33/11KV S/S | 22 | 1000661.8275 | 1022544.4626 | 983939.833 | 990185.2541 | 977004.8332
775 | 11 kV SS Road | A793O | 11 | 0 | 00000175 | 1 | 68058352 | 69392152 | 1333800 | 1 | 0 | 1333800 | 1337205.7052 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 1396187.0064 | 1386083.0342 | 1389631.5256 | 1367265.5042 | 1304240.0244
776 | 11 kV Spare | 0 | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0
777 | 33/0.415 kV Auxiliary-1 | 0 | 0.415 | 0 | 0 | 1 | 2599.39 | 2640.91 | 41.52 | 100 | 0 | 4152 | 4162.6017 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 6314.1794 | 3653.8216 | 8763.4945 | 8081.1571 | 8402.5235
778 | 33/0.415 kV Auxiliary-2 | 0 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 22 | 0 | 0 | 0 | 0 | 0
779 | 11 kV Masdair Feeder (F-8) | A727M | 11 | 0 | XA575914 | 1 | 219192.9 | 222435 | 3242.1 | 1000 | 0 | 3242100 | 3291294.4584 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 3221867.4125 | 3104675.7264 | 3190609.1379 | 3086175.0273 | 3077099.4263
780 | 11 kV Narayangonj (F-7) | A727N | 11 | 0 | XA575915 | 1 | 168351.2 | 169847.6 | 1496.4 | 1000 | 0 | 1496400 | 1519105.835 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1446695.3457 | 1509012.0982 | 1221622.7778 | 1186514.4598 | 1307443.1804
781 | 11 kV Nearest Feeder (F-6) | A727B | 11 | 0 | XA575927 | 1 | 107456.1 | 108569.7 | 1113.6 | 1000 | 0 | 1113600 | 1130497.3656 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1036613.3317 | 1067352.4897 | 767732.4068 | 814473.5094 | 997748.2737
782 | 11 kV BSCIC-2 Feeder (F-5) | A7272 | 11 | 0 | XA575916 | 1 | 118651.3 | 120037.9 | 1386.6 | 1000 | 0 | 1386600 | 1407639.7693 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1294481.9465 | 1274162.1574 | 1118663.9439 | 1197874.4889 | 1341268.5888
783 | 11 kV Abonti Color Tex. (F-4) | A727A | 11 | 0 | XA575912 | 1 | 56646.1 | 57538.4 | 892.3 | 1000 | 0 | 892300 | 905839.439 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 991802.3648 | 906095.6122 | 696086.8403 | 614760.142 | 701320.2188
784 | 11 kV BSCIC-1 Feeder (F-3) | A7271 | 11 | 0 | DHK66615 | 1 | 228.1138 | 246.1468 | 18.033 | 60000 | 0 | 1081978.68 | 1098396.235 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 953150.2952 | 1090118.5393 | 864699.4622 | 933339.9033 | 1045632.3523
785 | 11 kV Shasongaon Feeder (F-2) | A727S | 11 | 0 | XA575920 | 1 | 233276 | 234533.8 | 1257.8 | 1000 | 0 | 1257800 | 1276885.4045 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 27 | 676995.0442 | 906804.2112 | 982770.4437 | 813154.9346 | 1189560.6195
786 | 11 kV Fakir Apparels Feeder (F-1) | A727F | 11 | 0 | XA575929 | 1 | 22437.4 | 23731.9 | 1294.5 | 1000 | 0 | 1294500 | 1314142.277 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1121815.8354 | 1179007.44 | 1159908.2799 | 1225868.8461 | 1274022.8667
787 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | A727G | 11 | 0 | HA021100913-02 | 1 | 42019.89 | 44435.628 | 2415.738 | 1000 | 0 | 2415738 | 2452393.5389 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1730245.9891 | 1391497.0345 | 582908.1262 | 649651.6597 | 916096.371
788 | 11 kV BSCIC-4 Feeder (F-11) | A7274 | 11 | 0 | HA021100682-02 | 1 | 64204.485 | 66687.61 | 2483.125 | 1000 | 0 | 2483125 | 2520803.045 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 2363695.2567 | 2414952.831 | 1958482.735 | 2197501.257 | 2366722.3025
789 | 11 kV BSCIC-3 Feeder (F-10) | A7273 | 11 | 0 | HA021100455-02 | 1 | 57860.6 | 59670.325 | 1809.725 | 1000 | 0 | 1809725 | 1837185.1157 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 1324011.9627 | 2155990.2798 | 1459919.7827 | 1675803.0813 | 1827353.8856
790 | 11/0.415 KV Transformer,AT-1 | 0 | 0.415 | Analog | 2001123043161 | 1 | 3930.2 | 3995.5 | 65.3 | 160 | 0 | 10448 | 10606.5342 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 9471.9695 | 9523.57 | 9809.4637 | 10077.9686 | 6902.8139
791 | 11/0.415 KV Transformer,AT-2 | 0 | 0.415 | Analog | 2001123043118 | 1 | 4106.3 | 4108.1 | 1.8 | 160 | 0 | 288 | 292.37 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 27 | 213.7771 | 583.0757 | 16.214 | 519.3156 | 421.2985
792 | 11 kV Outgoing Feeder-1 (=F1) | 0 | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
793 | 11 kV Char-Syedpur Feeder(=F2) | E331C | 11 | 0 | 041808902749 | 1 | 446.8 | 468.54 | 21.74 | 60000 | 0 | 1304400 | 1302048.296 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1299547.0336 | 1326519.4669 | 1258154.7044 | 1256317.0074 | 1308593.1901
794 | 11 kV UltraTech Cement Feeder (=F3) | 0 | 11 | 0 | 041808902759 | 1 | 474.87 | 492.75 | 17.88 | 60000 | 0 | 1072800 | 1070865.8478 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1018127.8829 | 1172245.3124 | 1166152.8884 | 1226848.5855 | 1401162.4833
795 | 11 kV Outgoing Feeder-4 (=F4) | 0 | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
796 | 11 kV Outgoing Feeder-5 (=F5) | 0 | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
797 | 11 kV Outgoing Feeder-6 (=F6) | 0 | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
798 | 11 kV Outgoing Feeder-7 (=F7) | 0 | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
799 | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
800 | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
801 | 11 kV Mokterpur Feeder (=F8) | E331M | 11 | 0 | 041808902786 | 1 | 330.24 | 356.76 | 26.52 | 60000 | 0 | 1591200 | 1588331.224 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 1607255.8715 | 1649959.1034 | 1406910.8874 | 1384414.4332 | 1059738.0772
802 | 11 kV Dhaleshwary Feeder (=F9) | E331E | 11 | 0 | 041808902789 | 1 | 201.91 | 215.77 | 13.86 | 60000 | 0 | 831600 | 830100.7076 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 664412.0926 | 761840.3225 | 831600.8302 | 763171.9877 | 845746.7241
803 | 11 kV Outgoing Feeder-12 (=F10) | 0 | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
804 | 11 kV Outgoing Feeder-13 (=F11) | 0 | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
805 | 11 kV Outgoing Feeder-14 (=F12) | 0 | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
806 | 11 kV Outgoing Feeder-15 (=F13) | 0 | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
807 | 11 kV Outgoing Feeder-16 (=F14) | 0 | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
808 | 33/0.415 kV Transformer AT-1 | 0 | 0.415 | 0 | 041811907976 | 1 | 1814.62 | 1916.44 | 101.82 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
809 | 33/0.415 kV Transformer AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 31 | 0 | 0 | 0 | 0 | 0
810 | 11 kV Manikdia Feeder | B9102I | 11 | Mugdapara | HA021100482-02 | 1 | 71472942 | 72083645 | 610703 | 1 | 0 | 610703 | 618877.1744 | Mugdapara | Amulia 33/11 kv | 102 | 747742.2401 | 669679.7315 | 704760.429 | 655997.4572 | 731782.37
811 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0
812 | 11 kV Kayetpara Feeder | E1102KY | 11 | Demra | HA021100967-02 | 1 | 16734017 | 18045139 | 1311122 | 1 | 0 | 1311122 | 1328671.185 | Demra | Amulia 33/11 kv | 102 | 1368274.6157 | 1317757.7287 | 1370677.2015 | 1292488.6152 | 1242034.7233
813 | 11 kV Paity Feeder | E1102I | 11 | Demra | HA021188676-02 | 1 | 1820347 | 2394570 | 574223 | 1 | 0 | 574223 | 581908.8947 | Demra | Amulia 33/11 kv | 102 | 369688.6181 | 572405.5108 | 546070.575 | 498813.9667 | 550647.0061
814 | 11 kV Bamuil Feeder | E1102O | 11 | Demra | HA021100981-02 | 1 | 68779188 | 71254185 | 2474997 | 1 | 0 | 2474997 | 2508124.4895 | Demra | Amulia 33/11 kv | 102 | 2591251.8147 | 2450741.6785 | 2341533.0936 | 2143176.0462 | 2258006.7634
815 | 11 kV Ali Ahmed School Feeder | B9102C | 11 | Mugdapara | HA021101235-02 | 1 | 15389909 | 16052331 | 662422 | 1 | 0 | 662422 | 671288.426 | Mugdapara | Amulia 33/11 kv | 102 | 654683.7051 | 639938.2711 | 588274.3679 | 552448.5186 | 1045691.8176
816 | 11 kV Amulia Model Town Feeder | E1102A | 11 | Demra | 0 | 1 | 51992736 | 52158655 | 165919 | 1 | 0 | 165919 | 168139.8027 | Demra | Amulia 33/11 kv | 102 | 155971.1495 | 189931.2691 | 165276.4 | 158821.9675 | 145542.9861
817 | 11 kV Rajakhali Feeder | E1102R | 11 | Demra | HA021100483-02 | 1 | 13720036 | 15044850 | 1324814 | 1 | 0 | 1324814 | 1342546.4505 | Demra | Amulia 33/11 kv | 102 | 1461872.9578 | 1326521.6668 | 1251754.1184 | 1263380.0786 | 1242709.7581
818 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0
819 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0
820 | 33/0.415 kV Transformer, AT-2 | 0 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 102 | 0 | 0 | 0 | 0 | 0
821 | 11 kV Nearest Feeder | B2110N | 11 | 0 | HA021101060-02 | 1 | 78705271 | 80316933 | 1611662 | 1 | 0 | 1611662 | 1615577.819 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1668539.8072 | 1666551.6834 | 1691601.9901 | 1589546.8433 | 1558145.6337
822 | 11kV Spare | 0 | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
823 | 11 kV City Palli Feeder | B2110C | 11 | 0 | HA021100937-02 | 1 | 79002373 | 79831670 | 829297 | 1 | 0 | 829297 | 831311.9243 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 885994.3441 | 907412.698 | 936164.8797 | 876024.4652 | 849393.0553
824 | 11 kV R K Mission Road Feeder | B2110R | 11 | 0 | HA021101035-02 | 1 | 17311553 | 18813697 | 1502144 | 1 | 0 | 1502144 | 1505793.7255 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1587170.4652 | 1556832.94 | 1647566.9154 | 1564049.4804 | 1502639.6704
825 | 11 kV Janapath Feeder | B2110J | 11 | 0 | HA021100864-02 | 1 | 31862091 | 33876168 | 2014077 | 1 | 0 | 2014077 | 2018970.5577 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 2145298.3795 | 2127410.4471 | 2194112.6593 | 2093083.5306 | 2005205.5254
826 | 11 kV Dhalpur Feeder | B2110D | 11 | 0 | HA021100851-02 | 1 | 87890591 | 88732684 | 842093 | 1 | 0 | 842093 | 844139.0145 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 879803.8192 | 873504.546 | 859344.4269 | 844664.2379 | 860069.6023
827 | 11kV WTP | B2110O | 11 | 0 | X0599387 | 1 | 2253.4 | 2253.4 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 285986.2262 | 561982.597 | 0 | 0 | 145877.5724
828 | 11kV Kamalapur Water pumping | B2110F | 11 | 0 | HA021100474-02 | 1 | 7640348 | 7657094 | 16746 | 1 | Estimated | 97306.272 | 97542.6949 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 82536.7668 | 73055.4392 | 36822.7275 | 20221.1849 | 24456.8935
829 | 11 kV Wasa Road Feeder | B2110A | 11 | 0 | HA021001011-02 | 1 | 25404116 | 26301986 | 897870 | 1 | Estimated | 2067758.28 | 2072782.2659 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 2063419.1707 | 2142959.5506 | 2098895.465 | 1863737.1947 | 2040994.3579
830 | 11kV Sutikhalpar Feeder | B2110K | 11 | 0 | HA021101047-02 | 1 | 79911027 | 80885566 | 974539 | 1 | Estimated | 1885309.02 | 1889889.713 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 1886554.6703 | 2069904.1114 | 2025250.0101 | 1882771.0147 | 2076315.0532
831 | 11kV Spare | 0 | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
832 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
833 | 11kV Spare | 0 | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
834 | 11kV Spare | 0 | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
835 | 11kV Spare | 0 | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
836 | AT-1 | 0 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 110 | 0 | 0 | 0 | 0 | 0
837 | 11kV Fakirapul Panir Tank Feeder | A174Y | 11 | 0 | DHK86058 | 1 | 1731.8 | 1749.51 | 17.71 | 60000 | 0 | 1062600 | 1078290.2684 | Motijheel | Motijheel old 33/11 kV | 75 | 1069121.0153 | 1083441.1947 | 1084055.9235 | 997541.2473 | 913140.3988
838 | 11kV Station Road Feeder | A175H | 11 | 0 | DHK86075 | 1 | 2379.78 | 2381.38 | 1.6 | 60000 | 0 | 96000 | 97417.5285 | Motijheel | Motijheel old 33/11 kV | 75 | 97902.6548 | 101497.5399 | 109816.6442 | 95033.1244 | 121832.4707
839 | 11kV Box Culvert Road Feeder | A175F | 11 | 0 | DHK86071 | 1 | 3219.65 | 3251.61 | 31.96 | 60000 | 0 | 1917600 | 1945915.1314 | Motijheel | Motijheel old 33/11 kV | 75 | 1920213.4191 | 1954278.0752 | 1833753.908 | 1479451.1554 | 1996966.8828
840 | 11kV Mohamedan Club Feeder | A174V | 11 | 0 | DHK86062 | 1 | 1707.66 | 1722.37 | 14.71 | 60000 | 0 | 882600 | 895632.4025 | Motijheel | Motijheel old 33/11 kV | 75 | 840281.0677 | 917081.3217 | 976079.7817 | 1139171.2585 | 731597.9549
841 | 11kV Amina Ahmed Co. | 0 | 11 | 0 | DHK95754 | 1 | 115650 | 119456 | 3806 | 60 | 0 | 228360 | 231731.9459 | Motijheel | Motijheel old 33/11 kV | 75 | 212983.3214 | 238309.0167 | 251289.93 | 373020.341 | 139323.2709
842 | 11kV Bangabhaban -1 | 0 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0
843 | 11kV Sonali Bank | A175SB | 11 | 0 | DHK95753 | 1 | 76280 | 84919 | 8639 | 60 | 0 | 518340 | 525993.7678 | Motijheel | Motijheel old 33/11 kV | 75 | 476719.8595 | 524063.6289 | 553807.1772 | 446839.6196 | 345775.0268
844 | 11kV NCC Bank Feeder | A133S | 11 | 0 | DHK68123 | 1 | 327.89 | 331.8 | 3.91 | 60000 | 0 | 234600 | 238064.0852 | Motijheel | Motijheel old 33/11 kV | 75 | 224635.5392 | 249239.521 | 237424.8118 | 404044.0578 | 147163.9744
845 | 11kV IFIC BANK Feeder | 0 | 11 | 0 | DHK68116 | 1 | 412.05 | 419.59 | 7.54 | 60000 | 0 | 452400 | 459080.103 | Ramna | Motijheel old 33/11 kV | 75 | 425846.5168 | 457039.218 | 500616.6574 | 354381.5863 | 554880.5594
846 | 11kV Arambagh Feeder | A174X | 11 | 0 | DHK68117 | 1 | 3414.8 | 3437.26 | 22.46 | 60000 | 0 | 1347600 | 1367498.5561 | Motijheel | Motijheel old 33/11 kV | 75 | 1397665.5071 | 1278373.3459 | 1267688.622 | 59250.2714 | 488536.1447
847 | 11kV Nikotborti Feeder | A175K | 11 | 0 | DHK68114 | 1 | 1435.2 | 1439.72 | 4.52 | 60000 | 0 | 271200 | 275204.518 | Motijheel | Motijheel old 33/11 kV | 75 | 264277.1049 | 302690.8881 | 931907.7237 | 862042.4055 | 655000.3125
848 | 11kV Agrani Bank Feeder | A174O | 11 | 0 | DHK95756 | 1 | 374973 | 378789 | 3816 | 60 | 0 | 228960 | 232340.8054 | Motijheel | Motijheel old 33/11 kV | 75 | 213403.7622 | 236867.6315 | 255891.186 | 369219.0161 | 144691.1372
849 | 11kV Bangladesh Bank-2 | A133D | 11 | 0 | DHK95755 | 1 | 529 | 546 | 17 | 60000 | Estimated | 973062.72 | 987430.8879 | Motijheel | Motijheel old 33/11 kV | 75 | 706996.5136 | 913123.8185 | 781881.091 | 669891.5592 | 180939.3128
850 | 11kV PDB Design Feeder 14 | 0 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0
851 | 11kV Bangabhaban-2 | 0 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 0 | 0 | 0 | 0 | 0
852 | 11/0.4 kV AT | 0 | 0.415 | 0 | ELIC5429 | 1 | 422280 | 422280 | 0 | 1 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 75 | 5453.7184 | 4994.8 | 6386.5434 | 8270.9474 | 3518.2644
853 | 11 kV Central Weman | A1111CW | 11 | 0 | 41812909492 | 1 | 166.18 | 179.49 | 13.31 | 60000 | 0 | 798600 | 780631.0755 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 589767.3774 | 585552.4072 | 614594.3851 | 602582.0913 | 559727.7485
854 | 11 kV Spare Feeder 2 | 0 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
855 | 11 kV K. M. Das Len | 0 | 11 | 0 | 41812909499 | 1 | 282.85 | 297.27 | 14.42 | 60000 | 0 | 865200 | 845732.5401 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 957285.5746 | 992186.0233 | 1031748.0667 | 1006914.6746 | 933883.7569
856 | 11 kV Gopibag | A1111GP | 11 | 0 | 41812909517 | 1 | 42.2 | 44.79 | 2.59 | 60000 | 0 | 155400 | 151903.4174 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 162651.6346 | 159641.3456 | 169750.8488 | 161492.0005 | 148216.3898
857 | 11kV SPICE TV | B1111E | 11 | 0 | 41812909518 | 1 | 22.22 | 26.14 | 3.92 | 60000 | 0 | 235200 | 229907.875 | Narinda | Motijheel 33/11 KV SS (new) | 111 | 224111.6034 | 223497.8838 | 229344.2319 | 216326.9708 | 196416.8418
858 | 11 kV Spare Feeder 6 | 0 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
859 | 11 kV Spare Feeder 7 | 0 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
860 | 11 kV BPT-1 | 0 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
861 | 11 kV BPT-2 | 0 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
862 | 10 kV Spare Feeder 8 | 0 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
863 | 11 kV Spare Feeder 9 | 0 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
864 | 11 kV South Kamlapur | A1111SK | 11 | 0 | 41812909473 | 1 | 395.68 | 406.2 | 10.52 | 60000 | 0 | 631200 | 616997.6645 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 555002.1425 | 559648.3398 | 571253.7429 | 550760.0315 | 1048359.8303
865 | 11 kV Spare Feeder 11 | 0 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 111 | 0 | 0 | 0 | 0 | 0
866 | 11 kV Answer Camp | A1111AC | 11 | 0 | 41812909514 | 1 | 203.83 | 215.83 | 12 | 60000 | 0 | 720000 | 703799.6173 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 759868.7052 | 750615.5343 | 784345.2339 | 758048.2709 | 729031.836
867 | 11 kV Shapla Chattar | A1111SC | 11 | 0 | 41812909516 | 1 | 175.12 | 194.83 | 19.71 | 60000 | 0 | 1182600 | 1155990.8714 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 1143527.9043 | 1182550.7976 | 639274.4731 | 598966.5988 | 591058.0422
868 | 11 kV Sayedabad | 0 | 11 | 0 | 41812909497 | 1 | 105.04 | 110.21 | 5.17 | 60000 | 0 | 310200 | 303220.3351 | Swamibag | Motijheel 33/11 KV SS (new) | 111 | 309783.0751 | 311451.2289 | 306394.2625 | 315753.0159 | 300047.8135
869 | 33/0.4 kV Aux Transformer | 0 | 0.415 | 0 | 41901920686 | 1 | 1297.07 | 1382.5 | 85.43 | 1 | 0 | 85.43 | 83.5078 | Motijheel | Motijheel 33/11 KV SS (new) | 111 | 86.4785 | 0 | 0 | 0 | 0
870 | Inner Circular Road Feeder | A161Z | 11 | 0 | BD014042 | 1 | 41532 | 42241 | 709 | 1000 | 0 | 709000 | 717359.185 | Motijheel | P & T 33/11 KV SS | 61 | 740621.6003 | 751211.0308 | 786225.5313 | 2044037.2926 | 2028898.6132
871 | NSI New Building Expres Feeder | D361NS | 11 | 0 | BD013982 | 1 | 10393 | 10797 | 404 | 1000 | 0 | 404000 | 408763.2027 | Ramna | P & T 33/11 KV SS | 61 | 366793.6012 | 408464.6789 | 417588.6558 | 429529.4901 | 413128.6457
872 | Police Hospital RMU Feeder | D661H | 11 | 0 | BD014044 | 1 | 3761 | 3920 | 159 | 1000 | 0 | 159000 | 160874.6268 | Rajarbag | P & T 33/11 KV SS | 61 | 178874.6877 | 184011.3157 | 189813.0254 | 182072.2195 | 167833.5123
873 | Jonaki O/H Feeder | D661J | 11 | 0 | BD014013 | 1 | 35526 | 36961 | 1435 | 1000 | 0 | 1435000 | 1451918.8017 | Rajarbag | P & T 33/11 KV SS | 61 | 1556611.7488 | 1494333.6521 | 1501520.9321 | 1581312.3149 | 1420129.7195
874 | Nayapalton Overhead Feeder | D361N | 11 | 0 | BD014014 | 1 | 25646 | 26556 | 910 | 1000 | 0 | 910000 | 920728.9962 | Ramna | P & T 33/11 KV SS | 61 | 1002904.148 | 1013073.2878 | 1003011.9866 | 1008941.636 | 976215.0449
875 | Masjid Gali Over Head Feeder | D361MG | 11 | 0 | BD014016 | 1 | 15482 | 16316 | 834 | 1000 | 0 | 834000 | 843832.9482 | Ramna | P & T 33/11 KV SS | 61 | 902412.7504 | 918034.4764 | 899114.3306 | 924444.0314 | 878891.4697
876 | Spare Feeder (Feeder-8) | 0 | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 61 | 0 | 0 | 0 | 0 | 0
877 | Mid Way Over Head Feeder | D361MW | 11 | 0 | BD014015 | 1 | 23839 | 24754 | 915 | 1000 | 0 | 915000 | 925787.9468 | Ramna | P & T 33/11 KV SS | 61 | 990845.1803 | 982741.7522 | 1022992.3051 | 1000894.2451 | 972242.6541
878 | Palton Thana Over Head Feeder | D661F | 11 | 0 | BD014033 | 1 | 25001 | 26289 | 1288 | 1000 | 0 | 1288000 | 1303185.6562 | Rajarbag | P & T 33/11 KV SS | 61 | 1382761.6309 | 1360874.8956 | 1387633.1169 | 1346932.0545 | 1294006.3108
879 | Police Hospital (South) U/G Feeder 7 | 0 | 11 | 0 | BD014034 | 1 | 12571 | 12743 | 172 | 1000 | 0 | 172000 | 174027.8982 | Rajarbag | P & T 33/11 KV SS | 61 | 183899.2576 | 186033.4181 | 181820.898 | 172012.9808 | 167833.5123
880 | China Town Express Feeder | D361CT | 11 | 0 | BD013943 | 1 | 6660 | 6925 | 265 | 1000 | 0 | 265000 | 268124.378 | Ramna | P & T 33/11 KV SS | 61 | 282380.8272 | 287138.5367 | 264739.2196 | 295741.6161 | 284025.9439
881 | Fakirapul Bazar O/H Feeder | A161FB | 11 | 0 | BD014032 | 1 | 30742 | 32179 | 1437 | 1000 | 0 | 1437000 | 1453942.382 | Motijheel | P & T 33/11 KV SS | 61 | 1464159.663 | 1476134.7307 | 1280738.4132 | 1354979.4454 | 1402253.9607
882 | PWD Ouarter (RMU) | A161PW | 11 | 0 | BD013937 | 1 | 2467 | 2615 | 148 | 1000 | 0 | 148000 | 149744.9357 | Motijheel | P & T 33/11 KV SS | 61 | 156766.5803 | 149635.5754 | 151850.4203 | 150888.5797 | 145985.3628
883 | Postal Quarter RMU | A161PO | 11 | 0 | BD013945 | 1 | 3035 | 3209 | 174 | 1000 | 0 | 174000 | 176051.4784 | Motijheel | P & T 33/11 KV SS | 61 | 181889.4296 | 177945.0086 | 177824.8343 | 174024.8285 | 164854.2192
884 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | DHKH4409 | 1 | 1476 | 1476 | 0 | 100 | 0 | 0 | 0 | Rajarbag | P & T 33/11 KV SS | 61 | 4220.6387 | 5762.9918 | 6093.9971 | 301.7772 | 0
885 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | DHKH4411 | 1 | 522 | 578 | 56 | 100 | 0 | 5600 | 5666.0246 | Rajarbag | P & T 33/11 KV SS | 61 | 1406.8796 | 0 | 5394.686 | 0 | 5362.7276
886 | Amtola O/H Feeder | D6106A | 11 | Rajarbag | 112 | 1 | 430.5 | 452 | 21.5 | 40000 | 0 | 860000 | 873041.3399 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 948762.3589 | 895110.6473 | 1426015.7648 | 1381038.2208 | 1302977.567
887 | Police Telecom | D6106O | 11 | Rajarbag | 130 | 1 | 74 | 78.6 | 4.6 | 40000 | 0 | 184000 | 186790.2402 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 199525.1313 | 209665.557 | 202559.0575 | 214648.1692 | 201076.785
888 | Railway Colony O/H | D6106I | 11 | Rajarbag | 177 | 1 | 305 | 324.1 | 19.1 | 40000 | 0 | 764000 | 775585.5625 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 851035.764 | 818502.0784 | 866952.7661 | 866692.6078 | 735941.0332
889 | Shahjahanpur O/H Feeder | D6106P | 11 | Rajarbag | 12 | 1 | 738.6 | 768.6 | 30 | 40000 | 0 | 1200000 | 1218197.2185 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 1388532.036 | 1274121.462 | 2264610.2629 | 2211281.1394 | 2079133.9572
890 | 11 KV Majar Feeder | 0 | 11 | 0 | 96 | 1 | 62 | 71.1 | 9.1 | 40000 | 0 | 364000 | 369519.8229 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 407194.1454 | 391106.9045 | 417271.6585 | 400946.5802 | 382045.8916
891 | 11 kV Feeder-6 | 0 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0
892 | Momenbagh O/H | D6106V | 11 | Rajarbag | 107 | 1 | 343.4 | 355.6 | 12.2 | 40000 | 0 | 488000 | 495400.2022 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 517136.5647 | 483843.5932 | 563114.1799 | 1081340.777 | 1001362.3894
893 | 11 kV Feeder-8 | 0 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0
894 | 11 kV Uttara Bank Goli Feeder-9 | D6106T | 11 | Rajarbag | 169 | 1 | 224.2 | 232.7 | 8.5 | 40000 | 0 | 340000 | 345155.8786 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 354258.9065 | 330626.4553 | 352452.7601 | 340197.0984 | 337808.9988
895 | 11 kV Baraka O/H Feeder-10 | D6106K | 11 | Rajarbag | 49 | 1 | 330.7 | 363.8 | 33.1 | 40000 | 0 | 1324000 | 1344077.5978 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 2296574.9803 | 2165200.0794 | 449681.1077 | 437396.2693 | 402153.5701
896 | 11 kV Feeder-11 | 0 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0
897 | Dhaka Railway | 0 | 11 | Motijheel | 150 | 1 | 69.3 | 71.8 | 2.5 | 40000 | 0 | 100000 | 101516.4349 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 199525.1313 | 209665.557 | 230917.3256 | 222748.1001 | 217162.9278
898 | Jasimuddin Feeder-13 | 0 | 11 | 0 | 91 | 1 | 234.5 | 270.1 | 35.6 | 40000 | 0 | 1424000 | 1445594.0326 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 1653208.2305 | 1568459.6478 | 1713649.6265 | 1656435.8718 | 1097879.2463
899 | Police Box Feeder-14 | 0 | 11 | 0 | 18 | 1 | 100.7 | 115.6 | 14.9 | 40000 | 0 | 596000 | 605037.9519 | Motijheel | Kamalapur Railway 33/11 KV SS | 106 | 655582.5742 | 628996.6711 | 656291.3463 | 664194.3349 | 643445.7121
900 | 11 kV Feeder-15 | 0 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0
901 | 11 kV Feeder-16 | 0 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 106 | 0 | 0 | 0 | 0 | 0
902 | Auxiliary -1 (AT-1 ) | 0 | 0.415 | 0 | DHKF 7632 | 1 | 948.92 | 1018.7 | 69.78 | 100 | 0 | 6978 | 7083.8168 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 0 | 4701.3469 | 8715.1034 | 2871.4255 | 5128.4634
903 | Auxiliary -1 (AT-2 ) | 0 | 0.415 | 0 | DHKF 7733 | 1 | 137.5 | 156.6 | 19.1 | 100 | 0 | 1910 | 1938.9639 | Rajarbag | Kamalapur Railway 33/11 KV SS | 106 | 1823.2118 | 0 | 0 | 0 | 0
904 | 11 kV DIT S/S-1 Feeder | 0 | 11 | Motijheel | 4150750 | 1 | 217443.1 | 218543.72 | 1100.62 | 1000 | Estimated | 729797.04 | 730932.291 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 825621.5358 | 884099.9496 | 816951.1322 | 793502.3098 | 860468.6016
905 | 11 kV Bangabhaban Switching Circuit-1 | 0 | 11 | Motijheel | 4150743 | 1 | 24265.4 | 24310.71 | 45.31 | 1000 | 0 | 45310 | 45380.4829 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 61964.371 | 72049.9558 | 82523.1488 | 83389.7606 | 79020.0597
906 | 11 kV Saidabad Water Treatment | B233T | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0
907 | 11 kV Bangladesh Bank Feeder | 0 | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 240728.715
908 | 11 kV P & T Substation | 0 | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0
909 | 11 kV Osmani Feeder | 0 | 11 | Ramna | 4150754 | 1 | 33881.92 | 33902.7 | 20.78 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 20212.3186
910 | 11 kV Modhumita via Ovisar | A133J | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 668980.62 | 670021.2667 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 766648.569 | 798145.7878 | 731598.0289 | 710599.0834 | 737544.5157
911 | 11 kV Sugar Bhaban & Car Parking | A133B | 11 | Motijheel | 4150753 | 1 | 15953.16 | 16026.75 | 73.59 | 1000 | 0 | 73590 | 73704.4745 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 67064.6079 | 76956.258 | 79365.3753 | 70158.8804 | 76837.1293
912 | 11 kV Motijheel-1 Feeder | 0 | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0
913 | 11 kV Navana O/H Feeder | A133W | 11 | Motijheel | 4150752 | 1 | 248922.27 | 250080.37 | 1158.1 | 1000 | 0 | 1158100 | 1159901.5065 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 1104426.7361 | 1181560.7231 | 1155594.7497 | 1181422.0182 | 1217478.907
914 | 11 kV Bangabhaban Switching Circuit-2 | 0 | 11 | Motijheel | 4150737 | 1 | 14821.23 | 14984.45 | 163.22 | 1000 | 0 | 163220 | 163473.9003 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 173027.2895 | 175243.8256 | 162199.2891 | 174416.2041 | 171420.6744
915 | 11 kV Motijheel-2 Feeder | 0 | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 0 | 0 | 0 | 0
916 | 11 kV WAPDA building RMU Feeder | A133T | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
917 | 11 kV PDB Design Feeder | A133I | 11 | Motijheel | 4150747 | 1 | 164465.14 | 164831.63 | 366.49 | 1000 | 0 | 366490 | 367060.1011 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 339501.426 | 365711.3213 | 363925.8833 | 326878.2024 | 270087.1078
918 | 11 kV BB Hospital Zone RMU Feeder | A133M | 11 | Motijheel | 4150739 | 1 | 20709.49 | 20763.9 | 54.41 | 1000 | Estimated | 182449.26 | 182733.0727 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 235891.8674 | 282420.8172 | 243866.0096 | 236866.3611 | 245848.1719
919 | 11 kV Sonali Bank RMU Feeder | A133C | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
920 | 11 kV Janata Bank Feeder | A133E | 11 | Motijheel | 4150755 | 1 | 123520.52 | 123820.22 | 299.7 | 1000 | 0 | 299700 | 300166.2046 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 298839.8125 | 325451.3768 | 302665.0764 | 348419.8864 | 313139.3465
921 | 11 kV DIT S/S RMU Feeder | A133R | 11 | Motijheel | 4150740 | 1 | 273191.92 | 273191.92 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 0 | 98812.5217 | 790606.2505 | 819439.2218 | 796304.7174
922 | 11 kV Sena Kalyan Feeder | A133N | 11 | Motijheel | 4150745 | 1 | 81705.33 | 81979.59 | 274.26 | 1000 | 0 | 274260 | 274686.6308 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 474442.2708 | 529113.3929 | 587426.078 | 481785.1466 | 474463.9677
923 | 11 kV BCIC Feeder | A133Q | 11 | Motijheel | 4150756 | 1 | 192767.86 | 192879.03 | 111.17 | 1000 | Estimated | 243265.68 | 243644.097 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 294864.8342 | 368374.979 | 341412.4135 | 331612.9056 | 368772.2578
924 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 63412931 | 1 | 78910 | 78910 | 0 | 1 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 5939.9222 | 6215.6589 | 3575.8026 | 0 | 0
925 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 63403117 | 1 | 22885.4 | 22885.4 | 0 | 1 | Estimated | 5000 | 5007.7779 | Motijheel | Bangabhaban 132/11KV S/S | 33 | 5010.0559 | 5047.636 | 5012.339 | 5030.7529 | 5053.0797
926 | 11 kV Bonogram Feeder | B124B | 11 | 0 | 06604467 | 1 | 25025.97 | 25159.72 | 133.75 | 8000 | 0 | 1070000 | 1081937.7982 | Narinda | Narinda 33/11KV S/S | 24 | 1068648.5129 | 1111412.0708 | 1143423.9412 | 1139801.4532 | 1096395.2732
927 | 11 kV Sha Saheb Len Feeder | B524H | 11 | 0 | 06604469 | 1 | 16887.94 | 16969.66 | 81.72 | 8000 | 0 | 653760 | 661053.8831 | Swamibag | Narinda 33/11KV S/S | 24 | 660371.6402 | 659718.6519 | 672430.175 | 685656.1379 | 629657.0471
928 | 11 kV Sadiabad Water Treatment | B224W | 11 | 0 | 06604354 | 1 | 510.35 | 530.01 | 19.66 | 40000 | 0 | 786400 | 795173.7239 | Maniknagar | Narinda 33/11KV S/S | 24 | 352381.8247 | 28757.3823 | 552771.4205 | 653217.1868 | 492385.8425
929 | 11 kV Manashi Feeder | B124M | 11 | 0 | 06604353 | 1 | 5586.07 | 5614.2 | 28.13 | 40000 | 0 | 1125200 | 1137753.6547 | Narinda | Narinda 33/11KV S/S | 24 | 1160429.802 | 1160826.1643 | 1102291.2443 | 1122855.7324 | 1066634.3599
930 | 11 kV Jatrabari Feeder | B524E | 11 | 0 | 06604324 | 1 | 3530.9 | 3581.5 | 50.6 | 40000 |  | 2024000 | 2046581.4052 | Swamibag | Narinda 33/11KV S/S | 24 | 2127657.1553 | 2119945.619 | 2124511.9226 | 2030258.73 | 1913892.8816
931 | 11 kV Wari Feeder | B124W | 11 | 0 | 06604291 | 1 | 8641.1 | 8679.86 | 38.76 | 40000 | 0 | 1550400 | 1567697.5349 | Narinda | Narinda 33/11KV S/S | 24 | 1678876.6245 | 1616488.912 | 1686359.282 | 1652611.2397 | 1532808.0158
932 | 11 kV Narinda Feeder | B124N | 11 | 0 | 06604348 | 1 | 7378.81 | 7414.52 | 35.71 | 40000 | 0 | 1428400 | 1444336.4028 | Narinda | Narinda 33/11KV S/S | 24 | 1555745.5042 | 1546013.0737 | 1594908.1278 | 1590073.4608 | 1585232.3889
933 | 11 kV Distillary Feeder | B524D | 11 | 0 | 06604347 | 1 | 6064.21 | 6095.73 | 31.52 | 40000 | 0 | 1260800 | 1274866.5196 | Swamibag | Narinda 33/11KV S/S | 24 | 1339455.9704 | 1343496.2969 | 1318115.968 | 1326607.8506 | 1271895.9437
934 | 11 kV Thatari Bazar Feeder | B124T | 11 | 0 | 06604296 | 1 | 5085.7 | 5110.49 | 24.79 | 40000 | 0 | 991600 | 1002663.1035 | Narinda | Narinda 33/11KV S/S | 24 | 1062005.913 | 1059567.7759 | 1097413.8494 | 1083315.7174 | 1015016.5156
935 | 11 kV Swamibagh Feeder | B524C | 11 | 0 | 06604352 | 1 | 7861.81 | 7894.28 | 32.47 | 40000 | 0 | 1298800 | 1313290.4788 | Swamibag | Narinda 33/11KV S/S | 24 | 1313533.6293 | 1354837.2364 | 1370141.5135 | 1100261.4381 | 886375.1694
936 | 11 kV Tipu Sultan Feeder | B124S | 11 | 0 | 06604322 | 1 | 6432.11 | 6459.68 | 27.57 | 40000 | 0 | 1102800 | 1115103.7419 | Narinda | Narinda 33/11KV S/S | 24 | 1147873.668 | 1151915.4261 | 1136839.4581 | 1115189.8112 | 1101315.099
937 | 11 kV Spare | 0 | 11 | 0 | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0
938 | 11 kV Folder Street Feeder | B124F | 11 | 0 | DHK00089 | 1 | 37642.3 | 41171.3 | 3529 | 444.44 | 0 | 1568428.76 | 1585927.4386 | Narinda | Narinda 33/11KV S/S | 24 | 1742899.9791 | 1675427.0415 | 1798340.7365 | 1748933.3106 | 1624153.5662
939 | 11 kV Bhajohari Feeder | B124V | 11 | 0 | DHK27842 | 1 | 414466 | 424175 | 9709 | 80 | 0 | 776720 | 785385.7258 | Narinda | Narinda 33/11KV S/S | 24 | 835023.4135 | 806745.8319 | 813305.5973 | 819688.7194 | 775800.0686
940 | 11 kV Lal mohon shaha Feeder | B124L | 11 | 0 | DHK00086 | 1 | 39197.2 | 41548.8 | 2351.6 | 444.44 | 0 | 1045145.104 | 1056805.6006 | Narinda | Narinda 33/11KV S/S | 24 | 1090752.6026 | 1096369.8618 | 1097222.2328 | 1092539.7614 | 1048880.237
941 | 11 kV Dupkhola Feeder | B524A | 11 | 0 | 8838024/8838029 | 1 | 37971.7 | 38567.6 | 595.9 | 1000 | 0 | 595900 | 602548.3495 | Swamibag | Narinda 33/11KV S/S | 24 | 612719.0865 | 555706.0354 | 579800.3171 | 568589.4506 | 537047.3757
942 | 11/0.4 kV Aux Transformer-1 | 0 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0
943 | 11/0.4 kV Aux Transformer-2 | 0 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 24 | 0 | 0 | 0 | 0 | 0
944 | 11kV Babubazar Feeder | A619B | 11 | Banglabazar | DHK00004 | 1 | 63208 | 63497.4 | 289.4 | 2222.22 | 0 | 643110.468 | 648124.404 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 633672.3537 | 653524.1946 | 604954.0102 | 476949.7245 | 555416.4351
945 | 11kV Islampur Feeder | A619I | 11 | Banglabazar | 06604381 | 1 | 4655.85 | 4688.31 | 32.46 | 40000 | 0 | 1298400 | 1308522.8246 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1300047.3482 | 1372334.5518 | 1164609.944 | 1430849.1736 | 1481110.4937
946 | 11kV Champatully Feeder | B619C | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0
947 | 11kV Majar O/H Feeder | A619M | 11 | Banglabazar | 06604385 | 1 | 5168.65 | 5181.29 | 12.64 | 40000 | 0 | 505600 | 509541.8516 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 496023.0204 | 523045.3096 | 442936.2442 | 536568.4401 | 493703.4979
948 | 11kV Spare | 0 | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0
949 | 11kV Sadarghat Feeder | A619S | 11 | Banglabazar | 06604315 | 1 | 5499.06 | 5527.79 | 28.73 | 40000 | 0 | 1149200 | 1158159.6042 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1128130.2786 | 1172692.7423 | 878663.7611 | 1216221.7976 | 1419397.5564
950 | 11kV Mitford Hospital Feeder | B619M | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 40077.0255 | 0
951 | 11kV Zindabahar Feeder | A619Z | 11 | Banglabazar | 06604405 | 1 | 4141.09 | 4169.95 | 28.86 | 40000 | 0 | 1154400 | 1163400.1454 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1221939.8271 | 1252630.6213 | 1111745.9438 | 834662.018 | 740555.2468
952 | 11kV Police fari Feeder | A619K | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1070368.992 | 1078713.9994 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1184790.4407 | 1110503.0608 | 1217802.7423 | 1144679.3389 | 925694.0585
953 | 11kV Patuatully Feeder | A619P | 11 | Banglabazar | 06604383 | 1 | 5956.75 | 5983.44 | 26.69 | 40000 | 0 | 1067600 | 1075923.4193 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 1095518.3755 | 1129680.4826 | 931127.2764 | 1021492.1651 | 1019206.2302
954 | 11kV Laxmibazar Feeder | A619L | 11 | Banglabazar | 06604407 | 1 | 8287.89 | 8334.99 | 47.1 | 40000 | 0 | 1884000 | 1898688.3869 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 2041666.1823 | 1567512.8248 | 2037666.9172 | 1989498.8221 | 1947085.7372
955 | 11kV Jhonson Road Feeder | A619J | 11 | Banglabazar | 06604384 | 1 | 3780.65 | 3791.32 | 10.67 | 40000 | 0 | 426800 | 430127.4966 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 443280.3129 | 472729.0813 | 450545.4563 | 410865.9482 | 427409.0643
956 | 11kV Dholaikhal Feeder | A619D | 11 | Banglabazar | 06604379 | 1 | 7270.69 | 7301.75 | 31.06 | 40000 | 0 | 1242400 | 1252086.2271 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 586209.0241 | 1209618.3616 | 1050071.2769 | 1251993.0269 | 1073805.1079
957 | 11kV Bikrompur Garden City Feeder | A619G | 11 | Banglabazar | 06604406 | 1 | 3600.06 | 3606.94 | 6.88 | 40000 | 0 | 275200 | 277345.5648 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 287870.5029 | 292158.7455 | 264720.4859 | 275126.2119 | 281286.3072
958 | 11/0.4 kV AT-1 | 0 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 0 | 0 | 0 | 0 | 0
959 | 11/0.4 kV AT-2 | 0 | 0.415 | 0 | 05378636 | 1 | 173865.2 | 176640.6 | 2775.4 | 2 | 0 | 5550.8 | 5594.0762 | Banglabazar | Kumertuly 33/11KV S/S | 19 | 5930.3337 | 4006.0239 | 7168.6788 | 4775.6076 | 4915.4072
960 | 11 kV Bangladesh Math Feeder | B677B | 11 | Bangshal | 340180017728 | 1 | 39891564 | 40639116 | 747552 | 1 | 0 | 747552 | 748100.1808 | Bangshal | Banshal 33/11KV S/S | 78 | 769760.338 | 773303.2759 | 760951.1172 | 778854.3109 | 716311.3918
961 | 11 kV Spare Feeder | 0 | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0
962 | 11 kV Siddikbazar Feeder | 0 | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0
963 | 11 kV Tatibazar feeder | A619T | 11 | Banglabazar | 340180016042 | 1 | 52546725 | 53863751 | 1317026 | 1 | 0 | 1317026 | 1317991.7768 | Banglabazar | Banshal 33/11KV S/S | 78 | 1424094.0148 | 1411190.2742 | 1426877.2604 | 1429747.5487 | 1353751.6158
964 | 11 kV Bangsal Road Feeder | B678L | 11 | Bangshal | 340180015747 | 1 | 22130205 | 22867036 | 736831 | 1 | 0 | 736831 | 737371.3191 | Bangshal | Banshal 33/11KV S/S | 78 | 742977.1081 | 744097.7084 | 751903.1259 | 737930.5287 | 715455.6721
965 | 11 kV Hazi Osman Gani Feeder | B678H | 11 | Bangshal | 340180012709 | 1 | 49587871 | 51129746 | 1541875 | 1 | 0 | 1541875 | 1543005.6588 | Bangshal | Banshal 33/11KV S/S | 78 | 1634853.1578 | 1636226.6255 | 1167271.1296 | 1660584.0104 | 1409457.3709
966 | 11 kV French Road Feeder | B678F | 11 | Bangshal | 340180016889 | 1 | 64655261 | 65782506 | 1127245 | 1 | 0 | 1127245 | 1128071.6101 | Bangshal | Banshal 33/11KV S/S | 78 | 1204002.0348 | 1205928.3277 | 1183358.8995 | 1169829.7548 | 1127796.6211
967 | 11 kV North-South Road Feeder | B678T | 11 | Bangshal | 340180015534 | 1 | 32104912 | 32609799 | 504887 | 1 | 0 | 504887 | 505257.2343 | Bangshal | Banshal 33/11KV S/S | 78 | 581501.911 | 1106821.025 | 1430551.6276 | 1633419.2244 | 1486833.0286
968 | 11 kV Nazirabazar Feeder | B678N | 11 | Bangshal | 340180025261 | 1 | 65935153 | 67416873 | 1481720 | 1 | 0 | 1481720 | 1482806.5471 | Bangshal | Banshal 33/11KV S/S | 78 | 1592214.2158 | 1582391.9071 | 1508639.2033 | 1596892.4609 | 1498407.2378
969 | 11 kV Suritolla Feeder | B177R | 11 | Narinda | 340180025212 | 1 | 52819246 | 54042708 | 1223462 | 1 | 0 | 1223462 | 1224359.1662 | Narinda | Banshal 33/11KV S/S | 78 | 1261180.3015 | 1301441.3762 | 1139549.3681 | 1267199.3373 | 1145519.8164
970 | AT-1 | 0 | 0.415 | 0 | DHK-4415 | 1 | 734.14 | 764.01 | 29.87 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 78 | 0 | 0 | 0 | 0 | 0
971 | AT-2 | 0 | 0.415 | 0 | DHK-4410 | 1 | 764.83 | 771.03 | 6.2 | 100 | 0 | 7000 | 7005.1331 | Bangshal | Banshal 33/11KV S/S | 78 | 7007.3859 | 7008.295 | 7021.7228 | 7023.9917 | 6997.7081
972 | 11 kV Nayanagor Feeder | A418N | 11 | 0 | DHK-61125 | 1 | 904496 | 933689.8 | 29193.8 | 60 | 0 | 1751628 | 1775388.4538 | Kazla | Kazla 33/11KV S/S | 18 | 1866468.623 | 1836553.7788 | 1866699.9643 | 1792344.292 | 1710856.4639
973 | 11 kV Madrasa Bazar Feeder | A418B | 11 | 0 | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1581226.92 | 1602675.9202 | Kazla | Kazla 33/11KV S/S | 18 | 1563148.5482 | 1846586.4161 | 1853855.1196 | 1913492.0332 | 1855425.2355
974 | 11 kV Kazla Feeder | A418K | 11 | 0 | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2675922.48 | 2712220.788 | Kazla | Kazla 33/11KV S/S | 18 | 2825691.6063 | 2954538.2657 | 3027963.362 | 3049627.928 | 2968680.3768
975 | 11 kV Sayedabad Feeder | B218S | 11 | 0 | HA021101239-02 | 1 | 36964646 | 36964648 | 2 | 1000 | Estimated | 1216328.4 | 1232827.6309 | Maniknagar | Kazla 33/11KV S/S | 18 | 1202421.9601 | 1231057.6107 | 988722.7304 | 1076339.2687 | 556627.5706
976 | 11 kV Zenith Feeder | A418Z | 11 | 0 | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0
977 | 11 kV Paterbagh Feeder | B318P | 11 | 0 | HA-021200060 | 1 | 118988.3 | 120971.5 | 1983.2 | 1000 | 0 | 1983200 | 2010101.6778 | Jurain | Kazla 33/11KV S/S | 18 | 2308939.6211 | 2025231.2443 | 2541656.3466 | 2207984.2138 | 2092993.2394
978 | 11 kV Matuail Feeder | A418M | 11 | 0 | HA-021100984 | 1 | 59876429 | 59876429 | 0 | 1 | Estimated | 1824492.6 | 1849241.4463 | Kazla | Kazla 33/11KV S/S | 18 | 1803632.9402 | 1969692.1771 | 1730264.7783 | 1734102.1551 | 1855425.2355
979 | 11 kV Kutubkhali Feeder | B326C | 11 | 0 | DHK-61117 | 1 | 798597.4 | 838596.4 | 39999 | 60 | 0 | 2399940 | 2432494.6655 | Jurain | Kazla 33/11KV S/S | 18 | 2317847.2676 | 2260753.1891 | 2379719.4891 | 2279252.9698 | 2232712.5636
980 | 11 kV Mridhabari Feeder | A418R | 11 | 0 | DHK-61118 | 1 | 674765.1 | 699957.1 | 25192 | 60 | 0 | 1511520 | 1532023.4409 | Kazla | Kazla 33/11KV S/S | 18 | 1493309.739 | 1567790.1074 | 1353302.4526 | 1381440.9902 | 1371332.0993
981 | 11 kV Muslim Nagar Feeder | A418U | 11 | 0 | DHK-61011 | 1 | 111124.4 | 154325.8 | 43201.4 | 60 | 0 | 2592084 | 2627245.0572 | Kazla | Kazla 33/11KV S/S | 18 | 2655800.5175 | 2583205.2246 | 2385633.1534 | 2345596.1288 | 2459477.0573
982 | 11 kV Jatrabari Thana Feeder | A418H | 11 | 0 | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0
983 | 11 kV Mirhazirbag Feeder | B518D | 11 | 0 | DHK-61008 | 1 | 316031.7 | 348875.3 | 32843.6 | 60 | 0 | 1970616 | 1997346.9786 | Swamibag | Kazla 33/11KV S/S | 18 | 2119778.8003 | 2106094.7503 | 2092254.4374 | 2069592.0061 | 1962979.7252
984 | 11 kV Mukti Sharani Feeder | B318T | 11 | 0 | DHK-61014 | 1 | 193957.2 | 213216.9 | 19259.7 | 60 | 0 | 1155582 | 1171257.2192 | Jurain | Kazla 33/11KV S/S | 18 | 2474942.6039 | 2420269.7538 | 2465205.4697 | 2452063.3964 | 2370251.5382
985 | 11 kV Kadamtali Feeder | B418K | 11 | 0 | DHK-61006 | 1 | 415256.6 | 452013.2 | 36756.6 | 60 | 0 | 2205396 | 2235311.7183 | Shyampur | Kazla 33/11KV S/S | 18 | 2567504.4926 | 2822437.563 | 2221373.5062 | 2471771.8805 | 3092469.9692
986 | 11kV Rayerbagh Feeder | E218R | 11 | 0 | DHK-61012 | 1 | 424206.8 | 448270.6 | 24063.8 | 60 | 0 | 1443828 | 1463413.2136 | Matuail | Kazla 33/11KV S/S | 18 | 898785.6229 | 322767.8137 | 1280357.0984 | 1277473.0974 | 837095.6004
987 | 11 kV Donia Feeder | B318D | 11 | 0 | DHK-61013 | 1 | 2047373 | 2084796 | 37423 | 60 | 351948 | 2245380 | 2275838.0926 | Jurain | Kazla 33/11KV S/S | 18 | 2097995.927 | 2006588.1861 | 2090084.0617 | 2017361.1702 | 1952856.964
988 | 11 kV Nimtoli Feeder | A418T | 11 | 0 | HA-021100855-02 | 1 | 32429125 | 34003353 | 1574228 | 1 | 0 | 1574228 | 1595582.0613 | Kazla | Kazla 33/11KV S/S | 18 | 1529815.767 | 1526570.9331 | 1509829.6282 | 1633862.5979 | 1591423.3402
989 | 11 kV Gobindapur Feeder | A441G | 11 | 0 | HA-021101057-02 | 1 | 28077525 | 28747928 | 670403 | 1 | 0 | 670403 | 679496.8713 | Kazla | Kazla 33/11KV S/S | 18 | 715534.2901 | 710807.5855 | 721136.817 | 697773.6086 | 686441.9856
990 | 11 kV Eidgaon (Kabarsthan) Feeder | A418E | 11 | 0 | 9A56136 | 1 | 3626 | 3801 | 175 | 10000 | 0 | 1750000 | 1773738.3704 | Kazla | Kazla 33/11KV S/S | 18 | 1822390.0739 | 1778276.5099 | 1887901.7718 | 1946667.4736 | 1703398.1226
991 | 11 kV Samad Nagar Gate (Old) | A418A | 11 | 0 | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0
992 | 11 kV Dharmik Para | A418D | 11 | 0 | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 23977.7413 | 1140208.9403
993 | 11 kV Sheikhdi Feeder | A418I | 11 | 0 | 9A56133 | 1 | 15959.8 | 16766 | 806.2 | 4000 | 0 | 3224800 | 3268543.7125 | Kazla | Kazla 33/11KV S/S | 18 | 3436798.8591 | 3359798.9198 | 3415699.9979 | 3248780.7482 | 3103743.9224
994 | 11 kV Spare Feeder | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | T-5 Sum | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 0
995 | 11 kV Jenith Feeder | A418Z | 11 | 0 | 61903661 | 1 | 22062 | 22659 | 597 | 2000 | 3898000 | 1194000 | 1210196.351 | Kazla | Kazla 33/11KV S/S | 18 | 1200080.6383 | 617589.258 | 551840.3941 | 574043.3834 | 0
996 | 11 KV Samad Nagor Gate | A418A | 11 | 0 | 61903675 | 1 | 19029 | 19683 | 654 | 2000 | 0 | 1308000 | 1325742.7363 | Kazla | Kazla 33/11KV S/S | 18 | 1296103.4337 | 1368574.557 | 1134163.594 | 1293375.6231 | 1288887.6302
997 | 11 KV Bibir Bagicha | B218I | 11 | 0 | 61903557 | 1 | 37768 | 38466 | 698 | 2000 | 0 | 1396000 | 1414936.4372 | Maniknagar | Kazla 33/11KV S/S | 18 | 1478955.3526 | 1458247.4647 | 1460126.3972 | 1445370.1189 | 1356006.601
998 | 33/0.4 kV AT-1 | 0 | 0.415 | 0 | 503043 | 1 | 96204 | 96204 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 18 | 0 | 0 | 0 | 0 | 244.069
999 | 33/0.4 kV AT-2 | 0 | 0.415 | 0 | 503044 | 1 | 95386 | 95990 | 604 | 10 | 0 | 6040 | 6121.9313 | Kazla | Kazla 33/11KV S/S | 18 | 14219.5459 | 6072.6574 | 6096.5612 | 6096.0359 | 6101.7246
1000 | Auxiliary Transformer | 0 | 0.415 | 0 | 41901920685 | 1 | 2645.13 | 2767.96 | 122.83 | 160 | 0 | 19652.8 | 19919.386 | Kazla | Kazla 33/11KV S/S | 18 | 20587.2873 | 0 | 0 | 0 | 0
1001 | 11 kV HR (Hajrat_Rahima) Steel Express | B426H | 11 | Shympur | 0 | 1 | 707.49 | 752.49 | 45 | 40000 | 0 | 1800000 | 1814264.1154 | Shyampur | Shyampur 33/11KV S/S | 26 | 1610415.5328 | 1658511.8396 | 1848660.4463 | 1329002.2614 | 1796570.0888
1002 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1003 | 11 kV Road No.-21 Feeder | B426E | 11 | 0 | BD001943 | 1 | 1071.17 | 1085.02 | 13.85 | 40000 | 0 | 554000 | 558390.1777 | Shyampur | Shyampur 33/11KV S/S | 26 | 490213.532 | 606607.4764 | 536986.5578 | 689153.8135 | 726162.1684
1004 | 11 kV New Chakda Feeder | B426N | 11 | Shympur | BD001932 | 1 | 1561.8 | 1583.91 | 22.11 | 40000 | 0 | 884400 | 891408.4354 | Shyampur | Shyampur 33/11KV S/S | 26 | 575920.7998 | 812129.1164 | 684264.5087 | 768373.9842 | 842780.9272
1005 | 11 kV Burigonga Feeder | B426B | 11 | Shympur | BD001946 | 1 | 1454.49 | 1473.51 | 19.02 | 40000 | 0 | 760800 | 766828.9661 | Shyampur | Shyampur 33/11KV S/S | 26 | 770964.9094 | 745215.0941 | 653846.0494 | 678120.977 | 664045.6474
1006 | 11 kV Dapa-Pagla Feeder | B826D | 11 | Fatulla | BD001953 | 1 | 1365.13 | 1390.8 | 25.67 | 40000 | 0 | 1026800 | 1034936.8854 | Fatullah | Shyampur 33/11KV S/S | 26 | 1058124.3068 | 991363.1049 | 1100803.9423 | 1060453.8119 | 1011898.1651
1007 | 11 kV S. R. Steel Feeder. | B426J | 11 | Shympur | BD001945 | 1 | 3398.03 | 3458.08 | 60.05 | 40000 | 0 | 2402000 | 2421034.6696 | Shyampur | Shyampur 33/11KV S/S | 26 | 2293670.6681 | 2291008.6698 | 1731865.3068 | 2347543.3088 | 2415731.5404
1008 | 11 kV Rahima Steel Feeder. | old | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1009 | 11 kV Chand Textile Feeder | B426I | 11 | Shympur | BD001933 | 1 | 2212.37 | 2255.93 | 43.56 | 40000 | 0 | 1742400 | 1756207.6637 | Shyampur | Shyampur 33/11KV S/S | 26 | 1462630.5709 | 1686790.98 | 1265223.6985 | 1510257.147 | 1400226.6095
1010 | 11 kV Kamalpur Feeder | B826K | 11 | Fatulla | BD001922 | 1 | 492.99 | 496.84 | 3.85 | 40000 | 0 | 154000 | 155220.3743 | Fatullah | Shyampur 33/11KV S/S | 26 | 135769.9243 | 127455.2807 | 91577.1387 | 112254.6055 | 96981.9232
1011 | 11 kV Alizan Steel Feeder | B4265 | 11 | Shympur | BD001931 | 1 | 3222.54 | 3269.99 | 47.45 | 40000 | 0 | 1898000 | 1913040.7173 | Shyampur | Shyampur 33/11KV S/S | 26 | 1822681.1962 | 2162756.7937 | 1853587.4081 | 1927999.1795 | 1824622.7112
1012 | 11 kV Redwan Steel Feeder | B426C | 11 | Shympur | BD001933 | 1 | 2013.89 | 2051.33 | 37.44 | 40000 | 0 | 1497600 | 1509467.744 | Shyampur | Shyampur 33/11KV S/S | 26 | 1396147.3632 | 1389660.8569 | 915888.0248 | 1677475.7016 | 1601003.2355
1013 | 11 kV Kadamtolly Steel Feeder | B426U | 11 | Shympur | BD001923 | 1 | 1509.68 | 1523.24 | 13.56 | 40000 | 0 | 542400 | 546698.2534 | Shyampur | Shyampur 33/11KV S/S | 26 | 888712.2774 | 1726620.7552 | 1517234.7817 | 1359049.2203 | 1887540.7358
1014 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1015 | 11 kV Orient-Al-Islam Feeder | B426O | 11 | Shympur | BD001949 | 1 | 845.91 | 864.46 | 18.55 | 40000 | 0 | 742000 | 747879.9854 | Shyampur | Shyampur 33/11KV S/S | 26 | 273141.8536 | 751986.1559 | 501987.0295 | 565017.3838 | 552636.6613
1016 | 11 kV Delpara Feeder | B426D | 11 | Shympur | BD001937 | 1 | 1352.04 | 1370.29 | 18.25 | 40000 | 0 | 730000 | 735784.8913 | Shyampur | Shyampur 33/11KV S/S | 26 | 764156.3881 | 763138.4929 | 788989.597 | 774228.7961 | 1030332.7456
1017 | 11 kV Wasa Feeder | B426W | 11 | Shympur | BD001928 | 1 | 3136.88 | 3205.07 | 68.19 | 40000 | 0 | 2727600 | 2749214.8896 | Shyampur | Shyampur 33/11KV S/S | 26 | 3128315.2765 | 2945013.5787 | 2827927.2998 | 2567335.031 | 2104748.1835
1018 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1019 | 11 kV Al Noor-Femous Steel Feeder | B426F | 11 | Shympur | BD001938 | 1 | 1114.7 | 1121.46 | 6.76 | 40000 | 0 | 270400 | 272542.7871 | Shyampur | Shyampur 33/11KV S/S | 26 | 255119.2973 | 227029.7187 | 174848.8273 | 295251.5179 | 251271.3464
1020 | 11 kV Shyampur Bazar Feeder | B426S | 11 | Shympur | BD001939 | 1 | 2017.21 | 2055.4 | 38.19 | 40000 | 0 | 1527600 | 1539705.4793 | Shyampur | Shyampur 33/11KV S/S | 26 | 1292017.0377 | 1541412.3005 | 1200352.7042 | 1365805.0805 | 1428279.2319
1021 | 11 kV Spare Feeder | spare | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1022 | 11 kV Binimoy Feeder | B426L | 11 | Shympur | BD001942 | 1 | 1390.26 | 1411.57 | 21.31 | 40000 | 0 | 852400 | 859154.8511 | Shyampur | Shyampur 33/11KV S/S | 26 | 801803.5058 | 808146.1389 | 598969.7492 | 543740.6288 | 732574.1964
1023 | 11 kV Akbar-Nabi Steel | B4264 | 11 | Shympur | BD001941 | 1 | 1358.68 | 1384.37 | 25.69 | 40000 | 0 | 1027600 | 1035743.225 | Shyampur | Shyampur 33/11KV S/S | 26 | 446558.8956 | 946355.4589 | 931203.8377 | 1080348.9594 | 971021.4868
1024 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1025 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1026 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1027 | 11 kV Rasulpur Feeder | B426P | 11 | Shympur | BD001943 | 1 | 2314.14 | 2351.37 | 37.23 | 40000 | 0 | 1489200 | 1501001.1782 | Shyampur | Shyampur 33/11KV S/S | 26 | 1526310.2699 | 1579250.5869 | 1494594.8892 | 1526560.1151 | 1250345.4555
1028 | 11 Kv Pioneer Steel Feeder | B4262 | 11 | Shympur | BD001924 | 1 | 174.8 | 175.82 | 1.02 | 40000 | 0 | 40800 | 41123.3199 | Shyampur | Shyampur 33/11KV S/S | 26 | 3604.5113 | 82447.6347 | 75834.9927 | 95891.5675 | 84558.6189
1029 | 11 kV Spare Feeder | spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1030 | 11 kV Sun Steel Feeder | B426A | 11 | Shympur | BD001935 | 1 | 1234.74 | 1256.25 | 21.51 | 40000 | 0 | 860400 | 867218.2472 | Shyampur | Shyampur 33/11KV S/S | 26 | 889112.7786 | 908118.8747 | 695610.598 | 869607.7672 | 875642.5706
1031 | 11 kV Taher Steel Feeder | B4266 | 11 | Shympur | BD001942 | 1 | 3772.66 | 3812.96 | 40.3 | 40000 | 0 | 1612000 | 1624774.3078 | Shyampur | Shyampur 33/11KV S/S | 26 | 1797850.1185 | 1620673.5531 | 2160897.1026 | 1905144.5888 | 2092324.8793
1032 | 11 kV Igloo Feeder | B4269 | 11 | Shympur | BD001942 | 1 | 1119.74 | 1128.27 | 8.53 | 40000 | 0 | 341200 | 343903.8423 | Shyampur | Shyampur 33/11KV S/S | 26 | 438548.8705 | 532125.7967 | 778413.3204 | 463585.7706 | 590307.3256
1033 | 11/0.4 kV Aux Transformer, T-1 | 0 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1034 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0.415 | DPDC | DHK26108 | 1 | 64792.6 | 65260.8 | 468.2 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1035 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0.415 | 0 | 0 | 1 | 611666 | 619265 | 7599 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1036 | 11/0.4 kV Aux Transformer, T-2 | 0 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 26 | 0 | 0 | 0 | 0 | 0
1037 | 11 kV Nama shyampur Feeder | 0 | 11 | Shympur | HA-021101066-02 | 1 | 42309350 | 44443826 | 2134476 | 1 | 0 | 2134476 | 2124178.3588 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 2141060 | 2242087.5527 | 2142439.5507 | 2098065.1104 | 2051822.5774
1038 | 11 kV Bombay SweetsFeeder | B327M | 11 | Jurain | HA-021101063-02 | 1 | 22873022 | 23612106 | 739084 | 1 | 0 | 739084 | 735518.3371 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 786111 | 782826.8086 | 745206.3758 | 738065.3088 | 731764.9753
1039 | 11 kV H. R Steel | 0 | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0
1040 | 11 kV Shyampur Incoming (F1) | 0 | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 0 | 0 | 0 | 0 | 0
1041 | 11 kV Ali Bahar Feeder (F2) | B326A | 11 | Jurain | DHK61021 | 1 | 498635.8 | 528325.7 | 29689.9 | 60 | 0 | 1781394 | 1772799.78 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1740318 | 1920297.8361 | 1596859.747 | 1920766.0882 | 1940683.7189
1042 | 11 kV Mosjid Road Feeder (F3) | B327E | 11 | Jurain | DHK60936 | 1 | 642966.5 | 668712.2 | 25745.7 | 60 | 0 | 1544742 | 1537289.4923 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1379322 | 1531676.01 | 1098969.809 | 1475476.6819 | 1381608.0185
1043 | 11 kV Shyampur O/H Feeder (F4) | B327S | 11 | Jurain | DHK60938 | 1 | 661715.4 | 685766.2 | 24050.8 | 60 | 0 | 1443048 | 1436086.1084 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 1338426 | 1403188.8641 | 1231235.1282 | 1429313.0963 | 1378277.4296
1044 | 11 kV Road No-11 Feeder (F5) | B484Y | 11 | Shympur | DHK60937 | 1 | 385320 | 403627.9 | 18307.9 | 60 | 0 | 1098474 | 1093174.4833 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 818646 | 1160551.0823 | 887582.2839 | 954363.7317 | 1019394.7492
1045 | 11 kV Hanif Express Feeder (F6) | B327F | 11 | Jurain | DHK60939 | 1 | 518062.2 | 521552.7 | 3490.5 | 60 | 0 | 209430 | 208419.6185 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 288 | 3130.962 | 385792.207 | 8184.8678 | 8596.203
1046 | 11 kV Zia Sharani Road Feeder(F7) | B327Z | 11 | Jurain | DHK60940 | 1 | 967640.9 | 1012323.7 | 44682.8 | 60 | 0 | 2680968 | 2668033.8435 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2872542 | 2819649.0049 | 2794077.3284 | 2700808.4363 | 2561826.8196
1047 | 11 kV Road-12 & 13 Feeder(F8) | B484Z | 11 | Shympur | DHK60941 | 1 | 304035.4 | 328026.8 | 23991.4 | 60 | 0 | 1439484 | 1432539.3027 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1270602 | 1528603.9007 | 1237892.1591 | 1229098.1908 | 1284557.7074
1048 | 11 kV Rahman and Baset (F9). | B327H | 11 | Jurain | DHK60944 | 1 | 475560.2 | 498710.3 | 23150.1 | 60 | 0 | 1389006 | 1382304.8305 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 530982 | 646002.2013 | 711159.0569 | 480060.5409 | 1215195.8482
1049 | 11 kV Sabujbagh Feeder (F10) | B3B4G | 11 | Jurain | DHK61020 | 1 | 617165.5 | 659724.2 | 42558.7 | 60 | 0 | 2553522 | 2541202.6985 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 2715606 | 2647616.7695 | 2636452.1751 | 2526376.4464 | 2465450.8355
1050 | 11 kV Road No-7 & 8 Feeder(F11) | B327Q | 11 | Jurain | DHK60943 | 1 | 881811.3 | 894406.3 | 12595 | 60 | 0 | 755700 | 752054.1743 | Jurain | Shyampur BISIC 33/11KV S/S | 27 | 714972 | 785812.6007 | 661368.2767 | 689554.7346 | 725640.3272
1051 | 11 kV Hossain Express Feeder(F12) | B4277 | 11 | Shympur | DHK60942 | 1 | 8046.7 | 38811.9 | 30765.2 | 60 | 0 | 1845912 | 1837006.5171 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 1401510 | 1411640.1073 | 1301431.6729 | 1235612.3209 | 1199610.0995
1052 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB7380 | 1 | 615780 | 659160 | 43380 | 1 | 0 | 43380 | 43170.716 | Shyampur | Shyampur BISIC 33/11KV S/S | 27 | 3507 | 3715.5651 | 3553.7906 | 3904.2091 | 3633.5474
1053 | 11 kV Spare | spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0
1054 | 11 kV Khaza Moinuddin | B889Z | 11 | 0 | 00000026 | 1 | 6767583 | 7422622 | 655039 | 1 | 0 | 655039 | 656635.1076 | Fatullah | Nandalalpur 33/11 kV | 89 | 680847.6789 | 682477.6462 | 727695.4191 | 676115.2751 | 672821.6526
1055 | 11 kV Chitashal | B489Q | 11 | 0 | 00000027 | 1 | 34722676 | 35456592 | 733916 | 1 | 0 | 733916 | 735704.304 | Shyampur | Nandalalpur 33/11 kV | 89 | 743621.9237 | 740092.1663 | 801503.5058 | 725908.576 | 676035.0889
1056 | 11 kV Local Feeder | B489G | 11 | 0 | 00000157 | 1.5 | 18844474 | 19031274 | 186800 | 1 | Estimated | 668980.62 | 670610.6986 | Shyampur | Nandalalpur 33/11 kV | 89 | 650428.6635 | 670079.927 | 673810.7719 | 652026.96 | 610908.7086
1057 | 11 kV Rasel Germants | 0 | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0
1058 | 11 kV Matuail Medical (Adorsho nagar) | E289A | 11 | 0 | 00000121 | 1 | 78230880 | 80634160 | 2403280 | 1 | 0 | 2403280 | 2409135.9772 | Matuail | Nandalalpur 33/11 kV | 89 | 2474142.3426 | 2710158.1798 | 2342109.1991 | 2438091.1118 | 2521439.5722
1059 | 11 kV Nandalalpur | B890X | 11 | 0 | 00000010 | 1 | 85321072 | 86136912 | 815840 | 1 | 0 | 815840 | 817827.925 | Fatullah | Nandalalpur 33/11 kV | 89 | 726019.9781 | 743459.691 | 869061.7913 | 928548.3765 | 892208.2473
1060 | 11 kV Sharif Bagh | B489SB | 11 | 0 | 00000132 | 1 | 75334576 | 77028008 | 1693432 | 1 | 0 | 1693432 | 1697558.3187 | Shyampur | Nandalalpur 33/11 kV | 89 | 1769871.618 | 1607397.0329 | 1797879.9406 | 1716982.5939 | 1682233.437
1061 | 11 kV Spare | spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0
1062 | 11 KV Nayamati | B890Y | 11 | 0 | 00000158 | 1 | 67337432 | 68472832 | 1135400 | 1 | 0 | 1135400 | 1138166.5842 | Fatullah | Nandalalpur 33/11 kV | 89 | 1094447.1869 | 1160143.2858 | 1059913.8974 | 1145403.0364 | 1037983.1413
1063 | 11 kV Pulpar | B889S | 11 | 0 | 00000160 | 1 | 9343257 | 10315015 | 971758 | 1 | 0 | 971758 | 974125.8442 | Fatullah | Nandalalpur 33/11 kV | 89 | 814027.697 | 905763.961 | 653442.1412 | 808373.695 | 916555.6279
1064 | 11 kV Shahi Bazar | B489X | 11 | 0 | 00000170 | 1 | 42551376 | 43318576 | 767200 | 1 | 0 | 767200 | 769069.4058 | Shyampur | Nandalalpur 33/11 kV | 89 | 789833.0592 | 884250.6672 | 830388.5657 | 784445.919 | 785444.6114
1065 | 11 kV Pagla Bazar | B890G | 11 | 0 | 00000060 | 1 | 51571436 | 52221152 | 649716 | 1 | 0 | 649716 | 651299.1372 | Fatullah | Nandalalpur 33/11 kV | 89 | 675946.8632 | 703594.2894 | 679748.7175 | 834561.5067 | 783154.3223
1066 | 11 kV Delpara bazar | B489M | 11 | 0 | 00000063 | 1 | 82332920 | 83841392 | 1508472 | 1 | 0 | 1508472 | 1512147.634 | Shyampur | Nandalalpur 33/11 kV | 89 | 1531851.518 | 1668168.7326 | 1521265.0516 | 1508132.7308 | 1527622.8486
1067 | 11 kV Bhuighor (Board mill) | E289C | 11 | 0 | 00000146 | 1 | 45140688 | 45875048 | 734360 | 1 | 0 | 734360 | 736149.3859 | Matuail | Nandalalpur 33/11 kV | 89 | 684221.3852 | 711807.7641 | 702632.7597 | 668462.9794 | 1074021.0416
1068 | 11 kV Spare | 0 | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 89 | 0 | 0 | 0 | 0 | 0
1069 | 33/0.415 kV, 200 kVA AT-1 | 0 | 11 | 0 | 7803 | 1 | 2552 | 2600 | 48 | 100 | 0 | 4800 | 4811.696 | Shyampur | Nandalalpur 33/11 kV | 89 | 5827.1281 | 5909.6952 | 6446.2091 | 6244.3055 | 5725.7228
1070 | 33/0.415 kV, 200 kVA AT-2 | 0 | 11 | 0 | 7805 | 1 | 62 | 71.1 | 9.1 | 100 | 0 | 910 | 912.2174 | Shyampur | Nandalalpur 33/11 kV | 89 | 1004.6773 | 100.1643 | 0 | 0 | 0
1071 | 11 kV Station Road Feeder | A524N | 11 | Postogola | HA021100907-02 | 1 | 64899212 | 66131524 | 1232312 | 1 | 0 | 1232312 | 1255334.9139 | Postogola | Postogola 33/11KV S/S | 25 | 1334586.3999 | 1219095.1394 | 1335055.4691 | 1307497.2614 | 1269812.3426
1072 | 11 kV Samon & Sons Feeder. | B325Y | 11 | Jurain | HA021100501-02 | 1 | 10944921 | 10944921 | 0 | 1 | Estimated | 1216328.4 | 1239052.6971 | Jurain | Postogola 33/11KV S/S | 25 | 1255387.5265 | 1323367.1334 | 1374189.6942 | 1360936.1962 | 1367079.5822
1073 | 11 kV Alam Bagh Feeder. | B325L | 11 | Postogola | HA021100718-02 | 1 | 25117608 | 25644920 | 527312 | 1 | 0 | 527312 | 537163.6113 | Jurain | Postogola 33/11KV S/S | 25 | 519931.6597 | 537056.744 | 474949.556 | 542387.1952 | 435813.5436
1074 | 11 kV Majar O/H Feeder | A525M | 11 | Postogola | HA021100714-02 | 1 | 77506907 | 79011228 | 1504321 | 1 | 0 | 1504321 | 1532425.7761 | Postogola | Postogola 33/11KV S/S | 25 | 1609308.7492 | 1557430.4575 | 1587221.6201 | 1546887.4107 | 1509702.7057
1075 | 11 kV Cyca Feeder | A580S | 11 | Postogola | DHK61081 | 1 | 450849.6 | 461916 | 11066.4 | 60 | 0 | 663984 | 676389.0131 | Postogola | Postogola 33/11KV S/S | 25 | 678803.9555 | 662617.3772 | 636891.4703 | 664686.4068 | 678488.3278
1076 | 11 kV Housing O/H Feeder. | A525H | 11 | Postogola | DHK61085 | 1 | 906382.3 | 925873.2 | 19490.9 | 60 | 0 | 1169454 | 1191302.5568 | Postogola | Postogola 33/11KV S/S | 25 | 1270287.67 | 1139734.1436 | 1267305.3443 | 1258808.5211 | 1186933.4512
1077 | 11 kV Munshi Bari | A525U | 11 | Postogola | DHK61078 | 1 | 794197.3 | 814922.6 | 20725.3 | 60 | 0 | 1243518 | 1266750.2722 | Postogola | Postogola 33/11KV S/S | 25 | 1384014.8487 | 1419724.1658 | 1247409.4401 | 1227619.0196 | 1164704.2052
1078 | 11 kV Cantonment Feeder | A525T | 11 | Jurain | DHK60953 | 1 | 524334.2 | 526393.2 | 2059 | 60 | 0 | 123540 | 125848.0606 | Postogola | Postogola 33/11KV S/S | 25 | 126732.5803 | 134717.5169 | 129509.8262 | 124992.5587 | 126222.4118
1079 | 11 kV DIT Feeder. | A525I | 11 | Postogola | DHK60868 | 1 | 881725.3 | 905082.3 | 23357 | 60 | 0 | 1401420 | 1427602.3077 | Postogola | Postogola 33/11KV S/S | 25 | 1330189.3065 | 1373424.2339 | 1052907.1287 | 1323292.4846 | 1331811.5849
1080 | 11 kV Jurain WASA Road Feeder | B325W | 11 | Jurain | DHK60862 | 1 | 405545.3 | 445618.9 | 40073.6 | 60 | 0 | 2404416 | 2449336.9799 | Jurain | Postogola 33/11KV S/S | 25 | 2475377.6895 | 2446524.7479 | 2443876.2234 | 2429557.5202 | 2393972.4885
1081 | 11 kV Khorshed Ali O/H Feeder. | B325K | 11 | Jurain | HA021100484-02 | 1 | 42901124 | 45310492 | 2409368 | 1 | 0 | 2409368 | 2454381.4966 | Jurain | Postogola 33/11KV S/S | 25 | 2115704.7964 | 2221056.7969 | 2061497.5542 | 2071894.6482 | 1933992.5359
1082 | 11 kV Murad pur Feeder. | B325R | 11 | Jurain | HA021100680-02 | 1 | 13201.1 | 15592.1 | 2391 | 1000 | 0 | 2391000 | 2435670.3328 | Jurain | Postogola 33/11KV S/S | 25 | 2485795.0121 | 2477072.4328 | 2360182.711 | 2388027.6504 | 2351667.7366
1083 | 11 kV Habib Oil Feeder. | A525B | 11 | Postogola | HA021101240-02 | 1 | 59377915 | 60970541 | 1592626 | 1 | 0 | 1592626 | 1622380.5518 | Postogola | Postogola 33/11KV S/S | 25 | 1682719.5891 | 1655098.2 | 1632466.5583 | 1639249.0712 | 1571920.5306
1084 | 11 kV Rajabari Feeder. | A525R | 11 | Postogola | HA021100681-02 | 1 | 53444745 | 53444745 | 0 | 1 | Estimated | 243265.68 | 247810.5394 | Postogola | Postogola 33/11KV S/S | 25 | 239121.4336 | 245164.3984 | 245637.4316 | 262708.1006 | 303872.8913
1085 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 11 | 0 | ELIB67385 | 1 | 483.1 | 539.63 | 56.53 | 80 | 0 | 4522.4 | 4606.8906 | Postogola | Postogola 33/11KV S/S | 25 | 4570.7831 | 4670.5121 | 4307.9725 | 5751.9551 | 4375.6621
1086 | 11 kV Feeder-1 | 0 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0
1087 | 11 kV Feeder-2 | 0 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0
1088 | 11 kV Dholaikal RMU | A619R | 11 | 0 | DHK60970 | 1 | 294537.9 | 325962.4 | 31424.5 | 60 | 0 | 1885470 | 1912589.3597 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 2044107.1526 | 2258178.5414 | 2013206.2605 | 1942348.072 | 1890634.7965
1089 | 11 kV Alom Gonj | A581A | 11 | 0 | DHK60894 | 1 | 501244.8 | 511135.3 | 9890.5 | 60 | 0 | 593430 | 601965.5066 | Postogola | IG Gate GIS 33/11 kV | 87 | 622652.7534 | 676806.1857 | 596654.2301 | 589855.3321 | 589628.102
1090 | 11 kV Dhalka Nagar Feeder (F-5) | A580K | 11 | 0 | DHK60895 | 1 | 599147 | 625193.4 | 26046.4 | 60 | 0 | 1562784 | 1585262.0566 | Postogola | IG Gate GIS 33/11 kV | 87 | 1935090.8799 | 1875565.0903 | 1850628.0181 | 1792355.2732 | 1711977.4089
1091 | 11 kV Farashgonj Feeder (F-6) | A619F | 11 | 0 | DHK68133 | 1 | 3653.37 | 3683.69 | 30.32 | 60000 | 0 | 1819200 | 1845366.1756 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 1846529.6992 | 2047321.2801 | 1803939.5949 | 1748762.5817 | 1815572.1775
1092 | 11 kV Doyaganj | B587Y | 11 | 0 | DHK68134 | 1 | 2436.85 | 2463.08 | 26.23 | 60000 | 0 | 1573800 | 1596436.5035 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1387958.4974 | 1645033.4081 | 1687142.9696 | 1819772.2117 | 1955417.8504
1093 | 11 kV Faridabad | A587F | 11 | 0 | DHK68140 | 1 | 818.15 | 838.74 | 20.59 | 60000 | 0 | 1235400 | 1253169.1806 | Postogola | IG Gate GIS 33/11 kV | 87 | 1329183.0163 | 1411966.4378 | 1296128.1808 | 1292615.9757 | 1233789.9626
1094 | 11 kV Gandaria | A524D | 11 | 0 | DHK60969 | 1 | 441701.8 | 473557.9 | 31856.1 | 60 | 0 | 1911366 | 1938857.8307 | Postogola | IG Gate GIS 33/11 kV | 87 | 2106445.8973 | 2096887.3731 | 2186472.7241 | 2176408.4497 | 2008723.2675
1095 | 11 kV Walter Road | A687W | 11 | 0 | DHK68136 | 1 | 1032.13 | 1054.29 | 22.16 | 60000 | 0 | 1329600 | 1348724.0914 | Banglabazar | IG Gate GIS 33/11 kV | 87 | 2063264.286 | 1501529.2301 | 1391040.5522 | 1437042.3417 | 1402694.4766
1096 | 11 kV Murgitola Feeder (F-11) | B587G | 11 | 0 | DHK68138 | 1 | 3970.36 | 4009.01 | 38.65 | 60000 | 0 | 2319000 | 2352354.9699 | Swamibag | IG Gate GIS 33/11 kV | 87 | 2412855.9498 | 2416392.1157 | 2307519.2472 | 2337901.7997 | 2438521.0841
1097 | 11 kV Feeder-12 | 0 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 87 | 0 | 0 | 0 | 0 | 0
1098 | 11 kV Begumgonj Feeder (F-13) | B587B | 11 | 0 | DHK60899 | 1 | 724879 | 752453.5 | 27574.5 | 60 | 0 | 1654470 | 1678266.8077 | Swamibag | IG Gate GIS 33/11 kV | 87 | 1754827.7038 | 1727816.5375 | 1778252.8009 | 1741101.9665 | 1809148.9629
1099 | 11 kV Lohar Pool Feeder (F-14) | A525L | 11 | 0 | DHK60967 | 1 | 199239 | 214602.5 | 15363.5 | 60 | 0 | 921810 | 935068.7084 | Postogola | IG Gate GIS 33/11 kV | 87 | 1005323.9927 | 1010280.3195 | 1031522.1618 | 1006862.3928 | 984580.1304
1100 | 11/0.415 kV, 200 kVA AT-1+2 | 0 | 0.415 | 0 | ELIB2774 | 1 | 282863.01 | 284380 | 1516.99 | 1 | 0 | 1516.99 | 1538.8094 | Postogola | IG Gate GIS 33/11 kV | 87 | 3608.1717 | 0 | 1665.5005 | 1667.9239 | 1718.3058
1101 | Nizambag | F1114Z | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1216328.4 | 1217190.9472 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1180785.7325 | 1158100.6579 | 1095738.2283 | 1008260.1492 | 972380.6635
1102 | Merry Stopes | F1114P | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 304082.1 | 304297.7368 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 318812.1478 | 329144.3975 | 365246.0761 | 355856.5232 | 364642.7488
1103 | Mujibur Ghat | F1114V | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1277144.82 | 1278050.4946 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1298864.3057 | 1340958.6566 | 1217486.9203 | 1304807.2519 | 1337023.4124
1104 | Madrasa | F1114U | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1581226.92 | 1582348.2314 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1653100.0255 | 1462863.989 | 1424459.6968 | 1542044.934 | 1701666.1612
1105 | Thana | F1114Q | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1217190.9472 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1298864.3057 | 1219053.3241 | 1217486.9203 | 1423426.093 | 1337023.4124
1106 | Al-Hera | 0 | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0
1107 | Waz Uddin School | F1114W | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 851429.88 | 852033.6631 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 1003667.8726 | 975242.6593 | 730492.1522 | 830331.8876 | 972380.6635
1108 | 11/0.4 kV Auxiliary Transformer | 0 | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 114 | 0 | 0 | 0 | 0 | 0
1109 | Bashundhara City | 0 | 33 | 0 | 660434 | 1 | 791.06 | 803.19 | 12.13 | 180000 | 0 | 2183400 | 2191476.9852 | Shere b.nagar | Moghbazar 132/33/11KV S/S |  | 2303155.9363 | 2253160.9458 | 2286948.2926 | 2480389.347 | 2161081.9864
1110 | 33 kV Apollo Ispat Feeder | 0 | 33 | DPDC | 7389486 | 1 | 4570.36 | 4592.74 | 22.38 | 240000 | 0 | 5371200 | 5345006.6439 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 5626849.4493 | 4868511.8333 | 6352475.5818 | 7317548.4229 | 5615154.9463
1111 | 33 kV Adamjee EPZ Feeder | 0 | 33 | DPDC | ABB03919 | 1 | 370823 | 375764.6 | 4941.6 | 2000 | 0 | 9883200 | 9835003.2885 | Siddirgonj | Siddhirganj 132/33/11KV S/S |  | 9088565.8308 | 9139513.6232 | 7905743.5896 | 8068621.1441 | 8850787.3005
1112 | 33 KV Multi Oil Refinery*** | A816O | 33 | EXPORT | DHK95595 | 1 | 1015.73 | 1019.06 | 3.33 | 240000 | 0 | 799200 | 799200 | Siddirgonj | Demra 33/11KV S/S | 16 | 616800 | 492000 | 571200 | 446400 | 0
1113 | 33 kV ACI Pharmacuticles Feeder | 0 | 33 | 0 | DHKC4791 | 1 | 927.23 | 943.24 | 16.01 | 90000 | 0 | 1440900 | 1440900 | N.Gonj (East) | Khanpur 33/11KV S/S |  | 1206900 | 1225800 | 1291500 | 1045800 | 0
1114 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | E241AZ | 33 | DPDC | 0 | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 8133 | 8160.0632 | Matuail | Matuail 132/33 KV S/S | 41 | 8383.4623 | 9119.9454 | 10440.0638 | 10260.3419 | 10991.7418
1115 | 33 KV Shah Cement Feeder (F2) | 0 | 33 | DPDC | H/A030800181-03 | 1 | 41084.318 | 41084.427 | 0.109 | 1000 | 0 | 109 | 108.9746 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 64646.4953 | 944204.0986 | 2494536.8881 | 923421.8011 | 1229303.7954
1116 | 33/0.415 KV Transformer AT-1 | 0 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6559.9 | 4 | 160 | 0 | 640 | 639.8509 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0
1117 | 33/0.415 KV Transformer AT-2 | 0 | 0.415 | DPDC | 2001123043171 | 1 | 4763.3 | 4786.1 | 22.8 | 160 | 0 | 3648 | 3647.1499 | Sytalakhya | Sitalakhya 132/33KV S/S |  | 6180.7322 | 7797.005 | 4755.5609 | 4035.644 | 2848.7249
1118 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 0 | 33 | Main | 041808902866 | 1 | 343.51 | 361.28 | 17.77 | 360000 | 0 | 6397200 | 6404881.1253 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 5779395.3475 | 7171154.3348 | 6850018.059 | 6815752.3123 | 6616060.3155
1119 | 33 kV Delta Agro Premier Cement (=H2) | 0 | 33 | Main | 041808902876 | 1 | 114.83 | 122.98 | 8.15 | 360000 | 0 | 2934000 | 2937522.8571 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 2682130.383 | 2390384.7783 | 2530901.4092 | 2430058.343 | 2458012.5886
1120 | 33 kV Outgoing Feeder-3 (=H3) | 0 | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0
1121 | 33 kV Outgoing Feeder-4 (=H4) | 0 | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0
1122 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 0 | 33 | Main | 041808902856 | 1 | 43.78 | 43.78 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 400185.2656 | 1006790.1928 | 1108090.8439
1123 | 33 kV Outgoing Feeder-6 (=H12) | 0 | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0
1124 | 33 kV Outgoing Feeder-7 (=H13) | 0 | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 0 | 0 | 0 | 0 | 0
1125 | 33 kV Shah Cement VRM (=H14) | 0 | 33 | Main | 041808902860 | 1 | 499.66 | 499.66 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 2277825.3993 | 11858183.3118 | 9272761.2883 | 10712537.375 | 10817421.0397
1126 | 11 KV Shahidbagh Feeder | 0 | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 490476 | 492002.3987 | Rajarbag | Santinagar Switching S/S |  | 599477.6789 | 597504.11 | 524779.3911 | 36416.7693 | -3994.0825
1127 | 11 Fortune(MogBazar)-new | 0 | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 121824 | 122203.1256 | Moghbazar | Santinagar Switching S/S |  | 123551.4515 | 107474.29 | 138756.0658 | 127666.1608 | 126229.899
1128 | Centerpoint-Kakrail | 0 | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 61200 | 61390.4591 | Kakrail | Santinagar Switching S/S |  | 62067.8095 | 43848 | 71600.1051 | 81766.8748 | 80846.9863
1129 | 11 KV Shyamoli O/H | 0 | 11 | 0 | DHK-15026 | 1 | 9207.17 | 9219.86 | 12.69 | 40000 | 0 | 507600 | 520290 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 602290 | 545300 | 584660 | 530950
1130 | 11 KV Nearest RMU | 0 | 11 | 0 | DHK-15027 | 1 | 3871.9 | 3875.73 | 3.83 | 40000 | 0 | 153200 | 157030 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 160310 | 164820 | 182450 | 165230
1131 | 11 KV Sher-e-bangla Nagar | 0 | 11 | 0 | DHK-15025 | 1 | 3979.7 | 3980.52 | 0.82 | 40000 | 0 | 32800 | 33620 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 51660 | 44280 | 49610 | 45920
1132 | Export to DESCO | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S |  | 0 | 0 | 0 | -13837.5
1133 | 33/0.4 kV, 500 kVA AT-1 | 0 | 0.4 | 0 | 84.2659 | 1 | 321080 | 323466 | 2386 | 10 | 0 | 23860 | 23956.6474 | Paribag | Dhanmondi 33/11KV S/S |  | 23982.7488 | 25078.0786 | 24914.239 | 24707.6715
1134 | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0.4 | 0 | 84.2673 | 1 | 478776 | 478776 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S |  | 875.2094 | 10.0032 | 0 | 0
1135 | 33 KV Japan Genden City | 0 | 33 | 0 | DHK15681 | 1 | 606.8 | 687.9 | 81.1 | 18000 | 0 | 1459800 | 1459800 | Adabor | Japan Garden 33/11 KV |  | 1502640 | 1451700 | 1519200 | 1531620
1136 | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0.415 | 0 | DHKE6223 | 1 | 43427.32 | 43619.2 | 191.88 | 120 | 0 | 23025.6 | 23301.1673 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 23194.682 | 23415.1565 | 24412.3409 | 25361.4506
1137 | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar 33/11KV S/S |  | 0 | 0 | 0 | 0
1138 | AT-1 | 0 | 0.415 | 0 | 0 | 1 | 789.61 | 950.84 | 161.23 | 80 | 0 | 12898.4 | 12954.5544 | Mugdapara | Madarteck 33/11KV S/S |  | 10606.4337 | 12573.2122 | 11708.7885 | 9611.7345
1139 | AT-2 | 0 | 0.415 | 0 | 63394003 | 1 | 399.81 | 475.19 | 75.38 | 80 | 0 | 6030.4 | 6056.6539 | Mugdapara | Madarteck 33/11KV S/S |  | 7745.9106 | 5649.4556 | 6156.9427 | 5477.3433
1140 | 33 kV Shahriar Steel Feeder | 0 | 33 | Main | 41812909534 | 1 | 613.69 | 633.58 | 19.89 | 360000 | 0 | 7160400 | 7150980.086 | Kazla | Kazla 132/133 KV SS |  | 7435235.4244 | 7833434.8553 | 7323524.0635 | 7145780.8426
1141 | 33 kV Zahir Steel | A418J | 33 | Main | 41812909521 | 1 | 691.06 | 721.82 | 30.76 | 360000 | 0 | 11073600 | 11059032.0485 | Kazla | Kazla 132/133 KV SS |  | 10618692.0573 | 11070629.7471 | 10019388.2364 | 9121125.0936
1142 | 33kV Water Treatment Plant | 0 | 33 | Digital | 80379618 | 1 | 21552 | 21815 | 263 | 2000 | 0 | 526000 | 526937.9846 | Maniknagar | Maniknagar 132/33 KV SS |  | 686173.136 | 531621.6224 | 605078.9898 | 1062218.4705
1143 | Axuxilary -1 | 0 | 0.415 | 0 | AH14044078 | 1 | 414749.8 | 420573.6 | 5823.8 | 1 | 0 | 5823.8 | 5837.95 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 5955.9261 | 5213.2044 | 5831.4157 | 6475.0369
1144 | Axuxilary -2 | 0 | 0.415 | 0 | AH14044072 | 1 | 383501.3 | 388432.8 | 4931.5 | 1 | 0 | 4931.5 | 4943.482 | Maniknagar | Maniknagar 132/33/11KV S/S |  | 4558.0495 | 4382.3431 | 5377.7142 | 4841.9103
1145 | 33 kV Rani RRM Feeder | 0 | 33 | Export | BD001809 | 1 | 749.791 | 760.393 | 10.602 | 240000 | 0 | 2544480 | 2543674.3806 | Shyampur | Shyampur 132/33KV S/S |  | 3093749.2487 | 2731257.9254 | 2448780.2928 | 2460914.9302
1146 | 33 kV Rahima Steel feeder | 0 | 33 | Export | BD001803 | 1 | 654.799 | 656.416 | 1.617 | 240000 | 0 | 388080 | 387957.1282 | Shyampur | Shyampur 132/33KV S/S |  | 1848762.9304 | 2408497.5549 | 1851141.9981 | 2281164.2763
1147 | 33 kV Salam Steel Feeder | 0 | 33 | Export | BD001849 | 1 | 1212.322 | 1251.608 | 39.286 | 240000 | 0 | 9428640 | 9425654.7552 | Shyampur | Shyampur 132/33KV S/S |  | 6942639.1851 | 9555598.3573 | 9761265.4061 | 10754060.1599
1148 | 33 kV Steel Famus feeder | 0 | 33 | Export | BD001806 | 1 | 145.878 | 153.6104 | 7.7324 | 240000 | 0 | 1855776 | 1855188.4343 | Shyampur | Shyampur 132/33KV S/S |  | 668060.7526 | 1802076.7353 | 1343089.4196 | 1442423.9509
1149 | 33 kV Rani Kamal Steel Feeder | 0 | 33 | Export | BD001829 | 1 | 1569.566 | 1593.2569 | 23.6909 | 240000 | 0 | 5685816 | 5684015.7878 | Shyampur | Shyampur 132/33KV S/S |  | 6636959.5785 | 7405918.76 | 5422228.9014 | 6501978.5941
1150 | 33 kV Chakda Steel Feeder | 0 | 33 | Export | BD001832 | 1 | 2441.53 | 2477.8933 | 36.3633 | 240000 | 0 | 8727192 | 8724428.8439 | Shyampur | Shyampur 132/33KV S/S |  | 9042995.7002 | 9230581.7605 | 8256580.7385 | 8640663.1605
1151 | 33 kV Akhter Steel Feeder | 0 | 33 | Export | BD001828 | 1 | 686.506 | 690.9784 | 4.4724 | 240000 | Prime Textile | 1073376 | 1073036.1535 | Fatullah | Shyampur 132/33KV S/S |  | 1039008.3182 | 1167285.0702 | 1147950.5517 | 674551.2513
1152 | Aux Tr-1 | 0 | 0.44kv | Export | DHKG9742 | 1.025 | 347.544 | 349.667 | 2.123 | 2400 | 0 | 5222.58 | 5222.58 | Fatullah | Shyampur 132/33KV S/S |  | 5052.84 | 5102.04 | 5527.62 | 10071.24
1153 | Aux Tr-2 | 0 | 0.44kv | Export | DHKG9743 | 1.025 | 109.988 | 117.946 | 7.958 | 2400 | 0 | 19576.68 | 19576.68 | Fatullah | Shyampur 132/33KV S/S |  | 17894.04 | 18044.1 | 19434 | 11042.94
1154 | 132 kV MI Cement Feeder [MICFL] | 0 | 132 | P. Cell | 08993599 | 1 | 325.031 | 350.233 | 25.202 | 480000 |  | 12087360 | 12087360 | Sytalakhya | MI CEMENT 132/33 kV |  | 11905920 | 10329120 | 10749120 | 9239520
1155 | 33 kV Shah Cement Feeder | 0 | 33 | 0 | 8993 841 | 1 | 39462.866 | 39516.99 | 54.124 | 36000 | 0 | 1948464 | 1948464 | Sytalakhya | Madonganj 132/33 KV SS |  | 817416 | 2360592 | 3210156 | 3227092
1156 | 33 kV Mondol Para (Premire cement) Feeder | 0 | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS |  | 0 | 0 | 0 | 0
1157 | 11 kV Rayer Bazar Feeder | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 0 | 0 | Dhanmondi | Jigatola Switching |  | 0 | 0 | 679467.069
1158 | 11 kV Madina Masjid Feeder | 0 | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1459594.08 | 1463157.2985 | Jigatola | Jigatola Switching |  | 1648779.5998 | 1579031.3193 | 1587392.6308
1159 | 11 kV Mitali | 0 | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1471405.92 | 1474997.974 | Jigatola | Jigatola Switching |  | 1417602.7084 | 1504281.4171 | 1520651.6572
1160 | 132 kV Shah Cement | 0 | 132 | EXPORT | 042003953369 | 1 | 8.92 | 21.5 | 12.58 | 1200000 |  | 15096000 | 15096000 | Sytalakhya | Char Syedpur 132/33KV S/S |  | 10668000

## SS List (hidden)
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2283.1 | 2305.89 | 22.79 | 720000 | 16408800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2252.99 | 2274.38 | 21.39 | 720000 | 15400800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1992.33 | 2024.16 | 31.83 | 720000 | 22917600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1868.1 | 1886.38 | 18.28 | 480000 | 8774400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2143.91 | 2170.41 | 26.5 | 240000 | 0 | 6360000 | 6385761.8419 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2447.27 | 2475.1 | 27.83 | 240000 | 0 | 6679200 | 6706254.7947 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1494.65 | 1512.88 | 18.23 | 240000 | 0 | 4375200 | 4392922.2029 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 870.12 | 890.27 | 20.15 | 240000 | 0 | 4836000 | 4855588.7213 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1874.11 | 1890.5 | 16.39 | 240000 | 0 | 3933600 | 3949533.4562 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1223.1 | 1236.03 | 12.93 | 240000 | 0 | 3103200 | 3115769.8346 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 433.43 | 446.7 | 13.27 | 240000 | 0 | 3184800 | 3197700.3639 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2145.29 | 2172.52 | 27.23 | 240000 | 0 | 6535200 | 6561671.5077 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1656.79 | 1676.76 | 19.97 | 240000 | 0 | 4792800 | 4812213.7352 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 740.94 | 755.4 | 14.46 | 240000 | 0 | 3470400 | 3484457.2164 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2023.72 | 2057.42 | 33.7 | 240000 | 0 | 8088000 | 8120761.2858 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1865.27 | 1867.53 | 2.26 | 240000 | 0 | 542400 | 544597.0477 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 164.76 | 170.67 | 5.91 | 240000 | 0 | 1418400 | 1424145.3768 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1473.63 | 1502.1 | 28.47 | 240000 | 0 | 6832800 | 6860476.9675 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.11.2023 | Reading at 00.00hr 01.11.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2283.1 | 2305.89 | 22.79 | 720000 | 16408800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2252.99 | 2274.38 | 21.39 | 720000 | 15400800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1992.33 | 2024.16 | 31.83 | 720000 | 22917600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1868.1 | 1886.38 | 18.28 | 480000 | 8774400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2143.91 | 2170.41 | 26.5 | 240000 | 0 | 6360000 | 6385761.8419 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2447.27 | 2475.1 | 27.83 | 240000 | 0 | 6679200 | 6706254.7947 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1494.65 | 1512.88 | 18.23 | 240000 | 0 | 4375200 | 4392922.2029 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 870.12 | 890.27 | 20.15 | 240000 | 0 | 4836000 | 4855588.7213 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1874.11 | 1890.5 | 16.39 | 240000 | 0 | 3933600 | 3949533.4562 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1223.1 | 1236.03 | 12.93 | 240000 | 0 | 3103200 | 3115769.8346 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 433.43 | 446.7 | 13.27 | 240000 | 0 | 3184800 | 3197700.3639 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2145.29 | 2172.52 | 27.23 | 240000 | 0 | 6535200 | 6561671.5077 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1656.79 | 1676.76 | 19.97 | 240000 | 0 | 4792800 | 4812213.7352 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 740.94 | 755.4 | 14.46 | 240000 | 0 | 3470400 | 3484457.2164 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 2023.72 | 2057.42 | 33.7 | 240000 | 0 | 8088000 | 8120761.2858 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1865.27 | 1867.53 | 2.26 | 240000 | 0 | 542400 | 544597.0477 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 164.76 | 170.67 | 5.91 | 240000 | 0 | 1418400 | 1424145.3768 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1473.63 | 1502.1 | 28.47 | 240000 | 0 | 6832800 | 6860476.9675 | 0 | Dhanmondi 132/33/11KV S/S