## PDB Bill AMR
BPDB BILL FOR DPDC
[8 empty] | 132 KV LEVEL |  |  |  | Month May-2023 | [45 empty] | Considering P.F | [17 empty] | 132KV LEVEL | [7 empty] | Month :January--2018
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import / Export at 132 kV level |  | Remarks for KWH | KVAR CALCULATION | [5 empty] | PFC Calculation |  |  |  |  | Remarks for KVAR | Remarks for KVAR |  |  |  | DPDC |  |  |  | PDB |  |  |  |  | DPDC-PDB | [17 empty] | 0.9 | 0.9 | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import / Export at 132 kV level |  | KVAR CALCULATION |  |  | Reactive Energy Import / Export at 132 kV level |  | P.F | Remark
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Diff. | KVAR Import | KVAR Export | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit |  |  |  |  | NAME OF THE CIRCUIT | PF | CF | Pfc unit | PFC Surcharge | PF | CF | Pfc unit | PFC Surcharge | Difference |  |  |  | PF | 132 kv PFC CALCULATION===> | [13 empty] | 0.9 | 0.9 | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff | Diff | [5 empty] | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 29 | 30 |  |  | 2 | [7 empty] | Rate | Unit | Taka | [7 empty] | (A) 132 KV Level | [6 empty] | Month May-2023 |  |  | 0.9 | 0.9 | [11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [27 empty] | 0.89 | 0.005 | [18 empty] | SS | Meter No | Feeder Name | Net Mwh | Net Mvarh | PF | Percent | PF Unit | PFCharge(Tk.) | Remark | 0.9 | 0.9
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | AMR | Digital | 960000 | 2225.602 | 2226.297 | 0.695 |  | 667200 |  |  | 1940.692 | 1943.884 | 3.192 |  | 3064320 | -4482240 | -1995840 | 0.96 | 0 | 0 | Loop PFC is Considered |  | 0.88 | 0.01 | Hasnabad to Lalbagh | 0.96 | 0 | #REF! | #REF! | 0.8 | 9% | 3715286 | 21838451.108 | #REF! | #REF! | 0.89 | 0.005 | #REF! |  | 17610187.05 | #REF! |  | HARIG | EXP-08993646E | Haripur-Matuail 132 KV CKT | 19797120 | 7349760 | 0.94 |  |  |  |  | 0.9 | 0.9 | 0 | 667200 | 0 | 31939200 | 0 | -31272000 | [5 empty] | 1 | Hasnabad to Lalbagh | Hasnabad Grid | 132 | Export | 8993531 | AMR | Digital | 960000 | 2225.602 | 2226.297 | 0.695 |  | 667200 | 2020.336 | 2046.546 | 26.21 |  | 25161600 | 0.026507
|  |  | 132 | Import |  |  |  | 960000 | 660.75 | 666.114 | 5.364 | 5149440 |  |  |  | 366.817 | 372.088 | 5.271 | 5060160 | [5 empty] | 0 |  |  | 0.87 | 0.02 | [11 empty] | 0.88 | 0.01 | [5 empty] | HARIG | EXP-08993647E | Haripur-Shyampur 132 KV CKT IMP | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | 0.9 | 0.9 | 5149440 | 0 |  |  | 5149440 | 0 | [8 empty] | 132 | Import |  |  |  | 960000 | 660.75 | 666.114 | 5.364 | 5149440 |  | 1108.958 | 1108.958 | 0 | 0 |  | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | AMR | Digital | 960000 | 205.751 | 231.085 | 25.334 |  | 24320640 |  |  | 91.736 | 103.312 | 11.576 |  | 11112960 | 24320640 | 11112960 | 0.91 | 0 | 0
|  |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | AMR | Digital | 960000 | 108.597 | 117.004 | 8.407 |  | 8070720 |  |  | 39.173 | 41.721 | 2.548 |  | 2446080 | 8070720 | 2446080 | 0.96 | 0 | 0 |  |  | 0.86 | 0.03 | Hasnabad to Shyampur | 0.96 | 0 | #REF! | #REF! | 0.86 | 3% | 936662 | 5505699.236 | #REF! | #REF! | 0.87 | 0.02 | #REF! |  | 3624083.25 | #REF! |  | HARIG |  |  | 19876800 | 7246080 | 0.94 | 0% | #REF! | #REF! |  | 0.9 | 0.9 | 0 | 8070720 |  | 25914240 | 0 | -17843520 | [5 empty] | 2 | Hasnabad to Shyampur |  | 132 | Export | 8993532 | AMR | Digital | 960000 | 108.597 | 117.004 | 8.407 |  | 8070720 | 1401.753 | 1424.799 | 23.046 |  | 22124160 | 0.3427
|  |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  | 0.85 | 0.04 | [11 empty] | 0.86 | 0.03 | [5 empty] | HASNG | EXP-50146912E | Hasnabad-kamrangirchar 132 kv CKT-1 IMP | 46360320 | 13018560 | 0.96 | 0% | #REF! | #REF! | disputed | 0.9 | 0.9 | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  | 131.694 | 131.694 | 0 | 0 |  | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | AMR | Digital | 960000 | 344.582 | 363.871 | 19.289 |  | 18517440 |  |  | 210.435 | 211.998 | 1.563 |  | 1500480 | 18451200 | 1455360 |  |  | 0 | [22 empty] | HASNG | EXP-08993531E | Hasnabad-Lalbag 132 KV CKT IMP | -4482240 | -1995840 | 0.96 | 0% | #REF! | #REF! | [23 empty] | 344.582
|  |  | 132 | Import |  |  |  | 960000 | 5.35 | 5.419 | 0.069 | 66240 |  |  |  | 4.022 | 4.069 | 0.047 | 45120 | [5 empty] | 0 | [22 empty] | HASNG | EXP-08993532E | Hasnabad-Shyampur 132 KV CKT IMP | 8070720 | 2446080 | 0.96 | 0% | #REF! | #REF! | [23 empty] | 5.35
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [10 empty] | Total=> | 5215680 | 51576000 | 46360320 | Total=> |  |  |  | 5105280 | 18123840 | 46360320 | 13018560 | 0.96 |  | 0 |  |  | 0.84 | 0.05 | Hasnabad to Kamrangirchar | 0.96 | 0 | #REF! | #REF! |  |  |  | 0 | #REF! | #REF! | 0.85 | 0.04 | #REF! |  |  | 17576092.7654 |  | KALLG | EXP-5014660E | Kallyanpur-Lalbag 132 kv Ckt-2 Exp | 19178880 | 9517440 | 0.9 | 0 | #REF! | #REF! |  | 0.9 | 0.9 | 5215680 | 51576000 |  | 26328000 | 5215680 | 25248000 | [5 empty] | 3 | Hasnabad to Kamrangirchar |  | 132 | Export | 50146912 | AMR | Digital | 960000 | 0 | 0 | 0 |  | 0 | 362.107 | 372.478 | 10.371 |  | 9956160 | #DIV/0!
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | AMR | Digital | 960000 | 4716.502 | 4743.032 | 26.53 |  | 25468800 |  |  | 2365.324 | 2372.854 | 7.53 |  | 7228800 | 25468800 | 7228800 | 0.96 | 0 | 0 |  |  | 0.81 | 0.08 | [11 empty] | 0.82 | 0.07 | [5 empty] | MANIG | 50147582E | 230/132 kv Transformer-2 | 92013120 | 26007840 | 0.96 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 25468800 | 197760 |  | -197760 | 25468800 | [8 empty] | 132 | Import |  |  |  | 960000 | 4716.502 | 4743.032 | 26.53 | 25468800 |  | 2.109 | 2.187 | 0.078 | 74880 |  | 1
|  |  | 132 | Import |  | AMR |  | 960000 | 11.003 | 11.003 | 0 | 0 |  |  |  | 7.78 | 7.78 | 0 | 0 | [5 empty] | 0 |  |  | 0.8 | 0.09 | [11 empty] | 0.81 | 0.08 |  |  | 0 |  |  | PPACK | EXP-12393383E | Powerpack-Hasnabad-Kamrangirchar 132 kv | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | P.Plant | #REF! | #REF! | 0 | 0 | 197760 | 84181440 | -197760 | -84181440 | [16 empty] | Total=> | #REF! | #REF! |  |  |  | 74880 | 57241920
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [10 empty] | Total=> | 0 | 25468800 | 25468800 | Total=> |  |  |  | 0 | 7228800 | 25468800 | 7228800 | 0.96 |  | 0 |  |  | 0.78 | 0.12 | [11 empty] | 0.79 | 0.105 | [5 empty] | RAMPG | EXP-08993661E | Rampura-Mogbazar 132 kv CKT-2 | 12360960 | 117120 | 1 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 25468800 |  |  | 0 | 25468800 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 2.168 | 2.179 | 0.011 | 10560 |  | #DIV/0!
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | AMR | Digital | 960000 | 1057.877 | 1078.582 | 20.705 |  | 19876800 |  |  | 740.492 | 748.04 | 7.548 |  | 7246080 | 19876800 | 7246080 | 0.94 | 0 | 0 |  |  | 0.77 | 0.135 | Maniknager-2 (new line) | 0.94 | 0 | #REF! |  | 0.91028 | [5 empty] | 0.78 | 0.12 | #REF! |  | 423441.72 | #REF! |  | RAMPG | EXP-08993661E | Rampura-Ullon U/G 132 kv CKT-2 | 88177920 | 35030400 | 0.93 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 19876800 |  | 17099520 | 0 | 2777280 | [5 empty] | 6 | Maniknager-2 (new line) |  | 132 | Export | 8993624 | AMR | Digital | 960000 | 1057.877 | 1078.582 | 20.705 |  | 19876800 | 1800.618 | 1803.395 | 2.777 |  | 2665920 | 0.99113
|  |  | 132 | Import |  | AMR |  | 960000 | 70.056 | 70.056 | 0 | 0 |  |  |  | 141.149 | 141.149 | 0 | 0 | [5 empty] | 0 |  |  | 0.76 | 0.15 | [11 empty] | 0.77 | 0.135 | [5 empty] | RAMPG | EXP-08993661E | Rampura-Madartheck 132 kv CKT-1 | 61808640 | 18512640 | 0.96 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 | 22080 |  | -22080 | 0 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 70.056 | 70.056 | 0 | 0 |  | 0.11 | 0.289 | 0.179 | 171840 |  | #DIV/0!
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | AMR | Digital | 960000 | 234.584 | 255.206 | 20.622 |  | 19797120 |  |  | 93.84 | 101.496 | 7.656 |  | 7349760 | 19797120 | 7347840 | 0.94 | 0 | 0 |  |  | 0.75 | 0.165 | Matuail | 0.94 | 0 | #REF! | 0 | 0 | [5 empty] | 0.76 | 0.15 | #REF! |  |  |  |  | SIDDG | 08993683E | Siddhirgonj 132/33 kv Transformer-1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 19797120 |  | 29952960 | 0 | -10155840 | [5 empty] | 7 | Matuail |  | 132 | Export | 8993646 | AMR | Digital | 960000 | 234.584 | 255.206 | 20.622 |  | 19797120 | 1660.595 | 1660.595 | 0 |  | 0 | 0
|  |  | 132 | Import |  | AMR |  | 960000 | 4.361 | 4.361 | 0 | 0 |  |  |  | 30.489 | 30.491 | 0.002 | 1920 | [5 empty] | 0 | [15 empty] | 0.75 | 0.165 | [5 empty] | SIDDG | 08993682E | Siddhirgonj 132/33 kv Transformer-2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 4.361 | 4.361 | 0 | 0 |  | 0.002 | 0.002 | 0 | 0 |  | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [10 empty] | Total=> | 0 | 39673920 | 39673920 | Total=> |  |  |  | 1920 | 14595840 | 39673920 | 14593920 | 0.94 |  | 0 | [19 empty] | #REF! |  |  | SIDDG | EXP-08993681E | Siddhirgong-Ullon 132 kv CKT-1 IMP | 12029760 | 1085760 | 1 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 39673920 | 22080 | 47052480 | -22080 | -7378560 | [16 empty] | Total=> | 0 | 39673920 |  |  |  | 182400 | 2665920
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 |  | Digital | 480000 | 2694.555 | 2736.898 | 42.343 |  | 20324640 |  |  | 1105.032 | 1120.433 | 15.401 |  | 7392480 | 20324640 | 7392480 | 0.94 | 0 | 0 |  |  |  |  | Kallyanpur to Lalbagh 1 | 0.94 | 0 | #REF! |  | 0.92609 | [7 empty] | #REF! |  | 304546.23 | #REF! |  | SIDDG | EXP-08993680E | Siddhirgong-Maniknagar 132 kv CKT-2 IMP | 10200960 | 1266240 | 0.99 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 20324640 |  | 349440 | 0 | 19975200 | [5 empty] | 8 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | AMR | Digital | 960000 | 2694.555 | 2736.898 | 42.343 |  | 40649280 | 634.446 | 634.49 | 0.044 |  | 42240 | 1
10 | Tranformer 1 |  | 132 | Export | 80505634 | AMR |  | 480000 | 8302.15 | 8341.911 | 39.761 |  | 19085280 |  |  | 4879.469 | 4899.194 | 19.725 |  | 9468000 | 19085280 | 9468000 | 0.9 | 0 | 0 | [22 empty] | SIDDG | EXP- 8993555E | Siddhirgong-Matuail 132 kv CKT IMP | 24696960 | 9458880 | 0.93 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 19085280 |  |  | 0 | 19085280 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 8302.15 | 8341.911 | 39.761 | 38170560 |  | 132.04 | 132.04 | 0 | 0 |  | 0
11 | Tranformer 2 |  | 132 | Export | 80505637 | AMR |  | 480000 | 8253.814 | 8293.77 | 39.956 |  | 19178880 |  |  | 4838.654 | 4858.482 | 19.828 |  | 9517440 | 19178880 | 9517440 | 0.9 | 0 | 0 |  |  |  |  | Kallyanpur to Lalbagh 2 | 0.9 | 0 | #REF! | 0 | 0.93379 | [7 empty] | #REF! |  |  |  |  | SITAG | 080505634NE | Sitalakhya 132/33 kv Transformer-1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 19178880 |  | 352320 | 0 | 18826560 | [5 empty] | 9 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | AMR | Digital | 960000 | 8253.814 | 8293.77 | 39.956 |  | 38357760 | 6.002 | 6.043 | 0.041 |  | 39360 | 1
12 | MI CEMENT |  | 132 | Export | 38992489 (New) |  |  | 480000 | 214.544 | 237.085 | 22.541 |  | 10819680 |  |  | 43.146 | 46.824 | 3.678 |  | 1765440 | 10819680 | 1765440 | 0.99 | 0 | 0 | Main+ Backup | [21 empty] | SITAG | 080505637NE | Sitalakhya 132/33 kv Transformer-2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 10819680 |  |  | 0 | 10819680 | [8 empty] | 132 | Import |  | AMR |  | 960000 | 214.544 | 237.085 | 22.541 | 21639360 |  | 2.422 | 2.425 | 0.003 | 2880
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [10 empty] | Total=> |  | 69408480 | 69408480 | Total=> |  |  |  |  | 28143360 | 69408480 | 28143360 | 0.93 | 0 | 0 | [19 empty] | 0 |  |  |  |  | Sub Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 69408480 |  | 701760 | 0 | 68706720 | [16 empty] | Total=> | 59809920 | 79007040 |  |  | 0 | 2880 | 81600
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | AMR | Digital | 960000 | 8225.403 | 8261.732 | 36.329 |  | 34875840 |  |  | 4598.562 | 4614.751 | 16.189 |  | 15541440 | 34875840 | 15541440 | 0.91 | 0 | 0 |  |  |  |  | 132 kv DPAL | [27 empty] | #REF! | #REF! | 0 | 34875840 |  |  | 0 | 34875840 | [5 empty] | PP | 132 kv DPAL |  | 132 | Export | 16529653 |  |  | 144000 | 8225.403 | 8261.732 | 36.329
14 | XFR- T2 |  | 132 | Export | 8993682 | AMR | Digital | 960000 | 8216.58 | 8252.57 | 35.99 |  | 34550400 |  |  | 4593.393 | 4609.479 | 16.086 |  | 15442560 | 34550400 | 15442560 | 0.91 | 0 | 0 | [24 empty] | PDB Bill= |  |  |  |  | 12015662.3971 | 70628063.57 |  | #REF! | #REF! | 0 | 34550400 |  |  | 0 | 34550400 | [8 empty] | 132 | Import |  |  |  | 144000 | 8216.58 | 8252.57 | 35.99
15 | Ullon-1 |  | 132 | Export | 8993681 | AMR | Digital | 1440000 | 2570.44 | 2593.526 | 23.086 |  | 33243840 |  |  | 1361 | 1364.675 | 3.675 |  | 5292000 | 33243840 | 5292000 | 0.99 | 0 | 0 | [24 empty] | Difference= |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 33243840 |  |  | 0 | 33243840
|  |  | 132 | Import |  | AMR |  | 1440000 | 9.184 | 9.184 | 0 | 0 |  |  |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0 |  |  |  |  | Tranformer 3 | 0 | 0 | #REF! |  | 0.91797 | [7 empty] | #REF! | [27 empty] | 10 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 |  | Digital | 480000 | 9.184 | 9.184 | 0 |  | 0 | 155.967 | 169.111 | 13.144 |  | 6309120 | #DIV/0!
16 | Ullon-2 |  | 132 | Export | 8993680 | AMR | Digital | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 |  |  | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Tranformer 1 | 0 | 0 | #REF! | #REF! | 0.85075 | 4% | 550541 | 3236079.998 | #REF! | #REF! |  |  | #REF! |  | 4415892.17 | #REF! |  | (B) 33 KV Level | [9 empty] | #REF! | #REF! | 0 | 0 |  | 18315840 | 0 | -18315840 | [5 empty] | 11 | Tranformer 1 |  | 132 | Export | 80505634 | AMR |  | 480000 | 1373.548 | #REF! | #REF! |  | #REF! | 3659.429 | 3677.143 | 17.714 |  | 8502720 | #REF!
|  |  | 132 | Import |  | AMR |  | 1440000 | 22.279 | 22.279 | 0 | 0 |  |  |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0 |  |  |  |  | Tranformer 2 | 0 | 0 | #REF! | #REF! | 0.85475 | 4% | 562291 | 3305146.498 | #REF! | #REF! |  |  | #REF! |  | 4436657.97 | #REF! |  | SS | Meter No | Feeder Name | Net Mwh | Net Mvarh | PF | Percent | PF Unit | PFCharge(Tk.) | Remark | #REF! | #REF! | 0 | 0 |  | 18543840 | 0 | -18543840 | [5 empty] | 12 | Tranformer 2 |  | 132 | Export | 80505637 | AMR |  | 480000 | 22.279 | 22.279 | 0 |  | 0 | 3613.988 | 3631.772 | 17.784 |  | 8536320 | #DIV/0!
17 | Matuail |  | 132 | Export | 8993555 |  |  | 1440000 | 2698.916 | 2725.888 | 26.972 |  | 38839680 |  |  | 1260.703 | 1272.534 | 11.831 |  | 17036640 | 38839680 | 17036640 | 0.92 | 0 | 0 |  |  |  |  | MI CEMENT | 0.92 | 0 | #REF! |  | 0.97856 | [7 empty] | #REF! | [14 empty] | #REF! | #REF! | 0 | 38839680 |  | 6388800 | 0 | 32450880 | [5 empty] | 13 | MI CEMENT |  | 132 | Export | 8993599 |  |  | 480000 | 2698.916 | 2725.888 | 26.972 |  | 12946560 | 86.18 | 90.41 | 4.23 |  | 2030400 | 0.98792
|  |  | 132 | Import |  |  |  | 1440000 | 771.699 | 771.699 | 0 | 0 |  |  |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0 | [19 empty] | 0 |  |  | HASNG | 8993839 | Hasnabad-Lalbag 33kv CKT-1 | 8362800 | 3018780 | 0.94059 | 0% | #REF! | #REF! |  | #REF! | #REF! | 1373.548 | 0 |  | 43248480 | 1373.548 | -43248480 | [18 empty] | #REF! |  |  |  |  | 25378560
[11 empty] | Total=> | 0 | 141509760 | 141509760 | Total=> |  |  |  | 0 | 53312640 | 141509760 | 53312640 | 0.94 |  | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [7 empty] | 132 KV LEVEL |  |  |  | Month May-2023
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | AMR | Digital | 960000 | 5674.721 | 5714.359 | 39.638 |  | 38052480 |  |  | 2902.544 | 2921.368 | 18.824 |  | 18071040 | 38052480 | 18071040 | 0.9 | 0 | 0 | [23 empty] | 8993831 | Hasnabad-Postogola 33kv CKT | 5152680 | 1774080 | 0.94553 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 38052480 |  |  | 0 | 38052480
|  |  |  | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0 |  |  |  |  | XFR- T1 | 0 | 0 | #REF! | #REF! | 0.88207 | 1% | 257688 | 1514690.064 | #REF! | #REF! |  |  | #REF! |  | 2442859.18 | #REF! |  | KALLG | 0 | Kallyanpur-Lalmatia 33Kv U/G CKT | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  | 25236000 | 0 | -25236000 | [5 empty] | 14 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | AMR | Digital | 480000 | 0 | 0 | 0 |  | 0 | 3455.283 | 3483.956 | 28.673 |  | 13763040 | #DIV/0!
19 | Mogbazar-2 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 4851.765 | 4882.347 | 30.582 |  | 29358720 |  |  | 2470.878 | 2485.2 | 14.322 |  | 13749120 | 29358720 | 13749120 | 0.91 | 0 | 0 | [20 empty] | #REF! |  |  | 0 | Kallyanpur-Sherebanglanagar 33Kv U/G CKT | 0 | 0 | 0 | 0% | #REF! | #REF!
|  |  |  | Import |  | AMR |  | 960000 | 0.084 | 0.084 | 0 | 0 |  |  |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0 |  |  |  |  | XFR- T2 | 0 | 0 | #REF! | #REF! | 0.88144 | 1% | 261797 | 1538842.766 | #REF! | #REF! |  |  | #REF! |  |  |  |  | SATMG | 0 | Satmosjid 132/33 Transformer 2 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  | 25056000 | 0 | -25056000 | [5 empty] | 15 | XFR- T2 |  | 132 | Export | 8993682 | AMR | Digital | 480000 | 0.084 | 0.084 | 0 |  | 0 | 3443.894 | 3473.119 | 29.225 |  | 14028000 | #DIV/0!
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 4362.119 | 4374.65 | 12.531 |  | 12029760 | 80943360 |  | 1766.417 | 1767.606 | 1.189 |  | 1141440 | 12029760 | 1085760 | 1 | 0 | 0 |  |  |  |  | Ullon-1 | 1 | 0 | #REF! |  | 0 | [7 empty] | #REF! |  | 1720626.97 | #REF! |  |  | 0 | Satmosjid 132/33 Transformer 1 | 0 | 0 | 0 | 0% | #REF! | #REF! |  | #REF! | #REF! | 0 | 12029760 |  | 19805760 | 0 | -7776000 | [5 empty] | 16 | Ullon-1 |  | 132 | Export | 8993681 | AMR | Digital | 1440000 | 4362.119 | 4374.65 | 12.531 |  | 18044640 | 1028.421 | 1028.891 | 0.47 |  | 676800
|  |  |  | Import |  | AMR |  | 960000 | 1.56 | 1.56 | 0 | 0 |  |  |  | 8.636 | 8.694 | 0.058 | 55680 | [5 empty] | 0 | [24 empty] | Sub Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 1440000 | 1.56 | 1.56 | 0 | 0 |  | 17.383 | 17.383 | 0 | 0 |  | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | AMR | Digital | 960000 | 4049.578 | 4060.204 | 10.626 |  | 10200960 |  |  | 1627.178 | 1628.497 | 1.319 |  | 1266240 | 10200960 | 1266240 | 0.99 | 0 | 0 |  |  |  |  | Maniknagar -1 | 0.99 | 0 | #REF! | 0 | 0.54893 |  |  |  |  | D |  |  | #REF! |  | 286432.59 | #REF! | [11 empty] | #REF! | #REF! | 0 | 10200960 |  |  | 0 | 10200960 | [5 empty] | 17 | Maniknagar -1 |  | 132 | Export | 8993680 | AMR | Digital | 1440000 | 4049.578 | 4060.204 | 10.626 |  | 15301440 | 1172.921 | 1173.122 | 0.201 |  | 289440 | 0.99982
|  |  |  | Import |  | AMR |  | 960000 | 1.329 | 1.329 | 0 | 0 |  |  |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  | 0.80443 |  |  |  |  | D | [5 empty] | #REF! |  |  |  | PDB Bill= |  |  |  |  | 966275.4892 | 5728081.1 |  | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [8 empty] | 132 | Import |  | AMR |  | 1440000 | 1.329 | 1.329 | 0 | 0 |  | 7.625 | 10.539 | 2.914 | 4196160 |  | #DIV/0!
22 | Madartheck 1 |  | 132 | Export | 50146667 | AMR | Digital | 960000 | 1705.13 | 1730.856 | 25.726 |  | 24696960 |  |  | 620.848 | 630.701 | 9.853 |  | 9458880 | 24696960 | 9458880 | 0.93 | 0 | 0 | [19 empty] | 9263097.88 | #REF! |  |  |  | Difference= |  |  |  |  | #REF! | #REF! | [23 empty] | 1705.13 | 1730.856 | 25.726
23 | Madartheck 2 |  | 132 | Export | 50146668 | AMR | Digital | 960000 | 1499.805 | 1525.358 | 25.553 |  | 24530880 |  |  | 646.071 | 655.937 | 9.866 |  | 9471360 | 24530880 | 9471360 | 0.93 | 0 | 0 | [19 empty] | 0 |  |  |  |  | G.Total==>> |  |  |  |  | #REF! | #REF! |  | #REF! | #REF! | 0 | 24530880 |  | 70097760 | 0 | -45566880 | [16 empty] | Total=> | 0 | 33346080 |  |  |  | 4196160 | 28757280
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | AMR | Digital | 960000 | 121.203 | 134.079 | 12.876 |  | 12360960 |  |  | 2.359 | 2.481 | 0.122 |  | 117120 | 12360960 | 117120 | 1 | 0 | 0 |  |  |  |  | Mogbazar-1 | 1 | 0 | #REF! | #REF! | 0.87223 | 2% | 449203 | 2640415.234 | #REF! | #REF! |  |  | #REF! |  | 4005767.65 | #REF! | [11 empty] | #REF! | #REF! | 0 | 12360960 |  | 28729920 | 0 | -16368960 | [5 empty] | 18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | AMR | Digital | 960000 | 121.203 | 134.079 | 12.876 |  | 12360960 | 1862.487 | 1875.606 | 13.119 |  | 12594240 | 0.70047
| Dhaka University-1 (Imp) |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 48.234 | 51.664 | 3.43 | 3292800 |  | 0 | [36 empty] | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 |  | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | AMR | Digital | 960000 | 122.247 | 135.244 | 12.997 |  | 12477120 |  |  | 1.722 | 1.801 | 0.079 |  | 75840 | 12477120 | 75840 | 1 | 0 | 0 |  |  |  |  | Mogbazar-2 | 1 | 0 | #REF! | #REF! | 0.85962 | 4% | 712666 | 4189050.748 | #REF! | #REF! |  |  | #REF! |  | 1576789.96 | #REF! | [11 empty] | #REF! | #REF! | 0 | 12477120 |  | 22309440 | 0 | -9832320 | [5 empty] | 19 | Mogbazar-2 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 122.247 | 135.244 | 12.997 |  | 12477120 | 1668.059 | 1679.09 | 11.031 |  | 10589760 | 0.76242
| Dhaka University-2 (Imp) |  | 132 | Import |  |  |  | 960000 | 0 | 0 | 0 | 0 |  |  |  | 50.764 | 51.662 | 0.898 | 862080 | [38 empty] | #REF! | #REF! | 0 | 0 |  |  | 0 | 0 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 |  | 0
Maniknagar 230/132 Kv s/s | [10 empty] | Total=> | 0 | 163707840 | 163707840 | Total=> |  |  |  | 4210560 | 53351040 | 163707840 | 49140480 | 0.96 |  | 0 |  |  |  |  | Ullon U/G -1 | 0.96 | 0 |  |  | 0.92127 | [7 empty] | #REF! |  | 0 | [12 empty] | #REF! | #REF! | 0 | 163707840 |  | 20752320 | 0 | 142955520 | [5 empty] | 20 | Ullon U/G -1 |  | 132 | Export | 8993659 | AMR | Digital | 960000 | 0 | 0 | 0 |  | 288 | 1191.821 | 1208.951 | 17.13 |  | 16444800 | #DIV/0!
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 |  |  | 1920000 | 3042.09 | 3087.962 | 45.872 |  | 88074240 |  | July | 1556.031 | 1574.245 | 18.214 |  | 34970880 | 88074240 | 34970880 | 0.93 | 0 | 0 | [32 empty] | #REF! | #REF! | 0 | 88074240 |  |  | 0 | 88074240 | [9 empty] | Import |  | AMR |  | 960000 | 3042.09 | 3087.962 | 45.872 | 44037120 |  | 4.871 | 4.871 | 0 | 0 |  | 0
27 | Maniknagar-2 |  | 132 | Export | 50147585 |  |  | 1920000 | 3035.644 | 3081.57 | 45.926 |  | 88177920 |  |  | 1553.507 | 1571.752 | 18.245 |  | 35030400 | 88177920 | 35030400 | 0.93 | 0 | 0 |  |  |  |  | Ullon U/G -2 | 0.93 | 0 |  |  | 0.9144 | [7 empty] | #REF! |  | 1640187.72 | #REF! | [11 empty] | #REF! | #REF! | 0 | 88177920 |  | 19657920 | 0 | 68520000 | [5 empty] | 21 | Ullon U/G -2 |  | 132 | Export | 8993660 | AMR | Digital | 960000 | 3035.644 | 3081.57 | 45.926 |  | 44088960 | 1094.655 | 1111.663 | 17.008 |  | 16327680 | 0.93776
Shyampur 230/132 Kv s/s | [10 empty] | Total=> |  | 176252160 | 176252160 | T-1 Missing Unit |  |  |  |  | 70001280 | 176252160 | 70001280 | 0.93 | [34 empty] | #REF! | #REF! | 0 | 176252160 | 1920 |  | -1920 | 176252160 | [9 empty] | Import |  | AMR |  | 960000 | 0 | 0 | 0 | 0 |  | 3.421 | 3.421 | 0 | 0 |  | 0
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 |  |  | 1920000 | 1344.176 | 1376.368 | 32.192 |  | 61808640 |  | 0 | 677.227 | 686.869 | 9.642 |  | 18512640 | 61808640 | 18512640 | 0.96 | 0 | 0 | Loop PFC is Considered |  |  |  | Madartheck 1 | 0.96 | 0 |  |  | 0.93148 | [7 empty] | #REF! |  | 403606.99 | #REF! | [11 empty] | #REF! | #REF! | 0 | 61808640 |  | 6391680 | 0 | 55416960 | [5 empty] | 22 | Madartheck 1 |  | 132 | Export | 50146667 | AMR | Digital | 960000 | 1344.176 | 1376.368 | 32.192 |  | 30904320 | 182.547 | 185.946 | 3.399 |  | 3263040 | 0.99447
|  |  | 132 | Import | wp002497 |  |  | 1920000 | 0.245 | 0.245 | 0 | 0 |  |  |  | 9.389 | 9.391 | 0.002 | 3840 |  |  |  |  | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 |  |  | 1920000 | 0.216 | 0.216 | 0 | 0 |  |  |  | 9.655 | 9.657 | 0.002 | 3840 | [6 empty] | 0 | Missing Unit |  |  | Madartheck 2 | 0 |  |  |  | 0.92039 | [7 empty] | #REF! | [14 empty] | #REF! | #REF! | 0 | 0 |  | 6862080 | 0 | -6862080 | [5 empty] | 23 | Madartheck 2 |  | 132 | Export | 50146668 | AMR | Digital | 960000 | 0.216 | 0.216 | 0 |  | 0 | 152.673 | 156.273 | 3.6 |  | 3456000 | #DIV/0!
|  |  | 132 | Export | 38992559 |  |  | 1920000 | 1435.585 | 1467.736 | 32.151 |  | 61729920 |  |  | 717.048 | 726.775 | 9.727 |  | 18675840 | 61729920 | 18675840 | 0.96 | 0 | 0 | Loop PFC is Considered | [53 empty] | 1435.585
keranigonj 230/132 Kv s/s | [6 empty] | PDB | 81086400 |  |  | Total=> | 0 | 123538560 | 123538560 |  |  |  | 37180800 | 7680 | 37188480 | 123538560 | 37180800 | 0.94 | [56 empty] | 0
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 |  |  | 1440000 | 786.173 | 816.161 | 29.988 |  | 43182720 |  |  | 182.301 | 185.308 | 3.007 |  | 4330080 | 43182720 | 3432960 | 1 | 0 | 0 | [54 empty] | 786.173
|  |  | 132 | Import |  |  |  | 1440000 | 0.021 | 0.021 | 0 | 0 |  |  |  | 0.208 | 0.831 | 0.623 | 897120 | [60 empty] | 0.021
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 |  |  | 1440000 | 505.695 | 539.605 | 33.91 |  | 48830400 |  |  | 202.18 | 217.857 | 15.677 |  | 22574880 | 48830400 | 22574880 | 0.91 | 0 | 0 | [19 empty] | 0 | [12 empty] | #REF! | #REF! | 0 | 48830400 | 1920 | 104703360 | -1920 | -55872960 | [16 empty] | Total=> | 44037120 | 99831648 |  |  |  | 0 | 62675520
|  |  | 132 | Import |  |  |  | 1440000 | 0 | 0 | 0 | 0 |  |  |  | 0.831 | 0.831 | 0 | 0 |  | 0 | 0 | [7 empty] | Maniknagar-1 | 0 | 0 | #REF! | #REF! | 0.88854 | 1% | 586810 | 3449269.18 | #REF! | #REF! | 3 |  | #REF! |  | 3285623.31 | #REF! | [11 empty] | #REF! | #REF! | 0 | 0 |  | 37914240 | 0 | -37914240 | [5 empty] | 24 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 |  |  | 1920000 | 0 | 0 | 0 |  | 0 | 645.022 | 660.803 | 15.781 |  | 30299520 | #DIV/0!
Madangonj 132/33 Kv s/s | [10 empty] | Total=> | 0 | 92013120 | 92013120 | Missing Unit |  |  |  | 897120 | 26904960 | 92013120 | 26007840 | 0.96 |  |  | Missing Unit |  |  |  | Maniknagar-2 | 0.96 | 0 | #REF! | #REF! | 0.88875 | 1% | 578093 | 3398030.654 | #REF! | #REF! | 2 |  | #REF! |  | 3282801.87 | #REF! | [11 empty] | #REF! | #REF! | 0 | 92013120 |  | 38054400 | 0 | 53958720 | [5 empty] | 25 | Maniknagar-2 |  | 132 | Export | 50147585 |  |  | 1920000 | 0 | 0 | 0 |  | 0 | 646.845 | 662.374 | 15.529 |  | 29815680 | #DIV/0!
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 |  |  | 960000 | 223.259 | 235.539 | 12.28 |  | 11788800 |  | 0 | 58.863 | 61.712 | 2.849 |  | 2735040 | 11788800 | 2735040 | 0.97 | 0 | 0 | 0 | [16 empty] | #REF! |  | #REF! |  | 67003528.91 | 11399035.2007 | [9 empty] | #REF! | #REF! | 0 | 11788800 |  | 75968640 | 0 | -64179840 | [12 empty] | PDB | 81086400 | Diff | Diff | Total=> |  | 0 |  |  |  | 0 | 60115200
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 |  |  | 960000 | 130.476 | 144.939 | 14.463 |  | 13884480 |  |  | 27.6 | 31.207 | 3.607 |  | 3462720 | 13884480 | 3462720 | 0.97 | 0 | 0 | [21 empty] | #REF! | #REF! | [9 empty] | #REF! | #REF! | 0 | 13884480 | 221760 | 425953920 | -221760 | -412069440 | [7 empty] | TOTAL Import | [6 empty] | Active Energy ==> |  |  | #REF! | #REF! | Reactive Energy ==> |  |  | 4456320 | 236916000
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 |  |  | 960000 | 28.343 | 32.177 | 3.834 |  | 3680640 |  |  | 13.878 | 16.205 | 2.327 |  | 2233920 | 3680640 | 2233920 | [8 empty] | Unit | #REF! | #REF! | #REF! |  |  | 8611037 | 50615675.486 | #REF! | #REF! | #REF! |  |  |  | #REF! | [12 empty] | #REF! | #REF! |  | 3680640 |  | 425732160 | 0 | -422051520 | [7 empty] | NET TOTAL IMPORT (Energy export - Energy import) | [6 empty] | Active Energy ==> |  |  |  | #REF! | Reactive Energy ==> |  |  |  | 232459680 | #REF!
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 |  |  | 960000 | 8.797 | 18.041 | 9.244 | 8874240 |  |  |  | 12.084 | 14.511 | 2.427 | 2329920 | [53 empty] | Average Power Factor at 132 KV level | [16 empty] | #REF!
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[11 empty] | Total=> | 8874240 | 29353920 | 20479680 |  |  |  |  | 2329920 | 8431680 | 20479680 | 6101760 | 0.96 | [7 empty] | PDB 132 |  |  | 70628063.57 | [11 empty] | 2019622.176 | #REF!
[47 empty] | #REF! | #REF! | [9 empty] | 0 | 0 | 0 | 0 | 0 | 515260800 | 0 | -515260800 | [7 empty] | TOTAL Import | [6 empty] | Active Energy ==> |  |  | #VALUE! | #REF! | Reactive Energy ==> |  |  | 2880 | 258165600
TOTAL => | [11 empty] | 14089920 | 912502560 | [5 empty] | 12552480 | 317281920 | [10 empty] | Unit | #REF! | #REF! | #REF! |  |  | 12570126 | 73887200.628 | #REF! | #REF! | #REF! |  |  |  | #REF! | [12 empty] | 0 | 0 |  | 912502560 |  | 515260800 | 0 | 397241760 | [7 empty] | NET TOTAL IMPORT (Energy export - Energy import) | [6 empty] | Active Energy ==> |  |  |  | #REF! | Reactive Energy ==> |  |  |  | 258162720 | #REF!
NET TOTAL IMPORT (Energy export - Energy import) => | [10 empty] | BPDB |  | 898412640 | 898412640 | 0 |  |  |  |  | 304729440 | 898412640 | 304729440 | 0.95 |  | 0 |  | 0.94701 | [45 empty] | Average Power Factor at 132 KV level | [16 empty] | #REF!
[12 empty] | 132 KV level | KWH | KVARH
[13 empty] | 898412640 | 304729440
[13 empty] | 650527200 | 211203360 | [16 empty] | Diff |  |  | #REF!
| 33 KV LEVEL | [6 empty] | 33 KV LEVEL |  |  |  | Month May-2023
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 33kV voltage levels |  | Remarks for KWH | KVAR CALCULATION | [5 empty] | PFC Calculation |  |  |  |  | Remarks for KVAR | Remarks for KVAR (Bus Loss)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Diff. | KVAR Import | KVAR Export | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 11 | 12 | 13 | 14 | 15 | 16 | 18 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 30 | 28
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | AMR-1 | Digital | 48000 | 11910.314 | 11910.314 | 0 |  | 0 |  |  | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | PF 0.90 Considered | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | AMR-2 | Digital | 48000 | 14467.636 | 14467.636 | 0 |  | 0 |  |  | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | AMR-3 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 |  |  | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [52 empty] | 33 KV LEVEL
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  | 5241 | 179431602 |  |  | Total=> |  | 0 | [6 empty] | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | DPDC |  |  |  | PDB |  |  |  | DPDC-PDB | [20 empty] | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 33kV voltage levels |  | KVAR CALCULATION |  |  | Reactive Energy Import / Export at 33 kV level |  | P.F | Remark
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 29344.892 | 29344.892 | 0 |  | 0 |  |  | 7711.314 | 7711.314 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | NAME OF THE CIRCUIT | PF | CF | Pfc unit | PFC Surcharge | PF | CF | Pfc unit | PFC Surcharge | Difference | [19 empty] | PDB | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff | [6 empty] | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
4 | Shah Cement |  | 33 | Export | 8993841 | AMR-4 | Digital | 36000 | 39110.871 | 39195.806 | 84.935 |  | 3057660 |  |  | 10319.809 | 10339.1 | 19.291 |  | 694476 | 3057660 | 694476 | 0.97516 | 0 | 0 |  | 733 |  |  | 2 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | [30 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
5 | Mandal para |  | 33 | Export | 8993842 | AMR-5 | Digital | 180000 | 2588.486 | 2588.486 | 0 |  | 0 |  |  | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | [43 empty] | 1: Pagla Power Generation
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [10 empty] | Total=> |  | 3057660 | Missing Unit | [5 empty] | 694476 | 3057660 | 694476 |  |  | 0 |  | 733 |  |  | Shyampur 33//11kv S/S | [29 empty] | 0 | 3057660 | 0 | NO NEED | [7 empty] | 1 | Shyampur 33//11kv S/S | Pagla Rental | 33 | Export | 96833444 | - | Digital | 1000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | AMR-6 | Digital | 180000 | 1072.053 | 1072.053 | 0 |  | 0 | KWH | KVARH | 547.36 | 547.36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | Meter Replaced | [33 empty] | 180000 | 0 | 0 | NO NEED | [7 empty] | 5: Import; 8: Digital; 9: 1000; 10: 1072.053; 11: 1072.053; 12: 0; 13: 0; 15: 547.36; 16: 547.36; 17: 0; 18: 0; 20: 0
|  |  | 33 | Export | 38992490 (new) |  |  | 180000 | 1.046 | 1.103 | 0.057 |  | 10260 |  |  | 0.103 | 0.103 | 0 |  | 0 | 10260 | 0 | 0 | 0 | 0 | on 27/7/2022 |  |  |  | Shyampur 33//11kv S/S | [41 empty] | Shyampur 33//11kv S/S | Pagla Rental | 33 | Export | 216742477 | new |  | 82500 | 1.046 | 1.103 | 0.057 |  | 4705.5 | 0.103 | 0.103 | 0 |  | 0 | 0
7 | Shere Bangla |  | 33 | Export | 8993833 | AMR-7 | Digital | 180000 | 317.19 | 317.19 | 0 |  | 0 |  |  | 244.203 | 244.203 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | [45 empty] | 5: Import; 9: 82500; 10: 317.19; 11: 317.19; 12: 0; 13: 0; 15: 244.203; 16: 244.203; 17: 0; 18: 0; 20: 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | AMR-8 | Digital | 180000 | 4168.459 | 4175.969 | 7.51 |  | 1351800 |  |  | 2252.994 | 2253.803 | 0.809 |  | 145620 | 1351800 | 145620 | 0.99425 | 0 | 0 | [45 empty] | 12: 0; 13: 0; 14: 4705.5
9 | Satmosjid -2 |  | 33 | Export | 8993669E | AMR-9 | Digital | 180000 | 5659.613 | 5705.38 | 45.767 |  | 8238060 |  | 16790 | 2589.457 | 2607.416 | 17.959 |  | 3232620 | 8238060 | 3232620 | 0.9309 | 0 | 0 | [45 empty] | 1: HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS); 7: Units without wheeling Charge=>; 12: 4705.5; 18: 0; 19: 0
10 | Kallayanpur T3 |  | 33 | Export | 8993831 |  |  | 180000 | 6430.133 | 6458.759 | 28.626 |  | 5152680 |  |  | 3151.803 | 3161.659 | 9.856 |  | 1774080 | 5152680 | 1774080 | 0.94553 | 0 | 0 |  |  |  |  | Postagola (IG GATE) | 0.94553 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [19 empty] | 0 | 5152680 | 0 | 0 | 0 | [6 empty] | 2 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | AMR-1 | Digital | 48000 | 6430.133 | 6458.759 | 28.626 |  | 1374048 | 3151.803 | 3161.659 | 9.856 |  | 473088 | 0.94553
11 | Kallayanpur T4 |  | 33 | Export | 8993839 |  |  | 180000 | 8527.596 | 8574.056 | 46.46 |  | 8362800 |  |  | 3986.699 | 4003.47 | 16.771 |  | 3018780 | 8362800 | 3018780 | 0.94059 | 0 | 0 |  |  |  |  | Lalbag-1 | 0.94059 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [18 empty] | 13363 | 0 | 8362800 | 0 | 2863680 | 0 | [6 empty] | 3 | Lalbag-1 |  | 33 | Export | 8993861E | AMR-2 | Digital | 48000 | 8527.596 | 8574.056 | 46.46 |  | 2230080 | 3986.699 | 4003.47 | 16.771 |  | 805008 | 0.94059
12 | Kallayanpur T5 |  | 33 | Export | 38992611 |  |  | 180000 | 48.725 | 65.069 | 16.344 |  | 2941920 |  | 57240 | 12.308 | 15.871 | 3.563 |  | 641340 | 2941920 | 641340 | 0.97705 | 0 | 0 |  |  |  |  | Lalbag-2 | 0.97705 | 0 | #REF! | #REF! |  |  |  |  | #REF! | [5 empty] | 0 | [13 empty] | 8899 | 0 | 2941920 | 0 | 129744 | 0 | [6 empty] | 4 | Lalbag-2 |  | 33 | Export | 8993820 | AMR-3 | Digital | 48000 | 48.725 | 65.069 | 16.344 |  | 784512 | 12.308 | 15.871 | 3.563 |  | 171024 | 0.97705
| Export to Desco at 11 KV | [10 empty] | 6451145 | [6 empty] | 1061563.8 |  | -6451145 | -1061563.8 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | AMR-10 | 1 | 180000 | 5396.465 | 5413.706 | 17.241 |  | 3103380 |  |  | 2664.927 | 2671.485 | 6.558 |  | 1180440 | 3103380 | 1180440 | 0.93467 | 0 | 0
[11 empty] | Total=> | 6451145 | 29160900 | 22709755 |  |  |  |  | 1061563.8 | 9992880 | 22709755 | 8931316.2 |  |  |  |  | 0 |  |  | Aganagor-1 | [40 empty] | 1: 1; 2: Aganagor-1; 4: 33; 5: import; 6: 122218112; 7: REB; 8: 1.005; 9: 1000; 10: 0; 11: 0; 12: 0; 13: 0
SATMOSJID 132/33KV SS (
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E |  | 1 | 750000 | 3020.456 | 3062.422 | 41.966 |  | 31474500 |  |  | 1530.034 | 1546.826 | 16.792 |  | 12594000 | 31474500 | 12594000 | 0.92843 | 0 | 0 |  |  |  |  | Aganagor-2 | [40 empty] | 1: 2; 2: Aganagor-2; 4: 33; 5: import; 6: 12920031; 7: REB; 8: 1.005; 9: 5500; 10: 3020.456; 11: 3062.422; 12: 41.966; 13: 231967.065
15 | Transformer-2 |  | 33 | Export | 50148569E |  | 1 | 750000 | 2658.44 | 2701.161 | 42.721 |  | 32040750 |  |  | 1325.539 | 1342.604 | 17.065 |  | 12798750 | 32040750 | 12798750 | 0.92865 | 0 | 0 |  |  |  |  | Aganagor-3 | [40 empty] | 1: 3; 2: Aganagor-3; 4: 33; 5: import; 6: 15716186; 7: REB; 8: 1.005; 9: 5500; 10: 2658.44; 11: 2701.161; 12: 42.721; 13: 236140.3275
AGARGAON 132/33KV SS | [5 empty] | CF | = | 1.0003 |  |  | Total=> |  | 63515250 | [6 empty] | 25392750 | 63515250 | 25392750 |  | 0 | 0 | [45 empty] | 1: MADANGONJ 132/33 KV S/S (Tel: 01711-202009); 6: 33 KV Buss Loss; 8: 12922; 12: Total=>; 13: 468107.3925; 14: 4388640; 19: 1449120; 20: 0
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 1.0003 | 1 | 180000 | 1827.532 | 1853.024 | 25.492 |  | 4590030.6748 |  |  | 623.879 | 629.834 | 5.955 |  | 1072243.5536 | 4590030.6748 | 1072243.5536 | 0.97378 | 0 | 0 |  |  |  |  | 132 kv102 MW | [40 empty] | 1: PP; 2: 132 kv102 MW; 4: QRPP; 5: import; 6: 13176571; 9: 960000; 10: 1827.532; 11: 1853.024; 12: 25.492
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 1.0003 | 1 | 180000 | 614.698 | 630.272 | 15.574 |  | 2804218.4893 |  |  | 41.854 | 43.198 | 1.344 |  | 241997.5375 | 2804218.4893 | 241997.5375 | 0.9963 | 0 | 0 | [45 empty] | 5: Export; 9: 960000; 10: 614.698; 11: 630.272; 12: 15.574
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 1.0003 | 1 | 180000 | 106.915 | 106.915 | 0 |  | 0 |  |  | 4.16 | 4.16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 1.0003 | 1 | 180000 | 956.721 | 990.553 | 33.832 |  | 6091711.8229 |  |  | 411.088 | 422.754 | 11.666 |  | 2100553.0304 | 6091711.8229 | 2100553.0304 | 0.94537 | 0 | 0
20 | Monipuripara-2 |  |  |  |  | 1.0003 | 1 | 180000 | 693.36 | 716.372 | 23.012 |  | 4143487.5996 |  |  | 261.79 | 268.299 | 6.509 |  | 1171995.5148 | 4143487.5996 | 1171995.5148 | 0.96225 | 0 | 0 | [45 empty] | 2: Units without wheeling Charge( UNITS FROM QRPP)=>
| Maniknagar 230/132 kv |  |  |  |  | CF | = | 1.025 |  |  |  |  | 17629448.5865 | [6 empty] | 4586789.6363 | 17629448.5865 | 4586789.6363 |  |  | 0 |  |  |  |  | Shah Cement | 0 | 0 | #REF! | [26 empty] | 0 | 17629448.5865 | 0 | 5352552 | 0 | [6 empty] | 5 | Shah Cement | Madangonj Grid | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 1.025 |  | 1 | 384321.4 | 391339 | 7017.6 |  | 7193.04 |  |  | 246248.5 | 250703.8 | 4455.3 |  | 4566.6825 | 7193.04 | 4566.6825 | 0.84423 | 0.05 | 0 |  |  |  |  | Shah Cement | 0.84423 | 0.05 | #REF! | [26 empty] | 0 | 7193.04 | 0 | 5352552 | 0 | [6 empty] | 5 | Shah Cement |  | 33 | Export | 8993841 | AMR-4 | Digital | 18000 | 384321.4 | 391339 | 7017.6 |  | 126316800 | 246248.5 | 250703.8 | 4455.3 |  | 80195400 | 0.84423
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 1.025 |  | 1 | 359618.5 | 364399.6 | 4781.1 |  | 4900.6275 |  |  | 124499.7 | 126702.6 | 2202.9 |  | 2257.9725 | 4900.6275 | 2257.9725 | 0.90823 | 0 | 0 |  |  |  |  | Mandal para | 0.90823 | 0 | #REF! | [26 empty] | 0 | 4900.6275 | 0 | 4402000 | 0 | [6 empty] | 6 | Mandal para |  | 33 | Export | 8993842 | AMR-5 | Digital | 180000 | 359618.5 | 364399.6 | 4781.1 |  | 860598000 | 124499.7 | 126702.6 | 2202.9 |  | 396522000 | 0.90823
Shyampur 230/132 kv | [5 empty] | CF | = | 1.025 |  |  |  |  | 12093.6675 | [6 empty] | 6824.655 | 12093.6675 | 6824.655 |  |  | 0 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 1.025 | 1 | 2400 | 329.26 | 337.075 | 7.815 |  | 19224.9 |  |  | 207.893 | 213.274 | 5.381 |  | 13237.26 | 19224.9 | 13237.26 | [7 empty] | Aux T1 | [29 empty] | 0 | 19224.9 | 0 | 0 | 0 | [6 empty] | 7 | Aux T1 |  | 0.4 | Export | 9187973 | G.E.C | Analog | 10 | 329.26 | 337.075 | 7.815 |  | 0 | 207.893 | 213.274 | 5.381 |  | 53.81 | 0.82364
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 1.025 |  | 2400 | 82.006 | 82.99 | 0.984 |  | 2420.64 |  |  | 45.561 | 46.059 | 0.498 |  | 1225.08 | 2420.64 | 1225.08 | [7 empty] | Aux T2 | [29 empty] | 0 | 2420.64 | 0 | 15440 | 0 | [6 empty] | 8 | Aux T2 |  | 0.4 | Export | 9187972 | G.E.C | Analog | 10 | 82.006 | 82.99 | 0.984 | 1.025 | 10.086 | 45.561 | 46.059 | 0.498 |  | 4.98 | 0.89224
[13 empty] | 21645.54 | [6 empty] | 14462.34 | 21645.54 | 14462.34 | [48 empty] | 1: HARIPUR 130/132 KV S/S (Tel: 01730-335255); 14: 986914810.086
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  |  | PGCB | #REF! |  |  |  | 6451145 | 113396997.794 |  | Total KVAR/P.F.C UNIT => |  |  |  | 1061563.8 | 40688182.6313 |  |  |  |  | 0 | Bus Loss Unit | 733 | [43 empty] | 1: KALLYANPUR 132/33 KV S/S (Tel: 9007406); 12: Total=>; 19: 476717458.79
NET TOTAL IMPORT 33 KV (Energy export - Energy import) => | [6 empty] | PGCB | #REF! |  |  | BPDB |  | 106945852.794 | NET KVAR/ PFC UNIT AT 33 KV LEVEL => | [5 empty] | 39626618.8313 | 106945852.794 | 39626618.8313 | 0.9377 |  |  |  | 0.9377 |  |  | Jigatala (JP garden) | [29 empty] | 0 | #REF! | 0 | 0 | 0 | [6 empty] | 9 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 | AMR-6 | Digital | 180000 | 1071.741 | 0 | -1071.741 |  | -192913380 | 0 | 0 | 0 |  | 0 | 0
NET TOTAL IMPORT 11 KV (Energy export - Energy import) => | [6 empty] | PGCB | [5 empty] | 753375 | Tariff point Total ( 33 KV and 11 Kv )=> |  |  |  | 107699227.794
[30 empty] | Shere Bangla | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [19 empty] | 0 | 0 | 0 | 640000 | 0 | [6 empty] | 10 | Shere Bangla |  | 33 | Export | 8993833 | AMR-7 | Digital | 180000 | 298.605 | 0 | -298.605 |  | -53748900 | 0 | 0 | 0 |  | 0 | 0
[12 empty] | 33 KV level | KWH | KVARH | [15 empty] | Satmosjid-1 | [27 empty] | PDB Wrong | 114789 | 33 KV level | KWH | 0 | 12255000 | #VALUE! | [6 empty] | 11 | Satmosjid-1 |  | 33 | Export | 8993638E | AMR-8 | Digital | 180000 | 3925.828 | 0 | -3925.828 |  | -706649040 | 0 | 0 | 0 |  | 0 | 0
[13 empty] | 106945852.794 | 39626618.8313 | [15 empty] | Satmosjid -2 | 0 | 0 | #REF! | [26 empty] | 0 | 106945852.794 | 0 | 1370000 | 0 | [6 empty] | 12 | Satmosjid -2 |  | 33 | Export | 8993669E | AMR-9 | Digital | 180000 | 3400.926 | 0 | -3400.926 |  | -612166680 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Lalmatia | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [18 empty] | 137051 | 0 | 0 | 0 | 10341000 | 0 | [6 empty] | 13 | Lalmatia |  | 33 | Export | 8993836E | AMR-10 | 1 | 180000 | 4091.905 | 0 | -4091.905 |  | -736542900 | 0 | 0 | 0 |  | 0 | 0
[60 empty] | 180000 | #REF! | 0 | 42721968 | [7 empty] | 1: SATMOSJID 132/33KV SS (; 12: Total=>; 14: -2302020900; 19: 0
| 11&0.4 KV LEVEL | [11 empty] | 0 | [16 empty] | Transformer-1 | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E |  | 1 | 750000 | 872.986 | 0 | -872.986 | 0 | -654739500 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Transformer-2 | 0 | 0 | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 15 | Transformer-2 |  | 33 | Export | 50148569E |  | 1 | 750000 | 467.14 | 0 | -467.14 |  | -350355000 | 0 | 0 | 0 |  | 0 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [7 empty] | KWH CALCULATION |  |  |  | Energy Import/Export at 11 kV voltage levels |  | Remarks for KWH | KVAR CALCULATION | [11 empty] | Remarks for KVAR | [5 empty] | #REF! | [37 empty] | 12: Total=>; 14: -1005094500; 19: 0; 20: 0
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | CF | OMF | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Differance | Energy Import (KWh) | Energy Export (KWh) |  | KVAR METER NO | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | Diff. | KVAR Import | KVAR Export |  |  | P.F | P.F.C Corr. Factor | [5 empty] | DPDC-CKT-1 | [40 empty] | 16 | DPDC-CKT-1 | Sher-e Bangla S/S | 33 | Export |  | 1.0016 |  | 180000 | 579.468 | Reading at 00.00hr 01.06.2023 | #VALUE! |  | #VALUE! | Reading at 00.00hr 01.05.2023 | Reading at 00.00hr 01.06.2023 | #VALUE! |  | #VALUE! | #VALUE!
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 11 | 12 | 13 | 14 | 15 | 16 | 18 | 18 | 19 | 20 | 21 |  |  | 22 | 23 |  |  | 26 |  |  | DPDC-CKT-2 | [40 empty] | 17 | DPDC-CKT-2 |  | 33 | Export |  | 1.0016 |  | 180000 | 110.481 | 11 | -99.481 |  | -17934396.0456 | 18 | 18 | 0 |  | 0 | 0
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [29 empty] | DPDC-CKT-2 | [40 empty] | 17 | DPDC-CKT-2 |  | 33 | Export |  | 1.0016 |  | 180000 | 110.481 | 0 | -110.481 |  | -19917471.7736 | 0 | #REF! | #REF! |  | #REF! | #REF!
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | Secure | Digital | 40000 | 1915.47 | 1915.47 | 0 |  | 0 |  | Same Meter | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | L & G | Digital | 8000 | 40126.43 | 40126.43 | 0 |  | 0 |  |  | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | Secure | Digital | 40000 | 9317.28 | 9317.28 | 0 |  | 0 |  |  | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1 | [46 empty] | 2: Maniknagar 230/132 kv; 14: #VALUE!
| Swerage 11KV O/H |  | 11 | Export | 14959 | Secure | Digital | 40000 | 782.24 | 782.24 | 0 |  | 0 |  |  | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1 | [5 empty] | Axuxilary -1 | [40 empty] | 18 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 1 |  | 1 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | L & G | Digital | 8000 | 34050.59 | 34050.59 | 0 |  | 0 |  |  | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1 | [5 empty] | Axuxilary -2 | [40 empty] | 19 | Axuxilary -2 |  | 33 | Export | AH14044072 | 1 |  | 1 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | Secure | Digital | 40000 | 994.03 | 994.03 | 0 |  | 0 |  |  | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1 | [6 empty] | Unit | #REF! | [38 empty] | 14: 0; 19: 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | Secure | Digital | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 |  |  | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [10 empty] | Total=> |  | 0 | 0 | [5 empty] | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | Secure | Digital | 40000 | 9139.22 | 9151.97 | 12.75 |  | 510000 | 522750 | Same Meter | 3448.61 | 3452.81 | 4.2 |  | 168000 | 172200 |  | 0.94979 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | Secure | Digital | 40000 | 3840.99 | 3855.49 | 14.5 |  | 580000 | 594500 |  | 1259.75 | 1262.76 | 3.01 |  | 120400 | 123410 |  | 0.97913 | 1 |  | 38403.4483 | RMU Feeder KVARH Back Calculation as per KWH Percentage |  |  |  |  | 5.928 | [26 empty] | SHYAMPUR 33KV | NET=> | #REF! | NET=> | 42721968 | [7 empty] | 3: TOTAL Import; 10: Active Energy ==>; 13: 468107.3925; 14: #VALUE!; 15: Reactive Energy ==>; 18: 0; 19: 478166578.79 | Bus Loss Unit
3a | PD Betar |  | 11 | Import | 2612100427 |  | Digital | 600 | 8696 | 8820 | 124 | 74400 |  | 76260 |  | 2868 | 2870 | 2 | 1200 |  | 1230 |  | 0.99987 | 1 | [6 empty] | 0 | #REF! | #REF! | #REF! |  |  |  |  | #REF! | #REF! | [30 empty] | 3: NET TOTAL IMPORT (Energy export - Energy import); 10: Active Energy ==>; 14: #VALUE!; 15: Reactive Energy ==>; 19: 478166578.79; 20: #VALUE!
3b | SE,NB,Betar |  | 11 | Import | 2612100517 |  | Digital | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 0 |  | 572 | 572 | 0 | 0 |  | 0 |  | 0 | 1 | [46 empty] | 3: Average Power Factor at 33 KV level; 20: #VALUE!
3b | SE,NB,Betar |  | 11 | Import | 645015020085 |  | Digital | 300 | 1398 | 1398 | 0 | 0 |  | 0 |  | 494 | 494 | 0 | 0 |  | 0 |  | 0 | 1 | [6 empty] | PDB 33 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 |  |  | 300 | 647 | 739 | 92 | 27600 |  | 28290 |  | 198 | 236 | 38 | 11400 |  | 11685 |  | 0.92426 | 1 |  | Estimated |  |  |  |  | Diff | #REF!
3c | NINS & H |  | 11 | Import | Dhk-59122 |  | Digital | 1000 | 26592 | 26885 | 293 | 293000 |  | 300325 |  | 11551.97 | 11652 | 100.03 | 100035 |  | 102535.875 |  | 0.94637 | 1 | [5 empty] | 11 kv
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | Secure | Digital | 40000 | 3974.03 | 3975.03 | 1 |  | 40000 | 41000 |  | 1885.43 | 1886.11 | 0.68 |  | 27200 | 27880 |  | 0.82693 | 1.0884
5 | BICC - U/G |  | 11 | Export | 15024 | Secure | Digital | 40000 | 1038.1 | 1038.1 | 0 |  | 0 | 0 |  | 297.32 | 297.32 | 0 |  | 0 | 0 |  | 0 | 1
6 | NEC |  | 11 | Export | 15023 | Secure | Digital | 40000 | 431.56 | 431.56 | 0 |  | 0 | 0 |  | 56.29 | 56.29 | 0 |  | 0 | 0 |  | 0 | 1
7 | Manikmia Avenue |  | 11 | Export | 76026327 | L & G | Digital | 40000 | 3357 | 3357 | 0 |  | 0 | 0 |  | 1465 | 1465 | 0 |  | 0 | 0 |  | 0 | 1
| Manikmia Avenue | new | 11 | Export | DHK27341 |  | Digital | 40000 | 175.92 | 175.92 | 0 |  | 0 | 0 |  | 57.975 | 57.975 | 0 |  | 0 | 0
[11 empty] | Total=> |  | 1130000 | 1158250 |  |  |  |  | 112635 | 315600
TOTAL => | [11 empty] | 395000 | 1130000 | [5 empty] | 112635 | 315600
NET TOTAL IMPORT (Energy export - Energy import) => | [12 empty] | 735000 | [6 empty] | 202965 | [6 empty] | 0.96392
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB) | [12 empty] | 753375 | [6 empty] | 208039.125 |  |  | 0.96392 |  |  |  | 0.96392 | [22 empty] | Accoding to PDB | [20 empty] | 6: 11&0.4 KV LEVEL
| 11 KV P.C Culture Housing | [11 empty] | 33 KV level | KWH | KVARH | [34 empty] | Input | KWH | KVAR | [7 empty] | Acording to DPDC |  | Acording to PDB |  | Acording to DPDC | [6 empty] | 1: SUBSTATION-FEEDER-METERS INFORMATION; 9: KWH CALCULATION; 13: Energy Import/Export at 11 kV voltage levels; 15: KVAR CALCULATION; 18: Reactive Energy Import / Export at 11 kV level; 20: P.F; 21: Remark
| 11 KV Nearest RMU | [12 empty] | 753375 | 208039.125 | [14 empty] | NAME OF THE CIRCUIT | [18 empty] | BICC |  | 962.34 | 265.23 | [7 empty] | Energy Import (KWh) | Energy Export (KWh) | Energy Import (KWh) | Energy Export (KWh) | Diff |  | 11 KV and .4 KV import converted into 132 KV for maching the calculation with PDB |  |  |  | Energy Import/Export at 132 kV voltage levels |  | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Make | Digital/Analog | OMF | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Differance | Energy Import (KWh) | Energy Export (KWh) | Reading at 00.00hr 01.01.18 | Reading at 00.00hr 01.02.18 | Diff. | KVAR Import | KVAR Export
| 11 KV NEC Feeder. | [28 empty] | 2 | [18 empty] | NEC |  | 431.17 | 56.22 | [7 empty] | 0 | 0 |  |  |  |  | Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Energy Import (KWh) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| 11 KV Shyamoli O/H | [47 empty] | Shamoly 11KV O/H |  | 8700.85 | 3294.12 | [7 empty] | 0 | 0 | 0 | 0 |  |  | 1 | 2 | 3 | 4 | 14 | 1: KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| 11 KV BCFCC Feeder. | [28 empty] | Adabor 11KV O/H | [18 empty] | Sher-E-Bangla Nagar |  | 3602.65 | 1739.62 | [6 empty] | #REF! | 0 | 0 | 0 | 1770400 | 0 |  | KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) |  |  |  |  | 1 | Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
| 11 KV Sher-e-bangla Nagar | [28 empty] | Monsurabab 11KV O/H | [18 empty] | Manik Mia 11KV O/H |  | 2963 | 1326 | [7 empty] | 0 | 0 | 0 | 2723600 | 0 |  | 1 | Adabor 11KV O/H | Kallyanpur 33/11KV | 11 |  | 2 | Monsurabab 11KV O/H |  | 11 | Export | 77816681 | L & G | Digital | 8000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
| 11 KV Manik Mia Feeder. | [28 empty] | Beri Bandh 11KV O/H | [29 empty] | 0 | 0 | 0 | 2425600 | 0 |  | 2 | Monsurabab 11KV O/H |  | 11 |  | 3 | Beri Bandh 11KV O/H |  | 11 | Export | 14960 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Swerage 11KV O/H | [18 empty] | 11KV RMU U/G |  | 3335.92 | 1118.77 | [7 empty] | 0 | 0 | 0 | 2718800 | 0 |  | 3 | Beri Bandh 11KV O/H |  | 11 |  | 4 | Swerage 11KV O/H |  | 11 | Export | 14959 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Ring Road 11KV O/H | [28 empty] | #REF! | 0 | 0 | 0 | 2162240 | 0 |  | 4 | Swerage 11KV O/H |  | 11 |  | 5 | Ring Road 11KV O/H |  | 11 | Export | 77816675 | L & G | Digital | 8000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | RMU Feeder | [18 empty] | PD Betar |  | 2961 | 799 | [7 empty] | 0 | 0 | 0 | 203200 | 0 |  | 5 | Ring Road 11KV O/H |  | 11 |  | 6 | RMU Feeder |  | 11 | Export | 14997 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | P.C Culture Housing 11 KV | [18 empty] | SE, NB, Betar |  | 2075 | 509 | [6 empty] | #REF! | 0 | 0 | 0 | 1652000 | 0 |  | 6 | RMU Feeder |  | 11 |  |  | P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[49 empty] | NINS&H |  | 13570 | 6541 | [6 empty] | #REF! |  | 0 |  | 13655840 |  |  | 7 | P.C Culture Housing 11 KV |  | 11 |  | 1: AGARGAON 33/11 KV S/S (Tel: 8122865); 12: Total=>; 14: 0; 16: 0; 19: 0
[30 empty] | Shyamoli 11KV O/H | [28 empty] | #REF! | 0 | 0 | 0 | 2340400 | 0 |  | AGARGAON 33/11 KV S/S (Tel: 8122865) |  |  |  |  | 7 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | 11 KV R.M.U Feeder | [18 empty] | Adabor 11KV O/H |  | 1568.4 | 6107.4 | [6 empty] | #REF! | 0 | 0 | 0 | 906000 | 0 |  | 7 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 |  | 8 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[49 empty] | (Beri Bandh) 11KV O/H |  | 9192.76 | 3796.33 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[49 empty] | Ring Road 11 KV O/H |  | 32749.69 | 16758.17 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[80 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0
[80 empty] | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0
[49 empty] | Swerage 11KV O/H |  | 480.82 | 4422.64 | [8 empty] | 0 | [9 empty] | 10: 0; 11: 0; 12: 0; 15: 0; 16: 0; 17: 0; 20: 0
[30 empty] | 11 KV Sher-e-banglanagar | [18 empty] | RMU 11 KV |  | 993.85 | 211.73 | [6 empty] | #REF! | 0 | 0 | 0 | 443600 | 0 |  | 8 | 11 KV R.M.U Feeder |  | 11 |  | 9 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | BICC - U/G | [18 empty] | Monsurabad |  | 38635.52 | 19957.6 | [6 empty] | #REF! | 0 | 0 | 0 | 322800 | 0 |  | 9 | Sher-e-banglanagar |  | 11 |  | 10 | BICC - U/G |  | 11 | Export | 15024 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | NEC | [29 empty] | 0 | 0 | 0 | 115200 | 0 |  | 10 | BCFCC - U/G |  | 11 |  | 11 | NEC |  | 11 | Export | 15023 | Secure | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[30 empty] | Manikmia Avenue | [29 empty] | 0 | 0 | 0 | 900000 | 0 |  | 11 | NEC |  | 11 |  | 12 | Manikmia Avenue |  | 11 | Export | 76026327 | L & G | Digital | 40000 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0
[66 empty] | 12 | Manikmia Avenue |  | 11 |  | 1: Import from Baridhara 33/11 KV S/S (Tel: 02-9888965, Mob: 01730-335248); 12: Total==>; 14: 0; 19: 0
[59 empty] | SHYAMPUR 11KV | #REF! | 0 | 118200 | 18683840 |  |  | 4 | Nanruti S/S (Yousuf-01818284943) | Tejgaon | 0.4 | #REF! | 3: TOTAL ==>; 14: 0; 19: 0
[66 empty] | Sum > |  |  |  | #REF! | 3: NET TOTAL IMPORT (Energy export - Energy import) ==>; 14: 0; 19: 0
[66 empty] | Net 132KV Import > |  |  |  |  | 3: 11 kV import converted into 33 kV import (Adding 2.5%) ==>; 14: 0; 19: 0
[73 empty] | Average Power Factor at 33 KV level==> | [16 empty] | 0

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month May-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 898412640 | 8.1335 | 7307239207 |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 898412640 | 898412640 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 7307239207 | 7307239207 | 0
2a | 33kv | 106945852.794 | 8.22 | 879094910 |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 106945852.794 | 106945852.794 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 879094910 | 879094910 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 753375 | 8.22 | 6192743 |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 753375 | 753375 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 6192743 | 6192743 | 0
2c | Bus Loss Units (33kv) | 733 | 8.22 | 6024 |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 733 | 733 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 6024 | 6024 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 107699960.794 |  | 885293677 |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 107699960.794 | 107699960.794 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 885293677 | 885293677 | 0
4 | TOTAL 132kv & 33kv (1+3) | 1006112600.794 |  | 8192532884 |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 1006112600.794 | 1006112600.794 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 8192532884 | 8192532884 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 0 | 8.22 | 0 |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 0 |  | 0 |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 0 | 0 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 0 | 0 | 0
8 | TOTAL Billed Amount => (4+7) | 1006112600.794 |  | 8192532884 |  | 8330288836.94 | 10 | সর্বমোট (৬+৯) | 1006112600.794 | 1006112600.794 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 8192532884 | 8192532884 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 491551973 | Source Tax
10 | NET BILL TOTAL => (8-9) |  |  | 7700980911
11*** | 21th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  | 137755952.94 | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 7838736863.94
"In word: Taka Seven Hundred Eighty Three Crore Eighty Seven Lac Thirty Six Thousand Eight Hundred Sixty Three and Poisa Ninety Four"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | #VALUE!
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Certified For Payment
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0
| Total | 3306142870.56
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month May-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [8 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[11 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month May-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 898412640 | 0.2886 | 259281887.904 |  |  | 1 | 132 †Kwf (GbvwR©) | 898412640 | 898412640 | 898412640 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 7307239207 | 259281887.904 | 259281887.904 | 0
2a | 33kv Level | 106945852.794 | 0.2944 | 31484859.0626 |  |  | 2 | 33 †Kwf (GbvwR©) | 106945852.794 | 106945852.794 | 106945852.794 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 879094910 | 31484859.0626 | 31484859.0626 | 0 |  | 33KV Amount (2+3+4) => | 31706868.4578
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 753375 | 0.2944 | 221793.6 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 753375 | 753375 | 753375 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 6192743 | 221793.6 | 221793.6 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 733 | 0.2944 | 216.1952 |  |  | 4 | 33 ‡Kwf evm jm | 733 | 733 | 733 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 6024 | 215.7952 | 216.1952 | -0.4 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 107699960.794 | 0.2944 | 31706868.8578 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 107699960.794 | 107699960.794 | 107699960.794 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 885293677 | 31706868.4578 | 31706868.8578 | -0.4
4 | TOTAL=> (1+3) | 1006112600.794 |  | 290988756.7618 |  |  | 6 | me©‡gvU (1+5) | 1006112600.794 | 1006112600.794 | 1006112600.794 | 0 |  |  | 6 | me©‡gvU (1+5) | 8192532884 | 290988756.3618 | 290988756.7618 | -0.4
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000
6*** | Add: Ref. No. 27.87.0000.517.31.031.20.43; Date:09/11/2022 (8th Installment) |  |  | 25993419.79 |  |  | ‡gvU (GbvwR©) |  | 1006111867.794 | 1006111867.794 | 1006111867.794 | 0 |  |  | ‡gvU (GbvwR©) |  | 8192526860 | 290988540.5666 | 31706868.8578 | 259281671.7088
7 | Grand TOTAL=> (4-5+6) |  |  | 315482176.5518
| CERTIFED UNITS |  |  | 1006112600.794
| CERTIFED TAKA |  |  | 290988756.7618
| CERTIFED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 8th Installment of Wheeling Charge Due) |  |  | 315482176.5518
evsjv
In word: Taka Thirty One Crore Fifty Four Lac Eighty Two Thousand One Hundred and Seventy Seven
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Certified For Payment
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
| CERTIFED UNITS | 0
| CERTIFED TAKA | 0
In word:Nine Core Ninety Lac Seventy Six Thousand Eight Hundred Eighty Three Taka only.
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check (hidden)
[6 empty] | Month May-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import / Export at 132 kV level | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 14 | 15
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 132335565.54 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 132116688 | Fatullah Grid | 39074400 | 218877.54 | 0.1654%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 667200 |  |  |  | Shyampur Grid | 93042288
|  |  | 132 | Import |  | 5149440 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 24320640 | 32391360 | Postogola 132/33 KV Grid | 33076800 | Postogola Grid | 33076800 | -685440 | -2.116%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 8070720
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 18517440 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 66240 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 5215680 | 51576000
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 25468800 | 105781440 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 105109210.026 | Ullon Grid | 21800410.026 | 672229.974 | 0.6355%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 69967200
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 25468800 |  |  |  | DU Grid | 13341600
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 19876800 | 131687040 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 129119463.44 | Lalbagh Grid | 48474410 | 2567576.56 | 1.95%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 37704253.44
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 19797120 |  |  |  | Jigatola Grid | 42940800
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 39673920
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 20324640 | 58588800 | Sitalakhya 132/33 KV Grid | 58436017 | Sitalakhya Grid | 58436017 | 152783 | 0.2608%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 19085280
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 19178880
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 10819680 | 10819680 | Sitalakhya NOCS | 10819680 | Sitalakhya NOCS | 10819680 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 69408480
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 34875840 | 69426240 | Siddirganj 132/33 KV Grid | 69391584 | Siddirganj Grid | 69391584 | 34656 | 0.04992%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 34550400
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 33243840 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 38839680 | 38839680 | Matuail 132/33 KV Grid | 38799560.37 | Matuail Grid | 38799560.37 | 40119.63 | 0.1033%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 141509760
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | Month May-2023 | 0
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 38052480 | 67411200 | Moghbazar 132/33 KV Grid | 67267200 | Moghbazar Gird | 67267200 | 144000 | 0.2136%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 29358720
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 12029760 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 0 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 10200960
|  |  |  | Import |  | 0 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 24696960 | 49227840 | Madartek 132/33 KV Grid | 49227840 | Madartek Grid | 49227840 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 24530880
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 12360960 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 12477120
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 0 | 163707840
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 88074240 | 176252160 | Maniknagar 132/33 KV Grid | 174752480 | Kazla Grid | 57549600 | 1499680 | 0.8509%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 88177920 |  |  |  | Motijheel Grid | 23256000
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 176252160 |  |  |  | Narinda Grid | 37939200
[11 empty] | Bangabhaban Grid | 6492000
[11 empty] | Maniknagar Grid | 49515680
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 61808640 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 61729920
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 123538560
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 43182720 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 48830400
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 92013120
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 11788800 | 25673280 | Charsyedpur 132/33 KV Grid | 25614924 | Charsyedpur Grid | 25614924 | 58356 | 0.2273%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 13884480
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 3680640 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 8874240 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 8874240 | 29353920 | 898434285.54 |  | 893731446.836 |  | 893731446.836 | 4702838.704 | 0.5234%
[9 empty] | 33 KV Transmission Loss |  | 106924207.254 | 107102336.6891 | -178129.4351 | -0.1666%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 753375 | 754605 | -1230 | -0.1633%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 1006111867.794 | 1001588388.5252 | 4523479.2688 | 0.4496%
[9 empty] | From Summary Sheet |  |  |  | 5984733.6677 | 0.5948%
[9 empty] | Mismatch in KWH |  |  |  | -1461254.3989
| 33 KV LEVEL |  |  |  |  | Month May-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import/Export at 33kV voltage levels | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 13 | 14
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 3057660 | 3057660 | Sitalakhya NOCS | 3058393 | Sitalakhya NOCS | 3058393 | -733 | -0.02397%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 3057660
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 10260 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 10260 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 10260
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 1351800 | 76208490 | Shatmasjid 132/33 KV Grid | 76598204.8023 | Asadgate SS | 17793034.2 | -389714.8023 | -0.5114%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 8238060 |  |  |  | Lalmatia SS | 13830210
[11 empty] | Japan Garden SS | 15206400
[11 empty] | Jigatola Old SS | 1445282.3546
[11 empty] | Shatmasjid SS | 19243178.2478
[11 empty] | BGB SS | 9080100
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 5152680 | 10006255 | Adabor NOCS | 9804412 | Adabor NOCS | 9804412 | 201843 | 2.017%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 8362800
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 2941920
| Export to Desco at 11 KV |  |  |  |  | 6451145 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 3103380 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 6451145 | 29160900
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 31474500 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 32040750
AGARGAON 132/33KV SS | [5 empty] | 0 | 63515250
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 4590030.6748 | 7394249.1641 | Sherebanglanagar 33/11 KV SS | 7394249.1641 | Sherebanglanagar SS | 7394249.1641 | 0 | 0%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 2804218.4893
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 0 | 6091711.8229 | 10235199.4224 | Monipuripara 33/11 KV SS | 10235199.4224 | Monipuripara SS | 10235199.4224 | 0 | 0%
20 | Monipuripara-2 |  |  |  |  | 0 | 4143487.5996
| Maniknagar 230/132 kv |  |  |  |  | 0 | 17629448.5865
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 7193.04 | 12093.6675 | Maniknagar 33/11 KV SS | 11878.3003 | Maniknagar 33/11 KV SS | 11878.3003 | 215.3672 | 1.781%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 4900.6275
Shyampur 230/132 kv | [5 empty] | 0 | 12093.6675
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 19224.9 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 2420.64
[6 empty] | 0 | 21645.54
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 6451145 | 113396997.794 | 106924207.254 |  | 107102336.6891 |  | 107102336.6891 | -178129.4351 | -0.1666%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | Energy Import/Export at 11 kV voltage levels | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Import (KWh) | Energy Export (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 13 | 14
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 510000 | 753375 | Sherebanglanagar NOCS | 754605 | Sherebanglanagar NOCS | 754605 | -1230 | -0.1633%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 580000
3a | PD Betar |  | 11 | Import | 2612100427 | 74400 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 27600 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 293000 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 40000
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 0
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 1130000
TOTAL => | [5 empty] | 395000 | 1130000 | 753375 |  | 754605 |  | 754605 | -1230 | -0.1633%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [11 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month March-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month May-2023 | [13 empty] | FINAL |  |  |  |  | Date: 30.03.2023 | [5 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 9097367.1959 | 20122538.1817 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 8131672.4645 |  | North | 293298928.1144 | Tejgaon | 59103996.9445 | Tejgaon | 33009538.7975 | 29604792.2707 | 3404746.5268 | 11.5007 | North | 293298928.1144 | 170492292.74 | 41.8708 | Tejgaon | 59103996.9445 | 35166376 | 40.5008 | Tejgaon | 33009538.7975 | 20199721 | 38.8064 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 126381.9385 | [5 empty] | Kakrail | 26094458.147 | 24217993.013 | 1876465.134 | 7.7482 | [8 empty] | Kakrail | 26094458.147 | 14966655 | 42.6443 | Tejgaon | 20199721 | 302266 | 20501987 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | -80846.9863
|  |  |  | Maghbazar | 2767116.5828 |  |  |  | Moghbazar | 35006280.2911 | Moghbazar | 19191663.6958 | 19720495.0318 | -528831.3359 | -2.6816 |  |  |  |  | Moghbazar | 35006280.2911 | 19835673 | 43.3368 | Moghbazar | 19191663.6958 | 10887400 | 43.2702 | Kakrail | 14966655 | 232062 | 15198717 | A1 | Motijheel | 13861115 | 815334 | 14676449
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 13414120.4173 |  |  |  |  | Khilgaon | 15814616.5953 | 15784786.3392 | 29830.2561 | 0.18898 | [8 empty] | Khilgaon | 15814616.5953 | 8948273 | 43.4177 | Moghbazar | 10887400 | 79577 | 10966977 | A2 | Khilgaon | 8948273 | 34510 | 8982783
|  |  |  | Jigatola | 2330780.8195 |  |  |  | Satmasjid | 45715884.3454 | Satmosjid | 21874027.2652 | 20807178.2283 | 1066849.0369 | 5.1273 |  |  |  |  | Satmasjid | 45715884.3454 | 25873317 | 43.4041 | Satmosjid | 21874027.2652 | 11701525 | 46.5049 | Khilgaon | 8948273 | 34510 | 8982783 | A3 | Lalbag | 28703571 | 61891 | 28765462
|  |  |  | Paribagh | 11083339.5978 | [5 empty] | Sherebanglanagar | 23841857.0802 | 22745685.0951 | 1096171.985 | 4.8193 | [8 empty] | Sherebangla nagar | 23841857.0802 | 14171792 | 40.5592 | Satmosjid | 11701525 | 235777 | 11937302 | A4 | Kazla | 29884465 | 182467 | 30066932
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 13830210 |  |  | Dhanmondi | 50655522.9607 | Dhanmondi | 23157735.0016 | 22678079.2657 | 479655.7359 | 2.1151 |  |  |  |  | Dhanmondi | 50655522.9607 | 30161156.68 | 40.4583 | Dhanmondi | 23157735.0016 | 13489094 | 41.7512 | Sherebanglanagar | 14171792 | 119967 | 14291759 | A5 | Postogola | 9695544 | 189129 | 9884673
[11 empty] | Jhigatala | 27497787.9591 | 26819694.8074 | 678093.1517 | 2.5283 | [8 empty] | Jhigatala | 27497787.9591 | 16672062.68 | 39.3694 | Dhanmondi | 13489094 | 275350 | 13764444 | A6 | Banglabazar | 10167631 | 85969 | 10253600
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 53199529.922 | Azimpur | 19273690.4419 | 18212410.3463 | 1061280.0956 | 5.8272 |  |  |  |  | Azimpur | 53199529.922 | 30817493.06 | 42.0719 | Azimpur | 19273690.4419 | 11128395 | 42.2612 | Jhigatala | 16672062.68 | 296691.0826 | 16968753.7626 | A7 | N.Gonj (West) | 21844474 | 212619 | 22057093
|  |  |  | Dhanmondi | 13830210 | [5 empty] | Paribagh | 33925839.4802 | 33210749.529 | 715089.9511 | 2.1532 | [8 empty] | Paribagh | 33925839.4802 | 19689098.06 | 41.9643 | Azimpur | 11128395 | 83587 | 11211982 | A8 | Siddirgonj | 38393921 | 340017 | 38733938
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 21237030.7039 | 21237030.7039 |  |  | Shamoly | 49617713.6507 | Shyamoli | 18283221.4148 | 17475754.924 | 807466.4908 | 4.6205 |  |  |  |  | Shamoly | 49617713.6507 | 28638277 | 42.2822 | Shyamoli | 18283221.4148 | 10257103 | 43.8988 | Paribagh | 19689098.06 | 813621.9241 | 20502719.9841 | A9 | Bashabo | 7785628 | 21994 | 7807622
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 14597158.7767 |  |  |  |  | Adabor | 31334492.2359 | 30708326.9338 | 626165.3022 | 2.0391 | [8 empty] | Adabor | 31334492.2359 | 18381174 | 41.3388 | Shyamoli | 10257103 | 88444 | 10345547 | B1 | Narinda | 8402769 | 28248 | 8431017
|  |  |  | RAMNA | 1241185.9012 |  | Central | 267623419.9499 | Lalbagh | 77810301.553 | Lalbagh | 36512406.1293 | 29413211.3833 | 7099194.746 | 24.1361 | Central | 267623419.9499 | 170373738 | 36.3383 | Lalbagh | 77810301.553 | 59529325 | 23.4943 | Lalbagh | 36512406.1293 | 28703571 | 21.3868 | Adabor | 18381174 | 249448 | 18630622 | B2 | Maniknagar | 12998706 | 71180 | 13069886
|  |  |  | Kakrail | 1765948.0868 | [5 empty] | Kamrangirchar | 41297895.4236 | 36459807.8636 | 4838087.56 | 13.2696 | [8 empty] | Kamrangirchar | 41297895.4236 | 30825754 | 25.3576 | Lalbagh | 28703571 | 61891 | 28765462 | B3 | Jurain | 20332610 | 238128 | 20570738
|  |  |  | Paribagh | 11590024.7886 |  |  |  | Ramna | 46016210.9129 | Ramna | 27950585.9269 | 23660754.4382 | 4289831.4887 | 18.1306 |  |  |  |  | Ramna | 46016210.9129 | 26201928 | 43.0594 | Ramna | 27950585.9269 | 16257493 | 41.8349 | Kamrangirchar | 30825754 | 145798 | 30971552 | B4 | Shyampur | 68397934 | 310179 | 68708113
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 4010755.5343 |  |  |  |  | Rajarbagh | 18065624.986 | 18029244.0029 | 36380.9831 | 0.20179 | [8 empty] | Rajarbagh | 18065624.986 | 9944435 | 44.9538 | Ramna | 16257493 | 360414 | 16617907 | B5 | Swamibag | 7953821 | 51563 | 8005384
|  |  |  | Kakrail | 258497.9936 |  |  |  | Bashabo | 38032707.6314 | Bashabo | 14134545.9205 | 14288466.1321 | -153920.2116 | -1.0772 |  |  |  |  | Bashabo | 38032707.6314 | 21433127 | 43.6455 | Bashabo | 14134545.9205 | 7785628 | 44.9177 | Rajarbagh | 9944435 | 129781 | 10074216 | B6 | Bangshal | 12738507 | 164889 | 12903396
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 23898161.7109 | 23814227.1875 | 83934.5235 | 0.35246 | [8 empty] | Bonossri | 23898161.7109 | 13647499 | 42.8931 | Bashabo | 7785628 | 21994 | 7807622 | B7 | N.Gonj (East) | 22399809 | 326607 | 22726416
|  |  |  | Shere Bangla Nagar | 3752257.5407 |  |  |  | Motijheel | 40418336.2389 | Motijheel | 22370326.0361 | 20610444.9515 | 1759881.0847 | 8.5388 |  |  |  |  | Motijheel | 40418336.2389 | 23946630 | 40.7531 | Motijheel | 22370326.0361 | 13861115 | 38.0379 | Bnossri | 13647499 | 71095 | 13718594 | B8 | Fateullah | 24703083 | 607298 | 25310381
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1065434.2731 | 7641416.1132 |  |  |  |  | Mughdapara | 18048010.2028 | 17877686.0067 | 170324.1962 | 0.95272 | [8 empty] | Mughdapara | 18048010.2028 | 10085515 | 44.1184 | Motijheel | 13861115 | 815334 | 14676449 | B9 | Mugdapara | 10085515 | 139755 | 10225270
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 36137114.8898 | Banglabazar | 16832238.2088 | 15542259.1155 | 1289979.0933 | 8.2998 |  |  |  |  | Banglabazar | 36137114.8898 | 22906138 | 36.6133 | Banglabazar | 16832238.2088 | 10167631 | 39.5943 | Mughdapara | 10085515 | 139755 | 10225270 | C1 | Tejgaon | 20199721 | 302266 | 20501987
|  |  |  | Narinda | 409490.3581 | [5 empty] | Bongshal | 19304876.681 | 18238230.678 | 1066646.003 | 5.8484 | [8 empty] | Bongshal | 19304876.681 | 12738507 | 34.014 | Banglabazar | 10167631 | 85969 | 10253600 | C2 | Satmasjid | 11701525 | 235777 | 11937302
|  |  |  | Motijheel | 737447.4233 |  |  |  | Narinda | 29208748.7239 | Narinda | 14569881.1136 | 13875342.0353 | 694539.0783 | 5.0056 |  |  |  |  | Narinda | 29208748.7239 | 16356590 | 44.0011 | Narinda | 14569881.1136 | 8402769 | 42.3278 | Bongshal | 12738507 | 164889 | 12903396 | C3 | Paribagh | 19689098.06 | 813621.9241 | 20502719.9841
|  |  |  | RAMNA | 5429044.0587 | [5 empty] | Swamibagh | 14638867.6103 | 14066843.8218 | 572023.7885 | 4.0665 | [8 empty] | Swamibagh | 14638867.6103 | 7953821 | 45.6664 | Narinda | 8402769 | 28248 | 8431017 | C6 | Kakrail | 14966655 | 232062 | 15198717
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 439205519.0619 | Kazla | 61446257.348 | Kazla | 41076724.8443 | 32810065.324 | 8266659.5203 | 25.1955 | South | 439205519.0619 | 342142704 | 22.0996 | Kazla | 61446257.348 | 42883171 | 30.2103 | Kazla | 41076724.8443 | 29884465 | 27.2472 | Swamibagh | 7953821 | 51563 | 8005384 | D1 | Moghbazar | 10887400 | 79577 | 10966977
|  | Khillgaon 33/11KV S/S |  | Kakrail | 80846.9863 | 6240060 |  |  |  |  | Maniknagar | 20369532.5037 | 19204304.2311 | 1165228.2725 | 6.0675 | [8 empty] | Maniknagar | 20369532.5037 | 12998706 | 36.1855 | Kazla | 29884465 | 182467 | 30066932 | D2 | Dhanmondi | 13489094 | 275350 | 13764444
|  |  |  | Khilgaon | 241.3343 |  |  |  | Shyampur | 95026455.4313 | Shyampur | 71611732.1812 | 57974819.9398 | 13636912.2414 | 23.5221 |  |  |  |  | Shyampur | 95026455.4313 | 83903077 | 11.7056 | Shyampur | 71611732.1812 | 68397934 | 4.4878 | Maniknagar | 12998706 | 71180 | 13069886 | D3 | Ramna | 16257493 | 360414 | 16617907
| 9 |  |  | Maghbazaar | 126229.899 | [5 empty] | Matuail | 23414723.2501 | 22215978.8776 | 1198744.3725 | 5.3959 | [8 empty] | Matuail | 23414723.2501 | 15505143 | 33.7804 | Shyampur | 68397934 | 310179 | 68708113 | D4 | Shyamoli | 10257103 | 88444 | 10345547
|  |  |  | Rajarbagh | 6032741.7805 |  |  |  | Postogola | 45218645.6584 | Postogola | 15678261.2905 | 14723061.8823 | 955199.4082 | 6.4878 |  |  |  |  | Postogola | 45218645.6584 | 30028154 | 33.5934 | Postogola | 15678261.2905 | 9695544 | 38.1593 | Matuail | 15505143 | 265847 | 15770990 | D5 | Shere b.nagar | 14171792 | 119967 | 14291759
| 10 | Goran 33/11KV S/S |  | Bashabo | 1411235.5236 | 9407041.253 |  |  |  |  | Jurain | 29540384.3679 | 27924599.9285 | 1615784.4394 | 5.7862 | [8 empty] | Jurain | 29540384.3679 | 20332610 | 31.1701 | Postogola | 9695544 | 189129 | 9884673 | D6 | Rajarbag | 9944435 | 129781 | 10074216
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 64055161.0882 | Narayangonj-West | 31820650.1222 | 28027470.8878 | 3793179.2344 | 13.5338 |  |  |  |  | Narayangonj | 64055161.0882 | 44244283 | 30.9278 | Narayangonj- West | 31820650.1222 | 21844474 | 31.3513 | Jurain | 20332610 | 238128 | 20570738 | D8 | Jhigatala | 16672062.68 | 296691.0826 | 16968753.7626
|  |  |  | Banosree | 7995805.7294 | [5 empty] | Narayangonj-East | 32234510.966 | 28588513.8298 | 3645997.1362 | 12.7534 | [8 empty] | Narayangonj- East | 32234510.966 | 22399809 | 30.5099 | Narayangonj-West | 21844474 | 212619 | 22057093 | D9 | Azimpur | 11128395 | 83587 | 11211982
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 11043836.3832 | 14028480 |  |  | Demra | 73578139.5617 | Demra | 23689068.4661 | 22270658.3692 | 1418410.0969 | 6.369 |  |  |  |  | Damra | 73578139.5617 | 53766885 | 26.9255 | Damra | 23689068.4661 | 15372964 | 35.1052 | Narayangonj-East | 22399809 | 326607 | 22726416 | E1 | Demra | 15372964 | 297748 | 15670712
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 49889071.0956 | 42716034.5555 | 7173036.5401 | 16.7924 | [8 empty] | Siddhirgonj | 49889071.0956 | 38393921 | 23.0414 | Damra | 15372964 | 297748 | 15670712 | E2 | Matuail | 15505143 | 265847 | 15770990
|  |  |  | Bashabo | 2984643.6168 |  |  |  | Fatullah | 99880859.9743 | Fatulla | 33687593.9843 | 29428164.8729 | 4259429.1114 | 14.474 |  |  |  |  | Fatullah | 99880859.9743 | 87317134 | 12.5787 | Fatulla | 33687593.9843 | 24703083 | 26.6701 | Siddhirgonj | 38393921 | 340017 | 38733938 | E3 | Sytalakha | 62614051 | 309617 | 62923668
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 19243178.2478 |  |  |  |  | Shitalakha | 66193265.9901 | 61408904.565 | 4784361.4251 | 7.791 | [8 empty] | Sytalakhya | 66193265.9901 | 62614051 | 5.4072 | Fatulla | 24703083 | 607298 | 25310381 | F1 | Kamrangirchar | 30825754 | 145798 | 30971552
|  |  |  | Shyamoli | 2720091.9688 |  | TOTAL=> | 1000127867.1263 | TOTAL=> | 1000127867.1263 | TOTAL=> | 1000127867.1263 | 915155040.664 | 84972826.4624 | 9.2851 |  | 1000127867.1263 | 683008734.74 |  | TOTAL=> | 1000127867.1263 | 683008734.74 |  | Total=> | 1000127867.1263 | 683008734.74 | 31.7079 | Shitalokko | 62614051 | 309617 | 62923668 | F2 | Banosree | 13647499 | 71095 | 13718594
|  |  |  | Shere Bangla Nagar | 0 | [22 empty] | Total => | 683008734.74 | 8238868.0068 | 691247602.7468 | G1 | Adabor | 18381174 | 249448 | 18630622
|  |  |  | Satmosjid | 9990298.011 | [14 empty] | 132KV Import => |  |  |  |  | 910675196.83 | [7 empty] | Total => | 683008734.74 | 8238868.0068 | 691247602.7468
|  |  |  | Dhanmondi NOCS | 6532788.268 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 1006112600.794 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 1000127867.1263
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 1000127867.1263 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | -9.8227
| 13 | Japan garden Building |  | Adabor | 1366020 | 1366020 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.59484 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 683008734.74
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 5984733.6677 | [8 empty] | System loss at 132kv level => |  |  |  |  | 24.9997
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 1441842.1484 | 1441842.1484
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 9804412 | 10559017
| 16 |  |  | Shere Bangla Nagar | 754605
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 25921734.6186 | 25921734.6186
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1250534.8854 | 10588018.9139
|  |  |  | Lalbagh | 9337484.0285
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 7398355.5645
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 7398355.5645
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 3072130.4931 | 10706555.7915
|  |  |  | Rajarbaghl | 2912134.6589
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 4722290.6395 | 4722290.6395
|  | Banshal 33/11 KV S/S |  | Bangshal | 6961259.0304 | 9460530.4625
|  |  |  | Banglabazar | 1353751.6158
|  |  |  | Narinda | 1145519.8164
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 11326067.9767 | 15206400
|  |  |  | Shamoly | 2988981.0408
|  |  |  | Satmosjit | 891350.9825
|  | Azimpur 33/11 KV |  | jigatola | 253340.1998 | 15802448.6906
|  |  |  | Azimpur | 13322748.4543
|  |  |  | RAMNA | 1578207.9127
|  |  |  | Paribagh | 648152.1238
|  | T&T 33/11 KV |  | Kakrail | 3269238.3163 | 11037667.2737
|  |  |  | Mogbazar | 6105444.0851
|  |  |  | Khilgaon | 1662984.8723
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 3516772.3495 | 7394249.1641
|  |  |  | Shamoly | 3225043.5825
|  |  |  | Tejgaon | 652433.232
|  |  |  | Satmosjit | 0
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 23128995.7056 | 25555207.0633
|  |  |  | Kamrangirchar | 2426211.3577
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 4294021.9471 | 5593471.2
|  |  |  | Kakrail | 1299449.2529
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1191754.0645
|  |  |  | Shere Bangla Nagar | 1769725.8951
|  |  |  | Shamoly | 9349104.8226
|  |  |  | Satmosjit | 5482449.4177
|  | Banasree 33/11SS |  | Khilgaon | 2380050.8737
|  |  |  | Bansree | 12097325.9641 | 12097325.9641
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 727503.1317 | 18797648
|  |  |  | Bashabo | 7887172.0058
|  |  |  | Mugdapara | 5587177.1466
|  |  |  | Maniknagor | 4595795.7159
|  | DMC |  | Bangshal | 2847088.0097
|  |  |  | RAMNA | 2067003.4309 | 5009929.1941
|  |  |  | Lalbagh | 2942925.7632
|  | Green Road Dormatory |  | Paribagh | 7801860.469
|  |  |  | Shere Bangla Nagar | 5368229.531
|  | BSMMU 33/11KV S/S |  | Kakrail | 1940201.2053
|  |  |  | Paribagh | 2802462.5008
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 8837992.2592
|  |  |  | Satmasjid | 5509928.8541
|  | Dhaka University 33/11 KV SS |  | RAMNA | 1917564.9326
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 6392802.8391
|  |  |  | Kakrail | 853994.1863
|  |  |  | Tejgaon | 2988402.3971
|  | BGB 33/11 KV SS |  | Kamrangirchar | 6264832.3855
|  |  |  | Jigatola | 5206353.9812
|  |  |  | Azimpur | 4700407.1021
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2161081.9864
|  | BB Avenue 33/11 KV SS |  | Narinda | 2105904.5733
|  |  |  | Ramna | 4251830.6142
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 18265470.8102
|  |  |  | Dhanmondi | 1602982.669
|  | Ispahani 33/11 KV SS |  | Moghbazar | 2794517.5644
|  |  |  | Kakrail | 2806624.2841
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 6685117.0618
|  |  |  | Total=> | 461987145.5674 | 300932326.5586
NORTH ZONE TOTAL=>
|  | NOCS |  | 461987145.5674 |  | 200857461
|  | diff |  |  | -461987145.5674
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 6492000
|  |  |  | RAMNA | 20212.3186
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 6471787.6814
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 492385.8425 | 16443803.7839
|  |  |  | Swamibagh | 5238868.4174
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 10712549.524
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 10369585.1424
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 10369585.1424
| 4 | Maderteck 33/11KV S/S |  | Banosree | 3805030.0175 | 17478317.1945
|  |  |  | Bashabo | 1851494.7743
|  |  |  | Maniknagar | 1138433.534
|  |  |  | Mugdapara | 10683358.8687
| 5 | Kazla 33/11KV S/S |  | Matual | 837095.6004 | 38195639.9748
|  |  |  | Jurain | 8648814.3053
|  |  |  | Swamibagh | 1962979.7252
|  |  |  | Maniknagar | 1912634.1716
|  |  |  | Shyampur | 3092469.9692
|  |  |  | Kazla | 21741646.2032
|  | Shyampur 132/11KV S/S |  | Shyampur | 32318976.0687 | 32893979.5386
|  |  |  | Fatullah. | 575003.4699
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 26231606.4542
|  |  |  | Fatullah | 1108880.0883
|  |  |  | Shyampur | 25122726.3659
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 5559018.6808 | 17968062.8567
|  |  |  | Jurain | 12409044.1758
| 8 | Postogola 33/11KV S/S |  | Jurain | 8482525.8868 | 17630370
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 9147844.1132
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 12939140.354 | 14222707.7973
|  |  |  | Narayanganj (West) | 1590508.2027
|  |  |  | Shitalakhy | 1283567.4432
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 989646.7653 | 15037355.2436
|  |  |  | Shitalakhy | 9772495.2533
|  |  |  | Narayanganj (West) | 3043060.7047
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 1232152.5203
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 1189560.6195
| 11 |  |  | Narayanganj (West) | 14862031.5785 | 16051592.198
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 14465942.2468 | 14465942.2468
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 13698420.7618 | 13698420.7618
|  |  |  | Matuail | 424399.7103
| 14 | Sarulia 33/11KV S/S |  | Demra | 15769069.8336 | 18155587.9103
|  |  |  | Matuail | 2386518.0767
|  | Demra 33/11KV S/S |  | Matuail | 7279500.629 | 22647233.3709
| 15 |  |  | Demra | 2481057.3956
|  |  |  | Siddhirganj | 12886675.3463
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1256708.9709
| 16 |  |  | Narayanganj (East) | 5210440.6901 | 13686637.3522
|  |  |  | Narayanganj (West) | 8476196.6621
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 3848852.9741 | 17488342.8955
|  |  |  | Narayanganj (East) | 13639489.9214
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 4644322.6476 | 17126297.0274
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 230570.6792
|  |  |  | Fatullah | 3359655.0807
|  |  |  | Matuail | 8891748.62
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 3058393 | 3058393
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 1155307.5753
|  |  |  | Maniknagar | 11074975.6644 | 11074975.6644
|  | IG Gate 33/11 kv |  | Swamibagh | 6203087.8974 | 17842406.5253
|  |  |  | Banglabazr | 5108901.4507
|  |  |  | Postogola | 6530417.1772
|  | Motijil 33/11kv |  | kamlapur | 6002171.151 | 6557051.7104
|  |  |  | RAMNA | 554880.5594
|  | Mitford 33/11kv |  | Banshal | 8431095.3679 | 9534096
|  |  |  | Lalbagh | 1103000.6321
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 5287970.4174 | 13186154.0225
|  |  |  | Fatullah | 4302722.9914
|  |  |  | Matuail | 3595460.6138
|  | MI CEMENT |  | Shitalakhy | 10819680 | 10819680
|  | Dapa 33/11 kV |  | Fatullah | 11402192 | 11402192
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7750610.9416 | 16588643.6824
|  |  |  | Siddhirganj | 8838032.7408
|  | Amulia 33/11 KV SS |  | Mugdapara | 1777474.1875 | 7216415.4244
|  |  |  | Demra | 5438941.2369
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 11965882.9205
|  | P&T 33/11 KV SS |  | Motijeel | 3741992.1559
|  |  |  | RAMNA | 3524503.7583
|  |  |  | Rajarbagh | 3055165.7825
|  | Kazla 132/33 KV SS |  | Kazla | 19335078.6411
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 6065582.7642
|  |  |  | Motijeel | 2340533.7777
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 25614825.2624
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 3076393.8468
|  |  |  | Swamibagh | 1233931.5704
|  |  |  | Narinda | 196416.8418
|  |  |  | Total=> | 538140721.5589 | 418356238.6713
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 538140721.5589
| Diff zone&Nocs |  |  |  | -25541479.2338
|  |  |  | Diff= | 0

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 65.069 | 48.725 |  | 16.344 | 180000 | 2941920 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Previous | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8574.056 | 8527.596 |  | 46.46 | 180000 | 8362800 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.55 | 995.68 | 0.13
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6458.759 | 6430.133 |  | 28.626 | 180000 | 5152680 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9605.8 | 9633.08 | 27.28
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4072.73 | 4319.26 | 246.53
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 3311 | 3311 |  | 0 | 8000 | 0 | 0 | #DIV/0! |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 50477.94 | 51326.05 | 848.11
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 41176.67 | 41632.55 | 455.88
03 |  | 11 KV Bashir Uddin |  | 74819925 | 10207.725 | 10034.225 |  | 177.8375 | 16000 | 2845400 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 1946.92 | 1991.3 | 44.38
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 7899.33 | 8076.21 | 176.88
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1111.6 | 1082.77 |  | 29.5507 | 40000 | 1182030 | 0 | 1 |  | #DIV/0! | 0 |  | 0 |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9296.06 | 9341.2 | 45.14
05 |  | 11 KV Lalkuthy |  | DHK15018 | 995.15 | 995.15 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9446.45 | 9387.34 |  | 60.5878 | 40000 | 2423510 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [6 empty] | 0
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 51326.05 | 51055.21 |  | 277.611 | 8000 | 2220888 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  |  | 0
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8076.21 | 8022.92 |  | 54.6222 | 40000 | 2184890 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  |  | 0
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 1991.3 | 1978.23 |  | 13.3967 | 40000 | 535870 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  |  | 0
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  |  | 0
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.691 | 3273.686 |  | 0.005125 | 40000 | 205 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  |  | 0
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9633.08 | 9628.58 |  | 4.6125 | 40000 | 184500 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  |  | 0
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9341.2 | 9327.58 |  | 13.9605 | 40000 | 558420 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  |  | 0
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4319.26 | 4246.2 |  | 74.8865 | 40000 | 2995460 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  |  | 0
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.68 | 995.65 |  | 0.03075 | 40000 | 1230 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 41632.55 | 41495.43 |  | 140.548 | 8000 | 1124384 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 6451145 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 10006255 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 33009538.7975 | 33009538.7975 | 0 | 0
Kakrail | 25376613.52 | 26094458.147 | -717844.627 | -2.7509 | DPH-1 Fdr Add To Kakrail NOCS
Moghbazar | 19786757.6698 | 19191663.6958 | 595093.974 | 3.1008 | Ullon 132/33 Kv 33 kv Fdr Adjustment and Loss Fix
Khilgaon | 15814616.5953 | 15814616.5953 | 0 | 0
Satmosjid | 21886045.2652 | 21874027.2652 | 12018 | 0.054942
Sherebanglanagar | 23841857.0802 | 23841857.0802 | 0 | 0
Dhanmondi | 23157735.0016 | 23157735.0016 | 0 | 0
Jhigatala | 27497787.9591 | 27497787.9591 | 0 | 0
Azimpur | 19273690.4419 | 19273690.4419 | 0 | 0
Paribagh | 33925839.4802 | 33925839.4802 | 0 | 0
Shyamoli | 18271203.4148 | 18283221.4148 | -12018 | -0.065732
Adabor | 31334492.2359 | 31334492.2359 | 0 | 0
Lalbagh | 36512406.1293 | 36512406.1293 | 0 | 0
Kamrangirchar | 41297895.4236 | 41297895.4236 | 0 | 0
Ramna | 27950585.9269 | 27950585.9269 | 0 | 0
Rajarbagh | 18065624.986 | 18065624.986 | 0 | 0
Bashabo | 14134545.9205 | 14134545.9205 | 0 | 0
Bonoseeri | 24098580.2967 | 23898161.7109 | 200418.5858 | 0.83864 | Bonosree 33/11 Loss Fix Reading Adjusted
Motijheel | 22370326.0361 | 22370326.0361 | 0 | 0
Mughdapara | 18496280.9073 | 18048010.2028 | 448270.7045 | 2.4838 | Madartek 33/11 Loss Fix and Green Model Town Reading Change
Banglabazar | 16832238.2088 | 16832238.2088 | 0 | 0
Bongshal | 19304876.681 | 19304876.681 | 0 | 0
Narinda | 14569881.1136 | 14569881.1136 | 0 | 0
Swamibagh | 14638867.6103 | 14638867.6103 | 0 | 0
Kazla | 41076724.8443 | 41076724.8443 | 0 | 0
Maniknagar | 20369532.5037 | 20369532.5037 | 0 | 0
Shyampur | 71611732.1812 | 71611732.1812 | 0 | 0
Matuail | 23414723.2501 | 23414723.2501 | 0 | 0
Postogola | 15678261.2905 | 15678261.2905 | 0 | 0
Jurain | 29540384.3679 | 29540384.3679 | 0 | 0
Narayangonj-West | 31820650.1222 | 31820650.1222 | 0 | 0
Narayangonj-East | 32234510.966 | 32234510.966 | 0 | 0
Damra | 23689068.4661 | 23689068.4661 | 0 | 0
Siddhirgonj | 49889071.0956 | 49889071.0956 | 0 | 0
Fatulla | 33687593.9843 | 33687593.9843 | 0 | 0
Shitalakha | 66193265.9901 | 66193265.9901 | 0 | 0
TOTAL=> | 1000653805.7636 | 1000127867.1263 | 525938.6373 | 0.052587

## %Loss
Source 132 kv Tariff Point
Source 33 kv Tariff Point
Source 132 kv NON Tariff Point
Source 33 kv NON Tariff Point
[135 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
IMPORT
|  | NORTH | [171 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[134 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
| 1 | Moghbazar 132/33/11KV S/S | 1 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
| 2 | Moghbazar 33/11KV S/S | 2 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
| 3 | Green Road 33/11KV S/S | 3 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
| 4 | Lalmatia 33/11KV S/S | 4 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
| 5 | Tejgoan 33/11KV S/S | 5 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
| 6 | Moghbazar T&T 33/11 KV, | 6 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
| 7 | Dhanmondi 132/33/11KV S/S | 7 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
| 8 | Dhanmondi 33/11KV S/S | 8 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
| 9 | Kawranbazar 33/11KV S/S | 9 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
| 10 | New Ramna 33/11KV S/S | 10 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
| 11 | Ullon 132/33/11KV S/S | 11 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
| 12 | Ullon local 33/11KV S/S | 12 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
| 13 | Kakrail 33/11KV S/S | 13 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
| 14 | Khillgaon 33/11KV S/S | 14 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
| 15 | Goran 33/11KV S/S | 15 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
| 16 | Taltola 33/11KV S/S | 16 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
| 17 | Satmasjid 33/11KV S/S | 17 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
| 18 | Jigatola OLD 33/11KV S/S | 18 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
| 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| 20 | Kamrangirchar 132/33/11KV S/S | 20 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
| 21 | Kamrangirchar 33/11KV S/S | 21 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
| 22 | Lalbagh OLD 33/11KV S/S | 22 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
Narinda | 23 | Banshal 33/11KV S/S | 23 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
| 24 | Japan Garden 33/11 KV, | 24 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
| 25 | Azimpur 33/11 KV, | 25 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
| 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
| 27 | LALBAGH 132/33 KV S/S | 27 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
| 28 | LALBAGH 33/11 KV S/S | 28 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
| 29 | Asad Gate 33/11 KV S/S | 29 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
| 30 | Shatmasjid 132/33 KV S/S | 30 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
Madartek | 31 | Banasree 33/11 SS | 31 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
Maniknagar | 32 | Mugdhapara Hospital | 32 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
| 33 | DMC | 33 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
| 34 | Green Road Dormatory 33/11 SS | 34 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
| 35 | BSMMU 33/11KV S/S | 35 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
| 36 | Dhaka Uddyan 33/11 KV S/S | 36 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
| 37 | Dhaka University 132/33 KV S/S | 37 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
| 38 | Dhaka University 33/11 KV S/S | 38 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
| 39 | Monipuripara 33/11 KV S/S | 39 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
Not Clear | 40 | BGB 33/11 KV S/S | 40 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
| 41 | BB Aveneu 33/11 KV S/S | 41 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
| 42 | Jigatola 132/33 KV S/S | 42 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
| 43 | Jigatola New 33/11 KV S/S | 43 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
| 44 | Ispahani 33/11 KV S/S |  | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
| 45 | Kamrangirchar-2 33/11 KV S/S |  | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
| 1 | Bangabhaban 132/11KV S/S | 1 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
| 2 | Narinda 132/33KV S/S | 2 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
| 3 | Narinda 33/11KV S/S | 3 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
| 4 | Kumertuly 33/11KV S/S | 4 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
| 5 | Maniknagar 132/33/11KV S/S | 5 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
| 6 | Maniknagar 33/11KV S/S | 26 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
| 7 | Madarteck 132/33KV S/S | 6 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
| 8 | Madarteck 33/11KV S/S | 7 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
| 9 | Kazla 132/133 KV SS | 39 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
| 10 | Kazla 33/11KV S/S | 8 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
| 11 | Shyampur 132/33KV S/S | 9 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
| 12 | Shyampur 33/11KV S/S | 10 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
| 13 | Shyampur BISIC 33/11KV S/S | 11 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
| 14 | Postogola 132/33 KV S/S | 43 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
| 15 | Postogola 33/11KV S/S | 12 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
| 16 | Fatullah Old 33/11KV S/S | 13 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
| 17 | Sitalakhya 132/33KV S/S | 14 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
| 18 | Sitalakhya 33/11KV S/S | 15 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
| 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
|  | Char Syedpur 33/11KV S/S | 17 | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
| 20 | Siddhirganj 132/33/11KV S/S | 18 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
| 21 | Siddhirganj 33/11KV S/S | 19 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
| 22 | Demra 33/11KV S/S | 20 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
| 23 | Mondalpara 33/11KV S/S | 21 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
| 24 | Khanpur 33/11KV S/S | 22 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
| 25 | Matuail 132/33 KV S/S | 24 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
| 26 | Matuail 33/11KV S/S | 23 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
| 27 | Sarulia 33/11KV S/S | 25 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
| 28 | IG Gate GIS 33/11 kV | 27 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
| 29 | Motijheel Old 33/11 kV | 28 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
| 30 | Mitford 33/11 kV | 29 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
| 31 | Biddyut Bhaban 33/11 KV | 30 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
| 32 | Nandalalpur 33/11 kV | 31 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
| 33 | Dapa 33/11 kV | 32 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
| 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
| 35 | Amulia 33/11 kv | 34 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
| 36 | New Fatullah 132/33 KV SS | 35 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
| 37 | New Fatullah 33/11 KV SS | 36 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
| 38 | P & T 33/11 KV SS | 37 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
| 39 | Motijheel 132/33 KV SS | 38 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
| 40 | Motijheel 33/11 KV SS (new) | 39 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| 41 | Kamalapur Railway 33/11 KV SS | 40 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
| 42 | Char Syedpur 132/33KV S/S | 41 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
| 43 | Char Syedpur 33/11 KV S/S New | 42 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
| 44 | MI CEMENT 132/33 kV

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
ULLON 132 KV SIDE
| 132 KV DHANMONDI-1 CKT (IMP) | 132 | IMPORT |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-1 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-2 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000 | 0
| 132 KV DHANMONDI-2 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000
| 132 KV DHANMONDI-3 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000
[8 empty] | Total Import/Export |  | 0 | 0
[9 empty] | Net Total | 69540000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 | 132 |  | SIEM0480 | 1 | 1632756 | 1632756 | 0 | 1000 | 0
| 132 kV Dhaka University | 132 |  | SIEM0480 | 1 | 48558 | 59905 | 11347 | 1000 | 11347000
3 | 132 kV Dhaka University | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 | 132 |  | SIEM0481 | 1 | 2042005 | 2071385 | 29380 | 1000 | 29380000
8 | 132 kV Ullon Circuit-3 | 132 |  | SIEM0484 | 1 | 2799000 | 2827813 | 28813 | 1000 | 28813000
[8 empty] | Total Import/Export |  | 69540000 | 0
[8 empty] | Net Total |  | 69540000
DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 KV Dhaka University (Export) | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) | 132 |  |  | 1 | 48558 | 59905 | 11347 | 1000 |  | 11347000
[9 empty] | Total |  | 11347000
DHANMONDI 132 KV SIDE
4 | 132/33kV, 50/75 MVA GT-4 (HV) | 132 | NET IMPORT | SIEM0487 | 1 | 837255 | 849792 | 12537 | 1000 |  | 12537000
5 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | SIEM0496 | 1 | 1436120 | 1445679 | 9559 | 2000 |  | 19118000
9 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | SIEM0493 | 1 | 1311215 | 1317896 | 6681 | 2000 |  | 13362000
10 | 132/33kV, 80/120 MVA GT-3 (HV) | 132 |  | SIEM0497 | 1 | 1261225 | 1273558 | 12333 | 2000 |  | 24666000
[9 empty] | Total |  | 69683000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV DHANMONDI-3 CKT(EXP) |  | 69683000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 69683000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 69683000 |  | 132/33 kv GT LV Side |  | 69967200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -284200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.4078%
| 132 KV TOTAL IMPORT |  | 69683000
33 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2157.9 | 2184.48 | 26.58 | 720000 | 19137600
12 | 132/33 kV GT-2 Incoming | 33 |  | BD001818 | 1 | 2140.12 | 2158.72 | 18.6 | 720000 | 13392000
17 | 132/33 kV GT-3 Incoming | 33 |  | BD001863 | 1 | 1829.88 | 1864.35 | 34.47 | 720000 | 24818400
24 | 132/33 kV GT-4 Incoming | 33 |  | BD001916 | 1 | 1736.03 | 1762.32 | 26.29 | 480000 | 12619200
[9 empty] | Total | 69967200 |  | 0
DHANMONDI 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [10 empty] | 14573212.3246 | Dhanmondi 33/11 kv ss | 0.43195 | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 | 33 |  | BD001861 | 1 | 1997.28 | 2024.03 | 26.75 | 240000 |  | 6420000 | 6424413.8049 |  |  |  |  | 33/11 kV 20/28 MVA T-1 | 6424413.8049 | 5833111.3769 | 591302.428 | 10.137 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 |  | BD001892 | 1 | 2282.03 | 2315.96 | 33.93 | 240000 |  | 8143200 | 8148798.5197 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 8148798.5197 | 8491511.6627 | -342713.143 | -4.0359 | OK
| 33 KV Feeders | [7 empty] | Total |  | 14563200 | 14573212.3246 |  |  |  |  | 33 KV Feeders | 14573212.3246 | 14324623.0396 | 248589.285 | 1.7354 | OK
5 | New Ramna Circuit-1 | 33 |  | BD001919 | 1 | 1420.28 | 1435.41 | 15.13 | 240000 |  | 3631200 | 3633696.4811 |  | 6083379.502 | New Ramna 33/11 kv ss | 2.0966 | New Ramna Circuit-1 | 3633696.4811 | 3287579.0346 | 346117.4465 | 10.528 | OK
8 | Kakrail Circuit-1 | 33 |  | BD001825 | 1 | 761.21 | 782.32 | 21.11 | 240000 |  | 5066400 | 5069883.1933 |  |  |  |  | Kakrail Circuit-1 | 5069883.1933 | 4509914.848 | 559968.3453 | 12.4164 | OK
9 | Kawran Bazar Circuit-1 | 33 |  | BD001820 | 1 | 1794.62 | 1811.32 | 16.7 | 240000 |  | 4008000 | 4010755.5343 |  | 10706555.7915 | Kakrail 33/11 kv ss | 1.0363 | Kawran Bazar Circuit-1 | 4010755.5343 | 3635788.6474 | 374966.8868 | 10.3132 | OK
10 | New Ramna Circuit-2 | 33 |  | BD001816 | 1 | 1154.36 | 1164.56 | 10.2 | 240000 |  | 2448000 | 2449683.0209 |  |  |  |  | New Ramna Circuit-2 | 2449683.0209 | 1772266.8572 | 677416.1637 | 38.2231 | OK
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 |  | 0 | 0 |  | 4010755.5343 | Kawran Bazar 33/11 kv ss | -0.31753 | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder | 33 |  | BD001840 | 1 | 365.9 | 377.52 | 11.62 | 240000 |  | 2788800 | 2790717.3239 |  |  |  |  | DMC Hospital Feeder | 2790717.3239 | 0 | 2790717.3239 | #DIV/0! | #DIV/0!
15 | Green Road Circuit-2 (U/G) | 33 |  | BD001918 | 1 | 2001.34 | 2031.88 | 30.54 | 240000 |  | 7329600 | 7334639.1627 |  | 2790717.3239 | DMC Hospital 33/11 kv ss | 0.27387 | Green Road Circuit-2 (U/G) | 7334639.1627 | 9382447.9825 | -2047808.8198 | -21.826 | OK
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1542.04 | 1565.51 | 23.47 | 240000 |  | 5632800 | 5636672.5982 |  |  |  |  | Kakrail Circuit-2 | 5636672.5982 | 5040634.3269 | 596038.2713 | 11.8247 | OK
18 | BSMMU Hospital Circuit-1 | 33 |  | BD001920 | 1 | 664.59 | 679.62 | 15.03 | 240000 |  | 3607200 | 3609679.9809 |  | 14297022.5722 | Green Road 33/11 kv ss | 1.8105 | BSMMU Hospital Circuit-1 | 3609679.9809 | 3395644.0868 | 214035.894 | 6.3032 | OK
19 | Azimpur Circuit-1 | 33 |  | BD001822 | 1 | 1872.34 | 1906.63 | 34.29 | 240000 |  | 8229600 | 8235257.9204 |  |  |  |  | Azimpur Circuit-1 | 8235257.9204 | 8023229.7695 | 212028.1509 | 2.6427 | OK
20 | Azimpur Circuit-2 | 33 |  | BD001857 | 1 | 1786.24 | 1804.37 | 18.13 | 240000 |  | 4351200 | 4354191.4872 |  | 4892161.0918 | BSMMU 33/11 kv ss | 0.65778 | Azimpur Circuit-2 | 4354191.4872 | 7780683.7633 | -3426492.2761 | -44.0384 | CHECK
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 134.4 | 139.74 | 5.34 | 240000 |  | 1281600 | 1282481.111 |  |  |  |  | BSMMU Hospital Circuit-2 | 1282481.111 | 1061438.9578 | 221042.1531 | 20.8248 | OK
23 | Green Road Circuit-1 | 33 |  | BD001865 | 1 | 1318.74 | 1347.73 | 28.99 | 240000 |  | 6957600 | 6962383.4095 |  | 12589449.4076 | Azimpur 33/11 kv ss | 1.9396 | Green Road Circuit-1 | 6962383.4095 | 7334014.8806 | -371631.4711 | -5.0672 | OK
26 | 33/0.4 kV, 500 kVA AT-1 | 0.4 |  | 84.2659 | 1 | 310143 | 311229 | 1086 | 10 |  | 10860 | 10867.4663 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 10867.4663 | 16509.9385 | -5642.4722 | -34.1762 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 |  | 84.2673 | 1 | 477381 | 478688 | 1307 | 10 |  | 13070 | 13078.9857 |  |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 13078.9857 | 6423.867 | 6655.1187 | 103.5999 | FAULT
[9 empty] | Total |  | 55355930 | 55393987.6754 | [5 empty] | 55393987.6754 | 55246576.9604 | 147410.715 | 0.26682 | OK
[8 empty] | Grand Total |  | 69967200 | 69919130 | 69967200 | 0.068751
11 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming | 11 | IMPORT | DHK60884 | 1 | 755514.9 | 800612.84 | 45097.94 | 180 | 8117629.2 |  | 8176984.458
16 | 33/11 kV Transformer-1 Incoming | 11 |  | DHK60976 | 1 | 383231.9 | 418508.56 | 35276.66 | 180 | 6349798.8 |  | 6396227.8665
[9 empty] | Total | 14467428 |  | 14573212.3246
DHANMONDI 11 kV SIDE
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 2787666 | 3920074 | 1132408 | 1 |  | 1132408 | 1137299.4891 | Paribag |  |  |  | 11 kV Balaka Feeder | 1137299.4891 | 923980.5608 | 213318.9283 | 23.0869 | OK
5 | 11 kV Mogbazar O/H | 11 |  | HA021100463-02 | 1 | 43144802 | 44616340 | 1471538 | 1 |  | 1471538 | 1477894.3769 | Paribag |  |  |  | 11 kV Mogbazar O/H | 1477894.3769 | 1280438.1374 | 197456.2395 | 15.421 | OK
6 | 11 kV Panthopath Feeder | 11 |  | HA021101078-02 | 1 | 54778508 | 56931817 | 2153309 | 1 |  | 2153309 | 2162610.3185 | Paribag |  |  |  | 11 kV Panthopath Feeder | 2162610.3185 | 1943366.147 | 219244.1715 | 11.2817 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 |  | DHK60882 | 1 | 195352.1 | 201916.09 | 6563.99 | 60 |  | 393839.4 | 395540.6076 | Paribag |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 395540.6076 | 408935.4042 | -13394.7966 | -3.2755 | OK
8 | 11 kV P G Hospital Feeder | 11 |  | DHK60889 | 1 | 271780.2 | 275542.83 | 3762.63 | 60 |  | 225757.8 | 226732.9713 | Paribag |  |  |  | 11 kV P G Hospital Feeder | 226732.9713 | 180761.0839 | 45971.8874 | 25.4324 | OK
9 | 11 kV Abdul Monem Ltd | 11 |  | DHK60890 | 1 | 678.07 | 684.97 | 6.9 | 60000 |  | 414000 | 415788.2923 | Paribag |  |  |  | 11 kV Abdul Monem Ltd | 415788.2923 | 342920.2484 | 72868.0439 | 21.2493 | OK
10 | 11 kV Surjasen Hall Feeder | 11 |  | DHK60880 | 1 | 517969.5 | 526282.72 | 8313.22 | 60 |  | 498793.2 | 500947.7604 | Ramna |  |  |  | 11 kV Surjasen Hall Feeder | 500947.7604 | 324739.4591 | 176208.3014 | 54.2614 | FAULT
11 | 11 kV Azimpur-1 Feeder | 11 |  | DHK60872 | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | 11 |  | DHK60873 | 1 | 900320 | 910191.77 | 9871.77 | 60 |  | 592306.2 | 594864.6942 | Ramna |  |  |  | 11 kV TSC Feeder | 594864.6942 | 228589.4343 | 366275.2599 | 160.2328 | FAULT
13 | 11 kV SCADA Bhaban | 11 |  | DHK60883 | 1 | 27848.4 | 27965.2 | 116.8 | 60 |  | 7008 | 7038.2714 | Paribag |  |  |  | 11 kV SCADA Bhaban | 7038.2714 | 4746.7382 | 2291.5332 | 48.276 | FAULT
14 | 11 kV DPH Sw/S-2 | 11 |  | DHK60871 | 1 | 435234.3 | 455579.68 | 20345.38 | 60 |  | 1220722.8 | 1225995.769 | Paribag |  |  |  | 11 kV DPH Sw/S-2 | 1225995.769 | 2858553.1096 | -1632557.3406 | -57.1113 | CHECK
17 | 11 kV New Elephant Road Feeder | 11 |  | DHK60981 | 1 | 18328.3 | 38853.86 | 20525.56 | 60 |  | 1231533.6 | 1236853.2667 | Paribag |  |  |  | 11 kV New Elephant Road Feeder | 1236853.2667 | 1035057.8437 | 201795.423 | 19.4961 | OK
18 | 11 kV Dhanmondi O/H Feeder | 11 |  | DHK61110 | 1 | 334055.6 | 356765.96 | 22710.36 | 60 |  | 1362621.6 | 1368507.5074 | Paribag |  |  |  | 11 kV Dhanmondi O/H Feeder | 1368507.5074 | 1474328.4544 | -105820.947 | -7.1776 | OK
19 | 11 kV Sonargaon Feeder | 11 |  | DHK61115 | 1 | 255486.3 | 283945.16 | 28458.86 | 60 |  | 1707531.6 | 1714907.3622 | Paribag |  |  |  | 11 kV Sonargaon Feeder | 1714907.3622 | 1521286.2687 | 193621.0935 | 12.7275 | OK
20 | 11 kV Museum Feeder | 11 |  | DHK61107 | 1 | 540582.3 | 542994.77 | 2412.47 | 60 |  | 144748.2 | 145373.4466 | Ramna |  |  |  | 11 kV Museum Feeder | 145373.4466 | 102890.5133 | 42482.9333 | 41.2895 | FAULT
21 | 11 kV Shanta property | 11 |  | DHK61112 | 1 | 331698.9 | 334966.62 | 3267.72 | 60 |  | 196063.2 | 196910.1041 | Paribag |  |  |  | 11 kV Shanta property | 196910.1041 | 199118.7479 | -2208.6437 | -1.1092 | OK
22 | 11 kV BIRDEM RMU Feeder | 11 |  | DHK61108 | 1 | 655430.3 | 672823.56 | 17393.26 | 60 |  | 1043595.6 | 1048103.4598 | Kakrail |  |  |  | 11 kV BIRDEM RMU Feeder | 1048103.4598 | 1101953.7632 | -53850.3034 | -4.8868 | OK
23 | 11 kV Azimpur-2 Feeder | 11 |  | DHK61109 | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 | 11 |  | DHK60978 | 1 | 739678 | 751590.62 | 11912.62 | 60 |  | 714757.2 | 717844.627 | Kakrail |  |  |  | 11 kV DPH Sw/S-1 | 717844.627 | 392957.1255 | 324887.5015 | 82.6776 | FAULT
[9 empty] | Total | 14573212.3246 | 14510533.4 | 14573212.3246 | 0.43195
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag at 33 KV level |  |  | 11590024.7886
[6 empty] | Azimpur at 33 KV level |  |  | 0
[6 empty] | Ramna at 33 KV level |  |  | 1241185.9012
[6 empty] | Kakrail at 33 KV level |  |  | 1765948.0868
[6 empty] | Total = |  |  | 14597158.7767 | 1.8008e-09
33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1794.62 | 1811.32 | 16.7 | 240000 | 0 | 4008000 | 4010755.5343
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 4008000 | 4010755.5343
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar | 33 | 0 | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
KAWRANBAZAR 33 KV SIDE (RECEIVING)
1 | 33 kV Dhanmondi Circuit-1 | 33 |  | DHK61036 | 1 | 3377.06 | 3391.88 | 14.82 | 270000 | 4001400
5 | 33 kV Dhanmondi Circuit-2 | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar | 33 |  | DHK 61038 | 1 | 1059.48 | 1059.48 | 0 | 270000 | 0
[9 empty] | Total | 4001400 | 0 | 4010755.5343
KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
KAWRANBAZAR 33 KV SIDE
2 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | DHK61039 | 1 | 5069.58 | 5091.79 | 22.21 | 180000 |  | 3997800
3 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
[9 empty] | Total |  | 3997800 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHMANDI 33 KV SIDE |  | 4010755.5343 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 4010755.5343
| MOGBAZAR 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 4010755.5343 |  | 33 KV TX HV SIDE |  | 3997800
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 12955.5343
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.323%
| TOTAL IMPORT |  | 4010755.5343
11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK00182 | 1 | 12893.5 | 13286.8 | 393.3 | 10000 | 3933000 |  | 4010755.5343
15 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
[9 empty] | Total | 3933000 |  | 4010755.5343
KAWRANBAZAR 11 KV SIDE
6 | WASA Bhaban | 11 |  | 8536188 | 1.17 | 1895.3 | 2089.7 | 194.4 | 1000 | 970800 | 970800 | 967717.4567 | Shere b.nagar | From Customer End |  |  | WASA Bhaban | 967717.4567 | 666044.1791 | 301673.2776 | 45.2933 | FAULT
7 | Sangsad Bhaban | 11 |  | 8536178 | 1.17 | 562105 | 567782 | 5677 | 44 |  | 292251.96 | 291323.9838 | Shere b.nagar |  |  |  | Sangsad Bhaban | 291323.9838 | 0 | 291323.9838 | #DIV/0! | #DIV/0!
8 | Air Port Road (West) | 11 |  | 8536182 | 1.17 | 98669.9 | 99649.5 | 979.6 | 1000 |  | 1146132 | 1142492.7318 | Shere b.nagar |  |  |  | Air Port Road (West) | 1142492.7318 | 1186742.6102 | -44249.8784 | -3.7287 | OK
9 | ICC (PM Office) | 11 |  | 8536193 | 1.17 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | 11 |  | DHK00183 | 1.17 | 13920.9 | 14511.4 | 590.5 | 444.44 |  | 307056.9294 | 306081.9435 | Shere b.nagar |  |  |  | (UTC) Tower | 306081.9435 | 292781.4469 | 13300.4966 | 4.5428 | OK
11 | Sonargaon Hotel | 11 |  | 8536190 | 1.17 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Estimated |  |  | Sonargaon Hotel | 0 | 177493.4301 | -177493.4301 | -100 | CHECK
12 | Panthopath | 11 |  | 8536184 | 1.17 | 32519.8 | 33415.5 | 895.7 | 1000 |  | 1047969 | 1044641.4249 | Shere b.nagar |  |  |  | Panthopath | 1044641.4249 | 1087934.41 | -43292.9851 | -3.9794 | OK
13 | Titas Bhaban | 11 |  | DHK00190 | 1.17 | 54591.7 | 55090.4 | 498.7 | 444.44 |  | 259321.4068 | 258497.9936 | Kakrail |  |  |  | Titas Bhaban | 258497.9936 | 224792.5712 | 33705.4225 | 14.994 | OK
16 | Green Road Dormatory s/s | 11 |  | DHK00021 | 1.17 |  | 0 | 0 | 444.44 |  | 0 | 0 |  |  |  |  | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 | 11 |  | 85-12906 | 1.17 | 67673 | 67959 | 286 | 10 |  |  | 0 | Shere b.nagar |  |  |  | Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | Aux. Transformer, AT-2 | 11 |  | 85-12909 | 1.17 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 4010755.5343 | 4023531.2962 | 4010755.5343 | -0.31753
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail at 33 KV level |  |  | 258497.9936 | [8 empty] | Customer Name | Customer Number | Feeder name | Consumption | OMF
[5 empty] | Shere b.nagar at 33 KV level |  |  | 3752257.5407 | [8 empty] | Square Hospital | 27529489 | Wasa Bhaban | 970800 | 6000
[5 empty] | Total = |  |  | 4010755.5343 | 0
[17 empty] | NOCS Name | Previous Off Peak | Present Off-Peak | Previous Peak | Present Peak
[17 empty] | ShereBangla Nagar | 2134.95 | 2249.27 | 826.99 | 874.47
33 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1420.28 | 1435.41 | 15.13 | 240000 | 0 | 3631200 | 3633696.4811
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1154.36 | 1164.56 | 10.2 | 240000 | 0 | 2448000 | 2449683.0209
[9 empty] | Total | 0 | 6079200 | 6083379.502
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | ESTIMATED | 1556900.352 | 1558036.6112
[9 empty] | Total | 0 | 1556900.352 | 1558036.6112
NEW RAMNA 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 | 180 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
|  | 33 |  |  | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 7641416.1132
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  |  | 0 |  |  | 0
| Feeder No.2 | 33 | [5 empty] | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.3. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 7641416.1132 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 6083379.502 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 7641416.1132
| NARINDA 33 KV SIDE |  | 1558036.6112 |  | 33 KV NET IMPORT |  |  | 7641416.1132 |  | 33 KV TX HV SIDE |  | 7641416.1132
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7641416.1132
11 KV SIDE of___NEW RAMNA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK 00002 | 1 | 24196.5 | 24554.2 | 357.7 | 10000 | 3577000 |  | 3705836.4508
15 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK 00007 | 1 | 12642.6 | 12884.6 | 242 | 10000 | 2420000 |  | 2507163.6038
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming | 11 |  | DHKA2182 | 1 | 572.5362 | 574.76 | 2.2238 | 180000 | 1378756 |  | 1428416.0586 |  | 1378756 | Converted 9 Days Reading into 31 days | Due to BUS PT Missing
[9 empty] | Total | 7375756 |  | 7641416.1132
NEW RAMNA 11 KV SIDE
4 | Police Bhaban | 11 |  | DHK 00005 | 1 | 72590.4 | 72836.6 | 246.2 | 444.44 |  | 109421.128 | 111715.2077 | Ramna |  |  |  | Police Bhaban | 111715.2077 | 87598.6864 | 24116.5214 | 27.5307 | OK
5 | Water Works | 11 |  | DHK 00010 | 1 |  | 0 | 0 | 444.44 |  | 0 | 0 | Lalbag |  |  |  | Water Works | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | GPO | 11 |  | DHK 00060 | 1 | 96791.5 | 97306.6 | 515.1 | 444.44 |  | 228931.044 | 233730.721 | Ramna |  |  |  | GPO | 233730.721 | 339691.225 | -105960.504 | -31.1932 | OK
7 | Culvert Road | 11 |  | 8536184 | 1 | 39937.8 | 39940.4 | 2.6 | 444.44 | 62 | 754123.608 | 769934.2629 | Ramna |  |  |  | Culvert Road | 769934.2629 | 593056.4267 | 176877.8362 | 29.8248 | OK
8 | Secretariat (East) | 11 |  | DHK00059 | 1 | 81649.8 | 81714.5 | 64.7 | 444.44 |  | 28755.268 | 29358.1395 | Ramna |  |  |  | Secretariat (East) | 29358.1395 | 0 | 29358.1395 | #DIV/0! | #DIV/0!
9 | Siddik Bazar | 11 |  | DHK00076 | 1 | 25588.9 | 27275.4 | 1686.5 | 444.44 |  | 749548.06 | 765262.7858 | Bangshal |  |  |  | Siddik Bazar | 765262.7858 | 836442.0579 | -71179.2721 | -8.5098 | OK
10 | Bokshi Bazar | 11 |  | DHK 00206 | 1 | 83338.9 | 84325 | 986.1 | 444.44 |  | 438262.284 | 447450.7163 | Ramna |  |  |  | Bokshi Bazar | 447450.7163 | 214966.1015 | 232484.6148 | 108.1494 | FAULT
11 | Ramna 11 kV Sw/S Circuit-1 | 11 |  | DHK00198 | 1 | 41887.9 | 44281.1 | 2393.2 | 444.44 |  | 1063633.808 | 1085933.5304 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 1085933.5304 | 936401.2951 | 149532.2352 | 15.9688 | OK
12 | TNT RMU | 11 |  | DHK 00207 | 1 | 58458.1 | 59418.3 | 960.2 | 444.44 |  | 426751.288 | 435698.3854 | Ramna |  |  |  | TNT RMU | 435698.3854 | 419900.4516 | 15797.9337 | 3.7623 | OK
13 | DIT 11 kV Sw/S Circuit-1 | 11 |  | DHK 00052 | 1 | 2720.5 | 2799.1 | 78.6 | 444.44 |  | 34932.984 | 35665.375 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-1 | 35665.375 | 671.7691 | 34993.6059 | 5209.172 | FAULT
16 | Secretariat (West) | 11 |  | DHK 00006 | 1 | 66894.9 | 67064.7 | 169.8 | 444.44 |  | 75465.912 | 77048.1002 | Ramna |  |  |  | Secretariat (West) | 77048.1002 | 362665.7271 | -285617.6269 | -78.7551 | CHECK
17 | Ramna 11 kV Sw/S Circuit-2 | 11 |  | DHK00197 | 1 | 84759.4 | 84761.5 | 2.1 | 444.44 |  | 933.324 | 952.8917 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 952.8917 | 850.9075 | 101.9842 | 11.9853 | OK
18 | Sayed Nazrul Islam Road | 11 |  | DHK00186 | 1 | 18825.6 | 21662.7 | 2837.1 | 444.44 |  | 1260920.724 | 1287356.6852 | Ramna |  |  |  | Sayed Nazrul Islam Road | 1287356.6852 | 518247.4431 | 769109.2421 | 148.4058 | FAULT
19 | Gulistan Complex | 11 |  | DHK00030 | 1 | 53533.1 | 53974.5 | 441.4 | 444.44 |  | 196175.816 | 200288.7599 | Ramna |  |  |  | Gulistan Complex | 200288.7599 | 151954.163 | 48334.5969 | 31.8087 | OK
20 | Mohanagor Nattomanso | 11 |  | DHK 00008 | 1 | 99592.4 | 99681.5 | 89.1 | 444.44 |  | 39599.604 | 40429.8335 | Ramna |  |  |  | Mohanagor Nattomanso | 40429.8335 | 0 | 40429.8335 | #DIV/0! | #DIV/0!
21 | DIT 11 kV Sw/S Circuit-2 | 11 |  | DHK00196 | 1 | 22347.2 | 23893.8 | 1546.6 | 444.44 |  | 687370.904 | 701782.0483 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-2 | 701782.0483 | 712523.0573 | -10741.009 | -1.5075 | OK
22 | Jail | 11 |  | DHK00009 | 1 |  | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | 11 |  | HA021100713-02 | 1 | 75828041 | 75857044 | 29003 | 1 |  | 99899.2222 | 101993.6695 | Ramna | 99899.2222 | Converted 9 Days Reading into 31 days | Due to BUS PT Missing | Kosturi Bazar | 101993.6695 | 81587.505 | 20406.1645 | 25.0114 | OK
24 | Kaptan Bazar | 11 |  | HA021101251-02 | 1 | 5704466 | 5820909 | 116443 | 1 |  | 401081.4444 | 409490.3581 | Narinda | 401081.4444 |  |  | Kaptan Bazar | 409490.3581 | 351867.0872 | 57623.2709 | 16.3764 | OK
25 | G.T.V | 11 |  | HA-021101054-02 | 1 | 70326682 | 70498299 | 171617 | 1 |  | 591125.2222 | 603518.518 | Ramna | 591125.2222 |  |  | G.T.V | 603518.518 | 584214.178 | 19304.34 | 3.3043 | OK
26 | Kazi Alauddin Road | 11 |  | HA021100951-02 | 1 | 5582587 | 5667944 | 85357 | 1 |  | 294007.4444 | 300171.4873 | Bangshal | 294007.4444 |  |  | Kazi Alauddin Road | 300171.4873 | 363865.3386 | -63693.8513 | -17.5048 | OK
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 |  | 2436 | 1 | 67422 | 67423 | 1 | 10 |  | 10 | 10.2097 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 10.2097 | 2559.4657 | -2549.2561 | -99.6011 | CHECK
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 |  | 2437 | 1 | 87735 | 88090 | 355 | 10 |  | 3550 | 3624.4279 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 3624.4279 | 916.9739 | 2707.4539 | 295.2596 | FAULT
[9 empty] | Grand Total | 7641416.1132 | 7484499.0893 | 7641416.1132 | 2.0966
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 5429044.0587
[5 empty] | Lalbag | at 33 KV level |  | 0
[5 empty] | Bangshal | at 33 KV level |  | 1065434.2731
[5 empty] | Motijheel | at 33 KV level |  | 737447.4233
[5 empty] | Narinda | at 33 KV level |  | 409490.3581
[5 empty] | Total = |  |  | 7641416.1132 | 0
33 KV SIDE of___ KAKRAIL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 761.21 | 782.32 | 21.11 | 240000 | 0 | 5066400 | 5069883.1933
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1542.04 | 1565.51 | 23.47 | 240000 | 0 | 5632800 | 5636672.5982
[9 empty] | Total | 0 | 10699200 | 10706555.7915
ULLON 33 KV SIDE
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9044 | 1163.9044 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder | 33 | IMPORT |  | 1 | 226957 | 226957 | 0 | 1000 |  | 0
[9 empty] | Total | 0 | 0 | 0
KAKRAIL 33 KV SIDE (RECEIVING)
5 | 33 kV Dhanmondi-2 | 33 |  | 06604376 | 1 | 5191.05 | 5222.44 | 31.39 | 180000 | 5650200
2 | 33 kV Dhanmondi-1 | 33 |  | 06604375 | 1 | 1951.82 | 197976 | 196024.18 | 180000 | 35284352400
| 33 KV Kakrail From ULLON | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
[9 empty] | Total | 35290002600 | 0 | 0
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KAKRAIL 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 |  |  | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi 33 KV SIDE |  | 10706555.7915 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KAKRAIL 33 KV NET IMPORT |  | 10706555.7915
| ULLON 33 KV SIDE |  | 0 |  | KAKRAIL 33 KV NET IMPORT |  |  | 10706555.7915 |  | KAKRAIL KV NET IMPORT |  | 10512890.203
| Taltola 33 KV SIDE |  | 0 | [6 empty] | LOSS UNITS=> |  | 193665.5885
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.809%
| TOTAL IMPORT |  | 10706555.7915
11 KV SIDE of___KAKRAIL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK00017 | 1 | 17246 | 17807.9 | 561.9 | 8888.89 | 4994667.291 |  | 5086677.686
15 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK00018 | 1 | 3822 | 4442.8 | 620.8 | 8888.89 | 5518222.912 |  | 5619878.1055
[9 empty] | Total | 10512890.203 |  | 10706555.7915
KAKRAIL 11 KV SIDE
7 | Pioneer | 11 |  | 06604395 | 1 | 23539.01 | 23641.25 | 102.24 | 8000 |  | 817920 | 826396.2524 | Ramna |  |  |  | Pioneer | 826396.2524 | 699646.2675 | 126749.9849 | 18.1163 | OK
8 | Pir Saheber Goli | 11 |  | DHK-00102 | 1 | 72928.3 | 76172.5 | 3244.2 | 444.444 |  | 1441865.2248 | 1456807.534 | Rajarbag |  |  |  | Pir Saheber Goli | 1456807.534 | 1436998.6643 | 19808.8697 | 1.3785 | OK
9 | Montri Para | 11 |  | DHK-00110 | 1 | 12423.2 | 12504.9 | 81.7 | 2222.22 |  | 181555.374 | 183436.8651 | Kakrail |  |  |  | Montri Para | 183436.8651 | 174250.442 | 9186.4231 | 5.272 | OK
10 | Baily Road 11 kV Sw/S-2 | 11 |  | 9119865 | 1 | 58339.7 | 60588.9 | 2249.2 | 1000 |  | 2249200 | 2272508.865 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-2 | 2272508.865 | 2007787.7043 | 264721.1607 | 13.1847 | OK
11 | Jamuna U/G 11 KV Jonaki O/H | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | 11 |  | 1025651 | 1 | 28397.4 | 28699 | 301.6 | 1000 |  | 301600 | 304725.5352 | Ramna |  |  |  | High Court | 304725.5352 | 161432.1801 | 143293.355 | 88.7638 | FAULT
13 | Secretaiat | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | 11 |  | 06604402 | 1 | 5556.49 | 5592.5 | 36.01 | 40000 |  | 1440400 | 1455327.1248 | Rajarbag |  |  |  | Shanti Nagar Bazar | 1455327.1248 | 1398811.8437 | 56515.2812 | 4.0402 | OK
17 | Tottho Bhovon | 11 |  | 9119867 | 1 | 31865.1 | 31865.1 | 0 | 1000 | Estimated | 263790 | 266523.7033 | Kakrail |  |  |  | Tottho Bhovon | 266523.7033 | 264169.9429 | 2353.7604 | 0.891 | OK
18 | Central Police Hospital/ PNT (Circuit House) | 11 |  | DHK00199 | 1 | 77786.4 | 78080.07 | 293.67 | 2222.22 |  | 652599.3474 | 659362.3521 | Kakrail |  |  |  | Central Police Hospital/ PNT (Circuit House) | 659362.3521 | 656054.0269 | 3308.3252 | 0.50428 | OK
19 | Baily Road 11 kV Sw/S-1 | 11 |  | DHK00027 | 1 | 54237.6 | 54773.6 | 536 | 2222.22 |  | 1191109.92 | 1203453.6068 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-1 | 1203453.6068 | 1212854.2899 | -9400.6831 | -0.77509 | OK
20 | Bijoy Nagar | 11 |  | D1025656 | 1 | 63855.4 | 64877.9 | 1022.5 | 1000 |  | 1022500 | 1033096.3518 | Ramna |  |  |  | Bijoy Nagar | 1033096.3518 | 882869.7891 | 150226.5627 | 17.0157 | OK
21 | Shilpakala Academy | 11 |  | D0086137 | 1 | 23595.3 | 24493.9 | 898.6 | 1000 |  | 898600 | 907912.3538 | Ramna |  |  |  | Shilpakala Academy | 907912.3538 | 514039.318 | 393873.0358 | 76.6231 | FAULT
22 | Judges Complex | 11 |  | 06604344 | 1 | 664.38 | 667.77 | 3.39 | 40000 |  | 135600 | 137005.2472 | Kakrail |  |  |  | Judges Complex | 137005.2472 | 136596.4601 | 408.7871 | 0.29927 | OK
23 | Auxiliary Transformer, AT-1 | 11 |  | 39333 | 1 | 492441 | 492441 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-1 | 0 | 5038.2463 | -5038.2463 | -100 | CHECK
24 | Auxiliary Transformer, AT-2 | 11 |  | 39254 | 1 | 1195010 | 1195010 | 0 | 1 |  |  | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10706555.7915 | 10596739.8662 | 10706555.7915 | 1.0363
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH |  | 109815.9253
[5 empty] | Ramna | at 33 KV level |  | 3072130.4931
[5 empty] | Rajarbag | at 33 KV level |  | 2912134.6589
[5 empty] | Kakrail | at 33 KV level |  | 4722290.6395
[5 empty] | Total = |  |  | 10706555.7915 | 0
33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 664.59 | 679.62 | 15.03 | 240000 | 0 | 3607200 | 3609679.9809
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 134.4 | 139.74 | 5.34 | 240000 | 0 | 1281600 | 1282481.111
[9 empty] | Total |  | 4888800 | 4892161.0918 | 0.068751
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 | 33 |  | BD017073 | 1 | 56730.95 | 60215.13 | 3484.18 | 1000 | 3484180
4 | 33 kV Dhanmondi Incoming Circuit-2 | 33 |  | BD017074 | 1 | 32223.14 | 33466.76 | 1243.62 | 1000 | 1243620
| 33 KV Ullon-1 Feeder | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
[9 empty] | Total | 4727800 | 0 | 0
BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S)
Total
BSMMU HOSPITAL 33 KV SIDE
2 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017072 | 1 | 84128.3 | 88059.92 | 3931.62 | 888.89 |  | 3494777.7018
6 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017076 | 1 | 29086.77 | 30490.64 | 1403.87 | 888.89 |  | 1247886.0043
[9 empty] | Total |  | 4742663.7061 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHANMONDI 33 KV SIDE |  | 4892161.0918 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 4892161.0918
[5 empty] | 33 KV NET IMPORT |  |  | 4892161.0918 |  | 33/11 KV XF HV SIDE |  | 4742663.7061
[10 empty] | LOSS UNITS=> |  | 149497.3857
[10 empty] | LOSS % IN => |  | 3.056%
| TOTAL IMPORT |  | 4892161.0918
11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD017081 | 1 | 62603.8 | 66067.88 | 3464.08 | 1000 | 3464080 |  | 3606700.0081
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD017082 | 1 | 25041.99 | 26276.62 | 1234.63 | 1000 | 1234630 |  | 1285461.0837
[7 empty] | 0 |  | Total | 4698710 |  | 4892161.0918
| BSMMU HOSPITAL 11 KV SIDE | [5 empty] | 0
8 | 11 kV Jamuna (F1) | 11 |  | BD017073 | 1 | 0.34 | 0.3512 | 0.0112 | 2000 |  | 22.4 | 22.5473 | Kakrail |  |  |  | 11 kV Jamuna (F1) | 22.5473 | 22.3301 | 0.21723 | 0.9728 | OK
9 | 11 kV Pukur Par (F2) | 11 |  | BD017074 | 1 | 2860.85 | 2883.64 | 22.79 | 2000 |  | 45580 | 45879.8149 | Kakrail |  |  |  | 11 kV Pukur Par (F2) | 45879.8149 | 50313.1683 | -4433.3534 | -8.8115 | OK
10 | 11 kV BSMMU Convention center (F3) | 11 |  | BD017075 | 1 | 1669.21 | 1695.63 | 26.42 | 2000 |  | 52840 | 53187.5695 | Kakrail |  |  |  | 11 kV BSMMU Convention center (F3) | 53187.5695 | 24402.1884 | 28785.3812 | 117.9623 | FAULT
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 |  | BD017076 | 1 | 2756.04 | 2841.69 | 85.65 | 2000 |  | 171300 | 172426.7726 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 172426.7726 | 146453.3648 | 25973.4078 | 17.7349 | OK
12 | 11 kV Holi Family Feeder (F5) | 11 |  | BD017077 | 1 | 13334.88 | 13664.28 | 329.4 | 2000 |  | 658800 | 663133.437 | Kakrail |  |  |  | 11 kV Holi Family Feeder (F5) | 663133.437 | 643469.4128 | 19664.0242 | 3.0559 | OK
13 | 11 kV Navy House Feeder (F6) | 11 |  | BD017078 | 1 | 25676.26 | 25982.79 | 306.53 | 2000 |  | 613060 | 617092.5697 | Kakrail |  |  |  | 11 kV Navy House Feeder (F6) | 617092.5697 | 675616.731 | -58524.1614 | -8.6623 | OK
14 | 11 kV Paribagh Feeder (F7) | 11 |  | BD017079 | 1 | 29530.52 | 30291.6 | 761.08 | 2000 |  | 1522160 | 1532172.4233 | Paribag |  |  |  | 11 kV Paribagh Feeder (F7) | 1532172.4233 | 1495896.3942 | 36276.0291 | 2.425 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 |  | BD017080 | 1 | 5758.91 | 5957.89 | 198.98 | 2000 |  | 397960 | 400577.6906 | Paribag |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 400577.6906 | 357060.5455 | 43517.1452 | 12.1876 | OK
18 | 11 kV Oncology Bhaban (F9) | 11 |  | BD017083 | 1 | 2097.11 | 2161.63 | 64.52 | 2000 |  | 129040 | 129888.7959 | Paribag |  |  |  | 11 kV Oncology Bhaban (F9) | 129888.7959 | 115251.5559 | 14637.24 | 12.7003 | OK
19 | Rupayan Trade Center | 11 |  | BD017084 | 1 | 790.58 | 928.49 | 137.91 | 2000 |  | 275820 | 277634.2814 | Kakrail |  |  |  | Rupayan Trade Center | 277634.2814 | 235351.3619 | 42282.9196 | 17.9659 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 |  | BD017085 | 1 | 1941.64 | 1996.69 | 55.05 | 2000 |  | 110100 | 110824.2128 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 110824.2128 | 111992.5662 | -1168.3533 | -1.0432 | OK
21 | 11 kV BSMMU RMU (F12) | 11 |  | BD017086 | 1 | 1799.23 | 1881.92 | 82.69 | 2000 |  | 165380 | 166467.8321 | Paribag |  |  |  | 11 kV BSMMU RMU (F12) | 166467.8321 | 126195.3238 | 40272.5084 | 31.9128 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 |  | BD017087 | 1 | 3801.38 | 3915.28 | 113.9 | 2000 |  | 227800 | 229298.4167 | Paribag |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 229298.4167 | 198597.2001 | 30701.2166 | 15.459 | OK
23 | 11 kV BCS Academy RMU (F14) | 11 |  | BD017088 | 1 | 928.43 | 965.83 | 37.4 | 2000 |  | 74800 | 75292.0174 | Paribag |  |  |  | 11 kV BCS Academy RMU (F14) | 75292.0174 | 63791.706 | 11500.3114 | 18.0279 | OK
24 | Spare | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | 11 |  | BD017090 | 1 | 845.61 | 971.62 | 126.01 | 2000 |  | 252020 | 253677.7304 | Paribag |  |  |  | BSMMU Super Specialist Hospital RMU | 253677.7304 | 199522.5923 | 54155.1382 | 27.1424 | OK
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKD4418 | 1 | 2310.34 | 2460.23 | 149.89 | 100 |  | 14989 | 15087.5942 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 15087.5942 | 9234.81 | 5852.7842 | 63.3774 | FAULT
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 |  | 0 | 0 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 3911.7935 | -3911.7935 | -100 | CHECK
[9 empty] | Grand Total | 4742663.7061 | 4711671.4 | 4742663.7061 | 0.65778
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 1940201.2053
[5 empty] | Paribag | at 33 KV level |  | 2802462.5008
[5 empty] | Total = |  |  | 4742663.7061 | 0
132 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 | 132 |  | 8993518 | 1 | 1057.877 | 1078.582 | 20.705 | 960000 | 0 | 19876800
|  | 132 |  |  | 1 | 70.056 | 70.056 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 | 132 |  | 5014660 | 1 | 234.584 | 255.206 | 20.622 | 960000 | 0 | 19797120
|  | 132 |  |  | 1 | 4.361 | 4.361 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 | 132 |  | 38992597 | 1 | 505.695 | 539.605 | 33.91 | 1440000 | 0 | 48830400
|  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 88504320
[9 empty] | Net Total | 88504320
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 | 132 | RECEIVE | 6604452 | 1 | 219582 | 238756 | 19174 | 1000 | 19174000
|  | 132 |  |  | 1 | 6755 | 6755 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) | 132 |  |  | 1 | 4229950 | 4278687 | 48737 | 1000 | 48737000
|  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar | 132 |  |  | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  |  | 1 | 405030 | 442987 | 37957 | 1000 |  | 37957000
| Kallyanpur-2 | 132 |  | 6604428 | 1 | 318662 | 337429 | 18767 | 1000 | 18767000
|  | 132 |  |  | 1 | 7111 | 7111 | 0 | 1000 |  | 0
[8 empty] | Total Import/Export |  | 86678000 | 37957000
[8 empty] | Net Total |  | 48721000
LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S)
6 | Kamrangirchar | 132 |  | SIEM491 | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  | SIEM491 | 1 | 405030 | 442987 | 37957 | 1000 |  | 37957000
[9 empty] | Total |  | 37957000
LALBAGH 132 KV SIDE
4 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | SIEM494 | 1 | 2122324 | 2146660 | 24336 | 1000 |  | 24336000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | SIEM499 | 1 | 2234218 | 2258635 | 24417 | 1000 |  | 24417000
[9 empty] | Total |  | 48753000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 88504320 |  | EXPORT TO OTHER S/S |  |  | 37957000 |  | 132 KV NET IMPORT |  | 50547320
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 50547320 |  | 132/33 KV GT LV SIDE |  | 48718000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 1829320
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 3.619%
| 132 KV TOTAL IMPORT |  | 88504320
33 KV SIDE of___LALBAGH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) | 33 |  | SIEM0517 | 1 | 2121901 | 2146183 | 24282 | 1000 | 24282000
16 | 132/33 kV GT-2 Incoming (LV) | 33 |  | SIEM0518 | 1 | 2208191 | 2232627 | 24436 | 1000 | 24436000
[9 empty] | Total | 48718000 |  | 0
LALBAGH 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SIEM0502 | 1 | 819705 | 825730 | 6025 | 2000 |  | 12050000 | 12114093.0414 |  | 25555207.0633 | Lalbagh New 33/11 kv ss | 0.16561 | 33/11 kV, 20/28 MVA T-1 (HV) | 12114093.0414 | 10026054.2358 | 2088038.8056 | 20.8261 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SIEM0501 | 1 | 811972 | 818657 | 6685 | 2000 |  | 13370000 | 13441114.0219 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 13441114.0219 | 10951943.1494 | 2489170.8725 | 22.7281 | OK
| 33 KV Feeders | [7 empty] | Total |  | 25420000 | 25555207.0633 |  |  |  |  | 33 KV Feeders | 25555207.0633 | 20977997.3853 | 4577209.678 | 21.8191 | OK
9 | Spare | 33 |  | SIEM0500 | 1 |  |  |  | 2000 |  | 0 | 0 |  | 9106178.819 | Mitford 33/11 kv ss | 1.1436 | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 | 33 |  | SIEM0513 | 1 | 312160 | 314345 | 2185 | 2000 |  | 4370000 | 4393243.7005 |  |  |  |  | Mitford Circuit-1 | 4393243.7005 | 3886698.5164 | 506545.1841 | 13.0328 | OK
12 | Azimpur Circuit-1 | 33 |  | SIEM0503 | 1 | 70528 | 70528 | 0 | 2000 |  | 0 | 0 |  | 3212999.283 | Azimpur 33/11 kv ss | 1.9396 | Azimpur Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Azimpur Circuit-2 | 33 |  | SIEM0507 | 1 | 76523 | 78121 | 1598 | 2000 |  | 3196000 | 3212999.283 |  |  |  |  | Azimpur Circuit-2 | 3212999.283 | 0 | 3212999.283 | #DIV/0! | #DIV/0!
17 | Lalbagh old | 33 |  | SIEM0509 | 1 | 207032 | 212298 | 5266 | 2000 |  | 10532000 | 10588018.9139 |  | 10588018.9139 | Lalbagh old 33/11 kv ss | -0.62501 | Lalbagh old | 10588018.9139 | 8318755.7776 | 2269263.1363 | 27.2789 | OK
18 | Mitford Circuit-2 | 33 |  | SIEM0511 | 1 | 352694 | 355038 | 2344 | 2000 |  | 4688000 | 4712935.1185 |  |  |  |  | Mitford Circuit-2 | 4712935.1185 | 4128854.0785 | 584081.0401 | 14.1463 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKC7982 | 1 | 6972.14 | 7071.66 | 99.52 | 120 |  | 11942.4 | 12005.9207 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-1 | 12005.9207 | 12694.2422 | -688.3215 | -5.4223 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHU02670 | 1 | 27089.5 | 27089.5 | 0 | 120 |  | 0 | 0 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 22797942.4 | 22919202.9367 |  |  |  |  | 0 | 22919202.9367 | 16347002.6147 | 6572200.322 | 40.2043 | FAULT
[8 empty] | Grand Total |  | 48474410 | 48217942.4 | 48474410 | 0.53189
11 KV SIDE of___ LALBAGH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK98833 | 1 | 571416.3 | 577429.7 | 6013.4 | 2000 | 12026800 |  | 12119279.9863
11 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK98832 | 1 | 566748.7 | 573415.4 | 6666.7 | 2000 | 13333400 |  | 13435927.077
[9 empty] | Total | 25360200 |  | 25555207.0633
LALBAGH 11 kV SIDE
3 | Chata Mosjid | 11 |  |  | 1 | 164850.7 | 167272.9 | 2422.2 | 1000 |  | 2422200 | 2426211.3577 | Kamrangirchar |  |  |  | Chata Mosjid | 2426211.3577 | 2063369.3277 | 362842.03 | 17.5849 | OK
4 | AC mosjid | 11 |  |  | 1 | 27060.73 | 4071.8 | -22988.93 | 1000 | Estimated | 1337961.24 | 1340177.0113 | Lalbag | 110 |  |  | AC mosjid | 1340177.0113 | 1361089.5463 | -20912.5351 | -1.5365 | OK
5 | Kazi Reaz Uddin Road | 11 |  |  | 1 | 14366.9 | 16630.49 | 2263.59 | 1000 |  | 2263590 | 2267338.6868 | Lalbag |  |  |  | Kazi Reaz Uddin Road | 2267338.6868 | 1861617.4367 | 405721.2502 | 21.794 | OK
6 | Nazimuddin | 11 |  |  | 1 | 4214.292 | 4214.292 | 0 | 1000 | Estimated | 0 | 0 | Lalbag |  |  |  | Nazimuddin | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Kamal Bagh | 11 |  |  | 1 | 101936 | 117683.69 | 15747.69 | 1000 | Estimated | 1581226.92 | 1583845.5588 | Lalbag | 130 |  |  | Kamal Bagh | 1583845.5588 | 1301911.74 | 281933.8188 | 21.6554 | OK
8 | Rahamatganj | 11 |  |  | 1 | 37932 | 37932 | 0 | 1000 | Estimated | 2554289.64 | 2558519.7488 | Lalbag | 210 |  |  | Rahamatganj | 2558519.7488 | 1479445.159 | 1079074.5897 | 72.9378 | FAULT
9 | Water Works 11kV Sw/S-1 | 11 |  |  | 1 | 16928.9 | 18780.18 | 1851.28 | 1000 |  | 1851280 | 1854345.8684 | Lalbag |  |  |  | Water Works 11kV Sw/S-1 | 1854345.8684 | 1577485.6182 | 276860.2501 | 17.5507 | OK
12 | City Colony | 11 |  |  | 1 | 18357.9 | 20434.814 | 2076.914 | 1000 |  | 2076914 | 2080353.5364 | Lalbag |  |  |  | City Colony | 2080353.5364 | 1768961.385 | 311392.1513 | 17.6031 | OK
13 | Water Works 11kV Sw/S-2 | 11 |  |  | 1 | 26667.3 | 29754.25 | 3086.95 | 1000 |  | 3086950 | 3092062.2371 | Lalbag |  |  |  | Water Works 11kV Sw/S-2 | 3092062.2371 | 2624031.448 | 468030.7891 | 17.8363 | OK
14 | Chun Goli | 11 |  |  | 1 | 4641.936 | 5535.3348 | 893.3988 | 1000 |  | 893398.8 | 894878.3402 | Lalbag |  |  |  | Chun Goli | 894878.3402 | 730984.3547 | 163893.9855 | 22.421 | OK
15 | Alir Ghat | 11 |  |  | 1 | 115609.9 | 117703.2 | 2093.3 | 1000 |  | 2093300 | 2096766.6729 | Lalbag |  |  |  | Alir Ghat | 2096766.6729 | 1667306.1835 | 429460.4894 | 25.7577 | OK
16 | Club Ghat | 11 |  |  | 1 | 8835.142 | 11435.815 | 2600.673 | 1000 | Estimated | 2736738.9 | 2741271.1594 | Lalbag | 225 |  |  | Club Ghat | 2741271.1594 | 1952867.6099 | 788403.5495 | 40.3716 | FAULT
17 | Debidas Ghat | 11 |  |  | 1 | 21794.4 | 21794.4 | 0 | 1000 | Estimated | 2615106.06 | 2619436.8857 | Lalbag | 215 |  |  | Debidas Ghat | 2619436.8857 | 1775334.1908 | 844102.6948 | 47.5461 | FAULT
18 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 25555207.0633 | 25512955.56 | 25555207.0633 | 0.16561
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 2426211.3577
[5 empty] | Lalbag | at 33 KV level |  | 23128995.7056
[5 empty] | Total = |  |  | 25555207.0633 | 0
33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAG Grid 33 KV SIDE
17 | Lalbagh old | 33 | 0 | SIEM0509 | 1 | 207032 | 212298 | 5266 | 2000 | 0 | 10532000 | 10588018.9139
[9 empty] | Total |  | 10532000 | 10588018.9139 | 0.53189
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 | 33 | 0 | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
| 33 KV KAMRANGIRCHAR-1 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
| 34 KV KAMRANGIRCHAR-2 | 33 |  |  | 1 |  |  | 0 | 240000 |  | 0
[9 empty] | Total |  | 0 | 10588018.9139
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
LALBAGH OLD 33 KV SIDE
6 | 33/11 kV, 10/14 MVA T4 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
7 | 33/11 kV, 10/14 MVA T3 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
8 | 33/11 kV, 10/14 MVA T1 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
14 | 33/11 kV, 10/14 MVA T2 (HV) | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAG Grid 33 KV SIDE |  | 10588018.9139 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALBAGH OLD 33 KV NET IMPORT |  | 10588018.9139
| KAMRANGIRCHAR 33 KV SIDE |  | 0 |  | LALBAGH OLD 33 KV NET IMPORT |  |  | 10588018.9139 |  | 33 KV TX HV SIDE |  | 10588018.9139
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 10588018.9139
11 KV SIDE of___LALBAGH OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) | 11 |  | 8838010 | 1 | 71637.5 | 74809 | 3171.5 | 1000 | 3171500 |  | 4445325.7734
27 | 33/11 kV T1 Incoming (LV) | 11 |  | 06604426 | 1 | 35281.8 | 35456.08 | 174.28 | 16000 | 2788480 |  | 3908466.6601
28 | 33/11 kV T2 Incoming (LV) | 11 |  |  | 1 | 599038 | 600632 | 1594 | 1000 | 1594000 |  | 2234226.4804
[9 empty] | Total | 7553980 |  | 10588018.9139
LALBAGH OLD 11 KV SIDE
15 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | 11 |  | 8838019 | 1 | 69444.8 | 72291.8 | 2847 | 1000 |  | 2847000 | 2829205.9908 | Lalbag |  |  |  | Sowari Ghat | 2829205.9908 | 2119031.6661 | 710174.3247 | 33.5141 | OK
17 | Novo Kumar (Kara Odidoptor) | 11 |  | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 133796.124 | 132959.886 | Lalbag | 11 |  |  | Novo Kumar (Kara Odidoptor) | 132959.886 | 125148.169 | 7811.7171 | 6.242 | OK
19 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1337961.24 | 1329598.8604 | Lalbag | 110 |  |  | Eidgah | 1329598.8604 | 1001185.3517 | 328413.5087 | 32.8025 | OK
23 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | 11 |  |  | 1 | 77697 | 82497.9 | 4800.9 | 444.44 | Estimated | 2067758.28 | 2054834.6025 | Lalbag | 170 |  |  | Modumoti | 2054834.6025 | 1877222.5345 | 177612.068 | 9.4614 | OK
25 | Lalbagh O/H | 11 |  | 61389152 | 1 | 439042 | 439667 | 625 | 1000 | Estimated | 1094695.56 | 1087853.6131 | Lalbag | 90 |  |  | Lalbagh O/H | 1087853.6131 | 813463.0983 | 274390.5148 | 33.7312 | OK
26 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | 11 |  | 61389109 | 1 | 398934 | 399921 | 987 | 1000 |  | 987000 | 980831.1601 | Lalbag |  |  |  | Water Works 11 kV Sw/S-2 | 980831.1601 | 842052.7012 | 138778.4589 | 16.481 | OK
31 | Islambagh | 11 |  | 61389186 | 1 | 497490 | 498372 | 882 | 1000 |  | 882000 | 876487.4197 | Lalbag |  |  |  | Islambagh | 876487.4197 | 775574.8564 | 100912.5633 | 13.0113 | OK
32 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | 11 |  | 61389202 | 1 | 15370 | 15416 | 46 | 1000 |  | 46000 | 45712.4958 | Lalbag |  |  |  | WASA Low Lift Pump | 45712.4958 | 37267.8827 | 8444.6131 | 22.6592 | OK
34 | Shahi Mosjid | 11 |  | 06604459 | 1 | 35231.3 | 35388.6 | 157.3 | 8000 |  | 1258400 | 1250534.8854 | Azimpur |  |  |  | Shahi Mosjid | 1250534.8854 | 711514.3877 | 539020.4977 | 75.7568 | FAULT
35 | Spare | 11 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer | 0.415 |  | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 |  | 0 | 0 | Lalbag |  |  |  | 33/0.4 kV Auxiliary Transformer | 0 | 16295.1299 | -16295.1299 | -100 | CHECK
[9 empty] | Grand Total | 10588018.9139 | 10654611.204 | 10588018.9139 | -0.62501
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Lalbag | at 33 KV level |  | 9337484.0285
[5 empty] | Azimpur | at 33 KV level |  | 1250534.8854
[5 empty] | Total = |  |  | 10588018.9139 | 0
33 KV SIDE of___ MIDFORT 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 | 33 | 0 | SIEM0513 | 1 | 312160 | 314345 | 2185 | 2000 | 0 | 4370000 | 4393243.7005
18 | Mitford Circuit-2 | 33 | 0 | SIEM0511 | 1 | 352694 | 355038 | 2344 | 2000 | 0 | 4688000 | 4712935.1185
[9 empty] | Total | 0 | 9058000 | 9106178.819
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 1201.51 | 1210.49 | 8.98 | 540000 |  | 4849200
| Lalbagh Circuit-2 | 33 |  | DHK68131 | 1 | 1271.98 | 1278.66 | 6.68 | 540000 |  | 3607200
[9 empty] | Total |  | 8456400
MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S)
1 | Kumartuly Circuit-1 | 33 |  | DHK-66493 | 1 | 1284424 | 1284426 | 2 | 180 |  | 360
6 | Kumartuly Circuit-2 | 33 |  | DHK-60914 | 1 | 759323.6 | 759468.5 | 144.9 | 180 |  | 26082
[9 empty] | Total |  | 26442
MIDFORT 33 KV SIDE
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-66494 | 1 | 2729298 | 2756388 | 27090 | 180 |  | 4876200
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHKA-2193 | 1 | 509.5429 | 535.4201 | 25.8772 | 180000 |  | 4657896
[9 empty] | Total |  | 9534096 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 KV SIDE |  | 9106178.819 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9534096
| IMPORT-2 |  | 26442 |  | 33 KV NET IMPORT |  |  | 9534096 |  | 33 KV TX HV SIDE |  | 9534096
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 9132620.819
11 KV SIDE of___MIDFORT 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK-66484 | 1 | 2662574 | 2688460 | 25886 | 180 | 4659480 |  | 4769258.8903
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK-66476 | 1 | 1992776 | 2018638 | 25862 | 180 | 4655160 |  | 4764837.1097
[9 empty] | Total | 9314640 |  | 9534096
MIDFORT 11 KV SIDE
7 | Spare | 11 |  | DHK-66483 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | DHK-66478 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | 11 |  | DHK-60904 | 1 | 946220.21 | 954595.7 | 8375.49 | 60 |  | 502529.4 | 508276.2976 | Lalbag |  |  |  | Chawk Bazar | 508276.2976 | 453807.1489 | 54469.1486 | 12.0027 | OK
10 | Spare | 11 |  | DHK-66482 | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | 11 |  | DHK-66485 | 1 | 776910 | 782736 | 5826 | 60 |  | 349560 | 353557.5482 | Bangshal |  |  |  | Chatrabas | 353557.5482 | 305234.6153 | 48322.933 | 15.8314 | OK
12 | Begum Bazar | 11 |  | DHK-66481 | 1 | 3547689 | 3586533 | 38844 | 60 |  | 2330640 | 2357293.0663 | Bangshal |  |  |  | Begum Bazar | 2357293.0663 | 2140333.9168 | 216959.1494 | 10.1367 | OK
13 | SCC ROAD | 11 |  | DHK-60901 | 1 | 995636.3 | 1021576.1 | 25939.8 | 60 |  | 1556388 | 1574186.7645 | Bangshal |  |  |  | SCC ROAD | 1574186.7645 | 1412865.2619 | 161321.5026 | 11.418 | OK
16 | Spare | 11 |  | DHK-66483 | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | 11 |  | DHK-61104 | 1 | 636742.1 | 652439.3 | 15697.2 | 60 |  | 941832 | 952602.7371 | Bangshal |  |  |  | Armanitola | 952602.7371 | 874523.9369 | 78078.8002 | 8.9281 | OK
18 | Mitford Hospital (RMU) | 11 |  | DHK-61101 | 1 | 365803 | 374512.4 | 8709.4 | 60 |  | 522564 | 528540.0121 | Bangshal |  |  |  | Mitford Hospital (RMU) | 528540.0121 | 438993.9488 | 89546.0633 | 20.398 | OK
19 | Emamganj | 11 |  | DHK-68130 | 1 | 1416.62 | 1435.73 | 19.11 | 60000 |  | 1146600 | 1159712.4523 | Bangshal |  |  |  | Emamganj | 1159712.4523 | 958588.0479 | 201124.4043 | 20.9813 | OK
20 | Kamal Dho Road | 11 |  | DHK-68129 | 1 | 1196.02 | 1205.82 | 9.8 | 60000 |  | 588000 | 594724.3345 | Lalbag |  |  |  | Kamal Dho Road | 594724.3345 | 627573.6899 | -32849.3554 | -5.2343 | OK
21 | Spare | 11 |  | DHK-68128 | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | 11 |  | DHK-68127 | 1 | 1457.21 | 1481.94 | 24.73 | 60000 |  | 1483800 | 1500768.6523 | Bangshal |  |  |  | Panghat | 1500768.6523 | 1276066.5029 | 224702.1494 | 17.609 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | U0004460 | 1 | 5469.44 | 5513.28 | 43.84 | 100 |  | 4384 | 4434.1352 | Bangshal |  |  |  | 11/0.4 kV Auxiliary Transformer | 4434.1352 | 5114.9307 | -680.7955 | -13.31 | OK
[9 empty] | Grand Total | 9534096 | 9426297.4 | 9534096 | 1.1436
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 8431095.3679
[5 empty] | Lalbag | at 33 KV level |  | 1103000.6321
[5 empty] | Total = |  |  | 9534096 | 0
33 KV SIDE of___ AZIMPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 | 33 | 0 | SIEM0503 | 1 | 70528 | 70528 | 0 | 2000 | 0 | 0 | 0
15 | Azimpur Circuit-2 | 33 | 0 | SIEM0507 | 1 | 76523 | 78121 | 1598 | 2000 | 0 | 3196000 | 3212999.283
[9 empty] | Total | 0 | 3196000 | 3212999.283
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1872.34 | 1906.63 | 34.29 | 240000 | 0 | 8229600 | 8235257.9204
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1786.24 | 1804.37 | 18.13 | 240000 | 0 | 4351200 | 4354191.4872
[9 empty] | Total | 0 | 12580800 | 12589449.4076
[9 empty] | GRAND TOTAL |  | 15776800 | 15802448.6906
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 782901 | 782901 | 0 | 180 |  | 0
| Dhanmondi Circuit-1 | 33 |  | DHK68131 | 1 | 1138546 | 1153680 | 15134 | 540 |  | 8172360
| Dhanmondi Circuit-2 | 33 |  |  | 1 | 125088 | 133153 | 8065 | 540 |  | 4355100
| Lalbagh Circuit-2 | 33 |  | DHK68132 | 1 | 849071 | 866755 | 17684 | 180 |  | 3183120
[9 empty] | Total |  | 15710580 | #REF!
AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  | 1 |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  | 1 |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
AZIMPUR 33 KV SIDE
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK61094 | 1 | 144902 | 190365 | 45463 | 180 |  | 8183340
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK60919 | 1 | 283921 | 325834 | 41913 | 180 |  | 7544340
[9 empty] | Total |  | 15727680 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| LALBAGH 33 kV SIDE |  | 3212999.283 |  | EXPORT TO OTHER S/S |  |  | 0 |  | AZIMPUR 33 KV NET IMPORT |  | 15802448.6906
| DHANMONDI 33 kV SIDE |  | 12589449.4076 |  | AZIMPUR 33 KV NET IMPORT |  |  | 15802448.6906 |  | 33 KV TX HV SIDE |  | 15727680
[10 empty] | LOSS UNITS=> |  | 74768.6906
[10 empty] | LOSS % IN => |  | 0.4731%
| TOTAL IMPORT |  | 15802448.6906
11 KV SIDE of___AZIMPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) | 11 |  | DHK60909 | 1 | 147667 | 193178 | 45511 | 180 | 8191980 |  | 8211752.0251
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK60902 | 1 | 298879 | 340948 | 42069 | 180 | 7572420 |  | 7590696.6655
[9 empty] | Total | 15764400 |  | 15802448.6906
AZIMPUR 11 KV SIDE
7 | Chadni chwok | 11 |  | DHK60916 | 1 | 375816 | 386413 | 10597 | 60 |  | 635820 | 648152.1238 | Paribag |  |  |  | Chadni chwok | 648152.1238 | 839724.1803 | -191572.0564 | -22.8137 | OK
8 | BGB | 11 |  | DHK61090 | 1 | 657048 | 661190 | 4142 | 60 |  | 248520 | 253340.1998 | Jigatola |  |  |  | BGB | 253340.1998 | 235052.0415 | 18288.1583 | 7.7805 | OK
9 | Pari Bibi Mazar | 11 |  | DHK61091 | 1 | 673428 | 708482 | 35054 | 60 |  | 2103240 | 2144033.6462 | Azimpur |  |  |  | Pari Bibi Mazar | 2144033.6462 | 2031020.3634 | 113013.2828 | 5.5644 | OK
10 | Azimpur | 11 |  | DHK61086 | 1 | 246143 | 264194 | 18051 | 60 |  | 1083060 | 1104066.6214 | Azimpur |  |  |  | Azimpur | 1104066.6214 | 1083739.2957 | 20327.3257 | 1.8757 | OK
11 | Aazd | 11 |  | DHK61089 | 1 | 918408 | 938971 | 20563 | 60 |  | 1233780 | 1257709.9294 | Azimpur |  |  |  | Aazd | 1257709.9294 | 1149651.4246 | 108058.5049 | 9.3992 | OK
12 | Dayra Sharif | 11 |  | DHK61088 | 1 | 466279 | 482306 | 16027 | 60 |  | 961620 | 980271.2172 | Azimpur |  |  |  | Dayra Sharif | 980271.2172 | 924355.1099 | 55916.1073 | 6.0492 | OK
13 | Naya palton | 11 |  | DHK86065 | 1 | 1814.77 | 1842.39 | 27.62 | 60000 |  | 1657200 | 1689342.4234 | Azimpur |  |  |  | Naya palton | 1689342.4234 | 1567013.6097 | 122328.8136 | 7.8065 | OK
16 | Viqarunnisa Noon School | 11 |  | DHK66477 | 1 | 1537959 | 1560667 | 22708 | 60 |  | 1362480 | 1388906.1459 | Azimpur |  |  |  | Viqarunnisa Noon School | 1388906.1459 | 1269037.1307 | 119869.0152 | 9.4457 | OK
17 | Subal Das Lane | 11 |  | DHK66480 | 1 | 3943041 | 3964091 | 21050 | 60 |  | 1263000 | 1287496.6695 | Azimpur |  |  |  | Subal Das Lane | 1287496.6695 | 2049129.4312 | -761632.7617 | -37.1686 | OK
18 | Lalbagh | 11 |  | DHK61093 | 1 | 607520 | 646194 | 38674 | 60 |  | 2320440 | 2365446.3751 | Azimpur |  |  |  | Lalbagh | 2365446.3751 | 2236256.465 | 129189.9101 | 5.7771 | OK
19 | Zahrul Haque Hall | 11 |  | DHK66497 | 1 | 1206912 | 1217962 | 11050 | 60 |  | 663000 | 675859.2968 | Ramna |  |  |  | Zahrul Haque Hall | 675859.2968 | 499493.2098 | 176366.0871 | 35.309 | OK
20 | Eden College | 11 |  | DHK60917 | 1 | 910937 | 918378 | 7441 | 60 |  | 446460 | 455119.369 | Azimpur |  |  |  | Eden College | 455119.369 | 298281.3455 | 156838.0235 | 52.5806 | FAULT
21 | Nilkhet/ PWD-01 | 11 |  | DHK60918 | 1 | 445447 | 456044 | 10597 | 60 |  | 635820 | 648152.1238 | Azimpur |  |  |  | Nilkhet/ PWD-01 | 648152.1238 | 614610.7855 | 33541.3384 | 5.4573 | OK
22 | BUET | 11 |  | DHK66496 | 1 | 923075 | 937828 | 14753 | 60 |  | 885180 | 902348.6159 | Ramna |  |  |  | BUET | 902348.6159 | 1004352.0692 | -102003.4533 | -10.1561 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIG2780 | 1 | 377494 | 381002 | 3508 | 1 |  | 2162 | 2203.9333 | Azimpur |  |  |  | 11/0.4 kV Auxiliary Transformer | 2203.9333 | 2197.071 | 6.8624 | 0.31234 | OK
[9 empty] | Grand Total | 15802448.6906 | 15501782 | 15802448.6906 | 1.9396
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 648152.1238
[5 empty] | Jigatola | at 33 KV level |  | 253340.1998
[5 empty] | Azimpur | at 33 KV level |  | 13322748.4543
[5 empty] | Ramna | at 33 KV level |  | 1578207.9127
[5 empty] | Total = |  |  | 15802448.6906 | 0
132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar | 132 |  | 38992596 | 1 | 786.173 | 816.161 | 29.988 | 1440000 | 0 | 43182720
|  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 43182720
[9 empty] | Net Total | 43182720
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj | 132 | RECEIVE |  | 1 | 5539.96 | 5585.08 | 45.12 | 960000 | 43315200
|  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh | 132 |  |  | 1 | 2930.75 | 2970.27 | 39.52 | 960000 | 37939200
|  | 132 |  |  | 1 | 7.78 | 7.78 | 0 | 960000 |  | 0
[8 empty] | Total Import/Export |  | 81254400 | 0
[8 empty] | Net Total |  | 81254400
KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S)
5 | 132 kV Jigatola-1 | 132 |  | 42003953362 | 1 | 157.6 | 172.77 | 15.17 | 1440000 |  | 21844800
6 | 132 kV Jigatola-2 | 132 |  | 42003953364 | 1 | 154.41 | 169.18 | 14.77 | 1440000 |  | 21268800
[9 empty] | Total |  | 43113600
KAMRANGIRCHAR 132 KV SIDE
1 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | 30799138 | 1 | 3347.07 | 3359.89 | 12.82 | 960000 |  | 12307200
2 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | 30799148 | 1 | 3324.62 | 3337.49 | 12.87 | 960000 |  | 12355200
7 | 132/33 kV, 50/75 MVA GT-3 (HV) | 132 |  | BD001910 | 1 | 1122.45 | 1136.12 | 13.67 | 960000 |  | 13123200
[9 empty] | Total |  | 37785600
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Keranigonj 132 KV SIDE (TARIFF POINT) |  | 43182720 |  | EXPORT TO OTHER S/S |  |  | 43113600 |  | 132 KV NET IMPORT |  | 38008320
| FROM LALBAGH 132/33 KV GRID |  | 37939200 |  | 132 KV NET IMPORT |  |  | 38008320 |  | 33 KV NET IMPORT |  | 37766400
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 241920
[10 empty] | LOSS % IN => |  | 0.6365%
| 132 KV TOTAL IMPORT |  | 81121920
33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming | 33 |  | BD001914 | 1 | 2259.66 | 2286.99 | 27.33 | 480000 | 13118400 |  | 13202432.4555
14 | 132/33 kV GT-1 Incoming (LV) | 33 |  | 30799094 | 1 | 6793.16 | 6819.07 | 25.91 | 480000 | 12436800 |  | 12516466.3345
19 | 132/33 kV GT-2 Incoming | 33 |  | 30799150 | 1 | 6695.07 | 6720.51 | 25.44 | 480000 | 12211200 |  | 12289421.21
[9 empty] | Total | 37766400 |  | 38008320
KAMRANGIRCHAR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) | 33 |  | 30799129 | 1 | 6735.55 | 6770.39 | 34.84 | 240000 |  | 8361600 | 8414359.77 |  | 25921734.6186 | Kamrangir Char 33/11 kv ss | 1.8195 | 33/11 kV, 20/28 MVA T31 (HV) | 8414359.77 | 7313618.6031 | 1100741.1669 | 15.0506 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) | 33 |  | 30799110 | 1 | 6633.56 | 6668.04 | 34.48 | 240000 |  | 8275200 | 8327414.6059 |  |  |  |  | 33/11 kV, 20/28 MVA T32 (HV) | 8327414.6059 | 7258230.6453 | 1069183.9606 | 14.7306 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) | 33 |  | 30799137 | 1 | 3768.32 | 3806.33 | 38.01 | 240000 |  | 9122400 | 9179960.2427 |  |  |  |  | 33/11 kV, 20/28 MVA T-33 (HV) | 9179960.2427 | 8601990.6652 | 577969.5775 | 6.719 | OK
| 33 KV Feeders | [7 empty] | Total |  | 25759200 | 25921734.6186 |  |  |  |  | 33 KV Feeders | 25921734.6186 | 23173839.9136 | 2747894.705 | 11.8577 | OK
8 | Dhaka Uddyan 2 | 33 |  | BD001907 | 1 | 345.3 | 348.37 | 3.07 | 240000 |  | 736800 | 741449.0383 |  | 1523955.5152 | Dhaka Uddan 33/11 kv ss | 1.8057 | Dhaka Uddyan 2 | 741449.0383 | 0 | 741449.0383 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 | 33 |  | BD001912 | 1 | 424.99 | 428.23 | 3.24 | 240000 |  | 777600 | 782506.4769 |  |  |  |  | Dhaka Uddyan 1 | 782506.4769 | 0 | 782506.4769 | #DIV/0! | #DIV/0!
10 | Spare Feeder -2 | 33 |  | 30799130 | 1 |  | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) | 33 |  | 30799125 | 1 |  | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 | 33 |  | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 |  | 0 | 0 |  | 6685117.0618 | Kamrangir Char-2 33/11 kv ss | -0.070094 | Lalbagh Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Zigatola Circuit-1 (BGB-1) | 33 |  | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 | 33 |  |  | 1 |  | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 | 33 |  | 30799147 | 1 | 1437.29 | 1464.97 | 27.68 | 240000 |  | 6643200 | 6685117.0618 |  | 3573446.2444 | BGB 33/11 kv ss | 0.0035339 | Kamrangir Char-2 | 6685117.0618 | 5822960.0864 | 862156.9754 | 14.8062 | OK
22 | Zigatola Circuit-2 (BGB-2) | 33 |  | 30799131 | 1.35 | 1843.5 | 1854.46 | 10.96 | 240000 |  | 3551040 | 3573446.2444 |  |  |  |  | Zigatola Circuit-2 (BGB-2) | 3573446.2444 | 0 | 3573446.2444 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 11708640 | 11782518.8214 |  |  |  |  | 0 | 11782518.8214 | 5822960.0864 | 5959558.735 | 102.3459 | FAULT
[8 empty] | Grand Total |  | 37704253.44 | 37467840 | 37704253.44 | 0.63098
11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming | 11 |  |  | 1 |  | 0 | 0 | 160000 | 8209800 |  | 8403453.7814
11 | 33/11 kV T-32 Incoming | 11 |  | 6604433 | 1 | 7435.64 | 7481.25 | 45.61 | 180000 | 8209800 |  | 8403453.7814
22 | 33/11 kV T-33 Incoming | 11 |  | DHK 95817 | 1 | 4406634 | 4456105 | 49471 | 180 | 8904780 |  | 9114827.0559
[9 empty] | Total | 25324380 |  | 25921734.6186
KAMRANGIRCHAR 11 kV SIDE
4 | Rasulpur | 11 |  | HA-021101042-02 | 1 | 87852313 | 89078209 | 1225896 | 1 |  | 1225896 | 1248201.2259 | Kamrangirchar |  |  |  | Rasulpur | 1248201.2259 | 1139975.1714 | 108226.0546 | 9.4937 | OK
5 | Bheribadh | 11 |  | HA-021101105-02 | 1 | 57381342 | 59737086 | 2355744 | 1 |  | 2355744 | 2398606.8547 | Kamrangirchar |  |  |  | Bheribadh | 2398606.8547 | 2282403.3176 | 116203.5371 | 5.0913 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | 11 |  | 30799521 | 1 | 2615.33 | 2623.32 | 7.99 | 60000 |  | 479400 | 488122.7019 | Kamrangirchar |  |  |  | Panna Tower 11 KV Faridpur Tower Express | 488122.7019 | 280141.9243 | 207980.7775 | 74.2412 | FAULT
8 | Panna Battery Express | 11 |  | DHK15431 | 1 | 5225.42 | 5243.73 | 18.31 | 60000 |  | 1098600 | 1118589.0702 | Kamrangirchar |  |  |  | Panna Battery Express | 1118589.0702 | 740112.9442 | 378476.126 | 51.1376 | FAULT
9 | Eidgah | 11 |  | 30799460 | 1 | 5239.4 | 5297.07 | 57.67 | 60000 | ESTIMATED | 2797555.32 | 2848456.9491 | Kamrangirchar | 230 |  |  | Eidgah | 2848456.9491 | 759074.5155 | 2089382.4336 | 275.2539 | FAULT
10 | Bot Tola Mazar | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | 11 |  | HA-021101055-02 | 1 | 95819475 | 97687286 | 1867811 | 1 |  | 1867811 | 1901795.8946 | Kamrangirchar |  |  |  | Huzur Para | 1901795.8946 | 1668645.799 | 233150.0956 | 13.9724 | OK
13 | Kamrangirchar | 11 |  | HA-021101015-02 | 1 | 15882379 | 17588896 | 1706517 | 1 |  | 1706517 | 1737567.1439 | Kamrangirchar |  |  |  | Kamrangirchar | 1737567.1439 | 1756038.2539 | -18471.11 | -1.0519 | OK
14 | Munshihati | 11 |  | HA-021100854-02 | 1 | 47729145 | 48912982 | 1183837 | 1 |  | 1183837 | 1205376.9608 | Kamrangirchar |  |  |  | Munshihati | 1205376.9608 | 1209548.4387 | -4171.4779 | -0.34488 | OK
15 | Jhawchar | 11 |  | HA-021101028-02 | 1 | 96114856 | 97420106 | 1305250 | 1 |  | 1305250 | 1328999.0751 | Kamrangirchar |  |  |  | Jhawchar | 1328999.0751 | 1379969.9443 | -50970.8692 | -3.6936 | OK
16 | RMU Express | 11 |  | HA-021101248-02 | 1 | 4001997 | 4693909 | 691912 | 1 |  | 691912 | 704501.3661 | Kamrangirchar |  |  |  | RMU Express | 704501.3661 | 1079976.4781 | -375475.1121 | -34.767 | OK
17 | Koyla Ghat | 11 |  | HA-021101259-02 | 1 | 12262339 | 14045899 | 1783560 | 1 |  | 1783560 | 1816011.9444 | Kamrangirchar |  |  |  | Koyla Ghat | 1816011.9444 | 1565482.6179 | 250529.3264 | 16.0033 | OK
18 | Muslimbagh | 11 |  | HA-021100908-02 | 1 | 21197938 | 22904364 | 1706426 | 1 |  | 1706426 | 1737474.4882 | Kamrangirchar |  |  |  | Muslimbagh | 1737474.4882 | 1546637.2627 | 190837.2255 | 12.3388 | OK
19 | Noyagaon | 11 |  | HA-021101087-02 | 1 | 97903415 | 100516458 | 2613043 | 1 |  | 2613043 | 2660587.4202 | Kamrangirchar | METER |  |  | Noyagaon | 2660587.4202 | 2579943.8089 | 80643.6113 | 3.1258 | OK
20 | Nurbagh | 11 |  | HA-021100982-02 | 1 | 16859280 | 19118491 | 2259211 | 1 |  | 2259211 | 2300317.433 | Kamrangirchar | METER |  |  | Nurbagh | 2300317.433 | 2339949.036 | -39631.603 | -1.6937 | OK
21 | Ali Nagar | 11 |  | HA-021101022-02 | 1 | 15074988 | 17434438 | 2359450 | 1 |  | 2359450 | 2402380.2856 | Kamrangirchar | METER |  |  | Ali Nagar | 2402380.2856 | 2819938.5818 | -417558.2963 | -14.8074 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKE6223 | 1 | 42434.65 | 42637.18 | 202.53 | 120 |  | 24303.6 | 24745.805 |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 24745.805 | 25891.7198 | -1145.9148 | -4.4258 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 |  |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 110.0994 | -110.0994 | -100 | CHECK
[9 empty] | Total | 25921734.6186 | 25458515.92 | 25921734.6186 | 1.8195
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 25921734.6186
[5 empty] | Jigatola | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 25921734.6186 | 0
33 KV SIDE of___ BGB 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1843.5 | 1854.46 | 10.96 | 240000 | 0 | 3551040 | 3573446.2444
[9 empty] | TOTAL |  | 3551040 | 3573446.2444
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Zigatola-1 | 33 | 0 | 43998033 | 1 | 85.55 | 119.18 | 33.63 | 270000 |  | 9080100 | 9080100
[9 empty] | TOTAL |  | 9080100 | 9080100
JIGATOLA 33 KV SIDE
2 | BGB-1 | 33 | 0 | 0 | 1 | 36.64 | 36.64 | 0 | 360000 | 0 | 0 | 0
11 | BGB-2 | 33 | 0 | 0 | 1 | 210.69 | 220.47 | 9.78 | 360000 | 0 | 3520800 | 3518047.2244
[9 empty] | Total | 0 | 3520800 | 3518047.2244
[9 empty] | GRAND TOTAL |  | 16151940 | 16171593.4688
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 | 33 |  | 43998032 | 1 | 1043.59 | 1043.59 | 0 | 270000 | 0
8 | 33 kV Zigatola-1 | 33 |  | 43998033 | 1 | 85.55 | 119.18 | 33.63 | 270000 | 9080100
| 33 kV Zigatola-1 | 33 |  | 43998033 | 1 |  | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 | 33 |  | 43998027 | 1 | 727.95 | 741.9 | 13.95 | 270000 | 3766500
| 33 kV Zigatola-2 | 33 |  | 43998031 | 1 | 280.3 | 293.2 | 12.9 | 270000 | 3483000
[9 empty] | Total | 16329600 | 0 | 0
BGB 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
BGB 33 KV SIDE
6 | 33/11 kV T1 | 33 |  | 43998028 | 1 | 660.73 | 694.308 | 33.578 | 270000 |  | 9066060
9 | 33/11 kV T2 | 33 |  | 43998029 | 1 | 675 | 701.99 | 26.99 | 270000 |  | 7287300
11 | 33/11 kV T3 | 33 |  |  | 1 |  | 0 | 0 | 270000 |  | 0
[9 empty] | Total |  | 16353360
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| JIGATOLA 33 KV SIDE |  | 16171593.4688 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BGB 33 KV NET IMPORT |  | 16171593.4688
[5 empty] | BGB 33 KV NET IMPORT |  |  | 16171593.4688 |  | 33 KV TX HV SIDE |  | 16353360
[10 empty] | LOSS UNITS=> |  | -181766.5312
[10 empty] | LOSS % IN => |  | -1.124%
| TOTAL IMPORT |  | 16171593.4688
11 KV SIDE of___BGB 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming | 11 |  |  | 1 | 77088532 | 86023405 | 8934873 | 1 | 8934873 |  | 8956792.2533
29 | 33/11 kV T-2 Incoming | 11 |  |  | 1 | 80655936 | 87853081 | 7197145 | 1 | 7197145 |  | 7214801.2156
30 | 33/11 kV T-3 Incoming | 11 |  |  | 1 |  | 0 | 0 | 1 | 0
[9 empty] | Total | 16132018 |  | 16171593.4688
BGB 11 KV SIDE
12 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | 11 |  |  | 1 | 5185032 | 6757988 | 1572956 | 1 |  | 1572956 | 1573011.5868 | Azimpur |  |  |  | Nababgonj Park | 1573011.5868 | 1258240.5876 | 314770.9992 | 25.0168 | OK
16 | Kholamura Ghat | 11 |  |  | 1 | 69207512 | 72049102 | 2841590 | 1 |  | 2841590 | 2841690.4191 | Kamrangirchar |  |  |  | Kholamura Ghat | 2841690.4191 | 2255342.9889 | 586347.4303 | 25.9981 | OK
17 | Khalpar | 11 |  |  | 1 | 80177553 | 81615032 | 1437479 | 1 |  | 1437479 | 1437529.7992 | Kamrangirchar |  |  |  | Khalpar | 1437529.7992 | 1259084.7389 | 178445.0603 | 14.1726 | OK
18 | Shahidnagar | 11 |  |  | 1 | 10527781 | 12336427 | 1808646 | 1 |  | 1808646 | 1808709.9159 | Azimpur |  |  |  | Shahidnagar | 1808709.9159 | 1728570.5059 | 80139.41 | 4.6362 | OK
19 | BGB 1 No Gate | 11 |  |  | 1 | 28528895 | 29847534 | 1318639 | 1 |  | 1318639 | 1318685.5995 | Azimpur |  |  |  | BGB 1 No Gate | 1318685.5995 | 1288792.8329 | 29892.7666 | 2.3194 | OK
21 | Ganaktuli | 11 |  |  | 1 | 21176889 | 21869943 | 693054 | 1 |  | 693054 | 693078.4919 | Jigatola |  |  |  | Ganaktuli | 693078.4919 | 696443.8676 | -3365.3757 | -0.48322 | OK
22 | Thana | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | 11 |  |  | 1 | 26193780 | 28102896 | 1909116 | 1 |  | 1909116 | 1909183.4664 | Jigatola |  |  |  | Bot Tola Mazar | 1909183.4664 | 1714240.0336 | 194943.4328 | 11.372 | OK
24 | Sikder Medical | 11 |  |  | 1 | 32253872 | 33392224 | 1138352 | 1 |  | 1138352 | 1138392.2283 | Jigatola |  |  |  | Sikder Medical | 1138392.2283 | 1242331.3516 | -103939.1233 | -8.3665 | OK
25 | Gas Field | 11 |  |  | 1 | 47881720 | 49867262 | 1985542 | 1 |  | 1985542 | 1985612.1672 | Kamrangirchar |  |  |  | Gas Field | 1985612.1672 | 1885210.8081 | 100401.3591 | 5.3257 | OK
26 | Hazaribagh | 11 |  |  | 1 | 35481840 | 36947488 | 1465648 | 1 |  | 1465648 | 1465699.7946 | Jigatola |  |  |  | Hazaribagh | 1465699.7946 | 1445870.2849 | 19829.5097 | 1.3715 | OK
27 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 |  |  | 1 | 1938.35 | 1998.58 | 60.23 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 |  |  | 1 | 1534.23 | 1590.01 | 55.78 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 16171593.4688 | 16171022 | 16171593.4688 | 0.0035339
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Azimpur | at 33 KV level |  | 4700407.1021
[5 empty] | Kamrangirchar | at 33 KV level |  | 6264832.3855
[5 empty] | Jigatola | at 33 KV level |  | 5206353.9812
[5 empty] | Total = |  |  | 16171593.4688 | 0
132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 | 132 | 0 | 42003953362 | 1 | 157.6 | 172.77 | 15.17 | 1440000 | 0 | 21844800 | 0
6 | 132 kV Jigatola-2 | 132 | 0 |  | 1 | 154.41 | 169.18 | 14.77 | 1440000 | 0 | 21268800 | 0
[8 empty] | Total Import/Export |  | 0 | 43113600
[9 empty] | Net Total | 43113600
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 | 132 | RECEIVE | 6604452 | 1 | 189.05 | 207.24 | 18.19 | 1200000 | 21828000
| 132 kV Kamrangirchar 2 | 132 |  |  | 1 | 185.07 | 202.78 | 17.71 | 1200000 | 21252000
[8 empty] | Total Import/Export |  | 43080000 | 0
[8 empty] | Net Total |  | 43080000
JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
JIGATOLA 132 KV SIDE
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  |  | 1 | 150.73 | 163.21 | 12.48 | 1200000 |  | 14976000
3 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  |  | 1 | 223.52 | 246.97 | 23.45 | 1200000 |  | 28140000
[9 empty] | Total |  | 43116000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 43113600 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 43113600
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 43113600 |  | 33 KV NET IMPORT |  | 42940800
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 172800
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.4008%
| 132 KV TOTAL IMPORT |  | 43113600
33 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  |  | 1 | 249.82 | 270.5 | 20.68 | 720000 | 14889600
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  |  | 1 | 370.8 | 409.76 | 38.96 | 720000 | 28051200
[9 empty] | Total | 42940800 |  | 0
JIGATOLA 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  |  | 1 | 465.71 | 493.08 | 27.37 | 240000 |  | 6568800 | 6563664.1126 |  | 19868453.4793 | JIGATOLA NEW 3/11 KV SS | 0.13635 | 33/11 kV 28/35 MVA T-1 | 6563664.1126 | 5892672.7803 | 670991.3322 | 11.3869 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  |  | 1 | 312.88 | 345.81 | 32.93 | 240000 |  | 7903200 | 7897020.7975 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 7897020.7975 | 7498226.6278 | 398794.1697 | 5.3185 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  |  | 1 | 279.02 | 301.57 | 22.55 | 240000 |  | 5412000 | 5407768.5692 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 5407768.5692 | 5140673.9151 | 267094.6541 | 5.1957 | OK
| 33 KV Feeders | [7 empty] | Total |  | 19884000 | 19868453.4793 |  |  |  |  | 33 KV Feeders | 19868453.4793 | 18531573.3231 | 1336880.1561 | 7.2141 | OK
2 | BGB-1 | 33 |  |  | 1 | 36.64 | 36.64 | 0 | 360000 |  | 0 | 0 |  | 3518047.2244 | BGB 33/11 kv ss | 0.0035339 | BGB-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Spair | 33 |  |  | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 | 33 |  |  | 1 | 136.14 | 153.69 | 17.55 | 360000 |  | 6318000 | 6313060.2033 |  |  |  |  | Dhaka Uddyan-1 | 6313060.2033 | 6042588.9528 | 270471.2504 | 4.4761 | OK
4 | Green Road -1 | 33 |  |  | 1 | 17.64 | 23.2 | 5.56 | 360000 |  | 2001600 | 2000035.0274 |  | 12823965.5981 | Dhaka Uddan 33/11 kv ss | 1.8057 | Green Road -1 | 2000035.0274 | 6294847.5135 | -4294812.4862 | -68.2274 | CHECK
9 | Green Road -2 | 33 |  |  | 1 | 0.02 | 9.84 | 9.82 | 360000 |  | 3535200 | 3532435.9656 |  |  |  |  | Green Road -2 | 3532435.9656 | 0 | 3532435.9656 | #DIV/0! | #DIV/0!
10 | Dhaka Uddyan-2 | 33 |  |  | 1 | 135.18 | 153.28 | 18.1 | 360000 |  | 6516000 | 6510905.3948 |  |  |  |  | Dhaka Uddyan-2 | 6510905.3948 | 6390781.3535 | 120124.0414 | 1.8796 | OK
11 | BGB-2 | 33 |  |  | 1 | 210.69 | 220.47 | 9.78 | 360000 |  | 3520800 | 3518047.2244 |  | 1197862.7052 | Jigatla Old 33/11 kv ss | 1.481 | BGB-2 | 3518047.2244 | 7083539.1506 | -3565491.9262 | -50.3349 | CHECK
12 | Jigatola Old | 33 |  |  | 1 | 0.9 | 4.23 | 3.33 | 360000 |  | 1198800 | 1197862.7052 |  |  |  |  | Jigatola Old | 1197862.7052 | 0 | 1197862.7052 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  |  | 1 |  | 0 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 23090400 | 23072346.5207 |  |  |  |  | 0 | 23072346.5207 | 25811756.9704 | -2739410.4497 | -10.613 | OK
[8 empty] | Grand Total |  | 42940800 | 42974400 | 42940800 | -0.078186
11 KV SIDE of___JIGATOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 41.4 | 67.61 | 26.21 | 250000 | 6552500 |  | 6560243.9619
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 41.94 | 73.52 | 31.58 | 250000 | 7895000 |  | 7904330.5729
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 35.25 | 56.84 | 21.59 | 250000 | 5397500 |  | 5403878.9445
[9 empty] | Total | 19845000 |  | 19868453.4793
JIGATOLA 11 kV SIDE
| Salek Garden | 11 |  | 2761 | 1 | 465.5 | 506.46 | 40.96 | 60000 |  | 2457600 | 2460950.9042 | Jigatola |  |  |  | Salek Garden | 2460950.9042 | 2355446.6338 | 105504.2704 | 4.4792 | OK
4 | Jigatola Local | 11 |  | 2850 | 1 | 379.35 | 408.27 | 28.92 | 60000 |  | 1735200 | 1737565.9216 | Jigatola |  |  |  | Jigatola Local | 1737565.9216 | 1685404.4586 | 52161.463 | 3.0949 | OK
5 | Modina Rayer Bazar | 11 |  | 2851 | 1 | 603.31 | 603.31 | 0 | 60000 |  | 0 | 0 | Switching |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | City College | 11 |  | 2784 | 1 | 411.15 | 450.2 | 39.05 | 60000 |  | 2343000 | 2346194.6487 | Jigatola |  |  |  | City College | 2346194.6487 | 1852006.2653 | 494188.3834 | 26.6839 | OK
7 | Spare | 11 |  | 2799 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office | 11 |  | 2836 | 1 | 304.3 | 330.76 | 26.46 | 60000 |  | 1587600 | 1589764.671 | Jigatola |  |  |  | Post Office | 1589764.671 | 1552123.0133 | 37641.6577 | 2.4252 | OK
11 | Leather Institute | 11 |  | 2835 | 1 | 50.97 | 54.22 | 3.25 | 60000 |  | 195000 | 195265.8799 | Jigatola |  |  |  | Leather Institute | 195265.8799 | 184170.7245 | 11095.1554 | 6.0244 | OK
12 | Mina Bazar | 11 |  | 2853 | 1 | 157.71 | 169.47 | 11.76 | 60000 |  | 705600 | 706562.076 | Jigatola |  |  |  | Mina Bazar | 706562.076 | 694275.1652 | 12286.9108 | 1.7697 | OK
13 | Mitali | 11 |  | 2852 | 1 | 229.64 | 278.85 | 49.21 | 60000 |  | 2952600 | 2956625.83 | Jigatola |  |  |  | Mitali | 2956625.83 | 2892813.1883 | 63812.6416 | 2.2059 | OK
14 | Road-2 | 11 |  | 2839 | 1 | 505.57 | 546.35 | 40.78 | 60000 |  | 2446800 | 2450136.1786 | Jigatola |  |  |  | Road-2 | 2450136.1786 | 2180363.2806 | 269772.898 | 12.3728 | OK
15 | SS-2 | 11 |  | 2838 | 1 | 235.04 | 253.56 | 18.52 | 60000 |  | 1111200 | 1112715.1061 | Jigatola |  |  |  | SS-2 | 1112715.1061 | 1038383.624 | 74331.4821 | 7.1584 | OK
16 | Spare | 11 |  | 2772 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar | 11 |  | 2843 | 1 | 411.11 | 440.65 | 29.54 | 60000 |  | 1772400 | 1774816.6433 | Jigatola |  |  |  | Bou Bazar | 1774816.6433 | 1733264.614 | 41552.0293 | 2.3973 | OK
18 | BGB | 11 |  | 2764 | 1 | 137.32 | 152.88 | 15.56 | 60000 |  | 933600 | 934872.9509 | Jigatola |  |  |  | BGB | 934872.9509 | 780908.1047 | 153964.8463 | 19.7161 | OK
19 | Dhamondi-12 | 11 |  | 2763 | 1 | 328.2 | 354.88 | 26.68 | 60000 |  | 1600800 | 1602982.669 | Dhanmondi |  |  |  | Dhamondi-12 | 1602982.669 | 1582414.2509 | 20568.4182 | 1.2998 | OK
[9 empty] | Total | 19868453.4793 | 19841400 | 19868453.4793 | 0.13635
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Jigatola | at 33 KV level |  | 18265470.8102 | Including Switching
[5 empty] | Dhanmondi | at 33 KV level |  | 1602982.669
[5 empty] | Total = |  |  | 19868453.4793 | 0
11 KV SIDE of___JIGATOLA Switching S/S | [13 empty] | Month May-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
No. | Name of Feeders. |  | CF | Number |  | 2023-04-01 | 2023-04-01 |  |  | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar | 11 | 0 | 2851 | 1 | 603.31 | 603.31 | 0 | 60000 | 0 | 0 | 0
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated From source End | 0 | 0 | Dhanmondi
3 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 2184 | 200 | Estimated From source End | 0 | 0 | Jigatola
33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1843.5 | 1854.46 | 10.96 | 240000 | 0 | 3551040 | 3573446.2444
[9 empty] | Total |  | 3551040 | 3573446.2444
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit | 33 | 0 | 214393/37-2711 | 1 | 31.364 | 7975.877 | 7944.513 | 1000 | Estimated | 1487700 | 1445282.3546
[9 empty] | Total |  | 1487700 | 1445282.3546
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
|  | 33 | RECEIVE |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
|  | 33 |  |  | 1 |  |  | 0 |  |  | 0
[9 empty] | Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 | NET IMPORT | DHK61073 | 1 | 3991.98 | 3996.93 | 4.95 | 240000 |  | 1188000
2 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
[9 empty] | Total |  | 1188000 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Kamrangirchar 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 1445282.3546
| Satmasjid 33 KV SIDE |  | 1445282.3546 |  | 33 KV NET IMPORT |  |  | 1445282.3546 |  | ZIGATOLA OLD 11 KV NET IMPORT |  | 1188000
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 257282.3546
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 17.8%
| TOTAL IMPORT |  | 1445282.3546
11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming | 11 |  |  | 1 |  | 0 | 0 | 60000 | 0 |  | 0
16 | 33/11 kV T-2 Incoming | 11 |  | DHK61029 | 1.25 | 4793.84 | 4793.85 | 0.01 | 180000 | 2250 |  | 2995.1804
17 | 33/11 kV T-1 Incoming | 11 |  | DHK61028 | 1.32 | 1825.73 | 1830.29 | 4.56 | 180000 | 1083456 |  | 1442287.1742
[9 empty] | Total | 1085706 |  | 1445282.3546
ZIGATOLA OLD 11 KV SIDE
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | 11 |  | DHK60907 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Lalmatia SW |  |  |  | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | 11 |  | DHK66479 | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | 11 |  |  | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | 11 |  | DHK | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare | 11 |  |  | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | 11 |  | DHK60946 | 1 | 1096.72 | 1111.52 | 14.8 | 60000 |  | 888000 | 901151.3428 | Jigatola |  |  |  | Simanto Square | 901151.3428 | 923939.9984 | -22788.6557 | -2.4665 | OK
12 | Post Office | 11 |  | DHK61074 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | 11 |  |  | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | 11 |  | DHK61070 | 1 | 3387 | 3394.83 | 7.83 | 60000 |  | 469800 | 476757.7712 | Jigatola |  |  |  | Green Road Via Park | 476757.7712 | 578144.9892 | -101387.218 | -17.5366 | OK
15 | PWD Quarters 11 kV Saleq Grand | 11 |  | DHK61028 | 1 | 3627.12 | 3628.17 | 1.05 | 60000 |  | 63000 | 63933.0345 | Jigatola |  |  |  | PWD Quarters 11 kV Saleq Grand | 63933.0345 | 58239.1595 | 5693.875 | 9.7767 | OK
18 | Road No.-2 | 11 |  | DHK61035 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | 11 |  | DHK61033 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | 11 |  | DHK61030 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | 11 |  | DHK61031 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | 11 |  | DHK61032 | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | 11 |  | DHK61069 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 |  | 243284 | 1 | 83197 | 83536 | 339 | 10 |  | 3390 | 3440.2061 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 3440.2061 | 2749.3737 | 690.8325 | 25.1269 | OK
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 |  | 412277 | 1 | 38966 | 38966 | 0 | 10 |  | 0 | 0 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 1445282.3546 | 1424190 | 1445282.3546 | 1.481
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Jigatola | at 33 KV level |  | 1441842.1484
[5 empty] | Total = |  |  | 1441842.1484 | -3440.2061
33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | 0 | BD001907 | 1 | 345.3 | 348.37 | 3.07 | 240000 | 0 | 736800 | 741449.0383
1 | 34 kV Kamrangirchar Circuit-2 (O/H) | 33 | 0 | BD001912 | 1 | 424.99 | 428.23 | 3.24 | 240000 | 0 | 777600 | 782506.4769
[9 empty] | Total | 0 | 1514400 | 1523955.5152
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 | 33 | 0 | 0 | 1 | 136.14 | 153.69 | 17.55 | 360000 | 0 | 6318000 | 6313060.2033
10 | Dhaka Uddyan-2 | 33 | 0 | 0 | 1 | 135.18 | 153.28 | 18.1 | 360000 | 0 | 6516000 | 6510905.3948
[9 empty] | Total | 0 | 12834000 | 12823965.5981
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | RECEIVE | BD017107 | 1 | 89786.86 | 90469.03 | 682.17 | 1125 |  | 767441.25
| 33 kV Jigatala Incoming Circuit-1 | 33 |  | BD017098 | 1 | 43432.04 | 48947.36 | 5515.32 | 1125 |  | 6204735
| 33 kV Jigatala Incoming Circuit-2 | 33 |  | BD017097 | 1 | 43197.99 | 48882.9 | 5684.91 | 1125 |  | 6395523.75
| 33 kV Kamrangirchar Circuit-2 (O/H) | 33 |  | BD017108 | 1 | 73092.3 | 73739.05 | 646.75 | 1125 |  | 727593.75
[9 empty] | Total |  | 14095293.75 | 0
DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
DHAKA UDDYAN 33 KV SIDE
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017100 | 1 | 50494.8 | 57497.06 | 7002.26 | 1000 |  | 7002260
3 | 33/11 kV, 28/35 MVA T-3 (Future) | 33 |  | BD017075 | 1 |  | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017109 | 1 | 31216.83 | 38362.57 | 7145.74 | 1000 |  | 7145740
[9 empty] | Total |  | 14148000 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| KAMRANGIRCHAR 33 KV SIDE |  | 1523955.5152 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 14347921.1133
| JIGATOLA 33 KV SIDE |  | 12823965.5981 |  | 33 KV NET IMPORT |  |  | 14347921.1133 |  | 33 KV TX HV |  | 14148000
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 199921.1133
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.393%
| TOTAL IMPORT |  | 14347921.1133
11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD014060 | 1 | 49567.71 | 56544.83 | 6977.12 | 1000 | 6977120 |  | 7100025.7
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD014061 | 1 | 30657.98 | 37780.41 | 7122.43 | 1000 | 7122430 |  | 7247895.4133
[9 empty] | Total | 14099550 |  | 14347921.1133
DHAKA UDDYAN 11 KV SIDE
7 | Spare | 11 |  | BD014030 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | 11 |  | BD014031 | 1 | 47888.62 | 48238.67 | 350.05 | 1000 |  | 350050 | 356370.9019 | Adabor |  |  |  | D Block dhaka uddyan | 356370.9019 | 336094.4286 | 20276.4734 | 6.033 | OK
8 | Dill Mohammad O/H | 11 |  | BD014027 | 1 | 12080.08 | 13971.54 | 1891.46 | 1000 |  | 1891460 | 1925614.3584 | Adabor |  |  |  | Dill Mohammad O/H | 1925614.3584 | 1535875.5766 | 389738.7818 | 25.3757 | OK
9 | Turag O/H | 11 |  | BD014028 | 1 | 24338.76 | 24750.51 | 411.75 | 1000 |  | 411750 | 419185.0275 | Adabor |  |  |  | Turag O/H | 419185.0275 | 416257.7136 | 2927.3139 | 0.70325 | OK
10 | Nabadoy O/H | 11 |  | BD014025 | 1 | 32795.11 | 34037.39 | 1242.28 | 1000 |  | 1242280 | 1264712.0241 | Adabor |  |  |  | Nabadoy O/H | 1264712.0241 | 794833.108 | 469878.9161 | 59.1167 | FAULT
11 | Chandrima O/H | 11 |  | BD014024 | 1 | 2020.24 | 2884.39 | 864.15 | 1000 |  | 864150 | 879754.0777 | Adabor |  |  |  | Chandrima O/H | 879754.0777 | 833351.7058 | 46402.3718 | 5.5682 | OK
12 | Shyamoli Housing Project-2 | 11 |  | BD014029 | 1 | 21274.56 | 23461.67 | 2187.11 | 1000 |  | 2187110 | 2226602.9518 | Adabor |  |  |  | Shyamoli Housing Project-2 | 2226602.9518 | 2121967.5523 | 104635.3995 | 4.9311 | OK
13 | Spare | 11 |  | BD014022 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare | 11 |  | BD014026 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare | 11 |  | BD014023 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | 11 |  | BD013959 | 1 | 30498.01 | 33037.97 | 2539.96 | 1000 |  | 2539960 | 2585824.4138 | Satmasjid |  |  |  | U Lab | 2585824.4138 | 2172661.9695 | 413162.4443 | 19.0164 | OK
19 | Akota | 11 |  | BD014020 | 1 | 4552.75 | 5038.54 | 485.79 | 1000 |  | 485790 | 494561.9781 | Adabor |  |  |  | Akota | 494561.9781 | 469998.5745 | 24563.4036 | 5.2263 | OK
20 | Burigonga O/H | 11 |  | BD014019 | 1 | 3494.01 | 3859.78 | 365.77 | 1000 |  | 365770 | 372374.7602 | Adabor |  |  |  | Burigonga O/H | 372374.7602 | 363771.2706 | 8603.4895 | 2.3651 | OK
21 | Garden City | 11 |  | BD014021 | 1 | 76417.41 | 78655.82 | 2238.41 | 1000 |  | 2238410 | 2278829.2831 | Satmasjid |  |  |  | Garden City | 2278829.2831 | 2162138.7961 | 116690.487 | 5.397 | OK
22 | Avenue O/H | 11 |  | BD014017 | 1 | 10136.7 | 11015.72 | 879.02 | 1000 |  | 879020 | 894892.5874 | Adabor |  |  |  | Avenue O/H | 894892.5874 | 852994.2991 | 41898.2882 | 4.9119 | OK
23 | Chand Uddyan | 11 |  | BD014018 | 1 | 6109.27 | 6743.1 | 633.83 | 1000 |  | 633830 | 645275.1572 | Satmasjid |  |  |  | Chand Uddyan | 645275.1572 | 369834.2911 | 275440.8661 | 74.4768 | FAULT
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4416 | 1 | 1705.98 | 1720.85 | 14.87 | 100 |  | 1487 | 1513.851 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 1513.851 | 3591.0205 | -2077.1695 | -57.8434 | CHECK
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4412 | 1 | 227.66 | 251.33 | 23.67 | 100 |  | 2367 | 2409.7413 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 2409.7413 | 0 | 2409.7413 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 14347921.1133 | 14093434 | 14347921.1133 | 1.8057
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 8837992.2592
[5 empty] | Satmasjid | at 33 KV level |  | 5509928.8541
[5 empty] | Total = |  |  | 14347921.1133 | 0
132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 | 33 | IMPORT | 8993638E | 1 | 4168.459 | 4175.969 | 7.51 | 180000 | 0 | 1351800
9 | Satmosjid -2 | 33 |  | 8993669E | 1 | 5659.613 | 5705.38 | 45.767 | 180000 | 0 | 8238060
13 | Lalmatia | 33 |  |  | 1 | 5396.465 | 5413.706 | 17.241 | 180000 | 0 | 3103380
14 | Transformer-1 | 33 |  | 50147586E | 1 | 3020.456 | 3062.422 | 41.966 | 750000 | 0 | 31474500
15 | Transformer-2 | 33 |  | 50148569E | 1 | 2658.44 | 2701.161 | 42.721 | 750000 | 0 | 32040750
[8 empty] | Total Import/Export |  | 0 | 76208490
[9 empty] | Net Total | 76208490
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | RECEIVE |  | 1 |  |  | 0
| 33 KV GT-2 Incomming |  |  |  | 1 |  |  | 0
| 33 KV Satmosjid-1 Incomming |  |  |  | 1 |  |  | 0
Total Import/Export
[8 empty] | Net Total |  | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 |  | EXPORT | [7 empty] | 0
| Feeder No.2 | [9 empty] | 0
[9 empty] | Total |  | 0
SATMOSJID 132 KV SIDE
| 132/33 kV, 80/120 MVA T1 |  |  |  | 1
| 132/33 kV, 80/120 MVA T2 |  |  |  | 1
[9 empty] | Total |  | 0
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE (TARIFF POINT) |  | 76208490 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 76208490
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 76208490 |  | 33 KV NET IMPORT |  | 76208490
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 76208490
33 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming | 33 |  | 50147586 | 1 | 3020.456 | 3062.422 | 41.966 | 750000 | 31474500
10 | 132/33 kV, 80/120 MVA GT-2 Incoming | 33 |  | 50148569 | 1 | 2658.44 | 2701.161 | 42.721 | 750000 | 32040750
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 |  | 0 | 0 |  | 0 |  | 0
[9 empty] | Total | 63515250 |  | 76208490
SATMOSJID 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT |  |  |  | 0 | [9 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SICAM | 1 | 20.14 | 29.58 | 9.44 | 1000 | Estimated | 9903973.5 | 9621589.1239 |  | 0.16541 | Satmasjid 3/11 kv ss | 19243178.2478 | 33/11 kV, 20/28 MVA T-1 (HV) | 9621589.1239 | 9885465.3432 | -263876.2193 | -2.6693 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SICAM | 1 | 20.5 | 30.11 | 9.61 | 1000 | Estimated | 9903973.5 | 9621589.1239 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 9621589.1239 | 9885465.3432 | -263876.2193 | -2.6693 | OK
| 33 KV Feeders | [7 empty] | Total |  | 19807947 | 19243178.2478 |  |  |  |  | 33 KV Feeders | 19243178.2478 | 19770930.6863 | -527752.4386 | -2.6693 | OK
6 | BGB | 33 |  | 214393/40-2711 | 1 | 28.9757 | 31.1554 | 2.1797 | 1000 | Estimated | 9080100 | 8821206.0951 |  | 0.0035339 | BGB 33/11 KV SS | 8821206.0951 | BGB | 8821206.0951 | 7676216.9789 | 1144989.1162 | 14.9161 | OK
| Asad Gate Circuit-1 | 33 |  | 214393/44-2711 | 1 | 37.3466 | 46.0777 | 8.7311 | 1000 | Estimated | 8958087 | 8702671.9579 |  | 1.0942 | ASADGATE 33/11 KV SS | 17163040.0995 | Asad Gate Circuit-1 | 8702671.9579 | 8036851.528 | 665820.4299 | 8.2846 | OK
8 | Lalmatia Circuit-2 | 33 |  | SICAM | 1 | 37.78 | 58.14 | 20.36 | 1000 | Estimated | 13830210 | 13435879.8635 |  | 0.068319 | LALMATIA 33/11 KV SS | 13435879.8635 | Lalmatia Circuit-2 | 13435879.8635 | 13673470.3492 | -237590.4857 | -1.7376 | OK
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 74.8365 | 83.3379 | 8.5014 | 1000 | Estimated | 8708671.8 | 8460368.1416 |  | 1.481 | JIGATOLA OLD 33/11 KV SS | 1445282.3546 | Asad Gate Circuit-2 | 8460368.1416 | 5959347.1554 | 2501020.9862 | 41.968 | FAULT
13 | Jigatola U/G Circuit | 33 |  | 214393/37-2711 | 1 | 31.364 | 7975.877 | 7944.513 | 1000 | Estimated | 1487700 | 1445282.3546 |  | -0.49665 | JAPAN GARDEN 33/11 KV SS | 16099903.3397 | Jigatola U/G Circuit | 1445282.3546 | 1563073.5207 | -117791.1661 | -7.5359 | OK
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 16880 | 23770 | 6890 | 1000 | Estimated | 16572420 | 16099903.3397 |  |  |  |  | Japan Garden City-2 | 16099903.3397 | 18758199.7814 | -2658296.4418 | -14.1714 | OK
[9 empty] | Total |  | 58637188.8 | 56965311.7522 |  |  |  |  | 0 | 56965311.7522 | 55667159.3137 | 1298152.4386 | 2.332 | OK
[8 empty] | Grand Total |  | 76208490 | 78445135.8 | 76208490 | -2.8512
11 KV SIDE of___SATMOSJID 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming | 11 |  | DHK60998 | 1 | 4631.63 | 4684.51 | 52.88 | 180000 | 9518400 |  | 9538613.2897
24 | 33/11 kV T-2 Incoming | 11 |  | DHK61044 | 1 | 4717.6 | 4771.4 | 53.8 | 180000 | 9684000 |  | 9704564.9581
[9 empty] | Total | 19202400 |  | 19243178.2478
SATMOSJID 11 kV SIDE
16 | Lalmatia O/H | 11 |  | DHK61042 | 1 | 3082.55 | 3104.91 | 22.36 | 60000 |  | 1341600 | 1343819.1874 | Satmasjid |  |  |  | Lalmatia O/H | 1343819.1874 | 1490013 | -146193.8126 | -9.8116 | OK
16 | Asad Avenue (South) | 11 |  | DHK 60999 | 1 | 2890.2 | 2892.58 | 2.38 | 60000 |  | 142800 | 143036.2105 | Satmasjid |  |  |  | Asad Avenue (South) | 143036.2105 | 662697 | -519660.7895 | -78.416 | CHECK
17 | Madrasha Road | 11 |  | DHK61004 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | 11 |  | DHK61002 | 1 | 2288.59 | 2314.11 | 25.52 | 60000 |  | 1531200 | 1533732.8114 | Satmasjid |  |  |  | Bashbari | 1533732.8114 | 1584081 | -50348.1886 | -3.1784 | OK
19 | Road-27 | 11 |  | DHK61001 | 1 | 1423.31 | 1430.55 | 7.24 | 60000 |  | 434400 | 435118.5562 | Satmasjid |  |  |  | Road-27 | 435118.5562 | 408834 | 26284.5562 | 6.4292 | OK
20 | Boishakhi O/H | 11 |  | DHK61024 | 1 | 3945.95 | 3992.78 | 46.83 | 60000 |  | 2809800 | 2814447.7883 | Dhanmondi |  |  |  | Boishakhi O/H | 2814447.7883 | 2788272 | 26175.7883 | 0.93878 | OK
21 | Katasur O/H | 11 |  | DHK61003 | 1 | 3535.48 | 3557.69 | 22.21 | 60000 |  | 1332600 | 1334804.3002 | Satmasjid |  |  |  | Katasur O/H | 1334804.3002 | 1310922 | 23882.3002 | 1.8218 | OK
22 | Nurjahan Road | 11 |  | DHK61000 | 1 | 1746.44 | 1769.35 | 22.91 | 60000 |  | 1374600 | 1376873.7739 | Shyamoli |  |  |  | Nurjahan Road | 1376873.7739 | 1303083 | 73790.7739 | 5.6628 | OK
25 | polpar over head | 11 |  | DHK61003 | 1 | 1692.23 | 1725.79 | 33.56 | 60000 |  | 2013600 | 2016930.7661 | Dhanmondi |  |  |  | polpar over head | 2016930.7661 | 1975428 | 41502.7661 | 2.101 | OK
26 | Satmosjid Housing | 11 |  | DHK61043 | 1 | 2792.38 | 2792.38 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  | Satmosjid Housing | 0 | 273762 | -273762 | -100 | CHECK
27 | Physical College | 11 |  | DHK61041 | 1 | 3136.34 | 3172.69 | 36.35 | 60000 |  | 2181000 | 2184607.6683 | Satmasjid |  |  |  | Physical College | 2184607.6683 | 2123163 | 61444.6683 | 2.894 | OK
28 | Asad Avenue (North) | 11 |  | DHK61022 | 1 | 2725.31 | 2725.31 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  | Asad Avenue (North) | 0 | 551142 | -551142 | -100 | CHECK
29 | Spare Feeder | 11 |  | DHK61025 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | 11 |  | DHK61023 | 1 | 987.59 | 1015.9 | 28.31 | 60000 |  | 1698600 | 1701409.7136 | Dhanmondi |  |  |  | Ghraphic artch college | 1701409.7136 | 1615437 | 85972.7136 | 5.3219 | OK
31 | Mohammadpur O/H | 11 |  | DHK61025 | 1 | 2082.51 | 2104.86 | 22.35 | 60000 |  | 1341000 | 1343218.1949 | Shyamoli |  |  |  | Mohammadpur O/H | 1343218.1949 | 905103 | 438115.1949 | 48.405 | FAULT
32 | Bosila Feeder | 11 |  | DHK60997 | 1 | 3919.9 | 3970.07 | 50.17 | 60000 |  | 3010200 | 3015179.277 | Satmasjid |  |  |  | Bosila Feeder | 3015179.277 | 2816010 | 199169.277 | 7.0727 | OK
33 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIB 7375 | 1 | 5287.36 | 5415.28 | 127.92 | 60 |  |  | 0 | Satmasjid |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 19243178.2478 | 19211400 | 19243178.2478 | 0.16541
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Satmasjid | at 33 KV level |  | 9990298.011
[5 empty] | Shyamoli | at 33 KV level |  | 2720091.9688
[5 empty] | Dhanmondi | at 33 KV level |  | 6532788.268
[5 empty] | Total = |  |  | 19243178.2478 | 0
33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 | 33 |  | 38992490 (new) | 1 | 1.046 | 1.103 | 0.057 | 180000 | 0 | 10260 | 10260
| Kallyanpur to Japangarden-2 | 33 |  | 8993669E | 1 | 5659.613 | 5705.38 | 45.767 | 180000 | 0 | 8238060 | 8238060
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 16880 | 23770 | 6890 | 1000 | Estimated | 16572420 | 16099903.3397
[9 empty] | Total | 0 | 24820740 | 24348223.3397
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G | 33 | RECEIVE | DHK86051 | 1 | 2862.41 | 2888.25 | 25.84 | 270000 |  | 6976800
| kallyanpur U/G-2 | 33 |  | DHK61100 | 1 | 2744.32 | 2774.74 | 30.42 | 270000 |  | 8213400
[9 empty] | Total |  | 15190200
JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Japan Genden City | 33 |  | DHK15681 | 1 | 197.29 | 273.18 | 75.89 | 18000 |  | 1366020
0
[9 empty] | Total |  | 1366020
JAPAN GERDEN CITY 33 KV SIDE
| 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61080 | 1 | 4084.21 | 4133.56 | 49.35 | 180000 |  | 8883000
3 | 33/11 kV 20/28 MVA T-1 (HV) | 33 |  | 86052 | 1 | 4859.11 | 4894.24 | 35.13 | 180000 |  | 6323400
[9 empty] | Total |  | 15206400 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SENDING SIDE (Tariff Point) |  | 16572420 |  | EXPORT TO OTHER S/S |  |  | 1366020 |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 15206400
| IMPORT-2 |  |  |  | JAPAN GERDEN CITY 33 KV NET IMPORT |  |  | 15206400 |  | 33 KV TX HV SIDE |  | 15206400
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 16572420
11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK61079 | 1 | 5481.43 | 5521.1 | 39.67 | 160000 | 6347200 |  | 6320598.1559
10 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK61082 | 1 | 4541.4 | 4597.17 | 55.77 | 160000 | 8923200 |  | 8885801.8441
[9 empty] | Total | 15270400 |  | 15206400
JAPAN GERDEN CITY 11 KV SIDE
5 | Dhaka Uddyan | 11 |  | DHK86067 | 1 | 3249.24 | 3249.24 | 0 | 60000 |  | 0 | 0 | Adabor |  |  |  | Dhaka Uddyan | 0 | 291559.4944 | -291559.4944 | -100 | CHECK
| Shia Mosjid | 11 |  | DHK60950 | 1 | 3325.82 | 3353.91 | 28.09 | 60000 |  | 1685400 | 1677029.4105 | Shyamoli |  |  |  | Shia Mosjid | 1677029.4105 | 2148901.4585 | -471872.048 | -21.9588 | OK
6 | Shekhar Tek | 11 |  | DHK60977 | 1 | 2242.51 | 2275.45 | 32.94 | 60000 |  | 1976400 | 1966584.1503 | Adabor |  |  |  | Shekhar Tek | 1966584.1503 | 1955728.2956 | 10855.8547 | 0.55508 | OK
7 | Madrasha Road | 11 |  | DHK61083 | 1 | 1906.72 | 1925.96 | 19.24 | 60000 |  | 1154400 | 1148666.6379 | Shyamoli |  |  |  | Madrasha Road | 1148666.6379 | 1851342.7976 | -702676.1597 | -37.9549 | OK
8 | Baitul Aman Housing | 11 |  | DHK668115 | 1 | 3926.4 | 3971.87 | 45.47 | 60000 |  | 2728200 | 2714650.3131 | Adabor |  |  |  | Baitul Aman Housing | 2714650.3131 | 2915594.9437 | -200944.6306 | -6.8921 | OK
11 | Shyamoli Square | 11 |  | DHK86063 | 1 | 441.35 | 446.82 | 5.47 | 30000 |  | 164100 | 163284.9924 | Shyamoli |  |  |  | Shyamoli Square | 163284.9924 | 177575.3299 | -14290.3375 | -8.0475 | OK
12 | Mohammadi Housing | 11 |  | DHK60948 | 1 | 3696.61 | 3719.11 | 22.5 | 60000 |  | 1350000 | 1343295.1846 | Adabor |  |  |  | Mohammadi Housing | 1343295.1846 | 1763754.966 | -420459.7813 | -23.8389 | OK
13 | Chand Housing | 11 |  | DHK60867 | 1 | 2116.75 | 2131.68 | 14.93 | 60000 |  | 895800 | 891350.9825 | Satmasjid |  |  |  | Chand Housing | 891350.9825 | 1045654.7298 | -154303.7473 | -14.7567 | OK
14 | PC Culture Housing | 11 |  | DHK60979 | 1 | 3936.71 | 3977.85 | 41.14 | 60000 |  | 2468400 | 2456140.6176 | Adabor |  |  |  | PC Culture Housing | 2456140.6176 | 2397266.9537 | 58873.6638 | 2.4559 | OK
15 | Mehedibagh | 11 |  | DHK68121 | 1 | 2110.63 | 2158.29 | 47.66 | 60000 |  | 2859600 | 2845397.7111 | Adabor |  |  |  | Mehedibagh | 2845397.7111 | 2727821.0307 | 117576.6804 | 4.3103 | OK
16 | 33/11 kV Incoming (Spare) | 11 |  |  | 1 |  | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer | 11 |  |  | 1 | 630551 | 636966 | 6415 | 1 |  |  | 0 | Adabor |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15206400 | 15282300 | 15206400 | -0.49665
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Adabor | at 33 KV level |  | 11326067.9767
[5 empty] | Shyamoli | at 33 KV level |  | 2988981.0408
[5 empty] | Satmasjid | at 33 KV level |  | 891350.9825
[5 empty] | Total = |  |  | 15206400 | 0
132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | #REF! |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) | 132 |  | 42627810 | 1 | 121.203 | 134.079 | 12.876 | 960000 | 0 | 12360960
2 | Dhaka University-1 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) | 132 |  | 42627812 | 1 | 122.247 | 135.244 | 12.997 | 960000 | 0 | 12477120
3 | Dhaka University-2 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 24838080
[9 empty] | Net Total | 24838080
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 | 132 |  | 2877 | 1 | 97.01 | 107.3 | 10.29 | 1200000 |  | 12348000
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 | 132 |  | 2811 | 1 | 97.8 | 108.18 | 10.38 | 1200000 |  | 12456000
[8 empty] | Total Import/Export |  | 0 | 24804000
[8 empty] | Net Total |  | 24804000
DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Dhaka University | 132 | 0 | SIEM0480 | 1 | 48558 | 59905 | 11347 | 1000 |  | 11347000
[9 empty] | Total |  | 11347000
DHAKA UNIVERSITY 132 KV SIDE
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | 2752 | 1 | 185.02 | 190.62 | 5.6 | 1200000 |  | 6720000
4 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | 2867 | 1 | 203 | 208.59 | 5.59 | 1200000 |  | 6708000
[9 empty] | Total |  | 13428000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (TARIFF POINT) |  | 24838080 |  | EXPORT TO OTHER S/S |  |  | 11347000 |  | 132 KV NET IMPORT |  | 13428000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 13428000 |  | 33 KV NET IMPORT |  | 13341600
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 86400
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.6434%
| 132 KV TOTAL IMPORT |  | 24838080
33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  | 2769 | 1 | 306.25 | 315.51 | 9.26 | 720000 | 6667200
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  | 2830 | 1 | 335.17 | 344.44 | 9.27 | 720000 | 6674400
[9 empty] | Total | 13341600 |  | 0
DHAKA UNIVERSITY 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  | 2751 | 1.15 | 27.97 | 29.58 | 1.61 | 240000 |  | 444360 | 446503.3607 |  | 0.24911 | DHAKA UNIVERSITY 33/11 KV SS | 1917564.9326 | 33/11 kV 28/35 MVA T-1 | 446503.3607 | 254704.8127 | 191798.548 | 75.3023 | FAULT
8 | 33/11 kV 28/35 MVA T-2 | 33 |  | 4253 | 1 | 39.16 | 43.14 | 3.98 | 240000 |  | 955200 | 959807.3862 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 959807.3862 | 662232.513 | 297574.8733 | 44.9351 | FAULT
13 | 33/11 kV 28/35 MVA T-3 | 33 |  | 2808 | 1 | 12.28 | 14.4 | 2.12 | 240000 |  | 508800 | 511254.1856 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 511254.1856 | 359012.4979 | 152241.6878 | 42.4057 | FAULT
| 33 KV Feeders | [7 empty] | Total |  | 1908360 | 1917564.9326 |  |  |  |  | 33 KV Feeders | 1917564.9326 | 1275949.8236 | 641615.109 | 50.2853 | FAULT
2 | Spare | 33 |  | 2805 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 | 33 |  | 2804 | 1.48 | 123.49 | 130.96 | 7.47 | 360000 |  | 3980016 | 3999213.5198 |  | 1.6496 | BB AVENUE 33/11 KV SS | 6357735.1875 | BB Avenue-1 | 3999213.5198 | 0 | 3999213.5198 | #DIV/0! | #DIV/0!
3 | DMC Circuit-1 | 33 |  | 2861 | 1.45 | 142.62 | 145.81 | 3.19 | 360000 |  | 1665180 | 1673211.9592 |  |  |  |  | DMC Circuit-1 | 1673211.9592 | 2912367.6011 | -1239155.6419 | -42.5481 | CHECK
4 | Biddyut Bhaban Circuit-1 | 33 |  | 2858 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  | 0.27387 | DMC 33/11 KV SS | 5066299.8799 | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 | 33 |  | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Biddyut Bhaban Circuit-2 | 0 | 971516.9284 | -971516.9284 | -100 | CHECK
10 | DMC Circuit-2 | 33 |  | 2803 | 1 | 266.05 | 275.43 | 9.38 | 360000 |  | 3376800 | 3393087.9207 |  | 0.39047 | BIDDYUT BHABAN 33/11 KV SS | 0 | DMC Circuit-2 | 3393087.9207 | 4544661.5864 | -1151573.6657 | -25.339 | OK
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 169.45 | 175.97 | 6.52 | 360000 |  | 2347200 | 2358521.6677 |  |  |  |  | BB Avenue-2 | 2358521.6677 | 6036504.0607 | -3677982.393 | -60.929 | CHECK
12 | Spare | 33 |  | 2806 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 11369196 | 11424035.0674 |  |  |  |  | 0 | 11424035.0674 | 14465050.1764 | -3041015.109 | -21.0232 | OK
[8 empty] | Grand Total |  | 13341600 | 13277556 | 13341600 | 0.48235
11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 33.9 | 36.01 | 2.11 | 250000 | 527500 |  | 529589.268
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 36.32 | 40.08 | 3.76 | 250000 | 940000 |  | 943723.0558
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 11.35 | 13.12 | 1.77 | 250000 | 442500 |  | 444252.6087
[7 empty] | 0 |  | Total | 1910000 |  | 1917564.9326
| DHAKA UNIVERSITY 11 kV SIDE | [5 empty] | 0
| Mokarom Bhabon | 11 |  | 2761 | 1 | 40.93 | 44.12 | 3.19 | 60000 |  | 191400 | 191876.7922 | Ramna |  |  |  | Mokarom Bhabon | 191876.7922 | 99478.4731 | 92398.319 | 92.8827 | FAULT
4 | 11 kV Shaid Minar RMU | 11 |  | 2850 | 1 | 99.47 | 105.12 | 5.65 | 60000 |  | 339000 | 339844.4752 | Ramna |  |  |  | 11 kV Shaid Minar RMU | 339844.4752 | 272802.9294 | 67041.5458 | 24.5751 | OK
5 | 11 kV Shaidulla Hall | 11 |  | 2851 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  | 2784 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  | 2799 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | 11 |  | 2836 | 1 | 76.97 | 81.98 | 5.01 | 60000 |  | 300600 | 301348.8178 | Ramna |  |  |  | MBA Bhabon | 301348.8178 | 181258.3222 | 120090.4956 | 66.2538 | FAULT
11 | Suprime Court | 11 |  | 2835 | 1 | 34.09 | 39.19 | 5.1 | 60000 |  | 306000 | 306762.2696 | Ramna |  |  |  | Suprime Court | 306762.2696 | 225199.7337 | 81562.536 | 36.2179 | OK
12 | Karjon Hall | 11 |  | 2853 | 1 | 39.47 | 45.01 | 5.54 | 60000 |  | 332400 | 333228.0341 | Ramna |  |  |  | Karjon Hall | 333228.0341 | 248391.0342 | 84836.9999 | 34.1546 | OK
13 | Spare | 11 |  | 2852 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | 11 |  | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | Swimming Pool | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | 2838 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU | 11 |  | 2772 | 1 | 47.4 | 54.79 | 7.39 | 60000 |  | 443400 | 444504.5437 | Ramna |  |  |  | Police Head Quarter RMU | 444504.5437 | 347869.5073 | 96635.0363 | 27.7791 | OK
17 | Spare | 11 |  | 2843 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare | 11 |  | 2764 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Spare | 11 |  | 2763 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 1917564.9326 | 1912800 | 1917564.9326 | 0.24911
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 1917564.9326
[5 empty] | Total = |  |  | 1917564.9326 | 0
33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 | 33 | 0 | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 | 0 | 0 | 0
[9 empty] | Total | 0 | 0 | 0
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 67946.37 | 88662.91 | 20716.54 | 270 |  | 5593465.8
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 21216.13 | 21216.15 | 0.02 | 270 |  | 5.4
| Dhaka University Incoming-1 | 33 |  | DHK-C9341 | 1 |  | 0 | 0 | 270 |  | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58472.99 | 58472.99 | 0 | 270 |  | 0
| Dhaka University Incoming-2 | 33 |  | DHK-C9343 | 1 | 45329.41 | 45329.41 | 0 | 270 |  | 0
[9 empty] | Total |  | 5593471.2 | 0
BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
0
0
[9 empty] | Total |  | 0
BIDDYUT BHABAN 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-C9342 | 1 | 51089.98 | 60685.49 | 9595.51 | 270 |  | 2590787.7
3 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK-C9308 | 1 | 80598.32 | 91727.57 | 11129.25 | 270 |  | 3004897.5
[9 empty] | Total |  | 5595685.2
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| DHAKA UNIVERSITY 33 KV SIDE |  | 5593471.2 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 5593471.2
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 5593471.2 |  | 33 KV TX HV SIDE |  | 5595685.2
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -2214
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.03958%
| TOTAL IMPORT |  | 5593471.2
11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK-C9316 | 1 | 28337.73 | 39063.58 | 10725.85 | 240 | 2574204 |  | 2583041.6638
10 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK-C9377 | 1 | 26556.99 | 39057.53 | 12500.54 | 240 | 3000129.6 |  | 3010429.5362
[9 empty] | Total | 5574333.6 |  | 5593471.2
BIDDYUT BHABAN 11 KV SIDE
6 | Segunbagicha | 11 |  | DHK-C9360 | 1 | 50757.84 | 61185.99 | 10428.15 | 60 |  | 625689 | 628132.1417 | Ramna |  |  |  | Segunbagicha | 628132.1417 | 537969.1226 | 90163.0191 | 16.7599 | OK
| Secretariat RMU | 11 |  | DHK-C9379 | 1 | 63179.05 | 66319.31 | 3140.26 | 60 |  | 188415.6 | 189151.3106 | Ramna |  |  |  | Secretariat RMU | 189151.3106 | 134553.0082 | 54598.3023 | 40.5775 | FAULT
7 | NBR RMU | 11 |  | DHK-C9319 | 1 | 28250.97 | 35791.29 | 7540.32 | 60 |  | 452419.2 | 454185.7713 | Ramna |  |  |  | NBR RMU | 454185.7713 | 330913.1213 | 123272.65 | 37.2523 | OK
8 | Ramna 11 kV Sw/S-2 | 11 |  | DHK-C9364 | 1 | 60208.43 | 81944.91 | 21736.48 | 60 |  | 1304188.8 | 1309281.295 | Ramna |  |  |  | Ramna 11 kV Sw/S-2 | 1309281.295 | 950756.2697 | 358525.0253 | 37.7095 | OK
11 | Ramna 11 kV Sw/S-1 | 11 |  | DHK-C9375 | 1 | 29996.47 | 30061.75 | 65.28 | 60 |  | 3916.8 | 3932.094 | Ramna |  |  |  | Ramna 11 kV Sw/S-1 | 3932.094 | 95377.547 | -91445.453 | -95.8773 | CHECK
12 | Family Planning | 11 |  | DHK-C9378 | 1 | 26353.12 | 33829.12 | 7476 | 60 |  | 448560 | 450311.5022 | Ramna |  |  |  | Family Planning | 450311.5022 | 375762.3158 | 74549.1864 | 19.8395 | OK
13 | Muktijuddho Montranalaya | 11 |  | DHK-C9376 | 1 | 94472.83 | 109833.69 | 15360.86 | 60 |  | 921651.6 | 925250.3935 | Ramna |  |  |  | Muktijuddho Montranalaya | 925250.3935 | 859164.6271 | 66085.7663 | 7.6919 | OK
14 | Purana Palton | 11 |  | DHK-C9318 | 1 | 32574.67 | 38036.29 | 5461.62 | 60 |  | 327697.2 | 328976.7665 | Ramna |  |  |  | Purana Palton | 328976.7665 | 292826.2357 | 36150.5309 | 12.3454 | OK
15 | Tip Top Feeder | 11 |  | DHK-C9318 | 1 | 21243.74 | 42816.99 | 21573.25 | 60 |  | 1294395 | 1299449.2529 | Kakrail |  |  |  | Tip Top Feeder | 1299449.2529 | 1259824.9455 | 39624.3074 | 3.1452 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 |  | DHKD3784 | 1 | 326797 | 331579 | 4782 | 1 |  | 4782 | 4800.6724 | Ramna |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 4800.6724 | 5186.7071 | -386.0348 | -7.4428 | OK
[9 empty] | Grand Total | 5593471.2 | 5571715.2 | 5593471.2 | 0.39047
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 4294021.9471
[5 empty] | Kakrail | at 33 KV level |  | 1299449.2529
[5 empty] | Total = |  |  | 5593471.2 | 0
33 KV SIDE of___ DMCH 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 | 33 | 0 | 2861 | 1.45 | 142.62 | 145.81 | 3.19 | 360000 | 0 | 1665180 | 1673211.9592
10 | DMC Circuit-2 | 33 | 0 | 2803 | 1 | 266.05 | 275.43 | 9.38 | 360000 | 0 | 3376800 | 3393087.9207
[9 empty] | Total | 0 | 5041980 | 5066299.8799
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 365.9 | 377.52 | 11.62 | 240000 | 0 | 2788800 | 2790717.3239
[9 empty] | Total |  | 2788800 | 2790717.3239
DMCH 33 KV SIDE (RECEIVING)
| 33 kV DU Incoming Circuit-1 | 33 |  | 00000072 | 1 | 71560528 | 73279888 | 1719360 | 1 |  | 1719360
| 33 kV Dhanmondi Incoming | 33 |  | 00000082 | 1 |  | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 | 33 |  | 00000081 | 1 |  | 0 | 0 | 1 |  | 0
[9 empty] | Total |  | 1719360 | 0
DMCH 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
DMCH 33 KV SIDE
| 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | 00000069 | 1 | 115487760 | 118781280 | 3293520 | 1 |  | 3293520
2 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | 00000088 | 1 |  | 0 | 0 | 1 |  | 0
[9 empty] | Total |  | 3293520 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| DHAKA UNIVERSITY 33 kV SIDE |  | 5066299.8799 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 7857017.2037
| DHANMONDI 33 kV SIDE |  | 2790717.3239 |  | 33 KV NET IMPORT |  |  | 7857017.2037 |  | 33 KV TX HV SIDE |  | 7857017.2037
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7857017.2037
11 KV SIDE of___DMCH 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000056 | 1 | 114349456 | 117615056 | 3265600 | 1 | 3265600 |  | 3282482.0409
14 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000034 | 1 | 138712464 | 143263472 | 4551008 | 1 | 4551008 |  | 4574535.1629
[9 empty] | Total | 7816608 |  | 7857017.2037
DMCH 11 KV SIDE
6 | Nearest O/H | 11 |  | 00000126 | 1 | 6636144 | 6865423 | 229279 | 1 |  | 229279 | 229906.9253 | Ramna |  |  |  | Nearest O/H | 229906.9253 | 163844.7151 | 66062.2102 | 40.32 | FAULT
| Jagannath Hall | 11 |  | 00000002 | 1 | 2337514 | 2433494 | 95980 | 1 |  | 95980 | 96242.8599 | Ramna |  |  |  | Jagannath Hall | 96242.8599 | 97793.3113 | -1550.4514 | -1.5854 | OK
7 | Samsun Nahar Hall | 11 |  | 00000024 | 1 | 8451499 | 8763059 | 311560 | 1 |  | 311560 | 312413.2678 | Ramna |  |  |  | Samsun Nahar Hall | 312413.2678 | 232339.4612 | 80073.8067 | 34.4641 | OK
8 | Spare, 4L | 11 |  | 00000184 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | 11 |  | 00000023 | 1 | 19772992 | 20238430 | 465438 | 1 |  | 465438 | 466712.6927 | Lalbag |  |  |  | Board Office O/H, (5L) | 466712.6927 | 425563.4013 | 41149.2914 | 9.6694 | OK
10 | OT- Complex | 11 |  | 00000167 | 1 | 4882428 | 5287027 | 404599 | 1 |  | 404599 | 405707.0733 | Ramna |  |  |  | OT- Complex | 405707.0733 | 354421.4088 | 51285.6644 | 14.4703 | OK
11 | Alia Mdrasha O/H, (7L) | 11 |  | 00000148 | 1 | 9172738 | 9243737 | 70999 | 1 |  | 70999 | 71193.4446 | Lalbag |  |  |  | Alia Mdrasha O/H, (7L) | 71193.4446 | 84487.4411 | -13293.9965 | -15.7349 | OK
12 | Majed Sordar Road | 11 |  | 00000164 | 1 | 50061716 | 51746392 | 1684676 | 1 |  | 1684676 | 1689289.8138 | Bangshal |  |  |  | Majed Sordar Road | 1689289.8138 | 1571550.572 | 117739.2417 | 7.4919 | OK
15 | Chankharpool, 9L | 11 |  | 00000001 | 1 | 43302856 | 44457492 | 1154636 | 1 |  | 1154636 | 1157798.1959 | Bangshal |  |  |  | Chankharpool, 9L | 1157798.1959 | 1120139.9455 | 37658.2504 | 3.3619 | OK
16 | Shahidullah College O/H, (10L) | 11 |  | 00000003 | 1 | 12057891 | 12322570 | 264679 | 1 |  | 264679 | 265403.8751 | Lalbag |  |  |  | Shahidullah College O/H, (10L) | 265403.8751 | 265365.9145 | 37.9605 | 0.014305 | OK
17 | Ananda Bazar | 11 |  | 00000111 | 1 | 14330765 | 14499445 | 168680 | 1 |  | 168680 | 169141.9631 | Ramna |  |  |  | Ananda Bazar | 169141.9631 | 553976.8972 | -384834.9341 | -69.4677 | CHECK
18 | Hosseni Dalan O/H, (12L) | 11 |  | 00000165 | 1.5 | 25661818 | 26760014 | 1098196 | 1 |  | 1647294 | 1651805.4359 | Lalbag |  |  |  | Hosseni Dalan O/H, (12L) | 1651805.4359 | 1407987.415 | 243818.0209 | 17.3168 | OK
19 | Badrun Nessa College | 11 |  | 00000006 | 1 | 18016036 | 18502514 | 486478 | 1 |  | 486478 | 487810.3149 | Lalbag |  |  |  | Badrun Nessa College | 487810.3149 | 440150.3104 | 47660.0045 | 10.8281 | OK
20 | Dhaka Medical College, Unit-II | 11 |  | 00000125 | 1 | 10723614 | 11041413 | 317799 | 1 |  | 317799 | 318669.3545 | Ramna |  |  |  | Dhaka Medical College, Unit-II | 318669.3545 | 273261.5625 | 45407.7921 | 16.617 | OK
21 | Spare, 15L | 11 |  | 00000163 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | 11 |  | 00000127 | 1 | 18562194 | 19088354 | 526160 | 1 |  | 526160 | 527600.9918 | Ramna |  |  |  | Sheikh Hasina National Burn Institute | 527600.9918 | 459348.3579 | 68252.6338 | 14.8586 | OK
23 | Aux. Transformer, AT-1 | 0.415 |  | DHKF-7804 | 1 | 2396.38 | 2469.39 | 73.01 | 100 |  | 7301 | 7320.9952 | Ramna |  |  |  | Aux. Transformer, AT-1 | 7320.9952 | 6798.4735 | 522.5217 | 7.6859 | OK
24 | Aux. Transformer, AT-2 | 0.415 |  | DHKF-7802 | 1 |  | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7857017.2037 | 7835558 | 7857017.2037 | 0.27387
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2067003.4309
[5 empty] | Lalbag | at 33 KV level |  | 2942925.7632
[5 empty] | Bangshal | at 33 KV level |  | 2847088.0097
[5 empty] | Total = |  |  | 7857017.2037 | 0
33 KV SIDE of___ BB AVENEU 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 | 33 | 0 | 2804 | 1.48 | 123.49 | 130.96 | 7.47 | 360000 | 0 | 3980016 | 3999213.5198
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 169.45 | 175.97 | 6.52 | 360000 | 0 | 2347200 | 2358521.6677
[9 empty] | Total | 0 | 6327216 | 6357735.1875
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 | 33 |  | BD 017078 | 1 |  |  | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 | 33 |  | BD 017090 | 1 | 60953.8 | 63228.14 | 2274.34 | 1125 |  | 2558632.5
[9 empty] | Total | 0 | 2558632.5 | 0
BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
BB AVENEU 33 KV SIDE
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD 017093 | 1 | 78534.85 | 83011.26 | 4476.41 | 1000 |  | 4476410
3 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD 017094 | 1 | 46786.2 | 48613.46 | 1827.26 | 1000 |  | 1827260
[9 empty] | Total |  | 6303670 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 6357735.1875 |  | EXPORT TO OTHER S/S |  |  | 0 |  | BB AVENEU 33 KV NET IMPORT |  | 6357735.1875
[5 empty] | BB AVENEU 33 KV NET IMPORT |  |  | 6357735.1875 |  | 33 KV TX HV SIDE |  | 6303670
[10 empty] | LOSS UNITS=> |  | 54065.1875
[10 empty] | LOSS % IN => |  | 0.8504%
| TOTAL IMPORT |  | 6357735.1875
11 KV SIDE of___BB AVENEU 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD 014052 | 1 | 78821.6 | 83276.64 | 4455.04 | 1000 | 4455040 |  | 4524154.1271
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD 014055 | 1 | 46326.14 | 48131.71 | 1805.57 | 1000 | 1805570 |  | 1833581.0604
[9 empty] | Total | 6260610 |  | 6357735.1875
BB AVENEU 11 KV SIDE
6 | Secratariet East | 11 |  | BD 013966 | 1 | 2923.08 | 3164.56 | 241.48 | 1000 |  | 241480 | 245463.3743 | Ramna |  |  |  | Secratariet East | 245463.3743 | 205450.3207 | 40013.0536 | 19.4758 | OK
| Taher Bag O/H | 11 |  | BD 014045 | 1 | 16197.15 | 16925.42 | 728.27 | 1000 |  | 728270 | 740283.3012 | Narinda |  |  |  | Taher Bag O/H | 740283.3012 | 638299.1738 | 101984.1275 | 15.9775 | OK
7 | Al Raji Complex | 11 |  | BD 013983 | 1 | 11427.28 | 12207.81 | 780.53 | 1000 |  | 780530 | 793405.3649 | Ramna |  |  |  | Al Raji Complex | 793405.3649 | 647345.0524 | 146060.3125 | 22.563 | OK
8 | Raduni | 11 |  | BD 013999 | 1 | 23970.4 | 25230.43 | 1260.03 | 1000 |  | 1260030 | 1280815.0384 | Ramna |  |  |  | Raduni | 1280815.0384 | 1081221.6149 | 199593.4235 | 18.46 | OK
9 | Sundor Bon Square O/H | 11 |  | BD 013954 | 1 | 11288.72 | 11796.22 | 507.5 | 1000 |  | 507500 | 515871.5523 | Narinda |  |  |  | Sundor Bon Square O/H | 515871.5523 | 443075.0713 | 72796.481 | 16.4298 | OK
10 | Shromo Bhobon O/H | 11 |  | BD 013985 | 1 | 11101.22 | 11614.06 | 512.84 | 1000 |  | 512840 | 521299.6391 | Ramna |  |  |  | Shromo Bhobon O/H | 521299.6391 | 858829.3506 | -337529.7115 | -39.3011 | OK
11 | Nawabpur Road | 11 |  | BD 013953 | 1 | 16889.08 | 17725.04 | 835.96 | 1000 |  | 835960 | 849749.7199 | Narinda |  |  |  | Nawabpur Road | 849749.7199 | 684281.5421 | 165468.1778 | 24.1813 | OK
12 | Spair | 11 |  | BD 013991 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | BD 013942 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | 11 |  | BD 013984 | 1 | 9425.66 | 9842.75 | 417.09 | 1000 |  | 417090 | 423970.1788 | Ramna |  |  |  | Ahad Police Box | 423970.1788 | 542020.0923 | -118049.9135 | -21.7796 | OK
17 | Nearest O/H | 11 |  | BD 013997 | 1 | 2160.72 | 2274.44 | 113.72 | 1000 |  | 113720 | 115595.8875 | Ramna | CHECK |  |  | Nearest O/H | 115595.8875 | 107502.4832 | 8093.4043 | 7.5286 | OK
18 | Natab Bhaban | 11 |  | BD 014000 | 1 | 4267.75 | 4442.04 | 174.29 | 1000 |  | 174290 | 177165.0302 | Ramna |  |  |  | Natab Bhaban | 177165.0302 | 170172.4116 | 6992.6186 | 4.1091 | OK
19 | Spare | 11 |  | BD 014043 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | 11 |  | BD 013956 | 1 | 1386.15 | 1395.25 | 9.1 | 1000 |  | 9100 | 9250.1106 | Ramna |  |  |  | Awami League Party Office | 9250.1106 | 8933.9499 | 316.1607 | 3.5389 | OK
21 | Khaddar Bazar | 11 |  | BD 014012 | 1 | 8542.4 | 8928.66 | 386.26 | 1000 |  | 386260 | 392631.6173 | Ramna |  |  |  | Khaddar Bazar | 392631.6173 | 371633.9985 | 20997.6188 | 5.6501 | OK
22 | Bangobondu National Stidium | 11 |  | BD 014008 | 1 | 5576.75 | 5862.17 | 285.42 | 1000 |  | 285420 | 290128.194 | Ramna |  |  |  | Bangobondu National Stidium | 290128.194 | 269402.3422 | 20725.8518 | 7.6933 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4418 | 1 | 1107.72 | 1124.63 | 16.91 | 100 |  | 1691 | 1718.8942 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 1718.8942 | 8336.6573 | -6617.7631 | -79.3815 | CHECK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 38.09 | 41.9 | 3.81 | 100 |  | 381 | 387.2849 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 387.2849 | 0 | 387.2849 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 6357735.1875 | 6254562 | 6357735.1875 | 1.6496
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 4251830.6142
[5 empty] | Narinda | at 33 KV level |  | 2105904.5733
[5 empty] | Total = |  |  | 6357735.1875 | 0
33 KV SIDE of___ KALLYANPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
[9 empty] | Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 0
[5 empty] | KALLYANPUR 33 KV NET IMPORT |  |  | 0 |  | KALLYANPUR 11 KV NET IMPORT |  | 0
[5 empty] | TOTAL EXPORT |  |  | 0 |  | LOSS UNITS=> |  | 0
[5 empty] | 132KV NET LOSS => |  |  | #DIV/0! |  | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 0
11 KV SIDE of___KALLYANPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming | 11 |  | 74819926 | 1 |  | 0 | 0
[7 empty] | 0 |  | Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE | [5 empty] | 0
A | From Kallyanpur S/S. | [5 empty] | 0
| 11 KV Gano Bhavan RMU | 11 |  | DHK14997 | 1 | 995.65 | 995.68 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar |  |  |  | 11 KV Gano Bhavan RMU | 1230 | 820 | 410 | 50 | FAULT
| 11 KV Beribandh Feeder. | 11 |  | DHK14960 | 1 | 9628.58 | 9633.08 | 4.5 | 40000 |  | 180000 | 184500 | Adabor |  |  |  | 11 KV Beribandh Feeder. | 184500 | 478880 | -294380 | -61.4726 | CHECK
| 11 KV Adabor O/H | 11 |  | DHK14957 | 1 | 4246.2 | 4319.26 | 73.06 | 40000 |  | 2922400 | 2995460 | Adabor |  |  |  | 11 KV Adabor O/H | 2995460 | 2815060 | 180400 | 6.4084 | OK
| 11 KV Mansurabad | 11 |  | 77816681 | 1 | 51055.21 | 51326.05 | 270.84 | 8000 |  | 2166720 | 2220888 | Adabor |  |  |  | 11 KV Mansurabad | 2220888 | 1985384 | 235504 | 11.8619 | OK
| 11 KV Ring Road Feeder | 11 |  | 77816675 | 1 | 41495.43 | 41632.55 | 137.12 | 8000 |  | 1096960 | 1124384 | Adabor |  |  |  | 11 KV Ring Road Feeder | 1124384 | 1028772 | 95612 | 9.2938 | OK
| 11 KV Sewarage Pump | 11 |  | DHK14959 | 1 | 1978.23 | 1991.3 | 13.07 | 40000 |  | 522800 | 535870 | Adabor |  |  |  | 11 KV Sewarage Pump | 535870 | 495690 | 40180 | 8.1059 | OK
| 11 KV Technical School (DPDC) | 11 |  | DHK15019 | 1 | 8022.92 | 8076.21 | 53.29 | 40000 |  | 2131600 | 2184890 | Adabor |  |  |  | 11 KV Technical School (DPDC) | 2184890 | 2091410 | 93480 | 4.4697 | OK
| 11 KV Goidertek (DPDC) | 11 |  | DHK14996 | 1 | 9327.58 | 9341.2 | 13.62 | 40000 |  | 544800 | 558420 | Adabor |  |  |  | 11 KV Goidertek (DPDC) | 558420 | 514550 | 43870 | 8.5259 | OK
B | From Agargaon S/S. | 11 | [9 empty] | 0
| 11 KV P.C Culture Housing | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H | 11 |  | DHK-15026 | 1 | 9139.22 | 9151.97 | 12.75 | 40000 |  | 510000 | 522750 | Shere b.nagar
| 11 KV Nearest RMU | 11 |  | DHK-15027 | 1 | 3840.99 | 3855.49 | 14.5 | 40000 |  | 580000 | 594500 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar | 11 |  | DHK-15025 | 1 | 3974.03 | 3975.03 | 1 | 40000 |  | 40000 | 41000 | Shere b.nagar
| 11 KV BCFCC Feeder. | 11 |  | DHK-15024 | 1 | 1038.1 | 1038.1 | 0 | 40000 |  | 0 | 0
| 11 KV NEC Feeder. | 11 |  | DHK-15023 | 1 | 431.56 | 431.56 | 0 | 40000 |  | 0 | 0
| 11 KV Manik Mia Feeder. | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0
[6 empty] | Export To Desco |  | 404875 | Grand Total | 0 | 10696480 | 10963892 | 2.5
DESCO | 11 kV Tolarbugh | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Tolarbugh | 0 | 82 | -82 | -100 | CHECK
| 11 kV South Bisil | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Lalkhuthy | 0 | 888880 | -888880 | -100 | CHECK
| 11 kV Baghbari | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Baghbari | 0 | 1870830 | -1870830 | -100 | CHECK
| 11 kV Paikpara O/H | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara Sw/S | 0 | 1163260.2 | -1163260.2 | -100 | CHECK
[9 empty] | Grand Total | 0 | 0 | 0 | #DIV/0!
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 9804412
[5 empty] | Shere b.nagar | at 33 KV level |  | 754605
[5 empty] | Satmasjid | at 33 KV level
[5 empty] | DESCO | at 33 KV level |  | 404875
[5 empty] | Total = |  |  | 10963892 | 0
33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 | 33 | 0 | 30799147 | 1 | 1437.29 | 1464.97 | 27.68 | 240000 | 0 | 6643200 | 6685117.0618
[9 empty] | Total | 0 |  | 6685117.0618
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
[9 empty] | Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
| Kamrangirchar Incoming | 33 | EXPORT |  |  |  |  | 0 | 240000 |  | 0
| Lalbagh Incoming | 33 | [5 empty] | 0 | 240000 |  | 0
[9 empty] | Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV SIDE |  | 6685117.0618 |  | EXPORT TO OTHER S/S |  |  | 0 |  | KALLYANPUR 33 KV NET IMPORT |  | 6685117.0618
| IMPORT-2 |  |  |  | KALLYANPUR 33 KV NET IMPORT |  |  | 6685117.0618 |  | KALLYANPUR 11 KV NET IMPORT |  | 6685117.0618
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6685117.0618
11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar-2 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0
[9 empty] | Total | 0 |  | 6685117.0618
Kamrangirchar-2 11 KV SIDE
1 | Nizambag | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 973062.72 | 972380.6635 | Kamrangirchar | 80 |  |  | Nizambag | 972380.6635 | 713015.5208 | 259365.1428 | 36.3758 | OK
2 | Merry Stopes | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 364898.52 | 364642.7488 | Kamrangirchar | 30 |  |  | Merry Stopes | 364642.7488 | 297089.8003 | 67552.9485 | 22.7382 | OK
3 | Mujibur Ghat | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1337023.4124 | Kamrangirchar | 110 |  |  | Mujibur Ghat | 1337023.4124 | 1069523.2812 | 267500.1312 | 25.0112 | OK
4 | Madrasa | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1702859.76 | 1701666.1612 | Kamrangirchar | 140 |  |  | Madrasa | 1701666.1612 | 1544866.9617 | 156799.1995 | 10.1497 | OK
5 | Thana | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1337961.24 | 1337023.4124 | Kamrangirchar | 110 |  |  | Thana | 1337023.4124 | 1307195.1214 | 29828.2909 | 2.2819 | OK
6 | Al-Hera | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 973062.72 | 972380.6635 | Kamrangirchar | 80 |  |  | Waz Uddin School | 972380.6635 | 891269.401 | 81111.2626 | 9.1006 | OK
8 | 11/0.4 kV Auxiliary Transformer | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off | [7 empty] | Grand Total | 6685117.0618 | 6689806.2 | 6685117.0618 | -0.070094
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 6685117.0618
[5 empty] | Total = |  |  | 6685117.0618 | 0

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) | 132 | IMPORT | 8993631 | 1 | 5674.721 | 5714.359 | 39.638 | 960000 | 0 | 38052480
| 132 KV Mogbazar-2 CKT(EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) | 132 |  | 8993659 | 1 | 4851.765 | 4882.347 | 30.582 | 960000 | 0 | 29358720
| 132 KV Mogbazar-1 CKT(EXP) | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 67411200
[9 empty] | Net Total | 67411200
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE | 6604452 | 1 | 9138.9 | 9191.87 | 52.97 | 720000 | 38138400
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 |  | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  | 6604428 | 1 | 5448.86 | 5489.95 | 41.09 | 720000 | 29584800
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 |  | 0 | 0 | 720000 |  | 0
[8 empty] | Total Import/Export |  | 67723200 | 0
[8 empty] | Net Total |  | 67723200 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0 |  |  | future Scope
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
MOGBAZAR 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0 |  |  | No meter
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 67723200
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 67411200 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 67411200
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 67411200 |  | MOGBAZAR 33 KV NET IMPORT |  | 67267200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 144000
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.2136%
| 132 KV TOTAL IMPORT |  | 67411200
33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming | 33 | IMPORT | 76026303 | 1 | 9767.48 | 9814.76 | 47.28 | 480000 | 22694400 |  | 22742982.2749
| 132/33 KV GT-2 Incomming | 33 |  | 76026307 | 1 | 9762.59 | 9809.83 | 47.24 | 480000 | 22675200 |  | 22723741.1731
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 7975.89 | 8021.51 | 45.62 | 480000 | 21897600 |  | 21944476.552
[9 empty] | Total | 67267200 |  | 67411200
MOGBAZAR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. | 33 |  | 6604465 | 1 | 6910.28 | 6938.25 | 27.97 | 180000 |  | 5034600 | 5075185.8236 |  | 20525641.7881 | MOGBAZAR 33/11 KV SS | 2.1623 | 33/11 KV Transformer No.1. | 5075185.8236 | 4580235.2849 | 494950.5386 | 10.8062 | OK
| 33/11 KV Transformer No.2. | 33 |  | 202006985 | 1 | 35466289878 | 35648331276 | 182041398 | 3 | T2 Incomer side | 4788300 | 4826900.3057 |  |  |  |  | 33/11 KV Transformer No.2. | 4826900.3057 | 4351473.4789 | 475426.8267 | 10.9257 | OK
| 33/11 KV Transformer No.3. | 33 |  | 6604338 | 1 | 6957.13 | 6980.86 | 23.73 | 180000 |  | 4271400 | 4305833.3784 |  |  |  |  | 33/11 KV Transformer No.3. | 4305833.3784 | 4871786.6076 | -565953.2292 | -11.617 | OK
| 33/11 KV Transformer No.4 | 33 |  |  | 1 | 915694 | 992649 | 76955 | 180000 | T4 Incomer side | 6267200 | 6317722.2805 |  |  |  |  | 33/11 KV Transformer No.4 | 6317722.2805 | 5039158.6632 | 1278563.6173 | 25.3726 | OK
| 33 KV Feeders | [7 empty] | Total |  | 20361500 | 20525641.7881 |  |  |  |  | 33 KV Feeders | 20525641.7881 | 18842654.0346 | 1682987.7535 | 8.9318 | OK
8 | 33 kV Tejgaon U/G Feeder-1 | 33 |  | 76026300 | 1 | 6651.5 | 6673.48 | 21.98 | 360000 |  | 7912800 | 7976588.0874 |  | 21237030.7039 | Tejgoan 33/11 kv ss | 2.2435 | 33 kV Tejgaon U/G Feeder-1 | 7976588.0874 | 7220394.4845 | 756193.6028 | 10.473 | OK
9 | 33 kV Tejgaon U/G Feeder-2 | 33 |  | 06604453 | 1 | 6399.23 | 6435.77 | 36.54 | 360000 |  | 13154400 | 13260442.6166 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 13260442.6166 | 11399296.7759 | 1861145.8407 | 16.3268 | OK
10 | Bashundhara City | 33 |  | 660434 | 1 | 727.48 | 739.39 | 11.91 | 180000 |  | 2143800 | 2161081.9864 | Shere b.nagar | 5601141.8485 | Ispahani 33/11 kv ss | 1.6517 | Bashundhara City | 2161081.9864 | 2940709.0199 | -779627.0335 | -26.5115 | OK
11 | Ispahani-1 | 33 |  |  | 1 | 1929.47 | 1936.84 | 7.37 | 180000 | From Ispahani Downsteam Estimated | 2643950 | 2665263.8855 |  |  |  |  | Ispahani-1 | 2665263.8855 | 3408540.9108 | -743277.0252 | -21.8063 | OK
12 | Ispahani-2 | 33 |  |  | 1 | 3774.88 | 3791.06 | 16.18 | 180000 |  | 2912400 | 2935877.963 |  | 6704636.3993 | Green Road Dormatory 33/11 kv ss | 1.4639 | Ispahani-2 | 2935877.963 | 1783502.2269 | 1152375.7361 | 64.6131 | FAULT
13 | 33 kV Green Road Dormitory | 33 |  | 76026305 | 1 | 7974.85 | 7993.99 | 19.14 | 180000 | Reading From G. Dormitory Side | 6651020 | 6704636.3993 |  |  |  |  | 33 kV Green Road Dormitory | 6704636.3993 | 2547661.8429 | 4156974.5564 | 163.1682 | FAULT
14 | 33 KV T&T-1 | 33 |  | 6604337 | 1 | 4470.31 | 4500.97 | 30.66 | 180000 |  | 5518800 | 5563289.1437 |  | 11037667.2737 | T&T 33/11 kv ss | -0.2612 | 33 KV T&T-1 | 5563289.1437 | 5577268.8204 | -13979.6767 | -0.25065 | OK
13 | 33 KV T&T-2 | 33 |  | 6604336 | 1 | 5564.29 | 5594.46 | 30.17 | 180000 |  | 5430600 | 5474378.13 |  |  |  |  | 33 KV T&T-2 | 5474378.13 | 4959971.8842 | 514406.2458 | 10.3712 | OK
14 | 33KV Karwan Bazar | 33 |  | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | -0.31753 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | AT-1 | 33 |  | 6603338 | 1 | 1364.88 | 1546.46 | 181.58 | 80 |  |  | 0 |  |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | AT-2 | 33 |  | 6603849 | 1 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 46367770 | 46741558.2119 |  |  |  |  | 0 | 46741558.2119 | 39837345.9654 | 6904212.2465 | 17.331 | OK
[8 empty] | Grand Total |  | 67267200 | 66729270 | 67267200 | 0.80614
-0.3377
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2161081.9864
[8 empty] | Total = | 2161081.9864 | 0 | [17 empty] | 1.4463
11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 | 11 | Import | 6604457 | 1 | 523615.4 | 528622.1 | 5006.7 | 1000 | 5006700 |  | 5071194.632
2 | 33/11 kV Transformer-2 | 11 | Import | 30/11009-1101 | 1 | 566866.9 | 571655.2 | 4788.3 | 1000 | 4788300 |  | 4849981.2764
3 | 33/11 kV Transformer-3 | 11 | Import | 6604454 | 1 | 559970.2 | 564172.6 | 4202.4 | 1000 | 4202400 |  | 4256533.9089
4 | 33/11 kV Transformer-4 | 11 | Import |  | 1 | 880.74 | 919.91 | 39.17 | 160000 | 6267200 |  | 6347931.9707
[9 empty] | Total | 20264600 |  | 20525641.7881
MOGBAZAR 11 kV SIDE
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40401.6 | 40402.7 | 1.1 | 1000 |  | 1100 | 1119.369 | Moghbazar |  |  |  | 11 kV Doctor's Lane | 1119.369 | 1908.3381 | -788.9691 | -41.3433 | CHECK
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 78790.6 | 79796.2 | 1005.6 | 1000 |  | 1005600 | 1023306.7911 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 1023306.7911 | 754195.3028 | 269111.4884 | 35.6819 | OK
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 155650.4 | 157212.8 | 1562.4 | 1000 |  | 1562400 | 1589911.0287 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 1589911.0287 | 1684058.1491 | -94147.1204 | -5.5905 | OK
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 118462.4 | 118798.7 | 336.3 | 1000 |  | 336300 | 342221.6327 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 342221.6327 | 258630.0313 | 83591.6015 | 32.3209 | OK
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 118573.6 | 120528.2 | 1954.6 | 1000 |  | 1954600 | 1989016.959 | Moghbazar |  |  |  | 11KV Ambagan | 1989016.959 | 1321775.2277 | 667241.7313 | 50.4807 | FAULT
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 140567.1 | 141604.5 | 1037.4 | 1000 |  | 1037400 | 1055666.7314 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1055666.7314 | 964916.004 | 90750.7275 | 9.405 | OK
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9176.3 | 9327.8 | 151.5 | 1000 |  | 151500 | 154167.6401 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 154167.6401 | 145335.0117 | 8832.6283 | 6.0774 | OK
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 116515 | 118443.2 | 1928.2 | 1000 |  | 1928200 | 1962152.1029 | Kakrail |  |  |  | 11 kV Bangla Motor | 1962152.1029 | 1554291.1587 | 407860.9442 | 26.241 | OK
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 169516.9 | 171354 | 1837.1 | 1000 |  | 1837100 | 1869447.9972 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1869447.9972 | 1963378.5829 | -93930.5857 | -4.7841 | OK
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 114028.3 | 115816.3 | 1788 | 1000 |  | 1788000 | 1819483.4353 | Kakrail |  |  |  | 11 kV Iskaton | 1819483.4353 | 1883429.2606 | -63945.8253 | -3.3952 | OK
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 81390.3 | 81467.2 | 76.9 | 1000 |  | 76900 | 78254.0694 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 78254.0694 | 0 | 78254.0694 | #DIV/0! | #DIV/0!
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 121728.8 | 122407.2 | 678.4 | 1000 |  | 678400 | 690345.3929 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 690345.3929 | 1513512.9868 | -823167.5939 | -54.3879 | CHECK
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 110579.4 | 111507.7 | 928.3 | 1000 |  | 928300 | 944645.6784 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 944645.6784 | 897722.4153 | 46923.2631 | 5.2269 | OK
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43008 | 43325.7 | 317.7 | 1000 |  | 317700 | 323294.1205 | Kakrail |  |  |  | 11 kV BSRS Feeder | 323294.1205 | 452677.8838 | -129383.7634 | -28.5819 | OK
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8175 | 8294.9 | 119.9 | 1000 |  | 119900 | 122011.2214 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 122011.2214 | 87984.43 | 34026.7914 | 38.6737 | OK
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 13965044.1701 | 13723400 | 13965044.1701 | 1.7608 |  |  |  |  | 13965044.1701
1 | 11 kV TCB Feeder | 11 | T-4 |  | 1 | 33084.1 | 33653.6 | 569.5 | 1000 |  | 569500 | 587067.814 | Kakrail |  |  |  | 11 kV TCB Feeder | 587067.814 | 266719.3144 | 320348.4996 | 120.107 | FAULT
2 | 11 kV Tejgaon SS-2 | 11 | T-4 |  | 1 | 25742.8 | 27179.6 | 1436.8 | 1000 |  | 1436800 | 1481122.0985 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1481122.0985 | 1142878.4717 | 338243.6268 | 29.5958 | OK
3 | Holy Day Inn | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 479040 | 493817.3233 | Tejgaon |  |  |  | Holy Day Inn | 493817.3233 | 435903.7374 | 57913.5858 | 13.2859 | OK
4 | Polly Bhabon-2 | 11 | T-4 |  | 1 | 18298.6 | 18301.8 | 3.2 | 1000 | Consumer meter damaged, 12 months average | 28563 | 29444.1053 | Kakrail |  |  |  | Polly Bhabon-2 | 29444.1053 | 23242.6831 | 6201.4222 | 26.6812 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 |  | 1 | 9734.4 | 11538.8 | 1804.4 | 1000 |  | 1804400 | 1860061.7445 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1860061.7445 | 1661402.8837 | 198658.8608 | 11.9573 | OK
6 | 11 kV Tejturibazar | 11 | T-4 |  | 1 | 128464.6 | 129174.3 | 709.7 | 1000 |  | 709700 | 731592.6735 | Kakrail |  |  |  | 11 kV Tejturibazar | 731592.6735 | 561428.3232 | 170164.3503 | 30.3092 | OK
7 | Songsad | 11 | T-4 |  | 1 | 1826.4 | 1949 | 122.6 | 1000 |  | 122600 | 126381.9385 | Shere b.nagar |  |  |  | Songsad | 126381.9385 | 326274.0292 | -199892.0907 | -61.2651 | CHECK
| Chennel 24 | 11 | T-4 |  | 1 | 7306 | 7307.13 | 1.13 | 1000 |  | 1130 | 1164.858 | Moghbazar |  |  |  | Chennel 24 | 1164.858 | 1082.813 | 82.045 | 7.577 | OK
8 | Sonargaon | 11 | T-4 |  | 1 | 37300.4 | 38114.9 | 814.5 | 1000 |  | 814500 | 839625.5215 | Kakrail |  |  |  | Sonargaon | 839625.5215 | 518217.9556 | 321407.5659 | 62.0217 | FAULT
| AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  | 7000 | 7215.9345 | Moghbazar |  |  |  | AT -1 | 7215.9345 | 7150.6519 | 65.2826 | 0.91296 | OK
| AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 6157494.0116 | 5973233 | 6157494.0116 | 3.0848
[9 empty] | Total | 20525641.7881 | 19696633 | 20122538.1817 | 2.1623 | 6 months avg loss
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | [14 empty] | AMR Meter Information
[5 empty] | Moghbazar | at 33 KV level |  | 2767116.5828 | [14 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
[5 empty] | Tejgaon | at 33 KV level |  | 8131672.4645 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 76890 | 3000
[5 empty] | Kakrail | at 33 KV level |  | 9097367.1959 | [14 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 402150 | 3000
[5 empty] | Shere b.nagar | at 33 KV level |  | 126381.9385 | [14 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 28563 | 300
[5 empty] | Total = |  |  | 20122538.1817 | 0
AMR Meter Information
[23 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[23 empty] | Shah Garments | 712.18 | 732.02 | 194.76 | 200.55
[23 empty] | Habib Hotel | 2216.55 | 2314.07 | 714.57 | 751.1
[23 empty] | The Joint Director BRDB | 921.21 | 1002.66 | 192.73 | 206.49
[25 empty] | 732.02 | 200.55
| MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016 | [23 empty] | 2314.07 | 751.1
[25 empty] | 1002.66 | 206.49
33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 | 33 | 0 | 6604337 | 1 | 4470.31 | 4500.97 | 30.66 | 180000 | 0 | 5518800 | 5563289.1437
13 | 33 KV T&T-2 | 33 | 0 | 6604336 | 1 | 5564.29 | 5594.46 | 30.17 | 180000 | 0 | 5430600 | 5474378.13
0 | Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 10949400 | 11037667.2737
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder | 33 | Import | DHK60891 | 1 | 945792 | 955990 | 10198 | 360 | 3671280
2 | 33 kV Moghbazar-2 Feeder | 33 | Import | DHK68131 | 1 | 857.67 | 867.76 | 10.09 | 360 | 3632.4
| 33 kV Ullon Feeder | 33 | Import | DHK68132 | 1 | 349.75 | 349.75 | 0 | 180000 | 0
[9 empty] | Total | 3674912.4 | 0 | 0
Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[7 empty] | 0 |  | Total |  | 0
Mogbazar T&T 33 KV SIDE
3 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 935873 | 966463 | 30590 | 180 |  | 5506200
4 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 778897 | 799053 | 20156 | 180 |  | 5430600 |  |  | Meter Problem
[9 empty] | Total |  | 10936800 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 11037667.2737 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 11037667.2737
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 11037667.2737 |  | 33/11 KV XF LV SIDE |  | 11004660
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 33007.2737
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.299%
| TOTAL IMPORT |  | 11037667.2737
11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 951420 | 982217 | 30797 | 180 | 5543460 |  | 5560087.0018 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 899301 | 929641 | 30340 | 180 | 5461200 |  | 5477580.2719 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 11004660 |  | 11037667.2737 | 0.29994 | [6 empty] | 0 | #DIV/0! | #DIV/0!
| Mogbazar T&T 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 87735 | 109708 | 21973 | 60 |  | 1318380 | 1314936.3633 | Kakrail |  |  |  | 11 kV post office | 1314936.3633 | 1382328.0227 | -67391.6595 | -4.8752 | OK
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 352002 | 374779 | 22777 | 60 |  | 1366620 | 1363050.3594 | Kakrail |  |  |  | 11 kV anarkoli | 1363050.3594 | 1427067.0698 | -64016.7104 | -4.4859 | OK
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 925025 | 931981 | 6956 | 60 |  | 417360 | 416269.8468 | Moghbazar |  |  |  | 11 kV sonalibagh | 416269.8468 | 294240.6329 | 122029.2138 | 41.4726 | FAULT
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1898014 | 1912434 | 14420 | 60 |  | 865200 | 862940.0791 | Moghbazar |  |  |  | 11 Kv desh tv | 862940.0791 | 833038.6444 | 29901.4347 | 3.5894 | OK
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 505.31 | 532.55 | 27.24 | 60000 |  | 1634400 | 1630130.9123 | Moghbazar |  |  |  | 11 Kv Btcl | 1630130.9123 | 1641838.6137 | -11707.7015 | -0.71308 | OK
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 854873 | 864753 | 9880 | 60 |  | 592800 | 591251.5937 | Kakrail |  |  |  | 11 kV century | 591251.5937 | 562494.0297 | 28757.5641 | 5.1125 | OK
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 416670 | 434155 | 17485 | 60 |  | 1049100 | 1046359.7284 | Moghbazar |  |  |  | 11 kV cinema hall | 1046359.7284 | 1000418.152 | 45941.5764 | 4.5922 | OK
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 614262 | 642051 | 27789 | 60 |  | 1667340 | 1662984.8723 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1662984.8723 | 1576780.0804 | 86204.7919 | 5.4671 | OK
4 | 11 kv Sherebangla | 11 |  | DHK60915 | 1 | 621193 | 645233 | 24040 | 60 |  | 1442400 | 1438632.4204 | Moghbazar |  |  |  | 11 kv Sherebangla | 1438632.4204 | 1344643.5154 | 93988.9049 | 6.9899 | OK
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 285592 | 297424 | 11832 | 60 |  | 709920 | 708065.6738 | Khilgaon |  |  |  | 11 kV Nur Mosjid | 708065.6738 | 642686.6612 | 65379.0126 | 10.1728 | OK
6 | Auxiliary |  | Export | U0004461 | 1 | 7917.57 | 7968.46 | 50.89 | 60 |  | 3053.4 | 3045.4245 | Moghbazar |  |  |  | Auxiliary | 3045.4245 | 4284.5777 | -1239.1533 | -28.9212 | OK
[9 empty] | Grand Total | 11037667.2737 | 11066573.4 | 11037667.2737 | -0.2612
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 3269238.3163
[5 empty] | Moghbazar | at 33 KV level |  | 6105444.0851
[5 empty] | Khilgaon | at 33 KV level |  | 1662984.8723
[5 empty] | Total = |  |  | 11037667.2737 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
132 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 | 132 | IMPORT | 8993681 | 1 | 2570.44 | 2593.526 | 23.086 | 1440000 | 0 | 33243840
| Ullon-1 | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 33243840
[8 empty] | Net Total |  | 33243840
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) | 132 |  | 8993624 | 1 | 4716.502 | 4743.032 | 26.53 | 960000 | 0 | 25468800
| Maniknager-2 (new line to ullon) | 132 |  |  | 1 | 11.003 | 11.003 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 25468800
[8 empty] | Net Total |  | 25468800
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 | 132 |  | 8993659 | 1 | 4362.119 | 4374.65 | 12.531 | 960000 | 0 | 12029760
| Ullon U/G-1 | 132 |  |  | 1 | 1.56 | 1.56 | 0 | 960000 | 0 | 0
| Ullon U/G-2 | 132 |  | 8993660 | 1 | 4049.578 | 4060.204 | 10.626 | 960000 | 0 | 10200960
| Ullon U/G-2 | 132 |  |  | 1 | 1.329 | 1.329 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 22230720
[8 empty] | Net Total |  | 22230720
ULLON 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
| EXPORT TO OTHERS 132/33 KV SS | [12 empty] | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 | 132 |  |  | 1 | 1632756 | 1632756 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 | 132 |  |  | 1 | 2042005 | 2071385 | 29380 | 1000 |  | 29380000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 | 132 |  |  | 1 | 2799000 | 2827813 | 28813 | 1000 |  | 28813000 |  |  | 132 kV Ullon CKT-3 | 31978000
[9 empty] | Total |  | 58193000 |  |  | Total | 74518000
ULLON 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 22750360
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDIRGONJ 132 KV SIDE (TARIFF POINT) |  | 33243840 |  | EXPORT TO OTHER S/S |  |  | 58193000 |  | 132 KV NET IMPORT |  | 22750360
| HORIPUR 132 SIDE (TARIFF POINT) |  | 25468800 |  | 132 KV Net EXPORT |  |  | 22750360 |  | 132/33 KV GT LV Side |  | 22395504
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 22230720 | [6 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 354856
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.56%
| 132 KV TOTAL IMPORT |  | 80943360
33 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming | 33 | Import | BD001812 | 1 | 2083.2796 | 2106.811 | 23.5314 | 480000 | 11295072 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming | 33 | Import | BD001858 | 1 | 2006.5276 | 2029.6535 | 23.1259 | 480000 | 11100432 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 22395504 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 33 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1471.3116 | 1503.439 | 32.1274 | 240000 | Estimated | 6629904 | 6736010.2412 |  | 14252994.4549 | Taltola 33/11 kv ss | 0.082298 | Taltala-1 | 6736010.2412 | 6925471.7141 | -189461.473 | -2.7357 | OK
| Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Mgbazar T&T | 0 | 115319.0542 | -115319.0542 | -100 | CHECK
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9044 | 1163.9044 | 0 | 240000 |  | 0 | 0 |  | 0 | Mgbazar T&T 33/11 kv ss | -0.2612 | Kakrail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Taltala-2 | 33 | Export | BD001837 | 1 | 2432.5066 | 2463.334 | 30.8274 | 240000 |  | 7398576 | 7516984.2137 |  |  |  |  | Taltala-2 | 7516984.2137 | 8680174.6662 | -1163190.4525 | -13.4005 | OK
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 0 | Kakrail 33/11 kv ss | 1.0363 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 0.807 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.0586 | 61.6699 | 0.6113 | 240000 |  | 146712 | 149060.0067 |  | 0 | Tejgoan 33/11 kv ss | 2.2435 | Khailgaon | 149060.0067 | 2938.1785 | 146121.8282 | 4973.2114 | FAULT
4 | AT at GIS Building | 415 | Export | DHKE4577 | 1 | 134040 | 134040 | 0 | 1 |  |  | 0 |  | 149060.0067 | Khilgoan 33/11 kv ss | 0.55595 | AT at GIS Building | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[7 empty] | 0 |  | TOTAL= |  | 14175192 | 14402054.4615 |  |  |  |  | 0 | 14402054.4615 | 15723903.6131 | -1321849.1515 | -8.4066 | OK
| 33 KV Local Feeder -1 | 33 | NET IMPORT |  | 1 | 1083.7938 | 1097.744 | 13.9502 | 240000 |  | 3348048 | 3401630.7953 |  | 7398355.5645 | Ullon 33/11 kv ss | 0.53771 | 33 KV Local Feeder -1 | 3401630.7953 | 5117891.442 | -1716260.6467 | -33.5345 | OK
| 33KV Local Feeder- 2 | 33 |  |  | 1 | 810.9531 | 827.3438 | 16.3907 | 240000 |  | 3933768 | 3996724.7692 |  |  |  |  | 33KV Local Feeder- 2 | 3996724.7692 | 3307284.9449 | 689439.8243 | 20.8461 | OK
[9 empty] | TOTAL= |  | 7281816 | 7398355.5645 |  |  |  |  | 0 | 7398355.5645 | 8425176.3869 | -1026820.8224 | -12.1875 | OK
[9 empty] | Grand Total | 21800410.026 | 21457008 | 21800410.026 | 1.6004
1.6004
11 KV SIDE of___ULLON 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 7281816 |  | 7398355.5645 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| ULLON 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 973062.72 | 978294.9507 | Moghbazar | 80 |  |  | West Malibagh | 978294.9507 | 1067980.1054 | -89685.1547 | -8.3976 | OK
2 | Ullon | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1398777.66 | 1406298.9916 | Moghbazar | 115 |  |  | Ullon | 1406298.9916 | 2041028.6458 | -634729.6543 | -31.0985 | OK
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1337961.24 | 1345155.5572 | Moghbazar | 110 |  |  | Mohanagar | 1345155.5572 | 1364641.2458 | -19485.6886 | -1.4279 | OK
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1094695.56 | 1100581.8195 | Moghbazar | 90 |  |  | Bagichartek | 1100581.8195 | 1127312.3335 | -26730.514 | -2.3712 | OK
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1337961.24 | 1345155.5572 | Moghbazar | 110 |  |  | Mirbagh | 1345155.5572 | 1720634.6142 | -375479.0571 | -21.8221 | OK
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 1216328.4 | 1222868.6883 | Moghbazar | 100 |  |  | West Rampura | 1222868.6883 | 1103579.4422 | 119289.2461 | 10.8093 | OK
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7398355.5645 | 7358786.82 | 7398355.5645 | 0.53771
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 7398355.5645
[5 empty] | Total = |  |  | 7398355.5645 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
132 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 | 132 | Export | 50146667 | 1 | 1705.13 | 1730.856 | 25.726 | 960000 | 0 | 24696960
2 | Rampura to Madartek-2 | 132 | Export | 50146668 | 1 | 1499.805 | 1525.358 | 25.553 | 960000 | 0 | 24530880
[8 empty] | Total Import/Export |  | 0 | 49227840
[8 empty] | Net Total |  | 49227840
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 | 132 | Import | SIEM0492 | 1 | 1494804 | 1519412 | 24608 | 1000 | 24608000
|  | 132 | Export |  | 1 |  | 0 | 0
2 | 132 kV Rampura-2 | 132 | Import | SIEM0489 | 1 | 1444213 | 1468831 | 24618 | 1000 | 24618000
|  | 132 | Export |  | 1 |  |  | 0
[8 empty] | Total Import/Export |  | 49226000 | 0
[8 empty] | Net Total |  | 49226000
MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | [8 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
MADERTEK 132 KV SIDE
3 | 133 kV GT-1 | 132 | Export |  | 1 | 1330504 | 1355242 | 24738 | 1000 |  | 24738000
4 | 133 kV GT-2 | 132 | Export |  | 1 | 1319442 | 1344009 | 24567 | 1000 |  | 24567000
[9 empty] | Total |  | 49305000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| RAMPURA 132 KV SIDE (TARIFF POINT) |  | 49227840 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 49227840
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 49227840 |  | 33 KV NET IMPORT |  | 49524000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -296160
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.6016%
| 132 KV TOTAL IMPORT |  | 49227840
33 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0516 | 1 | 1479109 | 1503865 | 24756 | 1000 | 24756000 |  | 24607955.8808
2 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0515 | 3 | 491053 | 499309 | 8256 | 1000 | 24768000 |  | 24619884.1192
[9 empty] | Total | 49524000 |  | 49227840
MADERTEK 33 KV SIDE
33/11 kv Transforfers
1 | 33 kV T-1 | 33 | Import | SIEM0512 | 1 | 394701 | 399032 | 4331 | 2000 |  | 8662000 | 8696242.4049 |  | 17926587.899 | Madartek 33/11 kv ss
2 | 33 kV T-3 | 33 | Export |  | 1 | 72245 | 72634 | 389 | 2000 |  | 778000 | 781075.5704
2 | 33 kV T-2 | 33 | Export | SIEM0505 | 1 | 397563 | 401771 | 4208 | 2000 |  | 8416000 | 8449269.9237
| 33 kv Feeders | [7 empty] | Total |  | 17856000 | 17926587.899 |  | 14677795.4236 | Banasree 33/11 kv ss
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 89034 | 93583 | 4549 | 2000 |  | 9098000 | 9133965.9893
1 | Goran | 33 | Export | SIEM0510 | 1 | 335181 | 339866 | 4685 | 2000 |  | 9370000 | 9407041.253 |  | 9407041.253 | Goran 33/11 kv ss
3 | Amulia | 33 | Export | SIEM0505 | 1 | 32926 | 34124 | 1198 | 6000 |  | 7188000 | 7216415.4244
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 82757 | 85518 | 2761 | 2000 |  | 5522000 | 5543829.4343 |  | 7216415.4244 | Amulia 33/11 kv ss
[9 empty] | Total |  | 31178000 | 31301252.101
[8 empty] | Grand Total |  | 49227840 | 49034000 | 49227840 | 0.39532
11 KV SIDE of___MADERTEK 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | GJU 71154 | 1 | 367633.5 | 371943.7 | 4310.2 | 2000 | 8620400 |  | 8690982.4152 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | GJU 71155 | 1 | 370627.9 | 374822.1 | 4194.2 | 2000 | 8388400 |  | 8457082.8374 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming | 11 | Import | 6604399 | 1 | 4647.19 | 4651.48 | 4.29 | 180000 | 772200 |  | 778522.6464 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17781000 |  | 17926587.899 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Madertek 11 kV Side | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 4956.03 | 6677.95 | 1721.92 | 1000 |  | 1721920 | 1753548.1446 | Mugdapara |  |  |  | Sobujbagh | 1753548.1446 | 1758376.7576 | -4828.613 | -0.27461 | OK
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 93735.9 | 95560.9 | 1825 | 1000 |  | 1825000 | 1858521.5132 | Mugdapara |  |  |  | Madertek | 1858521.5132 | 1869405.7046 | -10884.1915 | -0.58223 | OK
3 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 4403.06 | 5644.71 | 1241.65 | 1000 |  | 1241650 | 1264456.5681 | Mugdapara |  |  |  | Rajarbagh | 1264456.5681 | 1345258.8988 | -80802.3307 | -6.0065 | OK
| Goran | 11 |  | X1390296 | 1 | 22865.9 | 24684 | 1818.1 | 1000 |  | 1818100 | 1851494.7743 | Bashabo |  |  |  | Goran | 1851494.7743 | 1900352.3978 | -48857.6235 | -2.571 | OK
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 4720.47 | 6722.86 | 2002.39 | 1000 |  | 2002390 | 2039169.8043 | Mugdapara |  |  |  | Dhakhingaon | 2039169.8043 | 2040924.1648 | -1754.3605 | -0.085959 | OK
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 78510.9 | 79376.5 | 865.6 | 1000 |  | 865600 | 881499.2996 | Maniknagar |  |  |  | Manda | 881499.2996 | 902782.6705 | -21283.3709 | -2.3575 | OK
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 76.4 | 282.33 | 205.93 | 1000 | Reading Corrected | 205930 | 209712.5124 | Mugdapara |  |  |  | Green Model Town | 209712.5124 | 202563.117 | 7149.3955 | 3.5295 | OK
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 1473.9 | 1799.56 | 325.66 | 1000 |  | 325660 | 331641.7074 | Mugdapara |  |  |  | Biswa Road | 331641.7074 | 371821.4438 | -40179.7364 | -10.8062 | OK
2 | Mugdapara | 11 |  | X0854272 | 1 | 3255.6 | 3507.9 | 252.3 | 1000 | New Meter | 252300 | 256934.2344 | Maniknagar |  |  |  | Mugdapara | 256934.2344 | 263661.7266 | -6727.4922 | -2.5516 | OK
| Singapur | 11 |  | X1390302 (N) | 1 | 26648 | 28808.4 | 2160.4 | 1000 |  | 2160400 | 2200082.1244 | Banosree |  |  |  | Singapur | 2200082.1244 | 2209102.0216 | -9019.8972 | -0.40831 | OK
| Trimohony | 11 |  | X1390308 | 1 | 20943.4 | 22519.4 | 1576 | 1000 |  | 1576000 | 1604947.893 | Banosree |  |  |  | Trimohony | 1604947.893 | 1858953.5103 | -254005.6172 | -13.6639 | OK
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 6826.83 | 8633.04 | 1806.21 | 1000 |  | 1806210 | 1839386.3794 | Mugdapara |  |  |  | Mayakanon | 1839386.3794 | 1868462.9577 | -29076.5783 | -1.5562 | OK
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 2522.3 | 3107.93 | 585.63 | 1000 |  | 585630 | 596386.824 | Mugdapara |  |  |  | Ahmedbagh | 596386.824 | 452446.8019 | 143940.022 | 31.8137 | OK
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 700605 | 702966 | 2361 | 200 |  | 472200 | 480873.3471 | Mugdapara |  |  |  | Wasa Road | 480873.3471 | 0 | 480873.3471 | #DIV/0! | #DIV/0!
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 737906 | 739373 | 1467 | 200 |  | 293400 | 298789.1572 | Mugdapara |  |  |  | Nandipara | 298789.1572 | 0 | 298789.1572 | #DIV/0! | #DIV/0!
| AT-1 | 0.415 |  |  | 1 | 110.74 | 238.06 | 127.32 | 80 |  | 10185.6 | 10372.6886 | [5 empty] | 10372.6886
3 | AT-2 | 0.415 |  | 63394003 | 1 | 83.3 | 89.44 | 6.14 | 80 |  | 491.2 | 500.2223 | Mugdapara |  |  |  | AT-2 | 500.2223 | 0 | 500.2223 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17478317.1945 | 17163066.8 | 17478317.1945 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 17478317.1945 | 17163066.8 | 17478317.1945 | 1.8368
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH |  |  |  |  | 1.8368
[5 empty] | Banosree | at 33 KV level |  | 3805030.0175
[5 empty] | Bashabo | at 33 KV level |  | 1851494.7743
[5 empty] | Maniknagar | at 33 KV level |  | 1138433.534
[5 empty] | Mugdapara | at 33 KV level |  | 10683358.8687
[5 empty] | Total = |  |  | 17478317.1945 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
33 KV SIDE of___TEJGOAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 | 33 | 0 | 76026300 | 1 | 6651.5 | 6673.48 | 21.98 | 360000 | 0 | 7912800 | 7976588.0874
9 | 33 kV Tejgaon U/G Feeder-2 | 33 | 0 | 06604453 | 1 | 6399.23 | 6435.77 | 36.54 | 360000 | 0 | 13154400 | 13260442.6166
0 | Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 21067200 | 21237030.7039
TEJGOAN 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 | 33 | Import | 76026300 | 1 | 6651.5 | 6673.48 | 21.98 | 360000 | 7912800
2 | 33 kV Moghbazar-2 | 33 | Import | 06604453 | 1 | 6499.23 | 6499.23 | 0 | 360000 | 0
3 | 33 kv Ullon | 33 | Import | 660434 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0
[9 empty] | Total | 7912800
TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
TEJGOAN 33 KV SIDE
1 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 581225.8 | 610667.6 | 29441.8 | 270 |  | 7949286
2 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 332278.5 | 381042.3 | 48763.8 | 180 |  | 8777484
3 | 33/11 kV Transfomer-3 (T3) | 33 | Export | BD001872 | 1 | 1091.523 | 1123.5396 | 32.0166 | 180000 |  | 5762988
[9 empty] | Total |  | 22489758 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 21237030.7039 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TEJGOAN 33 KV NET IMPORT |  | 21237030.7039
| IMPORT-2 |  |  |  | TEJGOAN 33 KV NET IMPORT |  |  | 21237030.7039 |  | 33 KV TX HV Side |  | 22489758
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -1252727.2961
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -5.899%
| TOTAL IMPORT |  | 21237030.7039
11 KV SIDE of___ TEJGOAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 709777.4 | 750350.9 | 40573.5 | 180 | 7303230 |  | 7593448.5242 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 624995.4 | 665903.9 | 40908.5 | 180 | 7363530 |  | 7656144.7485 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming | 11 | Import | BD001875 | 1 | 197286.3 | 203044.9 | 5758.6 | 1000 | 5758600 |  | 5987437.4313 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 20425360 |  | 21237030.7039 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| TEJGOAN 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | 11 |  | DHK60950 | 1 | 151292.3 | 176336.6 | 25044.3 | 60 |  | 1502658 | 1536369.5556 | Tejgaon |  |  |  | Nakhal Para Feeder | 1536369.5556 | 1455985.7702 | 80383.7854 | 5.5209 | OK
2 | Badda-Meghna Feeder | 11 |  | DHK60979 | 1 | 862789.4 | 876525.4 | 13736 | 60 |  | 824160 | 842649.7133 | Tejgaon |  |  |  | Badda-Meghna Feeder | 842649.7133 | 723241.8753 | 119407.838 | 16.5101 | OK
3 | Rasulbagh Feeder | 11 |  | DHK60948 | 1 | 900269.4 | 931276.3 | 31006.9 | 60 |  | 1860414 | 1902151.6741 | Tejgaon |  |  |  | Rasulbagh Feeder | 1902151.6741 | 1576418.059 | 325733.6152 | 20.6629 | OK
4 | Lukas | 11 |  | 8A021100948-02 | 1 | 59791447 | 62085526 | 2294079 | 1 |  | 2294079 | 2345545.782 | Tejgaon |  |  |  | Lukas | 2345545.782 | 2291410.3796 | 54135.4024 | 2.3625 | OK
5 | PWD RMU | 11 |  |  | 1 | 649133.3 | 650851.8 | 1718.5 | 1 |  | 1718.5 | 1757.0539 | Tejgaon |  |  |  | PWD RMU | 1757.0539 | 0 | 1757.0539 | #DIV/0! | #DIV/0!
1 | Civil Aviation Feeder | 11 |  | DHK60977 | 1 | 699019.7 | 744587.4 | 45567.7 | 60 |  | 2734062 | 2795399.6317 | Tejgaon |  |  |  | Civil Aviation Feeder | 2795399.6317 | 2710851.5749 | 84548.0568 | 3.1189 | OK
2 | Ahasanullah Eng. | 11 |  | DHK60867 | 1 | 837862.5 | 848834.7 | 10972.2 | 60 |  | 658332 | 673101.4258 | Tejgaon |  |  |  | Ahasanullah Eng. | 673101.4258 | 468692.9222 | 204408.5035 | 43.6125 | FAULT
3 | New GMG Feeder | 11 |  | DHK61106 | 1 | 933178.3 | 970375 | 37196.7 | 60 |  | 2231802 | 2281871.6214 | Tejgaon |  |  |  | New GMG Feeder | 2281871.6214 | 1504003.376 | 777868.2454 | 51.7198 | FAULT
4 | Shikajo | 11 |  | HA021101036-02 | 1 | 61139376 | 61878821 | 739445 | 1 |  | 739445 | 756034.1648 | Tejgaon |  |  |  | Shikajo | 756034.1648 | 729697.8271 | 26336.3378 | 3.6092 | OK
5 | Kahinur | 11 |  |  | 1 | 454902.7 | 475997.5 | 21094.8 | 60 |  | 1265688 | 1294083.2246 | Tejgaon |  |  |  | Kahinur | 1294083.2246 | 1149946.1437 | 144137.0809 | 12.5342 | OK
6 | Link road | 11 |  | 8A021100380-02 | 1 | 63080677 | 63506551 | 425874 | 1 |  | 425874 | 435428.3198 | Tejgaon |  |  |  | Link road | 435428.3198 | 793695.8241 | -358267.5044 | -45.1391 | CHECK
7 | Shanta | 11 |  |  | 1 | 279216.1 | 289500.3 | 10284.2 | 60 |  | 617052 | 630895.3248 | Tejgaon |  |  |  | Shanta | 630895.3248 | 537389.9553 | 93505.3695 | 17.3999 | OK
1 | Karnafuly Feeder | 11 |  | DHK61084 | 1 | 32293.4 | 33015.5 | 722.1 | 1000 |  | 722100 | 738300.0364 | Tejgaon |  |  |  | Karnafuly Feeder | 738300.0364 | 605952.4682 | 132347.5682 | 21.8412 | OK
2 | Butex | 11 |  |  | 1 | 713.5 | 803.1 | 89.6 | 1000 |  | 89600 | 91610.1416 | Tejgaon |  |  |  | Butex | 91610.1416 | 66444.8384 | 25165.3032 | 37.874 | OK
3 | OriON LAB | 11 |  |  | 1 | 7852368 | 7919755 | 67387 | 1 | 20 | 243265.68 | 248723.2522 | Tejgaon | Estimated |  |  | OriON LAB | 248723.2522 | 239913.1526 | 8810.0996 | 3.6722 | OK
4 | Nina kabbo | 11 |  | 201101025-2 | 1 | 16076731 | 16283296 | 206565 | 1 | 8 | 97306.272 | 99489.3009 | Tejgaon | Estimated |  |  | Nina kabbo | 99489.3009 | 95965.261 | 3524.0398 | 3.6722 | OK
5 | Satrong | 11 |  | HA021100515-2 | 1 | 86979890 | 88090387 | 1110497 | 1 | 110 | 1337961.24 | 1367977.887 | Tejgaon | Estimated |  |  | Satrong | 1367977.887 | 1319522.3394 | 48455.5476 | 3.6722 | OK
6 | South East RMU | 11 |  |  | 1 | 318.3 | 464.1 | 145.8 | 1000 |  | 145800 | 149070.967 | Tejgaon |  |  |  | South East RMU | 149070.967 | 89883.9685 | 59186.9985 | 65.8482 | FAULT
7 | Rangs Bhaban | 11 |  | HA021100939-2 | 1 | 2765 | 121073 | 118308 | 1 | 13 | 158122.692 | 161670.1139 | Tejgaon | Estimated |  |  | Rangs Bhaban | 161670.1139 | 155943.5492 | 5726.5647 | 3.6722 | OK
8 | Babli | 11 |  |  | 1 | 50404.8 | 51912.4 | 1507.6 | 1000 |  | 1507600 | 1541422.4274 | Tejgaon |  |  |  | Babli | 1541422.4274 | 875706.2831 | 665716.1443 | 76.0205 | FAULT
| SPL | 11 |  |  | 1 | 2691.7 | 3055.8 | 364.1 | 1000 |  | 364100 | 372268.4438 | Tejgaon |  |  |  | SPL | 372268.4438 | 301141.8674 | 71126.5764 | 23.619 | OK
9 | DNCC Hospital | 11 |  |  | 1 | 11564 | 12507.9 | 943.9 | 1000 |  | 943900 | 965076.0343 | Tejgaon |  |  |  | DNCC Hospital | 965076.0343 | 921769.2693 | 43306.765 | 4.6982 | OK
| 11/.415 kv Local transformer | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  | 6000 | 6134.6077 | Tejgaon
[9 empty] | Grand Total | 21237030.7039 | 20771040.384 | 21237030.7039 | 2.2435
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Tejgaon | at 33 KV level |  | 21237030.7039
[5 empty] | Total = |  |  | 21237030.7039 | 0
33 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 | 33 | 0 | 214393/44-2711 | 1 | 37.3466 | 46.0777 | 8.7311 | 1000 | Estimated | 8958087 | 8702671.9579
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 74.8365 | 83.3379 | 8.5014 | 1000 | Estimated | 8708671.8 | 8460368.1416
[9 empty] | Total |  | 17666758.8 | 9041302.7186
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import | DHKC9350 | 1 | 12252.51 | 45637.3 | 33384.79 | 270 | 9013893.3
2 | Shatmasjid-2 | 33 | Import | DHKC9354 | 1 | 60559.99 | 92961.2 | 32401.21 | 270 | 8748326.7
[9 empty] | Total | 17762220
ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
ASADGATE 33 KV SIDE
1 | Transfomer-1 (T1) | 33 | Export | DHKC9353 | 1 | 79398.64 | 129507.07 | 50108.43 | 180 |  | 9019517.4
2 | Transfomer-2 (T2) | 33 | Export | DHKC9305 | 1 | 12392.66 | 61134.42 | 48741.76 | 180 |  | 8773516.8
[9 empty] | Total |  | 17793034.2 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Satmosjid 33 KV SIDE |  | 17762220 |  | EXPORT TO OTHER S/S |  |  | 0 |  | ASADGATE 33 KV NET IMPORT |  | 17762220
| IMPORT-2 |  |  |  | ASADGATE 33 KV NET IMPORT |  |  | 17762220 |  | ASADGATE 11 KV NET IMPORT |  | 17793034.2
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 17762220 |  | LOSS UNITS=> |  | -30814.2
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | -0.1735%
| TOTAL IMPORT |  | 17762220
11 KV SIDE of___ASADGATE 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHKC9371 | 1 | 53355 | 103122.15 | 49767.15 | 180 | 8958087 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHKC9337 | 1 | 14875.34 | 63256.85 | 48381.51 | 180 | 8708671.8 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17666758.8 | [9 empty] | 0 | #DIV/0! | #DIV/0!
| ASADGATE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | 11 |  | DHKC9332 | 1 | 61864.31 | 65439.13 | 3574.82 | 60 |  | 214489.2 | 216836.1836 | Shere b.nagar |  |  |  | Gonobhaban | 216836.1836 | 192774.0414 | 24062.1423 | 12.482 | OK
2 | Rapa Plaza Feeder | 11 |  | DHKC9339 | 1 | 17025.01 | 36328.06 | 19303.05 | 60 |  | 1158183 | 1170856.0696 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1170856.0696 | 1090006.6004 | 80849.4692 | 7.4173 | OK
3 | Shukrabad/ South Plaza | 11 |  | DHKC9324 | 1 | 58877.32 | 77512.2 | 18634.88 | 60 |  | 1118092.8 | 1130327.1946 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 1130327.1946 | 775473.5997 | 354853.5949 | 45.7596 | FAULT
4 | Wasa O/H | 11 |  | DHKC9333 | 1 | 26316.53 | 43612.07 | 17295.54 | 60 |  | 1037732.4 | 1049087.4751 | Satmasjid |  |  |  | Wasa O/H | 1049087.4751 | 1292813.3493 | -243725.8742 | -18.8524 | OK
5 | Bangabandhu Memorial Museum | 11 |  | DHKC9334 | 1 | 14338.06 | 14682.59 | 344.53 | 60 |  | 20671.8 | 20897.995 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 20897.995 | 15191.4145 | 5706.5805 | 37.5645 | OK
6 | Iqbal Road O/H | 11 |  | DHKC9330 | 1 | 89627.44 | 116028.77 | 26401.33 | 60 |  | 1584079.8 | 1601413.1174 | Shyamoli |  |  |  | Iqbal Road O/H | 1601413.1174 | 1445983.4794 | 155429.638 | 10.7491 | OK
7 | Town Hall | 11 |  | DHKC9351 | 1 | 90486.3 | 129046.8 | 38560.5 | 60 |  | 2313630 | 2338946.2013 | Shyamoli |  |  |  | Town Hall | 2338946.2013 | 2443589.8569 | -104643.6556 | -4.2824 | OK
8 | Post Office | 11 |  | DHKC9331 | 1 | 89803.72 | 114408.51 | 24604.79 | 60 |  | 1476287.4 | 1492441.2314 | Shyamoli |  |  |  | Post Office | 1492441.2314 | 800074.8889 | 692366.3425 | 86.5377 | FAULT
9 | Shangshad Bhaban | 11 |  | DHKC9370 | 1 | 91884.25 | 98850.73 | 6966.48 | 60 |  | 417988.8 | 422562.5169 | Shere b.nagar |  |  |  | Shangshad Bhaban | 422562.5169 | 201468.8118 | 221093.7051 | 109.7409 | FAULT
10 | Jakir Hossain Road | 11 |  | DHKC9373 | 1 | 31102.13 | 52169.33 | 21067.2 | 60 |  | 1264032 | 1277863.2905 | Satmasjid |  |  |  | Jakir Hossain Road | 1277863.2905 | 932184.0427 | 345679.2478 | 37.0827 | OK
11 | New Colony O/H Feeder | 11 |  | DHKC9369 | 1 | 47348.96 | 69251.43 | 21902.47 | 60 |  | 1314148.2 | 1328527.8719 | Satmasjid |  |  |  | New Colony O/H Feeder | 1328527.8719 | 1049745.8615 | 278782.0104 | 26.5571 | OK
12 | Aurangzeb Feeder | 11 |  | DHKC9321 | 1 | 78884.84 | 112056.46 | 33171.62 | 60 |  | 1990297.2 | 2012075.4293 | Shyamoli |  |  |  | Aurangzeb Feeder | 2012075.4293 | 1228983.3054 | 783092.1238 | 63.7187 | FAULT
13 | Asadgate Local Feeder | 11 |  | DHKC9338 | 1 | 63243.46 | 93460.16 | 30216.7 | 60 |  | 1813002 | 1832840.2298 | Satmasjid |  |  |  | Asadgate Local Feeder | 1832840.2298 | 1138654.9426 | 694185.2872 | 60.9654 | FAULT
14 | Sonarbangla Road | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli | Check |  |  | Sonarbangla Road | 0 | 29498.9648 | -29498.9648 | -100 | CHECK
15 | Humayun Road | 11 |  | DHKC9366 | 1 | 15150.34 | 42688.17 | 27537.83 | 60 |  | 1652269.8 | 1670349.266 | Shyamoli |  |  |  | Humayun Road | 1670349.266 | 1193735.5816 | 476613.6844 | 39.9262 | OK
16 | NHA | 11 |  | DHKC9374 | 1 | 48654.25 | 52311.92 | 3657.67 | 60 | 12018 | 219460.2 | 221861.5773 | Shyamoli | From Satmasjid |  |  | NHA | 221861.5773 | 187072.6322 | 34788.9451 | 18.5965 | OK
17 | Auxiliary transformer | 0.415 |  |  | 1 | 620619 | 626701 | 6082 | 1 |  | 6082 | 6148.5505 | Satmasjid |  |  |  | Auxiliary transformer | 6148.5505 | 5151.827 | 996.7235 | 19.347 | OK
[9 empty] | Grand Total | 17793034.2 | 17600446.6 | 17793034.2 | 1.0942
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 1769725.8951
[5 empty] | Dhanmondi | at 33 KV level |  | 1191754.0645
[5 empty] | Satmasjid | at 33 KV level |  | 5482449.4177
[5 empty] | Shyamoli | at 33 KV level |  | 9349104.8226
at 33 KV level
[5 empty] | Total = |  |  | 17793034.2 | 0
33 KV SIDE of___ BANASREE 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADARTEK 33 KV SIDE
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 89034 | 93583 | 4549 | 2000 | 0 | 9098000 | 9133965.9893
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 82757 | 85518 | 2761 | 2000 | 0 | 5522000 | 5543829.4343
[9 empty] | Total |  | 14620000 | 14677795.4236 | 0.39532
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import |  | 1 | 17062220 | 17062220 | 0 | 1 | 0
2 | Madertek Circuit-02 | 33 | Import |  | 1 | 14889540 | 14889540 | 0 | 1 | 0
3 | Ullon O/H | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
[9 empty] | Total | 0 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 | 33 | Export | 14 | 1 | 3072240 | 12307620 | 9235380 | 1 |  | 9235380
2 | Transformer-02 | 33 | Export | 74 | 1 | 175600 | 7251760 | 7076160 | 1 |  | 5522000 |  |  | Meter Problem
[9 empty] | Total |  | 14757380 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV Import |  |  | KWH |  | BUS LOSS |  | KWH
| MADARTEK 33 KV SIDE |  | 14677795.4236 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 14477376.8378
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 14477376.8378 |  | 33 KV TX HV SIDE |  | 14757380 | 200418.5858
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -280003.1622
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -1.934%
| TOTAL IMPORT |  | 14677795.4236
11 KV SIDE of___BANASREE 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 9235380 |  | 9060150.0063 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | 198 | 1 |  |  | 0 | 1 | 5522000 |  | 5417226.8315 | [7 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 14757380 |  | 14477376.8378 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| BANASREE 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | 11 |  | 141 | 1 | 9842000 | 11717760 | 1875760 | 1 |  | 1875760 | 1879685.8324 | Banosree |  |  |  | Angur Jora | 1879685.8324 | 1498675.9006 | 381009.9318 | 25.4231 | OK
2 | Block F-G Avenue | 11 |  | 68 | 1 | 129240 | 2777480 | 2648240 | 1 |  | 2648240 | 2653782.5782 | Banosree | 2977480 |  |  | Block F-G Avenue | 2653782.5782 | 2238787.1921 | 414995.3861 | 18.5366 | OK
3 | Banasree Main Road(Monpura) | 11 |  | 168 | 1 | 1057540 | 2694560 | 1637020 | 1 |  | 1637020 | 1640446.1666 | Banosree |  |  |  | Banasree Main Road(Monpura) | 1640446.1666 | 1086141.2828 | 554304.8837 | 51.0343 | FAULT
4 | Baitul Kuddus | 11 |  | 62 | 1 | 3000320 | 5086120 | 2085800 | 1 |  | 2085800 | 2090165.4312 | Banosree |  |  |  | Baitul Kuddus | 2090165.4312 | 2076179.9483 | 13985.4829 | 0.67362 | OK
5 | Ideal | 11 |  |  | 1 | 5981320 | 6710680 | 729360 | 1 |  | 729360 | 730886.4987 | Banosree |  |  |  | Ideal | 730886.4987 | 674737.2841 | 56149.2146 | 8.3216 | OK
6 | Central Mosque | 11 |  | 46 | 1 | 3601600 | 5624400 | 2022800 | 1 |  | 2022800 | 2027033.5767 | Banosree |  |  |  | Central Mosque | 2027033.5767 | 2004627.9156 | 22405.6612 | 1.1177 | OK
7 | Larive | 11 |  | 47 | 1 | 6192360 | 7265440 | 1073080 | 1 |  | 1073080 | 1075325.8802 | Banosree |  |  |  | Larive | 1075325.8802 | 1072634.4234 | 2691.4568 | 0.25092 | OK
8 | Bank Colony | 11 |  |  | 1 | 2495880 | 3178720 | 682840 | 1 |  | 682840 | 684269.1356 | Khilgaon |  |  |  | Bank Colony | 684269.1356 | 699853.1782 | -15584.0426 | -2.2268 | OK
9 | Salambagh | 11 |  |  | 1 | 208800 | 1440440 | 1231640 | 1 |  | 1231640 | 1234217.735 | Khilgaon |  |  |  | Salambagh | 1234217.735 | 1063226.0579 | 170991.6771 | 16.0823 | OK
10 | Titas Road | 11 |  |  | 1 | 1065520 | 1526120 | 460600 | 1 |  | 460600 | 461564.0031 | Khilgaon |  |  |  | Titas Road | 461564.0031 | 598299.362 | -136735.3589 | -22.854 | OK
11 | AT-1 | 0.415 |  | 7734 | 1 | 3113.136 | 3113.136 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | AT-2 | 0.415 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 14477376.8378 | 14447140 | 14477376.8378 | 0.20929
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH |  |  |  |  | 0.20929
[5 empty] | Banosree | at 33 KV level |  | 12097325.9641
[5 empty] | Khilgaon | at 33 KV level |  | 2380050.8737
[5 empty] | Total = |  |  | 14477376.8378 | 0
33 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MADERTEK 33 KV SIDE
1 | Goran | 33 | Export | SIEM0510 | 1 | 335181 | 339866 | 4685 | 2000 | 0 | 9370000 | 9407041.253
ULLON 33 KV SIDE
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total | 0 | 9370000 | 9407041.253
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import | HA-030701133-03 | 1 | 79224060 | 88618525 | 9394465 | 1 | 9394465
2 | Ullon O/H | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
[9 empty] | Total | 9394465 | 0 | 0
GORAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
GORAN 33 KV SIDE
1 | Transformer-01 | 33 | Export | HA-030800176-03 | 1 | 6935886 | 9395119 | 2459233 | 1 |  | 2459233
2 | Transformer-02 | 33 | Export | HA-030701133-03 | 1 | 72102260 | 75193098 | 3090838 | 1 |  | 3090838
3 | Transformer-03 | 33 | Export | DHK-57075 | 1 | 11269.99 | 11429.52 | 159.53 | 120000 |  | 3819929 |  |  | Problem
[9 empty] | Total |  | 9370000
| 33 KV IMPORT |  | KWH |  | 33 KV IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MADERTEK 33 KV SIDE |  | 9407041.253 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9407041.253
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 9407041.253 |  | 33 KV TX HV SIDE |  | 9370000
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 37041.253
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.3938%
| TOTAL IMPORT |  | 9407041.253
11 KV SIDE of___GORAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming | 11 | IMPORT |  | 1 | 47547790 | 50001787 | 2453997 | 1 | 2453997 |  | 2468226.2351
| 33/11 kV Transfomer-2 Incoming | 11 |  |  | 1 | 79651406 | 82735440 | 3084034 | 1 | 3084034 |  | 3101916.4362
| 33/11 kV Transfomer-3 Incoming | 11 |  |  | 1 | 59748590 | 63563369 | 3814779 | 1 | 3814779 |  | 3836898.5817
[9 empty] | Total | 9352810 |  | 9407041.253
GORAN 11 KV SIDE
1 | Meradia | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estimated | 0 | 0 | Banosree | NO LOAD |  |  | Meradia | 0 | 668567.2242 | -668567.2242 | -100 | CHECK
2 | Shipahibagh | 11 |  | HA-021001030-02 | 1 | 33607890 | 35007828 | 1399938 | 1 |  | 1399938 | 1411235.5236 | Bashabo |  |  |  | Shipahibagh | 1411235.5236 | 1611501.2913 | -200265.7677 | -12.4273 | OK
3 | Farazi Hospital | 11 |  | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 |  | 0 | 0 | Banosree | NO LOAD |  |  | Farazi Hospital | 0 | 528636.3396 | -528636.3396 | -100 | CHECK
4 | West Bansree | 11 |  | New Meter | 1 | 87359660 | 89182268 | 1822608 | 1 |  | 1822608 | 1837316.4777 | Banosree |  |  |  | West Bansree | 1837316.4777 | 1813347.7746 | 23968.7031 | 1.3218 | OK
5 | Model School(Nearest) | 11 |  | HA-030701099-03 | 1 | 10314560 | 12612480 | 2297920 | 1 |  | 2297920 | 2316464.2537 | Banosree |  |  |  | Model School(Nearest) | 2316464.2537 | 2278837.8654 | 37626.3884 | 1.6511 | OK
6 | Bhuiyan Para | 11 |  | HA-021100508-02 | 1 | 48180236 | 50569666 | 2389430 | 1 |  | 2389430 | 2408712.741 | Banosree |  |  |  | Bhuiyan Para | 2408712.741 | 2384526.6441 | 24186.0968 | 1.0143 | OK
7 | Bonobithi (Ideal) School | 11 |  | HA-021100879-02 | 1 | 11161980 | 12579186 | 1417206 | 1 |  | 1417206 | 1428642.8767 | Banosree |  |  |  | Bonobithi (Ideal) School | 1428642.8767 | 1415588.5508 | 13054.3258 | 0.92218 | OK
8 | AT-01 | 0.415 |  | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 | 0.415 |  | 3043146 | 1 | 4579.3 | 4637.2 | 57.9 | 80 |  | 4632 | 4669.3803 | Banosree |  |  |  | AT-02 | 4669.3803 | 4883.3099 | -213.9296 | -4.3808 | OK
[9 empty] | Grand Total | 9407041.253 | 9331734 | 9407041.253 | 0.807
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 7995805.7294
[5 empty] | Bashabo | at 33 KV level |  | 1411235.5236
[5 empty] | Total = |  |  | 9407041.253 | 0
33 KV SIDE of___ LALMATIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV Sending SIDE (Tariff Point)
8 | Lalmatia Circuit-2 | 33 | 0 | SICAM | 1 | 37.78 | 58.14 | 20.36 | 1000 | Estimated | 13830210 | 13435879.8635
[9 empty] | Total |  | 13830210 | 13435879.8635
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import |  | 1 |  |  | 0 |  | 0
2 | Shatmasjid-2 | 33 | Import |  | 1 |  |  | 0 |  | 0
3 | Kallayanpur | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
[9 empty] | Total | 0 | 0 | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 13435879.8635 |  | EXPORT TO OTHER S/S |  |  | 0 |  | LALMATIA 33 KV NET IMPORT |  | 13435879.8635
| IMPORT-2 |  |  |  | LALMATIA 33 KV NET IMPORT |  |  | 13435879.8635 |  | LALMATIA 11 KV NET IMPORT |  | 13830210
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -394330.1365
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -2.935%
| TOTAL IMPORT |  | 13435879.8635
11 KV SIDE of___LALMATIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | DHK000180 | 1 | 2576522 | 2647739 | 71217 | 90 | 6409530 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | DHK000177 | 1 | 2517174 | 2599626 | 82452 | 90 | 7420680 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 13830210 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| Lalmatia 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 115 | 1398777.66 | 1399733.2864 | Dhanmondi |  |  |  | Shankor O/H | 1399733.2864 | 1481086.0293 | -81352.7429 | -5.4928 | OK
2 | Bangabobondhu museum | 11 | Export |  | 1 | 627449 | 627449 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 73972995 | 76132438 | 2159443 | 1 |  | 2159443 | 2160918.3029 | Dhanmondi |  |  |  | Road No-13/A | 2160918.3029 | 2138411.3491 | 22506.9539 | 1.0525 | OK
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 94656775 | 96836903 | 2180128 | 1 |  | 2180128 | 2181617.4346 | Dhanmondi |  |  |  | Jaforabad | 2181617.4346 | 2186321.8068 | -4704.3722 | -0.21517 | OK
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25049.8 | 25242.7 | 192.9 | 3333.33 |  | 642999.357 | 643438.6457 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 643438.6457 | 650938.4197 | -7499.774 | -1.1521 | OK
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 68422.1 | 68865.4 | 443.3 | 3333.33 |  | 1477665.189 | 1478674.7103 | Dhanmondi |  |  |  | Road No -15 | 1478674.7103 | 1554870.4313 | -76195.721 | -4.9005 | OK
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 76328 | 76765.7 | 437.7 | 3333.33 |  | 1458998.541 | 1459995.3095 | Dhanmondi |  |  |  | Road No-27 South | 1459995.3095 | 1391129.2206 | 68866.0889 | 4.9504 | OK
| Road 25 | 11 | Export |  | 1 | 69083.8 | 69416.1 | 332.3 | 3333.3 |  | 1107655.59 | 1108412.3257 | Dhanmondi |  |  |  | Road 25 | 1108412.3257 | 1065650.4198 | 42761.9059 | 4.0128 | OK
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37454.6 | 37575.5 | 120.9 | 3333.33 |  | 402999.597 | 403274.921 | Dhanmondi |  |  |  | Ibne Sina | 403274.921 | 348956.6786 | 54318.2424 | 15.5659 | OK
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 56367922 | 57291365 | 923443 | 1 |  | 923443 | 924073.8841 | Dhanmondi |  |  |  | Road No-31 (PARI) | 924073.8841 | 957418.9684 | -33345.0844 | -3.4828 | OK
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 63621040 | 64955658 | 1334618 | 1 | 20 days | 2068657.9 | 2070071.1797 | Dhanmondi | Converted to 31 days |  |  | Satmoszid Road West | 2070071.1797 | 1836546.6764 | 233524.5034 | 12.7154 | OK
[9 empty] | Grand Total | 13830210 | 13820767.834 | 13830210 | 0.068319
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Dhanmondi | at 33 KV level |  | 13830210
[5 empty] | Total = |  |  | 13830210 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
33 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2001.34 | 2031.88 | 30.54 | 240000 | 0 | 7329600 | 7334639.1627
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1318.74 | 1347.73 | 28.99 | 240000 | 0 | 6957600 | 6962383.4095
[9 empty] | Total | 0 | 14287200 | 14297022.5722
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 | 33 |  |  | 1 | 0 | 0 | 0 | 3000
[9 empty] | Total | 0 | 0 | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
| Green Road Dormatory | 33 | EXPORT | [7 empty] | 0
| Green Road Dormatory | 33 | [8 empty] | 0
Total
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0 | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Dhanmondi (33 KV Side) |  | 14297022.5722 |  | EXPORT TO OTHER S/S |  |  | 0 |  | Green Road 33 KV NET IMPORT |  | 14297022.5722
| IMPORT-2 |  |  |  | Green Road 33 KV NET IMPORT |  |  | 14297022.5722 |  | Green Road 11 KV NET IMPORT |  | 13414120.4173
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 14297022.5722 |  | LOSS UNITS=> |  | 882902.1549
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 6.175%
| TOTAL IMPORT |  | 14297022.5722
11 KV SIDE of___GREEN ROAD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 00138 | 1 | 2778024 | 2854577 | 76553 | 100 | 7655300
2 | Transfomer-2 Incoming | 11 | Import | HA-021101496 | 1 | 7981.2672 | 7981.2672 | 0 | 10000 | 7329600
[9 empty] | Total | 14984900 |  | 0
Green Road 11 KV SIDE
1 | Lab aid/local RMU | 11 |  | 3C65883 | 1 | 44242 | 48899 | 4657 | 300 |  | 1397100 | 1422394.5672 | Paribag |  |  |  | Lab aid/local RMU | 1422394.5672 | 1300800.6538 | 121593.9134 | 9.3476 | OK
2 | Green View | 11 |  | DHK000151 | 1 | 66171.3 | 66511.6 | 340.3 | 3333.33 |  | 1134332.199 | 1154869.3417 | Paribag |  |  |  | Green View | 1154869.3417 | 1138970.3673 | 15898.9744 | 1.3959 | OK
3 | Central Road | 11 |  | 65943 | 1 | 4190 | 9730 | 5540 | 300 |  | 1662000 | 1692090.5953 | Paribag |  |  |  | Central Road | 1692090.5953 | 1598247.1854 | 93843.4098 | 5.8716 | OK
4 | New Market | 11 |  | DHK000194 | 1 | 45601.3 | 45899.3 | 298 | 3333.33 |  | 993332.34 | 1011316.673 | Jigatola |  |  |  | New Market | 1011316.673 | 1327346.2785 | -316029.6055 | -23.8091 | OK
5 | DPH Feeder | 11 |  | HA-021100459 | 1 | 41222.8 | 41350 | 127.2 | 1 | 20 | 243265.68 | 247670.0176 | Paribag |  |  |  | DPH Feeder | 247670.0176 | 295911.0318 | -48241.0142 | -16.3025 | OK
6 | Dhanmondi Rd 4(md Banglo | 11 |  | 6604464 | 1 | 4428.98 | 4450.58 | 21.6 | 60000 |  | 1296000 | 1319464.1465 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1319464.1465 | 1648927.7304 | -329463.5839 | -19.9805 | OK
1 | Green Road East | 11 |  | HA-021101050 | 1 | 90783634 | 92229088 | 1445454 | 1 |  | 1445454 | 1471624.0188 | Paribag |  |  |  | Green Road East | 1471624.0188 | 1398367.7417 | 73256.2771 | 5.2387 | OK
2 | North Road | 11 |  | HA-021100884 | 1 | 75203876 | 76809718 | 1605842 | 1 |  | 1605842 | 1634915.8518 | Paribag |  |  |  | North Road | 1634915.8518 | 1695610.1435 | -60694.2917 | -3.5795 | OK
3 | Green road SS | 11 |  | DHK00135 | 1 | 14731419 | 16023524 | 1292105 | 1 |  | 1292105 | 1315498.6273 | Paribag |  |  |  | Green road SS | 1315498.6273 | 1209396.682 | 106101.9453 | 8.7731 | OK
4 | Plane Moszid | 11 |  | HA-021100962 | 1 |  | 0 | 0 | 1 | 80 | 973062.72 | 990680.0705 | Paribag |  |  |  | Plane Moszid | 990680.0705 | 946915.3019 | 43764.7686 | 4.6218 | OK
5 | Malancha | 11 |  | HA-021100953 | 1 | 29474408 | 30602490 | 1128082 | 1 |  | 1128082 | 1148505.9825 | Paribag |  |  |  | Malancha | 1148505.9825 | 848599.4692 | 299906.5133 | 35.3414 | OK
| AT -1 |  |  |  |  | 22891 | 22891 |  | 1 |  | 5000 | 5090.5253 | Paribag |  |  |  | AT -1 | 5090.5253 | 5027.8318 | 62.6934 | 1.2469 | OK
[9 empty] | Grand Total | 13414120.4173 | 13175575.939 | 13414120.4173 | 1.8105
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 11083339.5978
[5 empty] | Jigatola | at 33 KV level |  | 2330780.8195
[5 empty] | Total = |  |  | 13414120.4173 | 0
33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory | 33 | 0 | 76026305 | 1 | 7974.85 | 7993.99 | 19.14 | 180000 | Reading From G. Dormitory Side | 6651020 | 6704636.3993
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total | 0 | 6651020 | 6704636.3993
GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING)
1 | Mogbazar Grid | 33 | Import | BD 017064 | 1 | 7995.25 | 14646.27 | 6651.02 | 1000 | 6651020
2 | Green Road SS | 33 | Import | BD 017070 | 1 | 31763.57 | 32911.2 | 1147.63 | 1000 | 1147630
3 | Jigatola Ckt-1 | 33 | Import |  | 1 | 6080.44 | 8290.49 | 2210.05 | 1000 | 2210050
[9 empty] | Total | 10008700 | 0 | 0
GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
GREEN ROAD DORMITORY 33 KV SIDE
1 | Transformer-01 | 33 | Export | BD 017065 | 1 | 87683.21 | 97528.28 | 9845.07 | 888.89 |  | 8751184.2723
2 | Transformer-02 | 33 | Export | BD 017069 | 1 | 83718.42 | 88794.35 | 5075.93 | 888.89 |  | 4511943.4177
[9 empty] | Total |  | 13263127.69 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 6704636.3993 |  | EXPORT TO OTHER S/S |  |  | 0 |  | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 6704636.3993
[5 empty] | GREEN ROAD DORMITORY 33 KV NET IMPORT |  |  | 6704636.3993 |  | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 13170090
[5 empty] | TOTAL EXPORT |  |  | 6704636.3993 |  | LOSS UNITS=> |  | -6465453.6007
[5 empty] | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | -96.43%
| TOTAL IMPORT |  | 6704636.3993
11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD 014050 | 1 | 54324.8 | 63005.48 | 8680.68 | 1000 | 8680680
2 | Transformer-02 Incoming | 11 | Import | BD 014059 | 1 | 62159.23 | 66648.64 | 4489.41 | 1000 | 4489410
[9 empty] | Total | 13170090 |  | 0
GREEN ROAD DORMITORY 11 KV SIDE
1 | North Dhanmondi | 11 |  | BD 014039 | 1 | 21479.71 | 21702.59 | 222.88 | 2000 |  | 445760 | 452285.2955 | Paribag |  |  |  | North Dhanmondi | 452285.2955 | 463052.9514 | -10767.6559 | -2.3254 | OK
2 | Lake circus | 11 |  | BD 014047 | 1 | 32675.64 | 33605.68 | 930.04 | 2000 |  | 1860080 | 1887308.9386 | Paribag |  |  |  | Lake circus | 1887308.9386 | 1820096.9401 | 67211.9985 | 3.6928 | OK
3 | Bashir Uddin | 11 |  | BD 014037 | 1 | 13303.54 | 13668.5 | 364.96 | 2000 |  | 729920 | 740604.9957 | Paribag |  |  |  | Bashir Uddin | 740604.9957 | 721318.3686 | 19286.6271 | 2.6738 | OK
4 | Raza Bazar | 11 |  | BD 013939 | 1 | 19315.96 | 19945.29 | 629.33 | 2000 |  | 1258660 | 1277085.001 | Shere b.nagar |  |  |  | Raza Bazar | 1277085.001 | 1156597.3875 | 120487.6134 | 10.4174 | OK
5 | Rasel Squar | 11 |  | BD 013970 | 1 | 29493.11 | 30409.89 | 916.78 | 2000 |  | 1833560 | 1860400.7233 | Shere b.nagar |  |  |  | Rasel Squar | 1860400.7233 | 1926389.5081 | -65988.7848 | -3.4255 | OK
6 | Bow Bazar | 11 |  | BD 013967 | 1 | 22285.98 | 22875.2 | 589.22 | 2000 |  | 1178440 | 1195690.6937 | Shere b.nagar |  |  |  | Bow Bazar | 1195690.6937 | 855827.0012 | 339863.6925 | 39.7117 | OK
7 | BRB Hospital | 11 |  | BD 014003 | 1 | 11692.21 | 12053.73 | 361.52 | 2000 |  | 723040 | 733624.2823 | Shere b.nagar |  |  |  | BRB Hospital | 733624.2823 | 608795.7579 | 124828.5244 | 20.5042 | OK
8 | Green Road North | 11 |  | BD 013969 | 1 | 13569.2 | 14142.63 | 573.43 | 2000 |  | 1146860 | 1163648.4072 | Paribag |  |  |  | Green Road North | 1163648.4072 | 1179246.6075 | -15598.2003 | -1.3227 | OK
1 | Water Bhaban | 11 |  | BD 014004 | 1 | 4582.24 | 4730.78 | 148.54 | 2000 |  | 297080 | 301428.8307 | Shere b.nagar |  |  |  | Water Bhaban | 301428.8307 | 245765.1379 | 55663.6928 | 22.6491 | OK
2 | Alamin Road | 11 |  | BD 014006 | 1 | 17601.7 | 17886.83 | 285.13 | 2000 |  | 570260 | 578607.7993 | Paribag |  |  |  | Alamin Road | 578607.7993 | 566210.4011 | 12397.3981 | 2.1895 | OK
3 | Katal Bagan | 11 |  |  | 1 | 4467.6 | 5394.19 | 926.59 | 2000 |  | 1853180 | 1880307.9323 | Paribag |  |  |  | Katal Bagan | 1880307.9323 | 1367996.8058 | 512311.1265 | 37.4497 | OK
4 | Eastern Pantho chaya | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan | 11 |  | BD 014005 | 1 | 5236.41 | 5394.19 | 157.78 | 2000 |  | 315560 | 320179.3518 | Paribag |  |  |  | Kalabagan | 320179.3518 | 337608.0262 | -17428.6744 | -5.1624 | OK
6 | Univer Hospital | 11 |  | BD 013963 | 1 | 479.37 | 606.64 | 127.27 | 2000 |  | 254540 | 258266.1053 | Paribag |  |  |  | Univer Hospital | 258266.1053 | 227255.8819 | 31010.2235 | 13.6455 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 |  | BD 013971 | 1 | 9011.39 | 9267.96 | 256.57 | 2000 |  | 513140 | 520651.6433 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 520651.6433 | 453949.0502 | 66702.5931 | 14.6939 | OK
[9 empty] | Grand Total | 13170090 | 12980080 | 13170090 | 1.4639
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 7801860.469
[5 empty] | Shere b.nagar | at 33 KV level |  | 5368229.531
[5 empty] | Total = |  |  | 13170090 | 0
33 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
ULLON 33 KV SIDE
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1471.3116 | 1503.439 | 32.1274 | 240000 | Estimated | 6629904 | 6736010.2412
2 | Taltala-2 | 33 |  | BD001837 | 1 | 2432.5066 | 2463.334 | 30.8274 | 240000 | 0 | 7398576 | 7516984.2137
[9 empty] | Total | 0 | 14028480 | 14252994.4549
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 | 0 | 0
| 33 KV Ullon-ckt-2 incoming | 33 |  |  | 1 |  |  | 0 | 1000 | 0 | 0
[9 empty] | Total | 0 | 0 | 14252994.4549
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
| 33 KV Kakrail Feeder.(import) | 33 | EXPORT | [7 empty] | 0
| 33 KV Khilgaon Feeder(Import) | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 |  |  | 0 | 180 |  | 0 | 0
[9 empty] | Total |  | 0 | 14252994.4549 | #DIV/0!
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| ULLON 33 KV SIDE |  | 14252994.4549 |  | EXPORT TO OTHER S/S |  |  | 0 |  | TALTOLA 33 KV NET IMPORT |  | 14252994.4549
| IMPORT-2 |  |  |  | TALTOLA 33 KV NET IMPORT |  |  | 14252994.4549 |  | TALTOLA 11 KV NET IMPORT |  | 14028480
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 14252994.4549 |  | LOSS UNITS=> |  | 224514.4549
| IMPORT-4 |  |  |  | 33 KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 1.575%
| TOTAL IMPORT |  | 14252994.4549
11 KV SIDE of___TALTOLA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming | 11 | Import | 06604431 | 1 | 8421.28 | 8463.21 | 41.93 | 160000 | 6708800
2 | Transformer-02 Incoming | 11 | Import | 06604341 | 1 | 9126.35 | 9170.65 | 44.3 | 160000 | 7088000
3 | Transformer-03 Incoming | 11 | Import | 0211001039-02 | 1 | 98259961 | 98491641 | 231680 | 1 | 231680
[9 empty] | Total | 14028480 |  | 0
TALTOLA 11 KV SIDE
1 | Matir Masjid | 11 |  | DHK00170 | 1 | 15455.6 | 17730 | 2274.4 | 888.8889 |  | 2021688.8889 | 2023352.6919 | Khilgaon |  |  |  | Matir Masjid | 2023352.6919 | 2146676.0813 | -123323.3894 | -5.7449 | OK
2 | Hajipara | 11 |  | DHK-00108 | 1 | 919.3 | 1596.3 | 677 | 2222.2222 |  | 1504444.4444 | 1505682.5673 | Khilgaon |  |  |  | Hajipara | 1505682.5673 | 2127007.9326 | -621325.3653 | -29.2112 | OK
3 | Nearest Feeder | 11 |  | DHK-00106 | 1 | 90742 | 90788.1 | 46.1 | 2222.222 |  | 102444.4342 | 102528.7436 | Bashabo |  |  |  | Nearest Feeder | 102528.7436 | 771596.5243 | -669067.7807 | -86.7121 | CHECK
4 | Reazbagh | 11 |  | DHK-00109 | 1 | 93540 | 94301.5 | 761.5 | 2222.222 |  | 1692222.053 | 1693614.7124 | Khilgaon |  |  |  | Reazbagh | 1693614.7124 | 1745214.284 | -51599.5716 | -2.9566 | OK
5 | Chowdhury Para | 11 |  | DHK-00107 | 1 | 51625.8 | 51884.4 | 258.6 | 2222.222 |  | 574666.6092 | 575139.5465 | Khilgaon |  |  |  | Chowdhury Para | 575139.5465 | 495930.9841 | 79208.5624 | 15.9717 | OK
6 | Model Colleg | 11 |  | 9122392 | 1 | 2430.4 | 2456.34 | 25.94 | 40000 |  | 1037600 | 1038453.9207 | Khilgaon |  |  |  | Model Colleg | 1038453.9207 | 979981.0816 | 58472.8391 | 5.9667 | OK
1 | East Rampura | 11 |  | DHK-00181 | 1 | 96542 | 97163 | 621 | 2222.222 |  | 1379999.862 | 1381135.5698 | Khilgaon |  |  |  | East Rampura | 1381135.5698 | 912877.8949 | 468257.675 | 51.2947 | FAULT
2 | Adarshabagh | 11 |  | DHK-00090 | 1 | 46583.7 | 47488.7 | 905 | 2222.222 |  | 2011110.91 | 2012766.0076 | Bashabo |  |  |  | Adarshabagh | 2012766.0076 | 2078282.3339 | -65516.3263 | -3.1524 | OK
3 | Khailgaon Govt Colony | 11 |  | DHK00167 | 1 | 72902.7 | 73598.82 | 696.12 | 2222.222 |  | 1546933.1786 | 1548206.2687 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1548206.2687 | 1569891.8903 | -21685.6216 | -1.3813 | OK
4 | TV Road | 11 |  | 6604434 | 1 | 4966.58 | 4998.51 | 31.93 | 40000 |  | 1277200 | 1278251.1059 | Khilgaon |  |  |  | TV Road | 1278251.1059 | 1110137.9478 | 168113.1582 | 15.1434 | OK
5 | Tilpa Para | 11 |  | 06604476 | 1 | 6510.58 | 6526.36 | 15.78 | 40000 |  | 631200 | 631719.4629 | Bashabo |  |  |  | Tilpa Para | 631719.4629 | 17220.7546 | 614498.7083 | 3568.3611 | FAULT
1 | Navana | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 710861.7366 | -710861.7366 | -100 | CHECK
7 | Shantipur | 11 |  | 0660444 | 1 | 10045960 | 10278394 | 232434 | 1 |  | 232434 | 232625.2878 | Bashabo |  |  |  | Shantipur | 232625.2878 | 1103975.5207 | -871350.233 | -78.9284 | CHECK
2 | AT-01 | 0.415 |  | 9187958 | 1 | 148.1 | 283.22 | 135.12 | 80 |  | 5000 | 5004.1149 | Bashabo |  |  |  | AT-01 | 5004.1149 | 5006.0333 | -1.9184 | -0.038322 | OK
3 | AT-02 | 0.415 |  | 9187959 | 1 | 0 | 0 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 14028480 | 14016944.3804 | 14028480 | 0.082298
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Khilgaon | at 33 KV level |  | 11043836.3832
[5 empty] | Bashabo | at 33 KV level |  | 2984643.6168
[5 empty] | Total = |  |  | 14028480 | 0
33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 | 33 | Import | 35786569 | 1 | 1827.532 | 1853.024 | 25.492 | 180000 | 0 | 4590030.6748
2 | Sher-e-Banglanagar Ckt-02 | 33 | Import | 35786575 | 1 | 614.698 | 630.272 | 15.574 | 180000 | 0 | 2804218.4893
[9 empty] | Total | 0 | 7394249.1641 | 0
[9 empty] | Net Total | 7394249.1641
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
[9 empty] | Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 | 33 | Export | DHK 66510 | 1 |  | 0 | 0 | 180 |  | 0
4 | Transformer-02 | 33 | Export | DHK 66500 | 1 | 668419 | 696458 | 28039 | 180 |  | 5047020
[9 empty] | Total |  | 5047020 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV Sending SIDE (Tariff Point) |  | 7394249.1641 |  | EXPORT TO OTHER S/S |  |  | 0 |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 7394249.1641
| IMPORT-2 |  |  |  | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  |  | 7394249.1641 |  | 33 KV TX HV SIDE |  | 7394249.1641
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7394249.1641
11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 66503 | 1 | 2100400 | 2124390 | 23990 | 180 | 4318200 |  | 4550978.4352
2 | Transfomer-2 Incoming | 11 | Import | DHK 66495 | 1 | 663655 | 678643 | 14988 | 180 | 2697840 |  | 2843270.7289
[9 empty] | Total | 7016040 |  | 7394249.1641
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Sher-e-Banglanagar Local | 11 |  | DHK 66503 | 1 | 71658 | 73849 | 2191 | 60 |  | 131460 | 137740.1655 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 137740.1655 | 96854.5353 | 40885.6302 | 42.2134 | FAULT
2 | Mirpur Road East | 11 |  | DHK 60961 | 1 | 796344 | 805750 | 9406 | 60 |  | 564360 | 591320.8565 | Shere b.nagar |  |  |  | Mirpur Road East | 591320.8565 | 481840.9338 | 109479.9226 | 22.7212 | OK
3 | Gonobhaban school | 11 |  | DHK 66492 | 1 | 516834 | 519667 | 2833 | 60 |  | 169980 | 178100.36 | Shere b.nagar |  |  |  | Gonobhaban school | 178100.36 | 132559.6365 | 45540.7235 | 34.3549 | OK
4 | Babor Road | 11 |  | DHK 66489 | 1 | 663765 | 688132 | 24367 | 60 |  | 1462020 | 1531864.2685 | Shyamoli |  |  |  | Babor Road | 1531864.2685 | 1271623.5379 | 260240.7307 | 20.4652 | OK
5 | College Gate | 11 |  | DHK 66487 | 1 | 2526065 | 2552998 | 26933 | 60 |  | 1615980 | 1693179.314 | Shyamoli |  |  |  | College Gate | 1693179.314 | 1906249.0908 | -213069.7768 | -11.1774 | OK
6 | Parade ground | 11 |  | DHK 66490 | 1 | 938217 | 938217 | 0 | 60 |  | 0 | 0 | Satmosjit+Shyamoli |  |  |  | Parade ground | 0 | 652.4188 | -652.4188 | -100 | CHECK
7 | Hospital RMU | 11 |  | DHK 66491 | 1 | 864853 | 873509 | 8656 | 60 |  | 519360 | 544171.0965 | Shere b.nagar |  |  |  | Hospital RMU | 544171.0965 | 481781.623 | 62389.4735 | 12.9497 | OK
1 | Shamoly Square | 11 |  | DHK 61065 | 1 |  | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | 11 |  | DHK 60964 | 1 | 188092.2 | 189395.3 | 1303.1 | 60 |  | 78186 | 81921.1363 | Shere b.nagar |  |  |  | Gonobhaban RMU | 81921.1363 | 92981.5401 | -11060.4038 | -11.8953 | OK
3 | Krishi University | 11 |  | DHK 60963 | 1 | 321467.8 | 330598.6 | 9130.8 | 60 |  | 547848 | 574020.0379 | Shere b.nagar |  |  |  | Krishi University | 574020.0379 | 491360.3171 | 82659.7208 | 16.8226 | OK
4 | NEC | 11 |  | DHK 86073 | 1 | 20.77 | 25.3 | 4.53 | 60000 |  | 271800 | 284784.5503 | Shere b.nagar |  |  |  | NEC | 284784.5503 | 211739.5536 | 73044.9966 | 34.4976 | OK
5 | Novo Theater/Army Musium | 11 |  | DHK 86074 | 1 | 305.62 | 323.21 | 17.59 | 60000 |  | 1055400 | 1105819.0374 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 1105819.0374 | 945414.1415 | 160404.8959 | 16.9666 | OK
6 | Netor | 11 |  | DHK 60962 | 1 | 83465.3 | 92954.2 | 9488.9 | 60 |  | 569334 | 596532.4766 | Shere b.nagar |  |  |  | Netor | 596532.4766 | 549063.7938 | 47468.6828 | 8.6454 | OK
7 | BICC | 11 |  |  | 1 | 25.57 | 26.67 | 1.1 | 60000 |  | 66000 | 69152.9813 | Shere b.nagar |  |  |  | BICC | 69152.9813 | 213518.8776 | -144365.8963 | -67.6127 | CHECK
8 | Auxiliary | 0.415 |  |  | 1 | 5000.69 | 5090.45 | 89.76 | 60 |  | 5385.6 | 5642.8833 | Shere b.nagar |  |  |  | Auxiliary | 5642.8833 | 0 | 5642.8833 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7394249.1641 | 7057113.6 | 7394249.1641 | 4.7772
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 3516772.3495 | Including 41% of Novo Theatre
[5 empty] | Shyamoli | at 33 KV level |  | 3225043.5825
[5 empty] | Satmasjid | at 33 KV level |  | 0
[5 empty] | Tejgaon | at 33 KV level |  | 652433.232 | 59% of Novo Theatre
[5 empty] | Total = |  |  | 7394249.1641 | 0
33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | Estimated | 9510736 | 9571276.435
6 | 33kV Mugdapara Hospital-2 Feeder | 33 |  | ABB03918 | 1 | 283353 | 288011 | 4658 | 2000 | 0 | 9316000 | 9375300.8462
[9 empty] | Total | 0 | 18826736 | 18946577.2812
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 | 33 | Import | 38 | 1 | 261753392 | 271264128 | 9510736 | 1 | 9510736
2 | Maniknagor Incoming-02 | 33 | Import | 15 | 1 | 177070864 | 186357776 | 9286912 | 1 | 9286912
[9 empty] | Total | 18797648 | 0 | 0
MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
MUGDAPARA HOSPITAL 33 KV SIDE
3 | Transformer-01 | 33 | Export | 16 | 1 | 250383600 | 259894444 | 9510844 | 1 |  | 9510844
4 | Transformer-02 | 33 | Export | 196 | 1 | 188324400 | 197611920 | 9287520 | 1 |  | 9287520
[9 empty] | Total |  | 18798364 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANKNAGAR 33 KV SIDE |  | 18797648 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18797648
[5 empty] | 33 KV NET IMPORT |  |  | 18797648 |  | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 18798364
[10 empty] | LOSS UNITS=> |  | -716
[10 empty] | LOSS % IN => |  | -0.003809%
| TOTAL IMPORT |  | 18797648
11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | 192 | 1 | 248486928 | 257944528 | 9457600 | 1 | 9457600 |  | 9503221.1691
2 | Transformer-02 Incoming | 11 | Import | 118 | 1 | 186924688 | 196174496 | 9249808 | 1 | 9249808 |  | 9294426.8309
[9 empty] | Total | 18707408 |  | 18797648
MUGDAPARA HOSPITAL 11 KV SIDE
1 | City Corporation | 11 |  | 93 | 1 | 38123148 | 38782904 | 659756 | 1 |  | 659756 | 660250.7383 | Bashabo |  |  |  | City Corporation | 660250.7383 | 604435.768 | 55814.9702 | 9.2342 | OK
2 | Bot tola | 11 |  |  | 1 | 46813724 | 49052840 | 2239116 | 1 |  | 2239116 | 2240795.0697 | Maniknagar |  |  |  | Bot tola | 2240795.0697 | 2176144.9618 | 64650.1079 | 2.9709 | OK
3 | Jhilpar | 11 |  | 145 | 1 | 31434404 | 32593720 | 1159316 | 1 |  | 1159316 | 1160185.3486 | Mugdapara |  |  |  | Jhilpar | 1160185.3486 | 1293243.8655 | -133058.5169 | -10.2887 | OK
4 | Central Bashaboo | 11 |  | 128 | 1 | 32312322 | 34044596 | 1732274 | 1 |  | 1732274 | 1733572.9987 | Bashabo |  |  |  | Central Bashaboo | 1733572.9987 | 1063507.0164 | 670065.9824 | 63.0053 | FAULT
5 | Kadamtala | 11 |  | 8 | 1.5 | 16228480 | 17533438 | 1304958 | 1 |  | 1957437 | 1958904.8441 | Mugdapara |  |  |  | Kadamtala | 1958904.8441 | 2431031.9292 | -472127.0851 | -19.4209 | OK
6 | Ansar VDP | 11 |  | 119 | 1 | 16573440 | 17300398 | 726958 | 1 |  | 726958 | 727503.1317 | Khilgaon |  |  |  | Ansar VDP | 727503.1317 | 758727.2682 | -31224.1364 | -4.1153 | OK
7 | Mugda Hospital Express-01 | 11 |  |  | 1 | 5037147 | 5309707 | 272560 | 1 |  | 272560 | 272764.3875 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 272764.3875 | 234901.6234 | 37862.764 | 16.1186 | OK
8 | Boro Masjid | 11 |  | 7 | 1.22 | 44310612 | 45410408 | 1099796 | 1 |  | 1341751.12 | 1342757.2732 | Mugdapara |  |  |  | Boro Masjid | 1342757.2732 | 1333628.5362 | 9128.737 | 0.6845 | OK
1 | Anandodhara | 11 |  | 120 | 1 | 44045612 | 44960492 | 914880 | 1 |  | 914880 | 915566.0508 | Maniknagar |  |  |  | Anandodhara | 915566.0508 | 875174.4578 | 40391.593 | 4.6153 | OK
2 | Culvert | 11 |  | 117 | 1 | 33041120 | 34952276 | 1911156 | 1 |  | 1911156 | 1912589.1389 | Bashabo |  |  |  | Culvert | 1912589.1389 | 1755799.0089 | 156790.13 | 8.9298 | OK
3 | Mugda Hospital Express-02 | 11 |  | 97 | 1 | 4845548 | 4845548 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | 11 |  | 98 | 1 | 21673908 | 23101984 | 1428076 | 1 |  | 1428076 | 1429146.8866 | Bashabo |  |  |  | Jhor Pukur | 1429146.8866 | 780472.5797 | 648674.3068 | 83.113 | FAULT
5 | T&T | 11 |  | 99 | 1 | 21219428 | 22071346 | 851918 | 1 |  | 851918 | 852556.8368 | Mugdapara |  |  |  | T&T | 852556.8368 | 780310.3984 | 72246.4384 | 9.2587 | OK
6 | Haider Ali | 11 |  | 9 | 1 | 61336572 | 62774928 | 1438356 | 1 |  | 1438356 | 1439434.5953 | Maniknagar |  |  |  | Haider Ali | 1439434.5953 | 1401967.42 | 37467.1753 | 2.6725 | OK
| 11kv Tilpapara | 11 |  |  | 1 |  | 0 | 0 | 1 | Estimated | 2150000 | 2151612.2434 | Bashabo
7 | AT-01 | 11 |  |  | 1 | 2720 | 2782 | 62 | 1 |  | 0 | 0 | Mugdapara |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | AT-02 | 11 |  |  | 1 | 8.55 | 17 | 8.45 | 1 |  | 8.45 | 8.4563 | Mugdapara |  |  |  | AT-02 | 8.4563 | 0 | 8.4563 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 18797648 | 18783562.57 | 18797648 | 0.074988
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bashabo | at 33 KV level |  | 7887172.0058
[5 empty] | Maniknagar | at 33 KV level |  | 4595795.7159
[5 empty] | Mugdapara | at 33 KV level |  | 5587177.1466
[5 empty] | Khilgaon | at 33 KV level |  | 727503.1317
[5 empty] | Total = |  |  | 18797648 | 0
33 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Taltola 33 KV SIDE
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.0586 | 61.6699 | 0.6113 | 240000 | 0 | 146712 | 149060.0067
MANKNAGAR 33 KV SIDE
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 260650 | 263791 | 3141 | 2000 | 0 | 6282000 | 6321987.9686
[9 empty] | Total | 0 | 6428712 | 6471047.9753
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming | 33 | RECEIVE |  | 1 |  | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming | 33 |  |  | 1 |  | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming | 33 |  |  | 1 | 55887 | 55929 | 42 | 270 |  | 11340
| 33 kV Maniknagor Incoming | 33 |  |  | 1.08 | 897708 | 932297 | 34589 | 180 |  | 6724101.6
[9 empty] | Total |  | 6735441.6
KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
KHILGOAN 33 KV SIDE
3 | Transformer -01 | 33 | Export | DHK60982 | 1 | 805538 | 805616 | 78 | 180 |  | 14040
4 | Transformer -02 | 33 | Export | DHK60947 | 1 | 648028 | 682617 | 34589 | 180 |  | 6226020
[9 empty] | Total |  | 6240060 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| Taltola 33 KV SIDE |  | 6471047.9753 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 6240060
[5 empty] | 33 KV NET IMPORT |  |  | 6240060 |  | 33 KV TX HV SIDE |  | 6240060
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6471047.9753
11 KV SIDE of___KHILGOAN 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | DHK60927 | 1 | 806360 | 806409 | 49 | 180 | 8820 |  | 9271.1625
2 | Transformer-02 Incoming | 11 | Import | DHK60928 | 1 | 812108 | 845039 | 32931 | 180 | 5927580 |  | 6230788.8375
[9 empty] | Total | 5936400 |  | 6240060
KHILGOAN 11 KV SIDE
1 | Shantinagar s/s-1 | 11 |  | DHK60932 | 1 | 189060 | 232427 | 43367 | 60 |  | 2602020 | 2616486.0095 | Rajarbag |  |  |  | Shantinagar s/s-1 | 2616486.0095 | 2832273.6797 | -215787.6702 | -7.6189 | OK
2 | Gulbagh | 11 |  | DHK60934 | 1 | 106648 | 111867 | 5219 | 60 |  | 313140 | 314880.9114 | Rajarbag |  |  |  | Gulbagh | 314880.9114 | 851748.1263 | -536867.215 | -63.0312 | CHECK
3 | Rampura BTV | 11 |  | DHK60933 | 1 | 14049 | 14053 | 4 | 60 |  | 240 | 241.3343 | Khilgaon |  |  |  | Rampura BTV | 241.3343 | 182.2961 | 59.0382 | 32.3859 | OK
4 | West Shantibag | 11 |  | DHK60926 | 1 | 474980 | 490108 | 15128 | 60 |  | 907680 | 912726.2746 | Rajarbag |  |  |  | West Shantibag | 912726.2746 | 856730.8863 | 55995.3883 | 6.5359 | OK
1 | East Malibagh | 11 |  | DHK60929 | 1 | 516292 | 537667 | 21375 | 60 |  | 1282500 | 1289630.0978 | Rajarbag |  |  |  | East Malibagh | 1289630.0978 | 1258754.5436 | 30875.5543 | 2.4529 | OK
2 | Police Line | 11 |  | DHK60930 | 1 | 535700 | 545249 | 9549 | 60 |  | 572940 | 576125.2774 | Rajarbag |  |  |  | Police Line | 576125.2774 | 518510.8627 | 57614.4147 | 11.1115 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 |  | DHK61017 | 1 | 185510 | 187933 | 2423 | 60 |  | 145380 | 146188.2445 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 146188.2445 | 137208.195 | 8980.0495 | 6.5448 | OK
4 | Benjir Bagan | 11 |  | DHK60985 | 1 | 154680 | 157675 | 2995 | 60 |  | 179700 | 180699.0476 | Rajarbag |  |  |  | Benjir Bagan | 180699.0476 | 172634.403 | 8064.6446 | 4.6715 | OK
5 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 827595 | 830961 | 3366 | 60 |  | 201960 | 203082.8028 | Switching |  |  |  | Shantinagar s/s-2 | 203082.8028 | 530299.3436 | -327216.5408 | -61.7041 | CHECK
6 | AT-1 & AT-2 | 0.415 |  | ELIB 7374 | 1 | 1628.18 | 1628.18 | 0 | 60 |  | 0 | 0 | Rajarbag |  |  |  | AT-1 & AT-2 | 0 | 6737.6637 | -6737.6637 | -100 | CHECK
[9 empty] | Grand Total | 6240060 | 6205560 | 6240060 | 0.55595
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Rajarbag | at 33 KV level |  | 6032741.7805 | Including Switching
[5 empty] | Khilgaon | at 33 KV level |  | 241.3343
[5 empty] | Moghbazar | at 33 KV level |  | 126229.899
[5 empty] | Kakrail | at 33 KV level |  | 80846.9863
[5 empty] | Total = |  |  | 6240060 | 0
11 KV SIDE of___Santinagar Switching S/S | [13 empty] | Month May-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
From Source End
1 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 827595 | 830961 | 3366 | 60 |  | 201960 | 203082.8028 | 0.55595
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | -3972 | -3994.0825 | Rajarbag
2 | 11 Fortune(MogBazar)-new | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 125532 | 126229.899 | Moghbazar
3 | Centerpoint-Kakrail | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 80400 | 80846.9863 | Kakrail
[11 empty] | 201960 | 203082.8028 | 0.55595
33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 | 33 | Import |  | 1 | 956.721 | 990.553 | 33.832 | 180000 | 0 | 6091711.8229
2 | Sherebangla to Monipuripara-2 | 33 | Import |  | 1 | 693.36 | 716.372 | 23.012 | 180000 | 0 | 4143487.5996
[9 empty] | Total | 0 | 10235199.4224 | 0
[9 empty] | Net Total | 10235199.4224
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | BD017103 | 1 | 13234.85 | 18652.7 | 5417.85 | 1000 | 5417850
2 | Agargaon Ckt-02 | 33 | Import | BD017104 | 1 | 10836.11 | 14516.91 | 3680.8 | 1000 | 3680800
[9 empty] | Total | 9098650 | 0 | 0
MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
MONIPURIPARA 33 KV SIDE
3 | Transformer-01 | 33 | Export | BD017102 | 1 | 72701.16 | 78812.11 | 6110.95 | 888.8889 |  | 5431955.6235
4 | Transformer-02 | 33 | Export | BD017105 | 1 | 25171.13 | 29326.38 | 4155.25 | 888.8889 |  | 3693555.6017
[9 empty] | Total |  | 9125511.2252 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Agargoan 33 KV SIDE |  | 10235199.4224 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10235199.4224
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 10235199.4224 |  | 33 KV TX HV SIDE |  | 9125511.2252
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 1109688.1973
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 10.84%
| TOTAL IMPORT |  | 10235199.4224
11 KV SIDE of___MONIPURIPARA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD014058 | 1 | 72063.17 | 78157.18 | 6094.01 | 1000 | 6094010 |  | 6098245.8731
2 | Transformer -02 Incoming | 11 | Import | BD014062 | 1 | 24341.4 | 28475.48 | 4134.08 | 1000 | 4134080 |  | 4136953.5493
[9 empty] | Total | 10228090 | 0 | 10235199.4224
MONIPURIPARA 11 KV SIDE
1 | Spare | 11 |  | BD013944 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | 11 |  | BD013947 | 1 | 27765.03 | 28604.46 | 839.43 | 1000 |  | 839430 | 873090.4062 | Shere b.nagar |  |  |  | Monipuripara west | 873090.4062 | 818448.0507 | 54642.3555 | 6.6763 | OK
3 | Biggan College | 11 |  | BD013949 | 1 | 15670 | 16491.07 | 821.07 | 1000 |  | 821070 | 853994.1863 | Kakrail |  |  |  | Biggan College | 853994.1863 | 745351.4544 | 108642.7319 | 14.576 | OK
4 | Green Road South | 11 |  | BD013948 | 1 | 25691 | 26639.32 | 948.32 | 1000 |  | 948320 | 986346.7996 | Shere b.nagar |  |  |  | Green Road South | 986346.7996 | 966542.3647 | 19804.4349 | 2.049 | OK
5 | BARC Building O/H | 11 |  | BD014010 | 1 | 10958.76 | 11567.27 | 608.51 | 1000 |  | 608510 | 632910.7169 | Shere b.nagar |  |  |  | BARC Building O/H | 632910.7169 | 587212.7123 | 45698.0045 | 7.7822 | OK
6 | Green Road North | 11 |  | BD014036 | 1 | 51351.51 | 53150.66 | 1799.15 | 1000 |  | 1799150 | 1871294.3358 | Shere b.nagar |  |  |  | Green Road North | 1871294.3358 | 2172260.0458 | -300965.71 | -13.855 | OK
7 | Chundrima Uddan | 11 |  | BD014035 | 1 | 25998.03 | 26974.49 | 976.46 | 1000 |  | 976460 | 1015615.1889 | Shere b.nagar |  |  |  | Chundrima Uddan | 1015615.1889 | 927005.1376 | 88610.0513 | 9.5587 | OK
8 | Spare-02 | 11 |  | BD013940 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Spare-03 | 11 |  | BD013946 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-03 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | 11 |  | BD013964 | 1 | 40112.39 | 40112.39 | 0 | 1000 |  | 0 | 0 | Kakrail |  |  |  | kawran Bazar North | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | NAM Bhanan RMU | 11 |  | BD013950 | 1 | 12279.22 | 13253.69 | 974.47 | 1000 |  | 974470 | 1013545.3917 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 1013545.3917 | 993076.7342 | 20468.6575 | 2.0611 | OK
4 | Novo Theater | 11 |  | BD013938 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | 11 |  | BD013962 | 1 | 35167.77 | 35872.57 | 704.8 | 1000 |  | 704800 | 733061.8614 | Tejgaon |  |  |  | Monipuripara Nearest | 733061.8614 | 872045.4437 | -138983.5823 | -15.9377 | OK
6 | Holy Cross | 11 |  | BD013965 | 1 | 32798.35 | 33881.78 | 1083.43 | 1000 |  | 1083430 | 1126874.592 | Tejgaon |  |  |  | Holy Cross | 1126874.592 | 1167807.0819 | -40932.4899 | -3.5051 | OK
7 | Honda Goli | 11 |  | BD014011 | 1 | 10455.11 | 11371.49 | 916.38 | 1000 |  | 916380 | 953126.0337 | Tejgaon |  |  |  | Honda Goli | 953126.0337 | 771641.8296 | 181484.204 | 23.5192 | OK
8 | Navy Quarter | 11 |  | BD013941 | 1 | 4611.73 | 4780.31 | 168.58 | 1000 |  | 168580 | 175339.91 | Tejgaon |  |  |  | Navy Quarter | 175339.91 | 178532.5907 | -3192.6807 | -1.7883 | OK
9 | AT-01 | 0.415 |  |  | 1 | 1684.35 | 1762.39 | 78.04 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 585.48 | 585.48 | 0 | 1 |  | 0 | 0 | Shere b.nagar |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 10235199.4224 | 9840600 | 10235199.4224 | 4.0099
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 6392802.8391
[5 empty] | Kakrail | at 33 KV level |  | 853994.1863
[5 empty] | Tejgaon | at 33 KV level |  | 2988402.3971
[5 empty] | Total = |  |  | 10235199.4224 | 0
33 KV SIDE of___ Ispahani 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Mogbazar 33 KV SIDE
11 | Ispahani-1 | 33 | 0 | 0 | 1 | 1929.47 | 1936.84 | 7.37 | 180000 | From Ispahani Downsteam Estimated | 2643950 | 2665263.8855
12 | Ispahani-2 | 33 | 0 | 0 | 1 | 3774.88 | 3791.06 | 16.18 | 180000 | 0 | 2912400 | 2935877.963
[9 empty] | Total | 0 | 5556350 | 5601141.8485
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 | 33 | Import |  | 1 | 11005.81 | 13649.76 | 2643.95 | 1000 | 2643950
2 | Mogbazar Ckt-02 | 33 | Import |  | 1 | 13360.6 | 14271.41 | 910.81 | 1000 | 910810
[9 empty] | Total | 3554760 | 0 | 0
Ispahani 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
Ispahani 33 KV SIDE
3 | Transformer-01 | 33 | Export |  | 1 | 17831.45 | 20804.63 | 2973.18 | 888.8889 |  | 2642826.6997 |  | #DIV/0!
4 | Transformer-02 | 33 | Export |  | 1 | 7122.36 | 10392.07 | 3269.71 | 888.8889 |  | 2906408.9252
[9 empty] | Total |  | 5549235.6249 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Mogbazar 33 KV SIDE |  | 5601141.8485 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 5601141.8485
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 5601141.8485 |  | 33 KV TX HV SIDE |  | 5549235.6249
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 51906.2236
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.9267%
| TOTAL IMPORT |  | 5601141.8485
11 KV SIDE of___ Ispahani 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import |  | 1 | 15546.5 | 18126.62 | 2580.12 | 1000 | 2580120 |  | 4087481.5748
2 | Transformer -02 Incoming | 11 | Import |  | 1 | 2035.81 | 2991.27 | 955.46 | 1000 | 955460 |  | 1513660.2737
[9 empty] | Total | 3535580 | 0 | 5601141.8485
Ispahani 11 KV SIDE
1 | Doctor Goli | 11 |  | BD013944 | 1 | 4955.77 | 5839.76 | 883.99 | 1000 |  | 883990 | 898591.0283 | Moghbazar |  |  |  | Doctor Goli | 898591.0283 | 890502.9735 | 8088.0547 | 0.90826 | OK
2 | Ispahani | 11 |  | BD013947 | 1 | 5545.8 | 6529.14 | 983.34 | 1000 |  | 983340 | 999582.0108 | Moghbazar |  |  |  | Ispahani | 999582.0108 | 980405.5522 | 19176.4587 | 1.956 | OK
3 | BTCL | 11 |  | BD013949 | 1 | 2918.2 | 3442.04 | 523.84 | 1000 |  | 523840 | 532492.3633 | Kakrail |  |  |  | BTCL | 532492.3633 | 511701.2188 | 20791.1445 | 4.0631 | OK
4 | Vikarunnesa | 11 |  | BD013948 | 1 | 1899.46 | 2973.78 | 1074.32 | 1000 |  | 1074320 | 1092064.7445 | Kakrail |  |  |  | Vikarunnesa | 1092064.7445 | 1028066.8139 | 63997.9306 | 6.2251 | OK
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | 11 |  |  | 1 | 3813.87 | 4695.65 | 881.78 | 1000 |  | 881780 | 896344.5253 | Moghbazar |  |  |  | Wireless | 896344.5253 | 608635.6217 | 287708.9036 | 47.2711 | FAULT
2 | Kazir Goli | 11 |  |  | 1 | 2485.21 | 3648.07 | 1162.86 | 1000 |  | 1162860 | 1182067.1763 | Kakrail |  |  |  | Kazir Goli | 1182067.1763 | 1168270.1069 | 13797.0694 | 1.181 | OK
3 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 5601141.8485 | 5510130 | 5601141.8485 | 1.6517
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 2794517.5644
[5 empty] | Kakrail | at 33 KV level |  | 2806624.2841
[5 empty] | Total = |  |  | 5601141.8485 | 0

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 | 132 | IMPORT | 8993683 | 1 | 8225.403 | 8261.732 | 36.329 | 960000 | 0 | 34875840
| XFR- T2 | 132 |  | 8993682 | 1 | 8216.58 | 8252.57 | 35.99 | 960000 | 0 | 34550400
[9 empty] | Total | 0 | 69426240
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** | 132 | P. Cell | 08993685 | 1 | 8225.286 | 8261.725 | 36.439 | 960000 | 34981440
| 132/33 kV Transformer-2(HV) ** | 132 | P. Cell | 08993684 | 1 | 8216.565 | 8252.56 | 35.995 | 960000 | 34555200
[9 empty] | Total | 69536640
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SIDDHIRGANJ 132 KV SIDE (TARIFF POINT) |  | 69426240 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 69426240
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 69426240 |  | 33 KV NET IMPORT |  | 69599520
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 69426240 |  | LOSS UNITS=>(132 HV-33 LV) |  | -173280
| IMPORT-4 |  |  |  | Loss Units=> (132 IMP-132 EXP) |  |  | 0 |  | LOSS % IN => |  | -0.2496%
| 132 KV TOTAL IMPORT |  | 69426240 |  | 132 KV NET LOSS => |  |  | 0%
| 33 KV GT INCOMING-NOCS |  | 69599520
| Loss Units=> (132 IMP-33 IMP) |  | -173280
| LOSS % IN => |  | -0.2496%
33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | IMPORT
3 | 132/33 kV Transformer, T-1 (LV) | 33 | PGCB | J2002016494 | 1 | 21118.972 | 21360.979 | 242.007 | 144000 | 34849008
4 | 132/33 kV Transformer, T-2 (LV) | 33 | PGCB | J2002016859 | 1 | 31100.838 | 31340.717 | 239.879 | 144000 | 34542576
| DPDC | [5 empty] | 0 |  | Total | 69391584
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | DPDC | 07389553 | 1 | 1380.37 | 1453.21 | 72.84 | 480000 | 34963200
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | DPDC | 07389485 | 1.038 | 787.62 | 854.94 | 67.32 | 480000 | 33541516.8
| P.Cell | [5 empty] | 0 |  | Total | 68504716.8
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | P.Cell | 08993674 | 1 | 10645.601 | 10718.396 | 72.795 | 480000 | 34941600
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | P.Cell | 8993667 | 1 | 10556.347 | 10628.551 | 72.204 | 480000 | 34657920
[9 empty] | Total | 69599520
MOGBAZAR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 33 | DPDC | 07389555 | 1 | 5551.58 | 5578.69 | 27.11 | 240000 |  | 6506400 | 6486018.3466 |  | 14122820.4721 | Siddhirganj 33/11 kv ss | 0.73479 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 6486018.3466 | 6339867.5438 | 146150.8028 | 2.3053 | OK
|  | 33 | P.Cell | 08993675 | 1 | 4908.212 | 4935.315 | 27.103 | 240000 |  | 6504720 | 6484343.6093 |  |  |  |  | 0 | 6484343.6093 | 6330530.1256 | 153813.4837 | 2.4297 | OK
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 33 | DPDC | 07389487 | 1 | 5712.38 | 5744.3 | 31.92 | 240000 |  | 7660800 | 7636802.1255 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 7636802.1255 | 7280791.9942 | 356010.1313 | 4.8897 | OK
|  | 33 | P.Cell | 08993666 | 1 | 4976.55 | 5008.477 | 31.927 | 240000 |  | 7662480 | 7638476.8628 |  |  |  |  | 0 | 7638476.8628 | 7276003.5746 | 362473.2882 | 4.9818 | OK
| 33 KV Feeders | [5 empty] | 0 |  | Total |  | 14167200 | 14122820.4721 |  |  |  |  | 33 KV Feeders | 14122820.4721 | 13620659.538 | 502160.934 | 3.6868 | OK
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4113.802 | 4155.568 | 41.766 | 240000 |  | 10023840 | 9992439.7736 |  | 18155587.9103 | Sarulia 33/11 kv ss |  | 33 kV Sarulia-1 Feeder | 9992439.7736 | 9478916.0093 | 513523.7643 | 5.4175 | OK
|  | 33 | P.Cell | 08993679 | 1 | 4114.608 | 4156.359 | 41.751 | 240000 |  | 10020240 | 9988851.0508 |  |  |  |  | 0 | 9988851.0508 | 9475324.6946 | 513526.3562 | 5.4196 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss |  | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 5996.37 | 6047.67 | 51.3 | 240000 |  | 12312000 | 12273431.9874 |  |  |  |  | 33 kV Demra-1 Feeder | 12273431.9874 | 10979846.1314 | 1293585.856 | 11.7815 | OK
|  | 33 | P.Cell | 08993676 | 1 | 5641.918 | 5693.208 | 51.29 | 240000 |  | 12309600 | 12271039.5055 |  |  |  |  | 0 | 12271039.5055 | 10969551.0292 | 1301488.4763 | 11.8646 | OK
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5480.21 | 5523.57 | 43.36 | 240000 |  | 10406400 | 10373801.3835 |  | 22647233.3709 | Demra 33/11 kv ss |  | 33 kV Demra-2 Feeder | 10373801.3835 | 9782741.2326 | 591060.1509 | 6.0419 | OK
|  | 33 | P.Cell | 08993665 | 1 | 5188.438 | 5231.773 | 43.335 | 240000 |  | 10400400 | 10367820.1788 |  |  |  |  | 0 | 10367820.1788 | 9773882.6564 | 593937.5225 | 6.0768 | OK
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 356737.2598 | -356737.2598 | -100 | CHECK
|  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 358413.2067 | -358413.2067 | -100 | CHECK
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4446.37 | 4469.84 | 23.47 | 240000 |  | 5632800 | 5615154.9463 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 5615154.9463 | 3335134.2479 | 2280020.6984 | 68.3637 | FAULT
|  | 33 | P.Cell | 08993678 | 1 | 3692.046 | 3715.504 | 23.458 | 240000 |  | 5629920 | 5612283.968 |  |  |  |  | 0 | 5612283.968 | 3329388.1444 | 2282895.8236 | 68.568 | FAULT
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3852.28 | 3886.4 | 34.12 | 240000 |  | 8188800 | 8163148.1367 |  |  |  |  | 33 kV Sarulia-2 Feeder | 8163148.1367 | 7613587.1561 | 549560.9806 | 7.2182 | OK
|  | 33 | P.Cell | 08993663 | 1 | 3574.124 | 3608.278 | 34.154 | 240000 |  | 8196960 | 8171282.575 |  |  |  |  | 0 | 8171282.575 | 7592996.9518 | 578285.6232 | 7.616 | OK
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 349307.2 | 353746.5 | 4439.3 | 2000 |  | 8878600 | 8850787.3005 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 8850787.3005 | 6327098.4249 | 2523688.8756 | 39.887 | OK
[9 empty] | Total | 69391584 | 69609640 | 69391584 | -0.31326
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 14465942.2468
[5 empty] | Total = |  |  | 14465942.2468 | 0
11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | 2023-01-01 | 2023-01-01 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 8 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*11 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | IMPORT
8 | 33/11 kV Transformer-1 Incoming | 11 | New | XA587379 | 1 | 659329.6 | 665827.4 | 6497.8 | 1000 | 6497800 |  | 6500571.1538
9 | 33/11 kV Transformer-2 Incoming | 11 | New | DHKA9985 | 1 | 285352.1 | 292971.1 | 7619 | 1000 | 7619000 |  | 7622249.3183
[9 empty] | Total | 14116800 |  | 14122820.4721
| SIDDHIRGANJ 11 kV SIDE |  | EXPORT
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 205402.5 | 207823.5 | 2421 | 1000 |  | 2421000 | 2438789.3271 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 2438789.3271 | 2368144.719 | 70644.608 | 2.9831 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16450 | 16587.7 | 137.7 | 1000 |  | 137700 | 138711.8093 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 138711.8093 | 138785.7046 | -73.8953 | -0.053244 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 103711.2 | 105223.6 | 1512.4 | 1000 |  | 1512400 | 1523513.0022 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1523513.0022 | 1380887.4581 | 142625.5441 | 10.3285 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 162380.7 | 164769.1 | 2388.4 | 1000 |  | 2388400 | 2405949.7847 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2405949.7847 | 2407336.0243 | -1386.2396 | -0.057584 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6871.1 | 6907.4 | 36.3 | 1000 |  | 36300 | 36566.7297 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 36566.7297 | 79796.7297 | -43230 | -54.1752 | CHECK
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 70624.1 | 71952.3 | 1328.2 | 1000 |  | 1328200 | 1337959.5143 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1337959.5143 | 1303716.9498 | 34242.5645 | 2.6265 | OK
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj | Check if Zero |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 202.017 | -202.017 | -100 | CHECK
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 139518 | 141739.7 | 2221.7 | 1000 |  | 2221700 | 2238024.8856 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 2238024.8856 | 2245520.3774 | -7495.4919 | -0.3338 | OK
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 53.7495 | 64.2821 | 10.5326 | 40000 |  | 421304 | 424399.7103 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 424399.7103 | 994247.0505 | -569847.3402 | -57.3145 | CHECK
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 12120.8 | 12873.4 | 752.6 | 1000 |  | 752600 | 758130.0486 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 758130.0486 | 442720.3371 | 315409.7114 | 71.2436 | FAULT
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 137987.5 | 140787.7 | 2800.2 | 1000 |  | 2800200 | 2820775.6603 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2820775.6603 | 2249964.7523 | 570810.9081 | 25.3698 | OK
[9 empty] | Total | 14122820.4721 | 14019804 | 14122820.4721 | 0.73479
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 13698420.7618
[5 empty] | Matuail | at 33 KV level |  | 424399.7103
[5 empty] | Total = |  |  | 14122820.4721 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
33 KV SIDE of___ DEMRA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 5996.37 | 6047.67 | 51.3 | 240000 | 0 | 12312000 | 12273431.9874
0 | 0 | 33 | P.Cell | 08993676 | 1 | 5641.918 | 5693.208 | 51.29 | 240000 | 0 | 12309600 | 12271039.5055
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5480.21 | 5523.57 | 43.36 | 240000 | 0 | 10406400 | 10373801.3835
0 | 0 | 33 | P.Cell | 08993665 | 1 | 5188.438 | 5231.773 | 43.335 | 240000 | 0 | 10400400 | 10367820.1788
[9 empty] | Total | 0 | 22718400 | 22647233.3709
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 | 33 | Digital | DHK60885 | 3 | 251090.3 | 270310.8 | 19220.5 | 240 | 13838760
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
[9 empty] | Total | 13838760 | 0 | 0
DEMRA 33 KV SIDE (EXPORT TO OTHER S/S)
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1004.15 | 1006.87 | 2.72 | 240000 |  | 652800 |  | Siddirgonj
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 652800
DEMRA 33 KV SIDE
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60886 | 1 | 605727.3 | 645996.4 | 40269.1 | 240 |  | 9664584
8 | 33/11 kV, 10/14 MVA T-2 (HV) | 33 | Digital | 05002303 | 1 |  |  |  | 240 |  | 0
9 | 33/11 kV, 20/28 MVA T-3 (HV) | 33 |  |  | 1 |  |  |  | 180 |  | 0
[9 empty] | Total |  | 9664584 | 0
[5 empty] | 33 KV Export-Import |  |  | KWH
[5 empty] | Total Import |  |  | 22647233.3709
[5 empty] | Siddirgonj NOCS |  |  | 652800
[5 empty] | Net Import to Demra 33/11 KV SS |  |  | 21994433.3709
11 KV SIDE of___DEMRA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK60881 | 1 | 113110.2 | 166670.6 | 53560.4 | 180 | 9640872 |  | 10013826.885
19 | 33/11 kV, 20/28 MVA T-3 Incoming. | 11 |  | DHK60925 | 1 | 521779.2 | 589350.8 | 67571.6 | 180 | 12162888 |  | 12633406.4859
[9 empty] | Total | 21803760 |  | 22647233.3709
DEMRA 11 KV SIDE
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 |  | HA021101013-02 | 1 | 39314770 | 41495960 | 2181190 | 1 |  | 2181190 | 2206583.7096 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2206583.7096 | 1874567.7976 | 332015.912 | 17.7116 | OK
12 | 11 kV DND (WASA) Feeder. | 11 |  | HA021100992-02 | 1 | 5281672 | 5288520 | 6848 | 1 |  | 6848 | 6927.7253 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 6927.7253 | 7010.5473 | -82.8219 | -1.1814 | OK
13 | 11 kV Local Feeder | 11 |  | HA021100794-02 | 1 | 5234750 | 6636120 | 1401370 | 1 |  | 1401370 | 1417684.9395 | Siddirgonj |  |  |  | 11 kV Local Feeder | 1417684.9395 | 1373452.6221 | 44232.3174 | 3.2205 | OK
14 | 11 kV Mouchak Feeder | 11 |  | DHK60888 | 1 | 783539.3 | 817710.4 | 34171.1 | 60 |  | 2050266 | 2074135.4747 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2074135.4747 | 2006300.5649 | 67834.9097 | 3.3811 | OK
15 | 11 kV Overhead-1 Feeder | 11 |  | HA021100829-02 | 1 | 74811660 | 75894360 | 1082700 | 1 |  | 1082700 | 1095304.9401 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 1095304.9401 | 1131426.4606 | -36121.5204 | -3.1926 | OK
16 | 11 kV Provati Steel Feeder | 11 |  | DHK60874 | 1 | 544937.6 | 544937.6 | 0 | 60 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 0 | 36.5133 | -36.5133 | -100 | CHECK
17 | 11 kV Islambagh Feeder. | 11 |  | DHKA2190 | 1 | 901.5142 | 950.6676 | 49.1534 | 60000 |  | 2949204 | 2983539.0327 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 2983539.0327 | 2737156.2019 | 246382.8308 | 9.0014 | OK
20 | 11 kV Taj Jute Feeder. | 11 |  | DHK61062 | 1 | 535795.2 | 563396.8 | 27601.6 | 60 |  | 1656096 | 1675376.4941 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1675376.4941 | 1383073.8679 | 292302.6262 | 21.1343 | OK
21 | 11 kV Al-Aksa Steel Feeder | 11 |  | DHK61061 | 1 | 682450.7 | 708770.6 | 26319.9 | 60 |  | 1579194 | 1597579.1906 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1597579.1906 | 1240696.469 | 356882.7216 | 28.7647 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 |  | DHKA2189 | 1 | 866.1985 | 905.2486 | 39.0501 | 60000 |  | 2343006 | 2370283.5934 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2370283.5934 | 2259751.322 | 110532.2715 | 4.8913 | OK
23 | 11 kV Over Head Feeder-2. | 11 |  | HA021100488-02 | 1 | 20655375 | 22702980 | 2047605 | 1 |  | 2047605 | 2071443.4949 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 2071443.4949 | 1899440.4322 | 172003.0628 | 9.0555 | OK
24 | 11 kV Shimrail Express Feeder. | 11 |  | HA021100511-02 | 1 | 8067222 | 8067222 | 0 | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Sarder & Khadem Steel Feeder | 11 |  | HA021100413-02 | 1 | 79362440 | 79767340 | 404900 | 1 |  | 404900 | 409613.9007 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 409613.9007 | 305911.1933 | 103702.7074 | 33.8996 | OK
26 | 11 kV Siddhirgonj Mazar Feeder | 11 |  | HA021100393-02 | 1 | 45953012 | 46776260 | 823248 | 1 |  | 823248 | 832832.3648 | Siddirgonj |  |  |  | 11 kV Siddhirgonj Mazar Feeder | 832832.3648 | 837817.1954 | -4984.8306 | -0.59498 | OK
27 | 11 kV AST Beverage Feeder | 11 |  |  | 1 | 18048062 | 19198420 | 1150358 | 1 |  | 1150358 | 1163750.6238 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 1163750.6238 | 1048864.8927 | 114885.7311 | 10.9533 | OK
28 | 11 kV Karim Market Feeder | 11 |  |  | 1 | 50590947 | 52656280 | 2065333 | 1 |  | 2065333 | 2089377.8867 | Matuail |  |  |  | 11 kV Karim Market Feeder | 2089377.8867 | 1985822.7077 | 103555.179 | 5.2147 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 21994433.3709 | 21741318 | 21994433.3709 | 1.1642
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 7279500.629
[5 empty] | Demra | at 33 KV level |  | 2481057.3956
[5 empty] | Siddirgonj | at 33 KV level |  | 12233875.3463
[5 empty] | Total = |  |  | 21994433.3709 | 0
33 KV SIDE of___ SARULIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4113.802 | 4155.568 | 41.766 | 240000 | 0 | 10023840 | 9992439.7736
0 | 0 | 33 | P.Cell | 08993679 | 1 | 4114.608 | 4156.359 | 41.751 | 240000 | 0 | 10020240 | 9988851.0508
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3852.28 | 3886.4 | 34.12 | 240000 | 0 | 8188800 | 8163148.1367
| 0 | 33 | P.Cell | 08993663 | 1 | 3574.124 | 3608.278 | 34.154 | 240000 | 0 | 8196960 | 8171282.575
[9 empty] | Total | 0 | 18212640 | 18155587.9103
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) | 33 |  | 30799103 | 1 | 4228.47 | 4262.36 | 33.89 | 240000 | 8133600
7 | 33 kV Siddhirgonj-1 Incoming (=L41) | 33 |  | 30799100 | 1 | 4136.31 | 4177.23 | 40.92 | 240000 | 9820800
[9 empty] | Total | 17954400 | 0 | 0
SARULIA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
SARULIA 33 KV SIDE
4 | 33/11 kV Transformer-1 (=T31) | 33 |  | 30799099 | 1 | 4506.65 | 4551.82 | 45.17 | 180000 |  | 8130600
5 | 33/11 kV Transformer-2 (=T32) | 33 |  | 30799139 | 1 | 3939.3 | 3966.18 | 26.88 | 180000 |  | 4838400
6 | 33/11 kV Transformer-3 (=T33) | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 12969000 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Siddhirgonj 33 KV SIDE |  | 18155587.9103 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 18155587.9103
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 18155587.9103 |  | 33 KV NET Receiving |  | 17954400
| IMPORT-3 |  |  |  | TOTAL EXPORT |  |  | 18155587.9103 |  | LOSS UNITS=> |  | 201187.9103
| IMPORT-4 |  |  |  | 132KV NET LOSS => |  |  | 0% |  | LOSS % IN => |  | 1.108%
| TOTAL IMPORT |  | 18155587.9103
11 KV SIDE of___SARULIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) | 11 |  | 2007754972 | 1 | 9145.73 | 9196.41 | 50.68 | 160000 | 8108800 |  | 8719798.11
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) | 11 |  | 30799500 | 1 | 8675.73 | 8722.01 | 46.28 | 80000 | 3702400 |  | 3981375.8537
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) | 11 |  | HA021100368-02 | 1 | 27986358 | 33058580 | 5072222 | 1 | 5072222 |  | 5454413.9465
[9 empty] | Total | 16883422 |  | 18155587.9103
SARULIA 11 KV SIDE
8 | 11 kV Dayagonj Feeder (=L11) | 11 |  | 2007755114 | 1 | 5629.39 | 5681.21 | 51.82 | 60000 |  | 3109200 | 3036942.6611 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 3036942.6611 | 2683493.1554 | 353449.5058 | 13.1712 | OK
9 | 11 kV Karim Jute Feeder (=L12) | 11 |  | 30799484 | 1 | 20.6815 | 20.9002 | 0.2187 | 60000 |  | 13122 | 12817.0467 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 12817.0467 | 13119.435 | -302.3883 | -2.3049 | OK
11 | 11 kV Konapara (=L13) **** | 11 |  | DHKA2191 | 1 | 1907.6395 | 1949.7345 | 42.095 | 60000 |  | 2525700 | 2467003.1131 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 2467003.1131 | 2507825.3192 | -40822.2061 | -1.6278 | OK
12 | 11 kV Sanarpar Feeder (=L14) | 11 |  | 575926 | 1 | 43544.5 | 45987.8 | 2443.3 | 1000 |  | 2443300 | 2386518.0767 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2386518.0767 | 2429660.1673 | -43142.0906 | -1.7756 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | 11 |  | 30799450 | 1 | 1794.98 | 1800.14 | 5.16 | 60000 |  | 309600 | 302404.9427 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 302404.9427 | 216528.4595 | 85876.4832 | 39.6606 | OK
14 | 11 kV Tengra Feeder (=L16) | 11 |  | 30799145 | 1 | 5334.41 | 5390.98 | 56.57 | 60000 |  | 3394200 | 3315319.3041 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 3315319.3041 | 2716337.3599 | 598981.9442 | 22.0511 | OK
16 | 11 kV Police Line Feeder (=L17) | 11 |  | 30799480 | 1 | 3256.34 | 3276.53 | 20.19 | 60000 |  | 1211400 | 1183247.2468 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1183247.2468 | 1128867.4742 | 54379.7725 | 4.8172 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | 11 |  | 30799119 | 1 | 1613.27 | 1621.73 | 8.46 | 60000 |  | 507600 | 495803.4526 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 495803.4526 | 382574.1602 | 113229.2924 | 29.5967 | OK
18 | 11 kV Spare Feeder (=F9) | 11 |  | HA021100859-02 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | 11 |  | HA021100493-02 | 1 | 71888660 | 74707530 | 2818870 | 1 |  | 2818870 | 2753359.8865 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 2753359.8865 | 2630234.8585 | 123125.028 | 4.6811 | OK
21 | 11 kV Baser Pool Feeder (=L11) | 11 |  | HA021100518-02 | 1 | 50684128 | 50715102 | 30974 | 1 |  | 30974 | 30254.1689 | Demra |  |  |  | 11 kV Baser Pool Feeder (=L11) | 30254.1689 | 0 | 30254.1689 | #DIV/0! | #DIV/0!
22 | 11 kV Dip-Pur Feeder (=L12) | 11 |  | HA021100697-02 | 1 | 16036849 | 18260443 | 2223594 | 1 |  | 2223594 | 2171918.011 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 2171918.011 | 2383862.7761 | -211944.7652 | -8.8908 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 |  | 05395814 | 1 |  | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 18155587.9103 | 18587560 | 18155587.9103 | -2.324
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Demra | at 33 KV level |  | 15769069.8336
[5 empty] | Matuail | at 33 KV level |  | 2386518.0767
[5 empty] | Total = |  |  | 18155587.9103 | 0
33 KV SIDE of___ KHANPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 83681.645 | 92642.466 | 8960.821 | 1000 | 0 | 8960821 | 8963101.6544
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 299.8501 | 335.3629 | 35.5128 | 240000 | 0 | 8523072 | 8525241.2411
| Siddhirganj 33 KV SIDE | [7 empty] | Total |  | 17483893 | 17488342.8955
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
[9 empty] | Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) | 33 |  | 84663042 | 1 | 307.19 | 342.79 | 35.6 | 240000 | 8544000
6 | 33 kV Shitalakhya-2 Feeder (Old) | 33 |  | 05323185 | 1 |  | 0 | 0 | 240000 | 8523072 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
[9 empty] | Total | 17067072 | 0 | 0
KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
11 | 33 kV ACI Pharmacuticles Feeder | 33 |  | DHKC4791 | 1 | 861.45 | 874.23 | 12.78 | 90000 |  | 1150200 |  | N.Gonj (East)
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 1150200
KHANPUR 33 KV SIDE
9 | 33/11 kV, 20/28 MVA T1 Transformer | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer | 33 |  | DHKC 9361 | 1 | 40559.36 | 40559.36 | 0 | 240 |  | 0 |  |  | Meter Problem
[9 empty] | Total |  | 15916872 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV EXPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 17488342.8955 |  | EXPORT TO N.Gonj (East) |  |  | 1150200 |  | 33 KV NET IMPORT |  | 16338142.8955
| SIDDIRGANJ 33 KV SIDE |  | 0 |  | 33 KV NET IMPORT |  |  | 16338142.8955 |  | 33 KV TX HV SIDE |  | 15916872
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 421270.8955
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 2.578%
| TOTAL IMPORT |  | 17488342.8955
11 KV SIDE of___KHANPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. | 11 |  | DHKC 9313 | 1 | 8298474.9 | 12703062.9 | 4404588 | 1 | 4404588 |  | 1446342.1334
18 | 33/11 kV Transformer-2 Incoming. | 11 |  | DHKC 9346 | 1 | 3708585.71 | 40577422.11 | 36868836.4 | 1 | 36868836.4 |  | 12106683.1895
24 | 33/11 kV 20/28 MVA T4 Incoming | 11 |  | 06604325 | 1 | 49.98 | 74.01 | 24.03 | 240000 | 5767200 |  | 1893785.3783
30 | 33/11 kV 20/28 MVA T1 Incoming | 11 |  | 06604374 | 1 | 30.91 | 42.22 | 11.31 | 240000 | 2714400 |  | 891332.1943
[9 empty] | Total | 49755024.4 |  | 16338142.8955
KHANPUR 11 KV SIDE
12 | 11 kV Khanpur Feeder | 11 |  | DHKC 9348 | 1 | 58257.88 | 86157.18 | 27899.3 | 60 |  | 1673958 | 1689432.0922 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1689432.0922 | 1886405.6884 | -196973.5962 | -10.4417 | OK
13 | 11 kV Mission Para Feeder. | 11 |  | DHKC 9347 | 1 | 50276.86 | 76552.26 | 26275.4 | 60 |  | 1576524 | 1591097.4109 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1591097.4109 | 1544120.6583 | 46976.7526 | 3.0423 | OK
14 | 11 kV Esha Kha Feeder | 11 |  | DHKC 9311 | 1 | 32200.54 | 49376.9 | 17176.36 | 60 |  | 1030581.6 | 1040108.3114 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 1040108.3114 | 965969.3599 | 74138.9515 | 7.6751 | OK
15 | 11 kV New Hazigonj Feeder | 11 |  | DHKC 9314 | 1 | 65.15 | 100.41 | 35.26 | 60000 |  | 2115600 | 2135156.6373 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 2135156.6373 | 1776958.076 | 358198.5613 | 20.158 | OK
16 | 11 kV Spare Feeder. | 11 |  | DHKC 9345 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | 11 |  | 6604412 | 1 | 1.83 | 2.82 | 0.99 | 60000 |  | 59400 | 59949.0945 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 59949.0945 | 53478.9024 | 6470.192 | 12.0986 | OK
20 | 11 kV Old Hajiganj Feeder. | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | 11 |  | 06604389 | 1 | 42144.69 | 62961.9 | 20817.21 | 60 |  | 1249032.6 | 1260578.6756 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 1260578.6756 | 1227521.302 | 33057.3737 | 2.693 | OK
22 | 11 kV Spare Feeder. | 11 |  | 8576983 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | 11 |  | 6604415 | 1 | 95.99 | 140.58 | 44.59 | 40000 |  | 1783600 | 1800087.6245 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1800087.6245 | 1753864.9136 | 46222.7108 | 2.6355 | OK
26 | 11 kV Mondalpara Feeder. | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | 11 |  | 06604392 | 1 | 75.1 | 109.7 | 34.6 | 40000 |  | 1384000 | 1396793.7162 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1396793.7162 | 1400580.0431 | -3786.3268 | -0.27034 | OK
28 | 11 kV Bishaw Road Feeder. | 11 |  | 06604393 | 1 | 98.4 | 147.19 | 48.79 | 40000 |  | 1951600 | 1969640.6189 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 1969640.6189 | 1775337.5032 | 194303.1157 | 10.9446 | OK
29 | 11 kV Chasara Feeder. | 11 |  | 06604391 | 1 | 101.54 | 152.29 | 50.75 | 40000 |  | 2030000 | 2048765.3497 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 2048765.3497 | 1952790.2249 | 95975.1248 | 4.9148 | OK
31 | 11 kV Pathan Tully Feeder. | 11 |  | 06604388 | 1 | 32.71 | 32.71 | 0 | 40000 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 0 | 257265.9321 | -257265.9321 | -100 | CHECK
32 | 11 kV Spare Feeder. | 11 |  | 9120051 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | 11 |  | 6604289 | 1 | 73.9 | 107.18 | 33.28 | 40000 |  | 1331200 | 1343505.6323 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1343505.6323 | 1084568.3469 | 258937.2853 | 23.8747 | OK
34 | 11 kV Spare Feeder. | 11 |  | DHKC9310 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. | 11 |  | DHKC9349 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. | 11 |  | DHKC9312 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 |  | 412109 | 1 | 9109.5 | 9109.5 | 0 | 10 |  | 0 | 0 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 |  | 243285 | 1 | 6352.2 | 6388.1 | 35.9 | 10 |  | 3000 | 3027.732 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3027.732 | 3038.574 | -10.842 | -0.35681 | OK
[9 empty] | Grand Total | 16338142.8955 | 16188496.2 | 16338142.8955 | 0.9244
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3848852.9741
[5 empty] | N.Gonj (East) | at 33 KV level |  | 12489289.9214
[5 empty] | Total = |  |  | 16338142.8955 | 0
132 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail | 132 | Impt | 8993555 | 1 | 2698.916 | 2725.888 | 26.972 | 1440000 | 0 | 38839680
|  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar | 132 | Impt |  | 1 |  |  | 0 |  | 0 | 0
|  | 132 | Expt |  | 1 |  |  | 0 |  | 0
[8 empty] | Total Import/Export |  | 0 | 38839680
[9 empty] | Net Total | 38839680
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder | 132 | Impt |  | 1 |  |  | 0 | 1 | 0
|  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  | 132 | Expt |  | 1 | 8832554 | 8832554 | 0 | 1 | 0
|  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder | 132 | Impt | HA040700237-03 | 1 | 35292309 | 35292309 | 0 | 1
|  | 132 |  | 06604364 | 1 | 5968.09 | 6008.61 | 40.52 | 960000 | 38899200
|  | 132 | Expt | HA040700237-04 | 1 |  |  | 0 | 1 |  | 0
|  | 132 |  | 06604364 | 1 |  |  | 0 | 960000 |  | 0
[8 empty] | Total Import/Export |  | 38899200 | 0
[8 empty] | Net Total |  | 38899200
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
MOGBAZAR 132 KV SIDE
4 | 132/33 KV Transformer, GT-1 | 132 | DPDC | H/A040700240-03 | 1 | 79653.279 | 99094.673 | 19441.394 | 1000 |  | 19441394
|  | 132 | P. Cell | 08993572 | 1 | 4827.591 | 4868.146 | 40.555 | 480000 |  | 19466400
5 | 132/33 KV Transformer, GT-2 | 132 | DPDC | H/A030700918-03 | 1 | 40453.111 | 59813.966 | 19360.855 | 1000 |  | 19360855
|  | 132 | P. Cell | 08993577 | 1 | 4889.425 | 4919.775 | 30.35 | 480000 |  | 14568000
[9 empty] | Total |  | 38802249
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV Sending From Tariff |  | 38839680 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 38839680
| 132 KV Sending From Maniknagar |  | 0 |  | 132 KV NET IMPORT |  |  | 38839680 |  | 132/33 KV GT LV Side |  | 38877315
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -37635
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.0969%
| 132 KV TOTAL IMPORT |  | 38839680
33 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| MATUAIL 33 KV SIDE |  | IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 70864.865 | 90418.204 | 19553.339 | 1000 | 19553339
|  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 92156.368 | 111480.344 | 19323.976 | 1000 | 19323976
|  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
[9 empty] | Total | 38877315 |  | 0
MATUAIL 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 | 33 | DPDC | H/A060300287-03 | 1.36 | 37057.117 | 43922.238 | 6865.121 | 1000 |  | 9336564.56 | 9361396.9663 |  | 17115305.2855 | Matuail 33/11 kv ss | 1.0876 | 33/11 KV Transformer, T-3 | 9361396.9663 | 7582741.0664 | 1778655.8999 | 23.4566 | OK
|  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 | 33 | DPDC | H/A060300190-03 | 1 | 30102.816 | 37839.029 | 7736.213 | 1000 |  | 7736213 | 7756788.9606 |  |  |  |  | 33/11 KV Transformer, T-4 | 7756788.9606 | 7094966.3752 | 661822.5854 | 9.3281 | OK
|  | 33 | P. Cell | 08993581 | 1 | 6071.423 | 6114.386 | 42.963 | 180000 |  | 7733340 | 7753908.3193 |  |  |  |  | 0 | 7753908.3193 | 7077363.6368 | 676544.6824 | 9.5593 | OK
| 33 KV Feeders | [7 empty] | Total |  | 17069904.56 | 17115305.2855 |  |  |  |  | 33 KV Feeders | 17115305.2855 | 14660104.7032 | 2455200.5823 | 16.7475 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 8701920 | 15989040 | 7287120 | 1 |  | 7287120 | 7306501.5105 |  | 16588643.6824 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 7306501.5105 | 6891698.7318 | 414802.7787 | 6.0189 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC |  | 1 | 9901.453 | 9902.221 | 0.768 | 1000 | From Customer End | 10962.5847 | 10991.7418 | Matuail |  |  |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 10991.7418 | 10971.1473 | 20.5945 | 0.18772 | OK
|  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 0 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 50282.605 | 55353.737 | 5071.132 | 1000 |  | 5071132 | 5084619.6602 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 5084619.6602 | 3860914.3097 | 1223705.3505 | 31.6947 | OK
|  | 33 | P. Cell | 08993580 | 1.5 | 1294.23 | 1313.084 | 18.854 | 180000 |  | 5090580 | 5104119.3859 |  |  |  |  | 0 | 5104119.3859 | 3870500.7916 | 1233618.5943 | 31.8723 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 5084619.6602 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 | DPDC | 00000154 | 1 | 3564720 | 12822240 | 9257520 | 1 |  | 9257520 | 9282142.1719 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 9282142.1719 | 7956930.108 | 1325212.064 | 16.6548 | OK
[9 empty] | Total |  | 21626734.5847 | 21684255.0845 |  |  |  |  | 0 | 21684255.0845 | 18720514.2968 | 2963740.7877 | 15.8315 | OK
[8 empty] | Grand Total |  | 38799560.37 | 38696639.1447 | 38799560.37 | 0.26597
[5 empty] | 33 KV EXPORT |  |  | KWH
[5 empty] | EXPORT TO Matuail |  |  | 10991.7418
[5 empty] | Total Export |  |  | 10991.7418 | 0
11 KV SIDE of___ MATUAIL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426631 | 1 | 7208025 | 7311696 | 103671 | 90 | 9330390 |  | 9383882.5416
11 | 33/11 kV Transformer, T-4 Incoming | 11 |  | 51426633 | 1 | 6941059 | 7026474 | 85415 | 90 | 7687350 |  | 7731422.744
[9 empty] | Total | 17017740 |  | 17115305.2855
MATUAIL 11 kV SIDE
3 | 11 kV Link Road Feeder | 11 | Backup | DHK66629 | 1 | 22776.54 | 23009.26 | 232.72 | 8000 |  | 1861760 | 1882008.2759 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 1882008.2759 | 1663538.7529 | 218469.5229 | 13.1328 | OK
|  | 11 |  | HA021100475-02 | 1 | 81796.404 | 83653.744 | 1857.34 | 1000 |  | 1857340 | 1877540.2045 | N.Gonj (East) |  |  |  | 0 | 1877540.2045 | 1660117.0339 | 217423.1706 | 13.0969 | OK
4 | 11 kV Lamapara Express Feeder | 11 |  | HA021100928-03 | 1 | 74511.135 | 75563.19 | 1052.055 | 1000 |  | 1052055 | 1063497.0225 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 1063497.0225 | 716155.9388 | 347341.0837 | 48.5008 | FAULT
5 | 11 kV Kutubpur Feeder*** | 11 |  | DHK66616 | 1 | 17105.28 | 17315.9 | 210.62 | 8000 |  | 1684960 | 1703285.4205 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1703285.4205 | 1545976.2088 | 157309.2117 | 10.1754 | OK
|  | 11 | Backup | XA575929 | 1 | 35760.1 | 37443.2 | 1683.1 | 1000 |  | 1683100 | 1701405.1914 | N.Gonj (East) |  |  |  | 0 | 1701405.1914 | 1544189.3568 | 157215.8346 | 10.1811 | OK
6 | 11 kV Ramarbagh Feeder (F1) | 11 |  | DHK66625 | 1 | 3450.14 | 3463.92 | 13.78 | 60000 |  | 826800 | 835792.1765 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 835792.1765 | 43130.9124 | 792661.2641 | 1837.8031 | FAULT
|  | 11 | Backup |  | 1 | 7567.015 | 8395.82 | 828.805 | 1000 |  | 828805 | 837818.9826 | Fatullah |  |  |  | 0 | 837818.9826 | 43076.4853 | 794742.4973 | 1844.9567 | FAULT
7 | 11 kV Tushardhara Feeder (F2) | 11 |  | DHK66623 | 1 | 3656.03 | 3701.54 | 45.51 | 60000 |  | 2730600 | 2760297.6743 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2760297.6743 | 2583541.6531 | 176756.0212 | 6.8416 | OK
8 | 11 kV Matuail Medical Feeder (F3) | 11 |  | DHK66627 | 1 | 3247.29 | 3258.78 | 11.49 | 60000 |  | 689400 | 696897.8308 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 696897.8308 | 691943.0662 | 4954.7646 | 0.71607 | OK
|  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | 11 |  | HA021101044-02 | 1 | 64530.881 | 64851.309 | 320.428 | 1000 |  | 320428 | 323912.9361 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 323912.9361 | 351622.7095 | -27709.7735 | -7.8805 | OK
12 | 11 kV Shibu Market Feeder (F7) | 11 |  | DHK66624 | 1 | 2345.91 | 2356.06 | 10.15 | 60000 |  | 609000 | 615623.4101 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 615623.4101 | 1052394.2627 | -436770.8526 | -41.5026 | CHECK
13 | 11 kV Soma-Sagar Steel (F6) | 11 |  | HA060300286-03 | 1 | 73922.771 | 75021.472 | 1098.701 | 1000 |  | 1098701 | 1110650.3388 | Fatullah |  |  |  | 11 kV Soma-Sagar Steel (F6) | 1110650.3388 | 891121.6196 | 219528.7191 | 24.6351 | OK
14 | 11 kV Jhalkuri Feeder (F8) | 11 |  | DHK66626 | 1 | 4246.65 | 4291.01 | 44.36 | 60000 |  | 2661600 | 2690547.2387 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2690547.2387 | 1754811.979 | 935735.2597 | 53.324 | FAULT
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK6622 | 1 | 4122.31 | 4144.98 | 22.67 | 60000 |  | 1360200 | 1374993.3702 | Matuail |  |  |  | 0 | 1374993.3702 | 1224917.9123 | 150075.4579 | 12.2519 | OK
16 | 11 kV Rajmahal Feeder (F10) | 11 |  | DHKA2187 | 1 | 100.8649 | 104.4696 | 3.6047 | 60000 |  | 216282 | 218634.2568 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 218634.2568 | 199307.9462 | 19326.3106 | 9.6967 | OK
17 | 11 kV Bhuighor Bazar | 11 |  | HA021100861-02 | 1 | 72071.985 | 73094.967 | 1022.982 | 1000 |  | 1022982 | 1034107.8281 | Matuail |  |  |  | 11 kV Bhuighor Bazar | 1034107.8281 | 1233736.13 | -199628.3019 | -16.1808 | OK
18 | 11 kV Tokkar Math Feeder | 11 |  | HA021200298-02 | 1 | 78018.724 | 78743.932 | 725.208 | 1000 |  | 725208 | 733095.2742 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 733095.2742 | 699299.9675 | 33795.3067 | 4.8327 | OK
19 | 11 kV Osmani Stadium Feeder***** | 11 |  | XA575922 | 1 | 107.1 | 170.9 | 63.8 | 1000 |  | 63800 | 64493.8811 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 64493.8811 | 0 | 64493.8811 | #DIV/0! | #DIV/0!
16 | 33/0.415 KV Transformer, AT-1 | 0.415 |  | 2001123043119 | 1 | 7121 | 7194 | 73 | 160 |  | 11680 | 11807.0303 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 11807.0303 | 12027.363 | -220.3327 | -1.8319 | OK
17 | 33/0.415 KV Transformer, AT-2 | 0.415 |  | 2001123043157 | 1 | 4714.5 | 4715.3 | 0.8 | 160 |  | 128 | 129.3921 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 129.3921 | 0 | 129.3921 | #DIV/0! | #DIV/0!
[9 empty] | Total | 17115305.2855 | 16931164 | 17115305.2855 | 1.0876
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 4644322.6476
[5 empty] | Shyampur | at 33 KV level |  | 230570.6792
[5 empty] | Fatullah | at 33 KV level |  | 3359655.0807
[5 empty] | Matuail | at 33 KV level |  | 8880756.8781
[5 empty] | Total = |  |  | 17115305.2855 | 0
33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 8701920 | 15989040 | 7287120 | 1 | 0 | 7287120 | 7306501.5105
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 |  | 00000154 | 1 | 3564720 | 12822240 | 9257520 | 1 | 0 | 9257520 | 9282142.1719
[9 empty] | Total | 0 | 16544640 | 16588643.6824
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder | 33 |  | 00000079 | 1 | 301261696 | 310417664 | 9155968 | 1 | 9155968
7 | 33 kV Matuail-1 Feeder | 33 |  | 00000114 | 1 | 247031904 | 254261424 | 7229520 | 1 | 7229520
[9 empty] | Total | 16385488 | 0 | 0
LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
LAXMI NARAYAN COTTON MILL 33 KV SIDE
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000075 | 1 | 315889216 | 325047360 | 9158144 | 1 |  | 9158144
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000156 | 1 | 232467120 | 239696160 | 7229040 | 1 |  | 7229040
[9 empty] | Total |  | 16387184
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | BUS LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 16588643.6824 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 16588643.6824
| IMPORT-2 |  |  |  | 33 KV Net Import |  |  | 16588643.6824 |  | 33 KV TX HV Side |  | 16387184
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 201459.6824
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.214%
| TOTAL IMPORT |  | 16588643.6824
11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming | 11 |  | 00000144 | 1 | 314712352 | 323844352 | 9132000 | 1 | 9132000 |  | 9275619.8529
18 | 11 kV T-1 Incoming | 11 |  | 00000054 | 1 | 230985920 | 238185712 | 7199792 | 1 | 7199792 |  | 7313023.8296
[9 empty] | Total | 16331792 |  | 16588643.6824
LAXMI NARAYAN COTTON MILL 11 KV SIDE
1 | 11 kV Godnail (F16) | 11 |  | 00000109 | 1 | 19168914 | 21004948 | 1836034 | 1 |  | 1836034 | 1869406.9017 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1869406.9017 | 1924086.3812 | -54679.4795 | -2.8418 | OK
2 | 11 kV M. Circus (F15) | 11 |  | 00000123 | 1 | 101393752 | 103491504 | 2097752 | 1 |  | 2097752 | 2135882.0516 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 2135882.0516 | 1656394.6396 | 479487.412 | 28.9477 | OK
3 | 11 kV Wapderpool (F14) | 11 |  | 00000190 | 1 | 54594468 | 55179144 | 584676 | 1 |  | 584676 | 595303.4365 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 595303.4365 | 308554.3755 | 286749.0609 | 92.9331 | FAULT
4 | 11 kV Chowdhury Bari (F13) | 11 |  | 00000191 | 1 | 92008416 | 94163728 | 2155312 | 1 |  | 2155312 | 2194488.2982 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2194488.2982 | 2134643.7652 | 59844.533 | 2.8035 | OK
5 | 11 kV Ailpara (F12) | 1 |  | 00000192 | 1 | 44342692 | 46804564 | 2461872 | 1 |  | 2461872 | 2506620.5244 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2506620.5244 | 2099546.9745 | 407073.5498 | 19.3886 | OK
6 | 11 kV Spare (F11) | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | 11 |  | 00000197 | 1 | 11793891 | 13020328 | 1226437 | 1 |  | 1226437 | 1248729.4855 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1248729.4855 | 946745.9828 | 301983.5027 | 31.897 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 |  | 00000198 | 1 | 3943790 | 3985110 | 41320 | 1 |  | 41320 | 42071.0581 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 42071.0581 | 34694.5934 | 7376.4648 | 21.2611 | OK
12 | 11 kV Lucky Bazar (F5) | 11 |  | 00000199 | 1 | 84429552 | 85797352 | 1367800 | 1 |  | 1367800 | 1392661.9878 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1392661.9878 | 1273616.5848 | 119045.403 | 9.347 | OK
13 | 11 kV Enayetnagar (F4) | 11 |  | 00000200 | 1 | 26078056 | 27625972 | 1547916 | 1 |  | 1547916 | 1576051.8888 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1576051.8888 | 1741591.3981 | -165539.5093 | -9.5051 | OK
14 | 11 kV Bhuiyapara (F3) | 11 |  | 00000201 | 1 | 58396016 | 60310572 | 1914556 | 1 |  | 1914556 | 1949356.1666 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1949356.1666 | 1738828.831 | 210527.3357 | 12.1074 | OK
15 | 11 kV Arambagh (F2) | 11 |  | 00000202 | 1 | 4868388 | 5922585 | 1054197 | 1 |  | 1054197 | 1073358.7436 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 1073358.7436 | 984893.7851 | 88464.9585 | 8.9822 | OK
16 | 11 kV Spare (F1) | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 |  | 00000204 | 1 | 1485.81 | 1532.1 | 46.29 | 100 |  | 4629 | 4713.1396 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 4713.1396 | 5031.5286 | -318.389 | -6.3279 | OK
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 |  | 00000205 | 1 | 60.71 | 60.71 | 0 | 100 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 16588643.6824 | 16292501 | 16588643.6824 | 1.8177
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 7750610.9416
[5 empty] | Siddirgonj | at 33 KV level |  | 8838032.7408
[5 empty] | Total = |  |  | 16588643.6824 | 0
33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
| New Fatullah 33 kv Side | [7 empty] | Total | 0 | 0 | 0
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 607.2 | 633.63 | 26.43 | 360000 | 0 | 9514800 | 9508667.6365
0 | 0 | 33 | Backup | 041808904262 | 1 | 607.21 | 633.65 | 26.44 | 360000 | 0 | 9518400 | 9512265.3163
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 436.29 | 453.33 | 17.04 | 360000 | 0 | 6134400 | 6130446.3309
0 | 0 | 33 | Backup | 041808904258 | 1 | 436.46 | 453.51 | 17.05 | 360000 | 0 | 6138000 | 6134044.0107
[9 empty] | Total | 0 | 15649200 | 15639113.9674
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) | 33 | Digital | DHK60875 | 1 | 114650.2 | 154661.5 | 40011.3 | 240 | 9602712
9 | 33 kV New Fatulla-2 | 33 | Digital | DHK2186 | 1 | 280.5089 | 297.7603 | 17.2514 | 360000 | 6210504
[9 empty] | Total | 15813216 | 0 | 0
FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
FATULLAH OLD 33 KV SIDE
12 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60980 | 1 | 844285.1 | 871747.5 | 27462.4 | 240 |  | 6590976
13 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 | Digital | DHK60952 | 1 | 467991.4 | 480197.3 | 12205.9 | 240 |  | 9602712 |  |  | Meter Problem
[9 empty] | Total |  | 16193688 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV Net Import |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MATUAIL 33 KV SIDE |  | 0 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV Net Import |  | 15639113.9674
| New Fatullah 33 kv Side |  | 15639113.9674 |  | 33 KV Net Import |  |  | 15639113.9674 |  | 33 KV TX HV Side |  | 16193688
[10 empty] | LOSS UNITS=> |  | -554574.0326
[10 empty] | LOSS % IN => |  | -3.546%
| TOTAL IMPORT |  | 15639113.9674
11 KV SIDE of___FATULLAH OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | [5 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 | New | DHK61060 | 1 | 1009715.8 | 1009715.8 | 0 | 180 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 | New | DHK61054 | 1 | 342580.7 | 359028.9 | 16448.2 | 180 | 2960676 |  | 5022448.0522 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming | 11 | New | DHK60924 | 1.1 | 403841.3 | 435449.4 | 31608.1 | 180 | 6258403.8 |  | 10616665.9152 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming | 11 | New | DHK61051 | 1 | 833559.1 | 833559.1 | 0 | 90 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 9219079.8 |  | 15639113.9674 | [7 empty] | 0 | #DIV/0! | #DIV/0!
| FATULLAH OLD 11 KV SIDE | [18 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | 11 | New |  | 1 | 73664308 | 74349258 | 684950 | 1 |  | 684950 | 686221.5647 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 686221.5647 | 277780.4686 | 408441.0961 | 147.0374 | FAULT
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 85671760 | 86574371 | 902611 | 1 |  | 902611 | 904286.638 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 904286.638 | 681569.835 | 222716.803 | 32.677 | OK
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 57808.6 | 83099.6 | 25291 | 60 |  | 1517460 | 1520277.0648 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1520277.0648 | 1014339.8523 | 505937.2125 | 49.8785 | FAULT
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 259491.5 | 275685 | 16193.5 | 60 |  | 971610 | 973413.7301 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 973413.7301 | 968367.4932 | 5046.2369 | 0.52111 | OK
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 875315.6 | 906898.46 | 31582.86 | 60 |  | 1894971.6 | 1898489.4903 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 1898489.4903 | 1772327.559 | 126161.9313 | 7.1184 | OK
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 26016.8 | 37019.5 | 11002.7 | 60 |  | 660162 | 661387.5474 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 661387.5474 | 614553.3415 | 46834.2059 | 7.6209 | OK
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 574407.8 | 588771.6 | 14363.8 | 60 |  | 861828 | 863427.9271 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 863427.9271 | 710787.5218 | 152640.4053 | 21.4748 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 447240.7 | 466043.56 | 18802.86 | 60 |  | 1128171.6 | 1130265.9765 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1130265.9765 | 831941.7135 | 298324.263 | 35.8588 | OK
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 848225.6 | 855908.3 | 7682.7 | 60 |  | 460962 | 461817.7457 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 461817.7457 | 315580.2918 | 146237.4539 | 46.3392 | FAULT
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 478635.8 | 487049.3 | 8413.5 | 60 |  | 504810 | 505747.1466 | Fatullah |  |  |  | 11 kV Dhaka Steel | 505747.1466 | 255067.2341 | 250679.9125 | 98.2799 | FAULT
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 98157975 | 98802056 | 644081 | 1 |  | 644081 | 645276.6941 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 645276.6941 | 585326.5064 | 59950.1877 | 10.2422 | OK
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 23906084 | 24231901 | 325817 | 1 |  | 325817 | 326421.8579 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 326421.8579 | 308261.6394 | 18160.2185 | 5.8912 | OK
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14155030 | 14466321 | 311291 | 1 |  | 311291 | 311868.8913 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 311868.8913 | 436508.8251 | -124639.9338 | -28.5538 | OK
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 26378186 | 26912795 | 534609 | 1 |  | 534609 | 535601.4665 | Fatullah |  |  |  | 11 kV Aligonj Feeder | 535601.4665 | 528534.7802 | 7066.6863 | 1.337 | OK
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 7121858 | 9716958 | 2595100 | 1 |  | 2595100 | 2599917.6327 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 2599917.6327 | 2227277.3552 | 372640.2775 | 16.7308 | OK
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 99089910 | 100875390 | 1785480 | 1 |  | 1785480 | 1788794.6263 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1788794.6263 | 1753762.5774 | 35032.0489 | 1.9975 | OK
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 15813216 | 15783914.2 | 15813216 | 0.18564
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 12939140.354
[5 empty] | N.Gonj (West) | at 33 KV level |  | 1590508.2027
[5 empty] | Sytalakhya | at 33 KV level |  | 1283567.4432
[5 empty] | Total = |  |  | 15813216 | 0
132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder | 132 | Export | 041808902770 | 1 | 126.86 | 126.94 | 0.08 | 1200000 |  | 96000
|  | 132 |  | 041808904227 | 1 | 126.85 | 126.94 | 0.09 | 1200000 |  | 108000
|  | 132 | Import | 041808902770 | 1 | 144.25 | 157.03 | 12.78 | 1200000 | 15336000
|  | 132 |  | 041808904227 | 1 | 144.23 | 157.01 | 12.78 | 1200000 | 15336000
3 | 132 kV Haripur Feeder | 132 | Export | 041808902766 | 1 | 44.94 | 52.36 | 7.42 | 1200000 |  | 8904000
|  | 132 |  | 041808904230 | 1 | 44.95 | 52.38 | 7.43 | 1200000 |  | 8916000
|  | 132 | Import | 041808902766 | 1 | 716.36 | 719.42 | 3.06 | 1200000 | 3672000
|  | 132 |  | 041808904230 | 1 | 716.6 | 719.67 | 3.07 | 1200000 | 3684000
4 | 132 kV Aggreko Feeder | 132 | Export | 041808902768 | 1 | 29.36 | 30.27 | 0.91 | 1200000 |  | 1092000
|  | 132 |  | 041808904219 | 1 | 29.36 | 30.27 | 0.91 | 1200000 |  | 1092000
|  | 132 | Import | 041808902768 | 1 | 244.14 | 256.63 | 12.49 | 1200000 | 14988000
|  | 132 |  | 041808904219 | 1 | 244.15 | 256.63 | 12.48 | 1200000 | 14976000
6 | 132 kV Shyampur-2 Feeder | 132 | Export | 041808902793 | 1 | 120.63 | 120.72 | 0.09 | 1200000 |  | 108000
|  | 132 |  | 041808904278 | 1 | 120.65 | 120.73 | 0.08 | 1200000 |  | 96000
|  | 132 | Import | 041808902793 | 1 | 135.58 | 148.45 | 12.87 | 1200000 | 15444000
|  | 132 |  | 041808904278 | 1 | 135.61 | 148.48 | 12.87 | 1200000 | 15444000
[8 empty] | Total Import/Export |  | 49440000 | 10200000
[9 empty] | Net Total | 39240000
NEW FATULLAH 132 KV SIDE (RECEIVING)
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
FATULLAH 132 KV SIDE
2 | 132/33 kV, 80/120 MVA GT-1 | 132 | Export | 041808902767 | 1 | 520.23 | 539.67 | 19.44 | 1200000 |  | 23328000
|  | 132 | Export | 041808904228 | 1 | 520.1 | 539.54 | 19.44 | 1200000 |  | 23328000
5 | 132/33 kV, 80/120 MVA GT-2 | 132 | Export | 041808902792 | 1 | 401.45 | 414.71 | 13.26 | 1200000 |  | 15912000
|  | 132 | Export | 041808904251 | 1 | 401.3 | 414.56 | 13.26 | 1200000 |  | 15912000
[9 empty] | Total |  | 39240000
| 132 KV IMPORT |  | KWH | [6 empty] | TRANSMISSION LOSS |  | KWH
| 132 Sending Side |  | 39240000 | [6 empty] | 132 KV NET IMPORT |  | 39240000
| IMPORT-2 | [8 empty] | 132/33 KV GT LV Side |  | 39074400
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 165600
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.422%
| 132 KV TOTAL IMPORT |  | 39240000
33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902796 | 1 | 862.94 | 895.19 | 32.25 | 720000 | 23220000
|  | 33 | Backup | 041808904255 | 1 | 862.94 | 895.19 | 32.25 | 720000 | 23220000
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902802 | 1 | 666.15 | 688.17 | 22.02 | 720000 | 15854400
|  | 33 | Backup | 041808904281 | 1 | 665.99 | 688 | 22.01 | 720000 | 15847200
[9 empty] | Total | 39074400 |  | 0
FATULLAH 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902868 | 1 | 681.91 | 707.01 | 25.1 | 240000 |  | 6024000 | 6020117.4846 |  | 11965882.9205 | New Fatullah 33/11 kv ss | 0.247 | 33/11 kV, 28/35 MVA T-1 (=H5) | 6020117.4846 | 5580241.6107 | 439875.8738 | 7.8827 | OK
|  | 33 | Backup | 041808904277 | 1 | 681.49 | 706.58 | 25.09 | 240000 |  | 6021600 | 6017719.0314 |  |  |  |  | 0 | 6017719.0314 | 5577832.18 | 439886.8514 | 7.8863 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902824 | 1 | 588.13 | 612.92 | 24.79 | 240000 |  | 5949600 | 5945765.436 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 5945765.436 | 5365802.2742 | 579963.1617 | 10.8085 | OK
|  | 33 | Backup | 041808904267 | 1 | 588.04 | 612.83 | 24.79 | 240000 |  | 5949600 | 5945765.436 |  |  |  |  | 0 | 5945765.436 | 5365802.2742 | 579963.1617 | 10.8085 | OK
| 33 KV Feeders | [7 empty] | Total |  | 11973600 | 11965882.9205 |  |  |  |  | 33 KV Feeders | 11965882.9205 | 10946043.885 | 1019839.0356 | 9.317 | OK
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 690.84 | 712.24 | 21.4 | 360000 |  | 7704000 | 7699034.7114 |  | 11469403.1121 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 7699034.7114 | 7047584.9358 | 651449.7755 | 9.2436 | OK
|  | 33 | Backup | 041808904220 | 1 | 690.49 | 711.88 | 21.39 | 360000 |  | 7700400 | 7695437.0316 |  |  |  |  | 0 | 7695437.0316 | 7040356.6436 | 655080.388 | 9.3046 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 607.2 | 633.63 | 26.43 | 360000 |  | 9514800 | 9508667.6365 |  | 15639113.9674 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 9508667.6365 | 7466825.8859 | 2041841.7506 | 27.3455 | OK
|  | 33 | Backup | 041808904262 | 1 | 607.21 | 633.65 | 26.44 | 360000 |  | 9518400 | 9512265.3163 |  |  |  |  | 0 | 9512265.3163 | 7463211.7398 | 2049053.5765 | 27.4554 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 479.29 | 489.77 | 10.48 | 360000 |  | 3772800 | 3770368.4007 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 3770368.4007 | 3368384.1847 | 401984.216 | 11.934 | OK
|  | 33 | Backup | 041808904219 | 1 | 479.58 | 490.06 | 10.48 | 360000 |  | 3772800 | 3770368.4007 |  |  |  |  | 0 | 3770368.4007 | 3375612.477 | 394755.9237 | 11.6943 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 436.29 | 453.33 | 17.04 | 360000 |  | 6134400 | 6130446.3309 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 6130446.3309 | 5815161.1086 | 315285.2223 | 5.4218 | OK
|  | 33 | Backup | 041808904258 | 1 | 436.46 | 453.51 | 17.05 | 360000 |  | 6138000 | 6134044.0107 |  |  |  |  | 0 | 6134044.0107 | 5818775.2547 | 315268.756 | 5.4181 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907981 | 1 | 869.1 | 1007.9 | 138.8 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total |  | 27126000 | 27108517.0795 |  |  |  |  | 0 | 27108517.0795 | 23697956.115 | 3410560.9644 | 14.3918 | OK
[8 empty] | Grand Total |  | 39074400 | 39099600 | 39074400 | -0.064451
11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902832 | 1 | 652.74 | 676.78 | 24.04 | 250000 | 6010000 |  | 6019247.236
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902765 | 1 | 562.86 | 586.61 | 23.75 | 250000 | 5937500 |  | 5946635.6845
[9 empty] | Total | 11947500 |  | 11965882.9205
FATULLAH 11 kV SIDE
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902834 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 |  | 041808902801 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 790.28 | 823.84 | 33.56 | 60000 |  | 2013600 | 2018573.5941 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 2018573.5941 | 1823736.3611 | 194837.233 | 10.6834 | OK
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 341.43 | 366.25 | 24.82 | 60000 |  | 1489200 | 1492878.3256 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1492878.3256 | 1385628.7197 | 107249.6059 | 7.7401 | OK
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 495.29 | 506.79 | 11.5 | 60000 |  | 690000 | 691704.3007 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 691704.3007 | 667736.4742 | 23967.8266 | 3.5894 | OK
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1088.75 | 1118.86 | 30.11 | 60000 |  | 1806600 | 1811062.3039 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1811062.3039 | 1699857.6487 | 111204.6552 | 6.542 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902774 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902760 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902755 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 |  | 041808902788 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 |  | 041808902785 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 96.59 | 116.01 | 19.42 | 60000 |  | 1165200 | 1168078.0452 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 1168078.0452 | 1186818.4934 | -18740.4482 | -1.579 | OK
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 39.13 | 48.55 | 9.42 | 60000 |  | 565200 | 566596.0446 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 566596.0446 | 557756.349 | 8839.6956 | 1.5849 | OK
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1017.3 | 1045.24 | 27.94 | 60000 |  | 1676400 | 1680540.7098 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1680540.7098 | 1372938.7052 | 307602.0045 | 22.4046 | OK
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1192.19 | 1234.36 | 42.17 | 60000 |  | 2530200 | 2536449.5967 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2536449.5967 | 2251571.1337 | 284878.463 | 12.6524 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902781 | 1 |  | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 11965882.9205 | 11936400 | 11965882.9205 | 0.247
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 11965882.9205
[5 empty] | Total = |  |  | 11965882.9205 | 0
33 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 690.84 | 712.24 | 21.4 | 360000 | 0 | 7704000 | 7699034.7114
0 | 0 | 33 | Backup | 041808904220 | 1 | 690.49 | 711.88 | 21.39 | 360000 | 0 | 7700400 | 7695437.0316
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 479.29 | 489.77 | 10.48 | 360000 | 0 | 3772800 | 3770368.4007
0 | 0 | 33 | Backup | 041808904219 | 1 | 479.58 | 490.06 | 10.48 | 360000 | 0 | 3772800 | 3770368.4007
| DAPA 33 KV SIDE (RECEIVING) | [7 empty] | Total | 0 | 11476800 | 11469403.1121
5 | 33 kV New Fatullah Incoming Circuit-2 | 33 | Import |  | 1 | 172230576 | 175998960 | 3768384 | 1 | 3768384
6 | 33 kV Shyampur Incoming Circuit | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 | 33 | Import |  | 1 | 248272016 | 255965664 | 7693648 | 1 | 7693648
[9 empty] | Total | 11462032 | 0 | 0
DAPA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
DAPA 33 KV SIDE
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) | 33 | Export | 00000135 | 1 | 263794320 | 267562800 | 3768480 | 1 |  | 3768480
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) | 33 | Export | 00000193 | 1 | 249971040 | 257657760 | 7686720 | 1 |  | 7686720
[9 empty] | Total |  | 11455200 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NEW FATULLAH 33 KV SIDE |  | 11469403.1121 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 11469403.1121
[5 empty] | 33 KV NET IMPORT |  |  | 11469403.1121 |  | 33 KV TX HV SIDE |  | 11455200
[10 empty] | LOSS UNITS=> |  | 14203.1121
[10 empty] | LOSS % IN => |  | 0.1238%
| TOTAL IMPORT |  | 11469403.1121
11 KV SIDE of___DAPA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000035 | 1 | 48503728 | 56156320 | 7652592 | 1 | 7652592 |  | 7697700.8017
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000143 | 1 | 262650736 | 266400336 | 3749600 | 1 | 3749600 |  | 3771702.3103
[9 empty] | Total | 11402192 |  | 11469403.1121
DAPA 11 KV SIDE
11 | 11 kV Katherpol Feeder | 11 |  | 00000031 | 1 | 57646700 | 59742536 | 2095836 | 1 |  | 2095836 | 2095256.7912 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 2095256.7912 | 1881486.287 | 213770.5043 | 11.3618 | OK
12 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | 11 |  | 00000032 | 1 | 60506292 | 61871328 | 1365036 | 1 |  | 1365036 | 1364658.7564 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1364658.7564 | 1022984.374 | 341674.3823 | 33.3998 | OK
14 | 11 kV Shiachar Feeder | 11 |  | 00000030 | 1 | 60089012 | 61991488 | 1902476 | 1 |  | 1902476 | 1901950.2285 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 1901950.2285 | 1818485.4667 | 83464.7619 | 4.5898 | OK
15 | 11 kV Sastapur Feeder | 11 |  | 00000106 | 1 | 66398116 | 67891392 | 1493276 | 1 |  | 1493276 | 1492863.3157 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 1492863.3157 | 1608952.387 | -116089.0713 | -7.2152 | OK
17 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | 11 |  | 00000172 | 1 | 4097000 | 4889120 | 792120 | 1 |  | 792120 | 791901.0884 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 791901.0884 | 659073.1182 | 132827.9702 | 20.1538 | OK
19 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | 11 |  | 00000044 | 1 | 74571856 | 74945536 | 373680 | 1 |  | 373680 | 373576.7292 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 373576.7292 | 367417.5635 | 6159.1657 | 1.6763 | OK
23 | 11 kV Kotaler Bag Feeder | 11 |  | 00000050 | 1 | 78139288 | 79654888 | 1515600 | 1 |  | 1515600 | 1515181.1462 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 1515181.1462 | 1364191.1809 | 150989.9653 | 11.0681 | OK
24 | 11 kV Idrakpur Feeder | 11 |  | 00000021 | 1 | 72447944 | 73516904 | 1068960 | 1 |  | 1068960 | 1068664.5804 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 1068664.5804 | 999398.3161 | 69266.2643 | 6.9308 | OK
25 | 11 kV Isdair Feeder | 11 |  | 00000029 | 1 | 37647948 | 38441108 | 793160 | 1 |  | 793160 | 792940.801 | Fatullah |  |  |  | 11 kV Isdair Feeder | 792940.801 | 624332.0908 | 168608.7102 | 27.0063 | OK
26 | 11 kV Shah Fateullah Express | 11 |  | 0000051 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKF 7522 | 1 | 2848 | 2900 | 52 | 100 |  | 5200 | 5198.5629 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 5198.5629 | 5535.2158 | -336.6529 | -6.082 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 11402192 | 11405344 | 11402192 | -0.027636
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 11402192
[5 empty] | Total = |  |  | 11402192 | 0
132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 | 132 | IMPORT | 50501730 | 1 | 2694.555 | 2736.898 | 42.343 | 480000 | 0 | 20324640
2 | Tranformer 1 | 132 |  | 80505634 | 1 | 8302.15 | 8341.911 | 39.761 | 480000 | 0 | 19085280
3 | Tranformer 2 | 132 |  | 80505637 | 1 | 8253.814 | 8293.77 | 39.956 | 480000 | 0 | 19178880
4 | MI CEMENT | 132 |  | 38992489 (New) | 1 | 214.544 | 237.085 | 22.541 | 480000 | 0 | 10819680
[8 empty] | Total Import/Export |  | 0 | 69408480
[9 empty] | Net Total | 69408480
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 214.53 | 237.068 | 22.538 | 480000 |  | 10818240
|  | 132 | DPDC | 16402670 | 1 | 1739.619 | 1762.138 | 22.519 | 480000 |  | 10809120
[9 empty] | Total |  | 10809120
SITALAKHYA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
| 132/33 KV GT-3 | 132 | [8 empty] | 0
[9 empty] | Total |  | 58599360
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 69408480 |  | EXPORT TO OTHER S/S |  |  | 10809120 |  | 132 KV NET IMPORT |  | 58599360
| IMPORT-2 |  |  |  | 132 KV NET IMPORT for Sitalakhya 33/11 KV |  |  | 58599360 |  | GT (33 KV Side) |  | 58436017
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 163343
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.2787%
| 132 KV TOTAL IMPORT |  | 69408480
33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A030701130-03 | 1 | 14612.731 | 33767.132 | 19154.401 | 1000 | 19154401
|  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  | 33 | DPDC | BD001913 | 1 | 1609.7124 | 1649.3934 | 39.681 | 480000 | 19046880
18 | 132/33 KV Transformer, GT-3 Incoming | 33 | DPDC | BD001915 | 1 | 2687.3443 | 2729.5 | 42.1557 | 480000 | 20234736
[9 empty] | Total | 58436017 |  | 0
SITALAKHYA 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 | 33 | DPDC | H/A030701089-03 | 1 | 43324.794 | 52483.717 | 9158.923 | 1000 |  | 9158923 | 9161254.0741 |  | 13805202.7233 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 9161254.0741 | 8568075.1889 | 593178.8852 | 6.9231 | OK
|  | 33 | P. Cell | 08993597 | 1 | 5754.455 | 5792.471 | 38.016 | 240000 |  | 9123840 | 9126162.145 |  |  |  |  | 0 | 9126162.145 | 8550193.275 | 575968.87 | 6.7363 | OK
13 | 33/11 KV Transformer T-4 | 33 | DPDC | H/A030701087-03 | 1 | 56943.08 | 61585.847 | 4642.767 | 1000 |  | 4642767 | 4643948.6492 |  |  |  |  | 33/11 KV Transformer T-4 | 4643948.6492 | 4471702.675 | 172245.9742 | 3.8519 | OK
|  | 33 | P. Cell | 08993925 | 1 | 5577.513 | 5603.238 | 25.725 | 180000 |  | 4630500 | 4631678.5271 |  |  |  |  | 0 | 4631678.5271 | 4467427.9784 | 164250.5487 | 3.6766 | OK
| 33 KV Feeders | [7 empty] | Total |  | 13801690 | 13805202.7233 |  |  |  |  | 33 KV Feeders | 13805202.7233 | 13039777.8639 | 765424.8594 | 5.8699 | OK
10 | 33 KV Char Syedpur Feeder (F1) | 33 | DPDC | H/A030701083-03 | 1 | 42622.663 | 42622.663 | 0 | 1000 |  | 0 | 0 |  | 0 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 34 KV Char Syedpur Feeder (F1) | 33 | P. Cell | 08993596 | 1 | 2186.817 | 2186.817 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 88020.474 | 98984.656 | 10964.182 | 1000 |  | 10964182 | 10966972.5378 |  | 10966972.5378 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 10966972.5378 | 9242174.035 | 1724798.5028 | 18.6623 | OK
| 34 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9558.392 | 9619.053 | 60.661 | 180000 |  | 10918980 | 10921759.0333 |  |  |  |  | 34 KV Panchabati BSCIC Feeder (F3) | 10921759.0333 | 9233884.6842 | 1687874.349 | 18.2791 | OK
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 35431.875 | 36660.866 | 1228.991 | 1000 |  | 1228991 | 1229303.7954 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 1229303.7954 | 1851894.7708 | -622590.9754 | -33.6191 | OK
|  | 33 | P. Cell | 08993926 | 1 | 2272.334 | 2279.147 | 6.813 | 180000 |  | 1226340 | 1226652.1207 |  | 17488342.8955 | Khanpur 33/11 kv ss |  | 0 | 1226652.1207 | 1848541.2243 | -621889.1036 | -33.6422 | OK
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 83681.645 | 92642.466 | 8960.821 | 1000 |  | 8960821 | 8963101.6544 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 8963101.6544 | 8228320.8251 | 734780.8293 | 8.9299 | OK
|  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 8214198.5239 | -8214198.5239 | -100 | CHECK
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1439.7058 | 1480.0066 | 40.3008 | 180000 |  | 7254144 | 7255990.2812 |  | 14943346.3231 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 7255990.2812 | 6813012.1971 | 442978.0841 | 6.5019 | OK
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 299.8501 | 335.3629 | 35.5128 | 240000 |  | 8523072 | 8525241.2411 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 8525241.2411 | 7839341.44 | 685899.8012 | 8.7495 | OK
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1193.4139 | 1225.4364 | 32.0225 | 240000 |  | 7685400 | 7687356.0419 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 7687356.0419 | 7494645.2709 | 192710.771 | 2.5713 | OK
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4603.3 | 4621.1 | 17.8 | 160 |  | 2848 | 2848.7249 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 2848.7249 | 3664.5972 | -815.8723 | -22.2636 | OK
[9 empty] | Total |  | 44619458 | 44630814.2767 |  |  |  |  | 0 | 44630814.2767 | 41473053.1361 | 3157761.1406 | 7.614 | OK
[8 empty] | Grand Total |  | 58436017 | 58421148 | 58436017 | 0.025451
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1232152.5203
[5 empty] | Total = |  |  | 1232152.5203
11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming | 11 |  | DHK 9372 | 1 | 19848.5875 | 70573.2195 | 50724.632 | 180 | 9130433.76 |  | 9176521.1362
10 | 33/11 kV Transformer, T-4 Incoming | 11 |  | DHK 9368 | 1 | 8901.3491 | 34487.0985 | 25585.7494 | 180 | 4605434.892 |  | 4628681.5872
[9 empty] | Total | 13735868.652 |  | 13805202.7233
SITALAKHYA 11 kV SIDE
3 | 11 kV Bholail Feeder (F-3) | 11 |  | DHK 9335 | 1 | 76570.4462 | 117557.5729 | 40987.1267 | 60 |  | 2459227.602 | 2464743.5384 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 2464743.5384 | 1761565.1158 | 703178.4225 | 39.9178 | OK
4 | 11 kV Crony Apparels (F-2) | 11 |  | DHK 9336 | 1 | 86741.1599 | 110186.2566 | 23445.0967 | 60 |  | 1406705.802 | 1409860.9795 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1409860.9795 | 1062866.0479 | 346994.9316 | 32.6471 | OK
5 | 11 kV Baburail Feeder (F-5) | 11 |  | DHK 9322 | 1 | 81641.2934 | 114240.3356 | 32599.0422 | 60 |  | 1955942.532 | 1960329.6227 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 1960329.6227 | 1952139.6607 | 8189.962 | 0.41954 | OK
6 | 11 kV Goghchar Feeder (F-1) | 11 |  | DHK 9323 | 1 | 47575.3245 | 68546.5464 | 20971.2219 | 60 |  | 1258273.314 | 1261095.5642 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1261095.5642 | 1230104.9583 | 30990.6058 | 2.5193 | OK
7 | 11 kV Norshinghopur (F-2) | 11 |  | DHK 9365 | 1 | 23185.9177 | 47651.0611 | 24465.1434 | 60 |  | 1467908.604 | 1471201.0567 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1471201.0567 | 1293031.4033 | 178169.6533 | 13.7792 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 |  | DHK 9367 | 1 | 97389.3483 | 106609.7103 | 9220.362 | 60 |  | 553221.72 | 554462.5713 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 554462.5713 | 1247433.9822 | -692971.4109 | -55.5518 | CHECK
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 |  | H/A030701125-03 | 1 | 72378.143 | 72602.239 | 224.096 | 1000 |  | 224096 | 224598.6372 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 224598.6372 | 228747.9909 | -4149.3537 | -1.8139 | OK
12 | 11 kV Kashipur Feeder (F-7) | 11 |  | H/A030800169-03 | 1 | 29944.336 | 31592.82 | 1648.484 | 1000 |  | 1648484 | 1652181.4751 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1652181.4751 | 1648486.1659 | 3695.3092 | 0.22416 | OK
13 | 11 kV Spare Feeder (F-6) | 11 |  |  | 1 |  | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | 11 |  | H/A030701098-03 | 1 | 74950.975 | 76031.283 | 1080.308 | 1000 |  | 1080308 | 1082731.082 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 1082731.082 | 1042180.592 | 40550.49 | 3.8909 | OK
15 | 11 kV B. K. Road Feeder (F-9) | 11 |  | H/A030800205-03 | 1 | 92273.664 | 93037 | 763.336 | 1000 |  | 763336 | 765048.1281 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 765048.1281 | 586711.3248 | 178336.8033 | 30.396 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 |  | H/A030701091-03 | 1 | 50158.39 | 51115.194 | 956.804 | 1000 |  | 956804 | 958950.0681 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 958950.0681 | 986510.6218 | -27560.5537 | -2.7937 | OK
[9 empty] | Total | 13805202.7233 | 13774307.574 | 13805202.7233 | 0.2243
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 989646.7653
[5 empty] | Sytalakhya | at 33 KV level |  | 9772495.2533
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3043060.7047
[5 empty] | Total = |  |  | 13805202.7233 | 0
MI CEMENT 132/33 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
1 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 214.53 | 237.068 | 22.538 | 480000 | 10818240 |  | 10819680
|  | 132 | DPDC | 16402670 | 1 | 1739.619 | 1762.138 | 22.519 | 480000 | 10809120
2 | 132/33 kV Transformer (132 kV Side) | 132 |  | 06502030 | 1 | 3458.406 | 3503.713 | 45.307 | 240000 |  | 10873680
[8 empty] | Total Import/Export |  | 10809120 | 10873680
Net Total
3 | 132/33 kV Transformer (33 kV Side) | 33 |  | 14718815 | 1 | 6824.567 | 6914.144 | 89.577 | 120000 | 10749240
4 | 33 kV Outgoing Feeder-1 | 33 |  | 11745824 | 1 | 3577.987 | 3609.947 | 31.96 | 120000 |  | 3835200
5 | 33 kV Outgoing Feeder-2 | 33 |  |  | 1 |  | 0 | 0 | 120000 |  | 6914040
[8 empty] | Total Import/Export |  | 10749240 | 10749240
[8 empty] | Net Total |  | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 10819680
[5 empty] | Total = |  |  | 10819680
192
33 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1439.7058 | 1480.0066 | 40.3008 | 180000 | 0 | 7254144 | 7255990.2812
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1193.4139 | 1225.4364 | 32.0225 | 240000 | 0 | 7685400 | 7687356.0419
[9 empty] | Total | 0 | 14939544 | 14943346.3231
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder | 33 |  | 00000188 | 1 | 290547008 | 297807296 | 7260288 | 1 | 7260288
7 | 33 kV Shitalakhya-1 Feeder | 33 |  | 00000153 | 1 | 286806976 | 294503584 | 7696608 | 1 | 7696608
[9 empty] | Total | 14956896 | 0 | 0
MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
MONDOLPARA 33 KV SIDE
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000116 | 1 | 295163776 | 302422336 | 7258560 | 1 |  | 7258560
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000194 | 1 | 282027136 | 289720064 | 7692928 | 1 |  | 7692928
[9 empty] | Total |  | 14951488 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 14943346.3231 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 14943346.3231
[5 empty] | 33 KV NET IMPORT |  |  | 14943346.3231 |  | 33 KV TX HV SIDE |  | 14951488
[10 empty] | LOSS UNITS=> |  | -8141.6769
[10 empty] | LOSS % IN => |  | -0.05448%
| TOTAL IMPORT |  | 14943346.3231
11 KV SIDE of___MONDALPARA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming | 11 |  | 00000055 | 1 | 280661152 | 288316736 | 7655584 | 1 | 7655584 |  | 7714620.3206
19 | 11 kV T-2 Incoming | 11 |  | 00000017 | 1 | 293011552 | 300184960 | 7173408 | 1 | 7173408 |  | 7228726.0025
[9 empty] | Total | 14828992 |  | 14943346.3231
MONDOLPARA 11 KV SIDE
9 | 11 kV River View | 11 |  | 00000061 | 1 | 3921252 | 4718732 | 797480 | 1 |  | 797480 | 803073.4017 | N.Gonj (East) |  |  |  | 11 kV River View | 803073.4017 | 709369.5292 | 93703.8726 | 13.2095 | OK
10 | 11 kV Railgate B.B. Road | 11 |  | 00000191 | 1 | 20877230 | 21484788 | 607558 | 1 |  | 607558 | 611819.3181 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 611819.3181 | 680612.9948 | -68793.6767 | -10.1076 | OK
11 | 11 kV DIT | 11 |  | 00000174 | 1 | 127405168 | 130377160 | 2971992 | 1 |  | 2971992 | 2992837.0935 | N.Gonj (West) |  |  |  | 11 kV DIT | 2992837.0935 | 2989598.5296 | 3238.564 | 0.10833 | OK
12 | 11 kV Dalpatti | 11 |  | 00000182 | 1 | 1673315 | 2382434 | 709119 | 1 |  | 709119 | 714092.6513 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 714092.6513 | 607801.9662 | 106290.6851 | 17.4877 | OK
13 | 11 kV South Chasara | 11 |  | 00000043 | 1 | 86363752 | 88911104 | 2547352 | 1 |  | 2547352 | 2565218.7341 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2565218.7341 | 2514472.3313 | 50746.4028 | 2.0182 | OK
14 | 11 kV Spare | 11 |  | 00000137 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | 11 |  | 00000019 | 1 | 44799 | 67159 | 22360 | 1 |  | 22360 | 22516.8296 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 22516.8296 | 16336.6481 | 6180.1815 | 37.8302 | OK
17 | 11 kV Spare | 11 |  | 00000041 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | 11 |  | 00000173 | 1 | 2343714 | 3304592 | 960878 | 1 |  | 960878 | 967617.4501 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 967617.4501 | 866203.3675 | 101414.0826 | 11.7079 | OK
20 | 11 kV Nitaigonj | 11 |  | 00000189 | 1 | 55969784 | 56636980 | 667196 | 1 |  | 667196 | 671875.6098 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 671875.6098 | 605182.0519 | 66693.558 | 11.0204 | OK
21 | 11 kV Shahid Nagar | 11 |  | 00000020 | 1 | 53165432 | 54413388 | 1247956 | 1 |  | 1247956 | 1256708.9709 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1256708.9709 | 1213591.096 | 43117.8749 | 3.5529 | OK
22 | 11 kV Bangla Bazar | 11 |  | 00000139 | 1 | 64386124 | 65980440 | 1594316 | 1 |  | 1594316 | 1605498.2865 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1605498.2865 | 1554801.1512 | 50697.1353 | 3.2607 | OK
23 | 11 kV Vogoban Gonj | 11 |  | 00000181 | 1 | 1025797 | 1465156 | 439359 | 1 |  | 439359 | 442440.5963 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 442440.5963 | 405107.5263 | 37333.0699 | 9.2156 | OK
24 | 11 kV Tanbazar | 11 |  | 00000138 | 1 | 45709768 | 46679968 | 970200 | 1 |  | 970200 | 977004.8332 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 977004.8332 | 879714.3805 | 97290.4526 | 11.0593 | OK
25 | 11 kV SS Road | 11 |  | 00000175 | 1 | 61263892 | 62559048 | 1295156 | 1 |  | 1295156 | 1304240.0244 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1304240.0244 | 1255985.7062 | 48254.3183 | 3.8419 | OK
26 | 11 kV Spare | 11 |  | 00000094 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 | 0.415 |  |  | 1 | 2249.63 | 2333.07 | 83.44 | 100 |  | 8344 | 8402.5235 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 8402.5235 | 7769.9922 | 632.5313 | 8.1407 | OK
28 | 33/0.415 kV Auxiliary-2 | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 14943346.3231 | 14839266 | 14943346.3231 | 0.70138
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1256708.9709
[5 empty] | N.Gonj (East) | at 33 KV level |  | 5210440.6901
[5 empty] | N.Gonj (West) | at 33 KV level |  | 8476196.6621
[5 empty] | Total = |  |  | 14943346.3231 | 0
33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 88020.474 | 98984.656 | 10964.182 | 1000 | 0 | 10964182 | 10966972.5378
0 | 34 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9558.392 | 9619.053 | 60.661 | 180000 | 0 | 10918980 | 10921759.0333
| MATUAIL 33 KV SIDE | [7 empty] | Total |  | 10964182 | 10966972.5378
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 50282.605 | 55353.737 | 5071.132 | 1000 | 0 | 5071132 | 5084619.6602
0 | 0 | 33 | P. Cell | 08993580 | 1.5 | 1294.23 | 1313.084 | 18.854 | 180000 | 0 | 5090580 | 5104119.3859
[9 empty] | Total | 0 | 5071132 | 5084619.6602
| NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING) | [7 empty] | Total |  | 16035314 | 16051592.198
3 | 33 kV Matuail Feeder | 33 | Digital | ABB03910 | 1 | 78802.1568 | 79891.7347 | 1089.5779 | 4000 | 4358311.72
6 | 33 kV Shitalakhya Feeder | 33 | Old | HA030800161-03 | 1.5 | 105759.181 | 113039.175 | 7279.994 | 1000 | 10919991
|  | 33 | New | DHKA2199 | 1 | 3979.569 | 4034.087 | 54.518 | 180000 | 9813240
[9 empty] | Total | 15278302.72 | 0 | 0
NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
NARAYANGONJ BSCIC 33 KV SIDE
5 | 33/11 kV, 20/28 MVA Transformer-3 | 33 | Old | HA021100524-02 | 1 |  |  | 0 | 1000 |  | 0
|  | 33 | New | DHKA2200 | 1 | 4219.2923 | 4246.9223 | 27.63 | 180000 |  | 4973400
7 | 33/11 kV, 10/14 MVA Transformer-2 | 33 | Old | HA030800199-03 | 1 | 24168.912 | 29604.1 | 5435.188 | 1000 |  | 5435188
|  | 33 | New | DHKA2195 | 1 | 4318.5971 | 4374.8683 | 56.2712 | 90000 |  | 5064408
8 | 33/11 kV, 10/14 MVA Transformer-1 | 33 | Digital | ABB03909 | 1 | 410349.1334 | 415710.129 | 5360.9956 | 1000 |  | 5360995.59
[9 empty] | Total |  | 15769583.59 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| SITALAKHYA 33 KV SIDE |  | 10966972.5378 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 16051592.198
| MATUAIL 33 KV SIDE |  | 5084619.6602 |  | 33 KV NET IMPORT |  |  | 16051592.198 |  | 33 KV TX HV SIDE |  | 15769583.59
[10 empty] | LOSS UNITS=> |  | 282008.608
[10 empty] | LOSS % IN => |  | 1.757%
| TOTAL IMPORT |  | 16051592.198
11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming | 11 |  | 51426632 | 1 | 3558885 | 3618652 | 59767 | 90 | 5379030 |  | 5461095.2121
16 | 33/11 kV Transformer, T-1 Incoming | 11 |  | DHKA2192 | 1 | 3675.3145 | 3735.4904 | 60.1759 | 90000 | 5415831 |  | 5498457.6668
22 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426630 | 1 | 3871286 | 3927014 | 55728 | 90 | 5015520 |  | 5092039.319
[9 empty] | Total | 15810381 |  | 16051592.198
NARAYANGONJ BSCIC 11 KV SIDE
10 | 11 kV Masdair Feeder (F-8) | 11 |  | XA575914 | 1 | 203761.5 | 206799.9 | 3038.4 | 1000 |  | 3038400 | 3077099.4263 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 3077099.4263 | 2929370.845 | 147728.5813 | 5.043 | OK
11 | 11 kV Narayangonj (F-7) | 11 |  | XA575915 | 1 | 161786.6 | 163077.6 | 1291 | 1000 |  | 1291000 | 1307443.1804 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1307443.1804 | 1073353.3917 | 234089.7887 | 21.8092 | OK
12 | 11 kV Nearest Feeder (F-6) | 11 |  | XA575927 | 1 | 102847.3 | 103832.5 | 985.2 | 1000 |  | 985200 | 997748.2737 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 997748.2737 | 697613.892 | 300134.3817 | 43.023 | FAULT
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 |  | XA575916 | 1 | 112523.8 | 113848.2 | 1324.4 | 1000 |  | 1324400 | 1341268.5888 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1341268.5888 | 1029512.0542 | 311756.5346 | 30.282 | OK
14 | 11 kV Abonti Color Tex. (F-4) | 11 |  | XA575912 | 1 | 52800.5 | 53493 | 692.5 | 1000 |  | 692500 | 701320.2188 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 701320.2188 | 764034.0245 | -62713.8057 | -8.2082 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 |  | DHK66615 | 1 | 147.9431 | 165.1511 | 17.208 | 60000 |  | 1032481.86 | 1045632.3523 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 1045632.3523 | 820430.387 | 225201.9652 | 27.4492 | OK
17 | 11 kV Shasongaon Feeder (F-2) | 11 |  | XA575920 | 1 | 228775.4 | 229950 | 1174.6 | 1000 |  | 1174600 | 1189560.6195 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 1189560.6195 | 1058570.8622 | 130989.7573 | 12.3742 | OK
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 |  | XA575929 | 1 | 16570 | 17828 | 1258 | 1000 |  | 1258000 | 1274022.8667 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1274022.8667 | 968053.1816 | 305969.6852 | 31.6067 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 |  | HA021100913-02 | 1 | 36841.501 | 37746.076 | 904.575 | 1000 |  | 904575 | 916096.371 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 916096.371 | 564950.8148 | 351145.5562 | 62.1551 | FAULT
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 |  | HA021100682-02 | 1 | 53082.882 | 55419.839 | 2336.957 | 1000 |  | 2336957 | 2366722.3025 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 2366722.3025 | 1808759.934 | 557962.3685 | 30.8478 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 |  | HA021100455-02 | 1 | 49545.321 | 51349.693 | 1804.372 | 1000 |  | 1804372 | 1827353.8856 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1827353.8856 | 1381521.5441 | 445832.3416 | 32.2711 | OK
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3648.6 | 3691.2 | 42.6 | 160 |  | 6816 | 6902.8139 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 6902.8139 | 6706.8134 | 196.0005 | 2.9224 | OK
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4095.5 | 4098.1 | 2.6 | 160 |  | 416 | 421.2985 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 421.2985 | 210.6004 | 210.6981 | 100.0464 | FAULT
[9 empty] | Grand Total | 16051592.198 | 15849717.86 | 16051592.198 | 1.2737
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1189560.6195
[5 empty] | N.Gonj (West) | at 33 KV level |  | 14862031.5785
[5 empty] | Total = |  |  | 16051592.198 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  | IMPORT | 42627811 | 1 | 223.259 | 235.539 | 12.28 | 960000 | 0 | 11788800
| Madonganj to Charsyedpur-2 |  |  | 42627824 | 1 | 130.476 | 144.939 | 14.463 | 960000 | 0 | 13884480
[8 empty] | Total Import/Export |  | 0 | 25673280 | 0
[9 empty] | Net Total | 25673280
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 | 132 |  | 041808902821 | 1 | 186.11 | 195.94 | 9.83 | 1200000 | 11796000
|  | 132 |  | 041808904222 | 3 | 61.39 | 64.67 | 3.28 | 1200000 | 11808000
| 132 kV Madanganj Circuit-2 | 132 |  | 041808902865 | 1 | 104.14 | 115.71 | 11.57 | 1200000 | 13884000
|  | 132 |  | 041808904240 | 1 | 104.17 | 115.75 | 11.58 | 1200000 | 13896000
[8 empty] | Total Import/Export |  | 25680000 | 0 | 0
[8 empty] | Net Total |  | 25680000
CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
CHAR SYEDPUR 132 KV SIDE
4 | 132/33 kV, 80/120 MVA GT-1 | 132 | EXPORT | 041808902864 | 1 | 136.27 | 146.13 | 9.86 | 1200000 | 11832000 | 11832000
|  | 132 |  | 041808904224 | 1 | 136.18 | 146.03 | 9.85 | 1200000 | 11820000 | 11820000
7 | 132/33 kV, 80/120 MVA GT-2 | 132 |  | 041808902848 | 1 | 153.94 | 165.49 | 11.55 | 1200000 | 13860000 | 13860000
|  | 132 |  | 041808904244 | 1 | 154.01 | 165.59 | 11.58 | 1200000 | 13896000 | 13896000
[9 empty] | Total |  | 25692000
| 132 KV IMPORT |  | KWH |  | 132 KV EXPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SENDING SIDE (TARIFF POINT) |  | 25673280 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 25692000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 25692000 |  | 132/33 KV LV SIDE |  | 25552800
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 139200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5418%
| 132 KV TOTAL IMPORT |  | 25673280
33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902859 | 1 | 225.65 | 241.98 | 16.33 | 720000 | 11757600 |  | 11821650.0423
|  | 33 | Backup | 041808904285 | 1 | 225.65 | 241.98 | 16.33 | 720000 | 11757600 |  | 11821650.0423
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902812 | 1 | 255.36 | 274.52 | 19.16 | 720000 | 13795200 |  | 13870349.9577
|  | 33 | Backup | 041808904276 | 1 | 255.38 | 274.57 | 19.19 | 720000 | 13816800 |  | 13892067.6247
[9 empty] | Total | 25552800 |  | 25692000
CHAR SYEDPUR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902875 | 1 | 179.24 | 190.56 | 11.32 | 240000 |  | 2716800 | 2723906.2656 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2723906.2656 | 2449795.915 | 274110.3506 | 11.1891 | OK
|  | 33 | Backup | 041808904241 | 1 | 179.19 | 190.5 | 11.31 | 240000 |  | 2714400 | 2721499.988 |  |  |  |  | 0 | 2721499.988 | 2449795.915 | 271704.073 | 11.0909 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902844 | 3 | 51.14 | 53.76 | 2.62 | 240000 |  | 1886400 | 1891334.2091 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 1891334.2091 | 1920045.5263 | -28711.3172 | -1.4953 | OK
|  | 33 | Backup | 041808904259 | 3 | 51.13 | 53.76 | 2.63 | 240000 |  | 1893600 | 1898553.042 |  |  |  |  | 0 | 1898553.042 | 1920045.5263 | -21492.4843 | -1.1194 | OK
| 33 KV Feeders | [7 empty] | Total |  | 4603200 | 4615240.4747 |  |  |  |  | 33 KV Feeders | 4615240.4747 | 4369841.4413 | 245399.0334 | 5.6157 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 251.46 | 269.79 | 18.33 | 360000 |  | 6598800 | 6616060.3155 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 6616060.3155 | 5440128.9912 | 1175931.3243 | 21.6159 | OK
|  | 33 | Backup | 041808904221 | 1 | 251.57 | 269.81 | 18.24 | 360000 |  | 6566400 | 6583575.5677 |  |  |  |  | 0 | 6583575.5677 | 5440128.9912 | 1143446.5765 | 21.0187 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 80.23 | 87.04 | 6.81 | 360000 |  | 2451600 | 2458012.5886 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2458012.5886 | 1729479.21 | 728533.3786 | 42.1244 | FAULT
|  | 33 | Backup | 041808904237 | 1 | 80.17 | 87.04 | 6.87 | 360000 |  | 2473200 | 2479669.0872 |  |  |  |  | 0 | 2479669.0872 | 1729479.21 | 750189.8771 | 43.3766 | FAULT
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 36.82 | 39.89 | 3.07 | 360000 |  | 1105200 | 1108090.8439 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 1108090.8439 | 1006765.4445 | 101325.3994 | 10.0644 | OK
|  | 33 | Backup | 041808904232 | 1 | 36.84 | 39.92 | 3.08 | 360000 |  | 1108800 | 1111700.2603 |  |  |  |  | 0 | 1111700.2603 | 1006765.4445 | 104934.8158 | 10.423 | OK
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 375.19 | 405.16 | 29.97 | 360000 |  | 10789200 | 10817421.0397 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 10817421.0397 | 9060889.0006 | 1756532.0391 | 19.3859 | OK
|  | 33 | Backup | 041808904242 | 1 | 375.22 | 405.19 | 29.97 | 360000 |  | 10789200 | 10817421.0397 |  |  |  |  | 0 | 10817421.0397 | 9060889.0006 | 1756532.0391 | 19.3859 | OK
| 33/0.415 kV Transformer AT-1 |  |  |  | 1 | 1273.63 | 1372.11 | 98.48 | 1 |  | 98.48 | 98.7376 | [5 empty] | 98.7376 | 95.9124
[9 empty] | Total |  | 20944898.48 | 20999683.5253 |  |  |  |  | 0 | 20999683.5253 | 17237358.5587 | 3762324.9666 | 21.8266 | OK
[8 empty] | Grand Total |  | 25614924 | 25548098.48 | 25614924 | 0.26157
11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902756 | 1 | 171.29 | 182.1 | 10.81 | 250000 | 2702500 |  | 2798511.8317
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902778 | 1.72 | 108.58 | 112.66 | 4.08 | 250000 | 1754400 |  | 1816728.643
[9 empty] | Total | 4456900 |  | 4615240.4747
CHAR SYEDPUR 11 kV SIDE
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 |  | 041808902749 | 1 | 339.06 | 360.83 | 21.77 | 60000 |  | 1306200 | 1308593.1901 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 1308593.1901 | 1198405.9574 | 110187.2327 | 9.1945 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 |  | 041808902759 | 1 | 374.92 | 398.23 | 23.31 | 60000 |  | 1398600 | 1401162.4833 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1401162.4833 | 1255071.0278 | 146091.4554 | 11.6401 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | 11 |  | 041808902786 | 1 | 211.44 | 229.07 | 17.63 | 60000 |  | 1057800 | 1059738.0772 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1059738.0772 | 1003695.1303 | 56042.9469 | 5.5837 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 |  | 041808902789 | 1 | 137.32 | 151.39 | 14.07 | 60000 |  | 844200 | 845746.7241 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 845746.7241 | 912669.3257 | -66922.6016 | -7.3326 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907976 | 1 | 1273.63 | 1372.11 | 98.48 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4615240.4747 | 4606800 | 4615240.4747 | 0.18322
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 25614825.2624
[5 empty] | Total = |  |  | 25614825.2624 | 20999584.7877
33 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
FROM MADERTEK 33 KV SIDE
3 | Amulia | 33 | Export | SIEM0505 | 1 | 32926 | 34124 | 1198 | 6000 | 0 | 7188000 | 7216415.4244
[9 empty] | Total |  | 7188000 | 7216415.4244
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving | 33 |  |  | 1 | 1178.26 | 1217.99 | 39.73 | 180000 | 7151400
[9 empty] | Total | 7151400 | 0 | 0
AMULIA 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
AMULIA 33 KV SIDE
3 | 33/11 kV Transformer, T-1 | 33 |  | DHKA2194 | 1 | 310.9996 | 325.7547 | 14.7551 | 240000 |  | 3541224
4 | 33/11 kV Transformer, T-2 | 33 |  | DHKA2198 | 1 | 487.158 | 502.0763 | 14.9183 | 240000 |  | 3580392
[9 empty] | Total |  | 7121616 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| FROM MADERTEK 33 KV SIDE |  | 7216415.4244 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 7216415.4244
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 7216415.4244 |  | 33 KV TX HV SIDE |  | 7121616
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 94799.4244
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.314%
| TOTAL IMPORT |  | 7216415.4244
11 KV SIDE of___AMULIA 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming | 11 |  | HA021100461-02 | 1 | 6544627 | 10126071 | 3581444 | 1 | 3581444 |  | 3674382.5139
11 | 33/11 kV Transformer, T-1 Incoming | 11 |  | HA021100478-02 | 1 | 77520264 | 80972706 | 3452442 | 1 | 3452442 |  | 3542032.9105
[9 empty] | Total | 7033886 |  | 7216415.4244
AMULIA 11 KV SIDE
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 67974785 | 68696773 | 721988 | 1 |  | 721988 | 731782.37 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 731782.37 | 652140.5432 | 79641.8268 | 12.2124 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 10163057 | 11388468 | 1225411 | 1 |  | 1225411 | 1242034.7233 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1242034.7233 | 1238203.4365 | 3831.2868 | 0.30942 | OK
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 66774948 | 67318225 | 543277 | 1 |  | 543277 | 550647.0061 | Demra |  |  |  | 11 kV Paity Feeder | 550647.0061 | 438875.0126 | 111771.9935 | 25.4678 | OK
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 57031355 | 59259140 | 2227785 | 1 |  | 2227785 | 2258006.7634 | Demra |  |  |  | 11 kV Bamuil Feeder | 2258006.7634 | 2467621.492 | -209614.7286 | -8.4946 | OK
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 11924560 | 12956256 | 1031696 | 1 |  | 1031696 | 1045691.8176 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 1045691.8176 | 1243169.2645 | -197477.447 | -15.885 | OK
13 | 11 kV Amulia Model Town Feeder | 11 | Demra |  | 1 | 51179519 | 51323114 | 143595 | 1 |  | 143595 | 145542.9861 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 145542.9861 | 125872.2787 | 19670.7074 | 15.6275 | OK
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 7194545 | 8420622 | 1226077 | 1 |  | 1226077 | 1242709.7581 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1242709.7581 | 1131891.5259 | 110818.2322 | 9.7905 | OK
15 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 | 0.415 |  |  | 1 |  | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 7216415.4244 | 7119829 | 7216415.4244 | 1.3384
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Mugdapara | at 33 KV level |  | 1777474.1875
[5 empty] | Demra | at 33 KV level |  | 5438941.2369
[5 empty] | Total = |  |  | 7216415.4244 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
33 KV SIDE of___Modongonj 132/33 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| MOGBAZAR T&T 11 KV SIDE | [8 empty] | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder | 33 |  | 8993841 | 1 | 39110.871 | 39195.806 | 84.935 | 36000 | 733 | 3057660 | 3058393 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 3058393 | 4554980 | -1496587 | -32.8561 | OK
13 | 33 kV Mondol Para (Premire cement) Feeder | 33 |  | 8993842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total |  | 3057660 | 3058393 | 0.023973
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 3058393
[5 empty] | Total = |  |  | 3058393 | 0

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 | 132 | IMPORT | 50147584 | 1 | 3042.09 | 3087.962 | 45.872 | 1920000 | 0 | 88074240
| Maniknagar-2 | 132 |  | 50147585 | 1 | 3035.644 | 3081.57 | 45.926 | 1920000 | 0 | 88177920
[8 empty] | Total Import/Export |  | 0 | 176252160
[9 empty] | Net Total | 176252160
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 176252160
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 | 132 | EXPORT | 06604331 | 1 | 8751.82 | 8792.35 | 40.53 | 480000 |  | 19454400
| 132 kV Narinda Circuit-2 | 132 |  | 06604334 | 1 | 8761.87 | 8800.57 | 38.7 | 480000 |  | 18576000
| 132kV Motijheel Circuit-1 | 132 |  | 06604332 | 1 | 1786.17 | 1797.51 | 11.34 | 1440000 |  | 16329600
| 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1600.03 | 1609.68 | 9.65 | 1440000 |  | 13896000 |  |  | METER PROBLEM
| 132 kV Kazla Circuit-1 | 132 |  | ABB03905 | 1 | 647990 | 681650 | 33660 | 1000 |  | 33660000
| 132 kV Kazla Circuit-2 | 132 |  | ABB03904 | 1 | 489899 | 514116 | 24217 | 1000 |  | 24217000
[9 empty] | Total |  | 126133000
MANIKNAGAR 132 KV SIDE
9 | 132/33 kV 50/75 MVA GT-1 (HV) | 132 | Export | Nill | 1 |  | 0 | 0 | 1000 |  | 24709000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) | 132 | Export | ABB03903 | 1 | 233736 | 258899 | 25163 | 1000 |  | 25163000 |  |  | 49872000
[9 empty] | Total |  | 49872000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 230/132 KV SIDE (TARIFF POINT) |  | 176252160 |  | EXPORT TO OTHER S/S |  |  | 126133000 |  | 132 KV NET IMPORT |  | 50119160
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 50119160 |  | 33 KV NET IMPORT |  | 49915000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 204160
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.4073%
| 132 KV TOTAL IMPORT |  | 176252160
33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) | 33 | Digital | ABB03907 | 1 | 974286 | 998995 | 24709 | 1000 | 24709000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) | 33 | Digital | ABB03906 | 1 | 140686 | 165892 | 25206 | 1000 | 25206000
[9 empty] | Total | 49915000 |  | 0
MOGBAZAR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 11074975.6644 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK00121 | 1 | 8730.2 | 9651.2 | 921 | 4444 |  | 4092924 | 4118977.441 |  |  |  |  | 0 | 4118977.441 | 4084932.9993 | 34044.4417 | 0.83341 | OK
7 | 33 kV 20/28 MVA Transformer-2 | 33 | Digital | ABB03913 | 1 | 371253 | 374709 | 3456 | 2000 |  | 6912000 | 6955998.2234 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 6955998.2234 | 6643106.9367 | 312891.2867 | 4.71 | OK
| 33 KV Feeders | [7 empty] | Total |  | 11004924 | 11074975.6644 |  |  |  |  | 33 KV Feeders | 11074975.6644 | 10728039.936 | 346935.7284 | 3.2339 | OK
2 |  | 33 | Digital | ABB03916 | 1 |  | 0 | 0 | 2000 |  | 0 | 0 |  | 12016831.5104 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder | 33 |  | DHK86054 | 1 | 2370.66 | 2401.75 | 31.09 | 270000 | Estimated | 6446822.4 | 6487859.5429 |  |  |  |  | 33kV Motijheel-1 Feeder | 6487859.5429 | 5768185.7467 | 719673.7962 | 12.4766 | OK
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | Estimated | 9510736 | 9571276.435 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 9571276.435 | 9453990.4718 | 117285.9632 | 1.2406 | OK
|  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 18946577.2812 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder | 33 | Digital | ABB03918 | 1 | 283353 | 288011 | 4658 | 2000 |  | 9316000 | 9375300.8462 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 9375300.8462 | 8093575.7758 | 1281725.0704 | 15.8363 | OK
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 260650 | 263791 | 3141 | 2000 |  | 6282000 | 6321987.9686 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 6321987.9686 | 7312864.4535 | -990876.4849 | -13.5498 | OK
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 271707 | 274454 | 2747 | 2000 |  | 5494000 | 5528971.9675 |  | 6321987.9686 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 5528971.9675 | 3544469.7503 | 1984502.2172 | 55.9887 | FAULT
12 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 19544 | 20118 | 574 | 2000 |  | 1148000 | 1155307.5753 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 1155307.5753 | 595115.8659 | 560191.7094 | 94.1315 | FAULT
[9 empty] | Total |  | 38197558.4 | 38440704.3356 |  |  |  |  | 0 | 38440704.3356 | 34768202.064 | 3672502.2716 | 10.5628 | OK
[8 empty] | Grand Total |  | 49515680 | 49202482.4 | 49515680 | 0.63655
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 1155307.5753
[5 empty] | Total = |  |  | 1155307.5753 | 0
11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 | 11 | Import | 6604357 | 1 | 5292.17 | 5335.14 | 42.97 | 160000 | 6875200 |  | 6942178.324 |  | 0
9 | 11kV 10/14 MVA Transformer T-1 | 11 | Import | DHK00121 | 1 | 8730.2 | 9651.2 | 921 | 4444 | 4092924 |  | 4132797.3404 |  | Sum of Feeders under T1=
[9 empty] | Total | 10968124 |  | 11074975.6644
MOGBAZAR 11 kV SIDE
1 | 11 kV Nearest Feeder | 11 |  | HA021101060-02 | 1 | 70560333 | 72108037 | 1547704 | 1 |  | 1547704 | 1558145.6337 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1558145.6337 | 1525690.8024 | 32454.8313 | 2.1272 | OK
2 | 11kV Spare | 11 |  | HA021100679-02 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | 11 |  | HA021100937-02 | 1 | 74563517 | 75407218 | 843701 | 1 |  | 843701 | 849393.0553 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 849393.0553 | 840241.579 | 9151.4764 | 1.0891 | OK
4 | 11 kV R K Mission Road Feeder | 11 |  | HA021101035-02 | 1 | 9481733 | 10974303 | 1492570 | 1 |  | 1492570 | 1502639.6704 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1502639.6704 | 1474074.1461 | 28565.5243 | 1.9379 | OK
5 | 11 kV Janapath Feeder | 11 |  | HA021100864-02 | 1 | 21334986 | 23326754 | 1991768 | 1 |  | 1991768 | 2005205.5254 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 2005205.5254 | 1983935.5671 | 21269.9583 | 1.0721 | OK
6 | 11 kV Dhalpur Feeder | 11 |  | HA021100851-02 | 1 | 83588686 | 84442992 | 854306 | 1 |  | 854306 | 860069.6023 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 860069.6023 | 795009.9152 | 65059.687 | 8.1835 | OK
7 | 11kV WTP | 11 |  | X0599387 | 1 | 1261.6 | 1406.5 | 144.9 | 1000 |  | 144900 | 145877.5724 | Maniknagar |  |  |  | 11kV WTP | 145877.5724 | 0 | 145877.5724 | #DIV/0! | #DIV/0!
10 | 11kV Kamalapur Water pumping | 11 |  | HA021100474-02 | 1 | 7604026 | 7628319 | 24293 | 1 |  | 24293 | 24456.8935 | Maniknagar |  |  |  | 11kV Kamalapur Water pumping | 24456.8935 | 21094.6329 | 3362.2606 | 15.9389 | OK
11 | 11 kV Wasa Road Feeder | 11 |  | HA021001011-02 | 1 | 22420806 | 24448123 | 2027317 | 1 |  | 2027317 | 2040994.3579 | Maniknagar |  |  |  | 11 kV Wasa Road Feeder | 2040994.3579 | 2044032.5287 | -3038.1708 | -0.14864 | OK
12 | 11kV Sutikhalpar Feeder | 11 |  | HA021101047-02 | 1 | 76903368 | 78965769 | 2062401 | 1 |  | 2062401 | 2076315.0532 | Maniknagar |  |  |  | 11kV Sutikhalpar Feeder | 2076315.0532 | 2043960.7645 | 32354.2887 | 1.5829 | OK
13 | 11kV Spare | 11 |  | HA021101029-02 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare | 11 |  | Nill | 1 |  | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare | 11 |  | HA021101068-02 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare | 11 |  | HA021101243-02 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare | 11 |  | Nill | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 | 0.415 |  | AH14044078 | 1 | 384321.4 | 384321.4 | 7017.6 | 1 |  | 7017.6 | 7064.9445 | Maniknagar |  |  |  | Axuxilary -1 | 7064.9445 | 0 | 7064.9445 | #DIV/0! | #DIV/0!
| Axuxilary -2 | 0.415 |  | AH14044072 | 1 | 359618.5 | 359618.5 | 4781.1 | 1 |  | 4781.1 | 4813.3558 | Maniknagar |  |  |  | Axuxilary -2 | 4813.3558 | 0 | 4813.3558 | #DIV/0! | #DIV/0!
13 | AT-1 | 0.415 |  | 6603506 | 1 |  | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 11074975.6644 | 11000758.7 | 11074975.6644 | 0.67465
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 11074975.6644
[5 empty] | Total = |  |  | 11074975.6644 | 0
33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder | 33 | 0 | DHK86054 | 1 | 2370.66 | 2401.75 | 31.09 | 270000 | Estimated | 6446822.4 | 6487859.5429
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 271707 | 274454 | 2747 | 2000 | 0 | 5494000 | 5528971.9675
[9 empty] | Total | 0 | 11940822.4 | 12016831.5104
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 | 33 | Import | DHK86054 | 1 | 2370.66 | 2401.75 | 31.09 | 270000 | 8394300 |  |  |  | Reading Mismatch
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) | 33 | Import | DHK68120 | 1 | 2274.38 | 2296.33 | 21.95 | 270000 | 5926500
[9 empty] | Total | 14320800 | 0 | 0
MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S)
1 | 33kV Biddyut Bhaban Circuit | 33 | Import |  | 1 |  | 0 | 0 | 600 | 0
|  | 33 | Export |  | 1 | 454983 | 458833 | 3850 | 600 | Estimated | 5593465.8 |  |  | From Remote End
[9 empty] | Total |  | 5593465.8
MOGBAZAR T&T 33 KV SIDE
4 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK86053 | 1 | 2888.15 | 2908.29 | 20.14 | 180000 |  | 3625200
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) | 33 | Export | DHK86055 | 1 | 2274.38 | 2290.59 | 16.21 | 180000 |  | 2917800
[9 empty] | Total |  | 6543000 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MANIKNAGAR 33 KV SIDE |  | 12016831.5104 |  | EXPORT TO OTHER S/S |  |  | 5593465.8 |  | 33 KV NET IMPORT |  | 6423365.7104
[5 empty] | 33 KV NET IMPORT |  |  | 6423365.7104 |  | 33 KV TX HV SIDE |  | 6543000
[10 empty] | LOSS UNITS=> |  | -119634.2896
[10 empty] | LOSS % IN => |  | -1.862%
| TOTAL IMPORT |  | 12016831.5104
11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 | 11 | Import | DHK86059 | 1 | 3264.9 | 3289.14 | 24.24 | 160000 | 3878400 |  | 4455003.8575 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 | 11 | Import | DHK86057 | 1 | 2542.41 | 2553.12 | 10.71 | 160000 | 1713600 |  | 1968361.8529
[9 empty] | Total | 5592000 |  | 6423365.7104
MOTIJHEEL 11 KV SIDE
6 | 11kV Fakirapul Panir Tank Feeder | 11 |  | DHK86058 | 1 | 1646.88 | 1662.02 | 15.14 | 60000 |  | 908400 | 913140.3988 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 913140.3988 | 912597.457 | 542.9418 | 0.059494 | OK
7 | 11kV Station Road Feeder | 11 |  | DHK86075 | 1 | 2371.1 | 2373.12 | 2.02 | 60000 |  | 121200 | 121832.4707 | Motijheel |  |  |  | 11kV Station Road Feeder | 121832.4707 | 79852.2775 | 41980.1932 | 52.5723 | FAULT
8 | 11kV Box Culvert Road Feeder | 11 |  | DHK86071 | 1 | 3068.01 | 3101.12 | 33.11 | 60000 |  | 1986600 | 1996966.8828 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1996966.8828 | 1747744.2088 | 249222.674 | 14.2597 | OK
9 | 11kV Mohamedan Club Feeder | 11 |  | DHK86062 | 1 | 1631.78 | 1643.91 | 12.13 | 60000 | Import from Narinda | 727800 | 731597.9549 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 731597.9549 | 774507.0523 | -42909.0974 | -5.5402 | OK
10 | 11kV Amina Ahmed Co. | 11 |  | DHK95754 | 1 | 95646 | 97956 | 2310 | 60 | 133686 | 138600 | 139323.2709 | Motijheel |  |  |  | 11kV Amina Ahmed Co. | 139323.2709 | 132686.8671 | 6636.4038 | 5.0016 | OK
11 | 11kV Bangabhaban -1 | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | 11 |  | DHK95753 | 1 | 37569 | 43302 | 5733 | 60 |  | 343980 | 345775.0268 | Motijheel |  |  |  | 11kV Sonali Bank | 345775.0268 | 0 | 345775.0268 | #DIV/0! | #DIV/0!
15 | 11kV NCC Bank Feeder | 11 |  | DHK68123 | 1 | 307.1 | 309.54 | 2.44 | 60000 |  | 146400 | 147163.9744 | Motijheel |  |  |  | 11kV NCC Bank Feeder | 147163.9744 | 129684.9018 | 17479.0727 | 13.4781 | OK
16 | 11kV IFIC BANK Feeder | 11 |  | DHK68116 | 1 | 374.21 | 383.41 | 9.2 | 60000 |  | 552000 | 554880.5594 | Ramna |  |  |  | 11kV IFIC BANK Feeder | 554880.5594 | 383050.7747 | 171829.7847 | 44.8582 | FAULT
17 | 11kV Arambagh Feeder | 11 |  | DHK68117 | 1 | 3346.46 | 3354.56 | 8.1 | 60000 |  | 486000 | 488536.1447 | Motijheel |  |  |  | 11kV Arambagh Feeder | 488536.1447 | 472509.3412 | 16026.8034 | 3.3918 | OK
18 | 11kV Nikotborti Feeder | 11 |  | DHK68114 | 1 | 1385.65 | 1396.51 | 10.86 | 60000 |  | 651600 | 655000.3125 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 655000.3125 | 654428.4396 | 571.8729 | 0.087385 | OK
19 | 11kV Agrani Bank Feeder | 11 |  | DHK95756 | 1 | 354884 | 357283 | 2399 | 60 |  | 143940 | 144691.1372 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 144691.1372 | 141752.8024 | 2938.3348 | 2.0729 | OK
20 | 11kV Bangladesh Bank-2 | 11 |  | DHK95755 | 1 | 512 | 515 | 3 | 60000 |  | 180000 | 180939.3128 | Motijheel |  |  |  | 11kV Bangladesh Bank-2 | 180939.3128 | 0 | 180939.3128 | #DIV/0! | #DIV/0!
21 | 11kV PDB Design Feeder 14 | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT | 0.415 |  | ELIC5429 | 1 | 394002 | 397502 | 3500 | 1 |  | 3500 | 3518.2644 | Motijheel |  |  |  | 11/0.4 kV AT | 3518.2644 | 3474.2745 | 43.9899 | 1.2662 | OK
[9 empty] | Grand Total | 6423365.7104 | 6390020 | 6423365.7104 | 0.52184
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 6002171.151
[5 empty] | Ramna | at 33 KV level |  | 554880.5594
[5 empty] | Total = |  |  | 6557051.7104 | 133686
132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 | 132 | 0 | 06604332 | 1 | 1786.17 | 1797.51 | 11.34 | 1440000 | 0 | 16329600
2 | 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1600.03 | 1609.68 | 9.65 | 1440000 | 0 | 13896000
[8 empty] | Total Import/Export |  | 0 | 30225600
[9 empty] | Net Total | 30225600
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 | 132 | Imp/Main | 41812909527 | 1 | 272.07 | 285.51 | 13.44 | 1200000 | 16128000
|  | 132 | Imp/Backup | 41812909575 | 1 | 272.13 | 285.57 | 13.44 | 1200000 | 16128000
5 | 132 kV Mniknagar Circuit-2 | 132 | Imp/Main | 41812909512 | 1 | 96.02 | 107.49 | 11.47 | 1200000 | 13764000
|  | 132 | Imp/Backup | 41812909591 | 1 | 96.04 | 107.51 | 11.47 | 1200000 | 13764000
[8 empty] | Total Import/Export |  | 29892000 | 0
[8 empty] | Net Total |  | 29892000
MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S)
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 29.97 | 32.12 | 2.15 | 1200000 |  | 2580000
|  | 132 | Exp/Backup | 41812909570 | 1 | 29.95 | 32.1 | 2.15 | 1200000 |  | 2580000
7 | 132 kV Bangabhaban Circuit-2 | 132 | Exp/Main | 41812909559 | 1 | 77.23 | 80.49 | 3.26 | 1200000 |  | 3912000
|  | 132 | Exp/Backup | 41812909569 | 1 | 77.23 | 80.49 | 3.26 | 1200000 |  | 3912000
[9 empty] | Total |  | 6492000
MOTIJHEEL 132 KV SIDE
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41812909509 | 1 | 170.58 | 181.88 | 11.3 | 1200000 |  | 13560000
|  | 132 | Exp/Backup | 41812909594 | 1 | 170.58 | 181.88 | 11.3 | 1200000 |  | 13560000
6 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41812909508 | 1 | 90.33 | 98.54 | 8.21 | 1200000 |  | 9852000
|  | 132 | Exp/Backup | 41812909592 | 1 | 90.31 | 98.51 | 8.2 | 1200000 |  | 9840000
[9 empty] | Total |  | 23412000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE (TARIFF POINT) |  | 30225600 |  | EXPORT TO OTHER S/S |  |  | 6492000 |  | 132 KV NET IMPORT |  | 23733600
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 23733600 |  | 33 KV NET IMPORT |  | 23256000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 477600
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 2.012%
| 132 KV TOTAL IMPORT |  | 30225600
33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41812909543 | 1 | 282.15 | 300.89 | 18.74 | 720000 | 13492800
|  | 33 | Backup | 41812909617 | 1 | 282.35 | 301.1 | 18.75 | 720000 | 13500000
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41812909468 | 1 | 148.78 | 162.34 | 13.56 | 720000 | 9763200
|  | 33 | Backup | 41812909600 | 1 | 148.75 | 162.31 | 13.56 | 720000 | 9763200
[9 empty] | Total | 23256000 |  | 0
MOTIJHEEL 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) | 33 | Main | 41812909546 | 1 | 89.04 | 96.73 | 7.69 | 240000 |  | 1845600 | 1842469.3233 |  | 4506742.2589 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 1842469.3233 | 1838518.869 | 3950.4543 | 0.21487 | OK
|  | 33 | Backup | 41812909616 | 1 | 89.01 | 96.7 | 7.69 | 240000 |  | 1845600 | 1842469.3233 |  |  |  |  | 0 | 1842469.3233 | 1838518.869 | 3950.4543 | 0.21487 | OK
17 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41812909482 | 1 | 167.85 | 178.97 | 11.12 | 240000 |  | 2668800 | 2664272.9356 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2664272.9356 | 2049457.1486 | 614815.787 | 29.999 | OK
|  | 33 | Backup | 42003953371 | 1 | 167.89 | 179.01 | 11.12 | 240000 |  | 2668800 | 2664272.9356 |  |  |  |  | 0 | 2664272.9356 | 2051854.1745 | 612418.7611 | 29.8471 | OK
| 33 KV Feeders | [7 empty] | Total |  | 4514400 | 4506742.2589 |  |  |  |  | 33 KV Feeders | 4506742.2589 | 3887976.0176 | 618766.2413 | 15.9149 | OK
10 | 33 kV Spare Feeder 1 | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 371.51 | 387.88 | 16.37 | 360000 |  | 5893200 | 5883203.4113 |  | 10318067.8033 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 5883203.4113 | 5375330.5916 | 507872.8197 | 9.4482 | OK
|  | 33 | Backup | 41812909610 | 1 | 371.64 | 388.02 | 16.38 | 360000 |  | 5896800 | 5886797.3047 |  |  |  |  | 0 | 5886797.3047 | 5375330.5916 | 511466.7131 | 9.5151 | OK
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 158.01 | 174.02 | 16.01 | 360000 |  | 5763600 | 5753823.2508 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 5753823.2508 | 4857572.9961 | 896250.2546 | 18.4506 | OK
|  | 33 | Backup | 41812909595 | 1 | 158.08 | 174.09 | 16.01 | 360000 |  | 5763600 | 5753823.2508 |  | 8406116.5419 | Kamlapur Railway 33/11 kv ss |  | 0 | 5753823.2508 | 4861168.535 | 892654.7158 | 18.363 | OK
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 49.8 | 57.18 | 7.38 | 360000 |  | 2656800 | 2652293.2911 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 2652293.2911 | 3041825.8732 | -389532.5821 | -12.8059 | OK
|  | 33 | Backup | 41621865733 | 1 | 49.81 | 57.19 | 7.38 | 360000 |  | 2656800 | 2652293.2911 |  |  |  |  | 0 | 2652293.2911 | 3041825.8732 | -389532.5821 | -12.8059 | OK
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 111.56 | 123.9 | 12.34 | 360000 |  | 4442400 | 4434864.3919 |  |  |  |  | 33 kV P & T - 2 Feeder | 4434864.3919 | 4206780.463 | 228083.9289 | 5.4218 | OK
|  | 33 | Backup | 41812909598 | 1 | 111.53 | 123.87 | 12.34 | 360000 |  | 4442400 | 4434864.3919 |  |  |  |  | 0 | 4434864.3919 | 4203184.9241 | 231679.4678 | 5.512 | OK
20 | 33 kV Spare Feeder 9 | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) | 0.415 |  |  | 1 | 869.63 | 953.35 | 83.72 | 300 |  | 25116 | 25073.3959 | [5 empty] | 25073.3959 | 21714.0584
[9 empty] | Total |  | 18781116 | 18749257.7411 |  |  |  |  | 0 | 18749257.7411 | 17503223.9824 | 1246033.7587 | 7.1189 | OK
[8 empty] | Grand Total |  | 23256000 | 23295516 | 23256000 | -0.16963
11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) | 11 |  | 41812909493 | 1 | 84.77 | 92.1 | 7.33 | 250000 | 1832500 |  | 1840357.7024
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) | 11 |  | 41812909496 | 1 | 160.41 | 171.03 | 10.62 | 250000 | 2655000 |  | 2666384.5565
[9 empty] | Total | 4487500 |  | 4506742.2589
MOTIJHEEL 11 kV SIDE
2 | 11 kV Central Weman | 11 |  | 41812909492 | 1 | 117.46 | 126.75 | 9.29 | 60000 |  | 557400 | 559727.7485 | Motijheel |  |  |  | 11 kV Central Weman | 559727.7485 | 557588.8285 | 2138.9199 | 0.3836 | OK
3 | 11 kV Spare Feeder 2 | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len | 11 |  | 41812909499 | 1 | 201.61 | 217.11 | 15.5 | 60000 |  | 930000 | 933883.7569 | Swamibag |  |  |  | 11 kV K. M. Das Len | 933883.7569 | 932508.9216 | 1374.8352 | 0.14743 | OK
5 | 11 kV Gopibag | 11 |  | 41812909517 | 1 | 28.97 | 31.43 | 2.46 | 60000 |  | 147600 | 148216.3898 | Motijheel |  |  |  | 11 kV Gopibag | 148216.3898 | 147332.8161 | 883.5737 | 0.59971 | OK
6 | 11kV SPICE TV | 11 |  | 41812909518 | 1 | 4.24 | 7.5 | 3.26 | 60000 |  | 195600 | 196416.8418 | Narinda |  |  |  | 11kV SPICE TV | 196416.8418 | 185663.3049 | 10753.5369 | 5.792 | OK
7 | 11 kV Spare Feeder 6 | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | 11 |  | 41812909473 | 1 | 341.42 | 358.82 | 17.4 | 60000 |  | 1044000 | 1048359.8303 | Motijheel |  |  |  | 11 kV South Kamlapur | 1048359.8303 | 518060.512 | 530299.3183 | 102.3624 | FAULT
14 | 11 kV Spare Feeder 11 | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | 11 |  | 41812909514 | 1 | 141.42 | 153.52 | 12.1 | 60000 |  | 726000 | 729031.836 | Motijheel |  |  |  | 11 kV Answer Camp | 729031.836 | 722290.1474 | 6741.6886 | 0.93338 | OK
16 | 11 kV Shapla Chattar | 11 |  | 41812909516 | 1 | 106.7 | 116.51 | 9.81 | 60000 |  | 588600 | 591058.0422 | Motijheel |  |  |  | 11 kV Shapla Chattar | 591058.0422 | 486916.9899 | 104141.0523 | 21.3878 | OK
17 | 11 kV Sayedabad | 11 |  | 41812909497 | 1 | 79.57 | 84.55 | 4.98 | 60000 |  | 298800 | 300047.8135 | Swamibag |  |  |  | 11 kV Sayedabad | 300047.8135 | 309638.4794 | -9590.6659 | -3.0974 | OK
22 | 33/0.4 kV Aux Transformer | 0.415 |  | 41901920686 | 1 | 869.63 | 953.35 | 83.72 | 1 |  |  | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 4506742.2589 | 4488000 | 4506742.2589 | 0.41761
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Motijheel | at 33 KV level |  | 3076393.8468
[6 empty] | Swamibag | at 33 KV level |  | 1233931.5704
[6 empty] | Narinda | at 33 KV level |  | 196416.8418
[6 empty] | Total = |  |  | 4506742.2589 | 0
33 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOTIJHEEL 33 KV SIDE
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 371.51 | 387.88 | 16.37 | 360000 | 0 | 5893200 | 5883203.4113
0 | 0 | 33 | Backup | 41812909610 | 1 | 371.64 | 388.02 | 16.38 | 360000 | 0 | 5896800 | 5886797.3047
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 111.56 | 123.9 | 12.34 | 360000 | 0 | 4442400 | 4434864.3919
0 | 0 | 33 | Backup | 41812909598 | 1 | 111.53 | 123.87 | 12.34 | 360000 | 0 | 4442400 | 4434864.3919
[9 empty] | Total | 0 | 10339200 | 10321661.6966
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
5 | 33 kV Bidyut Bhaban Circuit | 33 | Import | BD017079 | 1 | 15736.93 | 15736.93 | 0 | 1000 | 0
|  | 33 | Export | BD017079 | 1 |  |  | 0 | 1000 |  | 0
7 | 33 kV Motijheel Circuit-1 | 33 | Import | BD017081 | 1 | 132983 | 132983 | 0 | 1000 | 0
8 | 33 kV Motijheel Circuit-2 | 33 | Import | BD017082 | 1 | 21371.33 | 21371.33 | 0 | 1000 | 4442400
11 | 33 kV Kamlapur Circuit | 33 | Import | BD017085 | 1 |  |  | 0 | 1000 | 0
|  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
[9 empty] | Total | 4442400 | 0 | 0
MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT | [7 empty] | 0
| Feeder No.2 | 33 | [8 empty] | 0
[9 empty] | Total |  | 0
MOGBAZAR T&T 33 KV SIDE
6 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | BD017080 | 1 | 23602 | 30305 | 6703 | 888.88 |  | 5958162.64 |  |  | % diffn betn 33 kV Impt & 11 kV Impt=
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | BD017084 | 1 | 89871 | 94924 | 5053 | 888.88 |  | 4491510.64
[9 empty] | Total |  | 10449673.28 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MOTIJHEEL 33 KV SIDE |  | 10321661.6966 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10321661.6966
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 10321661.6966 |  | 33 KV TX HV SIDE |  | 10449673.28
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -128011.5834
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -1.24%
| TOTAL IMPORT |  | 10321661.6966
11 KV SIDE of___P & T 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR T&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 | 11 | Import | BD014056 | 1 | 77487.94 | 77487.94 | 0 | 1000 | 5958162.64 |  | 5892792.3246 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | BD014057 | 1 | 79392 | 83870 | 4478 | 1000 | 4478000 |  | 4428869.372
[7 empty] | 0 |  | Total | 10436162.64 |  | 10321661.6966
| MOGBAZAR T&T 11 KV SIDE | [5 empty] | 0
12 | Inner Circular Road Feeder | 11 |  | BD014042 | 1 | 35190 | 37233 | 2043 | 1000 |  | 2043000 | 2028898.6132 | Motijheel |  |  |  | Inner Circular Road Feeder | 2028898.6132 | 1799798.1809 | 229100.4323 | 12.7292 | OK
13 | NSI New Building Expres Feeder | 11 |  | BD013982 | 1 | 8363 | 8779 | 416 | 1000 |  | 416000 | 413128.6457 | Ramna |  |  |  | NSI New Building Expres Feeder | 413128.6457 | 314414.5923 | 98714.0534 | 31.3961 | OK
14 | Police Hospital RMU Feeder | 11 |  | BD014044 | 1 | 2861 | 3030 | 169 | 1000 |  | 169000 | 167833.5123 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 167833.5123 | 147606.6412 | 20226.8711 | 13.7032 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | 11 |  | BD014013 | 1 | 27994 | 29424 | 1430 | 1000 |  | 1430000 | 1420129.7195 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1420129.7195 | 1600953.1621 | -180823.4427 | -11.2947 | OK
17 | Nayapalton Overhead Feeder | 11 |  | BD014014 | 1 | 20656 | 21639 | 983 | 1000 |  | 983000 | 976215.0449 | Ramna |  |  |  | Nayapalton Overhead Feeder | 976215.0449 | 874688.8617 | 101526.1832 | 11.6071 | OK
18 | Masjid Gali Over Head Feeder | 11 |  | BD014016 | 1 | 10972 | 11857 | 885 | 1000 |  | 885000 | 878891.4697 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 878891.4697 | 807737.2732 | 71154.1965 | 8.8091 | OK
19 | Spare Feeder (Feeder-8) | 11 |  | BD014009 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) | 11 |  | BD013988 | 1 | 12.18 | 12.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | 11 |  | BD014015 | 1 | 18883 | 19862 | 979 | 1000 |  | 979000 | 972242.6541 | Ramna |  |  |  | Mid Way Over Head Feeder | 972242.6541 | 882508.3813 | 89734.2728 | 10.1681 | OK
24 | Palton Thana Over Head Feeder | 11 |  | BD014033 | 1 | 18248 | 19551 | 1303 | 1000 |  | 1303000 | 1294006.3108 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1294006.3108 | 1244617.3693 | 49388.9415 | 3.9682 | OK
25 | Police Hospital (South) U/G Feeder 7 | 11 |  | BD014034 | 1 | 11682 | 11851 | 169 | 1000 |  | 169000 | 167833.5123 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 167833.5123 | 144510.7373 | 23322.775 | 16.1391 | OK
26 | China Town Express Feeder | 11 |  | BD013943 | 1 | 5250 | 5536 | 286 | 1000 |  | 286000 | 284025.9439 | Ramna |  |  |  | China Town Express Feeder | 284025.9439 | 295382.9626 | -11357.0187 | -3.8448 | OK
27 | Fakirapul Bazar O/H Feeder | 11 |  | BD014032 | 1 | 23784 | 25196 | 1412 | 1000 |  | 1412000 | 1402253.9607 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1402253.9607 | 1154071.0714 | 248182.8894 | 21.505 | OK
28 | PWD Ouarter (RMU) | 11 |  | BD013937 | 1 | 1714 | 1861 | 147 | 1000 |  | 147000 | 145985.3628 | Motijheel |  |  |  | PWD Ouarter (RMU) | 145985.3628 | 147304.8743 | -1319.5116 | -0.89577 | OK
29 | Postal Quarter RMU | 11 |  | BD013945 | 1 | 2161 | 2327 | 166 | 1000 |  | 166000 | 164854.2192 | Motijheel |  |  |  | Postal Quarter RMU | 164854.2192 | 163893.9202 | 960.299 | 0.58593 | OK
30 | 11/0.4 kV AT-1 | 0.415 |  | DHKH4409 | 1 | 1313 | 1313 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 0 | 4013.3969 | -4013.3969 | -100 | CHECK
31 | 11/0.4 kV AT-2 | 0.415 |  | DHKH4411 | 1 | 400 | 454 | 54 | 100 |  | 5400 | 5362.7276 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 5362.7276 | 609.6299 | 4753.0977 | 779.6694 | FAULT
[9 empty] | Grand Total | 10321661.6966 | 10393400 | 10321661.6966 | -0.69023
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 3741992.1559
[5 empty] | Ramna | at 33 KV level |  | 3524503.7583
[5 empty] | Rajarbag | at 33 KV level |  | 3055165.7825
[5 empty] | Total = |  |  | 10321661.6966 | 0
33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MOGBAZAR 33 KV SIDE
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 158.01 | 174.02 | 16.01 | 360000 | 0 | 5763600 | 5753823.2508
0 | 0 | 33 | Backup | 41812909595 | 1 | 158.08 | 174.09 | 16.01 | 360000 | 0 | 5763600 | 5753823.2508
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 49.8 | 57.18 | 7.38 | 360000 | 0 | 2656800 | 2652293.2911
0 | 0 | 33 | Backup | 41621865733 | 1 | 49.81 | 57.19 | 7.38 | 360000 | 0 | 2656800 | 2652293.2911
[9 empty] | Total | 0 | 8420400 | 8406116.5419
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
2 | 33 kV Motijheel Circuit-1 | 33 | Import | 101 | 1 | 210.1 | 231.8 | 21.7 | 270000 | 5859000
3 | 33 kV P&T Circuit | 33 | Import | 102 | 1 |  | 0 | 0 | 270000 | 0
6 | 33 kV Motijheel Circuit-2 | 33 | Import | 113 | 1 | 66.2 | 76.2 | 10 | 270000 | 2700000
[9 empty] | Total | 8559000 | 0 | 0
MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S)
[9 empty] | Total | 0 | 0
MOGBAZAR T&T 33 KV SIDE
1 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | 103 | 1 | 229.3 | 253.6 | 24.3 | 240000 |  | 5832000 |  |  | #VALUE!
4 | 33 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | 104 | 1 | 81.4 | 92.7 | 11.3 | 240000 |  | 2712000 |  |  | #VALUE!
[9 empty] | Total |  | 8544000 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| MOGBAZAR 33 KV SIDE |  | 8406116.5419 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 8406116.5419
[5 empty] | 33 KV NET IMPORT |  |  | 8406116.5419 |  | 33 KV TX HV SIDE |  | 8544000
[10 empty] | LOSS UNITS=> |  | -137883.4581
[10 empty] | LOSS % IN => |  | -1.64%
| TOTAL IMPORT |  | 8406116.5419
11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | 42 | 1 | 272.1 | 301.8 | 29.7 | 200000 | 5940000 |  | 5860602.3778 |  | 0
10 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | 64 | 1 | 96.3 | 109.2 | 12.9 | 200000 | 2580000 |  | 2545514.1641 |  | 7716000
[9 empty] | Total | 8520000 |  | 8406116.5419
KAMALAPUR RAILWAY 11 KV SIDE
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 283.3 | 315.7 | 32.4 | 40000 |  | 1296000 | 1302977.567 | Rajarbag |  |  |  | Amtola O/H Feeder | 1302977.567 | 1112515.3567 | 190462.2103 | 17.12 | OK
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 48.6 | 53.6 | 5 | 40000 |  | 200000 | 201076.785 | Rajarbag |  |  |  | Police Telecom | 201076.785 | 151893.2406 | 49183.5444 | 32.3803 | OK
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 202.7 | 221 | 18.3 | 40000 |  | 732000 | 735941.0332 | Rajarbag |  |  |  | Railway Colony O/H | 735941.0332 | 792307.9847 | -56366.9515 | -7.1143 | OK
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 510.7 | 562.4 | 51.7 | 40000 |  | 2068000 | 2079133.9572 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 2079133.9572 | 1572300.3012 | 506833.656 | 32.2352 | OK
5 | 11 KV Majar Feeder | 11 |  | 96 | 1 | 12.6 | 22.1 | 9.5 | 40000 |  | 380000 | 382045.8916 | Motijheel |  |  |  | 11 KV Majar Feeder | 382045.8916 | 369470.0447 | 12575.8469 | 3.4038 | OK
7 | 11 kV Feeder-6 | 11 |  | 11 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 253.2 | 278.1 | 24.9 | 40000 |  | 996000 | 1001362.3894 | Rajarbag |  |  |  | Momenbagh O/H | 1001362.3894 | 821044.5437 | 180317.8458 | 21.962 | OK
9 | 11 kV Feeder-8 | 11 |  | 179 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 181.8 | 190.2 | 8.4 | 40000 |  | 336000 | 337808.9988 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 337808.9988 | 336628.2629 | 1180.7359 | 0.35075 | OK
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 188.7 | 198.7 | 10 | 40000 |  | 400000 | 402153.5701 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 402153.5701 | 406417.0491 | -4263.4791 | -1.049 | OK
13 | 11 kV Feeder-11 | 11 |  | 92 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 42.6 | 48 | 5.4 | 40000 |  | 216000 | 217162.9278 | Motijheel |  |  |  | Dhaka Railway | 217162.9278 | 197050.6905 | 20112.2373 | 10.2066 | OK
15 | Jasimuddin Feeder-13 | 11 |  | 91 | 1 | 44.5 | 71.8 | 27.3 | 40000 |  | 1092000 | 1097879.2463 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1097879.2463 | 1527142.8513 | -429263.605 | -28.1089 | OK
16 | Police Box Feeder-14 | 11 |  | 18 | 1 | 20.4 | 36.4 | 16 | 40000 |  | 640000 | 643445.7121 | Motijheel |  |  |  | Police Box Feeder-14 | 643445.7121 | 607572.9623 | 35872.7498 | 5.9043 | OK
17 | 11 kV Feeder-15 | 11 |  | 171 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 | 11 |  | 204 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) | 0.415 |  | DHKF 7632 | 1 | 736.86 | 787.87 | 51.01 | 100 |  | 5101 | 5128.4634 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 5128.4634 | 5055.5818 | 72.8816 | 1.4416 | OK
20 | Auxiliary -1 (AT-2 ) | 0.415 |  | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 8406116.5419 | 8361101 | 8406116.5419 | 0.53839
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Rajarbag | at 33 KV level |  | 6065582.7642
[5 empty] | Motijheel | at 33 KV level |  | 2340533.7777
[5 empty] | Total = |  |  | 8406116.5419 | 0
132 KV SIDE of___ BANGABHABAN 132/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 29.97 | 32.12 | 2.15 | 1200000 | 0 | 2580000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 | 132 |  | 41812909559 | 1 | 77.23 | 80.49 | 3.26 | 1200000 | 0 | 3912000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
[9 empty] | Total | 0 | 6492000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
[9 empty] | Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
BANGABHABAN 33 KV SIDE
|  | 132 | NET IMPORT | [7 empty] | 0
|  | 132 | [8 empty] | 0
[9 empty] | Total |  | 0 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 132 KV SIDE MOTIJHEEL (SENDING) |  | 6492000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 6492000
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 6492000 |  | 33 KV TX HV SIDE |  | 6492000
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 0
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 6492000
11 KV SIDE of___BANGABHABAN 132/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) | 11 | Import | 4150744 | 1 | 1505518.1 | 1509378.4 | 3860.3 | 1000 | 3860300 |  | 4910083.7774
12 | 11 kV 28/35 MVA Transformer (GT-1) | 11 | Import | 4150742 | 1 | 1432174.3 | 1433418 | 1243.7 | 1000 | 1243700 |  | 1581916.2226
[9 empty] | Total | 5104000 |  | 6492000
BANGABHABAN 11 KV SIDE
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 211876.16 | 212943.22 | 1067.06 | 1000 | Estimated | 851429.88 | 860468.6016 | Motijheel | 70 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 860468.6016 | 817672.1758 | 42796.4258 | 5.2339 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 23888.8 | 23966.99 | 78.19 | 1000 |  | 78190 | 79020.0597 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 79020.0597 | 96954.7119 | -17934.6521 | -18.498 | OK
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 76839.23 | 77077.43 | 238.2 | 1000 |  | 238200 | 240728.715 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 240728.715 | 895179.88 | -654451.165 | -73.1083 | CHECK
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33812.48 | 33826.28 | 13.8 | 1000 | Estimated | 20000 | 20212.3186 | Ramna |  |  |  | 11 kV Osmani Feeder | 20212.3186 | 20167.3868 | 44.9319 | 0.22279 | OK
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 729797.04 | 737544.5157 | Motijheel | 60 | Meter Bad |  | 11 kV Modhumita via Ovisar | 737544.5157 | 685789.5668 | 51754.9489 | 7.5468 | OK
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15585.07 | 15661.1 | 76.03 | 1000 |  | 76030 | 76837.1293 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 76837.1293 | 61066.8471 | 15770.2822 | 25.8246 | OK
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 243118.01 | 244322.7 | 1204.69 | 1000 |  | 1204690 | 1217478.907 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1217478.907 | 1025330.1105 | 192148.7966 | 18.7402 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 13970.19 | 14139.81 | 169.62 | 1000 |  | 169620 | 171420.6744 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 171420.6744 | 190117.955 | -18697.2806 | -9.8346 | OK
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94891.92 | 94891.92 | 0 | 1000 | Estimated | 243265.68 | 245848.1719 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 245848.1719 | 131882.609 | 113965.5629 | 86.4144 | FAULT
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 162808.9 | 163076.15 | 267.25 | 1000 |  | 267250 | 270087.1078 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 270087.1078 | 239598.6384 | 30488.4694 | 12.7248 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20422.03 | 20481.33 | 59.3 | 1000 | Estimated | 243265.68 | 245848.1719 | Motijheel | 20 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 245848.1719 | 131882.609 | 113965.5629 | 86.4144 | FAULT
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82187.62 | 82365.95 | 178.33 | 1000 | Estimated | 364898.52 | 368772.2578 | Motijheel | 30 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 368772.2578 | 369271.3052 | -499.0474 | -0.13514 | OK
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 121941.84 | 122251.69 | 309.85 | 1000 |  | 309850 | 313139.3465 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 313139.3465 | 277311.6517 | 35827.6948 | 12.9197 | OK
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 270703.01 | 271490.95 | 787.94 | 1000 |  | 787940 | 796304.7174 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 796304.7174 | 732691.2448 | 63613.4726 | 8.6822 | OK
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 79173.42 | 79642.9 | 469.48 | 1000 |  | 469480 | 474463.9677 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 474463.9677 | 286770.1561 | 187693.8116 | 65.451 | FAULT
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192152.04 | 192345.5 | 193.46 | 1000 | Estimated | 364898.52 | 368772.2578 | Motijheel | 30 | Meter Bad |  | 11 kV BCIC Feeder | 368772.2578 | 369271.3052 | -499.0474 | -0.13514 | OK
23 | 11/0.4 kV AT-1 | 0.415 |  | 63412931 | 1 | 63258 | 63258 | 0 | 1 |  | 0 | 0 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV AT-2 | 0.415 |  | 63403117 | 1 | 7498 | 13772 | 6274 | 1 | Estimated | 5000 | 5053.0797 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5053.0797 | 5041.8467 | 11.233 | 0.22279 | OK
[9 empty] | Grand Total | 6492000 | 6423805.32 | 6492000 | 1.0616
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 0
[5 empty] | Ramna | at 33 KV level |  | 20212.3186
[5 empty] | Swamibag | at 33 KV level |  | 0
[5 empty] | Motijheel | at 33 KV level |  | 6471787.6814
[5 empty] | Total = |  |  | 6492000 | 0
132 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
MANIKNAGAR 132 KV SIDE
1 | 132 kV Maniknagar Circuit-1 at Maniknagar | 132 | Import | 06604331 | 1 | 8751.82 | 8792.35 | 40.53 | 480000 | 19454400
2 | 132 kV Maniknagar Circui-2 at Maniknagar | 132 | Import | 06604334 | 1 | 8761.87 | 8800.57 | 38.7 | 480000 | 18576000
[8 empty] | Total Import/Export |  | 38030400 | 0
[9 empty] | Net Total | 38030400
NARINDA 132 KV SIDE (RECEIVING)
[8 empty] | Total Import/Export |  | 0 | 0
[8 empty] | Net Total |  | 38030400
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT | [7 empty] | 0
| Feeder No.2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 0
NARINDA 132 KV SIDE
| 132/33 KV GT-1 | 132 | NET IMPORT | [7 empty] | 0
| 132/33 KV GT-2 | 132 | [8 empty] | 0
[9 empty] | Total |  | 38030400
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| MANIKNAGAR 132 KV SIDE |  | 38030400 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 38030400
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 38030400 |  | 33 KV NET IMPORT |  | 37939200
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 91200
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.2398%
| 132 KV TOTAL IMPORT |  | 38030400
33 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming | 33 | Import | 06604301 | 1 | 9126.46 | 9167 | 40.54 | 480000 | 19459200
7 | 132/33 kV 50/75 MVA GT-2 Incoming | 33 | Import | 06604304 | 1 | 8952.64 | 8991.14 | 38.5 | 480000 | 18480000
[9 empty] | Total | 37939200 |  | 0
NARINDA 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 | 33 | Export | 06604300 | 1 | 9574.82 | 9620.96 | 46.14 | 180000 |  | 8305200 | 8311261.3129 |  | 16577489.7839 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 8311261.3129 | 7438811.5739 | 872449.739 | 11.7283 | OK
8 | 33 kV 20/28 MVA Transformer T-4 | 33 | Export | 06604303 | 1 | 9704.39 | 9750.28 | 45.89 | 180000 |  | 8260200 | 8266228.471 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 8266228.471 | 8814038.9432 | -547810.4722 | -6.2152 | OK
| 33 KV Feeders | [7 empty] | Total |  | 16565400 | 16577489.7839 |  |  |  |  | 33 KV Feeders | 16577489.7839 | 16252850.5171 | 324639.2668 | 1.9974 | OK
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | ESTIMATED | 1556900.352 | 1558036.6112 |  | 1558036.6112 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 1558036.6112 | 1500133.9681 | 57902.6432 | 3.8598 | OK
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 9460530.4625 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5592.87 | 5618.07 | 25.2 | 180000 |  | 4536000 | 4539310.47 |  |  |  |  | 33 kV Kumertully-1 Feeder | 4539310.47 | 4233543.0779 | 305767.3921 | 7.2225 | OK
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5442.4 | 5474.62 | 32.22 | 180000 |  | 5799600 | 5803832.6724 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 5803832.6724 | 5313950.4622 | 489882.2102 | 9.2188 | OK
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder | 33 | Export | 06604328 | 1 |  | 0 | 0 | 180000 | Estimated SS End | 9453631 | 9460530.4625 |  | 10343143.1424 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 9460530.4625 | 9227521.9748 | 233008.4877 | 2.5251 | OK
[9 empty] | Total |  | 21346131.352 | 21361710.2161 |  |  |  |  | 0 | 21361710.2161 | 20275149.4829 | 1086560.7332 | 5.3591 | OK
[8 empty] | Grand Total |  | 37939200 | 37911531.352 | 37939200 | 0.072982
11 KV SIDE of___NARINDA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming | 11 | Import | 06604351 | 1 | 10767.44 | 10819.45 | 52.01 | 160000 | 8321600 |  | 8325562.4146 |  | 0
9 | 33/11 kV 20/28 MVA T-4 Incoming | 11 | Import | 06604295 | 1 | 11099.51 | 11151.06 | 51.55 | 160000 | 8248000 |  | 8251927.3693
[9 empty] | Total | 16569600 |  | 16577489.7839
NARINDA 11 kV SIDE
1 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24339 | 24474.94 | 135.94 | 8000 |  | 1087520 | 1096395.2732 | Narinda |  |  |  | 11 kV Bonogram Feeder | 1096395.2732 | 1053258.8812 | 43136.392 | 4.0955 | OK
2 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16479.22 | 16557.29 | 78.07 | 8000 | Export to Motijheel | 624560 | 629657.0471 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 629657.0471 | 766955.5711 | -137298.5241 | -17.9018 | OK
3 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 458.94 | 471.15 | 12.21 | 40000 | 133686 | 488400 | 492385.8425 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 492385.8425 | 442505.2562 | 49880.5863 | 11.2723 | OK
4 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5447.36 | 5473.81 | 26.45 | 40000 |  | 1058000 | 1066634.3599 | Narinda |  |  |  | 11 kV Manashi Feeder | 1066634.3599 | 1004671.6435 | 61962.7164 | 6.1675 | OK
5 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3275.98 | 3323.44 | 47.46 | 40000 |  | 1898400 | 1913892.8816 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 1913892.8816 | 0 | 1913892.8816 | #DIV/0! | #DIV/0!
6 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8439.28 | 8477.29 | 38.01 | 40000 |  | 1520400 | 1532808.0158 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1532808.0158 | 1743117.3478 | -210309.332 | -12.0651 | OK
7 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7184.27 | 7223.58 | 39.31 | 40000 |  | 1572400 | 1585232.3889 | Narinda |  |  |  | 11 kV Narinda Feeder | 1585232.3889 | 1548768.3968 | 36463.9921 | 2.3544 | OK
10 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5901.12 | 5932.66 | 31.54 | 40000 |  | 1261600 | 1271895.9437 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1271895.9437 | 1275716.1516 | -3820.2079 | -0.29946 | OK
11 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 4954.3 | 4979.47 | 25.17 | 40000 |  | 1006800 | 1015016.5156 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 1015016.5156 | 986200.4622 | 28816.0534 | 2.9219 | OK
12 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7712.97 | 7734.95 | 21.98 | 40000 |  | 879200 | 886375.1694 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 886375.1694 | 853288.2663 | 33086.903 | 3.8776 | OK
13 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6292.41 | 6319.72 | 27.31 | 40000 |  | 1092400 | 1101315.099 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 1101315.099 | 1011899.497 | 89415.602 | 8.8364 | OK
14 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 1622653.122 | -1622653.122 | -100 | CHECK
15 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 18538.4 | 22163.2 | 3624.8 | 444.44 |  | 1611006.112 | 1624153.5662 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1624153.5662 | 1719899.6311 | -95746.0649 | -5.567 | OK
16 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 364417 | 374036 | 9619 | 80 |  | 769520 | 775800.0686 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 775800.0686 | 757318.4331 | 18481.6355 | 2.4404 | OK
17 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 27129.7 | 29470.6 | 2340.9 | 444.44 |  | 1040389.596 | 1048880.237 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 1048880.237 | 947597.8174 | 101282.4195 | 10.6883 | OK
18 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 35150.8 | 35683.5 | 532.7 | 1000 |  | 532700 | 537047.3757 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 537047.3757 | 519000.0396 | 18047.3361 | 3.4773 | OK
1 | 11/0.4 kV Aux Transformer-1 | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 16577489.7839 | 16443295.708 | 16577489.7839 | 0.8161
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Narinda | at 33 KV level |  | 10712549.524
[5 empty] | Maniknagar | at 33 KV level |  | 492385.8425
[5 empty] | Swamibag | at 33 KV level |  | 5238868.4174
[5 empty] | Total = |  |  | 16443803.7839 | -133686
33 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5592.87 | 5618.07 | 25.2 | 180000 | 0 | 4536000 | 4539310.47
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5442.4 | 5474.62 | 32.22 | 180000 | 0 | 5799600 | 5803832.6724
| MITFORD 33 KV SIDE | [9 empty] | 10335600 | 10343143.1424
1 | Kumartuly Circuit-1 | 33 | 0 | DHK-66493 | 1 | 1284424 | 1284426 | 2 | 180 | 0 | 360 | 360
6 | Kumartuly Circuit-2 | 33 | 0 | DHK-60914 | 1 | 759323.6 | 759468.5 | 144.9 | 180 | 0 | 26082 | 26082
[9 empty] | Total |  | 26442 | 26442
KUMERTULY 33 KV SIDE (RECEIVING)
5 | 33 kV Mitford Circuit-1 | 33 | Import | DHK60965 | 1 | 278764.4 | 278764.4 | 0 | 180 | 0
6 | 33 kV Narinda Circuit-1 | 33 | Import | DHK60959 | 1 | 956971.8 | 965418 | 8446.2 | 540 | 4560948
9 | 33 kV Mitford Circuit-2 | 33 | Import | DHK86072 | 1 | 1760.38 | 1760.52 | 0.14 | 180000 | 25200
10 | 33 kV Narinda Circuit-2 | 33 | Import | DHK60957 | 1 | 860727.8 | 871496.3 | 10768.5 | 540 | 5814990
[9 empty] | Total | 10401138 | 0 | 0
KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
KUMERTULY 33 KV SIDE
7 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK60960 | 1 | 1044895.6 | 1044895.6 | 0 | 180 |  | 0
8 | 33/11 kV 20/28 MVA Transformer (T-2) | 33 | Export | DHK60958 | 1 | 196410.5 | 228896.8 | 32486.3 | 180 |  | 5847534
[9 empty] | Total |  | 5847534 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 10343143.1424 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 10369585.1424
| MITFORD 33 KV SIDE |  | 26442 |  | 33 KV NET IMPORT |  |  | 10369585.1424 |  | 33 KV TX HV SIDE |  | 10401138
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -31552.8576
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.3043%
| TOTAL IMPORT |  | 10369585.1424
11 KV SIDE of___KUMERTULY 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming | 11 | Import | 06604403 | 1 | 7218.48 | 7218.92 | 0.44 | 160000 | 70400 |  | 468922.658 |  | 0
20 | 33/11 kV 20/28 MVA T-2 Incoming | 11 | Import | 06604410 | 1 | 6582.85 | 6592.14 | 9.29 | 160000 | 1486400 |  | 9900662.4843 |  |  | PT Damage
[9 empty] | Total | 1556800 |  | 10369585.1424
KUMERTULY 11 KV SIDE
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62075.6 | 62100 | 24.4 | 2222.22 | Estimated | 547347.78 | 555416.4351 | Banglabazar | 45 |  |  | 11kV Babubazar Feeder | 555416.4351 | 531951.745 | 23464.6901 | 4.4111 | OK
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4531.23 | 4531.4 | 0.17 | 40000 | Estimated | 1459594.08 | 1481110.4937 | Banglabazar | 120 |  |  | 11kV Islampur Feeder | 1481110.4937 | 1418537.9868 | 62572.5069 | 4.4111 | OK
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5121.34 | 5121.51 | 0.17 | 40000 | Estimated | 486531.36 | 493703.4979 | Banglabazar | 40 |  |  | 11kV Majar O/H Feeder | 493703.4979 | 354634.4967 | 139069.0012 | 39.2147 | OK
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 |  | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5393.27 | 5393.48 | 0.21 | 40000 | Estimated | 1398777.66 | 1419397.5564 | Banglabazar | 115 |  |  | 11kV Sadarghat Feeder | 1419397.5564 | 1418537.9868 | 859.5696 | 0.060595 | OK
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal | NO LOAD |  |  | 11kV Mitford Hospital Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4023.81 | 4023.81 | 0 | 40000 | Estimated | 729797.04 | 740555.2468 | Banglabazar | 60 |  |  | 11kV Zindabahar Feeder | 740555.2468 | 709268.9934 | 31286.2534 | 4.4111 | OK
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 912246.3 | 925694.0585 | Banglabazar | 75 |  |  | 11kV Police fari Feeder | 925694.0585 | 803838.1925 | 121855.866 | 15.1593 | OK
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5828.13 | 5853.24 | 25.11 | 40000 |  | 1004400 | 1019206.2302 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 1019206.2302 | 948430.0255 | 70776.2046 | 7.4625 | OK
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8050.6 | 8098.57 | 47.97 | 40000 |  | 1918800 | 1947085.7372 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 1947085.7372 | 1814108.4266 | 132977.3106 | 7.3302 | OK
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3726.07 | 3736.6 | 10.53 | 40000 |  | 421200 | 427409.0643 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 427409.0643 | 290835.8062 | 136573.258 | 46.9589 | FAULT
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7144.81 | 7172.56 | 27.75 | 40000 | Estimated | 1058205.708 | 1073805.1079 | Banglabazar | 87 |  |  | 11kV Dholaikhal Feeder | 1073805.1079 | 1063903.4901 | 9901.6178 | 0.93069 | OK
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3565.38 | 3572.31 | 6.93 | 40000 |  | 277200 | 281286.3072 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 281286.3072 | 235801.9589 | 45484.3483 | 19.2892 | OK
27 | 11/0.4 kV AT-1 | 0.415 |  | 05379603 | 1 |  | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 | 0.415 |  | 05378636 | 1 | 160585.6 | 163007.6 | 2422 | 2 |  | 4844 | 4915.4072 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 4915.4072 | 5104.8915 | -189.4843 | -3.7118 | OK
[9 empty] | Grand Total | 10369585.1424 | 10218943.928 | 10369585.1424 | 1.4741
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 0
[5 empty] | Banglabazar | at 33 KV level |  | 10369585.1424
[5 empty] | Total = |  |  | 10369585.1424 | 0
33 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 9453631 | 9460530.4625
[9 empty] | Total | 0 | 9453631 | 9460530.4625
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 | 33 | Import | Mat-152447/1191738/007 | 1 | 107970100 | 111908100 | 3938000 | 1 | 3938000
5 | 33 kV Narinda Circuit-2 | 33 | Import | Mat-152447/1191738/002 | 1 | 216495100 | 221969900 | 5474800 | 1 | 5474800
[9 empty] | Total | 9412800 | 0 | 0
MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
MOGBAZAR T&T 33 KV SIDE
3 | 33/11 kV 28/35 MVA Transformer (T-1) | 33 | Export | Mat-152447/1191738/009 | 1 | 115091600 | 119054000 | 3962400 | 1 |  | 3962400 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) | 33 | Export | Mat-152447/1191738/004 | 1 | 214005800 | 219485000 | 5479200 | 1 |  | 5479200 |  |  | #VALUE!
[9 empty] | Total |  | 9441600 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| NARINDA 33 KV SIDE |  | 9460530.4625 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 9460530.4625
[5 empty] | 33 KV NET IMPORT |  |  | 9460530.4625 |  | 33 KV TX HV SIDE |  | 9441600
[10 empty] | LOSS UNITS=> |  | 18930.4625
[10 empty] | LOSS % IN => |  | 0.2001%
| TOTAL IMPORT |  | 9460530.4625
11 KV SIDE of___BANGSHAL 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 | 11 | Import | 340180016886 | 1 | 115120992 | 119075109 | 3954117 | 1 | 3954117 |  | 3957002.7993 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 | 11 | Import | 340180012685 | 1 | 217271774 | 222771288 | 5499514 | 1 | 5499514 |  | 5503527.6632
[9 empty] | Total | 9453631 |  | 9460530.4625
BANGSHAL 11 KV SIDE
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 36098890 | 36815436 | 716546 | 1 |  | 716546 | 716311.3918 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 716311.3918 | 731597.9901 | -15286.5982 | -2.0895 | OK
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 45513090 | 46867285 | 1354195 | 1 |  | 1354195 | 1353751.6158 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1353751.6158 | 1239436.4001 | 114315.2156 | 9.2232 | OK
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 18444117 | 19159807 | 715690 | 1 |  | 715690 | 715455.6721 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 715455.6721 | 673745.5603 | 41710.1118 | 6.1908 | OK
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 42091960 | 43501879 | 1409919 | 1 |  | 1409919 | 1409457.3709 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1409457.3709 | 1554740.9811 | -145283.6102 | -9.3446 | OK
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 58774329 | 59902495 | 1128166 | 1 |  | 1128166 | 1127796.6211 | Bangshal |  |  |  | 11 kV French Road Feeder | 1127796.6211 | 1053176.4841 | 74620.137 | 7.0852 | OK
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 25877226 | 27364546 | 1487320 | 1 |  | 1487320 | 1486833.0286 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 1486833.0286 | 1422838.9992 | 63994.0294 | 4.4976 | OK
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 58169790 | 59668688 | 1498898 | 1 |  | 1498898 | 1498407.2378 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1498407.2378 | 1491420.5994 | 6986.6384 | 0.46846 | OK
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 46714704 | 47860599 | 1145895 | 1 |  | 1145895 | 1145519.8164 | Narinda |  |  |  | 11 kV Suritolla Feeder | 1145519.8164 | 1053573.9718 | 91945.8446 | 8.727 | OK
13 | AT-1 | 0.415 |  | DHK-4415 | 1 | 649.28 | 685.05 | 35.77 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 | 0.415 |  | DHK-4410 | 1 | 658.98 | 658.98 | 0 | 100 |  | 7000 | 6997.7081 | Bangshal |  |  |  | AT-2 | 6997.7081 | 6990.9888 | 6.7193 | 0.096114 | OK
[9 empty] | Grand Total | 9460530.4625 | 9463629 | 9460530.4625 | -0.032742
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 6961259.0304
[5 empty] | Banglabazar | at 33 KV level |  | 1353751.6158
[5 empty] | Narinda | at 33 KV level |  | 1145519.8164
[5 empty] | Total = |  |  | 9460530.4625 | 0
132 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDING)
1 | 132kV Kazla Circuit-1 at Maniknagar | 132 | Import | ABB03905 | 1 | 647990 | 681650 | 33660 | 1000 | 33660000 |  |  |  | 132 kV line Loss=
2 | 132kV Kazla Circuit-2 at Maniknagar | 132 | Import | ABB03904 | 1 | 489899 | 514116 | 24217 | 1000 | 24217000 |  |  |  | 100
[8 empty] | Total Import/Export |  | 57877000 | 0
[9 empty] | Net Total | 57877000
KAZLA 132 KV SIDE (RECEIVING)
3 | 132kV Maniknagar Circuit-1 | 132 | Main | 41812909505 | 1 | 540.28 | 568.24 | 27.96 | 1200000 | 33552000
|  | 132 | Backup | 41812909603 | 1 | 540.26 | 568.22 | 27.96 | 1200000 | 33552000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 | 132 | Main | 41812909540 | 1 | 407.41 | 427.53 | 20.12 | 1200000 | 24144000
|  | 132 | Backup | 41812909587 | 1 | 407.42 | 427.54 | 20.12 | 1200000 | 24144000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
[8 empty] | Total Import/Export |  | 57696000 | 0
[8 empty] | Net Total |  | 57696000
KAZLA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
KAZLA 132 KV SIDE
4 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Main | 41812909542 | 1 | 540.64 | 568.57 | 27.93 | 1200000 |  | 33516000 |  |  | #DIV/0!
|  | 132 | Backup | 41812909589 | 1 | 540.95 | 568.9 | 27.95 | 1200000 |  | 33540000
7 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Main | 41812909501 | 1 | 407.26 | 427.37 | 20.11 | 1200000 |  | 24132000 |  |  | 100
|  | 132 | Backup | 41812909606 | 1 | 407.21 | 427.32 | 20.11 | 1200000 |  | 24132000
[9 empty] | Total |  | 57648000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 57877000 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 57877000
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 57877000 |  | 33 KV NET IMPORT |  | 57549600
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 327400
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.5657%
| 132 KV TOTAL IMPORT |  | 57877000
33 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) | 33 | Main | 41812909533 | 1 | 897.39 | 943.91 | 46.52 | 720000 | 33494400
|  | 33 | Backup | 41812909582 | 1 | 897.45 | 943.98 | 46.53 | 720000 | 33501600
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) | 33 | Main | 41812909479 | 1 | 676.57 | 709.98 | 33.41 | 720000 | 24055200
|  | 33 | Backup | 41812909622 | 1 | 676.48 | 709.89 | 33.41 | 720000 | 24055200
[9 empty] | Total | 57549600 |  | 0
KAZLA 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 | 33 | Main | 41812909465 | 1 | 894.53 | 942.09 | 47.56 | 240000 |  | 11414400 | 11426857.287 |  | 38195639.9748 | Kazla 33/11 kv ss | 1.6954 | 33/11 kV 20/28 MVA T-1 | 11426857.287 | 10882650.8914 | 544206.3956 | 5.0007 | OK
|  | 33 | Backup | 41812909596 | 1 | 894.3 | 941.85 | 47.55 | 240000 |  | 11412000 | 11424454.6677 |  |  |  |  | 0 | 11424454.6677 | 10880259.1 | 544195.5677 | 5.0017 | OK
13 | 33/11 kV 28/35 MVA T-5 | 33 | Main | 41812909536 | 1 | 86.92 | 94.27 | 7.35 | 360000 |  | 2646000 | 2648887.7542 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 2648887.7542 | 3171515.4026 | -522627.6484 | -16.4788 | OK
|  | 33 | Backup | 41812909578 | 1 | 86.93 | 94.28 | 7.35 | 360000 |  | 2646000 | 2648887.7542 |  |  |  |  | 0 | 2648887.7542 | 3171515.4026 | -522627.6484 | -16.4788 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 | Main | 41812909554 | 1 | 910.29 | 953.56 | 43.27 | 240000 |  | 10384800 | 10396133.6167 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 10396133.6167 | 10258393.3348 | 137740.2819 | 1.3427 | OK
|  | 33 | Backup | 41812909613 | 1 | 909.41 | 952.62 | 43.21 | 240000 |  | 10370400 | 10381717.901 |  |  |  |  | 0 | 10381717.901 | 10251217.9606 | 130499.9404 | 1.273 | OK
17 | 33/11 kV 20/28 MVA T-3 | 33 | Main | 41812909544 | 1 | 803.06 | 836.01 | 32.95 | 240000 |  | 7908000 | 7916630.5216 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 7916630.5216 | 7318881.6984 | 597748.8232 | 8.1672 | OK
|  | 33 | Backup | 41812909614 | 1 | 803.08 | 836.04 | 32.96 | 240000 |  | 7910400 | 7919033.1409 |  |  |  |  | 0 | 7919033.1409 | 7321273.4898 | 597759.6511 | 8.1647 | OK
22 | 33/11 kV 10/14 MVA T-4 | 33 | Main | 41812909506 | 1 | 403.91 | 428.08 | 24.17 | 240000 |  | 5800800 | 5807130.7954 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 5807130.7954 | 4800325.3492 | 1006805.4461 | 20.9737 | OK
|  | 33 | Backup | 41812909602 | 1 | 404.01 | 428.14 | 24.13 | 240000 |  | 5791200 | 5797520.3182 |  |  |  |  | 0 | 5797520.3182 | 4867295.5086 | 930224.8097 | 19.1117 | OK
| 33 KV Feeders | [7 empty] | Total |  | 38154000 | 38195639.9748 |  |  |  |  | 33 KV Feeders | 38195639.9748 | 36431766.6764 | 1763873.2984 | 4.8416 | OK
10 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 506.09 | 531.04 | 24.95 | 360000 |  | 8982000 | 8991802.6486 |  |  |  |  | 33 kV Shahriar Steel Feeder | 8991802.6486 | 5865868.42 | 3125934.2285 | 53.2902 | FAULT
|  | 33 | Backup | 41812909580 | 1 | 506.05 | 531 | 24.95 | 360000 |  | 8982000 | 8991802.6486 |  |  |  |  | 0 | 8991802.6486 | 5865868.42 | 3125934.2285 | 53.2902 | FAULT
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | 33 | Main | 41812909531 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909581 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 | 33 | Main | 41812909529 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909574 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 | 33 | Main | 41812909545 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909618 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 | 33 | Main | 41812909481 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909560 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Spare Feeder 7 | 33 | Main | 41812909523 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909565 | 1 |  | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 548.88 | 577.58 | 28.7 | 360000 |  | 10332000 | 10343275.9926 | Kazla |  |  |  | 33 kV Zahir Steel | 10343275.9926 | 6680273.3933 | 3663002.5992 | 54.8331 | FAULT
|  | 33 | Backup | 41812909563 | 1 | 549.07 | 577.77 | 28.7 | 360000 |  | 10332000 | 10343275.9926 |  |  |  |  | 0 | 10343275.9926 | 6683861.0804 | 3659414.9121 | 54.75 | FAULT
| Auxiliary Transformer-3 (AT-3) | 0.415 |  |  | 1 | 2055.77 | 2173.65 | 117.88 | 160 |  | 18860.8 | 18881.384 | [5 empty] | 18881.384 | 18091.5102
[9 empty] | Total |  | 19332860.8 | 19353960.0252 |  |  |  |  | 0 | 19353960.0252 | 12564233.3236 | 6789726.7016 | 54.0401 | FAULT
[8 empty] | Grand Total |  | 57549600 | 57486860.8 | 57549600 | 0.10914
[6 empty] | 33 KV EXPORT |  |  | KWH | S/S % of Loss
[6 empty] | KAZLA at 33 KV level |  |  | 19335078.6411
[6 empty] | Kazla 33/11 KV Substation |  |  | 38195639.9748
[8 empty] | Total = | 57530718.616 | -18881.384
11 KV SIDE of___KAZLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK-61009 | 1 | 7642037 | 7704264 | 62227 | 180 | 11200860 |  | 11426857.287
30 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK-61124 | 1 | 640422.7 | 696229.7 | 55807 | 180 | 10045260 |  | 10396133.6167
24 | 33/11 kV 20/28 MVA T-3 Incoming | 11 |  | DHK-61015 | 1 | 305915.3 | 349719.9 | 43804.6 | 180 | 7884828 |  | 7916630.5216
39 | 33/11 kV 10/14 MVA T-4 Incoming | 11 |  | 8L55984 | 1 | 24065 | 25488.7 | 1423.7 | 4000 | 5694800 |  | 5807130.7954
42 | 33/11 kv 28/35 MVA T-5 Incomer | 11 |  | DHK00112 | 1 | 93563.3 | 96519.7 | 2956.4 | 888.8 | 2627648.32 |  | 2648887.7542
[9 empty] | Total | 37453396.32 |  | 38195639.9748
KAZLA 11 kV SIDE
17 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 755740.9 | 783779.8 | 28038.9 | 60 |  | 1682334 | 1710856.4639 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1710856.4639 | 1673058.4611 | 37798.0029 | 2.2592 | OK
18 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1855425.2355 | Kazla | 150 |  |  | 11 kV Madrasa Bazar Feeder | 1855425.2355 | 1750585.7105 | 104839.525 | 5.9888 | OK
19 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2919188.16 | 2968680.3768 | Kazla | 240 |  |  | 11 kV Kazla Feeder | 2968680.3768 | 2957886.2004 | 10794.1763 | 0.36493 | OK
20 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963847 | 36963851 | 4 | 1000 | Estimated | 547347.78 | 556627.5706 | Maniknagar | 45 |  |  | 11 kV Sayedabad Feeder | 556627.5706 | 564115.0135 | -7487.4429 | -1.3273 | OK
21 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 107994.3 | 110052.4 | 2058.1 | 1000 |  | 2058100 | 2092993.2394 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 2092993.2394 | 2026095.9958 | 66897.2436 | 3.3018 | OK
23 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 41024544 | 0 | 1 | Estimated | 1824492.6 | 1855425.2355 | Kazla | 150 |  |  | 11 kV Matuail Feeder | 1855425.2355 | 1871315.7595 | -15890.524 | -0.84916 | OK
25 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 610537.6 | 647129.1 | 36591.5 | 60 |  | 2195490 | 2232712.5636 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2232712.5636 | 2157561.4612 | 75151.1024 | 3.4832 | OK
26 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 557250.1 | 579724.6 | 22474.5 | 60 |  | 1348470 | 1371332.0993 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1371332.0993 | 1132886.54 | 238445.5592 | 21.0476 | OK
27 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 907339.1 | 947647 | 40307.9 | 60 |  | 2418474 | 2459477.0573 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2459477.0573 | 2254948.2258 | 204528.8315 | 9.0702 | OK
28 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 146325.4 | 178496.3 | 32170.9 | 60 |  | 1930254 | 1962979.7252 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 1962979.7252 | 1929642.5851 | 33337.14 | 1.7276 | OK
31 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 994216.4 | 1033062 | 38845.6 | 60 |  | 2330736 | 2370251.5382 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 2370251.5382 | 2129671.6149 | 240579.9233 | 11.2966 | OK
32 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 199222.9 | 249904.8 | 50681.9 | 60 |  | 3040914 | 3092469.9692 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 3092469.9692 | 3068640.0293 | 23829.9399 | 0.77656 | OK
33 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 348551.4 | 362270.4 | 13719 | 60 |  | 823140 | 837095.6004 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 837095.6004 | 1217079.1673 | -379983.567 | -31.2209 | OK
34 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1880719 | 1912724 | 32005 | 60 |  | 1920300 | 1952856.964 | Jurain |  |  |  | 11 kV Donia Feeder | 1952856.964 | 1945273.6993 | 7583.2647 | 0.38983 | OK
35 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 24764299 | 26329191 | 1564892 | 1 |  | 1564892 | 1591423.3402 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1591423.3402 | 1433569.0732 | 157854.267 | 11.0113 | OK
36 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 24603267 | 25278265 | 674998 | 1 |  | 674998 | 686441.9856 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 686441.9856 | 675991.3287 | 10450.657 | 1.546 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 2727 | 2894.5 | 167.5 | 10000 |  | 1675000 | 1703398.1226 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1703398.1226 | 1613368.9386 | 90029.1839 | 5.5802 | OK
38 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 528 | 808.3 | 280.3 | 4000 |  | 1121200 | 1140208.9403 | Kazla |  |  |  | 11 kV Dharmik Para | 1140208.9403 | 192824.7683 | 947384.172 | 491.3187 | FAULT
41 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 11886 | 12649 | 763 | 4000 |  | 3052000 | 3103743.9224 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 3103743.9224 | 3171352.0396 | -67608.1172 | -2.1318 | OK
43 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 1000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 19756.3 | 19756.3 | 0 | 1000 |  | 0 | 0 | Kazla | NO LOAD |  |  | 11 kV Jenith Feeder | 0 | 431906.9676 | -431906.9676 | -100 | CHECK
45 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 15890.2 | 16523.9 | 633.7 | 2000 |  | 1267400 | 1288887.6302 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1288887.6302 | 1098075.5154 | 190812.1148 | 17.377 | OK
46 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 34227.2 | 34893.9 | 666.7 | 2000 |  | 1333400 | 1356006.601 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 1356006.601 | 1254796.9228 | 101209.6782 | 8.0658 | OK
47 | 33/0.4 kV AT-1 | 0.415 |  | 503043 | 1 | 96180 | 96204 | 24 | 10 |  | 240 | 244.069 | Kazla |  |  |  | 33/0.4 kV AT-1 | 244.069 | 0 | 244.069 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 | 0.415 |  | 503044 | 1 | 91766 | 92456 | 690 | 10 |  | 6000 | 6101.7246 | Kazla |  |  |  | 33/0.4 kV AT-2 | 6101.7246 | 6153.982 | -52.2573 | -0.84916 | OK
23 | Auxiliary Transformer | 0.415 |  | 41901920685 | 1 | 2055.77 | 2173.65 | 117.88 | 160 |  |  | 0 | Kazla |  |  |  | Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 38195639.9748 | 37558863.14 | 38195639.9748 | 1.6954
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 837095.6004
[5 empty] | Jurain | at 33 KV level |  | 8648814.3053
[5 empty] | Swamibag | at 33 KV level |  | 1962979.7252
[5 empty] | Maniknagar | at 33 KV level |  | 1912634.1716
[5 empty] | Shyampur | at 33 KV level |  | 3092469.9692
[5 empty] | Kazla | at 33 KV level |  | 21741646.2032
[5 empty] | Total = |  |  | 38195639.9748 | 0
132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT | 132 |  | 8993532 | 1 | 2225.602 | 2226.297 | 0.695 | 960000 | 0 | 667200
|  | 132 |  |  | 1 | 660.75 | 666.114 | 5.364 | 960000 | 5149440 | 0
1 | Tranformer - 1 at Shyampur 230/132 | 132 |  | 38992560 | 1 | 1344.176 | 1376.368 | 32.192 | 1920000 | 0 | 61808640
|  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  | 132 |  | 38992559 | 1 | 1435.585 | 1467.736 | 32.151 | 1920000 | 0 | 61729920
| Aggrekko 100 MW (Brammhongao) | 132 |  | PN-1711A04601 | 1 | 344.582 | 363.871 | 19.289 | 960000 | 0 | 18517440
|  | 132 |  |  | 1 | 5.35 | 5.419 | 0.069 | 960000 | 66240 | 0
| Madanganj-Fatullah Exp | 132 |  | 38992544 | 1 | 28.343 | 32.177 | 3.834 | 960000 | 0 | 3680640
| Madanganj-Fatullah Imp | 132 |  | 38992544 | 1 | 8.797 | 18.041 | 9.244 | 960000 | 8874240 | 0
[8 empty] | Total Import/Export |  | 14089920 | 146403840
[9 empty] | Net Total | 132313920
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) | 132 | Import | 08993727 | 1 | 8883.937 | 8945.468 | 61.531 | 720000 | 44302320
|  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) | 132 | Import | 08993726 | 1 | 6638.431 | 6705.919 | 67.488 | 720000 | 48591360
|  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
[8 empty] | Total Import/Export |  | 92893680 | 0
[8 empty] | Net Total |  | 92893680
SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S)
|  | 132 |  |  |  |  | 0
|  | 132 |  |  |  |  | 0
0
0
[9 empty] | Total |  | 39240000
SHYAMPUR 132 KV SIDE
5 | 132 kV 80/120 MVA ( GT-1) | 132 | Export | Nill | 1 |  | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) | 132 | Export | Nill | 1 |  | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) | 132 | Export | Nill | 1 |  | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) | 132 | Export | ABB3902 | 1 | 1473348.4 | 1735597.5 | 262249.1 | 1300 |  | 340923830
[9 empty] | Total |  | 53653680
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDNG) |  | 132313920 |  | EXPORT TO OTHER S/S |  |  | 39240000 |  | 132 KV NET IMPORT |  | 93073920
| IMPORT-2 |  |  |  | 132 KV NET IMPORT |  |  | 93073920 |  | 33 KV NET IMPORT |  | 93042288
| IMPORT-3 | [8 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 31632
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.03399%
| 132 KV TOTAL IMPORT |  | 132313920
33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) | 33 | Import | BD001826 | 1 | 3241.208 | 3292.028 | 50.82 | 480000 | 24393600
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) | 33 | Import | BD001850 | 1 | 3297.915 | 3348.8759 | 50.9609 | 480000 | 24461232
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) | 33 | Import | BD001835 | 1 | 2788.8688 | 2834.593 | 45.7242 | 480000 | 21947616
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) | 33 | Import | BD001831 | 1 | 3666.8081 | 3713.1411 | 46.333 | 480000 | 22239840
[9 empty] | Total | 93042288
SHYAMPUR 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) | 33 | Export | BD001808 | 1 | 2022.8489 | 2056.104 | 33.2551 | 240000 | From Downstream | 7966400 | 7973517.1986 |  | 26231606.4542 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 7973517.1986 | 6011352.2624 | 1962164.9362 | 32.641 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) | 33 | Export | BD001834 | 1 | 1835.604 | 1868.6779 | 33.0739 | 240000 | From Downstream | 7936000 | 7943090.0392 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 7943090.0392 | 6068892.4596 | 1874197.5796 | 30.882 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) | 33 | Export | BD001846 | 1 | 1347.092 | 1374.781 | 27.689 | 240000 |  | 6645360 | 6651296.9787 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 6651296.9787 | 4147713.1857 | 2503583.793 | 60.3606 | FAULT
22 | 33 kV 20/28 MVA Transformer-4 (T-4) | 33 | Export | BD001847 | 1 | 1225.436 | 1240.6878 | 15.2518 | 240000 |  | 3660432 | 3663702.2377 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 3663702.2377 | 4683532.2965 | -1019830.0588 | -21.7748 | OK
| 33 KV Feeders | [7 empty] | Total |  | 26208192 | 26231606.4542 |  |  |  |  | 33 KV Feeders | 26231606.4542 | 20911490.2042 | 5320116.25 | 25.4411 | OK
1 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 692.3275 | 705.0729 | 12.7454 | 240000 |  | 3058896 | 3061628.8242 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 3061628.8242 | 1819852.5851 | 1241776.2391 | 68.235 | FAULT
2 | 33 kV Postogola Feeder-1. | 33 | Export | BD001804 | 1 | 1564.54 | 1564.54 | 0 | 240000 |  | 0 | 0 |  | 2762225.5754 | Postogola 33/11 kv s/s |  | 33 kV Postogola Feeder-1. | 0 | 479.5016 | -479.5016 | -100 | CHECK
5 | 33 kV Prime Textile Feeder. | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 528290.935 | -528290.935 | -100 | CHECK
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1188.4909 | 1218.187 | 29.6961 | 240000 | From Downstream | 7110784 | 7117136.7895 |  | 13186154.0225 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 7117136.7895 | 6664689.2342 | 452447.5553 | 6.7887 | OK
7 | 33 kV Nondolalpur -2 feeder | 33 | Export | BD001807 | 1 | 1036.3189 | 1061.5839 | 25.265 | 240000 |  | 6063600 | 6069017.2331 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 6069017.2331 | 5410912.3136 | 658104.9195 | 12.1626 | OK
8 | 33 kV Postogola Feeder-2. | 33 | Export | BD001830 | 1 | 2120.393 | 2131.892 | 11.499 | 240000 |  | 2759760 | 2762225.5754 |  |  |  |  | 33 kV Postogola Feeder-2. | 2762225.5754 | 7506598.2187 | -4744372.6433 | -63.2027 | CHECK
11 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 609.2324 | 619.8515 | 10.6191 | 240000 |  | 2548584 | 2550860.9103 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 2550860.9103 | 1928172.0062 | 622688.9041 | 32.2943 | OK
12 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1011.4099 | 1058.144 | 46.7341 | 240000 |  | 11216184 | 11226204.5625 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 11226204.5625 | 7916931.7496 | 3309272.813 | 41.7999 | FAULT
13 | 33 kV Fatullah Feeder-2. | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 553357.9299 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2443.1918 | 2476.4919 | 33.3001 | 240000 |  | 8151864.48 | 8159147.373 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 8159147.373 | 7231076.5747 | 928070.7982 | 12.8345 | OK
17 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 667.4194 | 669.723 | 2.3036 | 240000 | Prime Textile | 552864 | 553357.9299 | Fatullah | 17968062.8567 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 553357.9299 | 44449.8023 | 508908.1276 | 1144.9053 | FAULT
18 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 118.6514 | 123.986 | 5.3346 | 240000 |  | 1280304 | 1281447.8263 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1281447.8263 | 845241.5209 | 436206.3054 | 51.6073 | FAULT
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.889 | 1544.89 | 0.001 | 240000 |  | 240 | 240.2144 |  | 240.2144 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 240.2144 | 1198.7541 | -958.5397 | -79.9613 | CHECK
20 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1437.362 | 1461.395 | 24.033 | 240000 |  | 5767920 | 5773073.0719 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 5773073.0719 | 4768188.3115 | 1004884.7604 | 21.0748 | OK
23 | 33 kV Shyampur BSCIC-2. | 33 | Export | BD001827 | 1 | 2344.2709 | 2385.1049 | 40.834 | 240000 |  | 9800160 | 9808915.4837 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 9808915.4837 | 8987059.541 | 821855.9427 | 9.1449 | OK
24 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2259.944 | 2295.02 | 35.076 | 240000 |  | 8418240 | 8425760.8734 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 8425760.8734 | 7150088.7473 | 1275672.1262 | 17.8413 | OK
23 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 329.26 | 337.075 | 7.815 | 2400 |  | 19224.9 | 19224.9 | Fatullah
24 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 82.006 | 82.99 | 0.984 | 2400 |  | 2420.64 | 2420.64 | Fatullah
[9 empty] | Total |  | 66751046.02 | 66810662.2076 |  |  |  |  | 0 | 66810662.2076 | 60803229.7958 | 6007432.4118 | 9.8801 | OK
[8 empty] | Grand Total |  | 93042288 | 92959238.02 | 93042268.6618 | 0.089319
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 32318976.0687
[5 empty] | Fatullah | at 33 KV level |  | 575003.4699
[6 empty] | Export to Other SS |  | 60148289.1233
[5 empty] | Total = |  |  | 93042268.6618 | 0
11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | BD001926 | 1 | 2723.73 | 2773.52 | 49.79 | 160000 | 7966400 |  | 7971628.9389 |  | 7966400
16 | 11 kV 20/28 MVA Transformer-2 | 11 |  | BD001952 | 1 | 2737.03 | 2786.63 | 49.6 | 160000 | 7936000 |  | 7941208.9852
27 | 11 kV20/28 MVA Transformer-3 | 11 |  | BD001927 | 1 | 1885.44 | 1927.01 | 41.57 | 160000 | 6651200 |  | 6655565.6757 |  | 1793200
36 | 11 kV 20/28 MVA Transformer-4 | 11 |  | BD001927 | 1 | 1833.96 | 1856.84 | 22.88 | 160000 | 3660800 |  | 3663202.8544 |  | 1793200
[9 empty] | Total | 26214400 |  | 26231606.4542
SHYAMPUR 11 kV SIDE
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur |  | 1 | 501.66 | 546.49 | 44.83 | 40000 |  | 1793200 | 1796570.0888 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1796570.0888 | 1570124.4069 | 226445.6819 | 14.4221 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | 11 |  | BD001943 | 1 | 995.02 | 1013.14 | 18.12 | 40000 |  | 724800 | 726162.1684 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 726162.1684 | 552962.0715 | 173200.0969 | 31.3222 | OK
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1469.8 | 1490.83 | 21.03 | 40000 |  | 841200 | 842780.9272 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 842780.9272 | 625330.9326 | 217449.9946 | 34.7736 | OK
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1366.77 | 1383.34 | 16.57 | 40000 |  | 662800 | 664045.6474 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 664045.6474 | 639724.7392 | 24320.9081 | 3.8018 | OK
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1234.72 | 1259.97 | 25.25 | 40000 |  | 1010000 | 1011898.1651 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 1011898.1651 | 982465.2649 | 29432.9003 | 2.9958 | OK
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3121.28 | 3181.56 | 60.28 | 40000 |  | 2411200 | 2415731.5404 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 2415731.5404 | 1432183.76 | 983547.7804 | 68.6747 | FAULT
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2029.39 | 2064.33 | 34.94 | 40000 |  | 1397600 | 1400226.6095 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1400226.6095 | 1303039.3282 | 97187.2812 | 7.4585 | OK
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 478.9 | 481.32 | 2.42 | 40000 |  | 96800 | 96981.9232 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 96981.9232 | 99157.3346 | -2175.4114 | -2.1939 | OK
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 2982.97 | 3028.5 | 45.53 | 40000 |  | 1821200 | 1824622.7112 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1824622.7112 | 1361014.3827 | 463608.3285 | 34.0634 | OK
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1839.53 | 1879.48 | 39.95 | 40000 |  | 1598000 | 1601003.2355 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 1601003.2355 | 1086732.4008 | 514270.8347 | 47.3227 | FAULT
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1325.38 | 1372.48 | 47.1 | 40000 |  | 1884000 | 1887540.7358 | Shyampur |  |  |  | 11 kV Kadamtolly Steel Feeder | 1887540.7358 | 1272252.5752 | 615288.1606 | 48.3621 | FAULT
20 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 779.83 | 793.62 | 13.79 | 40000 |  | 551600 | 552636.6613 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 552636.6613 | 343452.2194 | 209184.4419 | 60.9064 | FAULT
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1249.14 | 1274.85 | 25.71 | 40000 |  | 1028400 | 1030332.7456 | Shyampur |  |  |  | 11 kV Delpara Feeder | 1030332.7456 | 743280.1814 | 287052.5642 | 38.6197 | OK
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2797.89 | 2850.41 | 52.52 | 40000 |  | 2100800 | 2104748.1835 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2104748.1835 | 1618503.5903 | 486244.5932 | 30.0428 | OK
24 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1084.64 | 1090.91 | 6.27 | 40000 |  | 250800 | 251271.3464 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 251271.3464 | 179522.755 | 71748.5914 | 39.9663 | OK
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1846.66 | 1882.3 | 35.64 | 40000 |  | 1425600 | 1428279.2319 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1428279.2319 | 1019161.4752 | 409117.7567 | 40.1426 | FAULT
28 | 11 kV Spare Feeder | 11 | Shympur |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1303.2 | 1321.48 | 18.28 | 40000 |  | 731200 | 732574.1964 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 732574.1964 | 367042.0691 | 365532.1272 | 99.5886 | FAULT
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1249.41 | 1273.64 | 24.23 | 40000 |  | 969200 | 971021.4868 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 971021.4868 | 798856.2681 | 172165.2186 | 21.5515 | OK
31 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2129.9 | 2161.1 | 31.2 | 40000 |  | 1248000 | 1250345.4555 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1250345.4555 | 1486560.3628 | -236214.9073 | -15.89 | OK
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 166.25 | 168.36 | 2.11 | 40000 |  | 84400 | 84558.6189 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 84558.6189 | 74767.8289 | 9790.79 | 13.0949 | OK
37 | 11 kV Spare Feeder | 11 |  |  | 1 |  | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1128.88 | 1150.73 | 21.85 | 40000 |  | 874000 | 875642.5706 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 875642.5706 | 717691.1918 | 157951.3788 | 22.0083 | OK
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3533.57 | 3585.78 | 52.21 | 40000 |  | 2088400 | 2092324.8793 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 2092324.8793 | 1849204.3244 | 243120.5549 | 13.1473 | OK
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1049.77 | 1064.5 | 14.73 | 40000 |  | 589200 | 590307.3256 | Shyampur |  |  |  | 11 kV Igloo Feeder | 590307.3256 | 788460.7411 | -198153.4155 | -25.1317 | OK
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 62537.1 | 62985.9 | 448.8 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 |  |  | 1 | 571732 | 578955 | 7223 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 |  | DHK20964 | 1 |  | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Total | 26231606.4542 | 26182400 | 26231606.4542 | 0.18794
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 1108880.0883
[5 empty] | Shyampur | at 33 KV level |  | 25122726.3659
[5 empty] | Total = |  |  | 26231606.4542 | 0
33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2443.1918 | 2476.4919 | 33.3001 | 240000 | 0 | 8151864.48 | 8159147.373
23 | 33 kV Shyampur BSCIC-2. | 33 |  | BD001827 | 1 | 2344.2709 | 2385.1049 | 40.834 | 240000 | 0 | 9800160 | 9808915.4837
[9 empty] | Total | 0 | 17952024.48 | 17968062.8567
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 | 33 | Import | DHK61071 | 1 | 827865.4 | 857567.5 | 29702.1 | 270 | 8019567
5 | 33 kV Shyampur Circuit-2 | 33 | Import | DHK61067 | 1 | 605591.3 | 642122.8 | 36531.5 | 270 | 9863505
[9 empty] | Total | 17883072 | 0 | 0
SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
SHYAMPUR BISIC 33 KV SIDE
2 | 33 kV 20/28 MVA Transformer-1 | 33 | Export | DHK61068 | 1 | 755149.3 | 799750 | 44600.7 | 180 |  | 8028126
3 | 33 kV 20/28 MVA Transformer-2 | 33 | Export | DHK61066 | 1 | 402714.5 | 457508.2 | 54793.7 | 180 |  | 9862866
[9 empty] | Total |  | 17890992 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| 33 KV SIDE |  | 17968062.8567 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 17968062.8567
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 17968062.8567 |  | 33 KV TX HV SIDE |  | 17890992
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 77070.8567
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 0.4289%
| TOTAL IMPORT |  | 17968062.8567
11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK61019 | 1.05 | 899401.9 | 929250.4 | 29848.5 | 180 | 5641366.5 |  | 6591206.4928 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK61018 | 1 | 527403.5 | 581500 | 54096.5 | 180 | 9737370 |  | 11376856.3639
[9 empty] | Total | 15378736.5 |  | 17968062.8567
SHYAMPUR BISIC 11 KV SIDE
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 31461699 | 33561211 | 2099512 | 1 |  | 2099512 | 2051822.5774 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 2051822.5774 | 2114379 | -62556.4226 | -2.9586 | OK
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 19028427 | 19777200 | 748773 | 1 |  | 748773 | 731764.9753 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 731764.9753 | 717177 | 14587.9753 | 2.0341 | OK
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 344092 | 377188.5 | 33096.5 | 60 |  | 1985790 | 1940683.7189 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1940683.7189 | 1686510 | 254173.7189 | 15.071 | OK
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 526588 | 550150 | 23562 | 60 |  | 1413720 | 1381608.0185 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1381608.0185 | 1319208 | 62400.0185 | 4.7301 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 546830.2 | 570335.4 | 23505.2 | 60 |  | 1410312 | 1378277.4296 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1378277.4296 | 1174320 | 203957.4296 | 17.3681 | OK
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 303271.1 | 320655.9 | 17384.8 | 60 |  | 1043088 | 1019394.7492 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 1019394.7492 | 827058 | 192336.7492 | 23.2555 | OK
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511237.9 | 511384.5 | 146.6 | 60 |  | 8796 | 8596.203 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 8596.203 | 98862 | -90265.797 | -91.3048 | CHECK
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 734846.3 | 778535.8 | 43689.5 | 60 |  | 2621370 | 2561826.8196 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2561826.8196 | 2642466 | -80639.1804 | -3.0517 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 193075.4 | 214982.3 | 21906.9 | 60 |  | 1314414 | 1284557.7074 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1284557.7074 | 1175202 | 109355.7074 | 9.3053 | OK
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 414820 | 435544 | 20724 | 60 |  | 1243440 | 1215195.8482 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 1215195.8482 | 1017888 | 197307.8482 | 19.384 | OK
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 397196.8 | 439242.7 | 42045.9 | 60 |  | 2522754 | 2465450.8355 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2465450.8355 | 2520720 | -55269.1645 | -2.1926 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 821215.4 | 833590.5 | 12375.1 | 60 |  | 742506 | 725640.3272 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 725640.3272 | 606924 | 118716.3272 | 19.5603 | OK
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 897162 | 917620.2 | 20458.2 | 60 |  | 1227492 | 1199610.0995 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1199610.0995 | 1293408 | -93797.9005 | -7.252 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB7380 | 1 | 597162 | 600880 | 3718 | 1 |  | 3718 | 3633.5474 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3633.5474 | 3132 | 501.5474 | 16.0136 | OK
[9 empty] | Grand Total | 17968062.8567 | 18385685 | 17968062.8567 | -2.2715
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5559018.6808
[5 empty] | Jurain | at 33 KV level |  | 12409044.1758
[5 empty] | Total = |  |  | 17968062.8567 | 0
33 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1188.4909 | 1218.187 | 29.6961 | 240000 | From Downstream | 7110784 | 7117136.7895
7 | 33 kV Nondolalpur -2 feeder | 33 |  | BD001807 | 1 | 1036.3189 | 1061.5839 | 25.265 | 240000 | 0 | 6063600 | 6069017.2331
[9 empty] | Total | 0 | 13174384 | 13186154.0225
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) | 33 | Import | 00000084 | 1 | 285187680 | 292336064 | 7148384 | 1 | 7148384
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) | 33 | Import | 00000070 | 1 | 269212544 | 275297536 | 6084992 | 1 | 6084992
[9 empty] | Total | 13233376 | 0 | 0
NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
NANDALALPUR 33 KV SIDE
4 | 33 kV, 28/35 MVA T-1 | 33 | Export | 00000086 | 1 | 285400000 | 292542016 | 7142016 | 1 |  | 7142016
5 | 33 kV, 28/35 MVA T-2 | 33 | Export | 00000083 | 1 | 268668352 | 274750112 | 6081760 | 1 |  | 6081760
[9 empty] | Total |  | 13223776 | 0
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| SHYAMPUR 33 KV SIDE |  | 13186154.0225 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 13186154.0225
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 13186154.0225 |  | 33 KV TX HV SIDE |  | 13223776
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | -37621.9775
| IMPORT-4 | [8 empty] | LOSS % IN => |  | -0.2853%
| TOTAL IMPORT |  | 13186154.0225
11 KV SIDE of___NANDALALPUR 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. | 11 |  | 00000036 | 1 | 283643744 | 290754528 | 7110784 | 1 | 7110784 |  | 7120708.3903 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000033 | 1 | 267498336 | 273555328 | 6056992 | 1 | 6056992 |  | 6065445.6322
[9 empty] | Total | 13167776 |  | 13186154.0225
NANDALALPUR 11 KV SIDE
8 | 11 kV Spare | 11 |  | 00000090 | 1 |  |  | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | 11 |  | 00000026 | 1 | 3344951 | 4014750 | 669799 | 1 |  | 669799 | 672821.6526 | Fatullah |  |  |  | 11 kV Khaza Moinuddin | 672821.6526 | 668907.0071 | 3914.6455 | 0.58523 | OK
10 | 11 kV Chitashal | 11 |  | 00000027 | 1 | 31054124 | 31727122 | 672998 | 1 |  | 672998 | 676035.0889 | Shyampur |  |  |  | 11 kV Chitashal | 676035.0889 | 666651.4505 | 9383.6384 | 1.4076 | OK
11 | 11 kV Local Feeder | 11 |  | 00000157 | 1.5 | 17804636 | 18012236 | 207600 | 1 | Estimated | 608164.2 | 610908.7086 | Shyampur | 50 |  |  | 11 kV Local Feeder | 610908.7086 | 569182.1524 | 41726.5562 | 7.331 | OK
12 | 11 kV Rasel Germants | 11 |  | 00000124 | 1 |  | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 |  | 00000121 | 1 | 65806320 | 68316432 | 2510112 | 1 |  | 2510112 | 2521439.5722 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2521439.5722 | 2321355.5467 | 200084.0255 | 8.6193 | OK
14 | 11 kV Nandalalpur | 11 |  | 00000010 | 1 | 81183200 | 82071400 | 888200 | 1 |  | 888200 | 892208.2473 | Fatullah |  |  |  | 11 kV Nandalalpur | 892208.2473 | 752765.5576 | 139442.6897 | 18.5241 | OK
15 | 11 kV Sharif Bagh | 11 |  | 00000132 | 1 | 66803716 | 68478392 | 1674676 | 1 |  | 1674676 | 1682233.437 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1682233.437 | 1653654.391 | 28579.046 | 1.7282 | OK
18 | 11 kV Spare | 11 |  | 00000139 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | 11 |  | 00000158 | 1 | 61866928 | 62900248 | 1033320 | 1 |  | 1033320 | 1037983.1413 | Fatullah |  |  |  | 11 KV Nayamati | 1037983.1413 | 956174.6502 | 81808.4911 | 8.5558 | OK
20 | 11 kV Pulpar | 11 |  | 00000160 | 1 | 5264907 | 6177345 | 912438 | 1 |  | 912438 | 916555.6279 | Fatullah |  |  |  | 11 kV Pulpar | 916555.6279 | 715973.4912 | 200582.1367 | 28.0153 | OK
21 | 11 kV Shahi Bazar | 11 |  | 00000170 | 1 | 38497188 | 39279104 | 781916 | 1 |  | 781916 | 785444.6114 | Shyampur |  |  |  | 11 kV Shahi Bazar | 785444.6114 | 771422.506 | 14022.1054 | 1.8177 | OK
22 | 11 kV Pagla Bazar | 11 |  | 00000060 | 1 | 47913044 | 48692680 | 779636 | 1 |  | 779636 | 783154.3223 | Fatullah |  |  |  | 11 kV Pagla Bazar | 783154.3223 | 671771.03 | 111383.2923 | 16.5805 | OK
23 | 11 kV Delpara bazar | 11 |  | 00000063 | 1 | 74614216 | 76134976 | 1520760 | 1 |  | 1520760 | 1527622.8486 | Shyampur |  |  |  | 11 kV Delpara bazar | 1527622.8486 | 1356267.4689 | 171355.3798 | 12.6343 | OK
24 | 11 kV Bhuighor (Board mill) | 11 |  | 00000146 | 1 | 41318500 | 42387696 | 1069196 | 1 |  | 1069196 | 1074021.0416 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 1074021.0416 | 804545.6412 | 269475.4004 | 33.4941 | OK
25 | 11 kV Spare | 11 |  | 00000059 | 1 |  | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 | 11 |  | 7803 | 1 | 2252 | 2309 | 57 | 100 |  | 5700 | 5725.7228 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 5725.7228 | 6145.1072 | -419.3844 | -6.8247 | OK
27 | 33/0.415 kV, 200 kVA AT-2 | 11 |  | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[9 empty] | Grand Total | 13186154.0225 | 13126915.2 | 13186154.0225 | 0.45128
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5287970.4174
[5 empty] | Fatullah | at 33 KV level |  | 4302722.9914
[5 empty] | Matuail | at 33 KV level |  | 3595460.6138
[5 empty] | Total = |  |  | 13186154.0225 | 0
132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 | 132 | Import | 42627826 | 1 | 205.751 | 231.085 | 25.334 | 960000 | 0 | 24320640
[5 empty] | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Hasnabad to Postogola-2 | 132 |  | 42627815 | 1 | 108.597 | 117.004 | 8.407 | 960000 | 0 | 8070720
2 |  |  |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
[8 empty] | Total Import/Export |  | 0 | 32391360
[9 empty] | Net Total | 32391360
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 | 132 | Main | 41808902823 | 1 | 164.47 | 184.09 | 19.62 | 1200000 | 23544000
|  | 132 | Backup | 41808904269 | 1 | 164.47 | 184.09 | 19.62 | 1200000 | 23544000
4 | 132kV Hasnabad Circuit-2 | 132 | Imp/Main | 41808902845 | 1 | 86.8 | 93.51 | 6.71 | 1200000 | 8052000
|  | 132 | Imp/Backup | 41808904256 | 1 | 86.8 | 93.51 | 6.71 | 1200000 | 8052000
[8 empty] | Total Import/Export |  | 31596000 | 0
[8 empty] | Net Total |  | 31596000
POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 132 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 132 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
POSTOGOLA 132 KV SIDE
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41808902871 | 1 | 175.55 | 195.88 | 20.33 | 1200000 |  | 24396000
|  | 132 | Exp/Backup | 41808904257 | 1 | 175.55 | 195.88 | 20.33 | 1200000 |  | 24396000
5 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41808902846 | 1 | 75.66 | 82.23 | 6.57 | 1200000 |  | 7884000
|  | 132 | Exp/Backup | 41808904243 | 1 | 75.66 | 82.23 | 6.57 | 1200000 |  | 7884000
[9 empty] | Total |  | 32280000
| 132 KV IMPORT |  | KWH |  | 132 KV NET IMPORT |  |  | KWH |  | TRANSMISSION LOSS |  | KWH
| 132 KV SIDE (SENDING) |  | 32391360 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 132 KV NET IMPORT |  | 32391360
[5 empty] | 132 KV NET IMPORT |  |  | 32391360 |  | 33 KV NET IMPORT |  | 33076800
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | -685440
[10 empty] | LOSS % IN => |  | -2.116%
| 132 KV TOTAL IMPORT |  | 32391360
33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
| POSTOGOLA 33 KV SIDE | [7 empty] | Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41808902807 | 1 | 290.5 | 325.26 | 34.76 | 720000 | 25027200
|  | 33 | Backup | 41808904286 | 1 | 290.5 | 325.26 | 34.76 | 720000 | 25027200
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41808902869 | 1 | 124.9 | 136.08 | 11.18 | 720000 | 8049600
|  | 33 | Backup | 41808904268 | 1 | 124.9 | 136.08 | 11.18 | 720000 | 8049600
[9 empty] | Total | 33076800 |  | 0
POSTOGOLA 33 kV SIDE
| 33/11 KV Transforfers |  | EXPORT | [13 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss |  | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33 KV Feeders | [7 empty] | Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 308.49 | 335.74 | 27.25 | 360000 |  | 9810000 | 9802531.8108 |  | 17842406.5253 | IG Gate 33/11 kv ss |  | 33 kV IG Gate Ckt-2 | 9802531.8108 | 9444686.8112 | 357844.9996 | 3.7888 | OK
|  | 33 | Backup | 41808904225 | 1 | 308.49 | 335.74 | 27.25 | 360000 |  | 9810000 | 9802531.8108 |  |  |  |  | 0 | 9802531.8108 | 9463736.1997 | 338795.6111 | 3.5799 | OK
8 | 33 kV Spare Feeder 2 | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 | 33 | Main | 41808902810 | 1 | 273.04 | 315.39 | 42.35 | 360000 |  | 15246000 | 15234393.4747 |  |  |  |  | 33kV Postogola circuit-1 | 15234393.4747 | 8799003.2529 | 6435390.2218 | 73.1377 | FAULT
|  | 33 | Backup | 41808904252 | 1 | 273.04 | 315.39 | 42.35 | 360000 |  | 15246000 | 15234393.4747 |  |  |  |  | 0 | 15234393.4747 | 8809888.6178 | 6424504.8569 | 72.9238 | FAULT
14 | 31 kV Spare Feeder 4 | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 249.28 | 271.63 | 22.35 | 360000 |  | 8046000 | 8039874.7145 |  |  |  |  | 33 kV IG Gate Ckt-1 | 8039874.7145 | 7650234.4159 | 389640.2987 | 5.0932 | OK
|  | 33 | Backup | 41812909573 | 1 | 249.28 | 271.63 | 22.35 | 360000 |  | 8046000 | 8039874.7145 |  |  |  |  | 0 | 8039874.7145 | 7676903.5597 | 362971.1548 | 4.7281 | OK
[9 empty] | Total |  | 33102000 | 33076800 |  |  |  |  | 0 | 33076800 | 25893924.48 | 7182875.52 | 27.7396 | OK
[8 empty] | Grand Total |  | 33076800 | 33102000 | 33076800 | -0.076128
11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola | 33 | Import | BD001804 | 1 | 273.04 | 315.39 | 42.35 | 360000 | 15246000 |  | 15234393.4747
2 | 33 kV Postogola Circuit-2 at Shyampur | 33 | Import | BD001830 | 1 | 2120.393 | 2131.892 | 11.499 | 240000 | 2759760 |  | 2762225.5754
[9 empty] | Total | 18005760 |  | 17996619.0501
POSTOGOLA 33 KV SIDE (RECEIVING)
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  | DHK60863 | 1 | 299053.8 | 309310.3 | 10256.5 | 270 | 2769255
[9 empty] | Total | 2769255
POSTOGOLA 33 KV SIDE
3 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK61027 | 1 | 114322.9 | 156623 | 42300.1 | 180 |  | 7614018 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60870 | 1 | 503640.9 | 559287.3 | 55646.4 | 180 |  | 10016352
[9 empty] | Total |  | 17630370
POSTOGOLA 11 KV SIDE
8 | 11 kV 20/28 MVA T-1 Incoming. | 11 |  | DHK61005 | 1.165 | 720744.3 | 759820.5 | 39076.2 | 180 | 8194279.14 |  | 8143823.1126 |  | 35260740
9 | 11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK60861 | 1.165 | 746924 | 794200.3 | 47276.3 | 180 | 9913840.11 |  | 9852795.9376
[9 empty] | Total | 18108119.25 |  | 17996619.0501
POSTOGOLA 11 kV SIDE
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 58467092 | 59733520 | 1266428 | 1 |  | 1266428 | 1269812.3426 | Postogola |  |  |  | 11 kV Station Road Feeder | 1269812.3426 | 1253296.0166 | 16516.326 | 1.3178 | OK
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 5618521 | 6981957 | 1363436 | 1 |  | 1363436 | 1367079.5822 | Jurain |  |  |  | 11 kV Samon & Sons Feeder. | 1367079.5822 | 1365490.5483 | 1589.034 | 0.11637 | OK
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 22620681 | 23055333 | 434652 | 1 |  | 434652 | 435813.5436 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 435813.5436 | 334501.1188 | 101312.4247 | 30.2876 | OK
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 69737341 | 71243020 | 1505679 | 1 |  | 1505679 | 1509702.7057 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1509702.7057 | 1394570.8758 | 115131.8299 | 8.2557 | OK
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 395780.9 | 407058.9 | 11278 | 60 |  | 676680 | 678488.3278 | Postogola |  |  |  | 11 kV Cyca Feeder | 678488.3278 | 589856.0898 | 88632.238 | 15.0261 | OK
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 804867.8 | 824597.3 | 19729.5 | 60 |  | 1183770 | 1186933.4512 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 1186933.4512 | 1170797.6147 | 16135.8366 | 1.3782 | OK
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 687382.8 | 706742.8 | 19360 | 60 |  | 1161600 | 1164704.2052 | Postogola |  |  |  | 11 kV Munshi Bari | 1164704.2052 | 1133728.9368 | 30975.2684 | 2.7322 | OK
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 513686.3 | 515784.4 | 2098.1 | 60 |  | 125886 | 126222.4118 | Postogola |  |  |  | 11 kV Cantonment Feeder | 126222.4118 | 120880.0544 | 5342.3574 | 4.4196 | OK
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 775428.8 | 797566.5 | 22137.7 | 60 |  | 1328262 | 1331811.5849 | Postogola |  |  |  | 11 kV DIT Feeder. | 1331811.5849 | 1058331.8488 | 273479.7361 | 25.8406 | OK
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 203448.6 | 243241.8 | 39793.2 | 60 |  | 2387592 | 2393972.4885 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 2393972.4885 | 2280368.6229 | 113603.8656 | 4.9818 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 32551263 | 34480101 | 1928838 | 1 |  | 1928838 | 1933992.5359 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 1933992.5359 | 1832087.7591 | 101904.7769 | 5.5622 | OK
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 1201.7 | 3547.1 | 2345.4 | 1000 |  | 2345400 | 2351667.7366 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2351667.7366 | 2069474.1082 | 282193.6284 | 13.636 | OK
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 51239362 | 52807093 | 1567731 | 1 |  | 1567731 | 1571920.5306 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1571920.5306 | 1503638.1773 | 68282.3533 | 4.5411 | OK
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52405873 | 52708936 | 303063 | 1 |  | 303063 | 303872.8913 | Postogola |  |  |  | 11 kV Rajabari Feeder. | 303872.8913 | 194471.9279 | 109400.9634 | 56.2554 | FAULT
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 |  | ELIB67385 | 1 | 188.64 | 243.19 | 54.55 | 80 |  | 4364 | 4375.6621 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 4375.6621 | 4587.274 | -211.6119 | -4.613 | OK
[9 empty] | Total | 17630370 | 17583381 | 17630370 | 0.26724
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Postogola | at 33 KV level |  | 9147844.1132
[5 empty] | Jurain | at 33 KV level |  | 8482525.8868
[5 empty] | Total = |  |  | 17630370 | 0
33 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.889 | 1544.89 | 0.001 | 240000 | 0 | 240 | 240.2144
| Postogola 33 KV SIDE | [7 empty] | Total | 0 | 240 | 240.2144
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 308.49 | 335.74 | 27.25 | 360000 | 0 | 9810000 | 9802531.8108
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 249.28 | 271.63 | 22.35 | 360000 | 0 | 8046000 | 8039874.7145
[9 empty] | Total | 0 | 17856000 | 17842406.5253
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 | 33 | Import | DHK60973 | 1 | 220705.7 | 235334.2 | 14628.5 | 540 | 7899390
6 | 33 kV Postogola Incoming Feeder-2 | 33 | Import | DHK60966 | 1 | 388988.1 | 406797.9 | 17809.8 | 540 | 9617292
[9 empty] | Total | 17516682 | 0 | 0
IG GATE 33 KV SIDE (EXPORT TO OTHER S/S)
| Feeder No.1 | 33 | EXPORT |  |  |  | 0 |  |  |  | 0
| Feeder No.2 | 33 |  |  |  |  | 0 |  |  |  | 0
[9 empty] | Total |  | 0
IG GATE 33 KV SIDE
4 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK60893 | 1 | 626969.9 | 670808.2 | 43838.3 | 180 |  | 7890894
5 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60975 | 1 | 200761 | 254166.6 | 53405.6 | 180 |  | 9613008
[9 empty] | Total |  | 17503902 | 0 | -100
| 33 KV IMPORT |  | KWH |  | 33 KV NET IMPORT |  |  | KWH |  | BUS LOSS |  | KWH
| Shyampur 33 KV SIDE |  | 17842406.5253 |  | EXPORT TO OTHER S/S |  |  | 0 |  | 33 KV NET IMPORT |  | 17842406.5253
| IMPORT-2 |  |  |  | 33 KV NET IMPORT |  |  | 17842406.5253 |  | 33 KV TX HV SIDE |  | 17503902
| IMPORT-3 | [8 empty] | LOSS UNITS=> |  | 338504.5253
| IMPORT-4 | [8 empty] | LOSS % IN => |  | 1.897%
| TOTAL IMPORT |  | 17842406.5253
11 KV SIDE of___IG GATE GIS 33/11 KV S/S | [13 empty] | Month May-2023 |  |  | Name of Feeders. | Month May-2023 | Month April-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK68139 | 1 | 3569.43 | 3612.62 | 43.19 | 180000 | 7774200 |  | 8164143.8482 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK68137 | 1 | 4164.69 | 4215.89 | 51.2 | 180000 | 9216000 |  | 9678262.6771
[9 empty] | Total | 16990200 |  | 17842406.5253
IG GATE 11 KV SIDE
1 | 11 kV Feeder-1 | 11 |  | DHK60892 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 | 11 |  | DHK60968 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | 11 |  | DHK60970 | 1 | 126774.5 | 158004.4 | 31229.9 | 60 |  | 1873794 | 1890634.7965 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 1890634.7965 | 1729719.97 | 160914.8265 | 9.3029 | OK
4 | 11 kV Alom Gonj | 11 |  | DHK60894 | 1 | 450404.1 | 460143.7 | 9739.6 | 60 |  | 584376 | 589628.102 | Postogola |  |  |  | 11 kV Alom Gonj | 589628.102 | 557154.4002 | 32473.7018 | 5.8285 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 |  | DHK60895 | 1 | 447662.4 | 475941.2 | 28278.8 | 60 |  | 1696728 | 1711977.4089 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1711977.4089 | 1656827.6227 | 55149.7863 | 3.3286 | OK
6 | 11 kV Farashgonj Feeder (F-6) | 11 |  | DHK68133 | 1 | 3500.26 | 3530.25 | 29.99 | 60000 |  | 1799400 | 1815572.1775 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1815572.1775 | 1671943.1553 | 143629.0223 | 8.5905 | OK
7 | 11 kV Doyaganj | 11 |  | DHK68134 | 1 | 2289.97 | 2322.27 | 32.3 | 60000 |  | 1938000 | 1955417.8504 | Swamibag |  |  |  | 11 kV Doyaganj | 1955417.8504 | 1926501.361 | 28916.4895 | 1.501 | OK
10 | 11 kV Faridabad | 11 |  | DHK68140 | 1 | 709.65 | 730.03 | 20.38 | 60000 |  | 1222800 | 1233789.9626 | Postogola |  |  |  | 11 kV Faridabad | 1233789.9626 | 1185305.6308 | 48484.3318 | 4.0904 | OK
11 | 11 kV Gandaria | 11 |  | DHK60969 | 1 | 266897.3 | 300077.81 | 33180.51 | 60 |  | 1990830.6 | 2008723.2675 | Postogola |  |  |  | 11 kV Gandaria | 2008723.2675 | 1972698.5112 | 36024.7563 | 1.8262 | OK
12 | 11 kV Walter Road | 11 |  | DHK68136 | 1 | 903.39 | 926.56 | 23.17 | 60000 |  | 1390200 | 1402694.4766 | Banglabazar |  |  |  | 11 kV Walter Road | 1402694.4766 | 1306205.5901 | 96488.8865 | 7.387 | OK
13 | 11 kV Murgitola Feeder (F-11) | 11 |  | DHK68138 | 1 | 3773.45 | 3813.73 | 40.28 | 60000 |  | 2416800 | 2438521.0841 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2438521.0841 | 2216296.7407 | 222224.3434 | 10.0268 | OK
14 | 11 kV Feeder-12 | 11 |  | DHK60900 | 1 |  | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | 11 |  | DHK60899 | 1 | 579240.5 | 609124.4 | 29883.9 | 60 |  | 1793034 | 1809148.9629 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1809148.9629 | 1594178.3574 | 214970.6055 | 13.4847 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | 11 |  | DHK60967 | 1 | 115953.3 | 132216.8 | 16263.5 | 60 |  | 975810 | 984580.1304 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 984580.1304 | 925188.4571 | 59391.6732 | 6.4194 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB2774 | 1 | 274308 | 276011 | 1703 | 1 |  | 1703 | 1718.3058 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1718.3058 | 1728.4441 | -10.1384 | -0.58656 | OK
[9 empty] | Grand Total | 17842406.5253 | 17683475.6 | 17842406.5253 | 0.89875
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | [5 empty] | 1.2562
[5 empty] | Swamibag | at 33 KV level |  | 6203087.8974
[5 empty] | Banglabazar | at 33 KV level |  | 5108901.4507
[5 empty] | Postogola | at 33 KV level |  | 6530417.1772
[5 empty] | Total = |  |  | 17842406.5253 | 0
Swamibagh
Banglabazr
Postogola
Note on I385: No Reading Due to PT Out
Note on K385: Reading From Higher Side
Note on I644: No Reading due to PT Open
Note on L644: Energy From Bangshal SS End
Note on L649: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Linked_11KV
SL | Feeder_Name | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 2787666 | 3920074 | 1132408 | 1 | 0 | 1132408 | 1137299.4891 | Paribag | Dhanmondi 33/11KV S/S
5 | 11 kV Mogbazar O/H | 11 | 0 | HA021100463-02 | 1 | 43144802 | 44616340 | 1471538 | 1 | 0 | 1471538 | 1477894.3769 | Paribag | Dhanmondi 33/11KV S/S
6 | 11 kV Panthopath Feeder | 11 | 0 | HA021101078-02 | 1 | 54778508 | 56931817 | 2153309 | 1 | 0 | 2153309 | 2162610.3185 | Paribag | Dhanmondi 33/11KV S/S
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 | 0 | DHK60882 | 1 | 195352.1 | 201916.09 | 6563.99 | 60 | 0 | 393839.4 | 395540.6076 | Paribag | Dhanmondi 33/11KV S/S
8 | 11 kV P G Hospital Feeder | 11 | 0 | DHK60889 | 1 | 271780.2 | 275542.83 | 3762.63 | 60 | 0 | 225757.8 | 226732.9713 | Paribag | Dhanmondi 33/11KV S/S
9 | 11 kV Abdul Monem Ltd | 11 | 0 | DHK60890 | 1 | 678.07 | 684.97 | 6.9 | 60000 | 0 | 414000 | 415788.2923 | Paribag | Dhanmondi 33/11KV S/S
10 | 11 kV Surjasen Hall Feeder | 11 | 0 | DHK60880 | 1 | 517969.5 | 526282.72 | 8313.22 | 60 | 0 | 498793.2 | 500947.7604 | Ramna | Dhanmondi 33/11KV S/S
11 | 11 kV Azimpur-1 Feeder | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S
12 | 11 kV TSC Feeder | 11 | 0 | DHK60873 | 1 | 900320 | 910191.77 | 9871.77 | 60 | 0 | 592306.2 | 594864.6942 | Ramna | Dhanmondi 33/11KV S/S
13 | 11 kV SCADA Bhaban | 11 | 0 | DHK60883 | 1 | 27848.4 | 27965.2 | 116.8 | 60 | 0 | 7008 | 7038.2714 | Paribag | Dhanmondi 33/11KV S/S
14 | 11 kV DPH Sw/S-2 | 11 | 0 | DHK60871 | 1 | 435234.3 | 455579.68 | 20345.38 | 60 | 0 | 1220722.8 | 1225995.769 | Paribag | Dhanmondi 33/11KV S/S
17 | 11 kV New Elephant Road Feeder | 11 | 0 | DHK60981 | 1 | 18328.3 | 38853.86 | 20525.56 | 60 | 0 | 1231533.6 | 1236853.2667 | Paribag | Dhanmondi 33/11KV S/S
18 | 11 kV Dhanmondi O/H Feeder | 11 | 0 | DHK61110 | 1 | 334055.6 | 356765.96 | 22710.36 | 60 | 0 | 1362621.6 | 1368507.5074 | Paribag | Dhanmondi 33/11KV S/S
19 | 11 kV Sonargaon Feeder | 11 | 0 | DHK61115 | 1 | 255486.3 | 283945.16 | 28458.86 | 60 | 0 | 1707531.6 | 1714907.3622 | Paribag | Dhanmondi 33/11KV S/S
20 | 11 kV Museum Feeder | 11 | 0 | DHK61107 | 1 | 540582.3 | 542994.77 | 2412.47 | 60 | 0 | 144748.2 | 145373.4466 | Ramna | Dhanmondi 33/11KV S/S
21 | 11 kV Shanta property | 11 | 0 | DHK61112 | 1 | 331698.9 | 334966.62 | 3267.72 | 60 | 0 | 196063.2 | 196910.1041 | Paribag | Dhanmondi 33/11KV S/S
22 | 11 kV BIRDEM RMU Feeder | 11 | 0 | DHK61108 | 1 | 655430.3 | 672823.56 | 17393.26 | 60 | 0 | 1043595.6 | 1048103.4598 | Kakrail | Dhanmondi 33/11KV S/S
23 | 11 kV Azimpur-2 Feeder | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S
24 | 11 kV DPH Sw/S-1 | 11 | 0 | DHK60978 | 1 | 739678 | 751590.62 | 11912.62 | 60 | 0 | 714757.2 | 717844.627 | Kakrail | Dhanmondi 33/11KV S/S
6 | WASA Bhaban | 11 | 0 | 8536188 | 1.17 | 1895.3 | 2089.7 | 194.4 | 1000 | 970800 | 970800 | 967717.4567 | Shere b.nagar | Kawranbazar 33/11KV S/S
7 | Sangsad Bhaban | 11 | 0 | 8536178 | 1.17 | 562105 | 567782 | 5677 | 44 | 0 | 292251.96 | 291323.9838 | Shere b.nagar | Kawranbazar 33/11KV S/S
8 | Air Port Road (West) | 11 | 0 | 8536182 | 1.17 | 98669.9 | 99649.5 | 979.6 | 1000 | 0 | 1146132 | 1142492.7318 | Shere b.nagar | Kawranbazar 33/11KV S/S
9 | ICC (PM Office) | 11 | 0 | 8536193 | 1.17 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S
10 | (UTC) Tower | 11 | 0 | DHK00183 | 1.17 | 13920.9 | 14511.4 | 590.5 | 444.44 | 0 | 307056.9294 | 306081.9435 | Shere b.nagar | Kawranbazar 33/11KV S/S
11 | Sonargaon Hotel | 11 | 0 | 8536190 | 1.17 | 51744.1 | 51744.1 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Kawranbazar 33/11KV S/S
12 | Panthopath | 11 | 0 | 8536184 | 1.17 | 32519.8 | 33415.5 | 895.7 | 1000 | 0 | 1047969 | 1044641.4249 | Shere b.nagar | Kawranbazar 33/11KV S/S
13 | Titas Bhaban | 11 | 0 | DHK00190 | 1.17 | 54591.7 | 55090.4 | 498.7 | 444.44 | 0 | 259321.4068 | 258497.9936 | Kakrail | Kawranbazar 33/11KV S/S
16 | Green Road Dormatory s/s | 11 | 0 | DHK00021 | 1.17 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S
26 | Aux. Transformer, AT-1 | 11 | 0 | 85-12906 | 1.17 | 67673 | 67959 | 286 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S
27 | Aux. Transformer, AT-2 | 11 | 0 | 85-12909 | 1.17 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S
4 | Police Bhaban | 11 | 0 | DHK 00005 | 1 | 72590.4 | 72836.6 | 246.2 | 444.44 | 0 | 109421.128 | 111715.2077 | Ramna | New Ramna 33/11KV S/S
5 | Water Works | 11 | 0 | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Lalbag | New Ramna 33/11KV S/S
6 | GPO | 11 | 0 | DHK 00060 | 1 | 96791.5 | 97306.6 | 515.1 | 444.44 | 0 | 228931.044 | 233730.721 | Ramna | New Ramna 33/11KV S/S
7 | Culvert Road | 11 | 0 | 8536184 | 1 | 39937.8 | 39940.4 | 2.6 | 444.44 | 62 | 754123.608 | 769934.2629 | Ramna | New Ramna 33/11KV S/S
8 | Secretariat (East) | 11 | 0 | DHK00059 | 1 | 81649.8 | 81714.5 | 64.7 | 444.44 | 0 | 28755.268 | 29358.1395 | Ramna | New Ramna 33/11KV S/S
9 | Siddik Bazar | 11 | 0 | DHK00076 | 1 | 25588.9 | 27275.4 | 1686.5 | 444.44 | 0 | 749548.06 | 765262.7858 | Bangshal | New Ramna 33/11KV S/S
10 | Bokshi Bazar | 11 | 0 | DHK 00206 | 1 | 83338.9 | 84325 | 986.1 | 444.44 | 0 | 438262.284 | 447450.7163 | Ramna | New Ramna 33/11KV S/S
11 | Ramna 11 kV Sw/S Circuit-1 | 11 | 0 | DHK00198 | 1 | 41887.9 | 44281.1 | 2393.2 | 444.44 | 0 | 1063633.808 | 1085933.5304 | Ramna | New Ramna 33/11KV S/S
12 | TNT RMU | 11 | 0 | DHK 00207 | 1 | 58458.1 | 59418.3 | 960.2 | 444.44 | 0 | 426751.288 | 435698.3854 | Ramna | New Ramna 33/11KV S/S
13 | DIT 11 kV Sw/S Circuit-1 | 11 | 0 | DHK 00052 | 1 | 2720.5 | 2799.1 | 78.6 | 444.44 | 0 | 34932.984 | 35665.375 | Motijheel | New Ramna 33/11KV S/S
16 | Secretariat (West) | 11 | 0 | DHK 00006 | 1 | 66894.9 | 67064.7 | 169.8 | 444.44 | 0 | 75465.912 | 77048.1002 | Ramna | New Ramna 33/11KV S/S
17 | Ramna 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00197 | 1 | 84759.4 | 84761.5 | 2.1 | 444.44 | 0 | 933.324 | 952.8917 | Ramna | New Ramna 33/11KV S/S
18 | Sayed Nazrul Islam Road | 11 | 0 | DHK00186 | 1 | 18825.6 | 21662.7 | 2837.1 | 444.44 | 0 | 1260920.724 | 1287356.6852 | Ramna | New Ramna 33/11KV S/S
19 | Gulistan Complex | 11 | 0 | DHK00030 | 1 | 53533.1 | 53974.5 | 441.4 | 444.44 | 0 | 196175.816 | 200288.7599 | Ramna | New Ramna 33/11KV S/S
20 | Mohanagor Nattomanso | 11 | 0 | DHK 00008 | 1 | 99592.4 | 99681.5 | 89.1 | 444.44 | 0 | 39599.604 | 40429.8335 | Ramna | New Ramna 33/11KV S/S
21 | DIT 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00196 | 1 | 22347.2 | 23893.8 | 1546.6 | 444.44 | 0 | 687370.904 | 701782.0483 | Motijheel | New Ramna 33/11KV S/S
22 | Jail | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S
23 | Kosturi Bazar | 11 | 0 | HA021100713-02 | 1 | 75828041 | 75857044 | 29003 | 1 | 0 | 99899.2222 | 101993.6695 | Ramna | New Ramna 33/11KV S/S
24 | Kaptan Bazar | 11 | 0 | HA021101251-02 | 1 | 5704466 | 5820909 | 116443 | 1 | 0 | 401081.4444 | 409490.3581 | Narinda | New Ramna 33/11KV S/S
25 | G.T.V | 11 | 0 | HA-021101054-02 | 1 | 70326682 | 70498299 | 171617 | 1 | 0 | 591125.2222 | 603518.518 | Ramna | New Ramna 33/11KV S/S
26 | Kazi Alauddin Road | 11 | 0 | HA021100951-02 | 1 | 5582587 | 5667944 | 85357 | 1 | 0 | 294007.4444 | 300171.4873 | Bangshal | New Ramna 33/11KV S/S
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 | 0 | 2436 | 1 | 67422 | 67423 | 1 | 10 | 0 | 10 | 10.2097 | Ramna | New Ramna 33/11KV S/S
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 | 0 | 2437 | 1 | 87735 | 88090 | 355 | 10 | 0 | 3550 | 3624.4279 | Ramna | New Ramna 33/11KV S/S
7 | Pioneer | 11 | 0 | 06604395 | 1 | 23539.01 | 23641.25 | 102.24 | 8000 | 0 | 817920 | 826396.2524 | Ramna | Kakrail 33/11KV S/S
8 | Pir Saheber Goli | 11 | 0 | DHK-00102 | 1 | 72928.3 | 76172.5 | 3244.2 | 444.444 | 0 | 1441865.2248 | 1456807.534 | Rajarbag | Kakrail 33/11KV S/S
9 | Montri Para | 11 | 0 | DHK-00110 | 1 | 12423.2 | 12504.9 | 81.7 | 2222.22 | 0 | 181555.374 | 183436.8651 | Kakrail | Kakrail 33/11KV S/S
10 | Baily Road 11 kV Sw/S-2 | 11 | 0 | 9119865 | 1 | 58339.7 | 60588.9 | 2249.2 | 1000 | 0 | 2249200 | 2272508.865 | Kakrail | Kakrail 33/11KV S/S
11 | Jamuna U/G 11 KV Jonaki O/H | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S
12 | High Court | 11 | 0 | 1025651 | 1 | 28397.4 | 28699 | 301.6 | 1000 | 0 | 301600 | 304725.5352 | Ramna | Kakrail 33/11KV S/S
13 | Secretaiat | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S
16 | Shanti Nagar Bazar | 11 | 0 | 06604402 | 1 | 5556.49 | 5592.5 | 36.01 | 40000 | 0 | 1440400 | 1455327.1248 | Rajarbag | Kakrail 33/11KV S/S
17 | Tottho Bhovon | 11 | 0 | 9119867 | 1 | 31865.1 | 31865.1 | 0 | 1000 | Estimated | 263790 | 266523.7033 | Kakrail | Kakrail 33/11KV S/S
18 | Central Police Hospital/ PNT (Circuit House) | 11 | 0 | DHK00199 | 1 | 77786.4 | 78080.07 | 293.67 | 2222.22 | 0 | 652599.3474 | 659362.3521 | Kakrail | Kakrail 33/11KV S/S
19 | Baily Road 11 kV Sw/S-1 | 11 | 0 | DHK00027 | 1 | 54237.6 | 54773.6 | 536 | 2222.22 | 0 | 1191109.92 | 1203453.6068 | Kakrail | Kakrail 33/11KV S/S
20 | Bijoy Nagar | 11 | 0 | D1025656 | 1 | 63855.4 | 64877.9 | 1022.5 | 1000 | 0 | 1022500 | 1033096.3518 | Ramna | Kakrail 33/11KV S/S
21 | Shilpakala Academy | 11 | 0 | D0086137 | 1 | 23595.3 | 24493.9 | 898.6 | 1000 | 0 | 898600 | 907912.3538 | Ramna | Kakrail 33/11KV S/S
22 | Judges Complex | 11 | 0 | 06604344 | 1 | 664.38 | 667.77 | 3.39 | 40000 | 0 | 135600 | 137005.2472 | Kakrail | Kakrail 33/11KV S/S
23 | Auxiliary Transformer, AT-1 | 11 | 0 | 39333 | 1 | 492441 | 492441 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S
24 | Auxiliary Transformer, AT-2 | 11 | 0 | 39254 | 1 | 1195010 | 1195010 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S
8 | 11 kV Jamuna (F1) | 11 | 0 | BD017073 | 1 | 0.34 | 0.3512 | 0.0112 | 2000 | 0 | 22.4 | 22.5473 | Kakrail | BSMMU 33/11KV S/S
9 | 11 kV Pukur Par (F2) | 11 | 0 | BD017074 | 1 | 2860.85 | 2883.64 | 22.79 | 2000 | 0 | 45580 | 45879.8149 | Kakrail | BSMMU 33/11KV S/S
10 | 11 kV BSMMU Convention center (F3) | 11 | 0 | BD017075 | 1 | 1669.21 | 1695.63 | 26.42 | 2000 | 0 | 52840 | 53187.5695 | Kakrail | BSMMU 33/11KV S/S
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 | 0 | BD017076 | 1 | 2756.04 | 2841.69 | 85.65 | 2000 | 0 | 171300 | 172426.7726 | Kakrail | BSMMU 33/11KV S/S
12 | 11 kV Holi Family Feeder (F5) | 11 | 0 | BD017077 | 1 | 13334.88 | 13664.28 | 329.4 | 2000 | 0 | 658800 | 663133.437 | Kakrail | BSMMU 33/11KV S/S
13 | 11 kV Navy House Feeder (F6) | 11 | 0 | BD017078 | 1 | 25676.26 | 25982.79 | 306.53 | 2000 | 0 | 613060 | 617092.5697 | Kakrail | BSMMU 33/11KV S/S
14 | 11 kV Paribagh Feeder (F7) | 11 | 0 | BD017079 | 1 | 29530.52 | 30291.6 | 761.08 | 2000 | 0 | 1522160 | 1532172.4233 | Paribag | BSMMU 33/11KV S/S
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 | 0 | BD017080 | 1 | 5758.91 | 5957.89 | 198.98 | 2000 | 0 | 397960 | 400577.6906 | Paribag | BSMMU 33/11KV S/S
18 | 11 kV Oncology Bhaban (F9) | 11 | 0 | BD017083 | 1 | 2097.11 | 2161.63 | 64.52 | 2000 | 0 | 129040 | 129888.7959 | Paribag | BSMMU 33/11KV S/S
19 | Rupayan Trade Center | 11 | 0 | BD017084 | 1 | 790.58 | 928.49 | 137.91 | 2000 | 0 | 275820 | 277634.2814 | Kakrail | BSMMU 33/11KV S/S
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 | 0 | BD017085 | 1 | 1941.64 | 1996.69 | 55.05 | 2000 | 0 | 110100 | 110824.2128 | Kakrail | BSMMU 33/11KV S/S
21 | 11 kV BSMMU RMU (F12) | 11 | 0 | BD017086 | 1 | 1799.23 | 1881.92 | 82.69 | 2000 | 0 | 165380 | 166467.8321 | Paribag | BSMMU 33/11KV S/S
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 | 0 | BD017087 | 1 | 3801.38 | 3915.28 | 113.9 | 2000 | 0 | 227800 | 229298.4167 | Paribag | BSMMU 33/11KV S/S
23 | 11 kV BCS Academy RMU (F14) | 11 | 0 | BD017088 | 1 | 928.43 | 965.83 | 37.4 | 2000 | 0 | 74800 | 75292.0174 | Paribag | BSMMU 33/11KV S/S
24 | Spare | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S
25 | BSMMU Super Specialist Hospital RMU | 11 | 0 | BD017090 | 1 | 845.61 | 971.62 | 126.01 | 2000 | 0 | 252020 | 253677.7304 | Paribag | BSMMU 33/11KV S/S
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKD4418 | 1 | 2310.34 | 2460.23 | 149.89 | 100 | 0 | 14989 | 15087.5942 | Paribag | BSMMU 33/11KV S/S
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S
3 | Chata Mosjid | 11 | 0 | 0 | 1 | 164850.7 | 167272.9 | 2422.2 | 1000 | 0 | 2422200 | 2426211.3577 | Kamrangirchar | LALBAGH New 33/11 KV S/S
4 | AC mosjid | 11 | 0 | 0 | 1 | 27060.73 | 4071.8 | -22988.93 | 1000 | Estimated | 1337961.24 | 1340177.0113 | Lalbag | LALBAGH New 33/11 KV S/S
5 | Kazi Reaz Uddin Road | 11 | 0 | 0 | 1 | 14366.9 | 16630.49 | 2263.59 | 1000 | 0 | 2263590 | 2267338.6868 | Lalbag | LALBAGH New 33/11 KV S/S
6 | Nazimuddin | 11 | 0 | 0 | 1 | 4214.292 | 4214.292 | 0 | 1000 | Estimated | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S
7 | Kamal Bagh | 11 | 0 | 0 | 1 | 101936 | 117683.69 | 15747.69 | 1000 | Estimated | 1581226.92 | 1583845.5588 | Lalbag | LALBAGH New 33/11 KV S/S
8 | Rahamatganj | 11 | 0 | 0 | 1 | 37932 | 37932 | 0 | 1000 | Estimated | 2554289.64 | 2558519.7488 | Lalbag | LALBAGH New 33/11 KV S/S
9 | Water Works 11kV Sw/S-1 | 11 | 0 | 0 | 1 | 16928.9 | 18780.18 | 1851.28 | 1000 | 0 | 1851280 | 1854345.8684 | Lalbag | LALBAGH New 33/11 KV S/S
12 | City Colony | 11 | 0 | 0 | 1 | 18357.9 | 20434.814 | 2076.914 | 1000 | 0 | 2076914 | 2080353.5364 | Lalbag | LALBAGH New 33/11 KV S/S
13 | Water Works 11kV Sw/S-2 | 11 | 0 | 0 | 1 | 26667.3 | 29754.25 | 3086.95 | 1000 | 0 | 3086950 | 3092062.2371 | Lalbag | LALBAGH New 33/11 KV S/S
14 | Chun Goli | 11 | 0 | 0 | 1 | 4641.936 | 5535.3348 | 893.3988 | 1000 | 0 | 893398.8 | 894878.3402 | Lalbag | LALBAGH New 33/11 KV S/S
15 | Alir Ghat | 11 | 0 | 0 | 1 | 115609.9 | 117703.2 | 2093.3 | 1000 | 0 | 2093300 | 2096766.6729 | Lalbag | LALBAGH New 33/11 KV S/S
16 | Club Ghat | 11 | 0 | 0 | 1 | 8835.142 | 11435.815 | 2600.673 | 1000 | Estimated | 2736738.9 | 2741271.1594 | Lalbag | LALBAGH New 33/11 KV S/S
17 | Debidas Ghat | 11 | 0 | 0 | 1 | 21794.4 | 21794.4 | 0 | 1000 | Estimated | 2615106.06 | 2619436.8857 | Lalbag | LALBAGH New 33/11 KV S/S
18 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S
15 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
16 | Sowari Ghat | 11 | 0 | 8838019 | 1 | 69444.8 | 72291.8 | 2847 | 1000 | 0 | 2847000 | 2829205.9908 | Lalbag | Lalbagh Old 33/11KV S/S
17 | Novo Kumar (Kara Odidoptor) | 11 | 0 | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 133796.124 | 132959.886 | Lalbag | Lalbagh Old 33/11KV S/S
19 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
20 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
22 | Eidgah | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1337961.24 | 1329598.8604 | Lalbag | Lalbagh Old 33/11KV S/S
23 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
24 | Modumoti | 11 | 0 | 0 | 1 | 77697 | 82497.9 | 4800.9 | 444.44 | Estimated | 2067758.28 | 2054834.6025 | Lalbag | Lalbagh Old 33/11KV S/S
25 | Lalbagh O/H | 11 | 0 | 61389152 | 1 | 439042 | 439667 | 625 | 1000 | Estimated | 1094695.56 | 1087853.6131 | Lalbag | Lalbagh Old 33/11KV S/S
26 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
29 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
30 | Water Works 11 kV Sw/S-2 | 11 | 0 | 61389109 | 1 | 398934 | 399921 | 987 | 1000 | 0 | 987000 | 980831.1601 | Lalbag | Lalbagh Old 33/11KV S/S
31 | Islambagh | 11 | 0 | 61389186 | 1 | 497490 | 498372 | 882 | 1000 | 0 | 882000 | 876487.4197 | Lalbag | Lalbagh Old 33/11KV S/S
32 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
33 | WASA Low Lift Pump | 11 | 0 | 61389202 | 1 | 15370 | 15416 | 46 | 1000 | 0 | 46000 | 45712.4958 | Lalbag | Lalbagh Old 33/11KV S/S
34 | Shahi Mosjid | 11 | 0 | 06604459 | 1 | 35231.3 | 35388.6 | 157.3 | 8000 | 0 | 1258400 | 1250534.8854 | Azimpur | Lalbagh Old 33/11KV S/S
35 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
36 | 33/0.4 kV Auxiliary Transformer | 0.415 | 0 | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S
7 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV
8 | Spare | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV
9 | Chawk Bazar | 11 | 0 | DHK-60904 | 1 | 946220.21 | 954595.7 | 8375.49 | 60 | 0 | 502529.4 | 508276.2976 | Lalbag | Mitford 33/11 kV
10 | Spare | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV
11 | Chatrabas | 11 | 0 | DHK-66485 | 1 | 776910 | 782736 | 5826 | 60 | 0 | 349560 | 353557.5482 | Bangshal | Mitford 33/11 kV
12 | Begum Bazar | 11 | 0 | DHK-66481 | 1 | 3547689 | 3586533 | 38844 | 60 | 0 | 2330640 | 2357293.0663 | Bangshal | Mitford 33/11 kV
13 | SCC ROAD | 11 | 0 | DHK-60901 | 1 | 995636.3 | 1021576.1 | 25939.8 | 60 | 0 | 1556388 | 1574186.7645 | Bangshal | Mitford 33/11 kV
16 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV
17 | Armanitola | 11 | 0 | DHK-61104 | 1 | 636742.1 | 652439.3 | 15697.2 | 60 | 0 | 941832 | 952602.7371 | Bangshal | Mitford 33/11 kV
18 | Mitford Hospital (RMU) | 11 | 0 | DHK-61101 | 1 | 365803 | 374512.4 | 8709.4 | 60 | 0 | 522564 | 528540.0121 | Bangshal | Mitford 33/11 kV
19 | Emamganj | 11 | 0 | DHK-68130 | 1 | 1416.62 | 1435.73 | 19.11 | 60000 | 0 | 1146600 | 1159712.4523 | Bangshal | Mitford 33/11 kV
20 | Kamal Dho Road | 11 | 0 | DHK-68129 | 1 | 1196.02 | 1205.82 | 9.8 | 60000 | 0 | 588000 | 594724.3345 | Lalbag | Mitford 33/11 kV
21 | Spare | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV
22 | Panghat | 11 | 0 | DHK-68127 | 1 | 1457.21 | 1481.94 | 24.73 | 60000 | 0 | 1483800 | 1500768.6523 | Bangshal | Mitford 33/11 kV
23 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | U0004460 | 1 | 5469.44 | 5513.28 | 43.84 | 100 | 0 | 4384 | 4434.1352 | Bangshal | Mitford 33/11 kV
7 | Chadni chwok | 11 | 0 | DHK60916 | 1 | 375816 | 386413 | 10597 | 60 | 0 | 635820 | 648152.1238 | Paribag | Azimpur 33/11 KV
8 | BGB | 11 | 0 | DHK61090 | 1 | 657048 | 661190 | 4142 | 60 | 0 | 248520 | 253340.1998 | Jigatola | Azimpur 33/11 KV
9 | Pari Bibi Mazar | 11 | 0 | DHK61091 | 1 | 673428 | 708482 | 35054 | 60 | 0 | 2103240 | 2144033.6462 | Azimpur | Azimpur 33/11 KV
10 | Azimpur | 11 | 0 | DHK61086 | 1 | 246143 | 264194 | 18051 | 60 | 0 | 1083060 | 1104066.6214 | Azimpur | Azimpur 33/11 KV
11 | Aazd | 11 | 0 | DHK61089 | 1 | 918408 | 938971 | 20563 | 60 | 0 | 1233780 | 1257709.9294 | Azimpur | Azimpur 33/11 KV
12 | Dayra Sharif | 11 | 0 | DHK61088 | 1 | 466279 | 482306 | 16027 | 60 | 0 | 961620 | 980271.2172 | Azimpur | Azimpur 33/11 KV
13 | Naya palton | 11 | 0 | DHK86065 | 1 | 1814.77 | 1842.39 | 27.62 | 60000 | 0 | 1657200 | 1689342.4234 | Azimpur | Azimpur 33/11 KV
16 | Viqarunnisa Noon School | 11 | 0 | DHK66477 | 1 | 1537959 | 1560667 | 22708 | 60 | 0 | 1362480 | 1388906.1459 | Azimpur | Azimpur 33/11 KV
17 | Subal Das Lane | 11 | 0 | DHK66480 | 1 | 3943041 | 3964091 | 21050 | 60 | 0 | 1263000 | 1287496.6695 | Azimpur | Azimpur 33/11 KV
18 | Lalbagh | 11 | 0 | DHK61093 | 1 | 607520 | 646194 | 38674 | 60 | 0 | 2320440 | 2365446.3751 | Azimpur | Azimpur 33/11 KV
19 | Zahrul Haque Hall | 11 | 0 | DHK66497 | 1 | 1206912 | 1217962 | 11050 | 60 | 0 | 663000 | 675859.2968 | Ramna | Azimpur 33/11 KV
20 | Eden College | 11 | 0 | DHK60917 | 1 | 910937 | 918378 | 7441 | 60 | 0 | 446460 | 455119.369 | Azimpur | Azimpur 33/11 KV
21 | Nilkhet/ PWD-01 | 11 | 0 | DHK60918 | 1 | 445447 | 456044 | 10597 | 60 | 0 | 635820 | 648152.1238 | Azimpur | Azimpur 33/11 KV
22 | BUET | 11 | 0 | DHK66496 | 1 | 923075 | 937828 | 14753 | 60 | 0 | 885180 | 902348.6159 | Ramna | Azimpur 33/11 KV
23 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIG2780 | 1 | 377494 | 381002 | 3508 | 1 | 0 | 2162 | 2203.9333 | Azimpur | Azimpur 33/11 KV
4 | Rasulpur | 11 | 0 | HA-021101042-02 | 1 | 87852313 | 89078209 | 1225896 | 1 | 0 | 1225896 | 1248201.2259 | Kamrangirchar | Kamrangirchar 33/11KV S/S
5 | Bheribadh | 11 | 0 | HA-021101105-02 | 1 | 57381342 | 59737086 | 2355744 | 1 | 0 | 2355744 | 2398606.8547 | Kamrangirchar | Kamrangirchar 33/11KV S/S
7 | Panna Tower 11 KV Faridpur Tower Express | 11 | 0 | 30799521 | 1 | 2615.33 | 2623.32 | 7.99 | 60000 | 0 | 479400 | 488122.7019 | Kamrangirchar | Kamrangirchar 33/11KV S/S
8 | Panna Battery Express | 11 | 0 | DHK15431 | 1 | 5225.42 | 5243.73 | 18.31 | 60000 | 0 | 1098600 | 1118589.0702 | Kamrangirchar | Kamrangirchar 33/11KV S/S
9 | Eidgah | 11 | 0 | 30799460 | 1 | 5239.4 | 5297.07 | 57.67 | 60000 | ESTIMATED | 2797555.32 | 2848456.9491 | Kamrangirchar | Kamrangirchar 33/11KV S/S
10 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S
12 | Huzur Para | 11 | 0 | HA-021101055-02 | 1 | 95819475 | 97687286 | 1867811 | 1 | 0 | 1867811 | 1901795.8946 | Kamrangirchar | Kamrangirchar 33/11KV S/S
13 | Kamrangirchar | 11 | 0 | HA-021101015-02 | 1 | 15882379 | 17588896 | 1706517 | 1 | 0 | 1706517 | 1737567.1439 | Kamrangirchar | Kamrangirchar 33/11KV S/S
14 | Munshihati | 11 | 0 | HA-021100854-02 | 1 | 47729145 | 48912982 | 1183837 | 1 | 0 | 1183837 | 1205376.9608 | Kamrangirchar | Kamrangirchar 33/11KV S/S
15 | Jhawchar | 11 | 0 | HA-021101028-02 | 1 | 96114856 | 97420106 | 1305250 | 1 | 0 | 1305250 | 1328999.0751 | Kamrangirchar | Kamrangirchar 33/11KV S/S
16 | RMU Express | 11 | 0 | HA-021101248-02 | 1 | 4001997 | 4693909 | 691912 | 1 | 0 | 691912 | 704501.3661 | Kamrangirchar | Kamrangirchar 33/11KV S/S
17 | Koyla Ghat | 11 | 0 | HA-021101259-02 | 1 | 12262339 | 14045899 | 1783560 | 1 | 0 | 1783560 | 1816011.9444 | Kamrangirchar | Kamrangirchar 33/11KV S/S
18 | Muslimbagh | 11 | 0 | HA-021100908-02 | 1 | 21197938 | 22904364 | 1706426 | 1 | 0 | 1706426 | 1737474.4882 | Kamrangirchar | Kamrangirchar 33/11KV S/S
19 | Noyagaon | 11 | 0 | HA-021101087-02 | 1 | 97903415 | 100516458 | 2613043 | 1 | 0 | 2613043 | 2660587.4202 | Kamrangirchar | Kamrangirchar 33/11KV S/S
20 | Nurbagh | 11 | 0 | HA-021100982-02 | 1 | 16859280 | 19118491 | 2259211 | 1 | 0 | 2259211 | 2300317.433 | Kamrangirchar | Kamrangirchar 33/11KV S/S
21 | Ali Nagar | 11 | 0 | HA-021101022-02 | 1 | 15074988 | 17434438 | 2359450 | 1 | 0 | 2359450 | 2402380.2856 | Kamrangirchar | Kamrangirchar 33/11KV S/S
12 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
13 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
14 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
15 | Nababgonj Park | 11 | 0 | 0 | 1 | 5185032 | 6757988 | 1572956 | 1 | 0 | 1572956 | 1573011.5868 | Azimpur | BGB 33/11 KV S/S
16 | Kholamura Ghat | 11 | 0 | 0 | 1 | 69207512 | 72049102 | 2841590 | 1 | 0 | 2841590 | 2841690.4191 | Kamrangirchar | BGB 33/11 KV S/S
17 | Khalpar | 11 | 0 | 0 | 1 | 80177553 | 81615032 | 1437479 | 1 | 0 | 1437479 | 1437529.7992 | Kamrangirchar | BGB 33/11 KV S/S
18 | Shahidnagar | 11 | 0 | 0 | 1 | 10527781 | 12336427 | 1808646 | 1 | 0 | 1808646 | 1808709.9159 | Azimpur | BGB 33/11 KV S/S
19 | BGB 1 No Gate | 11 | 0 | 0 | 1 | 28528895 | 29847534 | 1318639 | 1 | 0 | 1318639 | 1318685.5995 | Azimpur | BGB 33/11 KV S/S
21 | Ganaktuli | 11 | 0 | 0 | 1 | 21176889 | 21869943 | 693054 | 1 | 0 | 693054 | 693078.4919 | Jigatola | BGB 33/11 KV S/S
22 | Thana | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
23 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 26193780 | 28102896 | 1909116 | 1 | 0 | 1909116 | 1909183.4664 | Jigatola | BGB 33/11 KV S/S
24 | Sikder Medical | 11 | 0 | 0 | 1 | 32253872 | 33392224 | 1138352 | 1 | 0 | 1138352 | 1138392.2283 | Jigatola | BGB 33/11 KV S/S
25 | Gas Field | 11 | 0 | 0 | 1 | 47881720 | 49867262 | 1985542 | 1 | 0 | 1985542 | 1985612.1672 | Kamrangirchar | BGB 33/11 KV S/S
26 | Hazaribagh | 11 | 0 | 0 | 1 | 35481840 | 36947488 | 1465648 | 1 | 0 | 1465648 | 1465699.7946 | Jigatola | BGB 33/11 KV S/S
27 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
28 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 0 | 1 | 1938.35 | 1998.58 | 60.23 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 0 | 1 | 1534.23 | 1590.01 | 55.78 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S
0 | Salek Garden | 11 | 0 | 2761 | 1 | 465.5 | 506.46 | 40.96 | 60000 | 0 | 2457600 | 2460950.9042 | Jigatola | Jigatola New 33/11 KV S/S
4 | Jigatola Local | 11 | 0 | 2850 | 1 | 379.35 | 408.27 | 28.92 | 60000 | 0 | 1735200 | 1737565.9216 | Jigatola | Jigatola New 33/11 KV S/S
6 | City College | 11 | 0 | 2784 | 1 | 411.15 | 450.2 | 39.05 | 60000 | 0 | 2343000 | 2346194.6487 | Jigatola | Jigatola New 33/11 KV S/S
7 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S
8 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S
10 | Post Office | 11 | 0 | 2836 | 1 | 304.3 | 330.76 | 26.46 | 60000 | 0 | 1587600 | 1589764.671 | Jigatola | Jigatola New 33/11 KV S/S
11 | Leather Institute | 11 | 0 | 2835 | 1 | 50.97 | 54.22 | 3.25 | 60000 | 0 | 195000 | 195265.8799 | Jigatola | Jigatola New 33/11 KV S/S
12 | Mina Bazar | 11 | 0 | 2853 | 1 | 157.71 | 169.47 | 11.76 | 60000 | 0 | 705600 | 706562.076 | Jigatola | Jigatola New 33/11 KV S/S
13 | Mitali | 11 | 0 | 2852 | 1 | 229.64 | 278.85 | 49.21 | 60000 | 0 | 2952600 | 2956625.83 | Jigatola | Jigatola New 33/11 KV S/S
14 | Road-2 | 11 | 0 | 2839 | 1 | 505.57 | 546.35 | 40.78 | 60000 | 0 | 2446800 | 2450136.1786 | Jigatola | Jigatola New 33/11 KV S/S
15 | SS-2 | 11 | 0 | 2838 | 1 | 235.04 | 253.56 | 18.52 | 60000 | 0 | 1111200 | 1112715.1061 | Jigatola | Jigatola New 33/11 KV S/S
16 | Spare | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S
17 | Bou Bazar | 11 | 0 | 2843 | 1 | 411.11 | 440.65 | 29.54 | 60000 | 0 | 1772400 | 1774816.6433 | Jigatola | Jigatola New 33/11 KV S/S
18 | BGB | 11 | 0 | 2764 | 1 | 137.32 | 152.88 | 15.56 | 60000 | 0 | 933600 | 934872.9509 | Jigatola | Jigatola New 33/11 KV S/S
19 | Dhamondi-12 | 11 | 0 | 2763 | 1 | 328.2 | 354.88 | 26.68 | 60000 | 0 | 1600800 | 1602982.669 | Dhanmondi | Jigatola New 33/11 KV S/S
0 | Mitali Road | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
7 | Bou Bazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
8 | Mina Bazar | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
10 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
11 | Simanto Square | 11 | 0 | DHK60946 | 1 | 1096.72 | 1111.52 | 14.8 | 60000 | 0 | 888000 | 901151.3428 | Jigatola | Jigatola Old 33/11KV S/S
12 | Post Office | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
13 | Hazaribagh Sw/S-2 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
14 | Green Road Via Park | 11 | 0 | DHK61070 | 1 | 3387 | 3394.83 | 7.83 | 60000 | 0 | 469800 | 476757.7712 | Jigatola | Jigatola Old 33/11KV S/S
15 | PWD Quarters 11 kV Saleq Grand | 11 | 0 | DHK61028 | 1 | 3627.12 | 3628.17 | 1.05 | 60000 | 0 | 63000 | 63933.0345 | Jigatola | Jigatola Old 33/11KV S/S
18 | Road No.-2 | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
19 | Hzaribagh O/H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
20 | B.G.B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
21 | 11 kV City College | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
23 | Jigatala Local | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 243284 | 1 | 83197 | 83536 | 339 | 10 | 0 | 3390 | 3440.2061 | Jigatola | Jigatola Old 33/11KV S/S
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 412277 | 1 | 38966 | 38966 | 0 | 10 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S
7 | Spare | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S
0 | D Block dhaka uddyan | 11 | 0 | BD014031 | 1 | 47888.62 | 48238.67 | 350.05 | 1000 | 0 | 350050 | 356370.9019 | Adabor | Dhaka Uddyan 33/11 KV S/S
8 | Dill Mohammad O/H | 11 | 0 | BD014027 | 1 | 12080.08 | 13971.54 | 1891.46 | 1000 | 0 | 1891460 | 1925614.3584 | Adabor | Dhaka Uddyan 33/11 KV S/S
9 | Turag O/H | 11 | 0 | BD014028 | 1 | 24338.76 | 24750.51 | 411.75 | 1000 | 0 | 411750 | 419185.0275 | Adabor | Dhaka Uddyan 33/11 KV S/S
10 | Nabadoy O/H | 11 | 0 | BD014025 | 1 | 32795.11 | 34037.39 | 1242.28 | 1000 | 0 | 1242280 | 1264712.0241 | Adabor | Dhaka Uddyan 33/11 KV S/S
11 | Chandrima O/H | 11 | 0 | BD014024 | 1 | 2020.24 | 2884.39 | 864.15 | 1000 | 0 | 864150 | 879754.0777 | Adabor | Dhaka Uddyan 33/11 KV S/S
12 | Shyamoli Housing Project-2 | 11 | 0 | BD014029 | 1 | 21274.56 | 23461.67 | 2187.11 | 1000 | 0 | 2187110 | 2226602.9518 | Adabor | Dhaka Uddyan 33/11 KV S/S
13 | Spare | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S
16 | Spare | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S
17 | Spare | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S
18 | U Lab | 11 | 0 | BD013959 | 1 | 30498.01 | 33037.97 | 2539.96 | 1000 | 0 | 2539960 | 2585824.4138 | Satmasjid | Dhaka Uddyan 33/11 KV S/S
19 | Akota | 11 | 0 | BD014020 | 1 | 4552.75 | 5038.54 | 485.79 | 1000 | 0 | 485790 | 494561.9781 | Adabor | Dhaka Uddyan 33/11 KV S/S
20 | Burigonga O/H | 11 | 0 | BD014019 | 1 | 3494.01 | 3859.78 | 365.77 | 1000 | 0 | 365770 | 372374.7602 | Adabor | Dhaka Uddyan 33/11 KV S/S
21 | Garden City | 11 | 0 | BD014021 | 1 | 76417.41 | 78655.82 | 2238.41 | 1000 | 0 | 2238410 | 2278829.2831 | Satmasjid | Dhaka Uddyan 33/11 KV S/S
22 | Avenue O/H | 11 | 0 | BD014017 | 1 | 10136.7 | 11015.72 | 879.02 | 1000 | 0 | 879020 | 894892.5874 | Adabor | Dhaka Uddyan 33/11 KV S/S
23 | Chand Uddyan | 11 | 0 | BD014018 | 1 | 6109.27 | 6743.1 | 633.83 | 1000 | 0 | 633830 | 645275.1572 | Satmasjid | Dhaka Uddyan 33/11 KV S/S
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4416 | 1 | 1705.98 | 1720.85 | 14.87 | 100 | 0 | 1487 | 1513.851 | Adabor | Dhaka Uddyan 33/11 KV S/S
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4412 | 1 | 227.66 | 251.33 | 23.67 | 100 | 0 | 2367 | 2409.7413 | Adabor | Dhaka Uddyan 33/11 KV S/S
16 | Lalmatia O/H | 11 | 0 | DHK61042 | 1 | 3082.55 | 3104.91 | 22.36 | 60000 | 0 | 1341600 | 1343819.1874 | Satmasjid | Satmasjid 33/11KV S/S
16 | Asad Avenue (South) | 11 | 0 | DHK 60999 | 1 | 2890.2 | 2892.58 | 2.38 | 60000 | 0 | 142800 | 143036.2105 | Satmasjid | Satmasjid 33/11KV S/S
17 | Madrasha Road | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S
18 | Bashbari | 11 | 0 | DHK61002 | 1 | 2288.59 | 2314.11 | 25.52 | 60000 | 0 | 1531200 | 1533732.8114 | Satmasjid | Satmasjid 33/11KV S/S
19 | Road-27 | 11 | 0 | DHK61001 | 1 | 1423.31 | 1430.55 | 7.24 | 60000 | 0 | 434400 | 435118.5562 | Satmasjid | Satmasjid 33/11KV S/S
20 | Boishakhi O/H | 11 | 0 | DHK61024 | 1 | 3945.95 | 3992.78 | 46.83 | 60000 | 0 | 2809800 | 2814447.7883 | Dhanmondi | Satmasjid 33/11KV S/S
21 | Katasur O/H | 11 | 0 | DHK61003 | 1 | 3535.48 | 3557.69 | 22.21 | 60000 | 0 | 1332600 | 1334804.3002 | Satmasjid | Satmasjid 33/11KV S/S
22 | Nurjahan Road | 11 | 0 | DHK61000 | 1 | 1746.44 | 1769.35 | 22.91 | 60000 | 0 | 1374600 | 1376873.7739 | Shyamoli | Satmasjid 33/11KV S/S
25 | polpar over head | 11 | 0 | DHK61003 | 1 | 1692.23 | 1725.79 | 33.56 | 60000 | 0 | 2013600 | 2016930.7661 | Dhanmondi | Satmasjid 33/11KV S/S
26 | Satmosjid Housing | 11 | 0 | DHK61043 | 1 | 2792.38 | 2792.38 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S
27 | Physical College | 11 | 0 | DHK61041 | 1 | 3136.34 | 3172.69 | 36.35 | 60000 | 0 | 2181000 | 2184607.6683 | Satmasjid | Satmasjid 33/11KV S/S
28 | Asad Avenue (North) | 11 | 0 | DHK61022 | 1 | 2725.31 | 2725.31 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S
29 | Spare Feeder | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S
30 | Ghraphic artch college | 11 | 0 | DHK61023 | 1 | 987.59 | 1015.9 | 28.31 | 60000 | 0 | 1698600 | 1701409.7136 | Dhanmondi | Satmasjid 33/11KV S/S
31 | Mohammadpur O/H | 11 | 0 | DHK61025 | 1 | 2082.51 | 2104.86 | 22.35 | 60000 | 0 | 1341000 | 1343218.1949 | Shyamoli | Satmasjid 33/11KV S/S
32 | Bosila Feeder | 11 | 0 | DHK60997 | 1 | 3919.9 | 3970.07 | 50.17 | 60000 | 0 | 3010200 | 3015179.277 | Satmasjid | Satmasjid 33/11KV S/S
33 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIB 7375 | 1 | 5287.36 | 5415.28 | 127.92 | 60 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S
5 | Dhaka Uddyan | 11 | 0 | DHK86067 | 1 | 3249.24 | 3249.24 | 0 | 60000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV
0 | Shia Mosjid | 11 | 0 | DHK60950 | 1 | 3325.82 | 3353.91 | 28.09 | 60000 | 0 | 1685400 | 1677029.4105 | Shyamoli | Japan Garden 33/11 KV
6 | Shekhar Tek | 11 | 0 | DHK60977 | 1 | 2242.51 | 2275.45 | 32.94 | 60000 | 0 | 1976400 | 1966584.1503 | Adabor | Japan Garden 33/11 KV
7 | Madrasha Road | 11 | 0 | DHK61083 | 1 | 1906.72 | 1925.96 | 19.24 | 60000 | 0 | 1154400 | 1148666.6379 | Shyamoli | Japan Garden 33/11 KV
8 | Baitul Aman Housing | 11 | 0 | DHK668115 | 1 | 3926.4 | 3971.87 | 45.47 | 60000 | 0 | 2728200 | 2714650.3131 | Adabor | Japan Garden 33/11 KV
11 | Shyamoli Square | 11 | 0 | DHK86063 | 1 | 441.35 | 446.82 | 5.47 | 30000 | 0 | 164100 | 163284.9924 | Shyamoli | Japan Garden 33/11 KV
12 | Mohammadi Housing | 11 | 0 | DHK60948 | 1 | 3696.61 | 3719.11 | 22.5 | 60000 | 0 | 1350000 | 1343295.1846 | Adabor | Japan Garden 33/11 KV
13 | Chand Housing | 11 | 0 | DHK60867 | 1 | 2116.75 | 2131.68 | 14.93 | 60000 | 0 | 895800 | 891350.9825 | Satmasjid | Japan Garden 33/11 KV
14 | PC Culture Housing | 11 | 0 | DHK60979 | 1 | 3936.71 | 3977.85 | 41.14 | 60000 | 0 | 2468400 | 2456140.6176 | Adabor | Japan Garden 33/11 KV
15 | Mehedibagh | 11 | 0 | DHK68121 | 1 | 2110.63 | 2158.29 | 47.66 | 60000 | 0 | 2859600 | 2845397.7111 | Adabor | Japan Garden 33/11 KV
16 | 33/11 kV Incoming (Spare) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV
17 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | 0 | 1 | 630551 | 636966 | 6415 | 1 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV
0 | Mokarom Bhabon | 11 | 0 | 2761 | 1 | 40.93 | 44.12 | 3.19 | 60000 | 0 | 191400 | 191876.7922 | Ramna | Dhaka University 33/11 KV S/S
4 | 11 kV Shaid Minar RMU | 11 | 0 | 2850 | 1 | 99.47 | 105.12 | 5.65 | 60000 | 0 | 339000 | 339844.4752 | Ramna | Dhaka University 33/11 KV S/S
5 | 11 kV Shaidulla Hall | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S
6 | Spare | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
7 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
8 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
10 | MBA Bhabon | 11 | 0 | 2836 | 1 | 76.97 | 81.98 | 5.01 | 60000 | 0 | 300600 | 301348.8178 | Ramna | Dhaka University 33/11 KV S/S
11 | Suprime Court | 11 | 0 | 2835 | 1 | 34.09 | 39.19 | 5.1 | 60000 | 0 | 306000 | 306762.2696 | Ramna | Dhaka University 33/11 KV S/S
12 | Karjon Hall | 11 | 0 | 2853 | 1 | 39.47 | 45.01 | 5.54 | 60000 | 0 | 332400 | 333228.0341 | Ramna | Dhaka University 33/11 KV S/S
13 | Spare | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
14 | Swimming Pool | 11 | 0 | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S
15 | Spare | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
16 | Police Head Quarter RMU | 11 | 0 | 2772 | 1 | 47.4 | 54.79 | 7.39 | 60000 | 0 | 443400 | 444504.5437 | Ramna | Dhaka University 33/11 KV S/S
17 | Spare | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
18 | Spare | 11 | 0 | 2764 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
19 | Spare | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S
6 | Segunbagicha | 11 | 0 | DHK-C9360 | 1 | 50757.84 | 61185.99 | 10428.15 | 60 | 0 | 625689 | 628132.1417 | Ramna | Biddyut Bhaban 33/11 KV
0 | Secretariat RMU | 11 | 0 | DHK-C9379 | 1 | 63179.05 | 66319.31 | 3140.26 | 60 | 0 | 188415.6 | 189151.3106 | Ramna | Biddyut Bhaban 33/11 KV
7 | NBR RMU | 11 | 0 | DHK-C9319 | 1 | 28250.97 | 35791.29 | 7540.32 | 60 | 0 | 452419.2 | 454185.7713 | Ramna | Biddyut Bhaban 33/11 KV
8 | Ramna 11 kV Sw/S-2 | 11 | 0 | DHK-C9364 | 1 | 60208.43 | 81944.91 | 21736.48 | 60 | 0 | 1304188.8 | 1309281.295 | Ramna | Biddyut Bhaban 33/11 KV
11 | Ramna 11 kV Sw/S-1 | 11 | 0 | DHK-C9375 | 1 | 29996.47 | 30061.75 | 65.28 | 60 | 0 | 3916.8 | 3932.094 | Ramna | Biddyut Bhaban 33/11 KV
12 | Family Planning | 11 | 0 | DHK-C9378 | 1 | 26353.12 | 33829.12 | 7476 | 60 | 0 | 448560 | 450311.5022 | Ramna | Biddyut Bhaban 33/11 KV
13 | Muktijuddho Montranalaya | 11 | 0 | DHK-C9376 | 1 | 94472.83 | 109833.69 | 15360.86 | 60 | 0 | 921651.6 | 925250.3935 | Ramna | Biddyut Bhaban 33/11 KV
14 | Purana Palton | 11 | 0 | DHK-C9318 | 1 | 32574.67 | 38036.29 | 5461.62 | 60 | 0 | 327697.2 | 328976.7665 | Ramna | Biddyut Bhaban 33/11 KV
15 | Tip Top Feeder | 11 | 0 | DHK-C9318 | 1 | 21243.74 | 42816.99 | 21573.25 | 60 | 0 | 1294395 | 1299449.2529 | Kakrail | Biddyut Bhaban 33/11 KV
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 | 0 | DHKD3784 | 1 | 326797 | 331579 | 4782 | 1 | 0 | 4782 | 4800.6724 | Ramna | Biddyut Bhaban 33/11 KV
6 | Nearest O/H | 11 | 0 | 00000126 | 1 | 6636144 | 6865423 | 229279 | 1 | 0 | 229279 | 229906.9253 | Ramna | DMC 33/11 KV SS
0 | Jagannath Hall | 11 | 0 | 00000002 | 1 | 2337514 | 2433494 | 95980 | 1 | 0 | 95980 | 96242.8599 | Ramna | DMC 33/11 KV SS
7 | Samsun Nahar Hall | 11 | 0 | 00000024 | 1 | 8451499 | 8763059 | 311560 | 1 | 0 | 311560 | 312413.2678 | Ramna | DMC 33/11 KV SS
8 | Spare, 4L | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS
9 | Board Office O/H, (5L) | 11 | 0 | 00000023 | 1 | 19772992 | 20238430 | 465438 | 1 | 0 | 465438 | 466712.6927 | Lalbag | DMC 33/11 KV SS
10 | OT- Complex | 11 | 0 | 00000167 | 1 | 4882428 | 5287027 | 404599 | 1 | 0 | 404599 | 405707.0733 | Ramna | DMC 33/11 KV SS
11 | Alia Mdrasha O/H, (7L) | 11 | 0 | 00000148 | 1 | 9172738 | 9243737 | 70999 | 1 | 0 | 70999 | 71193.4446 | Lalbag | DMC 33/11 KV SS
12 | Majed Sordar Road | 11 | 0 | 00000164 | 1 | 50061716 | 51746392 | 1684676 | 1 | 0 | 1684676 | 1689289.8138 | Bangshal | DMC 33/11 KV SS
15 | Chankharpool, 9L | 11 | 0 | 00000001 | 1 | 43302856 | 44457492 | 1154636 | 1 | 0 | 1154636 | 1157798.1959 | Bangshal | DMC 33/11 KV SS
16 | Shahidullah College O/H, (10L) | 11 | 0 | 00000003 | 1 | 12057891 | 12322570 | 264679 | 1 | 0 | 264679 | 265403.8751 | Lalbag | DMC 33/11 KV SS
17 | Ananda Bazar | 11 | 0 | 00000111 | 1 | 14330765 | 14499445 | 168680 | 1 | 0 | 168680 | 169141.9631 | Ramna | DMC 33/11 KV SS
18 | Hosseni Dalan O/H, (12L) | 11 | 0 | 00000165 | 1.5 | 25661818 | 26760014 | 1098196 | 1 | 0 | 1647294 | 1651805.4359 | Lalbag | DMC 33/11 KV SS
19 | Badrun Nessa College | 11 | 0 | 00000006 | 1 | 18016036 | 18502514 | 486478 | 1 | 0 | 486478 | 487810.3149 | Lalbag | DMC 33/11 KV SS
20 | Dhaka Medical College, Unit-II | 11 | 0 | 00000125 | 1 | 10723614 | 11041413 | 317799 | 1 | 0 | 317799 | 318669.3545 | Ramna | DMC 33/11 KV SS
21 | Spare, 15L | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS
22 | Sheikh Hasina National Burn Institute | 11 | 0 | 00000127 | 1 | 18562194 | 19088354 | 526160 | 1 | 0 | 526160 | 527600.9918 | Ramna | DMC 33/11 KV SS
23 | Aux. Transformer, AT-1 | 0.415 | 0 | DHKF-7804 | 1 | 2396.38 | 2469.39 | 73.01 | 100 | 0 | 7301 | 7320.9952 | Ramna | DMC 33/11 KV SS
24 | Aux. Transformer, AT-2 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS
6 | Secratariet East | 11 | 0 | BD 013966 | 1 | 2923.08 | 3164.56 | 241.48 | 1000 | 0 | 241480 | 245463.3743 | Ramna | BB Aveneu 33/11 KV S/S
0 | Taher Bag O/H | 11 | 0 | BD 014045 | 1 | 16197.15 | 16925.42 | 728.27 | 1000 | 0 | 728270 | 740283.3012 | Narinda | BB Aveneu 33/11 KV S/S
7 | Al Raji Complex | 11 | 0 | BD 013983 | 1 | 11427.28 | 12207.81 | 780.53 | 1000 | 0 | 780530 | 793405.3649 | Ramna | BB Aveneu 33/11 KV S/S
8 | Raduni | 11 | 0 | BD 013999 | 1 | 23970.4 | 25230.43 | 1260.03 | 1000 | 0 | 1260030 | 1280815.0384 | Ramna | BB Aveneu 33/11 KV S/S
9 | Sundor Bon Square O/H | 11 | 0 | BD 013954 | 1 | 11288.72 | 11796.22 | 507.5 | 1000 | 0 | 507500 | 515871.5523 | Narinda | BB Aveneu 33/11 KV S/S
10 | Shromo Bhobon O/H | 11 | 0 | BD 013985 | 1 | 11101.22 | 11614.06 | 512.84 | 1000 | 0 | 512840 | 521299.6391 | Ramna | BB Aveneu 33/11 KV S/S
11 | Nawabpur Road | 11 | 0 | BD 013953 | 1 | 16889.08 | 17725.04 | 835.96 | 1000 | 0 | 835960 | 849749.7199 | Narinda | BB Aveneu 33/11 KV S/S
12 | Spair | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S
15 | Spare | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S
16 | Ahad Police Box | 11 | 0 | BD 013984 | 1 | 9425.66 | 9842.75 | 417.09 | 1000 | 0 | 417090 | 423970.1788 | Ramna | BB Aveneu 33/11 KV S/S
17 | Nearest O/H | 11 | 0 | BD 013997 | 1 | 2160.72 | 2274.44 | 113.72 | 1000 | 0 | 113720 | 115595.8875 | Ramna | BB Aveneu 33/11 KV S/S
18 | Natab Bhaban | 11 | 0 | BD 014000 | 1 | 4267.75 | 4442.04 | 174.29 | 1000 | 0 | 174290 | 177165.0302 | Ramna | BB Aveneu 33/11 KV S/S
19 | Spare | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S
20 | Awami League Party Office | 11 | 0 | BD 013956 | 1 | 1386.15 | 1395.25 | 9.1 | 1000 | 0 | 9100 | 9250.1106 | Ramna | BB Aveneu 33/11 KV S/S
21 | Khaddar Bazar | 11 | 0 | BD 014012 | 1 | 8542.4 | 8928.66 | 386.26 | 1000 | 0 | 386260 | 392631.6173 | Ramna | BB Aveneu 33/11 KV S/S
22 | Bangobondu National Stidium | 11 | 0 | BD 014008 | 1 | 5576.75 | 5862.17 | 285.42 | 1000 | 0 | 285420 | 290128.194 | Ramna | BB Aveneu 33/11 KV S/S
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4418 | 1 | 1107.72 | 1124.63 | 16.91 | 100 | 0 | 1691 | 1718.8942 | Ramna | BB Aveneu 33/11 KV S/S
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 38.09 | 41.9 | 3.81 | 100 | 0 | 381 | 387.2849 | Ramna | BB Aveneu 33/11 KV S/S
0 | 11 KV Ring Road Feeder | 11 | 0 | 77816675 | 1 | 41495.43 | 41632.55 | 137.12 | 8000 | 0 | 1096960 | 1124384 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Gano Bhavan RMU | 11 | 0 | DHK14997 | 1 | 995.65 | 995.68 | 0.03 | 40000 | 0 | 1200 | 1230 | Shere b.nagar | Kallyanpur 33/11KV S/S
0 | 11 KV Adabor O/H | 11 | 0 | DHK14957 | 1 | 4246.2 | 4319.26 | 73.06 | 40000 | 0 | 2922400 | 2995460 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Goidertek (DPDC) | 11 | 0 | DHK14996 | 1 | 9327.58 | 9341.2 | 13.62 | 40000 | 0 | 544800 | 558420 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Beribandh Feeder. | 11 | 0 | DHK14960 | 1 | 9628.58 | 9633.08 | 4.5 | 40000 | 0 | 180000 | 184500 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Sewarage Pump | 11 | 0 | DHK14959 | 1 | 1978.23 | 1991.3 | 13.07 | 40000 | 0 | 522800 | 535870 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Technical School (DPDC) | 11 | 0 | DHK15019 | 1 | 8022.92 | 8076.21 | 53.29 | 40000 | 0 | 2131600 | 2184890 | Adabor | Kallyanpur 33/11KV S/S
0 | 11 KV Mansurabad | 11 | 0 | 77816681 | 1 | 51055.21 | 51326.05 | 270.84 | 8000 | 0 | 2166720 | 2220888 | Adabor | Kallyanpur 33/11KV S/S
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40401.6 | 40402.7 | 1.1 | 1000 | 0 | 1100 | 1119.369 | Moghbazar | Moghbazar 33/11KV S/S
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 78790.6 | 79796.2 | 1005.6 | 1000 | 0 | 1005600 | 1023306.7911 | Tejgaon | Moghbazar 33/11KV S/S
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 155650.4 | 157212.8 | 1562.4 | 1000 | 0 | 1562400 | 1589911.0287 | Tejgaon | Moghbazar 33/11KV S/S
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 118462.4 | 118798.7 | 336.3 | 1000 | 0 | 336300 | 342221.6327 | Tejgaon | Moghbazar 33/11KV S/S
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 114028.3 | 115816.3 | 1788 | 1000 | 0 | 1788000 | 1819483.4353 | Kakrail | Moghbazar 33/11KV S/S
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 118573.6 | 120528.2 | 1954.6 | 1000 | 0 | 1954600 | 1989016.959 | Moghbazar | Moghbazar 33/11KV S/S
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 140567.1 | 141604.5 | 1037.4 | 1000 | 0 | 1037400 | 1055666.7314 | Tejgaon | Moghbazar 33/11KV S/S
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8175 | 8294.9 | 119.9 | 1000 | 0 | 119900 | 122011.2214 | Tejgaon | Moghbazar 33/11KV S/S
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9176.3 | 9327.8 | 151.5 | 1000 | 0 | 151500 | 154167.6401 | Tejgaon | Moghbazar 33/11KV S/S
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 116515 | 118443.2 | 1928.2 | 1000 | 0 | 1928200 | 1962152.1029 | Kakrail | Moghbazar 33/11KV S/S
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 81390.3 | 81467.2 | 76.9 | 1000 | 0 | 76900 | 78254.0694 | Tejgaon | Moghbazar 33/11KV S/S
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 169516.9 | 171354 | 1837.1 | 1000 | 0 | 1837100 | 1869447.9972 | Tejgaon | Moghbazar 33/11KV S/S
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 121728.8 | 122407.2 | 678.4 | 1000 | 0 | 678400 | 690345.3929 | Moghbazar | Moghbazar 33/11KV S/S
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 110579.4 | 111507.7 | 928.3 | 1000 | 0 | 928300 | 944645.6784 | Kakrail | Moghbazar 33/11KV S/S
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43008 | 43325.7 | 317.7 | 1000 | 0 | 317700 | 323294.1205 | Kakrail | Moghbazar 33/11KV S/S
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 | 13965044.1701 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S
1 | 11 kV TCB Feeder | 11 | T-4 | 0 | 1 | 33084.1 | 33653.6 | 569.5 | 1000 | 0 | 569500 | 587067.814 | Kakrail | Moghbazar 33/11KV S/S
2 | 11 kV Tejgaon SS-2 | 11 | T-4 | 0 | 1 | 25742.8 | 27179.6 | 1436.8 | 1000 | 0 | 1436800 | 1481122.0985 | Tejgaon | Moghbazar 33/11KV S/S
3 | Holy Day Inn | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 479040 | 493817.3233 | Tejgaon | Moghbazar 33/11KV S/S
4 | Polly Bhabon-2 | 11 | T-4 | 0 | 1 | 18298.6 | 18301.8 | 3.2 | 1000 | Consumer meter damaged, 12 months average | 28563 | 29444.1053 | Kakrail | Moghbazar 33/11KV S/S
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 | 0 | 1 | 9734.4 | 11538.8 | 1804.4 | 1000 | 0 | 1804400 | 1860061.7445 | Kakrail | Moghbazar 33/11KV S/S
6 | 11 kV Tejturibazar | 11 | T-4 | 0 | 1 | 128464.6 | 129174.3 | 709.7 | 1000 | 0 | 709700 | 731592.6735 | Kakrail | Moghbazar 33/11KV S/S
7 | Songsad | 11 | T-4 | 0 | 1 | 1826.4 | 1949 | 122.6 | 1000 | 0 | 122600 | 126381.9385 | Shere b.nagar | Moghbazar 33/11KV S/S
0 | Chennel 24 | 11 | T-4 | 0 | 1 | 7306 | 7307.13 | 1.13 | 1000 | 0 | 1130 | 1164.858 | Moghbazar | Moghbazar 33/11KV S/S
8 | Sonargaon | 11 | T-4 | 0 | 1 | 37300.4 | 38114.9 | 814.5 | 1000 | 0 | 814500 | 839625.5215 | Kakrail | Moghbazar 33/11KV S/S
0 | AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 7000 | 7215.9345 | Moghbazar | Moghbazar 33/11KV S/S
0 | AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 6157494.0116 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 87735 | 109708 | 21973 | 60 | 0 | 1318380 | 1314936.3633 | Kakrail | T&T 33/11 KV
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 352002 | 374779 | 22777 | 60 | 0 | 1366620 | 1363050.3594 | Kakrail | T&T 33/11 KV
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 925025 | 931981 | 6956 | 60 | 0 | 417360 | 416269.8468 | Moghbazar | T&T 33/11 KV
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1898014 | 1912434 | 14420 | 60 | 0 | 865200 | 862940.0791 | Moghbazar | T&T 33/11 KV
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 505.31 | 532.55 | 27.24 | 60000 | 0 | 1634400 | 1630130.9123 | Moghbazar | T&T 33/11 KV
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 854873 | 864753 | 9880 | 60 | 0 | 592800 | 591251.5937 | Kakrail | T&T 33/11 KV
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 416670 | 434155 | 17485 | 60 | 0 | 1049100 | 1046359.7284 | Moghbazar | T&T 33/11 KV
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 614262 | 642051 | 27789 | 60 | 0 | 1667340 | 1662984.8723 | Khilgaon | T&T 33/11 KV
4 | 11 kv Sherebangla | 11 | 0 | DHK60915 | 1 | 621193 | 645233 | 24040 | 60 | 0 | 1442400 | 1438632.4204 | Moghbazar | T&T 33/11 KV
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 285592 | 297424 | 11832 | 60 | 0 | 709920 | 708065.6738 | Khilgaon | T&T 33/11 KV
6 | Auxiliary | 0 | Export | U0004461 | 1 | 7917.57 | 7968.46 | 50.89 | 60 | 0 | 3053.4 | 3045.4245 | Moghbazar | T&T 33/11 KV
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 973062.72 | 978294.9507 | Moghbazar | Ullon local 33/11KV S/S
2 | Ullon | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1398777.66 | 1406298.9916 | Moghbazar | Ullon local 33/11KV S/S
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1337961.24 | 1345155.5572 | Moghbazar | Ullon local 33/11KV S/S
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1094695.56 | 1100581.8195 | Moghbazar | Ullon local 33/11KV S/S
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1337961.24 | 1345155.5572 | Moghbazar | Ullon local 33/11KV S/S
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1216328.4 | 1222868.6883 | Moghbazar | Ullon local 33/11KV S/S
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S
4 | AT-1 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S
5 | AT-2 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 4956.03 | 6677.95 | 1721.92 | 1000 | 0 | 1721920 | 1753548.1446 | Mugdapara | Madarteck 33/11KV S/S
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 93735.9 | 95560.9 | 1825 | 1000 | 0 | 1825000 | 1858521.5132 | Mugdapara | Madarteck 33/11KV S/S
3 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 4403.06 | 5644.71 | 1241.65 | 1000 | 0 | 1241650 | 1264456.5681 | Mugdapara | Madarteck 33/11KV S/S
0 | Goran | 11 | 0 | X1390296 | 1 | 22865.9 | 24684 | 1818.1 | 1000 | 0 | 1818100 | 1851494.7743 | Bashabo | Madarteck 33/11KV S/S
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 4720.47 | 6722.86 | 2002.39 | 1000 | 0 | 2002390 | 2039169.8043 | Mugdapara | Madarteck 33/11KV S/S
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 78510.9 | 79376.5 | 865.6 | 1000 | 0 | 865600 | 881499.2996 | Maniknagar | Madarteck 33/11KV S/S
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 76.4 | 282.33 | 205.93 | 1000 | Reading Corrected | 205930 | 209712.5124 | Mugdapara | Madarteck 33/11KV S/S
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 1473.9 | 1799.56 | 325.66 | 1000 | 0 | 325660 | 331641.7074 | Mugdapara | Madarteck 33/11KV S/S
2 | Mugdapara | 11 | 0 | X0854272 | 1 | 3255.6 | 3507.9 | 252.3 | 1000 | New Meter | 252300 | 256934.2344 | Maniknagar | Madarteck 33/11KV S/S
0 | Singapur | 11 | 0 | X1390302 (N) | 1 | 26648 | 28808.4 | 2160.4 | 1000 | 0 | 2160400 | 2200082.1244 | Banosree | Madarteck 33/11KV S/S
0 | Trimohony | 11 | 0 | X1390308 | 1 | 20943.4 | 22519.4 | 1576 | 1000 | 0 | 1576000 | 1604947.893 | Banosree | Madarteck 33/11KV S/S
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 6826.83 | 8633.04 | 1806.21 | 1000 | 0 | 1806210 | 1839386.3794 | Mugdapara | Madarteck 33/11KV S/S
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 2522.3 | 3107.93 | 585.63 | 1000 | 0 | 585630 | 596386.824 | Mugdapara | Madarteck 33/11KV S/S
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 700605 | 702966 | 2361 | 200 | 0 | 472200 | 480873.3471 | Mugdapara | Madarteck 33/11KV S/S
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 737906 | 739373 | 1467 | 200 | 0 | 293400 | 298789.1572 | Mugdapara | Madarteck 33/11KV S/S
3 | AT-2 | 0.415 | 0 | 63394003 | 1 | 83.3 | 89.44 | 6.14 | 80 | 0 | 491.2 | 500.2223 | Mugdapara | Madarteck 33/11KV S/S
1 | Nakhal Para Feeder | 11 | 0 | DHK60950 | 1 | 151292.3 | 176336.6 | 25044.3 | 60 | 0 | 1502658 | 1536369.5556 | Tejgaon | Tejgoan 33/11KV S/S
2 | Badda-Meghna Feeder | 11 | 0 | DHK60979 | 1 | 862789.4 | 876525.4 | 13736 | 60 | 0 | 824160 | 842649.7133 | Tejgaon | Tejgoan 33/11KV S/S
3 | Rasulbagh Feeder | 11 | 0 | DHK60948 | 1 | 900269.4 | 931276.3 | 31006.9 | 60 | 0 | 1860414 | 1902151.6741 | Tejgaon | Tejgoan 33/11KV S/S
4 | Lukas | 11 | 0 | 8A021100948-02 | 1 | 59791447 | 62085526 | 2294079 | 1 | 0 | 2294079 | 2345545.782 | Tejgaon | Tejgoan 33/11KV S/S
5 | PWD RMU | 11 | 0 | 0 | 1 | 649133.3 | 650851.8 | 1718.5 | 1 | 0 | 1718.5 | 1757.0539 | Tejgaon | Tejgoan 33/11KV S/S
1 | Civil Aviation Feeder | 11 | 0 | DHK60977 | 1 | 699019.7 | 744587.4 | 45567.7 | 60 | 0 | 2734062 | 2795399.6317 | Tejgaon | Tejgoan 33/11KV S/S
2 | Ahasanullah Eng. | 11 | 0 | DHK60867 | 1 | 837862.5 | 848834.7 | 10972.2 | 60 | 0 | 658332 | 673101.4258 | Tejgaon | Tejgoan 33/11KV S/S
3 | New GMG Feeder | 11 | 0 | DHK61106 | 1 | 933178.3 | 970375 | 37196.7 | 60 | 0 | 2231802 | 2281871.6214 | Tejgaon | Tejgoan 33/11KV S/S
4 | Shikajo | 11 | 0 | HA021101036-02 | 1 | 61139376 | 61878821 | 739445 | 1 | 0 | 739445 | 756034.1648 | Tejgaon | Tejgoan 33/11KV S/S
5 | Kahinur | 11 | 0 | 0 | 1 | 454902.7 | 475997.5 | 21094.8 | 60 | 0 | 1265688 | 1294083.2246 | Tejgaon | Tejgoan 33/11KV S/S
6 | Link road | 11 | 0 | 8A021100380-02 | 1 | 63080677 | 63506551 | 425874 | 1 | 0 | 425874 | 435428.3198 | Tejgaon | Tejgoan 33/11KV S/S
7 | Shanta | 11 | 0 | 0 | 1 | 279216.1 | 289500.3 | 10284.2 | 60 | 0 | 617052 | 630895.3248 | Tejgaon | Tejgoan 33/11KV S/S
1 | Karnafuly Feeder | 11 | 0 | DHK61084 | 1 | 32293.4 | 33015.5 | 722.1 | 1000 | 0 | 722100 | 738300.0364 | Tejgaon | Tejgoan 33/11KV S/S
2 | Butex | 11 | 0 | 0 | 1 | 713.5 | 803.1 | 89.6 | 1000 | 0 | 89600 | 91610.1416 | Tejgaon | Tejgoan 33/11KV S/S
3 | OriON LAB | 11 | 0 | 0 | 1 | 7852368 | 7919755 | 67387 | 1 | 20 | 243265.68 | 248723.2522 | Tejgaon | Tejgoan 33/11KV S/S
4 | Nina kabbo | 11 | 0 | 201101025-2 | 1 | 16076731 | 16283296 | 206565 | 1 | 8 | 97306.272 | 99489.3009 | Tejgaon | Tejgoan 33/11KV S/S
5 | Satrong | 11 | 0 | HA021100515-2 | 1 | 86979890 | 88090387 | 1110497 | 1 | 110 | 1337961.24 | 1367977.887 | Tejgaon | Tejgoan 33/11KV S/S
6 | South East RMU | 11 | 0 | 0 | 1 | 318.3 | 464.1 | 145.8 | 1000 | 0 | 145800 | 149070.967 | Tejgaon | Tejgoan 33/11KV S/S
7 | Rangs Bhaban | 11 | 0 | HA021100939-2 | 1 | 2765 | 121073 | 118308 | 1 | 13 | 158122.692 | 161670.1139 | Tejgaon | Tejgoan 33/11KV S/S
8 | Babli | 11 | 0 | 0 | 1 | 50404.8 | 51912.4 | 1507.6 | 1000 | 0 | 1507600 | 1541422.4274 | Tejgaon | Tejgoan 33/11KV S/S
0 | SPL | 11 | 0 | 0 | 1 | 2691.7 | 3055.8 | 364.1 | 1000 | 0 | 364100 | 372268.4438 | Tejgaon | Tejgoan 33/11KV S/S
9 | DNCC Hospital | 11 | 0 | 0 | 1 | 11564 | 12507.9 | 943.9 | 1000 | 0 | 943900 | 965076.0343 | Tejgaon | Tejgoan 33/11KV S/S
0 | 11/.415 kv Local transformer | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 6000 | 6134.6077 | Tejgaon | Tejgoan 33/11KV S/S
1 | Gonobhaban | 11 | 0 | DHKC9332 | 1 | 61864.31 | 65439.13 | 3574.82 | 60 | 0 | 214489.2 | 216836.1836 | Shere b.nagar | Asad Gate 33/11 KV S/S
2 | Rapa Plaza Feeder | 11 | 0 | DHKC9339 | 1 | 17025.01 | 36328.06 | 19303.05 | 60 | 0 | 1158183 | 1170856.0696 | Dhanmondi | Asad Gate 33/11 KV S/S
3 | Shukrabad/ South Plaza | 11 | 0 | DHKC9324 | 1 | 58877.32 | 77512.2 | 18634.88 | 60 | 0 | 1118092.8 | 1130327.1946 | Shere b.nagar | Asad Gate 33/11 KV S/S
4 | Wasa O/H | 11 | 0 | DHKC9333 | 1 | 26316.53 | 43612.07 | 17295.54 | 60 | 0 | 1037732.4 | 1049087.4751 | Satmasjid | Asad Gate 33/11 KV S/S
5 | Bangabandhu Memorial Museum | 11 | 0 | DHKC9334 | 1 | 14338.06 | 14682.59 | 344.53 | 60 | 0 | 20671.8 | 20897.995 | Dhanmondi | Asad Gate 33/11 KV S/S
6 | Iqbal Road O/H | 11 | 0 | DHKC9330 | 1 | 89627.44 | 116028.77 | 26401.33 | 60 | 0 | 1584079.8 | 1601413.1174 | Shyamoli | Asad Gate 33/11 KV S/S
7 | Town Hall | 11 | 0 | DHKC9351 | 1 | 90486.3 | 129046.8 | 38560.5 | 60 | 0 | 2313630 | 2338946.2013 | Shyamoli | Asad Gate 33/11 KV S/S
8 | Post Office | 11 | 0 | DHKC9331 | 1 | 89803.72 | 114408.51 | 24604.79 | 60 | 0 | 1476287.4 | 1492441.2314 | Shyamoli | Asad Gate 33/11 KV S/S
9 | Shangshad Bhaban | 11 | 0 | DHKC9370 | 1 | 91884.25 | 98850.73 | 6966.48 | 60 | 0 | 417988.8 | 422562.5169 | Shere b.nagar | Asad Gate 33/11 KV S/S
10 | Jakir Hossain Road | 11 | 0 | DHKC9373 | 1 | 31102.13 | 52169.33 | 21067.2 | 60 | 0 | 1264032 | 1277863.2905 | Satmasjid | Asad Gate 33/11 KV S/S
11 | New Colony O/H Feeder | 11 | 0 | DHKC9369 | 1 | 47348.96 | 69251.43 | 21902.47 | 60 | 0 | 1314148.2 | 1328527.8719 | Satmasjid | Asad Gate 33/11 KV S/S
12 | Aurangzeb Feeder | 11 | 0 | DHKC9321 | 1 | 78884.84 | 112056.46 | 33171.62 | 60 | 0 | 1990297.2 | 2012075.4293 | Shyamoli | Asad Gate 33/11 KV S/S
13 | Asadgate Local Feeder | 11 | 0 | DHKC9338 | 1 | 63243.46 | 93460.16 | 30216.7 | 60 | 0 | 1813002 | 1832840.2298 | Satmasjid | Asad Gate 33/11 KV S/S
14 | Sonarbangla Road | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S
15 | Humayun Road | 11 | 0 | DHKC9366 | 1 | 15150.34 | 42688.17 | 27537.83 | 60 | 0 | 1652269.8 | 1670349.266 | Shyamoli | Asad Gate 33/11 KV S/S
16 | NHA | 11 | 0 | DHKC9374 | 1 | 48654.25 | 52311.92 | 3657.67 | 60 | 12018 | 219460.2 | 221861.5773 | Shyamoli | Asad Gate 33/11 KV S/S
17 | Auxiliary transformer | 0.415 | 0 | 0 | 1 | 620619 | 626701 | 6082 | 1 | 0 | 6082 | 6148.5505 | Satmasjid | Asad Gate 33/11 KV S/S
1 | Angur Jora | 11 | 0 | 141 | 1 | 9842000 | 11717760 | 1875760 | 1 | 0 | 1875760 | 1879685.8324 | Banosree | Banasree 33/11 SS
2 | Block F-G Avenue | 11 | 0 | 68 | 1 | 129240 | 2777480 | 2648240 | 1 | 0 | 2648240 | 2653782.5782 | Banosree | Banasree 33/11 SS
3 | Banasree Main Road(Monpura) | 11 | 0 | 168 | 1 | 1057540 | 2694560 | 1637020 | 1 | 0 | 1637020 | 1640446.1666 | Banosree | Banasree 33/11 SS
4 | Baitul Kuddus | 11 | 0 | 62 | 1 | 3000320 | 5086120 | 2085800 | 1 | 0 | 2085800 | 2090165.4312 | Banosree | Banasree 33/11 SS
5 | Ideal | 11 | 0 | 0 | 1 | 5981320 | 6710680 | 729360 | 1 | 0 | 729360 | 730886.4987 | Banosree | Banasree 33/11 SS
6 | Central Mosque | 11 | 0 | 46 | 1 | 3601600 | 5624400 | 2022800 | 1 | 0 | 2022800 | 2027033.5767 | Banosree | Banasree 33/11 SS
7 | Larive | 11 | 0 | 47 | 1 | 6192360 | 7265440 | 1073080 | 1 | 0 | 1073080 | 1075325.8802 | Banosree | Banasree 33/11 SS
8 | Bank Colony | 11 | 0 | 0 | 1 | 2495880 | 3178720 | 682840 | 1 | 0 | 682840 | 684269.1356 | Khilgaon | Banasree 33/11 SS
9 | Salambagh | 11 | 0 | 0 | 1 | 208800 | 1440440 | 1231640 | 1 | 0 | 1231640 | 1234217.735 | Khilgaon | Banasree 33/11 SS
10 | Titas Road | 11 | 0 | 0 | 1 | 1065520 | 1526120 | 460600 | 1 | 0 | 460600 | 461564.0031 | Khilgaon | Banasree 33/11 SS
11 | AT-1 | 0.415 | 0 | 7734 | 1 | 3113.136 | 3113.136 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS
12 | AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS
1 | Meradia | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | Estimated | 0 | 0 | Banosree | Goran 33/11KV S/S
2 | Shipahibagh | 11 | 0 | HA-021001030-02 | 1 | 33607890 | 35007828 | 1399938 | 1 | 0 | 1399938 | 1411235.5236 | Bashabo | Goran 33/11KV S/S
3 | Farazi Hospital | 11 | 0 | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S
4 | West Bansree | 11 | 0 | New Meter | 1 | 87359660 | 89182268 | 1822608 | 1 | 0 | 1822608 | 1837316.4777 | Banosree | Goran 33/11KV S/S
5 | Model School(Nearest) | 11 | 0 | HA-030701099-03 | 1 | 10314560 | 12612480 | 2297920 | 1 | 0 | 2297920 | 2316464.2537 | Banosree | Goran 33/11KV S/S
6 | Bhuiyan Para | 11 | 0 | HA-021100508-02 | 1 | 48180236 | 50569666 | 2389430 | 1 | 0 | 2389430 | 2408712.741 | Banosree | Goran 33/11KV S/S
7 | Bonobithi (Ideal) School | 11 | 0 | HA-021100879-02 | 1 | 11161980 | 12579186 | 1417206 | 1 | 0 | 1417206 | 1428642.8767 | Banosree | Goran 33/11KV S/S
8 | AT-01 | 0.415 | 0 | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S
9 | AT-02 | 0.415 | 0 | 3043146 | 1 | 4579.3 | 4637.2 | 57.9 | 80 | 0 | 4632 | 4669.3803 | Banosree | Goran 33/11KV S/S
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 115 | 1398777.66 | 1399733.2864 | Dhanmondi | Lalmatia 33/11KV S/S
2 | Bangabobondhu museum | 11 | Export | 0 | 1 | 627449 | 627449 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 73972995 | 76132438 | 2159443 | 1 | 0 | 2159443 | 2160918.3029 | Dhanmondi | Lalmatia 33/11KV S/S
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 94656775 | 96836903 | 2180128 | 1 | 0 | 2180128 | 2181617.4346 | Dhanmondi | Lalmatia 33/11KV S/S
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25049.8 | 25242.7 | 192.9 | 3333.33 | 0 | 642999.357 | 643438.6457 | Dhanmondi | Lalmatia 33/11KV S/S
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 68422.1 | 68865.4 | 443.3 | 3333.33 | 0 | 1477665.189 | 1478674.7103 | Dhanmondi | Lalmatia 33/11KV S/S
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 76328 | 76765.7 | 437.7 | 3333.33 | 0 | 1458998.541 | 1459995.3095 | Dhanmondi | Lalmatia 33/11KV S/S
0 | Road 25 | 11 | Export | 0 | 1 | 69083.8 | 69416.1 | 332.3 | 3333.3 | 0 | 1107655.59 | 1108412.3257 | Dhanmondi | Lalmatia 33/11KV S/S
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37454.6 | 37575.5 | 120.9 | 3333.33 | 0 | 402999.597 | 403274.921 | Dhanmondi | Lalmatia 33/11KV S/S
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 56367922 | 57291365 | 923443 | 1 | 0 | 923443 | 924073.8841 | Dhanmondi | Lalmatia 33/11KV S/S
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 63621040 | 64955658 | 1334618 | 1 | 20 days | 2068657.9 | 2070071.1797 | Dhanmondi | Lalmatia 33/11KV S/S
1 | Lab aid/local RMU | 11 | 0 | 3C65883 | 1 | 44242 | 48899 | 4657 | 300 | 0 | 1397100 | 1422394.5672 | Paribag | Green Road 33/11KV S/S
2 | Green View | 11 | 0 | DHK000151 | 1 | 66171.3 | 66511.6 | 340.3 | 3333.33 | 0 | 1134332.199 | 1154869.3417 | Paribag | Green Road 33/11KV S/S
3 | Central Road | 11 | 0 | 65943 | 1 | 4190 | 9730 | 5540 | 300 | 0 | 1662000 | 1692090.5953 | Paribag | Green Road 33/11KV S/S
4 | New Market | 11 | 0 | DHK000194 | 1 | 45601.3 | 45899.3 | 298 | 3333.33 | 0 | 993332.34 | 1011316.673 | Jigatola | Green Road 33/11KV S/S
5 | DPH Feeder | 11 | 0 | HA-021100459 | 1 | 41222.8 | 41350 | 127.2 | 1 | 20 | 243265.68 | 247670.0176 | Paribag | Green Road 33/11KV S/S
6 | Dhanmondi Rd 4(md Banglo | 11 | 0 | 6604464 | 1 | 4428.98 | 4450.58 | 21.6 | 60000 | 0 | 1296000 | 1319464.1465 | Jigatola | Green Road 33/11KV S/S
1 | Green Road East | 11 | 0 | HA-021101050 | 1 | 90783634 | 92229088 | 1445454 | 1 | 0 | 1445454 | 1471624.0188 | Paribag | Green Road 33/11KV S/S
2 | North Road | 11 | 0 | HA-021100884 | 1 | 75203876 | 76809718 | 1605842 | 1 | 0 | 1605842 | 1634915.8518 | Paribag | Green Road 33/11KV S/S
3 | Green road SS | 11 | 0 | DHK00135 | 1 | 14731419 | 16023524 | 1292105 | 1 | 0 | 1292105 | 1315498.6273 | Paribag | Green Road 33/11KV S/S
4 | Plane Moszid | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 80 | 973062.72 | 990680.0705 | Paribag | Green Road 33/11KV S/S
5 | Malancha | 11 | 0 | HA-021100953 | 1 | 29474408 | 30602490 | 1128082 | 1 | 0 | 1128082 | 1148505.9825 | Paribag | Green Road 33/11KV S/S
0 | AT -1 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5090.5253 | Paribag | Green Road 33/11KV S/S
1 | North Dhanmondi | 11 | 0 | BD 014039 | 1 | 21479.71 | 21702.59 | 222.88 | 2000 | 0 | 445760 | 452285.2955 | Paribag | Green Road Dormatory 33/11 SS
2 | Lake circus | 11 | 0 | BD 014047 | 1 | 32675.64 | 33605.68 | 930.04 | 2000 | 0 | 1860080 | 1887308.9386 | Paribag | Green Road Dormatory 33/11 SS
3 | Bashir Uddin | 11 | 0 | BD 014037 | 1 | 13303.54 | 13668.5 | 364.96 | 2000 | 0 | 729920 | 740604.9957 | Paribag | Green Road Dormatory 33/11 SS
4 | Raza Bazar | 11 | 0 | BD 013939 | 1 | 19315.96 | 19945.29 | 629.33 | 2000 | 0 | 1258660 | 1277085.001 | Shere b.nagar | Green Road Dormatory 33/11 SS
5 | Rasel Squar | 11 | 0 | BD 013970 | 1 | 29493.11 | 30409.89 | 916.78 | 2000 | 0 | 1833560 | 1860400.7233 | Shere b.nagar | Green Road Dormatory 33/11 SS
6 | Bow Bazar | 11 | 0 | BD 013967 | 1 | 22285.98 | 22875.2 | 589.22 | 2000 | 0 | 1178440 | 1195690.6937 | Shere b.nagar | Green Road Dormatory 33/11 SS
7 | BRB Hospital | 11 | 0 | BD 014003 | 1 | 11692.21 | 12053.73 | 361.52 | 2000 | 0 | 723040 | 733624.2823 | Shere b.nagar | Green Road Dormatory 33/11 SS
8 | Green Road North | 11 | 0 | BD 013969 | 1 | 13569.2 | 14142.63 | 573.43 | 2000 | 0 | 1146860 | 1163648.4072 | Paribag | Green Road Dormatory 33/11 SS
1 | Water Bhaban | 11 | 0 | BD 014004 | 1 | 4582.24 | 4730.78 | 148.54 | 2000 | 0 | 297080 | 301428.8307 | Shere b.nagar | Green Road Dormatory 33/11 SS
2 | Alamin Road | 11 | 0 | BD 014006 | 1 | 17601.7 | 17886.83 | 285.13 | 2000 | 0 | 570260 | 578607.7993 | Paribag | Green Road Dormatory 33/11 SS
3 | Katal Bagan | 11 | 0 | 0 | 1 | 4467.6 | 5394.19 | 926.59 | 2000 | 0 | 1853180 | 1880307.9323 | Paribag | Green Road Dormatory 33/11 SS
4 | Eastern Pantho chaya | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS
5 | Kalabagan | 11 | 0 | BD 014005 | 1 | 5236.41 | 5394.19 | 157.78 | 2000 | 0 | 315560 | 320179.3518 | Paribag | Green Road Dormatory 33/11 SS
6 | Univer Hospital | 11 | 0 | BD 013963 | 1 | 479.37 | 606.64 | 127.27 | 2000 | 0 | 254540 | 258266.1053 | Paribag | Green Road Dormatory 33/11 SS
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 | 0 | BD 013971 | 1 | 9011.39 | 9267.96 | 256.57 | 2000 | 0 | 513140 | 520651.6433 | Paribag | Green Road Dormatory 33/11 SS
1 | Matir Masjid | 11 | 0 | DHK00170 | 1 | 15455.6 | 17730 | 2274.4 | 888.8889 | 0 | 2021688.8889 | 2023352.6919 | Khilgaon | Taltola 33/11KV S/S
2 | Hajipara | 11 | 0 | DHK-00108 | 1 | 919.3 | 1596.3 | 677 | 2222.2222 | 0 | 1504444.4444 | 1505682.5673 | Khilgaon | Taltola 33/11KV S/S
3 | Nearest Feeder | 11 | 0 | DHK-00106 | 1 | 90742 | 90788.1 | 46.1 | 2222.222 | 0 | 102444.4342 | 102528.7436 | Bashabo | Taltola 33/11KV S/S
4 | Reazbagh | 11 | 0 | DHK-00109 | 1 | 93540 | 94301.5 | 761.5 | 2222.222 | 0 | 1692222.053 | 1693614.7124 | Khilgaon | Taltola 33/11KV S/S
5 | Chowdhury Para | 11 | 0 | DHK-00107 | 1 | 51625.8 | 51884.4 | 258.6 | 2222.222 | 0 | 574666.6092 | 575139.5465 | Khilgaon | Taltola 33/11KV S/S
6 | Model Colleg | 11 | 0 | 9122392 | 1 | 2430.4 | 2456.34 | 25.94 | 40000 | 0 | 1037600 | 1038453.9207 | Khilgaon | Taltola 33/11KV S/S
1 | East Rampura | 11 | 0 | DHK-00181 | 1 | 96542 | 97163 | 621 | 2222.222 | 0 | 1379999.862 | 1381135.5698 | Khilgaon | Taltola 33/11KV S/S
2 | Adarshabagh | 11 | 0 | DHK-00090 | 1 | 46583.7 | 47488.7 | 905 | 2222.222 | 0 | 2011110.91 | 2012766.0076 | Bashabo | Taltola 33/11KV S/S
3 | Khailgaon Govt Colony | 11 | 0 | DHK00167 | 1 | 72902.7 | 73598.82 | 696.12 | 2222.222 | 0 | 1546933.1786 | 1548206.2687 | Khilgaon | Taltola 33/11KV S/S
4 | TV Road | 11 | 0 | 6604434 | 1 | 4966.58 | 4998.51 | 31.93 | 40000 | 0 | 1277200 | 1278251.1059 | Khilgaon | Taltola 33/11KV S/S
5 | Tilpa Para | 11 | 0 | 06604476 | 1 | 6510.58 | 6526.36 | 15.78 | 40000 | 0 | 631200 | 631719.4629 | Bashabo | Taltola 33/11KV S/S
1 | Navana | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S
7 | Shantipur | 11 | 0 | 0660444 | 1 | 10045960 | 10278394 | 232434 | 1 | 0 | 232434 | 232625.2878 | Bashabo | Taltola 33/11KV S/S
2 | AT-01 | 0.415 | 0 | 9187958 | 1 | 148.1 | 283.22 | 135.12 | 80 | 0 | 5000 | 5004.1149 | Bashabo | Taltola 33/11KV S/S
3 | AT-02 | 0.415 | 0 | 9187959 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S
1 | Sher-e-Banglanagar Local | 11 | 0 | DHK 66503 | 1 | 71658 | 73849 | 2191 | 60 | 0 | 131460 | 137740.1655 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
2 | Mirpur Road East | 11 | 0 | DHK 60961 | 1 | 796344 | 805750 | 9406 | 60 | 0 | 564360 | 591320.8565 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
3 | Gonobhaban school | 11 | 0 | DHK 66492 | 1 | 516834 | 519667 | 2833 | 60 | 0 | 169980 | 178100.36 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
4 | Babor Road | 11 | 0 | DHK 66489 | 1 | 663765 | 688132 | 24367 | 60 | 0 | 1462020 | 1531864.2685 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S
5 | College Gate | 11 | 0 | DHK 66487 | 1 | 2526065 | 2552998 | 26933 | 60 | 0 | 1615980 | 1693179.314 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S
7 | Hospital RMU | 11 | 0 | DHK 66491 | 1 | 864853 | 873509 | 8656 | 60 | 0 | 519360 | 544171.0965 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
1 | Shamoly Square | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S
2 | Gonobhaban RMU | 11 | 0 | DHK 60964 | 1 | 188092.2 | 189395.3 | 1303.1 | 60 | 0 | 78186 | 81921.1363 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
3 | Krishi University | 11 | 0 | DHK 60963 | 1 | 321467.8 | 330598.6 | 9130.8 | 60 | 0 | 547848 | 574020.0379 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
4 | NEC | 11 | 0 | DHK 86073 | 1 | 20.77 | 25.3 | 4.53 | 60000 | 0 | 271800 | 284784.5503 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
5 | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 305.62 | 323.21 | 17.59 | 60000 | 0 | 432714 | 453385.8053 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
5 | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 305.62 | 323.21 | 17.59 | 60000 | 0 | 622686 | 652433.232 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S
6 | Netor | 11 | 0 | DHK 60962 | 1 | 83465.3 | 92954.2 | 9488.9 | 60 | 0 | 569334 | 596532.4766 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
7 | BICC | 11 | 0 | 0 | 1 | 25.57 | 26.67 | 1.1 | 60000 | 0 | 66000 | 69152.9813 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
8 | Auxiliary | 0.415 | 0 | 0 | 1 | 5000.69 | 5090.45 | 89.76 | 60 | 0 | 5385.6 | 5642.8833 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S
1 | City Corporation | 11 | 0 | 93 | 1 | 38123148 | 38782904 | 659756 | 1 | 0 | 659756 | 660250.7383 | Bashabo | Mugdhapara Hospital 33/11 KV SS
2 | Bot tola | 11 | 0 | 0 | 1 | 46813724 | 49052840 | 2239116 | 1 | 0 | 2239116 | 2240795.0697 | Maniknagar | Mugdhapara Hospital 33/11 KV SS
3 | Jhilpar | 11 | 0 | 145 | 1 | 31434404 | 32593720 | 1159316 | 1 | 0 | 1159316 | 1160185.3486 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
4 | Central Bashaboo | 11 | 0 | 128 | 1 | 32312322 | 34044596 | 1732274 | 1 | 0 | 1732274 | 1733572.9987 | Bashabo | Mugdhapara Hospital 33/11 KV SS
5 | Kadamtala | 11 | 0 | 8 | 1.5 | 16228480 | 17533438 | 1304958 | 1 | 0 | 1957437 | 1958904.8441 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
6 | Ansar VDP | 11 | 0 | 119 | 1 | 16573440 | 17300398 | 726958 | 1 | 0 | 726958 | 727503.1317 | Khilgaon | Mugdhapara Hospital 33/11 KV SS
7 | Mugda Hospital Express-01 | 11 | 0 | 0 | 1 | 5037147 | 5309707 | 272560 | 1 | 0 | 272560 | 272764.3875 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
8 | Boro Masjid | 11 | 0 | 7 | 1.22 | 44310612 | 45410408 | 1099796 | 1 | 0 | 1341751.12 | 1342757.2732 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
1 | Anandodhara | 11 | 0 | 120 | 1 | 44045612 | 44960492 | 914880 | 1 | 0 | 914880 | 915566.0508 | Maniknagar | Mugdhapara Hospital 33/11 KV SS
2 | Culvert | 11 | 0 | 117 | 1 | 33041120 | 34952276 | 1911156 | 1 | 0 | 1911156 | 1912589.1389 | Bashabo | Mugdhapara Hospital 33/11 KV SS
3 | Mugda Hospital Express-02 | 11 | 0 | 97 | 1 | 4845548 | 4845548 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
4 | Jhor Pukur | 11 | 0 | 98 | 1 | 21673908 | 23101984 | 1428076 | 1 | 0 | 1428076 | 1429146.8866 | Bashabo | Mugdhapara Hospital 33/11 KV SS
5 | T&T | 11 | 0 | 99 | 1 | 21219428 | 22071346 | 851918 | 1 | 0 | 851918 | 852556.8368 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
6 | Haider Ali | 11 | 0 | 9 | 1 | 61336572 | 62774928 | 1438356 | 1 | 0 | 1438356 | 1439434.5953 | Maniknagar | Mugdhapara Hospital 33/11 KV SS
0 | 11kv Tilpapara | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 2150000 | 2151612.2434 | Bashabo | Mugdhapara Hospital 33/11 KV SS
7 | AT-01 | 11 | 0 | 0 | 1 | 2720 | 2782 | 62 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
8 | AT-02 | 11 | 0 | 0 | 1 | 8.55 | 17 | 8.45 | 1 | 0 | 8.45 | 8.4563 | Mugdapara | Mugdhapara Hospital 33/11 KV SS
1 | Shantinagar s/s-1 | 11 | 0 | DHK60932 | 1 | 189060 | 232427 | 43367 | 60 | 0 | 2602020 | 2616486.0095 | Rajarbag | Khillgaon 33/11KV S/S
2 | Gulbagh | 11 | 0 | DHK60934 | 1 | 106648 | 111867 | 5219 | 60 | 0 | 313140 | 314880.9114 | Rajarbag | Khillgaon 33/11KV S/S
3 | Rampura BTV | 11 | 0 | DHK60933 | 1 | 14049 | 14053 | 4 | 60 | 0 | 240 | 241.3343 | Khilgaon | Khillgaon 33/11KV S/S
4 | West Shantibag | 11 | 0 | DHK60926 | 1 | 474980 | 490108 | 15128 | 60 | 0 | 907680 | 912726.2746 | Rajarbag | Khillgaon 33/11KV S/S
1 | East Malibagh | 11 | 0 | DHK60929 | 1 | 516292 | 537667 | 21375 | 60 | 0 | 1282500 | 1289630.0978 | Rajarbag | Khillgaon 33/11KV S/S
2 | Police Line | 11 | 0 | DHK60930 | 1 | 535700 | 545249 | 9549 | 60 | 0 | 572940 | 576125.2774 | Rajarbag | Khillgaon 33/11KV S/S
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 | 0 | DHK61017 | 1 | 185510 | 187933 | 2423 | 60 | 0 | 145380 | 146188.2445 | Rajarbag | Khillgaon 33/11KV S/S
4 | Benjir Bagan | 11 | 0 | DHK60985 | 1 | 154680 | 157675 | 2995 | 60 | 0 | 179700 | 180699.0476 | Rajarbag | Khillgaon 33/11KV S/S
6 | AT-1 & AT-2 | 0.415 | 0 | ELIB 7374 | 1 | 1628.18 | 1628.18 | 0 | 60 | 0 | 0 | 0 | Rajarbag | Khillgaon 33/11KV S/S
1 | Spare | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S
2 | Monipuripara west | 11 | 0 | BD013947 | 1 | 27765.03 | 28604.46 | 839.43 | 1000 | 0 | 839430 | 873090.4062 | Shere b.nagar | Monipuripara 33/11 KV S/S
3 | Biggan College | 11 | 0 | BD013949 | 1 | 15670 | 16491.07 | 821.07 | 1000 | 0 | 821070 | 853994.1863 | Kakrail | Monipuripara 33/11 KV S/S
4 | Green Road South | 11 | 0 | BD013948 | 1 | 25691 | 26639.32 | 948.32 | 1000 | 0 | 948320 | 986346.7996 | Shere b.nagar | Monipuripara 33/11 KV S/S
5 | BARC Building O/H | 11 | 0 | BD014010 | 1 | 10958.76 | 11567.27 | 608.51 | 1000 | 0 | 608510 | 632910.7169 | Shere b.nagar | Monipuripara 33/11 KV S/S
6 | Green Road North | 11 | 0 | BD014036 | 1 | 51351.51 | 53150.66 | 1799.15 | 1000 | 0 | 1799150 | 1871294.3358 | Shere b.nagar | Monipuripara 33/11 KV S/S
7 | Chundrima Uddan | 11 | 0 | BD014035 | 1 | 25998.03 | 26974.49 | 976.46 | 1000 | 0 | 976460 | 1015615.1889 | Shere b.nagar | Monipuripara 33/11 KV S/S
8 | Spare-02 | 11 | 0 | BD013940 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S
1 | Spare-03 | 11 | 0 | BD013946 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S
2 | kawran Bazar North | 11 | 0 | BD013964 | 1 | 40112.39 | 40112.39 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Monipuripara 33/11 KV S/S
3 | NAM Bhanan RMU | 11 | 0 | BD013950 | 1 | 12279.22 | 13253.69 | 974.47 | 1000 | 0 | 974470 | 1013545.3917 | Shere b.nagar | Monipuripara 33/11 KV S/S
4 | Novo Theater | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S
5 | Monipuripara Nearest | 11 | 0 | BD013962 | 1 | 35167.77 | 35872.57 | 704.8 | 1000 | 0 | 704800 | 733061.8614 | Tejgaon | Monipuripara 33/11 KV S/S
6 | Holy Cross | 11 | 0 | BD013965 | 1 | 32798.35 | 33881.78 | 1083.43 | 1000 | 0 | 1083430 | 1126874.592 | Tejgaon | Monipuripara 33/11 KV S/S
7 | Honda Goli | 11 | 0 | BD014011 | 1 | 10455.11 | 11371.49 | 916.38 | 1000 | 0 | 916380 | 953126.0337 | Tejgaon | Monipuripara 33/11 KV S/S
8 | Navy Quarter | 11 | 0 | BD013941 | 1 | 4611.73 | 4780.31 | 168.58 | 1000 | 0 | 168580 | 175339.91 | Tejgaon | Monipuripara 33/11 KV S/S
9 | AT-01 | 0.415 | 0 | 0 | 1 | 1684.35 | 1762.39 | 78.04 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S
10 | AT-02 | 0.415 | 0 | 0 | 1 | 585.48 | 585.48 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S
1 | Doctor Goli | 11 | 0 | BD013944 | 1 | 4955.77 | 5839.76 | 883.99 | 1000 | 0 | 883990 | 898591.0283 | Moghbazar | Ispahani 33/11 KV SS
2 | Ispahani | 11 | 0 | BD013947 | 1 | 5545.8 | 6529.14 | 983.34 | 1000 | 0 | 983340 | 999582.0108 | Moghbazar | Ispahani 33/11 KV SS
3 | BTCL | 11 | 0 | BD013949 | 1 | 2918.2 | 3442.04 | 523.84 | 1000 | 0 | 523840 | 532492.3633 | Kakrail | Ispahani 33/11 KV SS
4 | Vikarunnesa | 11 | 0 | BD013948 | 1 | 1899.46 | 2973.78 | 1074.32 | 1000 | 0 | 1074320 | 1092064.7445 | Kakrail | Ispahani 33/11 KV SS
5 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
6 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
7 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
8 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
1 | Wireless | 11 | 0 | 0 | 1 | 3813.87 | 4695.65 | 881.78 | 1000 | 0 | 881780 | 896344.5253 | Moghbazar | Ispahani 33/11 KV SS
2 | Kazir Goli | 11 | 0 | 0 | 1 | 2485.21 | 3648.07 | 1162.86 | 1000 | 0 | 1162860 | 1182067.1763 | Kakrail | Ispahani 33/11 KV SS
3 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
4 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
5 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
6 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
7 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
8 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
9 | AT-01 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
10 | AT-02 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 205402.5 | 207823.5 | 2421 | 1000 | 0 | 2421000 | 2438789.3271 | Siddirgonj | Siddhirganj 33/11KV S/S
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16450 | 16587.7 | 137.7 | 1000 | 0 | 137700 | 138711.8093 | Siddirgonj | Siddhirganj 33/11KV S/S
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 103711.2 | 105223.6 | 1512.4 | 1000 | 0 | 1512400 | 1523513.0022 | Siddirgonj | Siddhirganj 33/11KV S/S
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 162380.7 | 164769.1 | 2388.4 | 1000 | 0 | 2388400 | 2405949.7847 | Siddirgonj | Siddhirganj 33/11KV S/S
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6871.1 | 6907.4 | 36.3 | 1000 | 0 | 36300 | 36566.7297 | Siddirgonj | Siddhirganj 33/11KV S/S
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 70624.1 | 71952.3 | 1328.2 | 1000 | 0 | 1328200 | 1337959.5143 | Siddirgonj | Siddhirganj 33/11KV S/S
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 139518 | 141739.7 | 2221.7 | 1000 | 0 | 2221700 | 2238024.8856 | Siddirgonj | Siddhirganj 33/11KV S/S
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 53.7495 | 64.2821 | 10.5326 | 40000 | 0 | 421304 | 424399.7103 | Matuail | Siddhirganj 33/11KV S/S
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 12120.8 | 12873.4 | 752.6 | 1000 | 0 | 752600 | 758130.0486 | Siddirgonj | Siddhirganj 33/11KV S/S
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 137987.5 | 140787.7 | 2800.2 | 1000 | 0 | 2800200 | 2820775.6603 | Siddirgonj | Siddhirganj 33/11KV S/S
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 | 0 | HA021101013-02 | 1 | 39314770 | 41495960 | 2181190 | 1 | 0 | 2181190 | 2206583.7096 | Matuail | Demra 33/11KV S/S
12 | 11 kV DND (WASA) Feeder. | 11 | 0 | HA021100992-02 | 1 | 5281672 | 5288520 | 6848 | 1 | 0 | 6848 | 6927.7253 | Siddirgonj | Demra 33/11KV S/S
13 | 11 kV Local Feeder | 11 | 0 | HA021100794-02 | 1 | 5234750 | 6636120 | 1401370 | 1 | 0 | 1401370 | 1417684.9395 | Siddirgonj | Demra 33/11KV S/S
14 | 11 kV Mouchak Feeder | 11 | 0 | DHK60888 | 1 | 783539.3 | 817710.4 | 34171.1 | 60 | 0 | 2050266 | 2074135.4747 | Siddirgonj | Demra 33/11KV S/S
15 | 11 kV Overhead-1 Feeder | 11 | 0 | HA021100829-02 | 1 | 74811660 | 75894360 | 1082700 | 1 | 0 | 1082700 | 1095304.9401 | Siddirgonj | Demra 33/11KV S/S
16 | 11 kV Provati Steel Feeder | 11 | 0 | DHK60874 | 1 | 544937.6 | 544937.6 | 0 | 60 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S
17 | 11 kV Islambagh Feeder. | 11 | 0 | DHKA2190 | 1 | 901.5142 | 950.6676 | 49.1534 | 60000 | 0 | 2949204 | 2983539.0327 | Matuail | Demra 33/11KV S/S
20 | 11 kV Taj Jute Feeder. | 11 | 0 | DHK61062 | 1 | 535795.2 | 563396.8 | 27601.6 | 60 | 0 | 1656096 | 1675376.4941 | Siddirgonj | Demra 33/11KV S/S
21 | 11 kV Al-Aksa Steel Feeder | 11 | 0 | DHK61061 | 1 | 682450.7 | 708770.6 | 26319.9 | 60 | 0 | 1579194 | 1597579.1906 | Siddirgonj | Demra 33/11KV S/S
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 | 0 | DHKA2189 | 1 | 866.1985 | 905.2486 | 39.0501 | 60000 | 0 | 2343006 | 2370283.5934 | Siddirgonj | Demra 33/11KV S/S
23 | 11 kV Over Head Feeder-2. | 11 | 0 | HA021100488-02 | 1 | 20655375 | 22702980 | 2047605 | 1 | 0 | 2047605 | 2071443.4949 | Demra | Demra 33/11KV S/S
24 | 11 kV Shimrail Express Feeder. | 11 | 0 | HA021100511-02 | 1 | 8067222 | 8067222 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S
25 | 11 kV Sarder & Khadem Steel Feeder | 11 | 0 | HA021100413-02 | 1 | 79362440 | 79767340 | 404900 | 1 | 0 | 404900 | 409613.9007 | Demra | Demra 33/11KV S/S
26 | 11 kV Siddhirgonj Mazar Feeder | 11 | 0 | HA021100393-02 | 1 | 45953012 | 46776260 | 823248 | 1 | 0 | 823248 | 832832.3648 | Siddirgonj | Demra 33/11KV S/S
27 | 11 kV AST Beverage Feeder | 11 | 0 | 0 | 1 | 18048062 | 19198420 | 1150358 | 1 | 0 | 1150358 | 1163750.6238 | Siddirgonj | Demra 33/11KV S/S
28 | 11 kV Karim Market Feeder | 11 | 0 | 0 | 1 | 50590947 | 52656280 | 2065333 | 1 | 0 | 2065333 | 2089377.8867 | Matuail | Demra 33/11KV S/S
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S
8 | 11 kV Dayagonj Feeder (=L11) | 11 | 0 | 2007755114 | 1 | 5629.39 | 5681.21 | 51.82 | 60000 | 0 | 3109200 | 3036942.6611 | Demra | Sarulia 33/11KV S/S
9 | 11 kV Karim Jute Feeder (=L12) | 11 | 0 | 30799484 | 1 | 20.6815 | 20.9002 | 0.2187 | 60000 | 0 | 13122 | 12817.0467 | Demra | Sarulia 33/11KV S/S
11 | 11 kV Konapara (=L13) **** | 11 | 0 | DHKA2191 | 1 | 1907.6395 | 1949.7345 | 42.095 | 60000 | 0 | 2525700 | 2467003.1131 | Demra | Sarulia 33/11KV S/S
12 | 11 kV Sanarpar Feeder (=L14) | 11 | 0 | 575926 | 1 | 43544.5 | 45987.8 | 2443.3 | 1000 | 0 | 2443300 | 2386518.0767 | Matuail | Sarulia 33/11KV S/S
13 | 11 kV Latif Bawani Feeder (=L15) | 11 | 0 | 30799450 | 1 | 1794.98 | 1800.14 | 5.16 | 60000 | 0 | 309600 | 302404.9427 | Demra | Sarulia 33/11KV S/S
14 | 11 kV Tengra Feeder (=L16) | 11 | 0 | 30799145 | 1 | 5334.41 | 5390.98 | 56.57 | 60000 | 0 | 3394200 | 3315319.3041 | Demra | Sarulia 33/11KV S/S
16 | 11 kV Police Line Feeder (=L17) | 11 | 0 | 30799480 | 1 | 3256.34 | 3276.53 | 20.19 | 60000 | 0 | 1211400 | 1183247.2468 | Demra | Sarulia 33/11KV S/S
17 | 11 kV Demra Bazar Feeder (=L18) | 11 | 0 | 30799119 | 1 | 1613.27 | 1621.73 | 8.46 | 60000 | 0 | 507600 | 495803.4526 | Demra | Sarulia 33/11KV S/S
18 | 11 kV Spare Feeder (=F9) | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S
19 | 11 kV Boxnagar Feeder (=F10) | 11 | 0 | HA021100493-02 | 1 | 71888660 | 74707530 | 2818870 | 1 | 0 | 2818870 | 2753359.8865 | Demra | Sarulia 33/11KV S/S
21 | 11 kV Baser Pool Feeder (=L11) | 11 | 0 | HA021100518-02 | 1 | 50684128 | 50715102 | 30974 | 1 | 0 | 30974 | 30254.1689 | Demra | Sarulia 33/11KV S/S
22 | 11 kV Dip-Pur Feeder (=L12) | 11 | 0 | HA021100697-02 | 1 | 16036849 | 18260443 | 2223594 | 1 | 0 | 2223594 | 2171918.011 | Demra | Sarulia 33/11KV S/S
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S
12 | 11 kV Khanpur Feeder | 11 | 0 | DHKC 9348 | 1 | 58257.88 | 86157.18 | 27899.3 | 60 | 0 | 1673958 | 1689432.0922 | N.Gonj (East) | Khanpur 33/11KV S/S
13 | 11 kV Mission Para Feeder. | 11 | 0 | DHKC 9347 | 1 | 50276.86 | 76552.26 | 26275.4 | 60 | 0 | 1576524 | 1591097.4109 | N.Gonj (East) | Khanpur 33/11KV S/S
14 | 11 kV Esha Kha Feeder | 11 | 0 | DHKC 9311 | 1 | 32200.54 | 49376.9 | 17176.36 | 60 | 0 | 1030581.6 | 1040108.3114 | N.Gonj (East) | Khanpur 33/11KV S/S
15 | 11 kV New Hazigonj Feeder | 11 | 0 | DHKC 9314 | 1 | 65.15 | 100.41 | 35.26 | 60000 | 0 | 2115600 | 2135156.6373 | N.Gonj (East) | Khanpur 33/11KV S/S
16 | 11 kV Spare Feeder. | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
19 | 11 kV Hospital RMU Feeder. | 11 | 0 | 6604412 | 1 | 1.83 | 2.82 | 0.99 | 60000 | 0 | 59400 | 59949.0945 | N.Gonj (East) | Khanpur 33/11KV S/S
20 | 11 kV Old Hajiganj Feeder. | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S
21 | 11 kV Siraj-ud-daullah Feeder. | 11 | 0 | 06604389 | 1 | 42144.69 | 62961.9 | 20817.21 | 60 | 0 | 1249032.6 | 1260578.6756 | N.Gonj (East) | Khanpur 33/11KV S/S
22 | 11 kV Spare Feeder. | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
25 | 11 kV B. B. Road West Feeder. | 11 | 0 | 6604415 | 1 | 95.99 | 140.58 | 44.59 | 40000 | 0 | 1783600 | 1800087.6245 | N.Gonj (West) | Khanpur 33/11KV S/S
26 | 11 kV Mondalpara Feeder. | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
27 | 11 kV B. B. Road East Feeder. | 11 | 0 | 06604392 | 1 | 75.1 | 109.7 | 34.6 | 40000 | 0 | 1384000 | 1396793.7162 | N.Gonj (East) | Khanpur 33/11KV S/S
28 | 11 kV Bishaw Road Feeder. | 11 | 0 | 06604393 | 1 | 98.4 | 147.19 | 48.79 | 40000 | 0 | 1951600 | 1969640.6189 | N.Gonj (East) | Khanpur 33/11KV S/S
29 | 11 kV Chasara Feeder. | 11 | 0 | 06604391 | 1 | 101.54 | 152.29 | 50.75 | 40000 | 0 | 2030000 | 2048765.3497 | N.Gonj (West) | Khanpur 33/11KV S/S
31 | 11 kV Pathan Tully Feeder. | 11 | 0 | 06604388 | 1 | 32.71 | 32.71 | 0 | 40000 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S
32 | 11 kV Spare Feeder. | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
33 | 11 kV Nayamati Feeder. | 11 | 0 | 6604289 | 1 | 73.9 | 107.18 | 33.28 | 40000 | 0 | 1331200 | 1343505.6323 | N.Gonj (East) | Khanpur 33/11KV S/S
34 | 11 kV Spare Feeder. | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
35 | 11 kV Spare Feeder. | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
36 | 11 kV Spare Feeder. | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 | 0 | 412109 | 1 | 9109.5 | 9109.5 | 0 | 10 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 | 0 | 243285 | 1 | 6352.2 | 6388.1 | 35.9 | 10 | 0 | 3000 | 3027.732 | N.Gonj (East) | Khanpur 33/11KV S/S
3 | 11 kV Link Road Feeder | 11 | Backup | DHK66629 | 1 | 22776.54 | 23009.26 | 232.72 | 8000 | 0 | 1861760 | 1882008.2759 | N.Gonj (East) | Matuail 33/11KV S/S
0 | 0 | 11 | 0 | HA021100475-02 | 1 | 81796.404 | 83653.744 | 1857.34 | 1000 | 0 | 1857340 | 1877540.2045 | N.Gonj (East) | Matuail 33/11KV S/S
4 | 11 kV Lamapara Express Feeder | 11 | 0 | HA021100928-03 | 1 | 74511.135 | 75563.19 | 1052.055 | 1000 | 0 | 1052055 | 1063497.0225 | N.Gonj (East) | Matuail 33/11KV S/S
5 | 11 kV Kutubpur Feeder*** | 11 | 0 | DHK66616 | 1 | 17105.28 | 17315.9 | 210.62 | 8000 | 0 | 1684960 | 1703285.4205 | N.Gonj (East) | Matuail 33/11KV S/S
0 | 0 | 11 | Backup | XA575929 | 1 | 35760.1 | 37443.2 | 1683.1 | 1000 | 0 | 1683100 | 1701405.1914 | N.Gonj (East) | Matuail 33/11KV S/S
6 | 11 kV Ramarbagh Feeder (F1) | 11 | 0 | DHK66625 | 1 | 3450.14 | 3463.92 | 13.78 | 60000 | 0 | 826800 | 835792.1765 | Fatullah | Matuail 33/11KV S/S
0 | 0 | 11 | Backup | 0 | 1 | 7567.015 | 8395.82 | 828.805 | 1000 | 0 | 828805 | 837818.9826 | Fatullah | Matuail 33/11KV S/S
7 | 11 kV Tushardhara Feeder (F2) | 11 | 0 | DHK66623 | 1 | 3656.03 | 3701.54 | 45.51 | 60000 | 0 | 2730600 | 2760297.6743 | Matuail | Matuail 33/11KV S/S
8 | 11 kV Matuail Medical Feeder (F3) | 11 | 0 | DHK66627 | 1 | 3247.29 | 3258.78 | 11.49 | 60000 | 0 | 689400 | 696897.8308 | Matuail | Matuail 33/11KV S/S
0 | 0 | 11 | Backup | 0 | 1 | 63825.371 | 63825.371 | 0 | 1000 | 0 | 0 | 0 | Matuail | Matuail 33/11KV S/S
9 | 11 kV Rupayan Town Feeder (F4) | 11 | 0 | HA021101044-02 | 1 | 64530.881 | 64851.309 | 320.428 | 1000 | 0 | 320428 | 323912.9361 | Matuail | Matuail 33/11KV S/S
12 | 11 kV Shibu Market Feeder (F7) | 11 | 0 | DHK66624 | 1 | 2345.91 | 2356.06 | 10.15 | 60000 | 0 | 609000 | 615623.4101 | Fatullah | Matuail 33/11KV S/S
13 | 11 kV Soma-Sagar Steel (F6) | 11 | 0 | HA060300286-03 | 1 | 73922.771 | 75021.472 | 1098.701 | 1000 | 0 | 1098701 | 1110650.3388 | Fatullah | Matuail 33/11KV S/S
14 | 11 kV Jhalkuri Feeder (F8) | 11 | 0 | DHK66626 | 1 | 4246.65 | 4291.01 | 44.36 | 60000 | 0 | 2661600 | 2690547.2387 | Matuail | Matuail 33/11KV S/S
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 | 0 | 0 | 0 | Matuail | Matuail 33/11KV S/S
0 | 0 | 11 | 0 | DHK6622 | 1 | 4122.31 | 4144.98 | 22.67 | 60000 | 0 | 1360200 | 1374993.3702 | Matuail | Matuail 33/11KV S/S
16 | 11 kV Rajmahal Feeder (F10) | 11 | 0 | DHKA2187 | 1 | 100.8649 | 104.4696 | 3.6047 | 60000 | 0 | 216282 | 218634.2568 | Shyampur | Matuail 33/11KV S/S
17 | 11 kV Bhuighor Bazar | 11 | 0 | HA021100861-02 | 1 | 72071.985 | 73094.967 | 1022.982 | 1000 | 0 | 1022982 | 1034107.8281 | Matuail | Matuail 33/11KV S/S
18 | 11 kV Tokkar Math Feeder | 11 | 0 | HA021200298-02 | 1 | 78018.724 | 78743.932 | 725.208 | 1000 | 0 | 725208 | 733095.2742 | Fatullah | Matuail 33/11KV S/S
19 | 11 kV Osmani Stadium Feeder***** | 11 | 0 | XA575922 | 1 | 107.1 | 170.9 | 63.8 | 1000 | 0 | 63800 | 64493.8811 | Fatullah | Matuail 33/11KV S/S
16 | 33/0.415 KV Transformer, AT-1 | 0.415 | 0 | 2001123043119 | 1 | 7121 | 7194 | 73 | 160 | 0 | 11680 | 11807.0303 | Shyampur | Matuail 33/11KV S/S
17 | 33/0.415 KV Transformer, AT-2 | 0.415 | 0 | 2001123043157 | 1 | 4714.5 | 4715.3 | 0.8 | 160 | 0 | 128 | 129.3921 | Shyampur | Matuail 33/11KV S/S
1 | 11 kV Godnail (F16) | 11 | 0 | 00000109 | 1 | 19168914 | 21004948 | 1836034 | 1 | 0 | 1836034 | 1869406.9017 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
2 | 11 kV M. Circus (F15) | 11 | 0 | 00000123 | 1 | 101393752 | 103491504 | 2097752 | 1 | 0 | 2097752 | 2135882.0516 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
3 | 11 kV Wapderpool (F14) | 11 | 0 | 00000190 | 1 | 54594468 | 55179144 | 584676 | 1 | 0 | 584676 | 595303.4365 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
4 | 11 kV Chowdhury Bari (F13) | 11 | 0 | 00000191 | 1 | 92008416 | 94163728 | 2155312 | 1 | 0 | 2155312 | 2194488.2982 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
5 | 11 kV Ailpara (F12) | 1 | 0 | 00000192 | 1 | 44342692 | 46804564 | 2461872 | 1 | 0 | 2461872 | 2506620.5244 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
6 | 11 kV Spare (F11) | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV
7 | 11 kV Spare (F10) | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV
8 | 11 kV Spare (F9) | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV
9 | 11 kV Spare (F8) | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV
10 | 11 kV Zulfiqur Steel | 11 | 0 | 00000197 | 1 | 11793891 | 13020328 | 1226437 | 1 | 0 | 1226437 | 1248729.4855 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 | 0 | 00000198 | 1 | 3943790 | 3985110 | 41320 | 1 | 0 | 41320 | 42071.0581 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
12 | 11 kV Lucky Bazar (F5) | 11 | 0 | 00000199 | 1 | 84429552 | 85797352 | 1367800 | 1 | 0 | 1367800 | 1392661.9878 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
13 | 11 kV Enayetnagar (F4) | 11 | 0 | 00000200 | 1 | 26078056 | 27625972 | 1547916 | 1 | 0 | 1547916 | 1576051.8888 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
14 | 11 kV Bhuiyapara (F3) | 11 | 0 | 00000201 | 1 | 58396016 | 60310572 | 1914556 | 1 | 0 | 1914556 | 1949356.1666 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
15 | 11 kV Arambagh (F2) | 11 | 0 | 00000202 | 1 | 4868388 | 5922585 | 1054197 | 1 | 0 | 1054197 | 1073358.7436 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
16 | 11 kV Spare (F1) | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 | 0 | 00000204 | 1 | 1485.81 | 1532.1 | 46.29 | 100 | 0 | 4629 | 4713.1396 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 | 0 | 00000205 | 1 | 60.71 | 60.71 | 0 | 100 | 0 | 0 | 0 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV
14 | 11 kV Minan Steel Feeder | 11 | New | 0 | 1 | 73664308 | 74349258 | 684950 | 1 | 0 | 684950 | 686221.5647 | N.Gonj (West) | Fatullah OLD 33/11KV S/S
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 85671760 | 86574371 | 902611 | 1 | 0 | 902611 | 904286.638 | N.Gonj (West) | Fatullah OLD 33/11KV S/S
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 57808.6 | 83099.6 | 25291 | 60 | 0 | 1517460 | 1520277.0648 | Fatullah | Fatullah OLD 33/11KV S/S
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 259491.5 | 275685 | 16193.5 | 60 | 0 | 971610 | 973413.7301 | Fatullah | Fatullah OLD 33/11KV S/S
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 875315.6 | 906898.46 | 31582.86 | 60 | 0 | 1894971.6 | 1898489.4903 | Fatullah | Fatullah OLD 33/11KV S/S
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 26016.8 | 37019.5 | 11002.7 | 60 | 0 | 660162 | 661387.5474 | Fatullah | Fatullah OLD 33/11KV S/S
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 574407.8 | 588771.6 | 14363.8 | 60 | 0 | 861828 | 863427.9271 | Fatullah | Fatullah OLD 33/11KV S/S
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 447240.7 | 466043.56 | 18802.86 | 60 | 0 | 1128171.6 | 1130265.9765 | Fatullah | Fatullah OLD 33/11KV S/S
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 848225.6 | 855908.3 | 7682.7 | 60 | 0 | 460962 | 461817.7457 | Fatullah | Fatullah OLD 33/11KV S/S
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 478635.8 | 487049.3 | 8413.5 | 60 | 0 | 504810 | 505747.1466 | Fatullah | Fatullah OLD 33/11KV S/S
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 98157975 | 98802056 | 644081 | 1 | 0 | 644081 | 645276.6941 | Sytalakhya | Fatullah OLD 33/11KV S/S
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 23906084 | 24231901 | 325817 | 1 | 0 | 325817 | 326421.8579 | Sytalakhya | Fatullah OLD 33/11KV S/S
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14155030 | 14466321 | 311291 | 1 | 0 | 311291 | 311868.8913 | Sytalakhya | Fatullah OLD 33/11KV S/S
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 26378186 | 26912795 | 534609 | 1 | 0 | 534609 | 535601.4665 | Fatullah | Fatullah OLD 33/11KV S/S
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 7121858 | 9716958 | 2595100 | 1 | 0 | 2595100 | 2599917.6327 | Fatullah | Fatullah OLD 33/11KV S/S
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
0 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 99089910 | 100875390 | 1785480 | 1 | 0 | 1785480 | 1788794.6263 | Fatullah | Fatullah OLD 33/11KV S/S
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 790.28 | 823.84 | 33.56 | 60000 | 0 | 2013600 | 2018573.5941 | Sytalakhya | Fatullah New 33/11 KV SS
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 341.43 | 366.25 | 24.82 | 60000 | 0 | 1489200 | 1492878.3256 | Sytalakhya | Fatullah New 33/11 KV SS
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 495.29 | 506.79 | 11.5 | 60000 | 0 | 690000 | 691704.3007 | Sytalakhya | Fatullah New 33/11 KV SS
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1088.75 | 1118.86 | 30.11 | 60000 | 0 | 1806600 | 1811062.3039 | Sytalakhya | Fatullah New 33/11 KV SS
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 96.59 | 116.01 | 19.42 | 60000 | 0 | 1165200 | 1168078.0452 | Sytalakhya | Fatullah New 33/11 KV SS
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 39.13 | 48.55 | 9.42 | 60000 | 0 | 565200 | 566596.0446 | Sytalakhya | Fatullah New 33/11 KV SS
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1017.3 | 1045.24 | 27.94 | 60000 | 0 | 1676400 | 1680540.7098 | Sytalakhya | Fatullah New 33/11 KV SS
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1192.19 | 1234.36 | 42.17 | 60000 | 0 | 2530200 | 2536449.5967 | Sytalakhya | Fatullah New 33/11 KV SS
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS
11 | 11 kV Katherpol Feeder | 11 | 0 | 00000031 | 1 | 57646700 | 59742536 | 2095836 | 1 | 0 | 2095836 | 2095256.7912 | Fatullah | Dapa 33/11 kV
12 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
13 | 11 kV Union Parishad Feeder | 11 | 0 | 00000032 | 1 | 60506292 | 61871328 | 1365036 | 1 | 0 | 1365036 | 1364658.7564 | Fatullah | Dapa 33/11 kV
14 | 11 kV Shiachar Feeder | 11 | 0 | 00000030 | 1 | 60089012 | 61991488 | 1902476 | 1 | 0 | 1902476 | 1901950.2285 | Fatullah | Dapa 33/11 kV
15 | 11 kV Sastapur Feeder | 11 | 0 | 00000106 | 1 | 66398116 | 67891392 | 1493276 | 1 | 0 | 1493276 | 1492863.3157 | Fatullah | Dapa 33/11 kV
17 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
18 | 11 kV Jalal Ahmed Express | 11 | 0 | 00000172 | 1 | 4097000 | 4889120 | 792120 | 1 | 0 | 792120 | 791901.0884 | Fatullah | Dapa 33/11 kV
19 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
21 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
22 | 11 kV Lalpur Feeder | 11 | 0 | 00000044 | 1 | 74571856 | 74945536 | 373680 | 1 | 0 | 373680 | 373576.7292 | Fatullah | Dapa 33/11 kV
23 | 11 kV Kotaler Bag Feeder | 11 | 0 | 00000050 | 1 | 78139288 | 79654888 | 1515600 | 1 | 0 | 1515600 | 1515181.1462 | Fatullah | Dapa 33/11 kV
24 | 11 kV Idrakpur Feeder | 11 | 0 | 00000021 | 1 | 72447944 | 73516904 | 1068960 | 1 | 0 | 1068960 | 1068664.5804 | Fatullah | Dapa 33/11 kV
25 | 11 kV Isdair Feeder | 11 | 0 | 00000029 | 1 | 37647948 | 38441108 | 793160 | 1 | 0 | 793160 | 792940.801 | Fatullah | Dapa 33/11 kV
26 | 11 kV Shah Fateullah Express | 11 | 0 | 0000051 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV
27 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
28 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 | 0 | DHKF 7522 | 1 | 2848 | 2900 | 52 | 100 | 0 | 5200 | 5198.5629 | Fatullah | Dapa 33/11 kV
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV
3 | 11 kV Bholail Feeder (F-3) | 11 | 0 | DHK 9335 | 1 | 76570.4462 | 117557.5729 | 40987.1267 | 60 | 0 | 2459227.602 | 2464743.5384 | Sytalakhya | Sitalakhya 33/11KV S/S
4 | 11 kV Crony Apparels (F-2) | 11 | 0 | DHK 9336 | 1 | 86741.1599 | 110186.2566 | 23445.0967 | 60 | 0 | 1406705.802 | 1409860.9795 | Sytalakhya | Sitalakhya 33/11KV S/S
5 | 11 kV Baburail Feeder (F-5) | 11 | 0 | DHK 9322 | 1 | 81641.2934 | 114240.3356 | 32599.0422 | 60 | 0 | 1955942.532 | 1960329.6227 | N.Gonj (West) | Sitalakhya 33/11KV S/S
6 | 11 kV Goghchar Feeder (F-1) | 11 | 0 | DHK 9323 | 1 | 47575.3245 | 68546.5464 | 20971.2219 | 60 | 0 | 1258273.314 | 1261095.5642 | Sytalakhya | Sitalakhya 33/11KV S/S
7 | 11 kV Norshinghopur (F-2) | 11 | 0 | DHK 9365 | 1 | 23185.9177 | 47651.0611 | 24465.1434 | 60 | 0 | 1467908.604 | 1471201.0567 | Sytalakhya | Sitalakhya 33/11KV S/S
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 | 0 | DHK 9367 | 1 | 97389.3483 | 106609.7103 | 9220.362 | 60 | 0 | 553221.72 | 554462.5713 | Sytalakhya | Sitalakhya 33/11KV S/S
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 | 0 | H/A030701125-03 | 1 | 72378.143 | 72602.239 | 224.096 | 1000 | 0 | 224096 | 224598.6372 | N.Gonj (East) | Sitalakhya 33/11KV S/S
12 | 11 kV Kashipur Feeder (F-7) | 11 | 0 | H/A030800169-03 | 1 | 29944.336 | 31592.82 | 1648.484 | 1000 | 0 | 1648484 | 1652181.4751 | Sytalakhya | Sitalakhya 33/11KV S/S
13 | 11 kV Spare Feeder (F-6) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S
14 | 11 kV Paikpara Feeder (F-8) | 11 | 0 | H/A030701098-03 | 1 | 74950.975 | 76031.283 | 1080.308 | 1000 | 0 | 1080308 | 1082731.082 | N.Gonj (West) | Sitalakhya 33/11KV S/S
15 | 11 kV B. K. Road Feeder (F-9) | 11 | 0 | H/A030800205-03 | 1 | 92273.664 | 93037 | 763.336 | 1000 | 0 | 763336 | 765048.1281 | N.Gonj (East) | Sitalakhya 33/11KV S/S
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 | 0 | H/A030701091-03 | 1 | 50158.39 | 51115.194 | 956.804 | 1000 | 0 | 956804 | 958950.0681 | Sytalakhya | Sitalakhya 33/11KV S/S
9 | 11 kV River View | 11 | 0 | 00000061 | 1 | 3921252 | 4718732 | 797480 | 1 | 0 | 797480 | 803073.4017 | N.Gonj (East) | Mondalpara 33/11KV S/S
10 | 11 kV Railgate B.B. Road | 11 | 0 | 00000191 | 1 | 20877230 | 21484788 | 607558 | 1 | 0 | 607558 | 611819.3181 | N.Gonj (East) | Mondalpara 33/11KV S/S
11 | 11 kV DIT | 11 | 0 | 00000174 | 1 | 127405168 | 130377160 | 2971992 | 1 | 0 | 2971992 | 2992837.0935 | N.Gonj (West) | Mondalpara 33/11KV S/S
12 | 11 kV Dalpatti | 11 | 0 | 00000182 | 1 | 1673315 | 2382434 | 709119 | 1 | 0 | 709119 | 714092.6513 | N.Gonj (East) | Mondalpara 33/11KV S/S
13 | 11 kV South Chasara | 11 | 0 | 00000043 | 1 | 86363752 | 88911104 | 2547352 | 1 | 0 | 2547352 | 2565218.7341 | N.Gonj (West) | Mondalpara 33/11KV S/S
14 | 11 kV Spare | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S
16 | 11 kV NCC Express | 11 | 0 | 00000019 | 1 | 44799 | 67159 | 22360 | 1 | 0 | 22360 | 22516.8296 | N.Gonj (East) | Mondalpara 33/11KV S/S
17 | 11 kV Spare | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S
18 | 11 kV Masuya Bazar | 11 | 0 | 00000173 | 1 | 2343714 | 3304592 | 960878 | 1 | 0 | 960878 | 967617.4501 | N.Gonj (East) | Mondalpara 33/11KV S/S
20 | 11 kV Nitaigonj | 11 | 0 | 00000189 | 1 | 55969784 | 56636980 | 667196 | 1 | 0 | 667196 | 671875.6098 | N.Gonj (East) | Mondalpara 33/11KV S/S
21 | 11 kV Shahid Nagar | 11 | 0 | 00000020 | 1 | 53165432 | 54413388 | 1247956 | 1 | 0 | 1247956 | 1256708.9709 | Sytalakhya | Mondalpara 33/11KV S/S
22 | 11 kV Bangla Bazar | 11 | 0 | 00000139 | 1 | 64386124 | 65980440 | 1594316 | 1 | 0 | 1594316 | 1605498.2865 | N.Gonj (West) | Mondalpara 33/11KV S/S
23 | 11 kV Vogoban Gonj | 11 | 0 | 00000181 | 1 | 1025797 | 1465156 | 439359 | 1 | 0 | 439359 | 442440.5963 | N.Gonj (East) | Mondalpara 33/11KV S/S
24 | 11 kV Tanbazar | 11 | 0 | 00000138 | 1 | 45709768 | 46679968 | 970200 | 1 | 0 | 970200 | 977004.8332 | N.Gonj (East) | Mondalpara 33/11KV S/S
25 | 11 kV SS Road | 11 | 0 | 00000175 | 1 | 61263892 | 62559048 | 1295156 | 1 | 0 | 1295156 | 1304240.0244 | N.Gonj (West) | Mondalpara 33/11KV S/S
26 | 11 kV Spare | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S
27 | 33/0.415 kV Auxiliary-1 | 0.415 | 0 | 0 | 1 | 2249.63 | 2333.07 | 83.44 | 100 | 0 | 8344 | 8402.5235 | N.Gonj (West) | Mondalpara 33/11KV S/S
28 | 33/0.415 kV Auxiliary-2 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S
10 | 11 kV Masdair Feeder (F-8) | 11 | 0 | XA575914 | 1 | 203761.5 | 206799.9 | 3038.4 | 1000 | 0 | 3038400 | 3077099.4263 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
11 | 11 kV Narayangonj (F-7) | 11 | 0 | XA575915 | 1 | 161786.6 | 163077.6 | 1291 | 1000 | 0 | 1291000 | 1307443.1804 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
12 | 11 kV Nearest Feeder (F-6) | 11 | 0 | XA575927 | 1 | 102847.3 | 103832.5 | 985.2 | 1000 | 0 | 985200 | 997748.2737 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 | 0 | XA575916 | 1 | 112523.8 | 113848.2 | 1324.4 | 1000 | 0 | 1324400 | 1341268.5888 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
14 | 11 kV Abonti Color Tex. (F-4) | 11 | 0 | XA575912 | 1 | 52800.5 | 53493 | 692.5 | 1000 | 0 | 692500 | 701320.2188 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 | 0 | DHK66615 | 1 | 147.9431 | 165.1511 | 17.208 | 60000 | 0 | 1032481.86 | 1045632.3523 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
17 | 11 kV Shasongaon Feeder (F-2) | 11 | 0 | XA575920 | 1 | 228775.4 | 229950 | 1174.6 | 1000 | 0 | 1174600 | 1189560.6195 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 | 0 | XA575929 | 1 | 16570 | 17828 | 1258 | 1000 | 0 | 1258000 | 1274022.8667 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 | 0 | HA021100913-02 | 1 | 36841.501 | 37746.076 | 904.575 | 1000 | 0 | 904575 | 916096.371 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 | 0 | HA021100682-02 | 1 | 53082.882 | 55419.839 | 2336.957 | 1000 | 0 | 2336957 | 2366722.3025 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 | 0 | HA021100455-02 | 1 | 49545.321 | 51349.693 | 1804.372 | 1000 | 0 | 1804372 | 1827353.8856 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3648.6 | 3691.2 | 42.6 | 160 | 0 | 6816 | 6902.8139 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4095.5 | 4098.1 | 2.6 | 160 | 0 | 416 | 421.2985 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 | 0 | 041808902749 | 1 | 339.06 | 360.83 | 21.77 | 60000 | 0 | 1306200 | 1308593.1901 | Sytalakhya | Char Syedpur 33/11 KV S/S New
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 | 0 | 041808902759 | 1 | 374.92 | 398.23 | 23.31 | 60000 | 0 | 1398600 | 1401162.4833 | Sytalakhya | Char Syedpur 33/11 KV S/S New
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
13 | 11 kV Mokterpur Feeder (=F8) | 11 | 0 | 041808902786 | 1 | 211.44 | 229.07 | 17.63 | 60000 | 0 | 1057800 | 1059738.0772 | Sytalakhya | Char Syedpur 33/11 KV S/S New
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 | 0 | 041808902789 | 1 | 137.32 | 151.39 | 14.07 | 60000 | 0 | 844200 | 845746.7241 | Sytalakhya | Char Syedpur 33/11 KV S/S New
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
21 | 33/0.415 kV Transformer AT-1 | 0.415 | 0 | 041811907976 | 1 | 1273.63 | 1372.11 | 98.48 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New
22 | 33/0.415 kV Transformer AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 67974785 | 68696773 | 721988 | 1 | 0 | 721988 | 731782.37 | Mugdapara | Amulia 33/11 kv
6 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 10163057 | 11388468 | 1225411 | 1 | 0 | 1225411 | 1242034.7233 | Demra | Amulia 33/11 kv
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 66774948 | 67318225 | 543277 | 1 | 0 | 543277 | 550647.0061 | Demra | Amulia 33/11 kv
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 57031355 | 59259140 | 2227785 | 1 | 0 | 2227785 | 2258006.7634 | Demra | Amulia 33/11 kv
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 11924560 | 12956256 | 1031696 | 1 | 0 | 1031696 | 1045691.8176 | Mugdapara | Amulia 33/11 kv
13 | 11 kV Amulia Model Town Feeder | 11 | Demra | 0 | 1 | 51179519 | 51323114 | 143595 | 1 | 0 | 143595 | 145542.9861 | Demra | Amulia 33/11 kv
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 7194545 | 8420622 | 1226077 | 1 | 0 | 1226077 | 1242709.7581 | Demra | Amulia 33/11 kv
15 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv
16 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv
17 | 33/0.415 kV Transformer, AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv
1 | 11 kV Nearest Feeder | 11 | 0 | HA021101060-02 | 1 | 70560333 | 72108037 | 1547704 | 1 | 0 | 1547704 | 1558145.6337 | Maniknagar | Maniknagar 33/11 KV SS
2 | 11kV Spare | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS
3 | 11 kV City Palli Feeder | 11 | 0 | HA021100937-02 | 1 | 74563517 | 75407218 | 843701 | 1 | 0 | 843701 | 849393.0553 | Maniknagar | Maniknagar 33/11 KV SS
4 | 11 kV R K Mission Road Feeder | 11 | 0 | HA021101035-02 | 1 | 9481733 | 10974303 | 1492570 | 1 | 0 | 1492570 | 1502639.6704 | Maniknagar | Maniknagar 33/11 KV SS
5 | 11 kV Janapath Feeder | 11 | 0 | HA021100864-02 | 1 | 21334986 | 23326754 | 1991768 | 1 | 0 | 1991768 | 2005205.5254 | Maniknagar | Maniknagar 33/11 KV SS
6 | 11 kV Dhalpur Feeder | 11 | 0 | HA021100851-02 | 1 | 83588686 | 84442992 | 854306 | 1 | 0 | 854306 | 860069.6023 | Maniknagar | Maniknagar 33/11 KV SS
7 | 11kV WTP | 11 | 0 | X0599387 | 1 | 1261.6 | 1406.5 | 144.9 | 1000 | 0 | 144900 | 145877.5724 | Maniknagar | Maniknagar 33/11 KV SS
10 | 11kV Kamalapur Water pumping | 11 | 0 | HA021100474-02 | 1 | 7604026 | 7628319 | 24293 | 1 | 0 | 24293 | 24456.8935 | Maniknagar | Maniknagar 33/11 KV SS
11 | 11 kV Wasa Road Feeder | 11 | 0 | HA021001011-02 | 1 | 22420806 | 24448123 | 2027317 | 1 | 0 | 2027317 | 2040994.3579 | Maniknagar | Maniknagar 33/11 KV SS
12 | 11kV Sutikhalpar Feeder | 11 | 0 | HA021101047-02 | 1 | 76903368 | 78965769 | 2062401 | 1 | 0 | 2062401 | 2076315.0532 | Maniknagar | Maniknagar 33/11 KV SS
13 | 11kV Spare | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS
14 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS
15 | 11kV Spare | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS
16 | 11kV Spare | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS
17 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS
13 | AT-1 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS
6 | 11kV Fakirapul Panir Tank Feeder | 11 | 0 | DHK86058 | 1 | 1646.88 | 1662.02 | 15.14 | 60000 | 0 | 908400 | 913140.3988 | Motijheel | Motijheel old 33/11 kV
7 | 11kV Station Road Feeder | 11 | 0 | DHK86075 | 1 | 2371.1 | 2373.12 | 2.02 | 60000 | 0 | 121200 | 121832.4707 | Motijheel | Motijheel old 33/11 kV
8 | 11kV Box Culvert Road Feeder | 11 | 0 | DHK86071 | 1 | 3068.01 | 3101.12 | 33.11 | 60000 | 0 | 1986600 | 1996966.8828 | Motijheel | Motijheel old 33/11 kV
9 | 11kV Mohamedan Club Feeder | 11 | 0 | DHK86062 | 1 | 1631.78 | 1643.91 | 12.13 | 60000 | Import from Narinda | 727800 | 731597.9549 | Motijheel | Motijheel old 33/11 kV
10 | 11kV Amina Ahmed Co. | 11 | 0 | DHK95754 | 1 | 95646 | 97956 | 2310 | 60 | 133686 | 138600 | 139323.2709 | Motijheel | Motijheel old 33/11 kV
11 | 11kV Bangabhaban -1 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV
12 | 11kV Sonali Bank | 11 | 0 | DHK95753 | 1 | 37569 | 43302 | 5733 | 60 | 0 | 343980 | 345775.0268 | Motijheel | Motijheel old 33/11 kV
15 | 11kV NCC Bank Feeder | 11 | 0 | DHK68123 | 1 | 307.1 | 309.54 | 2.44 | 60000 | 0 | 146400 | 147163.9744 | Motijheel | Motijheel old 33/11 kV
16 | 11kV IFIC BANK Feeder | 11 | 0 | DHK68116 | 1 | 374.21 | 383.41 | 9.2 | 60000 | 0 | 552000 | 554880.5594 | Ramna | Motijheel old 33/11 kV
17 | 11kV Arambagh Feeder | 11 | 0 | DHK68117 | 1 | 3346.46 | 3354.56 | 8.1 | 60000 | 0 | 486000 | 488536.1447 | Motijheel | Motijheel old 33/11 kV
18 | 11kV Nikotborti Feeder | 11 | 0 | DHK68114 | 1 | 1385.65 | 1396.51 | 10.86 | 60000 | 0 | 651600 | 655000.3125 | Motijheel | Motijheel old 33/11 kV
19 | 11kV Agrani Bank Feeder | 11 | 0 | DHK95756 | 1 | 354884 | 357283 | 2399 | 60 | 0 | 143940 | 144691.1372 | Motijheel | Motijheel old 33/11 kV
20 | 11kV Bangladesh Bank-2 | 11 | 0 | DHK95755 | 1 | 512 | 515 | 3 | 60000 | 0 | 180000 | 180939.3128 | Motijheel | Motijheel old 33/11 kV
21 | 11kV PDB Design Feeder 14 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV
22 | 11kV Bangabhaban-2 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV
23 | 11/0.4 kV AT | 0.415 | 0 | ELIC5429 | 1 | 394002 | 397502 | 3500 | 1 | 0 | 3500 | 3518.2644 | Motijheel | Motijheel old 33/11 kV
2 | 11 kV Central Weman | 11 | 0 | 41812909492 | 1 | 117.46 | 126.75 | 9.29 | 60000 | 0 | 557400 | 559727.7485 | Motijheel | Motijheel 33/11 KV SS (new)
3 | 11 kV Spare Feeder 2 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
4 | 11 kV K. M. Das Len | 11 | 0 | 41812909499 | 1 | 201.61 | 217.11 | 15.5 | 60000 | 0 | 930000 | 933883.7569 | Swamibag | Motijheel 33/11 KV SS (new)
5 | 11 kV Gopibag | 11 | 0 | 41812909517 | 1 | 28.97 | 31.43 | 2.46 | 60000 | 0 | 147600 | 148216.3898 | Motijheel | Motijheel 33/11 KV SS (new)
6 | 11kV SPICE TV | 11 | 0 | 41812909518 | 1 | 4.24 | 7.5 | 3.26 | 60000 | 0 | 195600 | 196416.8418 | Narinda | Motijheel 33/11 KV SS (new)
7 | 11 kV Spare Feeder 6 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
8 | 11 kV Spare Feeder 7 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
9 | 11 kV BPT-1 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
10 | 11 kV BPT-2 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
11 | 10 kV Spare Feeder 8 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
12 | 11 kV Spare Feeder 9 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
13 | 11 kV South Kamlapur | 11 | 0 | 41812909473 | 1 | 341.42 | 358.82 | 17.4 | 60000 | 0 | 1044000 | 1048359.8303 | Motijheel | Motijheel 33/11 KV SS (new)
14 | 11 kV Spare Feeder 11 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new)
15 | 11 kV Answer Camp | 11 | 0 | 41812909514 | 1 | 141.42 | 153.52 | 12.1 | 60000 | 0 | 726000 | 729031.836 | Motijheel | Motijheel 33/11 KV SS (new)
16 | 11 kV Shapla Chattar | 11 | 0 | 41812909516 | 1 | 106.7 | 116.51 | 9.81 | 60000 | 0 | 588600 | 591058.0422 | Motijheel | Motijheel 33/11 KV SS (new)
17 | 11 kV Sayedabad | 11 | 0 | 41812909497 | 1 | 79.57 | 84.55 | 4.98 | 60000 | 0 | 298800 | 300047.8135 | Swamibag | Motijheel 33/11 KV SS (new)
22 | 33/0.4 kV Aux Transformer | 0.415 | 0 | 41901920686 | 1 | 869.63 | 953.35 | 83.72 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new)
12 | Inner Circular Road Feeder | 11 | 0 | BD014042 | 1 | 35190 | 37233 | 2043 | 1000 | 0 | 2043000 | 2028898.6132 | Motijheel | P & T 33/11 KV SS
13 | NSI New Building Expres Feeder | 11 | 0 | BD013982 | 1 | 8363 | 8779 | 416 | 1000 | 0 | 416000 | 413128.6457 | Ramna | P & T 33/11 KV SS
14 | Police Hospital RMU Feeder | 11 | 0 | BD014044 | 1 | 2861 | 3030 | 169 | 1000 | 0 | 169000 | 167833.5123 | Rajarbag | P & T 33/11 KV SS
16 | Jonaki O/H Feeder | 11 | 0 | BD014013 | 1 | 27994 | 29424 | 1430 | 1000 | 0 | 1430000 | 1420129.7195 | Rajarbag | P & T 33/11 KV SS
17 | Nayapalton Overhead Feeder | 11 | 0 | BD014014 | 1 | 20656 | 21639 | 983 | 1000 | 0 | 983000 | 976215.0449 | Ramna | P & T 33/11 KV SS
18 | Masjid Gali Over Head Feeder | 11 | 0 | BD014016 | 1 | 10972 | 11857 | 885 | 1000 | 0 | 885000 | 878891.4697 | Ramna | P & T 33/11 KV SS
19 | Spare Feeder (Feeder-8) | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS
23 | Mid Way Over Head Feeder | 11 | 0 | BD014015 | 1 | 18883 | 19862 | 979 | 1000 | 0 | 979000 | 972242.6541 | Ramna | P & T 33/11 KV SS
24 | Palton Thana Over Head Feeder | 11 | 0 | BD014033 | 1 | 18248 | 19551 | 1303 | 1000 | 0 | 1303000 | 1294006.3108 | Rajarbag | P & T 33/11 KV SS
25 | Police Hospital (South) U/G Feeder 7 | 11 | 0 | BD014034 | 1 | 11682 | 11851 | 169 | 1000 | 0 | 169000 | 167833.5123 | Rajarbag | P & T 33/11 KV SS
26 | China Town Express Feeder | 11 | 0 | BD013943 | 1 | 5250 | 5536 | 286 | 1000 | 0 | 286000 | 284025.9439 | Ramna | P & T 33/11 KV SS
27 | Fakirapul Bazar O/H Feeder | 11 | 0 | BD014032 | 1 | 23784 | 25196 | 1412 | 1000 | 0 | 1412000 | 1402253.9607 | Motijheel | P & T 33/11 KV SS
28 | PWD Ouarter (RMU) | 11 | 0 | BD013937 | 1 | 1714 | 1861 | 147 | 1000 | 0 | 147000 | 145985.3628 | Motijheel | P & T 33/11 KV SS
29 | Postal Quarter RMU | 11 | 0 | BD013945 | 1 | 2161 | 2327 | 166 | 1000 | 0 | 166000 | 164854.2192 | Motijheel | P & T 33/11 KV SS
30 | 11/0.4 kV AT-1 | 0.415 | 0 | DHKH4409 | 1 | 1313 | 1313 | 0 | 100 | 0 | 0 | 0 | Rajarbag | P & T 33/11 KV SS
31 | 11/0.4 kV AT-2 | 0.415 | 0 | DHKH4411 | 1 | 400 | 454 | 54 | 100 | 0 | 5400 | 5362.7276 | Rajarbag | P & T 33/11 KV SS
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 283.3 | 315.7 | 32.4 | 40000 | 0 | 1296000 | 1302977.567 | Rajarbag | Kamalapur Railway 33/11 KV SS
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 48.6 | 53.6 | 5 | 40000 | 0 | 200000 | 201076.785 | Rajarbag | Kamalapur Railway 33/11 KV SS
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 202.7 | 221 | 18.3 | 40000 | 0 | 732000 | 735941.0332 | Rajarbag | Kamalapur Railway 33/11 KV SS
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 510.7 | 562.4 | 51.7 | 40000 | 0 | 2068000 | 2079133.9572 | Rajarbag | Kamalapur Railway 33/11 KV SS
5 | 11 KV Majar Feeder | 11 | 0 | 96 | 1 | 12.6 | 22.1 | 9.5 | 40000 | 0 | 380000 | 382045.8916 | Motijheel | Kamalapur Railway 33/11 KV SS
7 | 11 kV Feeder-6 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 253.2 | 278.1 | 24.9 | 40000 | 0 | 996000 | 1001362.3894 | Rajarbag | Kamalapur Railway 33/11 KV SS
9 | 11 kV Feeder-8 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 181.8 | 190.2 | 8.4 | 40000 | 0 | 336000 | 337808.9988 | Rajarbag | Kamalapur Railway 33/11 KV SS
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 188.7 | 198.7 | 10 | 40000 | 0 | 400000 | 402153.5701 | Rajarbag | Kamalapur Railway 33/11 KV SS
13 | 11 kV Feeder-11 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 42.6 | 48 | 5.4 | 40000 | 0 | 216000 | 217162.9278 | Motijheel | Kamalapur Railway 33/11 KV SS
15 | Jasimuddin Feeder-13 | 11 | 0 | 91 | 1 | 44.5 | 71.8 | 27.3 | 40000 | 0 | 1092000 | 1097879.2463 | Motijheel | Kamalapur Railway 33/11 KV SS
16 | Police Box Feeder-14 | 11 | 0 | 18 | 1 | 20.4 | 36.4 | 16 | 40000 | 0 | 640000 | 643445.7121 | Motijheel | Kamalapur Railway 33/11 KV SS
17 | 11 kV Feeder-15 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS
18 | 11 kV Feeder-16 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS
19 | Auxiliary -1 (AT-1 ) | 0.415 | 0 | DHKF 7632 | 1 | 736.86 | 787.87 | 51.01 | 100 | 0 | 5101 | 5128.4634 | Rajarbag | Kamalapur Railway 33/11 KV SS
20 | Auxiliary -1 (AT-2 ) | 0.415 | 0 | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 211876.16 | 212943.22 | 1067.06 | 1000 | Estimated | 851429.88 | 860468.6016 | Motijheel | Bangabhaban 132/11KV S/S
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 23888.8 | 23966.99 | 78.19 | 1000 | 0 | 78190 | 79020.0597 | Motijheel | Bangabhaban 132/11KV S/S
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 76839.23 | 77077.43 | 238.2 | 1000 | 0 | 238200 | 240728.715 | Motijheel | Bangabhaban 132/11KV S/S
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33812.48 | 33826.28 | 13.8 | 1000 | Estimated | 20000 | 20212.3186 | Ramna | Bangabhaban 132/11KV S/S
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 729797.04 | 737544.5157 | Motijheel | Bangabhaban 132/11KV S/S
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15585.07 | 15661.1 | 76.03 | 1000 | 0 | 76030 | 76837.1293 | Motijheel | Bangabhaban 132/11KV S/S
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 243118.01 | 244322.7 | 1204.69 | 1000 | 0 | 1204690 | 1217478.907 | Motijheel | Bangabhaban 132/11KV S/S
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 13970.19 | 14139.81 | 169.62 | 1000 | 0 | 169620 | 171420.6744 | Motijheel | Bangabhaban 132/11KV S/S
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94891.92 | 94891.92 | 0 | 1000 | Estimated | 243265.68 | 245848.1719 | Motijheel | Bangabhaban 132/11KV S/S
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 162808.9 | 163076.15 | 267.25 | 1000 | 0 | 267250 | 270087.1078 | Motijheel | Bangabhaban 132/11KV S/S
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20422.03 | 20481.33 | 59.3 | 1000 | Estimated | 243265.68 | 245848.1719 | Motijheel | Bangabhaban 132/11KV S/S
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82187.62 | 82365.95 | 178.33 | 1000 | Estimated | 364898.52 | 368772.2578 | Motijheel | Bangabhaban 132/11KV S/S
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 121941.84 | 122251.69 | 309.85 | 1000 | 0 | 309850 | 313139.3465 | Motijheel | Bangabhaban 132/11KV S/S
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 270703.01 | 271490.95 | 787.94 | 1000 | 0 | 787940 | 796304.7174 | Motijheel | Bangabhaban 132/11KV S/S
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 79173.42 | 79642.9 | 469.48 | 1000 | 0 | 469480 | 474463.9677 | Motijheel | Bangabhaban 132/11KV S/S
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192152.04 | 192345.5 | 193.46 | 1000 | Estimated | 364898.52 | 368772.2578 | Motijheel | Bangabhaban 132/11KV S/S
23 | 11/0.4 kV AT-1 | 0.415 | 0 | 63412931 | 1 | 63258 | 63258 | 0 | 1 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S
24 | 11/0.4 kV AT-2 | 0.415 | 0 | 63403117 | 1 | 7498 | 13772 | 6274 | 1 | Estimated | 5000 | 5053.0797 | Motijheel | Bangabhaban 132/11KV S/S
1 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24339 | 24474.94 | 135.94 | 8000 | 0 | 1087520 | 1096395.2732 | Narinda | Narinda 33/11KV S/S
2 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16479.22 | 16557.29 | 78.07 | 8000 | Export to Motijheel | 624560 | 629657.0471 | Swamibag | Narinda 33/11KV S/S
3 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 458.94 | 471.15 | 12.21 | 40000 | 133686 | 488400 | 492385.8425 | Maniknagar | Narinda 33/11KV S/S
4 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5447.36 | 5473.81 | 26.45 | 40000 | 0 | 1058000 | 1066634.3599 | Narinda | Narinda 33/11KV S/S
5 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3275.98 | 3323.44 | 47.46 | 40000 |  | 1898400 | 1913892.8816 | Swamibag | Narinda 33/11KV S/S
6 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8439.28 | 8477.29 | 38.01 | 40000 | 0 | 1520400 | 1532808.0158 | Narinda | Narinda 33/11KV S/S
7 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7184.27 | 7223.58 | 39.31 | 40000 | 0 | 1572400 | 1585232.3889 | Narinda | Narinda 33/11KV S/S
10 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5901.12 | 5932.66 | 31.54 | 40000 | 0 | 1261600 | 1271895.9437 | Swamibag | Narinda 33/11KV S/S
11 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 4954.3 | 4979.47 | 25.17 | 40000 | 0 | 1006800 | 1015016.5156 | Narinda | Narinda 33/11KV S/S
12 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7712.97 | 7734.95 | 21.98 | 40000 | 0 | 879200 | 886375.1694 | Swamibag | Narinda 33/11KV S/S
13 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6292.41 | 6319.72 | 27.31 | 40000 | 0 | 1092400 | 1101315.099 | Narinda | Narinda 33/11KV S/S
14 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S
15 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 18538.4 | 22163.2 | 3624.8 | 444.44 | 0 | 1611006.112 | 1624153.5662 | Narinda | Narinda 33/11KV S/S
16 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 364417 | 374036 | 9619 | 80 | 0 | 769520 | 775800.0686 | Narinda | Narinda 33/11KV S/S
17 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 27129.7 | 29470.6 | 2340.9 | 444.44 | 0 | 1040389.596 | 1048880.237 | Narinda | Narinda 33/11KV S/S
18 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 35150.8 | 35683.5 | 532.7 | 1000 | 0 | 532700 | 537047.3757 | Swamibag | Narinda 33/11KV S/S
1 | 11/0.4 kV Aux Transformer-1 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S
2 | 11/0.4 kV Aux Transformer-2 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62075.6 | 62100 | 24.4 | 2222.22 | Estimated | 547347.78 | 555416.4351 | Banglabazar | Kumertuly 33/11KV S/S
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4531.23 | 4531.4 | 0.17 | 40000 | Estimated | 1459594.08 | 1481110.4937 | Banglabazar | Kumertuly 33/11KV S/S
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5121.34 | 5121.51 | 0.17 | 40000 | Estimated | 486531.36 | 493703.4979 | Banglabazar | Kumertuly 33/11KV S/S
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5393.27 | 5393.48 | 0.21 | 40000 | Estimated | 1398777.66 | 1419397.5564 | Banglabazar | Kumertuly 33/11KV S/S
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4023.81 | 4023.81 | 0 | 40000 | Estimated | 729797.04 | 740555.2468 | Banglabazar | Kumertuly 33/11KV S/S
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 912246.3 | 925694.0585 | Banglabazar | Kumertuly 33/11KV S/S
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5828.13 | 5853.24 | 25.11 | 40000 | 0 | 1004400 | 1019206.2302 | Banglabazar | Kumertuly 33/11KV S/S
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8050.6 | 8098.57 | 47.97 | 40000 | 0 | 1918800 | 1947085.7372 | Banglabazar | Kumertuly 33/11KV S/S
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3726.07 | 3736.6 | 10.53 | 40000 | 0 | 421200 | 427409.0643 | Banglabazar | Kumertuly 33/11KV S/S
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7144.81 | 7172.56 | 27.75 | 40000 | Estimated | 1058205.708 | 1073805.1079 | Banglabazar | Kumertuly 33/11KV S/S
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3565.38 | 3572.31 | 6.93 | 40000 | 0 | 277200 | 281286.3072 | Banglabazar | Kumertuly 33/11KV S/S
27 | 11/0.4 kV AT-1 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S
28 | 11/0.4 kV AT-2 | 0.415 | 0 | 05378636 | 1 | 160585.6 | 163007.6 | 2422 | 2 | 0 | 4844 | 4915.4072 | Banglabazar | Kumertuly 33/11KV S/S
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 36098890 | 36815436 | 716546 | 1 | 0 | 716546 | 716311.3918 | Bangshal | Banshal 33/11KV S/S
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 45513090 | 46867285 | 1354195 | 1 | 0 | 1354195 | 1353751.6158 | Banglabazar | Banshal 33/11KV S/S
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 18444117 | 19159807 | 715690 | 1 | 0 | 715690 | 715455.6721 | Bangshal | Banshal 33/11KV S/S
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 42091960 | 43501879 | 1409919 | 1 | 0 | 1409919 | 1409457.3709 | Bangshal | Banshal 33/11KV S/S
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 58774329 | 59902495 | 1128166 | 1 | 0 | 1128166 | 1127796.6211 | Bangshal | Banshal 33/11KV S/S
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 25877226 | 27364546 | 1487320 | 1 | 0 | 1487320 | 1486833.0286 | Bangshal | Banshal 33/11KV S/S
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 58169790 | 59668688 | 1498898 | 1 | 0 | 1498898 | 1498407.2378 | Bangshal | Banshal 33/11KV S/S
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 46714704 | 47860599 | 1145895 | 1 | 0 | 1145895 | 1145519.8164 | Narinda | Banshal 33/11KV S/S
13 | AT-1 | 0.415 | 0 | DHK-4415 | 1 | 649.28 | 685.05 | 35.77 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S
14 | AT-2 | 0.415 | 0 | DHK-4410 | 1 | 658.98 | 658.98 | 0 | 100 | 0 | 7000 | 6997.7081 | Bangshal | Banshal 33/11KV S/S
17 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 755740.9 | 783779.8 | 28038.9 | 60 | 0 | 1682334 | 1710856.4639 | Kazla | Kazla 33/11KV S/S
18 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1855425.2355 | Kazla | Kazla 33/11KV S/S
19 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2919188.16 | 2968680.3768 | Kazla | Kazla 33/11KV S/S
20 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963847 | 36963851 | 4 | 1000 | Estimated | 547347.78 | 556627.5706 | Maniknagar | Kazla 33/11KV S/S
21 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
22 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 107994.3 | 110052.4 | 2058.1 | 1000 | 0 | 2058100 | 2092993.2394 | Jurain | Kazla 33/11KV S/S
23 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 41024544 | 0 | 1 | Estimated | 1824492.6 | 1855425.2355 | Kazla | Kazla 33/11KV S/S
25 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 610537.6 | 647129.1 | 36591.5 | 60 | 0 | 2195490 | 2232712.5636 | Jurain | Kazla 33/11KV S/S
26 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 557250.1 | 579724.6 | 22474.5 | 60 | 0 | 1348470 | 1371332.0993 | Kazla | Kazla 33/11KV S/S
27 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 907339.1 | 947647 | 40307.9 | 60 | 0 | 2418474 | 2459477.0573 | Kazla | Kazla 33/11KV S/S
28 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
29 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 146325.4 | 178496.3 | 32170.9 | 60 | 0 | 1930254 | 1962979.7252 | Swamibag | Kazla 33/11KV S/S
31 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 994216.4 | 1033062 | 38845.6 | 60 | 0 | 2330736 | 2370251.5382 | Jurain | Kazla 33/11KV S/S
32 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 199222.9 | 249904.8 | 50681.9 | 60 | 0 | 3040914 | 3092469.9692 | Shyampur | Kazla 33/11KV S/S
33 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 348551.4 | 362270.4 | 13719 | 60 | 0 | 823140 | 837095.6004 | Matuail | Kazla 33/11KV S/S
34 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1880719 | 1912724 | 32005 | 60 | 0 | 1920300 | 1952856.964 | Jurain | Kazla 33/11KV S/S
35 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 24764299 | 26329191 | 1564892 | 1 | 0 | 1564892 | 1591423.3402 | Kazla | Kazla 33/11KV S/S
36 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 24603267 | 25278265 | 674998 | 1 | 0 | 674998 | 686441.9856 | Kazla | Kazla 33/11KV S/S
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 2727 | 2894.5 | 167.5 | 10000 | 0 | 1675000 | 1703398.1226 | Kazla | Kazla 33/11KV S/S
38 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
40 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 528 | 808.3 | 280.3 | 4000 | 0 | 1121200 | 1140208.9403 | Kazla | Kazla 33/11KV S/S
41 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 11886 | 12649 | 763 | 4000 | 0 | 3052000 | 3103743.9224 | Kazla | Kazla 33/11KV S/S
43 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
44 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 19756.3 | 19756.3 | 0 | 1000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
45 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 15890.2 | 16523.9 | 633.7 | 2000 | 0 | 1267400 | 1288887.6302 | Kazla | Kazla 33/11KV S/S
46 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 34227.2 | 34893.9 | 666.7 | 2000 | 0 | 1333400 | 1356006.601 | Maniknagar | Kazla 33/11KV S/S
47 | 33/0.4 kV AT-1 | 0.415 | 0 | 503043 | 1 | 96180 | 96204 | 24 | 10 | 0 | 240 | 244.069 | Kazla | Kazla 33/11KV S/S
48 | 33/0.4 kV AT-2 | 0.415 | 0 | 503044 | 1 | 91766 | 92456 | 690 | 10 | 0 | 6000 | 6101.7246 | Kazla | Kazla 33/11KV S/S
23 | Auxiliary Transformer | 0.415 | 0 | 41901920685 | 1 | 2055.77 | 2173.65 | 117.88 | 160 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur | 0 | 1 | 501.66 | 546.49 | 44.83 | 40000 | 0 | 1793200 | 1796570.0888 | Shyampur | Shyampur 33/11KV S/S
6 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
7 | 11 kV Road No.-21 Feeder | 11 | 0 | BD001943 | 1 | 995.02 | 1013.14 | 18.12 | 40000 | 0 | 724800 | 726162.1684 | Shyampur | Shyampur 33/11KV S/S
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1469.8 | 1490.83 | 21.03 | 40000 | 0 | 841200 | 842780.9272 | Shyampur | Shyampur 33/11KV S/S
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1366.77 | 1383.34 | 16.57 | 40000 | 0 | 662800 | 664045.6474 | Shyampur | Shyampur 33/11KV S/S
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1234.72 | 1259.97 | 25.25 | 40000 | 0 | 1010000 | 1011898.1651 | Fatullah | Shyampur 33/11KV S/S
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3121.28 | 3181.56 | 60.28 | 40000 | 0 | 2411200 | 2415731.5404 | Shyampur | Shyampur 33/11KV S/S
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2029.39 | 2064.33 | 34.94 | 40000 | 0 | 1397600 | 1400226.6095 | Shyampur | Shyampur 33/11KV S/S
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 478.9 | 481.32 | 2.42 | 40000 | 0 | 96800 | 96981.9232 | Fatullah | Shyampur 33/11KV S/S
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 2982.97 | 3028.5 | 45.53 | 40000 | 0 | 1821200 | 1824622.7112 | Shyampur | Shyampur 33/11KV S/S
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1839.53 | 1879.48 | 39.95 | 40000 | 0 | 1598000 | 1601003.2355 | Shyampur | Shyampur 33/11KV S/S
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1325.38 | 1372.48 | 47.1 | 40000 | 0 | 1884000 | 1887540.7358 | Shyampur | Shyampur 33/11KV S/S
20 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 779.83 | 793.62 | 13.79 | 40000 | 0 | 551600 | 552636.6613 | Shyampur | Shyampur 33/11KV S/S
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1249.14 | 1274.85 | 25.71 | 40000 | 0 | 1028400 | 1030332.7456 | Shyampur | Shyampur 33/11KV S/S
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2797.89 | 2850.41 | 52.52 | 40000 | 0 | 2100800 | 2104748.1835 | Shyampur | Shyampur 33/11KV S/S
24 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1084.64 | 1090.91 | 6.27 | 40000 | 0 | 250800 | 251271.3464 | Shyampur | Shyampur 33/11KV S/S
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1846.66 | 1882.3 | 35.64 | 40000 | 0 | 1425600 | 1428279.2319 | Shyampur | Shyampur 33/11KV S/S
28 | 11 kV Spare Feeder | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1303.2 | 1321.48 | 18.28 | 40000 | 0 | 731200 | 732574.1964 | Shyampur | Shyampur 33/11KV S/S
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1249.41 | 1273.64 | 24.23 | 40000 | 0 | 969200 | 971021.4868 | Shyampur | Shyampur 33/11KV S/S
31 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
32 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
33 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2129.9 | 2161.1 | 31.2 | 40000 | 0 | 1248000 | 1250345.4555 | Shyampur | Shyampur 33/11KV S/S
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 166.25 | 168.36 | 2.11 | 40000 | 0 | 84400 | 84558.6189 | Shyampur | Shyampur 33/11KV S/S
37 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1128.88 | 1150.73 | 21.85 | 40000 | 0 | 874000 | 875642.5706 | Shyampur | Shyampur 33/11KV S/S
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3533.57 | 3585.78 | 52.21 | 40000 | 0 | 2088400 | 2092324.8793 | Shyampur | Shyampur 33/11KV S/S
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1049.77 | 1064.5 | 14.73 | 40000 | 0 | 589200 | 590307.3256 | Shyampur | Shyampur 33/11KV S/S
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 62537.1 | 62985.9 | 448.8 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 | 0 | 0 | 1 | 571732 | 578955 | 7223 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 31461699 | 33561211 | 2099512 | 1 | 0 | 2099512 | 2051822.5774 | Shyampur | Shyampur BISIC 33/11KV S/S
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 19028427 | 19777200 | 748773 | 1 | 0 | 748773 | 731764.9753 | Jurain | Shyampur BISIC 33/11KV S/S
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 344092 | 377188.5 | 33096.5 | 60 | 0 | 1985790 | 1940683.7189 | Jurain | Shyampur BISIC 33/11KV S/S
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 526588 | 550150 | 23562 | 60 | 0 | 1413720 | 1381608.0185 | Jurain | Shyampur BISIC 33/11KV S/S
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 546830.2 | 570335.4 | 23505.2 | 60 | 0 | 1410312 | 1378277.4296 | Jurain | Shyampur BISIC 33/11KV S/S
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 303271.1 | 320655.9 | 17384.8 | 60 | 0 | 1043088 | 1019394.7492 | Shyampur | Shyampur BISIC 33/11KV S/S
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511237.9 | 511384.5 | 146.6 | 60 | 0 | 8796 | 8596.203 | Jurain | Shyampur BISIC 33/11KV S/S
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 734846.3 | 778535.8 | 43689.5 | 60 | 0 | 2621370 | 2561826.8196 | Jurain | Shyampur BISIC 33/11KV S/S
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 193075.4 | 214982.3 | 21906.9 | 60 | 0 | 1314414 | 1284557.7074 | Shyampur | Shyampur BISIC 33/11KV S/S
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 414820 | 435544 | 20724 | 60 | 0 | 1243440 | 1215195.8482 | Jurain | Shyampur BISIC 33/11KV S/S
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 397196.8 | 439242.7 | 42045.9 | 60 | 0 | 2522754 | 2465450.8355 | Jurain | Shyampur BISIC 33/11KV S/S
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 821215.4 | 833590.5 | 12375.1 | 60 | 0 | 742506 | 725640.3272 | Jurain | Shyampur BISIC 33/11KV S/S
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 897162 | 917620.2 | 20458.2 | 60 | 0 | 1227492 | 1199610.0995 | Shyampur | Shyampur BISIC 33/11KV S/S
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB7380 | 1 | 597162 | 600880 | 3718 | 1 | 0 | 3718 | 3633.5474 | Shyampur | Shyampur BISIC 33/11KV S/S
8 | 11 kV Spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV
9 | 11 kV Khaza Moinuddin | 11 | 0 | 00000026 | 1 | 3344951 | 4014750 | 669799 | 1 | 0 | 669799 | 672821.6526 | Fatullah | Nandalalpur 33/11 kV
10 | 11 kV Chitashal | 11 | 0 | 00000027 | 1 | 31054124 | 31727122 | 672998 | 1 | 0 | 672998 | 676035.0889 | Shyampur | Nandalalpur 33/11 kV
11 | 11 kV Local Feeder | 11 | 0 | 00000157 | 1.5 | 17804636 | 18012236 | 207600 | 1 | Estimated | 608164.2 | 610908.7086 | Shyampur | Nandalalpur 33/11 kV
12 | 11 kV Rasel Germants | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 | 0 | 00000121 | 1 | 65806320 | 68316432 | 2510112 | 1 | 0 | 2510112 | 2521439.5722 | Matuail | Nandalalpur 33/11 kV
14 | 11 kV Nandalalpur | 11 | 0 | 00000010 | 1 | 81183200 | 82071400 | 888200 | 1 | 0 | 888200 | 892208.2473 | Fatullah | Nandalalpur 33/11 kV
15 | 11 kV Sharif Bagh | 11 | 0 | 00000132 | 1 | 66803716 | 68478392 | 1674676 | 1 | 0 | 1674676 | 1682233.437 | Shyampur | Nandalalpur 33/11 kV
18 | 11 kV Spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV
19 | 11 KV Nayamati | 11 | 0 | 00000158 | 1 | 61866928 | 62900248 | 1033320 | 1 | 0 | 1033320 | 1037983.1413 | Fatullah | Nandalalpur 33/11 kV
20 | 11 kV Pulpar | 11 | 0 | 00000160 | 1 | 5264907 | 6177345 | 912438 | 1 | 0 | 912438 | 916555.6279 | Fatullah | Nandalalpur 33/11 kV
21 | 11 kV Shahi Bazar | 11 | 0 | 00000170 | 1 | 38497188 | 39279104 | 781916 | 1 | 0 | 781916 | 785444.6114 | Shyampur | Nandalalpur 33/11 kV
22 | 11 kV Pagla Bazar | 11 | 0 | 00000060 | 1 | 47913044 | 48692680 | 779636 | 1 | 0 | 779636 | 783154.3223 | Fatullah | Nandalalpur 33/11 kV
23 | 11 kV Delpara bazar | 11 | 0 | 00000063 | 1 | 74614216 | 76134976 | 1520760 | 1 | 0 | 1520760 | 1527622.8486 | Shyampur | Nandalalpur 33/11 kV
24 | 11 kV Bhuighor (Board mill) | 11 | 0 | 00000146 | 1 | 41318500 | 42387696 | 1069196 | 1 | 0 | 1069196 | 1074021.0416 | Matuail | Nandalalpur 33/11 kV
25 | 11 kV Spare | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV
26 | 33/0.415 kV, 200 kVA AT-1 | 11 | 0 | 7803 | 1 | 2252 | 2309 | 57 | 100 | 0 | 5700 | 5725.7228 | Shyampur | Nandalalpur 33/11 kV
27 | 33/0.415 kV, 200 kVA AT-2 | 11 | 0 | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur | Nandalalpur 33/11 kV
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 58467092 | 59733520 | 1266428 | 1 | 0 | 1266428 | 1269812.3426 | Postogola | Postogola 33/11KV S/S
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 5618521 | 6981957 | 1363436 | 1 | 0 | 1363436 | 1367079.5822 | Jurain | Postogola 33/11KV S/S
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 22620681 | 23055333 | 434652 | 1 | 0 | 434652 | 435813.5436 | Jurain | Postogola 33/11KV S/S
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 69737341 | 71243020 | 1505679 | 1 | 0 | 1505679 | 1509702.7057 | Postogola | Postogola 33/11KV S/S
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 395780.9 | 407058.9 | 11278 | 60 | 0 | 676680 | 678488.3278 | Postogola | Postogola 33/11KV S/S
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 804867.8 | 824597.3 | 19729.5 | 60 | 0 | 1183770 | 1186933.4512 | Postogola | Postogola 33/11KV S/S
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 687382.8 | 706742.8 | 19360 | 60 | 0 | 1161600 | 1164704.2052 | Postogola | Postogola 33/11KV S/S
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 513686.3 | 515784.4 | 2098.1 | 60 | 0 | 125886 | 126222.4118 | Postogola | Postogola 33/11KV S/S
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 775428.8 | 797566.5 | 22137.7 | 60 | 0 | 1328262 | 1331811.5849 | Postogola | Postogola 33/11KV S/S
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 203448.6 | 243241.8 | 39793.2 | 60 | 0 | 2387592 | 2393972.4885 | Jurain | Postogola 33/11KV S/S
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 32551263 | 34480101 | 1928838 | 1 | 0 | 1928838 | 1933992.5359 | Jurain | Postogola 33/11KV S/S
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 1201.7 | 3547.1 | 2345.4 | 1000 | 0 | 2345400 | 2351667.7366 | Jurain | Postogola 33/11KV S/S
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 51239362 | 52807093 | 1567731 | 1 | 0 | 1567731 | 1571920.5306 | Postogola | Postogola 33/11KV S/S
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52405873 | 52708936 | 303063 | 1 | 0 | 303063 | 303872.8913 | Postogola | Postogola 33/11KV S/S
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 | 0 | ELIB67385 | 1 | 188.64 | 243.19 | 54.55 | 80 | 0 | 4364 | 4375.6621 | Postogola | Postogola 33/11KV S/S
1 | 11 kV Feeder-1 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV
2 | 11 kV Feeder-2 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV
3 | 11 kV Dholaikal RMU | 11 | 0 | DHK60970 | 1 | 126774.5 | 158004.4 | 31229.9 | 60 | 0 | 1873794 | 1890634.7965 | Banglabazar | IG Gate GIS 33/11 kV
4 | 11 kV Alom Gonj | 11 | 0 | DHK60894 | 1 | 450404.1 | 460143.7 | 9739.6 | 60 | 0 | 584376 | 589628.102 | Postogola | IG Gate GIS 33/11 kV
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 | 0 | DHK60895 | 1 | 447662.4 | 475941.2 | 28278.8 | 60 | 0 | 1696728 | 1711977.4089 | Postogola | IG Gate GIS 33/11 kV
6 | 11 kV Farashgonj Feeder (F-6) | 11 | 0 | DHK68133 | 1 | 3500.26 | 3530.25 | 29.99 | 60000 | 0 | 1799400 | 1815572.1775 | Banglabazar | IG Gate GIS 33/11 kV
7 | 11 kV Doyaganj | 11 | 0 | DHK68134 | 1 | 2289.97 | 2322.27 | 32.3 | 60000 | 0 | 1938000 | 1955417.8504 | Swamibag | IG Gate GIS 33/11 kV
10 | 11 kV Faridabad | 11 | 0 | DHK68140 | 1 | 709.65 | 730.03 | 20.38 | 60000 | 0 | 1222800 | 1233789.9626 | Postogola | IG Gate GIS 33/11 kV
11 | 11 kV Gandaria | 11 | 0 | DHK60969 | 1 | 266897.3 | 300077.81 | 33180.51 | 60 | 0 | 1990830.6 | 2008723.2675 | Postogola | IG Gate GIS 33/11 kV
12 | 11 kV Walter Road | 11 | 0 | DHK68136 | 1 | 903.39 | 926.56 | 23.17 | 60000 | 0 | 1390200 | 1402694.4766 | Banglabazar | IG Gate GIS 33/11 kV
13 | 11 kV Murgitola Feeder (F-11) | 11 | 0 | DHK68138 | 1 | 3773.45 | 3813.73 | 40.28 | 60000 | 0 | 2416800 | 2438521.0841 | Swamibag | IG Gate GIS 33/11 kV
14 | 11 kV Feeder-12 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV
15 | 11 kV Begumgonj Feeder (F-13) | 11 | 0 | DHK60899 | 1 | 579240.5 | 609124.4 | 29883.9 | 60 | 0 | 1793034 | 1809148.9629 | Swamibag | IG Gate GIS 33/11 kV
16 | 11 kV Lohar Pool Feeder (F-14) | 11 | 0 | DHK60967 | 1 | 115953.3 | 132216.8 | 16263.5 | 60 | 0 | 975810 | 984580.1304 | Postogola | IG Gate GIS 33/11 kV
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB2774 | 1 | 274308 | 276011 | 1703 | 1 | 0 | 1703 | 1718.3058 | Postogola | IG Gate GIS 33/11 kV
1 | Nizambag | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 973062.72 | 972380.6635 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
2 | Merry Stopes | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 364898.52 | 364642.7488 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
3 | Mujibur Ghat | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1337961.24 | 1337023.4124 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
4 | Madrasa | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1702859.76 | 1701666.1612 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
5 | Thana | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1337961.24 | 1337023.4124 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
6 | Al-Hera | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
7 | Waz Uddin School | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 973062.72 | 972380.6635 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
8 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S
10 | Bashundhara City | 33 | 0 | 660434 | 1 | 727.48 | 739.39 | 11.91 | 180000 | 0 | 2143800 | 2161081.9864 | Shere b.nagar | Moghbazar 132/33/11KV S/S
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4446.37 | 4469.84 | 23.47 | 240000 | 0 | 5632800 | 5615154.9463 | Siddirgonj | Siddhirganj 132/33/11KV S/S
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 349307.2 | 353746.5 | 4439.3 | 2000 | 0 | 8878600 | 8850787.3005 | Siddirgonj | Siddhirganj 132/33/11KV S/S
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1004.15 | 1006.87 | 2.72 | 240000 | 0 | 652800 | 0 | Siddirgonj | Demra 33/11KV S/S
11 | 33 kV ACI Pharmacuticles Feeder | 33 | 0 | DHKC4791 | 1 | 861.45 | 874.23 | 12.78 | 90000 | 0 | 1150200 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC | 0 | 1 | 9901.453 | 9902.221 | 0.768 | 1000 | From Customer End | 10962.5847 | 10991.7418 | Matuail | Matuail 132/33 KV S/S
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 35431.875 | 36660.866 | 1228.991 | 1000 | 0 | 1228991 | 1229303.7954 | Sytalakhya | Sitalakhya 132/33KV S/S
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4603.3 | 4621.1 | 17.8 | 160 | 0 | 2848 | 2848.7249 | Sytalakhya | Sitalakhya 132/33KV S/S
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 251.46 | 269.79 | 18.33 | 360000 | 0 | 6598800 | 6616060.3155 | Sytalakhya | Char Syedpur 132/33KV S/S
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 80.23 | 87.04 | 6.81 | 360000 | 0 | 2451600 | 2458012.5886 | Sytalakhya | Char Syedpur 132/33KV S/S
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 36.82 | 39.89 | 3.07 | 360000 | 0 | 1105200 | 1108090.8439 | Sytalakhya | Char Syedpur 132/33KV S/S
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 375.19 | 405.16 | 29.97 | 360000 | 0 | 10789200 | 10817421.0397 | Sytalakhya | Char Syedpur 132/33KV S/S
1 | 11 KV Shahidbagh Feeder | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | -3972 | -3994.0825 | Rajarbag | Santinagar Switching S/S
2 | 11 Fortune(MogBazar)-new | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 125532 | 126229.899 | Moghbazar | Santinagar Switching S/S
3 | Centerpoint-Kakrail | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 80400 | 80846.9863 | Kakrail | Santinagar Switching S/S

## Sheet2
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2157.9 | 2184.48 | 26.58 | 720000 | 19137600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2140.12 | 2158.72 | 18.6 | 720000 | 13392000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1829.88 | 1864.35 | 34.47 | 720000 | 24818400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1736.03 | 1762.32 | 26.29 | 480000 | 12619200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 1997.28 | 2024.03 | 26.75 | 240000 | 0 | 6420000 | 6424413.8049 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2282.03 | 2315.96 | 33.93 | 240000 | 0 | 8143200 | 8148798.5197 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1420.28 | 1435.41 | 15.13 | 240000 | 0 | 3631200 | 3633696.4811 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 761.21 | 782.32 | 21.11 | 240000 | 0 | 5066400 | 5069883.1933 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1794.62 | 1811.32 | 16.7 | 240000 | 0 | 4008000 | 4010755.5343 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1154.36 | 1164.56 | 10.2 | 240000 | 0 | 2448000 | 2449683.0209 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 365.9 | 377.52 | 11.62 | 240000 | 0 | 2788800 | 2790717.3239 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2001.34 | 2031.88 | 30.54 | 240000 | 0 | 7329600 | 7334639.1627 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1542.04 | 1565.51 | 23.47 | 240000 | 0 | 5632800 | 5636672.5982 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 664.59 | 679.62 | 15.03 | 240000 | 0 | 3607200 | 3609679.9809 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1872.34 | 1906.63 | 34.29 | 240000 | 0 | 8229600 | 8235257.9204 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1786.24 | 1804.37 | 18.13 | 240000 | 0 | 4351200 | 4354191.4872 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 134.4 | 139.74 | 5.34 | 240000 | 0 | 1281600 | 1282481.111 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1318.74 | 1347.73 | 28.99 | 240000 | 0 | 6957600 | 6962383.4095 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | 2023-01-03 | 2023-01-03 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2157.9 | 2184.48 | 26.58 | 720000 | 19137600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2140.12 | 2158.72 | 18.6 | 720000 | 13392000 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1829.88 | 1864.35 | 34.47 | 720000 | 24818400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1736.03 | 1762.32 | 26.29 | 480000 | 12619200 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 1997.28 | 2024.03 | 26.75 | 240000 | 0 | 6420000 | 6424413.8049 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2282.03 | 2315.96 | 33.93 | 240000 | 0 | 8143200 | 8148798.5197 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1420.28 | 1435.41 | 15.13 | 240000 | 0 | 3631200 | 3633696.4811 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 761.21 | 782.32 | 21.11 | 240000 | 0 | 5066400 | 5069883.1933 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1794.62 | 1811.32 | 16.7 | 240000 | 0 | 4008000 | 4010755.5343 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1154.36 | 1164.56 | 10.2 | 240000 | 0 | 2448000 | 2449683.0209 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 365.9 | 377.52 | 11.62 | 240000 | 0 | 2788800 | 2790717.3239 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2001.34 | 2031.88 | 30.54 | 240000 | 0 | 7329600 | 7334639.1627 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1542.04 | 1565.51 | 23.47 | 240000 | 0 | 5632800 | 5636672.5982 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 664.59 | 679.62 | 15.03 | 240000 | 0 | 3607200 | 3609679.9809 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1872.34 | 1906.63 | 34.29 | 240000 | 0 | 8229600 | 8235257.9204 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1786.24 | 1804.37 | 18.13 | 240000 | 0 | 4351200 | 4354191.4872 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 134.4 | 139.74 | 5.34 | 240000 | 0 | 1281600 | 1282481.111 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1318.74 | 1347.73 | 28.99 | 240000 | 0 | 6957600 | 6962383.4095 | 0 | Dhanmondi 132/33/11KV S/S