## PDB Bill AMR
Detailed Calculation of PDB / PGCB Units | [24 empty] | 9 | 10
132 KV LEVEL | [10 empty] | Month July-2023 | [13 empty] | 14 | 15
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter Type | Meter No. | CF | OMF | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | Energy Imp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416)
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Exp | 8993 532 | 1 | 960000 | 2227.617 | 2227.617 | 0 |  | 0 | 1950.36 | 1950.36 | 0 |  | 0 | -86400 | -1288320 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp |  |  | 960000 | 666.456 | 666.546 | 0.09 | 86400 |  | 373.119 | 374.461 | 1.342 | 1288320 | [5 empty] | 0
2 | Hasnabad to Postogola-1 |  | 132 | Exp | 4262 7826 | 1 | 960000 | 260.441 | 289.542 | 29.101 |  | 27936960 | 116.75 | 129.381 | 12.631 |  | 12125760 | 27936960 | 12125760 | 0.92 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
3 | Hasnabad to Postogola-2 |  | 132 | Exp | 4262 7815 | 1 | 960000 | 125.28 | 133.648 | 8.368 |  | 8033280 | 44.06 | 46.369 | 2.309 |  | 2216640 | 8033280 | 2216640 | 0.96 | 0 | 0
|  |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | [5 empty] | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Exp | PN-1711A04601 | 1 | 960000 | 363.871 | 363.871 | 0 |  | 0 | 211.998 | 211.998 | 0 |  | 0 | 0 | 0 |  |  | 0
|  |  | 132 | Imp |  |  | 960000 | 5.419 | 5.419 | 0 | 0 |  | 4.069 | 4.069 | 0 | 0 | [5 empty] | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [9 empty] | Total=> | 86400 | 35970240 |  |  | Total=> | 1288320 | 14342400 | 35883840 | 13054080 | 0.94 |  | 0
5 | Maniknager-2 (new line to ullon) | Horipur Grid | 132 | Exp | 8993 624 | 1 | 960000 | 4768.057 | 4793.7 | 25.643 |  | 24617280 | 2380.261 | 2384.979 | 4.718 |  | 4529280 | 24617280 | 4529280 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 11.003 | 11.003 | 0 | 0 |  | 7.78 | 7.78 | 0 | 0 | [5 empty] | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 24617280 |  |  | Total=> | 0 | 4529280 | 24617280 | 4529280 | 0.98 |  | 0
6 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Exp | 8993 518 | 1 | 960000 | 1098.154 | 1115.068 | 16.914 |  | 16237440 | 755.249 | 760.831 | 5.582 |  | 5358720 | 16237440 | 5358720 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 70.056 | 70.056 | 0 | 0 |  | 141.149 | 141.149 | 0 | 0 | [5 empty] | 0
7 | Kallyanpur to Lalbagh 2 |  | 132 | Exp | 5014 660 | AMR | 960000 | 274.986 | 291.99 | 17.004 |  | 16323840 | 108.971 | 114.738 | 5.767 |  | 5536320 | 16323840 | 5536320 | 0.95 | 0 | 0
|  |  | 132 | Imp |  | AMR | 960000 | 4.361 | 4.361 | 0 | 0 |  | 30.491 | 30.491 | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [9 empty] | Total=> | 0 | 32561280 |  |  | Total=> | 0 | 10895040 | 32561280 | 10895040 | 0.95
8 | Tranformer 3 | Shitalakhya Grid | 132 | Exp | 5050 1730 |  | 480000 | 2778.291 | 2821.29 | 42.999 |  | 20639520 | 1135.696 | 1151.132 | 15.436 |  | 7409280 | 20639520 | 7409280 | 0.94 | 0 | 0
9 | Tranformer 1 |  | 132 | Exp | 8050 5634 | AMR | 480000 | 8380.88 | 8421.345 | 40.465 |  | 19423200 | 4918.609 | 4938.272 | 19.663 |  | 9438240 | 19423200 | 9438240 | 0.9 | 0 | 0
10 | Tranformer 2 |  | 132 | Exp | 8050 5637 | AMR | 480000 | 8332.942 | 8373.619 | 40.677 |  | 19524960 | 4878.004 | 4897.776 | 19.772 |  | 9490560 | 19524960 | 9490560 | 0.9 | 0 | 0
11 | MI CEMENT |  | 132 | Exp | 38992489 (New) |  | 480000 | 256.334 | 278.728 | 22.394 |  | 10749120 | 50.024 | 53.77 | 3.746 |  | 1798080 | 10749120 | 1798080 | 0.99 | 0 | 0
[10 empty] | Total=> | 0 | 70336800 |  |  | Total=> | 0 | 28136160 | 70336800 | 28136160 | 0.93
SIDDHIRGANJ 132 kV S/S (Tel: 7694743)
12 | XFR- T1 | Siddhirgonj Grid | 132 | Exp | 8993 683 | 1 | 960000 | 8298.965 | 8336.501 | 37.536 |  | 36034560 | 4632.01 | 4648.827 | 16.817 |  | 16144320 | 36034560 | 16144320 | 0.91 | 0 | 0
13 | XFR- T2 |  | 132 | Exp | 8993 682 | 1 | 960000 | 8289.656 | 8326.822 | 37.166 |  | 35679360 | 4626.732 | 4643.449 | 16.717 |  | 16048320 | 35679360 | 16048320 | 0.91 | 0 | 0
14 | Ullon-1 |  | 132 | Exp | 8993 681 | 1 | 1440000 | 2618.149 | 2642.939 | 24.79 |  | 35697600 | 1368.787 | 1373.998 | 5.211 |  | 7503840 | 35697600 | 7503840 | 0.98 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 9.184 | 9.184 | 0 | 0 |  | 19.005 | 19.005 | 0 | 0 | [5 empty] | 0
15 | Ullon-2 |  | 132 | Exp | 8993 680 | 1 | 1440000 | 1373.548 | 1373.548 | 0 |  | 0 | 1173.906 | 1173.906 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 22.279 | 22.279 | 0 | 0 |  | 21.331 | 21.331 | 0 | 0 | [5 empty] | 0
16 | Matuail |  | 132 | Exp | 8993 555 | 1 | 1440000 | 2753.041 | 2779.681 | 26.64 |  | 38361600 | 1284.566 | 1295.83 | 11.264 |  | 16220160 | 38361600 | 16220160 | 0.92 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 771.699 | 771.699 | 0 | 0 |  | 568.906 | 568.906 | 0 | 0 | [5 empty] | 0
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [9 empty] | Total=> | 0 | 145773120 |  |  | Total=> | 0 | 55916640 | 145773120 | 55916640 | 0.93 |  | 0
17 | Mogbazar-1 | Rumpura Grid | 132 | Exp | 8993 631 | 1 | 960000 | 5756.396 | 5799.375 | 42.979 |  | 41259840 | 2941.337 | 2961.515 | 20.178 |  | 19370880 | 41259840 | 19370880 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0 | 0 | 0 | 0 |  | 0.154 | 0.154 | 0 | 0 | [5 empty] | 0
18 | Mogbazar-2 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4914.803 | 4947.971 | 33.168 |  | 31841280 | 2500.392 | 2515.748 | 15.356 |  | 14741760 | 31841280 | 14741760 | 0.91 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 0.084 | 0.084 | 0 | 0 |  | 0.17 | 0.17 | 0 | 0 | [5 empty] | 0
19 | Ullon U/G -1 |  | 132 | Exp | 8993 659 | 1 | 960000 | 4387.45 | 4400.359 | 12.909 |  | 12392640 | 1768.899 | 1769.916 | 1.017 |  | 976320 | 12391680 | 976320 | 1 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.56 | 1.561 | 0.001 | 960 |  | 8.694 | 8.694 | 0 | 0 | [5 empty] | 0
20 | Ullon U/G -2 |  | 132 | Exp | 8993 660 | 1 | 960000 | 4072.298 | 4084.578 | 12.28 |  | 11788800 | 1630.313 | 1631.928 | 1.615 |  | 1550400 | 11787840 | 1550400 | 0.99 | 0 | 0
|  |  |  | Imp |  | AMR | 960000 | 1.329 | 1.33 | 0.001 | 960 |  | 5.269 | 5.269 | 0 | 0 | [5 empty] | 0
21 | Madartheck 1 |  | 132 | Exp | 5014 6667 | 1 | 960000 | 1758.566 | 1786.459 | 27.893 |  | 26777280 | 642.388 | 653.682 | 11.294 |  | 10842240 | 26777280 | 10842240 | 0.93 | 0 | 0
22 | Madartheck 2 |  | 132 | Exp | 5014 6668 | AMR | 960000 | 1552.894 | 1580.626 | 27.732 |  | 26622720 | 667.626 | 678.916 | 11.29 |  | 10838400 | 26622720 | 10838400 | 0.93 | 0 | 0
23 | Dhaka University-1 |  | 132 | Exp | 4262 7810 | 1 | 960000 | 145.541 | 157.05 | 11.509 |  | 11048640 | 2.481 | 2.506 | 0.025 |  | 24000 | 11048640 | 24000 | 1 | 0 | 0
| Dhaka University-1 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 55.44 | 59.408 | 3.968 | 3809280 |  | 0
24 | Dhaka University-2 |  | 132 | Exp | 4262 7812 | 1 | 960000 | 146.811 | 158.41 | 11.599 |  | 11135040 | 1.801 | 1.812 | 0.011 |  | 10560 | 11135040 | 10560 | 1 | 0 | 0
| Dhaka University-2 (Imp) |  | 132 | Imp |  |  | 960000 | 0 | 0 | 0 | 0 |  | 58.541 | 62.793 | 4.252 | 4081920
Maniknagar 230/132 Kv s/s | [9 empty] | Total=> | 1920 | 172866240 |  |  | Total=> | 7891200 | 58354560 | 172864320 | 50463360 | 0.96 |  | 0
25 | Maniknagar-1 | Maniknagar | 132 | Exp | 5014 7584 | 1 | 1920000 | 3134.038 | 3181.398 | 47.36 |  | 90931200 | 1592.402 | 1611.006 | 18.604 |  | 35719680 | 90931200 | 35719680 | 0.93 | 0 | 0
26 | Maniknagar-2 |  | 132 | Exp | 5014 7585 | 1 | 1920000 | 3127.49 | 3174.787 | 47.297 |  | 90810240 | 1589.865 | 1608.456 | 18.591 |  | 35694720 | 90810240 | 35694720 | 0.93 | 0 | 0
[10 empty] | Total=> |  | 181741440 |  |  | Total=> | 0 | 71414400 | 181741440 | 71414400 | 0.93
Shyampur 230/132 Kv s/s
27 | Tranformer - 1 | Shyampur 230/132 | 132 | Exp | 3899 2560 | 1 | 1920000 | 1408.991 | 1441.023 | 32.032 |  | 61501440 | 696.931 | 708.263 | 11.332 |  | 21757440 | 61501440 | 21757440 | 0.94 | 0 | 0 | Loop PFC is Considered
|  |  | 132 | Imp | wp002497 | 1 | 1920000 | 0.245 | 0.245 | 0 | 0 |  | 9.392 | 9.392 | 0 | 0 |  |  |  |  | 0 | 0
28 | Tranformer - 2 |  | 132 | Imp | 3899 2559 | 1 | 1920000 | 0.216 | 0.216 | 0 | 0 |  | 9.657 | 9.657 | 0 | 0
|  |  | 132 | Exp | 3899 2559 | 1 | 1920000 | 1500.185 | 1532.023 | 31.838 |  | 61128960 | 736.877 | 748.233 | 11.356 |  | 21803520 | 61128960 | 21803520 | 0.94 | 0 | 0 | Loop PFC is Considered
Keranigonj 230/132 Kv s/s | [9 empty] | Total=> | 0 | 122630400 |  |  | Total=> | 0 | 43560960 | 122630400 | 43560960 | 0.94
29 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Exp | 3899 2596 | 1 | 1440000 | 851.661 | 891.973 | 40.312 |  | 58049280 | 190.217 | 197.156 | 6.939 |  | 9992160 | 58049280 | 9992160 | 0.99 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0.021 | 0.021 | 0 | 0 |  | 0.835 | 0.835 | 0 | 0
30 | Keraniganj to Lalbagh-3 |  | 132 | Exp | 3899 2597 | 1 | 1440000 | 575.795 | 609.476 | 33.681 |  | 48500640 | 235.63 | 251.93 | 16.3 |  | 23472000 | 48500640 | 23472000 | 0.9 | 0 | 0
|  |  | 132 | Imp |  | 1 | 1440000 | 0 | 0 | 0 | 0 |  | 0.831 | 0.831 | 0 | 0 |  | 0 | 0
Madangonj 132/33 Kv s/s | [9 empty] | Total=> | 0 | 106549920 |  |  | Total=> | 0 | 33464160 | 106549920 | 33464160 | 0.95
31 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Exp | 4262 7811 | 1 | 960000 | 247.775 | 259.986 | 12.211 |  | 11722560 | 64.691 | 67.655 | 2.964 |  | 2845440 | 11722560 | 2845440 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-1 due to PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
32 | Char Syedpur Ckt-2 |  | 132 | Exp | 4262 7824 | 1 | 960000 | 159.043 | 171.744 | 12.701 |  | 12192960 | 35.118 | 38.247 | 3.129 |  | 3003840 | 12192960 | 3003840 | 0.97 | 0 | 0
|  |  | Calculated Unit for Char Sayedpur Ckt-2 due PT MCB Trip | [8 empty] | 0 |  |  |  |  | 0
33 | Madanganj-Fatullah |  | 132 | Exp | 3899 2544 | 1 | 960000 | 32.177 | 32.177 | 0 |  | 0 | 16.205 | 16.205 | 0 |  | 0 | 0 | 0
| Madanganj-Fatullah |  | 132 | Imp | 3899 2544 | 1 | 960000 | 18.041 | 18.041 | 0 | 0 |  | 14.511 | 14.511 | 0 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering
[10 empty] | Total=> | 0 | 23915520 |  |  | Total=> | 0 | 5849280 | 23915520 | 5849280 | 0.97
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 88320 | 916962240 |  |  |  | 9179520 | 326462880
NET TOTAL Imp (Energy Exp - EnergyImp) => | [11 empty] | 916873920 |  |  |  |  | 317283360 | 916873920 | 317283360 | 0.95 |  | 0 |  | 0.94502
132 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 916873920 |  | 317283360 |  | 0.95 | 0
[8 empty] | PDB Unit |  | 916873920 |  | KWH
[8 empty] | PGCB Unit |  | 916873920 |  | KWH
33 KV LEVEL | [10 empty] | Month July-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | KVARImp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS)
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Exp | 8993 640E | 1 | 48000 | 11910.314 | 11910.314 | 0 |  | 0 | 6895.224 | 6895.224 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Lalbag-1 |  | 33 | Exp | 8993861E | 1 | 48000 | 14467.636 | 14467.636 | 0 |  | 0 | 9301.512 | 9301.512 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Lalbag-2 |  | 33 | Exp | 8993 798 | 1 | 48000 | 60.352 | 60.352 | 0 |  | 0 | 19.51 | 19.51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss |  |  |  |  | Total=> | 0 | 0 |  |  | Total=> | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Exp | 8993 841 | 1 | 18000 | 29344.892 | 29344.892 | 0 |  | 0 | 7711.314 | 7711.314 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Shah Cement |  | 33 | Exp | 8993 841 | 1 | 36000 | 39285.417 | 39374.588 | 89.171 |  | 3210156 | 10366.967 | 10394.464 | 27.497 |  | 989892 | 3210156 | 989892 | 0.9556 | 0 | 0 | 1542
5 | Mandal para |  | 33 | Exp | 8993 842 | 1 | 180000 | 2588.486 | 2588.486 | 0 |  | 0 | 633.753 | 633.753 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [9 empty] | Total=> | 0 | 3210156 |  |  | Total=> | 0 | 989892 | 3210156 | 989892 | 0.9556 |  | 0 | 1542
6 | Jigatala (JP garden) | Kallyanpur | 33 | Exp | 8993834 (old) | 1 | 180000 | 1072.053 | 1072.053 | 0 |  | 0 | 547.36 | 547.36 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 33 | Exp | 38992490 (new) | 1 | 180000 | 1.16 | 1.22 | 0.06 |  | 10800 | 0.103 | 0.103 | 0 |  | 0 | 10800 | 0 | 0 | 0 | 0 | 1
7 | Shere Bangla |  | 33 | Exp | 8993 833 | 1 | 180000 | 317.19 | 317.19 | 0 |  | 0 | 244.203 | 244.204 | 0.001 |  | 180 | 0 | 180 | #DIV/0! | 0 | 0 | 0
8 | Satmosjid-1 |  | 33 | Exp | 8993 638E | 1 | 180000 | 4184.327 | 4191.915 | 7.588 |  | 1365840 | 2254.664 | 2255.39 | 0.726 |  | 130680 | 1365840 | 130680 | 0.99545 | 0 | 0 | 100
9 | Satmosjid -2 |  | 33 | Exp | 8993 669E | 1 | 180000 | 5753.894 | 5801.534 | 47.64 |  | 8575200 | 2625.381 | 2641.666 | 16.285 |  | 2931300 | 8575200 | 2931300 | 0.94624 | 0 | 0 | 627
10 | Kallayanpur T3 |  | 33 | Exp | 8993 831 | 1 | 180000 | 6495.578 | 6518.449 | 22.871 |  | 4116780 | 3176.135 | 3183.572 | 7.437 |  | 1338660 | 4116780 | 1338660 | 0.95099 | 0 | 0 | 301
11 | Kallayanpur T4 |  | 33 | Exp | 8993 839 | 1 | 180000 | 8617.568 | 8670.191 | 52.623 |  | 9472140 | 4020.639 | 4041.326 | 20.687 |  | 3723660 | 9472140 | 3723660 | 0.93067 | 0 | 0 | 693
12 | Kallayanpur T5 |  | 33 | Exp | 3899 2611 | 1 | 180000 | 86.616 | 116.135 | 29.519 |  | 5313420 | 21.209 | 29.486 | 8.277 |  | 1489860 | 5313420 | 1489860 | 0.96287 | 0 | 0 | 389
| Exp to Desco at 11 KV | [9 empty] | 7812738.6 |  |  |  |  | 1322299.2 |  | -7812738.6 | -1322299.2 | 0 | 0 | 0
13 | Lalmatia |  | 33 | Exp | 8993 836E | 1 | 180000 | 5450.602 | 5452.879 | 2.277 |  | 409860 | 2685.406 | 2686.619 | 1.213 |  | 218340 | 409860 | 218340 | 0.88258 | 0.01 | 4098.6 | 30
[10 empty] | Total=> | 7812738.6 | 29264040 |  |  | Total=> | 1322299.2 | 9832680 | 21451301.4 | 8510380.8 | 0.92952 |  |  | 2141
SATMOSJID 132/33KV SS
14 | Transformer-1 | Satmosjid | 33 | Exp | 50147586E | 1 | 750000 | 3099.791 | 3141.193 | 41.402 |  | 31051500 | 1562.816 | 1579.213 | 16.397 |  | 12297750 | 31051500 | 12297750 | 0.92974 | 0 | 0 | 0
15 | Transformer-2 |  | 33 | Exp | 50148569E | 1 | 750000 | 2739.184 | 2781.285 | 42.101 |  | 31575750 | 1358.853 | 1375.53 | 16.677 |  | 12507750 | 31575750 | 12507750 | 0.92972 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 62627250 |  |  | Total=> | 0 | 24805500 | 62627250 | 24805500 | 0.92973 | 0 | 0 | 0
AGARGAON 132/33KV SS
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Exp | 3578 6569 | 1.0008 | 180000 | 1885.528 | 1910.455 | 24.927 |  | 4490336.4191 | 638.443 | 643.896 | 5.453 |  | 981540 | 4490336.4191 | 981540 | 0.97693 | 0 | 0 |  | NO CF in VARH
17 | DPDC-CKT-2 |  | 33 | Exp | 3578 6575 | 1.0008 | 180000 | 646.365 | 663.099 | 16.734 |  | 3014453.7906 | 44.81 | 46.672 | 1.862 |  | 335160 | 3014453.7906 | 335160 | 0.99388 | 0 | 0 |  | NO CF in VARH
18 | DPDC-CKT-3 |  | 33 | Exp | 3578 6580 | 1.0008 | 180000 | 106.915 | 106.915 | 0 |  | 0 | 4.16 | 4.16 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | NO CF in VARH
19 | Monipuripara-1 |  |  |  |  | 1.0008 | 180000 | 1026.085 | 1061.83 | 35.745 |  | 6439085.1407 | 435.896 | 447.236 | 11.34 |  | 2041200 | 6439085.1407 | 2041200 | 0.95325 | 0 | 0 |  | NO CF in VARH
20 | Monipuripara-2 |  |  |  |  | 1.0008 | 180000 | 741.116 | 766.09 | 24.974 |  | 4498802.9739 | 275.308 | 280.977 | 5.669 |  | 1020420 | 4498802.9739 | 1020420 | 0.97523 | 0 | 0 |  | NO CF in VARH
Maniknagar 230/132 KV SS | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 18442678.3243 |  |  | Total=> | 0 | 4378320 | 18442678.3243 | 4378320 | 0.97296 |  | 0 | 0
21 | Axuxilary -1 | Maniknagar | 33 | Exp | AH14044078 | 1.025 | 1 | 397817.5 | 403596.2 | 5778.7 |  | 5923.1675 | 254717.8 | 258560 | 3842.2 |  | 3938.255 | 5923.1675 | 3938.255 | 0.83273 | 0.06 | 0 | 0
22 | Axuxilary -2 |  | 33 | Exp | AH14044072 | 1.025 | 1 | 369244.1 | 374573.2 | 5329.1 |  | 5462.3275 | 129044.5 | 131463.5 | 2419 |  | 2479.475 | 5462.3275 | 2479.475 | 0.91058 | 0 | 0 | 0
Shyampur 230/132 kv | [5 empty] | CF | 1.025 |  |  | Total=> | 0 | 11385.495 |  |  | Total=> | 0 | 6417.73 | 11385.495 | 6417.73 | 0.87114 |  | 4098.6 | 0
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Exp | DHKG9742 | 1.025 | 2400 | 341.169 | 343.416 | 2.247 |  | 5527.62 | 216.631 | 218.717 | 2.086 |  | 5131.56 | 5527.62 | 5131.56 | 0.73287 | 0 | 0 | 0
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Exp | DHKG9743 | 1.025 | 2400 | 87.479 | 95.379 | 7.9 |  | 19434 | 48.561 | 52.31 | 3.749 |  | 9222.54 | 19434 | 9222.54 | 0.90343 | 0 | 0 | 0
[10 empty] | Total=> | 0 | 24961.62 |  |  | Total=> | 0 | 14354.1 | 24961.62 | 14354.1 | 0.86689 |  |  | 0
TOTAL ( EnergyImp / Exp ) => | [10 empty] | 7812738.6 | 113580471.4393 |  |  |  | 1322299.2 | 40027163.83 | [5 empty] | 3683 | Total Bus Loss Unit
NET TOTAL Imp 33 KV (Energy Exp - EnergyImp) => | [11 empty] | 105767732.8393 |  |  |  |  | 38704864.63 | 105767732.8393 | 38704864.63 | 0.9391 |  | 4098.6 |  | 0.9391
NET TOTAL Imp 11 KV (Energy Exp - EnergyImp) => | [11 empty] | 816720 |  |  | 106584452.8393
33 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 105767732.8393 |  | 38704864.63 |  | 0.9391 | 4098.6
[8 empty] | PDB Unit |  | 105771831.4393 |  | KWH
[8 empty] | PGCB Unit |  | 105767732.8393 |  | KWH
11 KV LEVEL | [10 empty] | Month July-2023
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | KWH CALCULATION | [6 empty] | KVARH CALCULATION |  |  |  |  | Net Energy (KWH / KVARH) Calculaton |  | PFC Calculation |  |  | Bus Loss | Remarks
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | CF | OMF | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | EnergyImp (KWh) | Energy Exp (KWh) | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Diff. | KVAR Imp | KVAR Exp | Net Energy (KWH) | Net Energy (KVARH) | P.F | P.F.C Corr. Factor | PFC Unit | Bus Loss | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120)
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Exp | 14957 | 1 | 40000 | 1915.47 | 1915.47 | 0 |  | 0 | 6270.8 | 6270.8 | 0 |  | 0 |  |  | 0 | 1
| Monsurabab 11KV O/H |  | 11 | Exp | 77816681 | 1 | 8000 | 40126.43 | 40126.43 | 0 |  | 0 | 20599.05 | 20599.05 | 0 |  | 0 |  |  | 0 | 1
| Beri Bandh 11KV O/H |  | 11 | Exp | 14960 | 1 | 40000 | 9317.28 | 9317.28 | 0 |  | 0 | 3844.13 | 3844.13 | 0 |  | 0 |  |  | 0 | 1
| Swerage 11KV O/H |  | 11 | Exp | 14959 | 1 | 40000 | 782.24 | 782.24 | 0 |  | 0 | 4541.95 | 4541.95 | 0 |  | 0 |  |  | 0 | 1
| Ring Road 11KV O/H |  | 11 | Exp | 77816675 | 1 | 8000 | 34050.59 | 34050.59 | 0 |  | 0 | 17224.86 | 17224.86 | 0 |  | 0 |  |  | 0 | 1
| RMU Feeder |  | 11 | Exp | 14997 | 1 | 40000 | 994.03 | 994.03 | 0 |  | 0 | 211.73 | 211.73 | 0 |  | 0 |  |  | 0 | 1
| P.C Culture Housing 11 KV |  | 11 | Exp | Dhk-15019 | 1 | 40000 | 5335.08 | 5335.08 | 0 | ` | 0 | 2356.43 | 2356.43 | 0 |  | 0 |  |  | 0 | 1
AGARGAON 33/11 KV S/S (Tel: 8122865) | [9 empty] | Total=> |  | 0 |  |  |  |  | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Exp | 1502 6 | 1 | 40000 | 9164.92 | 9179.18 | 14.26 |  | 570400 | 3457.08 | 3461.52 | 4.44 |  | 177600 | 584660 | 182040 | 0.95479 | 1
2 | 11 KV R.M.U Feeder |  | 11 | Exp | 1502 7 | 1 | 40000 | 3859.52 | 3863.97 | 4.45 |  | 178000 | 1262.98 | 1263.16 | 0.18 |  | 7200 | 182450 | 7380 | 0.99918 | 1 |  | 7200 | RMU Feeder KVARH Back Calculation as per KWH Percentage
3a | PD Betar |  | 11 | Imp | 2612 100427 | 1 | 600 | 8834 | 8834 | 0 | 0 |  | 2874 | 2874 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 2612 100517 | 1 | 1800 | 2444.43 | 2444.43 | 0 | 0 |  | 572 | 572 | 0 | 0 |  | 0 | 0 | 0 | 1
3b | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 1398 | 1398 | 0 | 0 |  | 494 | 494 | 0 | 0 |  | 0 | 0 | 0 | 1
new | SE,NB,Betar |  | 11 | Imp | 6450 15020085 | 1 | 300 | 756 | 756 | 0 | 0 |  | 243 | 243 | 0 | 0 |  | 0 | 0 | 0 | 1
3c | NINS & H |  | 11 | Imp | Dhk-59122 | 1 | 1000 | 26885 | 26885 | 0 | 0 |  | 11652 | 11652 | 0 | 0 |  | 0 | 0 | 0 | 1
4 | 11 KV Sher-e-banglanagar |  | 11 | Exp | 1502 5 | 1 | 40000 | 3976.15 | 3977.36 | 1.21 |  | 48400 | 1886.88 | 1887.8 | 0.92 |  | 36800 | 49610 | 37720 | 0.79604 | 1.1306
5 | BICC - U/G |  | 11 | Exp | 1502 4 | 1 | 40000 | 1038.1 | 1038.1 | 0 |  | 0 | 297.32 | 297.32 | 0 |  | 0 | 0 | 0 | 0 | 1
6 | NEC |  | 11 | Exp | 1502 3 | 1 | 40000 | 431.56 | 431.56 | 0 |  | 0 | 56.29 | 56.29 | 0 |  | 0 | 0 | 0 | 0 | 1
7 | Manikmia Avenue |  | 11 | Exp | 7602 6327 | 1 | 40000 | 3357 | 3357 | 0 |  | 0 | 1465 | 1465 | 0 |  | 0 | 0 | 0 | 0 | 1
| Manikmia Avenue | new | 11 | Exp | DHK27341 | 1 | 40000 | 175.92 | 175.92 | 0 |  | 0 | 57.975 | 57.975 | 0 |  | 0 | 0 | 0
[10 empty] | Total=> | 0 | 796800 |  |  |  | 0 | 221600 | 816720 | 227140 | 0.96343
TOTAL ( Energy Import / Export ) => | [10 empty] | 0 | 796800 |  |  |  | 0 | 221600
NET TOTAL Import (Energy Export - Energy Import) => | [11 empty] | 796800 |  |  |  |  | 221600
11 kV Import Converted Into 33 kV Import (Adding 2.5%) => ( BPDB & PGCB) | [11 empty] | 816720 |  |  |  |  | 227140 | 816720 | 227140 | 0.96343 |  | 0 |  | 0.96343
11 KV TOTAL
[8 empty] | KWH |  | KVARH |  | PF | PFC
[8 empty] | 816720 |  | 227140 |  | 0.96343 | 0
[8 empty] | PDB Unit |  | 816720 |  | KWH
[8 empty] | PGCB Unit |  | 816720 |  | KWH

## PDB SUM AMR
SUMMARY OF PDB ENERGY BILL (Certified For Payment)
DPDC IMPORT UNIT & TAKA FOR THE |  |  |  | Month July-2023
Sl.No. | Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from February-2023) | Amount (Taka) | Remarks |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত ইউনিট | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত ইউনিট | পার্থক্য (ইউনিট) | মন্তব্য |  |  | ক্র: নং | ভোল্টেজ লেভেল | বিউবো কর্তৃক প্রেরিত বিল (টাকায়) | ডিপিডিসি (T&EA) কর্তৃক প্রত্যায়িত বিল (টাকায়) | পার্থক্য (টাকায়) | মন্তব্য
| a | b | c | d |  |  | a | b | c | d | e = c-d | f |  |  | a | b | c | d | e = c-d | f
1 | 132kv | 916873920.22 | 8.1335 | 7457394030 |  |  | 1 | ১৩২ কেভি ইউনিট (এনার্জি) | 916873920.22 | 916873920.22 | 0 |  |  |  | 1 | ১৩২ কেভি (এনার্জি) | 7457394030 | 7457394030 | 0
2a | 33kv | 105767732.8393 | 8.22 | 869410764 |  |  | 2 | ৩৩ কেভি ইউনিট (এনার্জি) | 105767732.8393 | 105767732.8393 | 0 |  |  |  | 2 | ৩৩ কেভি (এনার্জি) | 869410764 | 869410764 | 0
2b | 33KV (after adding 2.5% with 11KV ) | 816720 | 8.22 | 6713438 |  |  | 3 | ৩৩ কেভি ইউনিট (১১ কেভিকে ২.৫% যোগ করে) | 816720 | 816720 | 0 |  |  |  | 3 | ৩৩ কেভি (১১ কেভিকে ২.৫% যোগ করে) | 6713438 | 6713438 | 0
2c | Bus Loss Units (33kv) | 3683 | 8.22 | 30274 |  |  | 4 | ৩৩ কেভি বাসলস ইউনিট | 3683 | 3683 | 0 |  |  |  | 4 | ৩৩ কেভি বাসলস | 30274 | 30274 | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 106588135.8393 |  | 876154476 |  |  | 5 | ৩৩ কেভি মোট এনার্জি ইউনিট (২+৩+৪) | 106588135.8393 | 106588135.8393 | 0 |  |  |  | 5 | ৩৩ কেভি মোট এনার্জি (২+৩+৪) | 876154476 | 876154476 | 0
4 | TOTAL 132kv & 33kv (1+3) | 1023462056.0593 |  | 8333548506 |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 1023462056.0593 | 1023462056.0593 | 0 |  |  |  | 6 | ১৩২ ও ৩৩ কেভি মোট এনার্জি (১+৫) | 8333548506 | 8333548506 | 0
5 | 132KV P.F.C | 0 | 8.1335 | 0 |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 0 | 0 | 0 |  |  |  | 7 | ১৩২ কেভি পিএফসি সারচার্জ | 0 | 0 | 0
6 | 33KV P.F.C | 4098.6 | 8.22 | 33690.492 |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট | 4098.6 | 4098.6 | 0 |  |  |  | 8 | ৩৩ কেভি পিএফসি সারচার্জ | 33690.492 | 33690.492 | 0
7 | TOTAL 132kv & 33kv P.F.Surcharge=> (5+6) | 4098.6 |  | 33690.492 |  |  | 9 | মোট পিএফসি সারচার্জের ইকুইভেলেন্ট ইউনিট (৭+৮) | 4098.6 | 4098.6 | 0 |  |  |  | 9 | মোটপিএফসি সারচার্জ (৭+৮) | 33690.492 | 33690.492 | 0
8 | TOTAL Billed Amount => (4+7) | 1023466154.6593 |  | 8333582196.492 |  | 8471338149.432 | 10 | সর্বমোট (৬+৯) | 1023466154.6593 | 1023466154.6593 | 0 |  |  |  | 10 | সর্বমোট (৬+৯) | 8333582196.492 | 8333582196.492 | 0
9 | AIT => (6% * Total Billed Amount) |  |  | 500014932 | Source Tax
10 | NET BILL TOTAL => (8-9) |  |  | 7833567264.492
11*** | 21th Installment for PDB's PFC Surcharge Due (Oct-2009 to Nov-2017) |  |  | 137755952.94 | As per DPDC Board's Decision
12 | Grand TOTAL (Taka) => (10+11) |  |  | 7971323217.432
"In word: Taka Seven Hundred Ninety Five Crore Six Lac Forty One Thousand Three Hundred Fifty Eight and Poisa Ninety Four"
N.B:*** Detailed Calculation of Installment for PDB's PFC Surcharge Due has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PDB's PFC Surcharge Due
0
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month (TK) | Status of Payment of the Installment | #VALUE!
2021-09-01 | 1 | 137755952.94 | 137755952.94 | 3168386917.62 | Paid | #VALUE!
2021-10-01 | 2 | 137755952.94 | 275511905.88 | 3030630964.68 | Paid
2021-11-01 | 3 | 137755952.94 | 413267858.82 | 2892875011.74 | Paid
2021-12-01 | 4 | 137755952.94 | 551023811.76 | 2755119058.8 | Paid
2022-01-01 | 5 | 137755952.94 | 688779764.7 | 2617363105.86 | Paid
2022-02-01 | 6 | 137755952.94 | 826535717.64 | 2479607152.92 | Paid
2022-03-01 | 7 | 137755952.94 | 964291670.58 | 2341851199.98 | Paid
2022-04-01 | 8 | 137755952.94 | 1102047623.52 | 2204095247.04 | Paid
2022-05-01 | 9 | 137755952.94 | 1239803576.46 | 2066339294.1 | Paid
2022-06-01 | 10 | 137755952.94 | 1377559529.4 | 1928583341.16 | Paid
2022-07-01 | 11 | 137755952.94 | 1515315482.34 | 1790827388.22 | Paid
2022-08-01 | 12 | 137755952.94 | 1653071435.28 | 1653071435.28 | Paid
2022-09-01 | 13 | 137755952.94 | 1790827388.22 | 1515315482.34 | Paid
2022-10-01 | 14 | 137755952.94 | 1928583341.16 | 1377559529.4 | Paid
2022-11-01 | 15 | 137755952.94 | 2066339294.1 | 1239803576.46 | Paid
2022-12-01 | 16 | 137755952.94 | 2204095247.04 | 1102047623.52 | Paid
2023-01-01 | 17 | 137755952.94 | 2341851199.98 | 964291670.58 | Paid
2023-02-01 | 18 | 137755952.94 | 2479607152.92 | 826535717.64 | Paid
2023-03-01 | 19 | 137755952.94 | 2617363105.86 | 688779764.7 | Paid
2023-04-01 | 20 | 137755952.94 | 2755119058.8 | 551023811.76 | Paid
2023-05-01 | 21 | 137755952.94 | 2892875011.74 | 413267858.82 | Paid
2023-06-01 | 22 | 137755952.94 | 3030630964.68 | 275511905.88 | Certified For Payment
2023-07-01 | 23 | 137755952.94 | 3168386917.62 | 137755952.94
2023-08-01 | 24 | 137755952.94 | 3306142870.56 | 0
| Total | 3306142870.56
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
POWER CELL REPORT ON AVERAGE POWER FACTOR OF DPDC
SUMMARY OF PDB's POWER FGACTOR
P.F.C FOR THE MONTH OF |  |  |  | Month July-2023 | Remarks
SL. NO. | VOLTAGE LEVEL | KWH | KVARH | P.F
| A | B | C | D=COS(ATAN(C/B)
1 | 132kv Level | #REF! | #REF! | #REF!
2 | 33kv Level | #REF! | #REF! | #REF!
3 | 11kv Level | #REF! | #REF! | #REF!
| TOTAL=> | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2017 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | REMARKS
|  | A | B | C | D=COS(TAN-1(C/B))
1 | JULY--2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF!
2 | AUGUST--2018
3 | SEPTEMBER--2018
4 | OCTOBER--2018
5 | NOVEMBER--2018
6 | DECEMBER--2018
7 | JANUARY--2019
8 | FERRUARY--2019
9 | MARCH--2019
10 | APRIL--2019
11 | MAY--2019
12 | JUNE--2019 |  |  |  | #DIV/0!
13 | TOTAL=> |  | #REF! | #REF! | #REF!
POWER FACTOR FOR THE MONTH OF JULY-2016 TO |  |  |  | JUNE-2018
SL. NO. | NAME OF THE MONTH& YEAR | VOLTAGE LEVEL | KWH | KVARH | POWER FACTOR | Remarks
|  | A | B | C | D=COS(TAN-1(C/B))
1 | July to September-2018 | 132kv,33kv &11KV | #REF! | #REF! | #REF! | Every 3 Month
2 | October to December-2018
3 | January to March--2019
4 | April to June -- 2019
5 | TOTAL=> |  | #REF! | #REF! | #REF!
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audir, DPDC |  | Superintending Engineer Tariff & Energy Audir, DPDC
SUMMARY OF PGCB WHEELING CHARGE BILL | [8 empty] | wcwRwmwe BDwbU | [7 empty] | wcwRwmwe UvKv
[11 empty] | (cvMjv †i›Uv‡ji |  | BDwbU e¨vwZZ) | 0 | 0
WHEELING CHARGE BILL FOR THE |  |  |  | Month July-2023
SL.NO. | Voltage Level | Net import unit at respective voltage level (KWH) | Tariff rate at different voltage level | Amount (Taka) | Remarks |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ |  | µ: bs | ‡fv‡ëR †j‡fj | weD‡ev KZ©„K †cÖwiZ wej (wcGdwm ev‡`) | wcwRwmwe KZ©„K †cÖwiZ | T&EA KZ©„K cÖZ¨vwqZ | cv_©K¨ | gšÍe¨ | Calculations for Comparison
| Voltage Level | Net Import Unit at Respective Voltage Level (KWH) | Tariff Rate at Respective Voltage Level (Effective from March 2020) | Amount (Taka) | Remarks
| a | b | c | d=b*c | e |  | K | L | M | N | O | P = N-O | Q |  | K | L | M | N | O | P = N-O | Q | PGCB Amount
1 | 132kv Level | 916873920.22 | 0.2886 | 264609813.3755 |  |  | 1 | 132 †Kwf (GbvwR©) | 916873920.22 | 916873920.22 | 916873920.22 | 0 | kxZjÿv MÖxW¦ |  | 1 | 132 †Kwf (GbvwR©) | 7457394030 | 264609813.3755 | 264609813.3755 | 0
2a | 33kv Level | 105767732.8393 | 0.2944 | 31138020.5479 |  |  | 2 | 33 †Kwf (GbvwR©) | 105767732.8393 | 105767732.8393 | 105767732.8393 | 0 | g`bMÄ MÖxW¦ |  | 2 | 33 †Kwf (GbvwR©) | 869410764 | 31138020.5479 | 31138020.5479 | 0 |  | 33KV Amount (2+3+4) => | 31379547.1911
2b | 11KV Level after adding 2.5% (33KV LEVEL) | 816720 | 0.2944 | 240442.368 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 816720 | 816720 | 816720 | 0 |  |  | 3 | 33 †Kwf (11 †Kwf‡K 2.5% ‡hvM K‡i) | 6713438 | 240442.368 | 240442.368 | 0 |  | kxZjÿv MÖxW => | 0
2c | Bus Loss Units (33kv level) | 3683 | 0.2944 | 1084.6752 |  |  | 4 | 33 ‡Kwf evm jm | 3683 | 3683 | 3683 | 0 |  |  | 4 | 33 ‡Kwf evmjm | 30274 | 1084.2752 | 1084.6752 | -0.4 |  | g`bMÄ MÖxW => | 0
3 | SUB-TOTAL at 33KV (2a + 2b + 2c) | 106588135.8393 | 0.2944 | 31379547.5911 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 106588135.8393 | 106588135.8393 | 106588135.8393 | 0 |  |  | 5 | 33 ‡Kwf †gvU GbvwR© (2+3+4) | 876154476 | 31379547.1911 | 31379547.5911 | -0.4
4 | TOTAL=> (1+3) | 1023462056.0593 |  | 295989360.9666 |  |  | 6 | me©‡gvU (1+5) | 1023462056.0593 | 1023462056.0593 | 1023462056.0593 | 0 |  |  | 6 | me©‡gvU (1+5) | 8333548506 | 295989360.5666 | 295989360.9666 | -0.4
5 | Less: For Shitalkhya SS Maintenance (As per Power Division Decision) |  |  | 1500000
6*** | Add: Ref.No: 27.87.0000.517.31.031.20.43; Date: 09/11/2022 ( 8th Installment ) |  |  | 25993419.79 |  |  | ‡gvU (GbvwR©) |  | 1023458373.0593 | 1023458373.0593 | 1023458373.0593 | 0 |  |  | ‡gvU (GbvwR©) |  | 8333518232 | 295988276.2914 | 31379547.5911 | 264608728.7003
7 | Grand TOTAL=> (4-5+6) |  |  | 320482780.7566
| CERTIFED UNITS |  |  | 1023462056.0593
| CERTIFED TAKA |  |  | 295989360.9666
| CERTIFED TAKA (After Shitalkhya SS Maintenance Charge Deduction & Adding 8th Installment of Wheeling Charge Due) |  |  | 320482780.7566
evsjv
In word: Taka Thirty One Crore Ninety Seven Lac Eight Thousand and Sixty
N.B:*** Detailed Calculation of Installment for PGCB'S Due Wheeling Charge has been provided in Next Page
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
Detailed Calculation of Installment for PGCB'S Due Wheeling Charge
Bill Month | Installment No. | Amount Per Installment (TK) | Total Paid upto Bill Month (TK) | Total Remaining upto Bill Month | Status of Payment of the Installment
2022-10-01 | 1 | 25993419.79 | 25993419.79 | 597848655.17 | Paid
2022-11-01 | 2 | 25993419.79 | 51986839.58 | 571855235.38 | Paid
2022-12-01 | 3 | 25993419.79 | 77980259.37 | 545861815.59 | Paid
2023-01-01 | 4 | 25993419.79 | 103973679.16 | 519868395.8 | Paid
2023-02-01 | 5 | 25993419.79 | 129967098.95 | 493874976.01 | Paid
2023-03-01 | 6 | 25993419.79 | 155960518.74 | 467881556.22 | Paid
2023-04-01 | 7 | 25993419.79 | 181953938.53 | 441888136.43 | Paid
2023-05-01 | 8 | 25993419.79 | 207947358.32 | 415894716.64 | Paid
2023-06-01 | 9 | 25993419.79 | 233940778.11 | 389901296.85 | Certified For Payment
2023-07-01 | 10 | 25993419.79 | 259934197.9 | 363907877.06
2023-08-01 | 11 | 25993419.79 | 285927617.69 | 337914457.27
2023-09-01 | 12 | 25993419.79 | 311921037.48 | 311921037.48
2023-10-01 | 13 | 25993419.79 | 337914457.27 | 285927617.69
2023-11-01 | 14 | 25993419.79 | 363907877.06 | 259934197.9
2023-12-01 | 15 | 25993419.79 | 389901296.85 | 233940778.11
2024-01-01 | 16 | 25993419.79 | 415894716.64 | 207947358.32
2024-02-01 | 17 | 25993419.79 | 441888136.43 | 181953938.53
2024-03-01 | 18 | 25993419.79 | 467881556.22 | 155960518.74
2024-04-01 | 19 | 25993419.79 | 493874976.01 | 129967098.95
2024-05-01 | 20 | 25993419.79 | 519868395.8 | 103973679.16
2024-06-01 | 21 | 25993419.79 | 545861815.59 | 77980259.37
2024-07-01 | 22 | 25993419.79 | 571855235.38 | 51986839.58
2024-08-01 | 23 | 25993419.79 | 597848655.17 | 25993419.79
2024-09-01 | 24 | 25993419.79 | 623842074.96 | 0
| Total | 623842074.96
Sub-Divisional Engineer Tariff & Energy Audit, DPDC |  | Executive Engineer Tariff & Energy Audit, DPDC |  | Superintending Engineer Tariff & Energy Audit, DPDC
| CERTIFED UNITS | 0
| CERTIFED TAKA | 0
In word:Nine Core Ninety Lac Seventy Six Thousand Eight Hundred Eighty Three Taka only.
SUMMERY OF AVERAGE POWER FACTOR
AUGUST 2012
| Voltage Level | KWH | KVARH | Power Factor
| 132 KV | #REF! | #REF! | #REF!
| 33 KV | #REF! | #REF! | #REF!
| 11 KV | #REF! | #REF! | #REF!
| Total | #REF! | #REF! | #REF!

## Transmission_Check (hidden)
[6 empty] | Month July-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | Energy Imp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 03894180291 Ex-101,01936016025 /01755582416) | [5 empty] | 0 | 0 | 122568961.62 | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid | 122182512 | Fatullah Grid | 37396800 | 386449.62 | 0.3153%
1 | Hasnabad to Shyampur | Hasnabad Grid | 132 | Export | 8993532 | 0 | 0 |  |  |  | Shyampur Grid | 84785712
|  |  | 132 | Import |  | 86400 | 0
2 | Hasnabad to Postogola-1 |  | 132 | Export | 42627826 | 0 | 27936960 | 35970240 | Postogola 132/33 KV Grid | 35704800 | Postogola Grid | 35704800 | 265440 | 0.7379%
|  |  | 132 | Import |  | 0 | 0
3 | Hasnabad to Postogola-2 |  | 132 | Export | 42627815 | 0 | 8033280
|  |  | 132 | Import |  | 0 | 0
4 | Aggrekko 100 MW (Brammhongao) | Aggreko Plant | 132 | Export | PN-1711A04601 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
HARIPUR 230/132 KV S/S (Tel: 01711644856) | [5 empty] | 86400 | 35970240
6 | Maniknager-2 (new line to ullon) |  | 132 | Export | 8993624 | 0 | 24617280 | 106678080 | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid | 105753840 | Ullon Grid | 24225840 | 924240 | 0.8664%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Dhanmondi Grid | 69813600
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 24617280 |  |  |  | DU Grid | 11714400
7 | Kallyanpur to Lalbagh 1 | Kallyanpur Grid | 132 | Export | 8993518 | 0 | 16237440 | 139111200 | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid | 136860400 | Lalbagh Grid | 48370000 | 2250800 | 1.618%
|  |  | 132 | Import |  | 0 | 0 |  |  |  | Kamrangirchar Grid | 30940800
8 | Kallyanpur to Lalbagh 2 |  | 132 | Export | 5014660 | 0 | 16323840 |  |  |  | Jigatola Grid | 57549600
|  |  | 132 | Import |  | 0 | 0
132/33 KV SHITALAKHYA S/S (Tel: 7647373 / 01778500119) Plant Mn-01755525013 | [5 empty] | 0 | 32561280
9 | Tranformer 3 | Shitalakhya Grid | 132 | Export | 50501730 | 0 | 20639520 | 59587680 | Sitalakhya 132/33 KV Grid | 59622737 | Sitalakhya Grid | 59622737 | -35057 | -0.05883%
10 | Tranformer 1 |  | 132 | Export | 80505634 | 0 | 19423200
11 | Tranformer 2 |  | 132 | Export | 80505637 | 0 | 19524960
12 | MI CEMENT |  | 132 | Export | 38992489 (New) | 0 | 10749120 | 10749120 | Sitalakhya NOCS | 10749120 | Sitalakhya NOCS | 10749120 | 0 | 0%
SIDDHIRGANJ 132 kV S/S (Tel: 7694743) | [5 empty] | 0 | 70336800
13 | XFR- T1 | Siddhirgonj Grid | 132 | Export | 8993683 | 0 | 36034560 | 71713920 | Siddirganj 132/33 KV Grid | 72239040 | Siddirganj Grid | 72239040 | -525120 | -0.7322%
14 | XFR- T2 |  | 132 | Export | 8993682 | 0 | 35679360
15 | Ullon-1 |  | 132 | Export | 8993681 | 0 | 35697600 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
16 | Ullon-2 |  | 132 | Export | 8993680 | 0 | 0
|  |  | 132 | Import |  | 0 | 0
17 | Matuail |  | 132 | Export | 8993555 | 0 | 38361600 | 38361600 | Matuail 132/33 KV Grid | 38360688 | Matuail Grid | 38360688 | 912 | 0.002377%
|  |  | 132 | Import |  | 0 | 0
[6 empty] | 0 | 145773120
RAMPURA 230/132 KV S/S 8853954,01711644817(anis SDE) | [5 empty] | #REF! | #REF!
18 | Mogbazar-1 | Rumpura Grid | 132 | Export | 8993631 | 0 | 41259840 | 73101120 | Moghbazar 132/33 KV Grid | 72772800 | Moghbazar Gird | 72772800 | 328320 | 0.4491%
|  |  |  | Import |  | 0 | 0
19 | Mogbazar-2 |  | 132 | Export | 8993659 | 0 | 31841280
|  |  |  | Import |  | 0 | 0
20 | Ullon U/G -1 |  | 132 | Export | 8993659 | 0 | 12392640 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid
|  |  |  | Import |  | 960 | 0
21 | Ullon U/G -2 |  | 132 | Export | 8993660 | 0 | 11788800
|  |  |  | Import |  | 960 | 0
22 | Madartheck 1 |  | 132 | Export | 50146667 | 0 | 26777280 | 53400000 | Madartek 132/33 KV Grid | 53400000 | Madartek Grid | 53400000 | 0 | 0%
23 | Madartheck 2 |  | 132 | Export | 50146668 | 0 | 26622720
24 | Dhaka University-1 (Exp) |  | 132 | Export | 42627810 | 0 | 11048640 |  | Ullon 132/33 KV Grid & Dhanmondi 132/33 KV Grid and DU 132/33 KV Grid
| Dhaka University-1 (Imp) |  | 132 | Import |  | 0 | 0
25 | Dhaka University-2 (Exp) |  | 132 | Export | 42627812 | 0 | 11135040
| Dhaka University-2 (Imp) |  | 132 | Import |  | 0 | 0
Maniknagar 230/132 Kv s/s | [5 empty] | 1920 | 172866240
26 | Maniknagar-1 | Maniknagar | 132 | Export | 50147584 | 0 | 90931200 | 181741440 | Maniknagar 132/33 KV Grid | 180797000 | Kazla Grid | 56325600 | 944440 | 0.5197%
27 | Maniknagar-2 |  | 132 | Export | 50147585 | 0 | 90810240 |  |  |  | Motijheel Grid | 22795200
Shyampur 230/132 Kv s/s | [5 empty] | 0 | 181741440 |  |  |  | Narinda Grid | 40627200
[11 empty] | Bangabhaban Grid | 6252000
[11 empty] | Maniknagar Grid | 54797000
28 | Tranformer - 1 | Shyampur 230/132 | 132 | Export | 38992560 | 0 | 61501440 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
|  |  | 132 | Import | wp002497 | 0 | 0
29 | Tranformer - 2 |  | 132 | Import | 38992559 | 0 | 0
|  |  | 132 | Export | 38992559 | 0 | 61128960
keranigonj 230/132 Kv s/s | [5 empty] | 0 | 122630400
30 | Keraniganj to Kamrangirchar | Keraniganj 230/132 | 132 | Export | 38992596 | 0 | 58049280 |  | Lalbagh 132/33 KV Grid, Kamrangirchar 132/33 KV Grid & Jigatola 132/33 KV Grid
|  |  | 132 | Import |  | 0 | 0
31 | Keraniganj to Lalbagh-3 |  | 132 | Export | 38992597 | 0 | 48500640
|  |  | 132 | Import |  | 0 | 0
Madangonj 132/33 Kv s/s | [5 empty] | 0 | 106549920
32 | Char Syedpur Ckt-1 | Madonganj 132/33 KV | 132 | Export | 42627811 | 0 | 11722560 | 23915520 | Charsyedpur 132/33 KV Grid | 23716800 | Charsyedpur Grid | 23716800 | 198720 | 0.8309%
33 | Char Syedpur Ckt-2 |  | 132 | Export | 42627824 | 0 | 12192960
34 | Madanganj-Fatullah Exp |  | 132 | Export | 38992544 | 0 | 0 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
| Madanganj-Fatullah Imp |  | 132 | Import | 38992544 | 0 | 0
Calculated Unit for Hasnabad-Aggreko-Fatullah-Shampur-Horipur Loop Due to Horipur Fatullah Circuit withdrawn form billing point & Madanganj-Fatullah new billing point addition without proper Metering | [5 empty] | 0 | 0
[6 empty] | 0 | 23915520 | 916898881.62 |  | 912159737 |  | 912159737 | 4739144.62 | 0.5169%
[9 empty] | 33 KV Transmission Loss |  | 105742771.2193 | 106734546.2446 | -991775.0253 | -0.9379%
TOTAL => | [8 empty] | 11 KV Transmission Loss |  | 816720 | 817950 | -1230 | -0.1506%
NET TOTAL IMPORT (Energy export - Energy import) => | [8 empty] | Total Transmission Loss |  | 1023458372.8393 | 1019712233.2446 | 3746139.5947 | 0.366%
[9 empty] | From Summary Sheet |  |  |  | 4931404.5542 | 0.4818%
[9 empty] | Mismatch in KWH |  |  |  | -1185264.9595
| 33 KV LEVEL |  |  |  |  | Month July-2023 | 0
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | 0 | 0 | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | EnergyImp (KWh) | Energy Exp (KWh)
1 | 2 | 3 | 4 | 5 | 6 | 12 | 13
HASNABAD 132/33 KV S/S (Tel: 01936-016025, PBS) | [5 empty] | 0 | 0
1 | Postagola (IG GATE) | Hasnabad 132/33 kV | 33 | Export | 8993640E | 0 | 0
2 | Lalbag-1 |  | 33 | Export | 8993861E | 0 | 0
3 | Lalbag-2 |  | 33 | Export | 8993798 | 0 | 0
MADANGONJ 132/33 KV S/S (Tel: 01711-202009) |  |  |  |  | 33 KV Buss Loss | 0 | 0
| Shah Cement | Madangonj Grid | 33 | Export | 8993841 | 0 | 0
4 | Shah Cement |  | 33 | Export | 8993841 | 0 | 3210156 | 3210156 | Sitalakhya NOCS | 3210156 | Sitalakhya NOCS | 3210156 | 0 | 0%
5 | Mandal para |  | 33 | Export | 8993842 | 0 | 0
KALLYANPUR 132/33 KV S/S (Tel: 9007406) | [5 empty] | 0 | 3210156
6 | Jigatala (JP garden) | Kallyanpur | 33 | Export | 8993834 (old) | 0 | 0 | 10800 | Shatmasjid + Japan Garden Ckt |  | Shatmasjid + Japan Garden Ckt |  | 10800 | 100%
|  |  | 33 | Export | 38992490 (new) | 0 | 10800
7 | Shere Bangla |  | 33 | Export | 8993833 | 0 | 0
8 | Satmosjid-1 |  | 33 | Export | 8993638E | 0 | 1365840 | 72978150 | Shatmasjid 132/33 KV Grid | 73967702.7904 | Asadgate SS | 18691342.7904 | -989552.7904 | -1.356%
9 | Satmosjid -2 |  | 33 | Export | 8993669E | 0 | 8575200 |  |  |  | Lalmatia SS | 14625630
[11 empty] | Japan Garden SS | 17667200
[11 empty] | Jigatola Old SS | 2384330
[11 empty] | Shatmasjid SS | 20599200
[11 empty] | BGB SS | 0
10 | Kallayanpur T3 |  | 33 | Export | 8993831 | 0 | 4116780 | 11089601.4 | Adabor NOCS | 11102800 | Adabor NOCS | 11102800 | -13198.6 | -0.119%
11 | Kallayanpur T4 |  | 33 | Export | 8993839 | 0 | 9472140
12 | Kallayanpur T5 |  | 33 | Export | 38992611 | 0 | 5313420
| Export to Desco at 11 KV |  |  |  |  | 7812738.6 | 0
13 | Lalmatia |  | 33 | Export | 8993836E | 0 | 409860 |  | Shatmasjid 132/33 KV Grid
[6 empty] | 7812738.6 | 29264040
SATMOSJID 132/33KV SS ( | [5 empty] | 0 | 0
14 | Transformer-1 | Satmosjid | 33 | Export | 50147586E | 0 | 31051500 |  | Shatmasjid 132/33 KV Grid
15 | Transformer-2 |  | 33 | Export | 50148569E | 0 | 31575750
AGARGAON 132/33KV SS | [5 empty] | 0 | 62627250
16 | DPDC-CKT-1 | Sher-e Bangla S/S01777743202 | 33 | Export | 35786569 | 0 | 4490336.4191 | 7504790.2097 | Sherebanglanagar 33/11 KV SS | 7504790.2097 | Sherebanglanagar SS | 7504790.2097 | 0 | 0%
17 | DPDC-CKT-2 |  | 33 | Export | 35786575 | 0 | 3014453.7906
18 | DPDC-CKT-3 |  | 33 | Export | 35786580 | 0 | 0
19 | Monipuripara-1 |  |  |  |  | 0 | 6439085.1407 | 10937888.1146 | Monipuripara 33/11 KV SS | 10937888.1146 | Monipuripara SS | 10937888.1146 | 0 | 0%
20 | Monipuripara-2 |  |  |  |  | 0 | 4498802.9739
| Maniknagar 230/132 kv |  |  |  |  | 0 | 18442678.3243
21 | Axuxilary -1 | Maniknagar | 33 | Export | AH14044078 | 0 | 5923.1675 | 11385.495 | Maniknagar 33/11 KV SS | 11209.1299 | Maniknagar 33/11 KV SS | 11209.1299 | 176.3651 | 1.549%
22 | Axuxilary -2 |  | 33 | Export | AH14044072 | 0 | 5462.3275
Shyampur 230/132 kv | [5 empty] | 0 | 11385.495
23 | Aux Tr-1 | Shyampur 230/132 | 0.44kv | Export | DHKG9742 | 0 | 5527.62 |  | Loop Power to Shyampur 132/33 KV & Fatullah 132/33 KV Grid
24 | Aux Tr-2 | Shyampur 230/133 | 0.44kv | Export | DHKG9743 | 0 | 19434
[6 empty] | 0 | 24961.62
TOTAL impport => |  | Wheeling Charge Less (Non-Grid Units at 33 kv ) |  |  |  | 7812738.6 | 113580471.4393 | 105742771.2193 |  | 106734546.2446 |  | 106734546.2446 | -991775.0253 | -0.9379%
NET TOTAL IMPORT 33 KV (Energy export - Energy import) =>
NET TOTAL IMPORT 11 KV (Energy export - Energy import) =>
11&0.4 KV LEVEL
SUBSTATION-FEEDER-METERS INFORMATION | [5 empty] | #REF! | #REF! | Upstream Total | Receiving Circuit/Substation | Downstream Total | Downstream Substation | SS-wise Downstream | Transmission Loss (KWH) | Transmission Loss (%)
Sl No. | NAME OF THE CIRCUIT | Meter Location | Voltage Level (KV) | Meter ID | Meter No. | #REF! | #REF!
1 | 2 | 3 | 4 | 5 | 6 | #REF! | #REF!
KALLYANPUR 33/11 KV S/S (Tel: 01719-634120) | [5 empty] | 0 | 0
| Adabor 11KV O/H | Kallyanpur 33/11KV | 11 | Export | 14957 | 0 | 0
| Monsurabab 11KV O/H |  | 11 | Export | 77816681 | 0 | 0
| Beri Bandh 11KV O/H |  | 11 | Export | 14960 | 0 | 0
| Swerage 11KV O/H |  | 11 | Export | 14959 | 0 | 0
| Ring Road 11KV O/H |  | 11 | Export | 77816675 | 0 | 0
| RMU Feeder |  | 11 | Export | 14997 | 0 | 0
| P.C Culture Housing 11 KV |  | 11 | Export | Dhk-15019 | ` | 0
AGARGAON 33/11 KV S/S (Tel: 8122865) | [5 empty] | 0 | 0
1 | Shyamoli 11KV O/H | Agargaon 33/11KV | 11 | Export | 15026 | 0 | 570400 | 816720 | Sherebanglanagar NOCS | 817950 | Sherebanglanagar NOCS | 817950 | -1230 | -0.1506%
2 | 11 KV R.M.U Feeder |  | 11 | Export | 15027 | 0 | 178000
3a | PD Betar |  | 11 | Import | 2612100427 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 2612100517 | 0 | 0
3b | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
new | SE,NB,Betar |  | 11 | Import | 645015020085 | 0 | 0
3c | NINS & H |  | 11 | Import | Dhk-59122 | 0 | 0
4 | 11 KV Sher-e-banglanagar |  | 11 | Export | 15025 | 0 | 48400
5 | BICC - U/G |  | 11 | Export | 15024 | 0 | 0
6 | NEC |  | 11 | Export | 15023 | 0 | 0
7 | Manikmia Avenue |  | 11 | Export | 76026327 | 0 | 0
| Manikmia Avenue | new | 11 | Export | DHK27341 | 0 | 0
[6 empty] | 0 | 796800
TOTAL => | [5 empty] | 0 | 796800 | 816720 |  | 817950 |  | 817950 | -1230 | -0.1506%
NET TOTAL IMPORT (Energy export - Energy import) =>
11 kV import converted into 33 kV import (Adding 2.5%) => ( BPDB & PGCB)

## DESCO_NEW_FORMAT (hidden)
Monthly Energy Import / Export Statement
0
Helper Cell
Sl. No. | Consumer | Feeder Name | Meter Location | Meter No. | kWh Reading on |  | kVarh Reading on | Add 2.5% (only 0.4 kV Meter unit) E=(A-B)*1.025 | OMF F | Total Energy kWH G=(A-B)*1.025*F (For 11KV Feeder) G=(A-B)*F (For 33 KV Tariff Meters) | Total Reactive KVARH H=(C-D)*1.025*F (For 11KV Feeder) H=(C-D)*F (For 33 KV Tariff Meters) | PF G/SQRT (H*H+G*G) | PFC Units (kWh) Charged by BPDB | Energy Imposed For PFC Surcharge (Considering PF below 0.95) | Shared PFC units (kWh)
[5 empty] | 01-01-23 00:00 AM A | 01-12-22 00:00 AM B | [10 empty] | KVARH for Less thant 0.95 tracking | BPDB PFC Calculation with Range Lookup
01 | Tariff Point | 33/11 kV, 10/14 MVA T-5 (HV) | 33 KV Panel | 8993835 | 116.133 | 86.616 |  | 29.517 | 180000 | 5313060 | 0 | 1 | 0 |  |  |  |  | Lookup Factor | Range | Factor | A | From Kallyanpur S/S. |  |  | Previous | Current
02 |  | 33/11 kV, 20/28 MVA T-4(HV) |  | 8993839 | 8670.191 | 8617.568 |  | 52.623 | 180000 | 9472140 | 0 | 1 | 0 |  |  | T-5 |  | 0 | 0 | 0.165 | 1 | 11 KV Gano Bhavan RMU | 14997 | 1 | 995.68 | 995.74 | 0.06
03 |  | 33/11 kV, 20/28 MVA T-3 (HV) |  | 8993831 | 6518.449 | 6495.578 |  | 22.871 | 180000 | 4116780 | 0 | 1 | 0 |  |  | T-4 |  | 0 | 0.755 | 0.15 | 2 | 11 KV Beribandh Feeder. | 14960 | 1 | 9633.08 | 9646.16 | 13.08
|  | Feeder's Under T-5 | [13 empty] | T-3 |  | 0 | 0.765 | 0.135 | 3 | 11 KV Adabor O/H | 14957 | 1 | 4319.26 | 4419.91 | 100.65
01 | Desco | 11 KV Paikpara oh | 11 KV Panel |  | 3664.1 | 3408.3 |  | 262.195 | 8000 | 2097560 | 0 | 1 |  |  | 0 |  |  |  | 0.775 | 0.12 | 4 | 11 KV Mansurabad | 77816681 | 1 | 51326.05 | 51898.42 | 572.37
02 |  | 11 KV Kallyanpur*** |  | DHK27331 | 5017.044 | 5017.044 |  | 0 | 40000 | 0 | 0 | #DIV/0! | [6 empty] | 0.785 | 0.105 | 5 | 11 KV Ring Road Feeder | 77816675 | 1 | 41632.55 | 41923.11 | 290.56
03 |  | 11 KV Bashir Uddin |  | 74819925 | 581.163 | 394.664 |  | 191.1615 | 16000 | 3058583.6 | 0 | 1 | [6 empty] | 0.795 | 0.09 | 6 | 11 KV Sewarage Pump | 14959 | 1 | 1991.3 | 2112.81 | 121.51
|  | Feeder's Under T-4 | [16 empty] | 0.805 | 0.08 | 7 | 11 KV Technical School (DPDC) | DHK 15019 | 1 | 8076.21 | 8192.03 | 115.82
04 | Desco | 11 KV South Bishil | 11 KV Panel | DHK15017 | 1125.19 | 1125.19 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  | #DIV/0! | 0 |  | #DIV/0! |  | 0.815 | 0.07 | 8 | 11 KV Goidertek (DPDC) | DHK14996 | 1 | 9341.2 | 9369.92 | 28.72
05 |  | 11 KV Lalkuthy |  | DHK15018 | 995.15 | 995.15 |  | 0 | 40000 | 0 | 0 | #DIV/0! |  |  |  |  | #DIV/0! |  | 0.825 | 0.06 | 9
06 |  | 11 KV Baghbari |  | DHK14956 | 9575.06 | 9510.27 |  | 66.4097 | 40000 | 2656390 | 0 | 1 |  |  |  |  | 0 |  | 0.835 | 0.05 | [6 empty] | 0
07 | DPDC | 11 KV Monsurabad (DPDC) |  | 77816681 | 51898.42 | 51616.27 |  | 289.2038 | 8000 | 2313630 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.845 | 0.04 | B | From Agargaon S/S. |  |  |  |  | 0
08 |  | 11 KV Technical School (DPDC) |  | DHK 15019 | 8192.03 | 8133.47 |  | 60.024 | 40000 | 2400960 | 0 | 1 |  |  |  |  | 0 |  | 0.855 | 0.03 | 1 | 11 KV Nearest RMU | DHK-15027 | 1 |  |  | 0
09 |  | 11 KV Swerage (DPDC) |  | 14959 | 2112.81 | 2054.75 |  | 59.5115 | 40000 | 2380460 | 0 | 1 |  |  |  |  | 0 |  | 0.865 | 0.02 |  | 11 KV P.C Culture Housing | DHK-15019 | 1 |  |  | 0
|  | Feeder's Under T-3 | [16 empty] | 0.875 | 0.01 | 2 | 11 KV NEC Feeder. | DHK-15023 | 1 |  |  | 0
10 | Desco | Tolarbag | 11 KV Panel | DHK15016 | 3273.701 | 3273.696 |  | 0.005125 | 40000 | 205 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.885 | 0.005 | 3 | 11 KV Shyamoli O/H | DHK-15026 | 1 |  |  | 0
11 | DPDC | 11 KV Beribadh (DPDC) |  | 14960 | 9646.16 | 9640.43 |  | 5.8732 | 40000 | 234930 | 0 | 1 |  | 0 | 0 |  | 0 |  | 0.9 | 0 | 4 | 11 KV BCFCC Feeder. | DHK-15024 | 1 |  |  | 0
12 |  | 11 KV Goidertek (DPDC) |  | DHK14996 | 9369.92 | 9355.62 |  | 14.6575 | 40000 | 586300 | 0 | 1 |  |  |  |  | 0 |  |  |  | 5 | 11 KV Sher-e-bangla Nagar | DHK-15025 | 1 |  |  | 0
13 |  | 11 KV Adabor O/H (DPDC) |  | 14957 | 4419.91 | 4371.7 |  | 49.4153 | 40000 | 1976610 | 0 | 1 |  |  |  |  | 0 |  |  |  | 6 | 11 KV Manik Mia Feeder. | DHK27341 | 1 |  |  | 0
14 |  | 11 KV Ganabhaban (DPDC) |  | 14997 | 995.74 | 995.71 |  | 0.03075 | 40000 | 1230 | 0 | 1 |  |  |  |  | 0
15 |  | 11 KV Ring Road (DPDC) |  | 77816675 | 41923.11 | 41775.56 |  | 151.2388 | 8000 | 1209910 | 0 | 1 |  |  |  |  | 0
0
|  |  |  | Calculation For Active and Reactive Energy |  |  |  |  | KWH | KVARH
|  |  |  | A | Desco all 11KV Consumpsion (by adding 2.5%) |  |  |  | 7812738.6 | 0
|  |  |  | B | DPDC Total Consumption (T3 + T4 + T5 - B) |  |  |  | 11089241.4 | 0
|  |  |  | PFC Surcharge Unit Distribution |  |  |  |  | PFC Unit
|  |  |  | C | Charged By BPDB |  |  |  | 0
|  |  |  | D | Shared by DESCO |  |  |  | 0
|  |  |  | E | Shared by DPDC |  |  |  | 0
| Representative of DPDC | [10 empty] | Representative of DESCO

## %Loss
|  | 132 KV SS | 33 KV SS
NORTH-1 |  | 6 | 22 | 48
NORTH-2 |  | 3 | 17
SOUTH-1 |  | 5 | 15 | 41
SOUTH-2 |  | 7 | 14
TOTAL |  | 21 | 68 | [133 empty] | MONTHLY OPERATING DATA | [39 empty] | 2017-18 System Loss
|  | DPDC TOTAL SS | 89 | 89 | [171 empty] | IMPORT
|  | NORTH | [173 empty] | MONTH | YEAR | PDB |  | REB | DPDC
[136 empty] | 2012 |  |  |  | 2011 | [11 empty] | 2010 | [10 empty] | 2009 | [14 empty] | Total import | Sales at 132kv & 230kv
| Sl. No. | Name of S/S | Page No. | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2022 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | July--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--18 % of Loss | Febrruary--18 % of Loss | Dceember--17 % of Loss | November--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | JUNE--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November -09 % of Loss | October -09 % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
N-2 | 1 | Moghbazar 132/33 KV S/S | 1 | 0.67566 | -0.072945 | 0.80614 | -0.016693 | -0.11334 | -0.68605 | 0.44939 | 0.0090486 | -0.098821 | 0.32006 | 0.17349 | 0.46874 | 0.18608 | 0.24252 | 0.62751 | 0.77336 | 0.38277 | 0.13504 | 0.11428 | 0.11662 | 0.27907 | 0.38009 | 0.41977 | 0.10386 | -0.18852 | 0.68331 | 0.15592 | -0.01698 | 0.45163 | 0.9 | 0.38121 | 0.18935 | 0.17127 | 0.5498 | 0.84691 | 0.40656 | 0.56725 | 0.57649 | 0.078768 | -0.014092 | 1.3807 | 0.14822 | 0.68941 | 0.39405 | 0.282 | 0.83383 | -0.53849 | 0.032588 | 0.68342 | 0.58299 | 0.6645 | 1.2229 | 0.95241 | 0.036767 | -0.26886 | 0.28591 | 0.26178 | 0.33287 | 0.28226 | 0.1192 | 0.50194 | 0.74851 | 0.82427 | 0.68754 | 0.38765 | 0.17868 | 0.59003 | -0.57813 | -0.17418 | -0.41664 | 0.62283 | -0.78382 | 0.94591 | 0.028016 | -0.23634 | 0.01736 | 0.32663 | -0.11573 | 0.44316 | 0.33351 | 0.088577 | 0.11869 | 0.0085693 | 0.10701 | 0.50314 | 0.11811 | 0.078043 | -0.10562 | 0.15706 | 0.024412 | -0.22888 | -0.041219 | 0.046966 | 0.48021 | 0.49969 | 0.12369 | 0.12166 | -0.14266 | -0.41413 | 0.11967 | 0.20113 | 0.10653 | 0.16962 | 0.53127 | 0.062324 | 0.25006 | 0.13671 | 0.37487 | 0.19717 | 0.18783 | 0.17291 | 0.21198 | 0.21047 | 0.33159 | 0.3125 | 0.30578 | 0.26587 | 0.23553 | 0.40562 | 0 | 0 | 0.29067 | 0.3429 | -0.0060995 | 0.3664 | 0.25233 | 0 | 0.38563 | 0.24309 | 0.39181 | 0.37054 | 0.3575 | 0.31934 | 0.35891 | 0.20515 | 0.20022 | 0.22407 | 0.36061 | -0.034885 | 0.20572 | -0.029574 | -0.049879 | 0.0078695 | 0.50013 | 0.48451 | 0.52467 | 0.25798 | 0.094542 | 0.19348 | 0.2055 | 0.001528 | 0.70549 | 0.19796 | 0.75109 | 0.639 | 0.2823 | 0.27706 | 0.22714 | 0.22884 | -0.51719 | -0.21415 | -0.77828 | -0.80716 | -0.74316 | -0.77094 | -0.90364 | -0.54515 | -0.865 | -0.79461 | -0.79461 | -0.81865
N-2 | 2 | Moghbazar 33/11KV S/S | 2 | 6.4535 | 5.4552 | 2.1623 | 0.89287 | 2.8402 | 1.0635 | 3.327 | 2.8019 | 2.1044 | 3.0451 | 5.0167 | 6.9336 | 8.6062 | 4.9672 | 5.4038 | 6.0411 | 6.5726 | 7.0084 | 7.188 | 6.7054 | 2.3158 | 2.2163 | 1.8934 | 1.4851 | 1.4146 | 1.0047 | 2.753 | 3.5272 | 1.4644 | 9.65 | 3.3 | 3.9916 | 3.8595 | 4.4325 | 1.4342 | 3.9878 | 3.9695 | 2.3468 | 3.3773 | 2.5582 | 3.7011 | 1.6137 | 2.2891 | 3.1418 | 2.5012 | 3.27 | 3.0822 | 3.5073 | 2.753 | 1.1187 | 3.056 | 1.7858 | 1.3354 | 3.3266 | 3.0494 | -0.48094 | 0.40802 | 0.98643 | 1.1879 | 0.97548 | 1.2206 | 1.1959 | 1.2493 | 1.4703 | 0.66865 | -0.88744 | -0.11632 | 1.1065 | 1.8674 | 1.4098 | 0.58908 | 0.49851 | 3.6278 | 1.8513 | -0.58552 | -1.2854 | 3.2533 | -4.1309 | -0.68164 | 1.4154 | -0.41116 | 2.9049 | -3.1076 | 1.2889 | 1.5448 | 1.0329 | -1.6732 | -3.3346 | -2.4791 | -3.0577 | -2.1485 | 0.89358 | -0.66361 | 0.56376 | 0.99141 | 2.2562 | 1.8985 | 1.1026 | -0.37746 | 1.1613 | 4.8068 | 3.6262 | 3.301 | 3.1035 | 2.8241 | 2.1703 | 1.093 | 3.1177 | 3.1154 | 3.2932 | 3.8815 | 4.4536 | 4.6874 | 3.9426 | 3.7704 | 3.1106 | 0.6343 | 3.6762 | 4.8582 | 1.1482 | 2.656 | 3.746 | 4.3125 | 4.0906 | 4.1233 | 3.6031 | 1.221 | 5.6031 | 3.6518 | 3.9268 | 3.618 | 3.4433 | 3.8624 | 3.8203 | 3.6272 | 2.9373 | 2.1693 | 3.5785 | 2.7958 | 2.5971 | 3.1008 | 3.0818 | 3.0764 | 2.1686 | 2.3906 | 0.52261 | 0.32395 | 0.32972 | 0.20687 | 0.51539 | 1.4416 | 0.60991 | 1.4846 | 0.7506 | 0.89425 | 1.2247 | 1.2801 | 0.73966 | 0.90339 | 0.1367 | 2.4947 | 2.4624 | 3.0346 | 3.1053 | 2.4013 | 2.4869 | 2.1795 | 4.0733 | 4.0381 | 4.0381 | 4.0364
N-2 | 3 | Green Road 33/11KV S/S | 3 | 0.39606 | 0.33416 | 1.8105 | 0.55664 | 2.3081 | 0.78898 | 0.72466 | 0.38126 | 0.88071 | 0.31403 | 0.30779 | 0.58957 | 1.1978 | 1.3045 | 0.81204 | -0.13952 | 1.15 | -0.56283 | 0.66299 | 0.94172 | 0.5 | -0.04958 | 1.3754 | 0.44068 | 0.48633 | 0.34521 | 1.901 | 0.62127 | 2.2343 | 2.84 | 0.17695 | 1.5043 | 0.37486 | 0.69743 | 1.5014 | 1.5217 | 1.9456 | 0.48806 | -0.013721 | 1.5 | 1.5 | 1.4685 | 1.2383 | 0.57425 | 3.6304 | 2.2854 | -1.3892 | 1.6907 | -0.58227 | 2.2717 | 2.6148 | 1.7856 | 0.24241 | -0.86972 | -0.6132 | 1.6838 | 1.6114 | 0.91246 | 1.0142 | 0.87939 | 0.92484 | 1.6556 | -1.5995 | 0.47945 | -2.2202 | 0.52889 | 0.083714 | -0.30137 | 0.97078 | -1.0098 | 0.43272 | 0.31806 | 0.10799 | -0.1548 | -0.30332 | 1.1365 | 1.2804 | 1.1213 | 0.27973 | 0.20493 | 0.071542 | 0.087201 | 0.027532 | 0.080469 | 0.62398 | 0.48008 | 0.23279 | -0.14844 | 0.24495 | -2.3791 | 1.7001 | 0.42816 | -0.061577 | 0.75186 | 1.3356 | 0.26929 | 0.40202 | 0.49219 | -0.44325 | 1.3542 | 0.60665 | 0.88874 | -0.26395 | 1.2353 | 0.16735 | 1.5746 | 0.92361 | 0.63782 | -0.21673 | 0.82208 | 0.30394 | 1.7569 | 0.38276 | -0.085158 | 0.82582 | 0.26765 | 0.23495 | 0.21989 | 1.4493 | -0.31294 | 0.13855 | 0.021842 | 0.97962 | -0.77471 | 0.88869 | 0.52915 | 0.11722 | 0.98602 | 0.35916 | -0.13906 | 0.61385 | 0.35331 | 2.2397 | -1.3875 | 0.29486 | -0.095698 | 0.22423 | -0.45846 | 0.85268 | 0.58581 | 0.65427 | -0.39237 | 0.31987 | 70.2689 | 51.2555 | 0.54453 | 0.27862 | 0.025316 | 0.41436 | 0.39471 | 0.10914 | 0.85285 | 0.33171 | 0.95626 | 1.0543 | 0.56166 | 0.38096 | 1.4328 | 1.836 | 0.5408 | 0.10605 | 0.31177 | 0.83204 | 1.0529 | -0.66068 | 2.642 | 1.2287 | 0.038634 | 1.9154 | 1.9154 | 6.4994
N-2 | 4 | Lalmatia 33/11KV S/S | 4 | 1.0252 | 0.43418 | 0.068319 | 0.66068 | 0.82552 | 1.369 | -0.23631 | 1.0006 | 1 | 0.98457 | 0.98946 | 1 | 1 | 0.65605 | 0.59745 | 0.96833 | 1 | 1 | 1 | 0.8909 | 1 | 1 | 0.56816 | 0.46249 | 0.5 | 0.45479 | 0.48459 | 0.42692 | 0.54396 | 0.54 | 0.54396 | 0.99805 | 0.97246 | 0.90145 | 0.78661 | 0.68166 | 1 | 0.98112 | 1 | 1 | 0.80754 | 0.67045 | 0.57849 | 1 | 0.62431 | 0.73409 | 0.41754 | 0.071158 | 0.62665 | 0.70006 | 0.70006 | 0.68817 | 0.57476 | -0.29648 | -0.0055488 | 0.27174 | 0.86049 | 0.25938 | 0.63179 | 0.22319 | 0.59047 | 2.122 | 0.6246 | -0.81786 | 0.8789 | 0.20115 | -0.28177 | 1.021 | 0.20909 | -0.819 | 0.58381 | 1.3263 | 2.0728 | 1.7817 | 1.7534 | 2.8288 | 0.92698 | 0.02 | 1.545 | 2.1721 | 1.8145 | -0.011016 | -0.39376 | -0.12421 | -0.16301 | 1.2202 | 1.3969 | 0.94209 | 1.4442 | 1.7807 | 1.188 | 1.5878 | 1.1973 | 5.5255 | 1.6113 | 1.3991 | 1.3647 | 1.3664 | 2.2906 | 1.1874 | 1.3936 | 1.226 | 0.46198 | 2.375 | 1.1314 | 1.4247 | 1.4473 | 1.7233 | 1.574 | 3.0444 | 1.5197 | 1.4619 | 1.2994 | 1.6429 | 2.0628 | 1.4463 | 2.2323 | 1.027 | 3.6744 | 4.7612 | -0.75512 | -0.66979 | 0.67552 | 0.81715 | 1.7021 | 4.4681 | 0.043678 | 2.3197 | 2.0528 | 1.6981 | 1.3105 | 1.2925 | 1.5128 | 2.3961 | 4.6622 | 1.7256 | 1.4228 | 2.8494 | 1.2106 | 1.7398 | 1.6842 | 1.6448 | 1.6756 | 2.0927 | 1.9567 | 1.7051 | 1.4598 | 1.3846 | 1.5538 | 1.8377 | 2.2501 | 2.1745 | 1.9368 | 2.2143 | 2.2046 | 1.9365 | 2.2428 | 2.0629 | 1.7823 | 1.022 | -1.4434 | 4.0142 | 1.3069 | 1.3435 | 1.4744 | 1.2936 | 1.3121 | 1.1549 | 1.0605 | 1.0605 | -0.29099
N-2 | 5 | Tejgoan 33/11KV S/S | 5 | 1.1843 | 0.90377 | 2.2435 | 1.9093 | 2.7137 | 1.0549 | 2.371 | 1.0295 | 1.4647 | 1.4324 | -0.38145 | -0.3377 | 0.41758 | 1.3938 | 1.5814 | 1.8669 | 6.6301 | 1.8992 | 1.2045 | 0.47334 | 1.7117 | -0.098877 | 0.32212 | 3.1106 | 2.7232 | 3.4192 | 2.1095 | 3.7702 | 0.73871 | 0.54 | 1.1238 | 0.83113 | 0.41569 | 0.2831 | -1.3891 | 0.54936 | -0.72767 | 1.8124 | 0.52493 | 0.62945 | 2.2864 | 1.1222 | 1.8909 | 2.708 | -0.45466 | 0.58819 | 3.3894 | -0.79996 | 0.24756 | 1.3522 | 1.3174 | 1.4686 | 1.3242 | 0.78131 | 0.16009 | 0.70882 | 0.54086 | -1.1857 | 2.3114 | 0.037421 | 0.62076 | 0.38118 | 0.20064 | 0.078134 | 2.948 | 2.6807 | 2.7499 | 1.3162 | 2.0063 | 1.891 | 4.2293 | 2.7508 | 2.0262 | 0.90087 | 0.16774 | 0.32786 | 0.59031 | 0.39975 | 1.2697 | 0.50548 | 3.7818 | 0.5 | 0.38227 | -0.26559 | 1.3136 | 0.52201 | 5.179 | 1.729 | 0.49828 | 1.9205 | 1.3551 | 1.5226 | 2.9727 | 1.1358 | 2.5109 | -7.356 | 1.4726 | 4.1145 | -0.55895 | 2.7544 | 2.9005 | 0.35045 | 0.40234 | -0.6031 | 0.25035 | 0.69743 | -0.58488 | 0.8673 | 0.96864 | 0.12274 | 0.95349 | 1.9139 | 1.4657 | 1.3604 | 1.7173 | 0.52846 | 1.2016 | 0.95088 | 0.46161 | 1.5091 | 0.7672 | 1.094 | 1.0043 | -0.013965 | 0.47994 | 0.9006 | 0.21994 | 2.1881 | 1.4819 | 0.54697 | 0.75199 | -1.98 | 0.83281 | -0.46847 | 2.6687 | 1.0593 | 1.1062 | 1.2916 | 0.84155 | 1.2821 | 0.76268 | 1.1387 | 0.43899 | 1.6291 | 1.6818 | 1.5497 | 5.7376 | 2.5248 | 38.4996 | 37.5877 | 38.7807 | 36.8482 | 33.8855 | 36.7653 | 36.6318 | 17.2569 | 25.8476 | 25.547 | 24.2727 | 23.5253 | 22.7184 | 22.3415 | 22.5447 | 23.8396 | 22.212 | 19.0969 | 24.4209 | 20.4135 | 6.8099 | 6.8099 | -11.9939 | OMFis not correct
N-2 | 6 | Moghbazar T&T 33/11 KV, | 6 | -0.1882 | 0.02402 | -0.2612 | 0.49202 | -0.52421 | 0.54581 | 0.18626 | -0.2016 | 0.64563 | -0.63069 | 0.020124 | 2.4392 | -0.36433 | -0.25695 | 0.0035155 | -0.40812 | -0.073263 | -0.055375 | -0.11549 | -0.51853 | 0.026454 | -0.09914 | -0.034258 | -0.012683 | -0.23981 | -0.57747 | -0.63644 | -0.67239 | -0.6133 | -0.41 | -1.4935 | -0.55369 | 0.94228 | -0.0068488 | -1.1228 | 1.3167 | -0.14265 | -1.0038 | 0.93812 | -0.9649 | 0.9439 | -0.91388 | 0.80059 | -0.065223 | -0.194 | 0.15 | -0.59722 | -0.42384 | -0.85531 | 0.2 | 0.19688 | 1.5331 | -1.2076 | -0.22899 | 2.5862 | 0.2 | -0.21885 | -0.70249 | 0.22678 | 0.057762 | 1.4455 | 0.11659 | 0.09912 | 0.045497 | -0.29619 | 1.1674 | 0.89264 | -1.3688 | -0.81087 | -0.73216 | -0.20236 | 0.64176 | -1.4016 | -0.66042 | -0.74634 | -0.3985 | -0.48161 | -0.75577 | 1.2057 | -1.2093 | -2.529 | 1.0942 | -0.74485 | 2.2797 | -2.8664 | -0.20079 | -0.95061 | -0.60024 | -0.44254 | -0.51512 | -0.92471 | -0.53619 | -0.81374 | 0.061073 | 0.11059 | -0.61291 | 0.005348 | -1.2671 | -1.0537 | -0.40396 | -0.29511 | -0.37757 | -0.35513 | 0.40635 | -0.92032 | 4.8869 | -0.60863 | 0.66614 | -0.27214 | -0.26356 | -0.27425 | -0.70236 | -0.33709 | 0.61875 | -0.95863 | -0.4337 | -0.36921 | -0.54309
N-1 | 7 | Dhanmondi 132/33 KV S/S | 7 | 0.057185 | 0.031059 | 0.068751 | 0.060234 | 0.038674 | 0.072888 | 0.37919 | 0.22358 | 0.35663 | 0.11439 | 0.11266 | 0.12982 | 0.28898 | 0.37706 | 0.14841 | 0.15132 | 0.72034 | 0.091229 | 0.09162 | 0.13702 | 0.31165 | 0.36071 | 0.12915 | 0.27614 | 0.63818 | 0.40097 | 0.73007 | 2.7582 | -1 | 1.19 | 0.49426 | 0.3184 | 0.43253 | 0.47505 | 0.61564 | -0.079364 | -0.059525 | 0.75112 | 0.64268 | 0.67004 | 0.58716 | 0.69526 | 0.042351 | 0.33173 | 0.21459 | 0.16995 | 0.5 | 0.061949 | 0.040369 | 0.065101 | 0.03326 | 0.052399 | 0.4145 | -0.33626 | -0.094548 | 0.1859 | 0.24094 | 0.3909 | 0.20746 | 0.49203 | 0.059495 | -1.9476 | 0.50125 | 0.03026 | 0.18658 | 0.70127 | 0.11191 | -0.075729 | 0.011908 | 0.034029 | 0.13621 | -0.22199 | 0.8352 | 0.2825 | 0.57255 | 0.48502 | 0.32782 | 0.007265 | 0 | 0.2 | 0.49635 | -0.26903 | 0.025794 | -0.41738 | 0.054327 | 0.1819 | 0.05323 | 0 | 0 | 0.38145 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95184 | 2.5017 | -0.9195 | 0.31301 | 0.63714 | 0.56428 | 0 | 0 | -1.2156e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10233 | 0 | -1.2288e-14 | 1.455e-14 | 0 | -0.76205 | -0.059041 | 0.19345 | -0.0091278 | -0.32428 | -0.28668 | -0.67265 | 0.61437 | -0.3031 | 0.45194 | -0.11408 | 0.21374 | -0.57978 | -0.30939 | 0.59967 | 0.22555 | -0.55132 | -1.8503 | 0.59817 | -0.15146 | -0.17165 | -0.17616 | -0.26092 | -0.33654 | -0.38749 | -0.67994 | -0.13428 | -0.79062 | -0.3683 | -0.39809 | -0.091222 | -0.2342 | -0.43599 | -0.40573 | -0.48482 | -0.52386 | -0.35838 | -0.095441 | -0.25679 | -0.15021 | -0.15278 | -0.25203 | -0.18327 |  | 0 | 0 | 0 | 0 | 0.97411 | 0.97411 | 0.12685
N-1 | 8 | Dhanmondi 33/11 KV S/S | 8 | 0.46983 | 0.36165 | 0.43195 | 0.26908 | 0.20899 | 0.36343 | 0.72101 | 0.51489 | 0.38527 | 0.44409 | 0.31175 | 0.46479 | 0.41885 | 0.63711 | 0.71682 | 1.6615 | -0.26105 | 0.057382 | 0.097946 | 0.38832 | 0.42277 | 0.54347 | 0.23439 | 0.35101 | 0.77656 | 0.57507 | 0.87717 | 0.38758 | 1.4123 | 0.98 | 0.92902 | 0.31483 | 0.90434 | 0.66139 | 0.80201 | -0.04778 | 0.091552 | 1.0059 | 0.87948 | 0.67565 | -0.06161 | 2.1395 | 0.24856 | 0.94247 | 3.3926 | 0.85 | 0.57659 | 0.75 | 0.75 | 0.3 | 0.23263 | -0.010336 | 1.6939 | 0.084261 | 0.17085 | 0.4983 | 0.51519 | 0.025885 | 0.98072 | 0.73562 | 4.2067 | 1.5145 | 0.24834 | 0.1661 | 0.76438 | 0.93688 | 0.2881 | 0.10438 | -1.8616 | -0.22774 | 1.5292 | 0.91474 | 2.3155 | 1.639 | 0.54706 | 2.487 | 0.57893 | 0.69099 | -0.67647 | -0.38029 | 0.57219 | 0.5649 | -0.33063 | 4.774 | -1.6687 | 0 | 0.16286 | -0.32776 | 0.30342 | 1.629 | 1.4175 | 1.5815 | 1.7706 | 1.5896 | 0.25 | 1.1987 | 1.553 | 3.3447 | -0.88973 | 0.51603 | 0.93758 | 1.0014 | -0.66352 | -3.2028 | -2.6936 | 1.1758 | -0.26249 | 0.42732 | 0.33145 | 0.37718 | 0.34358 | 3.9508 | 0.2728 | 0.39539 | 0.60447 | 0.21774 | 0.74538 | 0.11895 | 0.27141 | 0.28488 | 0.027186 | 1.2007 | 0.8101 | 0.39231 | 0.23547 | 0.25821 | -0.34952 | -0.98351 | -0.31803 | 0.98438 | 0.17297 | 0.7671 | -0.23361 | -0.006106 | 0.5224 | 0.64785 | -0.1549 | -0.71305 | 0.81668 | 0.45808 | 0.17382 | 0.92283 | 0.073605 | 0.16729 | 0.27936 | 1.4777 | 0.51794 | 0.66671 | 1.6177 | 2.113 | 2.6943 | 1.7865 | 1.9814 | 2.3263 | 1.9322 | 2.0867 | 2.2253 | 2.5182 | 1.6263 | 1.9845 | 2.4023 | 2.1792 | 1.9583 | 2.55 | 2.5506 | 2.5671 | 2.705 | 1.8485 | 0.7985 | 0.7985 | 2.0177
N-1 | 9 | Kawranbazar 33/11KV S/S | 9 | 0.49247 | 0.69515 | -0.31753 | 0.40463 | -0.24648 | 2.0715 | 2.2654 | 0.73704 | 0.80286 | 0.52059 | 0.97365 | 1.4463 | 0.44377 | 0.98201 | 0.95606 | 0.75287 | 0.30446 | 0.67166 | 0.83746 | 1.2836 | 2.1038 | 1.4218 | 0.27409 | 1.2667 | 0.2109 | 1.5741 | 2.468 | 0.94651 | 0.39176 | 1.62 | 1.8289 | 0.27672 | 1.8561 | 0.89663 | 2.3429 | 0.83399 | 1.0579 | 1.0124 | 2.1065 | 2.2748 | 1.8313 | 1.9138 | 1.6569 | 2.4962 | 1.3219 | 0.63116 | 3.4334 | 2.4119 | 2.8633 | 3.5398 | 2.4231 | 4.7743 | 2.7178 | 1.7781 | 0.51123 | 2.0306 | 1.0536 | 0.98483 | 0.30532 | 0.2172 | 2.3127 | 1.3691 | 1.9547 | 1.5022 | 0.72814 | 2.8229 | 2.1674 | 2.3779 | 1.4086 | 2.7565 | 1.7174 | 1.7394 | 2.3657 | 2.2383 | 7.4135 | 1.0489 | -0.05619 | 1.4 | 2.7388 | 2.7086 | 2.2789 | 2.3899 | 0.65729 | 2.5051 | 2.2407 | 2 | -0.11035 | 0.21479 | 3.7393 | 4.0107 | 2.6827 | 3.5737 | 0.29734 | 4.9188 | 0.5 | 2.8484 | 4.2068 | 3.8187 | 1.4431 | 4.641 | 0 | 4.5919 | 0.88126 | 1.431 | 2.2908 | 2.2578 | 2.7884 | 2.8911 | 4.2526 | 1.7916 | 3.053 | 3.6916 | 4.8276 | 3.8849 | 3.2978 | 5.0728 | 4.9488 | 2.6858 | 3.2281 | 2.9604 | 3.7026 | 3.3633 | 4.2898 | 4.2127 | 2.8563 | 4.0142 | 3.0514 | 6.3697 | 1.6222 | 6.7213 | 0.90294 | 4.9776 | 3.561 | 3.2966 | 4.7188 | 4.0849 | 4.4679 | 5.8193 | 3.3965 | 4.8708 | 4.4454 | 4.3482 | 3.5601 | 4.9497 | 5.1475 | 0.34022 | 4.4027 | 4.067 | 4.1958 | 3.436 | 3.2678 | 2.1465 | 3.445 | 2.4177 | 2.9231 | 2.408 | 3.6441 | 4.2426 | 4.176 | 4.7111 | 3.3801 | 7.4508 | 5.3142 | 5.538 | 6.2975 | 4.7136 | 5.4724 | 5.7636 | 6.056 | 6.056 | 5.6999
N-1 | 10 | New Ramna 33/11KV S/S | 10 | 1.773 | 2.8644 | 2.0966 | 0.76637 | 2.0957 | 1.0807 | 1.2244 | 2.7013 | -0.60019 | 1.4777 | 2.2806 | 1.5831 | 0.31351 | 1.8827 | 2.0494 | 0.91572 | 0.8 | 0.8 | 1.4595 | 0.64383 | 2.1404 | -0.23129 | 0.17043 | -0.11538 | -0.74647 | 0.591 | 0.57038 | 1.8648 | 2.0845 | 3.03 | 0.29232 | 2.1682 | 0.082019 | 1.6609 | 1.9254 | 1.3429 | 1.9069 | 2.1567 | 1.4756 | 0.35198 | 1.3233 | 2.3159 | 1.5701 | 0.91341 | -0.24401 | 0.49427 | 1.6494 | 1.2907 | 1.262 | 0.1858 | 1.6824 | 0.68285 | 2.9669 | 2.4871 | 1.7713 | 0.72247 | 0.21199 | 0.076573 | 1.6073 | 0.29379 | 1.1974 | -0.36506 | 1.1188 | 1.5119 | 0.43363 | -0.53343 | -0.83376 | -2.4417 | 3.1084 | 2.1974 | 1.6198 | 0.99505 | 3.5903 | 1.5873 | 2.5697 | 0.95322 | -0.36684 | -0.60772 | 0.34376 | 0.70634 | 1.8341 | 1.6531 | -0.7002 | -0.3578 | 0.57261 | 1.7831 | 1.4351 | 1.2298 | 0.71376 | -0.99106 | 0.69417 | 0.70982 | 0.39649 | 0.55711 | 2.0996 | 2.5078 | 1.4867 | 2.3179 | 0.40786 | 0.36563 | -0.16857 | 1.4793 | 0.84924 | 1.1327 | 1.701 | 1.707 | 0.59372 | 1.6131 | 0.73515 | 0.68553 | -0.92433 | 0.052204 | 1.5264 | 0.21948 | 0.0025323 | 2.4322 | 0.52979 | 1.1431 | 1.947 | 0.9516 | 1.9611 | 1.5916 | 2.0054 | 0.89225 | 0.66175 | 0.89807 | 0.42304 | 2.2357 | 1.887 | 2.9946 | 1.8561 | 1.9784 | 2.4458 | -0.083061 | 1.8002 | 1.8348 | 0.86369 | 1.9143 | 0.24382 | 0.77915 | 0.29413 | 1.0631 | 0.44294 | 3.3443 | 3.0417 | 3.9723 | 3.194 | 2.9681 | 3.3133 | 2.5616 | 3.5478 | 3.0598 | 3.1767 | 2.6358 | 3.7211 | 3.156 | 3.056 | 1.8415 | 3.9523 | 3.9736 | 3.0104 | 2.5834 | 3.0895 | -0.40863 | 3.1332 | 1.0657 | 2.8266 | 2.5866 | 4.2826 | 4.2826 | 4.9529
N-2 | 11 | Ullon 132/33/11KV S/S | 11 | 0.2563 | 0.59112 | 1.6004 | -1.0714 | 0.6677 | -0.53272 | 0.39631 | 0.28458 | 0.62489 | 0.15475 | 0.86813 | 0.28867 | 0.09913 | 0.66885 | 0.18572 | 0.089871 | 0.13343 | -0.32963 | 0.022884 | 0.19334 | 0.84847 | 0.89735 | 0.13204 | 0.29349 | 0.89951 | -0.12905 | 0.010454 | 1.7165 | 0.4 | 0.5 | 2.1447 | -0.1315 | -0.25159 | 0.77702 | 0.59268 | 1.2011 | 1.4069 | -0.058468 | 0.59686 | -0.55639 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 0.60555 | 0.82489 | 0.5 | 0.48388 | 0.84448 | 1.5811 | 0.67298 | 0.79926 | 0.064624 | 0.9095 | 0.064714 | 0.15332 | 0.94859 | 0.26406 | 0.58486 | 0.5934 | 0.54485 | 0.8855 | 0.50774 | 0.95222 | 0.62386 | 0.60114 | 0.5385 | 0.46305 | 0.38989 | 0.39452 | 0.91699 | 0.80914 | 1.2855 | 0.063509 | 0.1 | 0.20487 | 0.043332 | 0.043037 | 0.042398 | 0.043271 | 0.043099 | 0.042337 | 0.043045 | 0.0433 | 0.042716 | 0.043134 | 0.043223 | 0.04275 | 0.042312 | 0.04267 | 0.043499 | 0.043939 | 0.043262 | 0.043027 | 0.042979 | 0.044014 | 0.043628 | 0.043569 | 0.043814 | 0.043723 | 0.043157 | 0.042778 | 0.042563 | 0.042389 | 0.04224 | 0.04182 | 0.041089 | 0.043581 | 0.043176 | 0.04323 | 0.043586 | 0.043011 | 0.042794 | 0.040124 | 0.042154 | 0.042327 | 0.042068 | 0.043398 | 0.043233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8969e-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5435 | -1.5435 | 0
N-2 | 12 | Ullon local 33/11KV S/S | 12 | 0.40829 | 1.7875 | 0.53771 | 0.81154 | 1.9539 | 0.74087 | 1.0891 | 0.8443 | 0.92998 | 0.79855 | 1.6333 | 0.32826 | 2.3298 | 0.2119 | 1.4668 | 1.5869 | 2.7194 | 1.9535 | 2.2847 | 1.3249 | 0.92585 | 2.2856 | 2.0752 | 1.085 | 2.025 | 1.6279 | 1.2745 | 4.9457 | 2.6338 | -1.1 | 1.8988 | -0.85001 | 1.1483 | 0.33643 | 0.31177 | 0.99465 | 0.18778 | -0.33235 | 0.65581 | 0 | 3.8867 | 1.1239 | 1.2522 | 2.0695 | -0.77185 | 3.6672 | 3.5019 | 2.6253 | 2.8866 | 2.5936 | 0.65685 | 1.2401 | -0.43088 | 1.1486 | -2.2253 | -0.56771 | 0.89502 | -0.22538 | 0.1807 | 0.2016 | -0.075366 | 0.80723 | 1.8605 | -0.56738 | 0.80889 | 0.098424 | -2.3262 | 2.7559 | 1.3308 | -1.6723 | 1.7689 | 0.29019 | 0.8953 | 0.9224 | 1.1738 | 0.12257 | -0.27765 | -0.18523 | -0.17326 | 1.2925 | 0.79611 | -0.20263 | 0.63799 | 1.7867 | 0.80805 | 0.9833 | -0.3014 | -0.056481 | -0.326 | 7.5985 | -6.8628 | 3.9379 | 1.7225 | -0.057636 | 0.2059 | -0.20158 | -0.69015 | -0.12816 | 0.49072 | 1.2186 | 2.018 | 0.40671 | -0.26586 | -1.0033 | 0.56725 | 0.8562 | 3.5611 | 0.66243 | 0.37487 | 1.0495 | -0.1624 | -0.2265 | -0.034658 | -0.20752 | 0.21899 | 0.28332 | -0.18212 | -0.21939 | 0.30839 | -0.64231 | 1.3216 | -0.47411 | 0.14517 | 0.22975 | 0.32701 | 0.15625 | 0.72886 | 0.27117 | -0.11094 | 0.062711 | 0.10789 | 0.62429 | -0.0005053 | 0.13224 | -0.15114 | 0.32521 | 0.043503 | -0.2042 | -0.26145 | -0.20962 | -0.20418 | -0.23604 | -0.24189 | -0.22277 | -0.23783 | -0.2162 | -0.24819 | -0.23053 | -0.25445 | -0.28477 | -0.22961 | -0.2034 | 0.093017 | -0.13259 | -0.13757 | 0.8199 | 3.552e-14 | 1.001 | 0.51391 | 0.33659 | -3.4443 | -0.88939 | -1.9543 | 0.43919 | 0.50925 | 0.31553 | 0.6299 | 4.8454 | -1.4366 | -1.4366 | 0.34407
N-1 | 13 | Kakrail 33/11KV S/S | 13 | 1 | 1.8285 | 1.0363 | 0.14403 | 0.90571 | 0.1475 | 2.882 | 2.7143 | 2.2239 | 1.5819 | 1.4313 | 1.2362 | 1.3452 | 2.6623 | 1.4288 | 1.4071 | 1.441 | 1.3372 | 1.5483 | 1.9419 | 1.4584 | 1.9314 | 1.6196 | 3.6426 | 1.5638 | 2.7196 | 2.5908 | 0.72258 | 0.76103 | 0.67 | 0.33992 | 0.34888 | -1.245 | 1.2643 | 0.7948 | 0.27343 | 0.55603 | 0.99655 | 1.7361 | 1.6783 | 1.6783 | 0.89333 | 0.73597 | 2.0547 | 0.62302 | 0.9236 | 1.7508 | 2.9004 | 1.6945 | 1.0176 | 2.4298 | -0.023491 | 0.93378 | 1.2701 | 0.29498 | 0.71003 | 0.23196 | 2.3337 | 0.57685 | 0.33883 | 1.8168 | 1.8196 | 1.343 | 4.6874 | -0.036188 | 1.0838 | -0.39539 | -0.036043 | -0.92336 | 1.9132 | -0.48694 | 1.1892 | 4.2628 | 0.024078 | 0.17923 | 0.01 | 0.7956 | 0.05 | 1.0447 | -0.87303 | 0.021945 | 0.1 | 0.99836 | 0.041978 | -0.59199 | 1.4389 | 0.51629 | 0.22471 | 0.51132 | -1.1811 | 1.8444 | 1.7955 | 2.6787 | 0.2024 | 0.090566 | 1.6786 | 2.0573 | 1.7036 | 1.7866 | -0.01032 | -0.077112 | 0.44339 | -1.283 | 2.1 | 2.1 | 2.5 | 2.5 | 2.159 | 1.0172 | 0 | 1.3919 | -0.043257 | -0.83898 | 0.11732 | 0.21438 | 1.2611 | 0.94831 | 1.3414 | 0.77 | -0.71287 | 0.14697 | 0.42341 | 1.5437 | 2.2742 | 0.33858 | 1.328 | 1.3984 | 1.8825 | 1.7481 | 0.26068 | 2.028 | 2.2641 | 2.5538 | 2.1184 | 2.4037 | 1.941 | 2.0301 | 1.2857 | 2.2262 | 0.46567 | 1.1082 | 2.27 | 1.3922 | 1.6684 | 2.9097 | 0.76342 | 2.5591 | 1.7253 | 2.8367 | 3.6113 | 1.3669 | 1.5506 | 1.4968 | 1.8574 | 1.1243 | 0.90056 | 1.5605 | 1.1991 | 1.7757 | 1.0225 | 1.4573 | 1.3546 | 0.27966 | 1.386 | 4.5793 | 6.6344 | 5.2321 | 5.2133 | 4.2515 | 4.2515 | -7.463
N-2 | 14 | Khillgaon 33/11KV S/S | 14 | 2.8737 | 1.7001 | 0.55595 | 1.2756 | 1.6314 | 2.0367 | 0.77768 | 2.2183 | 0.89482 | 0.96439 | 2.8059 | 0.24757 | 0.15858 | 1.6725 | 0.41548 | 0.45761 | 0.505 | 1.1472 | 2.0343 | 2.7839 | 0.38261 | 2.3047 | 2.072 | 1.3192 | 1.8338 | 1.22 | 2.2863 | 1.4425 | 1.1137 | 1.23 | 0.99501 | 2.6798 | 1.7506 | 2.332 | 2.4148 | 2.561 | 2.8395 | 2.5339 | 2.1802 | 1.1173 | 1.2774 | 1.5713 | 0.79875 | 2.0882 | 1.7911 | 3.4394 | 2.6742 | 3.377 | 2.8625 | 3.5608 | 2.1511 | 2.2911 | 2.9767 | 2.6111 | 1.6554 | 1.6554 | 3.5094 | 1.6236 | 2.5875 | 2.0506 | 1.0341 | 1.4096 | 2.4735 | 1.3173 | 1.641 | -2.0071 | 2.0268 | 2.95 | 1.9092 | 1.5615 | 1.6465 | 1.8256 | 2.9945 | -0.00075825 | 3.7311 | 3.4587 | 3.4183 | 0 | 0.27239 | 4.9343 | -0.25275 | 3.0357 | 1.709 | 2.1336 | 2.4635 | 0.1 | 2.065 | 2.3799 | 1.9581 | 3.3086 | 2.7363 | 2.1015 | 2.4442 | 1.9628 | 2.8752 | 1.2907 | 2.1881 | 1.6273 | 1.3389 | 2.2551 | 0 | 1.9213 | -0.56933 | 4.0563 | 2.921 | 0.55371 | 4.8394 | 1.4559 | 1.1728 | 2.5241 | 2.7172 | 2.1781 | 1.8816 | 2.102 | 1.5382 | 2.2251 | 1.8428 | 0.38019 | 2.8275 | 0.67235 | 0.59817 | 0.71647 | 1.443 | 0.62974 | 0.92521 | 0.23409 | -0.099228 | 1.7006 | 1.7151 | 1.6877 | 1.6325 | 1.8738 | 0.93416 | 0.014029 | 1.3412 | 1.1148 | 1.5191 | 1.54 | 2.0333 | 2.1732 | 2.1283 | 1.899 | 1.9011 | 1.6621 | 1.8017 | 1.1594 | 1.3269 | 0.96381 | 7.7461 | 2.1767 | 3.0631 | 1.8798 | 1.8943 | 1.8488 | 1.9333 | 1.8566 | 1.4768 | 1.9044 | 2.0193 | 1.5929 | 1.6008 | 1.5627 | 2.3037 | 1.9518 | 3.67 | -0.55871 | 1.8449 | 8.9729 | 2.3705 | 2.3705 | 1.7442
N-2 | 15 | Goran 33/11KV S/S | 15 | 0.14731 | 0.90044 | 0.807 | 0.23214 | 0.036098 | 0.53434 | -0.94124 | 0.65481 | -0.13897 | 0.57847 | 0.27366 | 0.52113 | 0.41725 | 0.44062 | 0.45208 | 0.037539 | 0.91596 | 0.12047 | 1.1188 | 0.76904 | 0.51084 | -0.031986 | 0.31217 | 0.53067 | 0.50683 | 0.2742 | 0.28678 | 1.1073 | 0.48603 | 0.23 | 0.42951 | 0.46226 | 0.31801 | 0.40585 | 0.39742 | 0.42297 | 0.25989 | 0.22362 | -0.39307 | -0.63598 | 0.060456 | -0.52785 | -0.61808 | 0.055871 | 3.4431 | 1.9839 | 2.343 | 2.4133 | 1.5037 | 3.0361 | 0 | 3.1704 | 4.6316 | 2.7831 | 4.0086 | 1.8289 | 2.3913 | 0.19032 | 0.51274 | 0.58186 | 1.3065 | 1.3486 | 0.29945 | 1.5432 | 1.1198 | 0.8347 | 0.79858 | 0.80446 | -0.43725 | 0.76004 | 0.90512 | 1.1921 | 0.64014 | 1.0378 | -0.26702 | 0.19496 | 0.70604 | 0.89748 | 0.53359 | 0.76646 | 1.1069 | 1.3067 | 0.85423 | 1.0474 | 1.4343 | 0.15041 | 4.7781 | 3.5261 | 1.0102 | 2.5867 | 1.5611 | 1.0255 | 1.8102 | 1.8119 | 0.14088 | 0.062622 | 0.25475 | 0.29189 | 0.33197 | 0.64814 | 0.27628 | 3.7193 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.67906 | 1.8911 | 1.7666 | 0.054111 | 1.3844 | 0.54102 | 1.6314 | 0.66209 | 0.7203 | 0.67644 | 0.86486 | 1.4223 | 0.73176 | 0.69489 | 0.73517 | 0.74493 | 3.1206 | 1.5448 | 1.5374 | 1.5225 | 1.688 | 1.9922 | 2.0515 | 1.9752 | 2.1005 | 2.1396 | 2.0148 | 1.9836 | 1.7592 | 2.0322 | 1.4822 | 1.7851 | 3.1232 | 0.82116 | 0.35787 | 2.6224 | 1.7076 | 1.8212 | -0.027455 | 2.8543 | 1.0912 | 0.57083 | 1.0911 | -1.0941 | 1.191 | 1.2838 | 1.4673 | -0.44562 | 1.5931 | 1.868 | 1.5877 | 2.0482 | 2.0482 | 0.67936
N-2 | 16 | Taltola 33/11KV S/S | 16 | 0.38493 | 1.017 | 0.082298 | 0.12069 | 0.97588 | 0.96936 | 1.0113 | 1.3231 | 0.33968 | 0.70712 | 0.098815 | -0.044911 | 0.23679 | 1.0524 | 1.6228 | 0.26558 | 0.23422 | 0.088502 | 0.33533 | 1.9263 | 1.329 | 1.6903 | 1.4706 | -0.37402 | 1.3713 | 0.37291 | 0.54296 | 2.2787 | 1.0118 | 0.84 | 1.9242 | 0.14334 | 0.094891 | 1.3425 | 1.0333 | 2.9747 | 1.7673 | 0.91935 | 1.2402 | -1.9507 | 0.14303 | 0.72478 | 0.018107 | -0.19213 | 1.9799 | 2.2339 | 1.9059 | 1.8886 | 2.253 | 1.5811 | 0.67298 | 1.1415 | 2.3053 | 0.77238 | 1.2238 | 0.68339 | 1.2116 | 0.93544 | 1.2193 | 1.0636 | 0.23313 | 0.65451 | 0.14218 | 0.012824 | 0.39087 | 0.019629 | 0.25748 | -0.12359 | 3.7619 | -0.4519 | 2.7097 | 3.3138 | 3.7913 | 3.882 | 1.2382 | 1.3504 | 1.2944 | 0.41019 | 0.2 | 1.5 | 1.5 | 2.0501 | 2.5063 | 1.9736 | 1.2604 | 0.1 | 2.9542 | 0.53467 | 0.3205 | 2.0036 | 2.4961 | 2.464 | 1.9952 | 1.5966 | 1.9537 | 1.8334 | 1.4968 | 1.3059 | 2.4342 | 0.5824 | 1.3939 | 1.7617 | 1.3058 | 1.4406 | 3.1382 | 0.21252 | -4.4991 | 2.0728 | 1.6816 | -0.18215 | 1.0382 | 0.017392 | 1.4181 | 1.7313 | 0.04541 | 0.010384 | -0.10288 | 0.041528 | 0.60712 | 3.1629 | -0.15564 | 1.4478 | 1.2702 | 1.2192 | 1.1784 | 1.3251 | 1.3932 | 1.3492 | 1.3857 | 1.6153 | 1.3077 | 1.2965 | 3.3284 | -1.4756 | 2.7211 | 1.5062 | 1.2974 | 1.036 | 1.6825 | 0.79398 | 1.3964 | 2.9254 | 1.9155 | 2.8335 | 1.1641 | 1.7072 | 1.6609 | 1.9291 | 1.8667 | 1.7262 | 1.748 | 1.7456 | 1.6867 | 1.7174 | 1.8837 | 1.7354 | 1.7606 | 1.725 | 2.8569 | 2.7666 | 3.8641 | 3.232 | 3.9663 | 4.9346 | 4.4833 | 4.1258 | 3.7329 | 5.3235 | 5.3741 | 5.3741 | 5.3664
N-1 | 17 | Satmasjid 33/11KV S/S | 17 | -0.13906 | -0.10672 | 0.16541 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.88762 | 0.18437 | -0.086687 | -0.71231 | 0.41387 | 0.2 | 0.2 | 0 | 0 | -0.30904 | 0.0041724 | 0.5 | 0.70618 | -0.091654 | -0.1959 | 1.3798 | 0.5 | 0.4 | 0.4 | 0.5 | -0.03367 | 0.33 | 0.6 | 1.2626 | 0.96483 | 0.35067 | -0.1596 | 0.5 | -0.18193 | -0.1998 | -0.071902 | 0.84121 | 0.83687 | 0.83244 | 0.71968 | 0.91348 | 0.54897 | 0.20547 | 0.62608 | 1.1785 | -0.15065 | 0.3 | 0.8492 | 0.66761 | 1.928 | -0.55825 | 0.85228 | 0.83831 | 0.82135 | 0.84398 | 1.1593 | 0.088174 | 1.4738 | 1.3444 | 1.0557 | 0.12414 | -0.70521 | 2.7212 | -0.35893 | 1.515 | 0.27244 | 3.4479 | 2.68 | 2.3604 | -0.75923 | 0.94138 | 0.96728 | 3.769 | 1.6522 | 0.2 | 0.2 | -1.0216 | 0.9964 | 3.8365 | -1.3805 | 0.60098 | 0.70721 | 0.54141 | 1 | 1 | 2.5 | 2.4844 | 2.2227 | 2.4 | 0.26007 | 0.25 | 0.25 | 0 | 2.2535 | 1.2885 | 0.77312 | 2.1444 | 0.58601 | 0.35187 | 0.29258 | 0.58706 | 2.4839 | -1.5617 | 4.5829 | 0.48286 | 0.87769 | -0.037264 | 2.5343 | 1.0797 | 0.61185 | 0.37841 | 0.29597 | 0.37846 | 1.9813 | 1.5322 | 0.70817 | 1.0397 | 0.24423 | 1.0771 | 0.24808 | 0.72286 | 1.0122 | 2.0606 | 0.012477 | 1.0437 | 1.1116 | 1.18 | 1.2319 | 1.2555 | 0.99613 | 2.7488 | -0.24601 | 0.13511 | 0.40624 | 0.27186 | 0.85623 | 0.45794 | 0.85258 | 0.92607 | 0.61792 | 0.089742 | -0.16314 | -0.32931 | -0.15721 | 1.9505 | 0.35268 | 0.13323 | 5.9828 | 6.495 | 7.8586 | 6.7853 | 7.1054 | 6.6003 | 7.7293 | 8.6937 | 11.9015 | 9.9033 | 9.9492 | 9.9232 | 7.0387 | 7.1306 | 9.388 | 11.1902 | 11.1396 | 8.9065 | 12.7976 | 12.7976 | 13.5608
N-1 | 18 | Jigatola OLD 33/11KV S/S | 18 | -1.953e-14 | 1.3735 | 1.481 | 1.1097 | -0.34957 | 1.0304 | 0.66378 | 1.8877 | 0.9546 | 0.60017 | 1.8957 | 0.33273 | 1 | 1 | 1 | 1 | 1 | 0.74446 | 0.996 | 0.50178 | 0.34686 | 0.37747 | 0.40239 | 0.42522 | 0.41761 | 0.4164 | 0.43376 | 0.43939 | 0.38528 | 0.39 | 0.4476 | 0.46226 | 0.48087 | 0.47749 | 0.43031 | 0.82591 | 0.7489 | 0.30807 | 0.43369 | 0.49231 | 0.81248 | 0.71899 | 1.2786 | 0.87064 | 0.61788 | 0.9905 | 0.93825 | 0.77965 | 0.011508 | 0.74092 | 1.2523 | 0.80648 | 2.2875 | 0.39203 | -0.012942 | 0.66646 | 1.0705 | 0.72583 | 0.80323 | 0.72363 | 0.25598 | 1.9578 | 1.7207 | -0.66295 | -0.090552 | -0.14123 | -0.63134 | 0.6167 | 0.20553 | -0.72805 | 0.61574 | 1.1023 | 1.0539 | 1.3166 | 0.62467 | 1.7145 | 1.8474 | 0.40367 | 0.69156 | -1.4902 | 0.054184 | 0.29633 | 0.171 | 0.15138 | 0.1326 | -0.039485 | 0.78653 | -2.2459 | 0.28517 | 0.55037 | 1.3715 | 2.2968 | 1.0017 | 0.3517 | 1.0345 | -0.83168 | 0.93557 | 0.67072 | 0.059287 | -0.0097544 | 0.5992 | 0.35012 | 0.79351 | 0.2806 | 1.9353 | -0.50051 | 0.79648 | 0.49518 | 1.2063 | 0.71283 | 0.798 | 0.62713 | 0.85986 | 0.63038 | 0.32644 | 1.4306 | 0.40014 | 0.99149 | 0.46137 | -1.9944 | 3.4085 | 0.88017 | 0.72929 | -1.7748 | 1.0777 | 0.85223 | -0.74444 | 3.7527 | -0.89815 | 0.7088 | 0.65738 | 0.60909 | 1.1814 | 0.20633 | 1.0356 | 0.10716 | 0.91212 | 0.72586 | 0.68127 | 0.84491 | 0.69032 | 0.36185 | 0.67077 | 4.9875 | -0.71101 | 0.61024 | 14.456 | 15.37 | 17.7933 | 7.5922 | -0.55397 | 3.5988 | 5.9395 | 3.5186 | 4.3204 | 4.8732 | 8.5938 | 25.2692 | 14.0877 | 12.7148 | 8.1985 | 3.7664 | 3.5619 | 3.888 | 17.9983 | 16.9876 | 6.3184 | 4.3215 | 8.9799 | 8.9799 | 10.6051 | PT FUSE OFF june
N-1 | 19 | Kallyanpur & Agargaon 33/11KV S/S | 19 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 3.2166 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 9.1332 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
N-1 | 20 | Kamrangirchar 132/33/11KV S/S | 20 | 0.048115 | 0.69668 | 0.63098 | 0.3405 | 0.54629 | 0.796 | 0.085596 | 0.52303 | 0.3525 | 0.10635 | 0.22543 | 0.40305 | 0.05177 | 0.75252 | -0.045673 | 0.12338 | 0.10806 | -0.42312 | 0.38848 | 0.11329 | 0.34653 | -0.080676 | -0.62867 | 0.38885 | -0.64251 | -0.35892 | -0.10824 | 0.79691 | 0.21066 | 0.93 | 0.9 | 0.9 | 0 | 1.6814 | 0 | 0.91061 | 0.78115 | 0.076997 | 0.26272 | 0.35759 | 0.88713 | 0.73197 | 1.6563 | 0.95805 | 0.69629 | 1.35 | 1.25 | 1.3509 | 0.019897 | 2.2488 | 2.1135 | 0.76476 | 2.2546 | -0.49305 | -1.4224 | 0.18519 | 1.3561 | 0.65217 | -0.24759 | 0.032912 | 0.82955 | 0.03416 | 0.13451 | 0.064361 | -0.41133 | -0.4483 | -0.43002 | -0.38738 | -0.39385 | -0.36241 | 0.39354 | 0.71961 | 0.85112 | 0.69041 | 0.9753 | -0.63864 | -0.29645 | -0.27427 | -0.19172 | -2.4852 | -0.19882 | 0.2 | 0 | -0.067607 | -0.15155 | -0.4029 | -0.27213 | -0.30226 | 0.019843 | -0.12475 | -0.079817 | -0.31342 | -0.11871 | -0.10062 | -0.074794 | 0.54391 | 0.40162 | 0.31148 | 0.1777 | -0.10738 | -0.11218 | -0.066663 | -0.38381 | -0.25307 | -0.3134 | -0.36997 | -0.32271 | -0.34208 | -0.13569 | -0.096335 | -0.039772 | -0.094607 | -0.05589 | -0.087884 | -0.13639 | 0.14915 | -0.43685 | -0.24219 | -0.13698 | -0.16029 | -0.2877 | -0.19915 | -0.04903 | -0.86878 | 0.69814 | -0.03221 | -0.11701 | -0.10396 | -0.2 | -0.069855 | -0.16785 | -0.22791 | -0.13755 | -0.087066 | -0.098808 | -0.43685 | 0.24503 | -0.070266 | -0.11087 | -0.16657 | -0.076155 | -0.20062 | -0.18692 | -0.22908 | -0.21096 | -0.22253 | -0.18457 | -0.076746 | -0.099771 | -0.14734 | -0.28808 | -0.1647 | -0.15988 | -0.21761 | -0.14454 | -0.13081 | -0.10871 | -0.0087635 | 0.013221 | -0.029011 | -0.2914 | 0.037956 | -0.091203 | -0.23856 | -0.1792 | -0.82589 | 0 | 0 | 0 | 0 | 0
N-1 | 21 | Kamrangirchar 33/11KV S/S | 21 | 0.82578 | 1.54 | 1.8195 | 1.9439 | 2.2893 | 1.2775 | 1.3026 | 2.4709 | 1.4918 | 2.1184 | 2.298 | 2.4614 | 1.4259 | 1.5001 | 0.51551 | 1.7331 | 0.30834 | 2.1105 | 2.5793 | 1.7476 | 2.4879 | 2.8005 | 2.432 | 2.7787 | 0.7301 | 0.59266 | 1.5984 | -0.38347 | 0.63608 | 4.43 | 0.25486 | 0.28238 | -0.71262 | 1.1382 | -0.3789 | 1.6729 | 0.036364 | -0.94911 | 0.27238 | 1.4851 | 2.2811 | 1.7083 | 0.33562 | 2.221 | 0.33053 | 1.0945 | 2.4817 | -1.9381 | -0.76542 | 0.20345 | 1.5823 | -0.020259 | 1.9763 | -0.64545 | -0.52879 | 0.45106 | 0.71646 | 1.2334 | 0.89126 | 0.60429 | 0.069228 | 1.5375 | 0.98496 | 0.77726 | 2.8295 | 2.4912 | 2.2495 | 2.1989 | 1.3441 | 1.5161 | 1.952 | 3.2022 | 2.7706 | 5.704 | 3.5894 | 1.4228 | 1.921 | 0.01 | 1.0967 | 6.9902 | -1.2482 | 2.1756 | 2.3691 | 0 | 0.44474 | 0.1 | 0.71245 | 0.31007 | -1.3519 | -0.60511 | 0.53995 | 0.041911 | 0.99191 | 0.4264 | 1.8368 | 2.4564 | 2.594 | 2.817 | 1.8005 | -0.46218 | -0.59946 | 0.14812 | -0.19405 | 0.0012936 | -1.0565 | 0.081125 | 2.4053 | -0.14659 | 0.1433 | -0.088893 | 0.017214 | -0.096977 | -0.017123 | -0.40494 | -0.10527 | -0.33514 | 0.3991 | -1.1139 | 0.47635 | -0.84427 | 0.68029 | -0.053106 | -0.1367 | -0.91351 | 0.38433 | 1.1768 | -1.3263 | -0.51865 | -0.076346 | -0.1429 | -0.50649 | -0.21485 | -0.20509 | -0.28413 | -0.3027 | 0.26577 | -0.53548 | -0.1507 | -0.13708 | 0.02849 | -0.42376 | 0.16748 | -0.81239 | -0.098916 | 0.58013 | -0.3631 | -0.33298 | 0.32139 | -0.094775 | 0.57426 | -0.17178 | 0.10482 | 0.067148 | -0.22611 | -0.1068 | -0.14713 | -0.28204 | -0.2723 | -0.045295 | -0.35652 | -0.19187 | -2.0556 | -1.0421 | -0.15908 | -0.25237 | -0.95465 | 1.1198 | -1.2455 | -0.060157 | -0.060157 | -0.23203
N-1 | 22 | Lalbagh OLD 33/11KV S/S | 22 | 0.18209 | 0.65746 | -0.62501 | 0.72401 | -0.96748 | 0.17412 | 1.0143 | 0.1223 | 0.7259 | 1.521 | 1.1358 | 2.0489 | 1.1623 | 1.1088 | 1.1848 | 0.17858 | 0.6513 | 0.58477 | 1.189 | 0.095281 | 1.5199 | 0.024022 | 1.8097 | 2.644 | 0.22406 | 1.6095 | 0.37821 | 1.4774 | 0.066333 | -0.07 | 1.495 | 0.67613 | -0.33217 | 1.0551 | 1.7915 | 1.7421 | -0.49325 | 1.8698 | 1.775 | 0.29768 | 0.78376 | 2.4164 | 1.6388 | 0.37666 | 1.2309 | 3.1113 | 3.8888 | 1.76 | 1.3987 | 1.5399 | 0.91829 | 1.7144 | 0.68085 | 0.961 | 1.8859 | 2.9832 | 4.1951 | 0.37221 | 1.0725 | 0.28096 | 0.83735 | 0.87676 | 2.2525 | -0.8401 | 0.86077 | -1.1849 | 0.70944 | 0.098531 | 0.1721 | 1.8266 | -0.46948 | 0.18754 | 0.83818 | 1.4182 | -0.47351 | 2.2812 | 1.1732 | 0.91672 | 0 | 2.3318 | -3.1225 | 0.58683 | 1.044 | 2.1102 | 4.4915 | 0.69106 | 3.8897 | 2.4364 | 2.5284 | 0.12059 | 2.5567 | 1.5417 | 0.62383 | 8.5225 | 1.9537 | 3.7921 | -0.66376 | 2.4039 | 1.3255 | 1.4692 | 2.4435 | 2.1646 | 5.8014 | 3.8514 | 3.7402 | 2.3903 | 4.4431 | 4.869 | 3.2659 | 5.0778 | 3.883 | 5.45 | 3.3211 | 2.559 | 3.284 | 2.8093 | 0.5 | 1.9269 | 4.2836 | 3.8342 | 7.7562 | 5.219 | 6.4671 | 4.6061 | 2.6441 | 7.8682 | 2.0937 | 5.4364 | 3.7299 | 4.3002 | 2.3275 | 3.3705 | 2.8598 | 4.3458 | 3.0405 | 2.3239 | 3.0642 | 2.8259 | 3.3816 | 3.126 | 3.3356 | 4.664 | 0.94133 | 4.5931 | 3.6903 | 3.2679 | 3.3467 | 7.4111 | 3.7029 | 2.3088 | 2.3132 | 3.6914 | 4.7552 | 3.1931 | 3.6059 | 2.4763 | 1.8424 | 2.537 | 2.659 | 2.684 | 2.4162 | 1.2374 | 4.2537 | 1.6822 | 1.9678 | 2.0076 | 5.4649 | 0.10744 | 7.3336 | 7.3336 | 15.8103
S-2 | 23 | Banshal 33/11KV S/S | 23 | 0.31033 | 0.34274 | -0.032742 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.9 | 0.9 | 0.16072 | 1.1009 | -0.15848 | 1.1205 | 0.15 | 0.32688 | 1.9509 | 2.7859 | 1.6396 | 3.2853 | -0.73511 | 3.2943 | 2.8739 | 1.9383 | 0.55295 | 0.58107 | 1.0477 | -0.54535 | 1.7407 | 3.1577 | 0.3 | 0.3 | 0.3 | 0.63559 | 1.1312 | 1.0188 | -1.0065 | -1.2377 | -1.5457 | 3.1587 | -0.24125 | 0.41437 | -0.13607 | 0.87285 | -0.8318 | -0.86641 | 4.1076 | 1.2053 | 0.60436 | 0.01 | -0.018637 | 0.01 | 2.3407 | 3.5495 | -0.21776 | -1.2969 | -0.14339 | 0.46767 | -0.17632 | 0.20391 | -1.0295 | 0.081238 | 1.0027 | -2.5469 | 0.34761 | -1.3655 | 1.8979 | -0.27559 | -1.3259 | 0.51717 | -0.5054 | 2.0317 | 0.77983 | -0.072548 | 1.094 | 0.08666 | -0.62497 | 0.41802 | 0.2057 | 7.4803 | -0.47426 | -2.0087 | -0.0082352 | -0.2719 | 0.60081 | 0.62928 | 2.8493 | 0.2219 | -0.97693 | 1.285 | -1.4035 | 0.85638 | 3.3642 | -2.2155 | 1.5608 | 0.12063 | 0.18264 | 1.0908 | 1.8259 | 2.7748 | 1.347 | 2.0542 | 0.35123 | -0.48899 | -0.14395 | -0.57697 | -0.60307 | -0.69369 | -1.1221 | -1.0961 | 0.1871 | -0.1776 | 0.19345 | 0.22497 | 0.76063 | 0.73319 | 0.59288 | 0.4153 | 0.59252 | -0.17651 | 0.19446 | -0.24921 | -0.10459 | 0.032942 | 0.15539 | 1.1279 | 0.23509 | 0.1816 | 0.10117 | 0.17119 | -1.5446 | -1.1835 | -1.3262 | -0.41959 | -0.89521 | 1.5629 | 3.2948 | -3.5788 | 2.9932 | -0.14241 | -5.9446
N-1 | 24 | Japan Garden 33/11 KV, | 24 | -0.07909 | -0.065475 | -0.49665 | -0.013891 | 1.7381 | 1.931 | 2.0415 | 2.5207 | 1.0972 | 0.35834 | 1.3813 | 0.56948 | 0.15711 | 2.3212 | 1.5192 | 0.39029 | -0.42093 | 0.10992 | 0.90231 | -0.048525 | 0.44664 | -0.83521 | 0.67652 | 0.88986 | 0.32547 | 0.24221 | 1.6758 | 0.045823 | 1.4927 | -0.79 | 3.1551 | 0.83295 | 1.9254 | 2.9892 | 0.8053 | 0.75571 | 0.37908 | 0.43995 | 0.99759 | 1.7356 | -0.20945 | 3.2587 | 1.478 | 1.6865 | 2.4567 | 1.9168 | 1.5436 | 0.79075 | 0.34495 | -0.76557 | 0.5018 | 1.0429 | 1.3376 | 0.53767 | 1.1517 | 1.2541 | 0.5592 | 0.077543 | 0.38731 | 0.12917 | 0.33227 | 1.8601 | 0.62328 | 14.194 | -8.6527 | 0.80994 | -0.98867 | -0.30907 | -0.040974 | -1.2997 | -1.3995 | 2.6514 | 1.6279 | 1.3734 | -0.086532 | -0.51099 | -0.32895 | -2.5099 | 1.1627 | -0.55786 | -2.8539 | -0.3007 | -1.2445 | 1.8112 | 1.2569 | -0.32008 | -0.3367 | -0.38423 | 0.5 | -2.6633 | 0.1 | 0.1 | -0.78942 | 0.19885 | -0.58528 | 2.2636 | 1.0552 | 0.46739 | 1.3941 | 0.94354 | 0.16951 | -0.1289 | -0.94113 | -0.93122 | 1.2012 | 0.047351 | 0.40487 | 0.1 | 0.1 | 0.1 | 0.1 | -1.8469 | -1.4186 | -2.312 | -1.4929 | 0.15887 | 0.27783 | 0.23366
N-1 | 25 | Azimpur 33/11 KV, | 25 | 1.3852 | 1.4942 | 1.9396 | 1.6222 | 2.3784 | 1.9293 | 1.5954 | 1.9107 | 1.9322 | 0.75226 | 1.3138 | 0.79291 | 0.90638 | 1.6819 | 1.0703 | 0.83033 | 1.8274 | 0.47014 | 1.3156 | 0.84899 | 1.1516 | 1.1005 | 1.3314 | 1.6274 | 0.29384 | 1.8405 | 1.1167 | 2.0479 | 0.99969 | 1.3 | 1.1076 | 0.45803 | 0.97747 | 0.96412 | 0.77551 | 0.12524 | -0.37497 | 0.36559 | 2.593 | 1.7775 | 2.2565 | 0.44877 | 1.375 | 1.4508 | -0.032073 | 0.098554 | 1.2844 | 0.26045 | 1.5959 | 4.3996 | 1.9141 | -1.2003 | 1.5924 | -0.26391 | -0.37937 | -0.69129 | 2.4738 | 2.5479 | 2.3977 | 2.902 | 2.3769 | 0.67316 | 2.8097 | 1.2479 | 2.7192 | 2.8872 | 2.6477 | 3.0101 | 0.32335 | 2.2534 | 1.0054 | -0.27759 | 0.49382 | -0.37004 | -0.81938 | 0.19047 | -0.37162 | 2.7583 | 0.21891 | -0.30534 | 0.39369 | 0.43733 | 2.5735 | -0.88759 | 0 | 0.2 | -0.59719 | -0.33199 | -0.49938 | 0.28856 | 0.036036 | 2.9466 | 1.596 | 4.7844e-05 | 5.1913 | 4.7632 | 0.9718 | 5.0259 | -0.45899 | 0.39559 | 1.1956 | 0.58757 | 0.13767 | 0.14847 | 0.064109 | 0.10354 | -0.82012 | 0.22705 | 0.50167 | 0.40496 | -1.6198 | 2.4732 | 0.39155 | 0.35757 | 0.30085 | 1.2774 | 5.7357 | 7.4551
N-2 | 26 | SHERE BANGLA NAGAR 33/11 KV S/S | 26 | -1.6544 | -1.0941 | 4.7772 | -1.1487 | -0.91183 | -3.5539 | -1.1299 | -0.03041 | 1.34 | 0.83275 | 1.9504 | 1.74 | -0.44815 | 0.40642 | 2.4685 | 1.0117 | 2.6191 | 1.615 | 2.1442 | 1.5763 | 2.2994 | 2.7514 | 2.4419 | 3.665 | 3.2509 | 2.7192 | 2.6436 | 2.5533 | 3.9586 | 3.83 | 2.3966 | 2.0457 | 1.0458 | 2.5105 | 3.8909 | 3.7077 | -3.9468 | 2.9548 | 1.7563 | 1.6372 | 2.8809 | 2.1601 | 0.18851 | 1.6314 | 0.085601 | 3.1566 | 1.5 | 0.91869 | 4.0012 | 2.0431 | 1.8198 | 2.9475 | 0.75771 | 0.88391 | -1.7841 | 0.14783 | 0.39783 | 1.1222 | 2.1372 | 0.23405 | 2.4471 | 0.12662 | 0.90768 | 0.91519 | 0.48253 | -79.0711 | -0.66006 | 1.3252 | 0.94511 | 1.1885 | 1.7492 | -0.8558 | 1.1059 | -0.84159 | 1.214 | 2.762 | -1.5822 | -1.1173 | 0.85854 | 1.7165 | 1.8712 | -0.034981 | -1.2269 | -3.1107 | 0.83594 | 0.37973 | -0.20467 | -0.32423 | -3.1281 | 1.6462 | 0.582 | -0.23698 | -0.97408 | 2.0948 | 2.0334 | 2.7134 | 1.5656 | 6.914 | 3.6065 | 3.9062 | 3.6549 | 3.3643 | 2.6115 | 2.17
N-1 | 27 | LALBAGH 132/33 KV S/S | 27 | 0.6536 | 0.7514 | 0.53189 | 1.746 | 0.38553 | 0.68199 | 0.44204 | 0.49857 | 0.36511 | 0.08009 | 0.22363 | 0.34225 | 0.15524 | 0.60269 | 0.48851 | 0.079531 | 0.82519 | 0.25539 | 0.43615 | 0.56525 | 0.5 | 1.1723 | 1.1311 | 2.0196 | 1.1992 | 1.2848 | 1.3841 | 0.84954 | 0.55685 | 0.8 | 0.82509 | 1.4752 | 0.7789 | 0.20279 | 0.44004 | 0.77228 | 0.40756 | 1.9914 | 0.90887 | 0.97376 | 0.31732 | 0.59359 | 1.4989 | 0.54451 | 1.7069 | 1.7958 | 1.5615 | 1.75 | 1.7521 | 1.3984 | 3.3156 | 0.3 | 0 | -0.10257 | -0.11178 | -0.92411 | 1.4436 | 0.59364 | 0.63432 | 0.36225 | 0.14356 | 0.94919 | 0.95211 | 0.83284 | 0.66436 | 0.36177 | 0.21841 | 0.16328 | 0.20551 | 1.4111 | 1.4943 | 1.2829 | 2.3111 | 0.30183 | 0.16477 | 0.36888 | 0.19374 | 0.31451 | 0.22578 | 0.19821 | 0.19675 | 0.19494 | 0.19163 | 0.17706 | 0.29012 | 0.41359 | 0.21179 | 0.080658 | 0.21712 | 0.19928 | 0.17938 | 0.22258 | 0.17324 | 0.19271 | 0.17345 | -0.45089 | 0.91219 | 0.15633 | 0.15421 | 0 | -0.26781 | 0.57194 | 0.12456
N-1 | 28 | LALBAGH 33/11 KV S/S | 28 | 0.91748 | 0.048472 | 0.16561 | 0.54916 | 2.823 | -4.7097 | 0.60815 | 0.74173 | 1.2576 | 1.2902 | 1.4779 | 1.8287 | -0.046619 | 0.45482 | 1.4639 | 1.0238 | 2.9749 | 0.55734 | -0.65567 | 2.8449 | 2.4988 | 1.2632 | -1.5589 | 2.9478 | 1.4506 | 2.0062 | 2.4816 | -0.57082 | -0.17104 | 4.76 | 1.3563 | 1.6823 | -0.46912 | 3.7429 | 2.3563 | 0.98668 | -0.94061 | 3.127 | -0.22819 | -0.10017 | 1.7124 | 2.7907 | 0.8307 | 0.71917 | 1.4864 | 3.6443 | 3.7546 | 2.1568 | 4.513 | 2.6935 | 2.0829 | 0.95636 | 0.46955 | 2.9877 | 1.9004 | 1.5359 | 3.3861 | 2.7771 | 0.7527 | 0.58565 | 0.40531 | 1.0032 | 0.86716 | 0.75326 | 0.554 | 0.2796 | 0.40956 | 0.6063 | 0.10137 | 0.82858 | 0.69458 | 0.14565 | 2.0206 | 0.33327 | 0.85226 | 0.80524 | -0.0057625 | -0.81783 | 0.83458 | -0.088142 | -0.45161 | 0.5108 | -0.068006 | 1.2655 | 0.01 | 0.01 | 1.0373 | 0.60421 | -0.043228 | -0.06162 | 0.1606 | -0.096624 | 5.4749 | 1.561 | 3.8245 | -4.7293 | -0.49743 | -0.3296 | -3.0498 | 2.5485 | 2.2852 | 0.78643 | 8.253 | -8.11
N-2 | 29 | Asad Gate 33/11 KV S/S | 29 | 0.8 | 1.0884 | 1.0942 | 1.1749 | 0.94949 | 0.88476 | 2.227 | 0.67417 | 1.3774 | 1.0028 | 0.99544 | 0.97448 | 1.073 | 1.0195 | 0.92013 | 1.0425 | 1.0152 | 0.97786 | 1.3269 | 0.65342 | 1.1813 | 1.0598 | 0.1558 | 1.9454 | 0.97524 | 1.2242 | 1.0406 | 1.0406 | 1.0312 | 1.06 | 1.0915 | 1.0659 | 1.1003 | 1.0459 | 1.2775 | 1.802 | 0.89492 | 0.81925 | -0.31309 | -0.1097 | 1.3977 | 1.4923 | 3.1548 | 1.7338 | 1.1755 | 1.409 | 0.82077 | 1.6571 | 0.61198 | 1.3112 | 1.248 | 1.6126 | 2.5188 | 0.4699 | 1.2213 | 1.594 | 1.6972 | 0.28505 | 1.2135 | 0.31995 | 1.2325 | -1.0596 | 1.2855 | 1.2639 | 1.1577 | 0.51684 | 1.0041 | 1.1733 | 0.65541 | -0.082523 | 1.3807 | 0.28786 | 0 | 0.3747 | 0.98929 | 0.01 | 0.01
N-1 | 30 | Shatmasjid 132/33 KV S/S | 30 | -0.45176 | -0.38966 | -2.8512 | -0.18688 | 5.3937 | -2.558 | -1.1576 | 0.67904 | 0.17093 | 0.74728 | -0.10235 | -0.73749 | -1.4906 | 0.47091 | -0.65027 | -1.3917 | -0.11126 | 0.42405 | 0.72484 | -1.3022 | -0.88376 | 0.48716 | 0.74622 | 0.055026 | -0.59109 | 0.13777 | -2.0156 | -0.64259 | -1.3594 | -1.75 | -4.2624 | -3.4763 | -4.7337 | -0.77981 | -4.46 | -0.26287 | 0.21989 | -0.61007 | -1.7129 | -1.4675 | -1.1666 | 0 | 0.45202 | 1.7484 | 0.17346 | 0.1271 | -0.29798 | 0.43873 | -0.62099 | 0.070509 | 0.82441 | 0.44973 | 1.2767 | -0.72331 | 0.015479 | 0 | 0.0050118 | -0.88588 | 0.73121 | 0.13798 | 0.2249 | 0.40866 | 0.32258 | 0.080651 | -0.14135 | 0.041003 | -0.053624 | 0.72278 | -0.18704
N-2 | 31 | Banasree 33/11 SS | 31 | 1.0595 | 1.1241 | 0.20929 | 0.94813 | 1.4266 | 1.2727 | 1.2441 | 1.1461 | 0 | 1.3034 | 1.7247 | 1.6737 | 0.08467 | 1.8747 | -0.26814 | 1.6832 | 1.504 | 0.7311 | -0.62435 | 2.8286 | 2.0741 | 1.122 | 0.93982 | 0.53747 | 1.4968 | 1.2166 | 0.95214 | 0.18964 | 1.5892 | 1.8 | 0.94593 | 1.2594 | 1.2177 | 1.4531 | 0.83882 | 2.6245 | -0.84169 | 0.73026 | 0.40817 | -1.1539 | 3.891 | 1.774 | 0.48838 | -0.79596 | 0.85169 | 0.15791 | 3.4656 | 0.26578 | 1.5314 | 0.80457 | 0.77414 | 1.5321 | -0.81789 | 0.19189 | 0.066093 | 0.1652 | 0.24237 | 1.0486
N-2 | 32 | Mugdhapara Hospital | 32 | 0.92608 | 1.4792 | 0.074988 | 0.11193 | 0.20967 | 0.28376 | 0.38421 | 0.32909 | 0.271 | 0.28491 | 0.22974 | 0.23672 | 0.22755 | -0.39357 | 0.81992 | 0.46059 | 0.71875 | 0.86594 | 1.0479 | -0.033198 | 3.9312 | 2.7052 | 0.93712 | 1.6304 | 0.76869 | 1.5338 | 2.3084 | -0.49724 | 0.75408 | 2.45 | 3.5317 | 3.2776 | 1.8906 | 5.3371 | 5.5428 | 4.0609 | 4.1256 | 5.1739 | 4.665 | 4.7191 | 2.8091 | 4.1852 | 4.3241 | 2.9998 | 0.93032 | 5.2788 | 5.3531 | 0.95387 | 1.6944 | 1.7822 | -0.95524 | 1.4642 | 2.0446 | 3.3462 | 0.59144
N-1 | 33 | DMC | 33 | 2.024 | 0.90537 | 0.27387 | 0.19858 | 1.7632 | 0.35738 | 2.0285 | 0.9521 | 1.3864 | 1.033 | 1.0898 | 2.9141 | 1.5525 | 2.1935 | 2.5361 | 1.2486 | -0.21757 | 1.4007 | 2.5956 | 0.58942 | 2.7362 | 2.4151 | 1.934 | 2.1296 | 2.9431 | 0.20155 | 2.8472 | 1.934 | 1.9059 | 4.4 | 3.8093 | 0.57134 | 0.24737 | 4.3247 | 4.2116 | 4.5305 | 2.7414 | 2.0543 | 2.8481 | 1.3159 | 3.1341 | -0.66926 | 0.92689 | 1.1508 | 0.86934 | 0.72002 | 1.0124 | 1.6157 | 0.69489 | 0.35117 | 9.3479 | 5.2717
N-2 | 34 | Green Road Dormatory 33/11 SS | 34 | 0.73671 | -0.81473 | 1.4639 | 0.48456 | 1.6157 | 2.2309 | 1.6082 | 1.7356 | 0.77297 | 0.18762 | 0.63907 | 0.84329 | -0.17966 | 0.3987 | 0.63593 | 0.12071 | 1.2655 | -0.28954 | 1.1018 | 2.2801 | 1.225 | 0.99364 | 0.8833 | 0.9282 | 1.065 | 0.85664 | 0.94439 | 0.96982 | 1.0397 | -0.06 | 1.6649 | 1.1068 | 0.91539 | 0.86179 | 0.97861 | 0.88618 | 3.6321 | -0.19151 | 1.2778 | 0.29639 | 3.4834 | 0.3414 | 0.15185 | 3.3097 | 1.5 | 5.4295 | 4.0103 | 3.6769 | 6.8988 | 4.7938 | 5.0474
N-1 | 35 | BSMMU 33/11KV S/S | 35 | 0.51158 | 0.89671 | 0.65778 | 0.5861 | 0.0029245 | 0.91943 | 1.2024 | 1.4445 | -0.43765 | 1.6695 | 0 | 0.37092 | 1.7504 | 0.6521 | 0.76418 | 0.75346 | 0.37083 | 1.7388 | 1.0752 | 0.75401 | -0.17448 | 0.39552 | 0.20029 | 0.62846 | 0.66759 | 0.67722 | 0.63491 | 0.70655 | 1.4965 | 0.85 | 2.4876 | 1.6805 | 0.25897 | -2.2556 | 5.9364 | -0.65119 | 0.042762 | 1.3602 | 2.628 | 2.1916 | 1.2094 | 1.4957 | 1.293 | 1.8 | 1.443 | 4.3187 | -1.5353 | 0.78622 | 0.32181 | 3.3391
N-1 | 36 | Dhaka Uddyan 33/11 KV S/S | 36 | -0.2151 | 0.41675 | 1.8057 | -0.44301 | 0.39604 | -0.16238 | 2.4238 | 0.59122 | 0.78967 | 0.62789 | 1.8916 | 0.34848 | 1.4295 | 1.9994 | 1.0523 | 1.0086 | 1.2535 | 0.36676 | 1.47 | 1.1419 | 1.4242 | 0.99532 | 0.43894 | 0.88648 | 0.28524 | 0.65882 | 0.77512 | 1.8873 | 1.3561 | 2.08 | 2.0256 | 1.8977 | 1.1252 | 2.8741 | 4 | 4 | 3 | 3 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.439
N-1 | 37 | Dhaka University 132/33 KV S/S | 37 | 0.38026 | 1.2411 | 0.48235 | 1.0733 | 1.117 | -0.1594 | 0.96151 | 0.90232 | -0.37932 | 0.091797 | 1.2206 | 0.5 | 0.93398 | 1.6061 | 0.59655 | -0.29575 | 0.10239 | 0.25293 | 0.62934 | 0.83023 | 0.03143 | 0.016276 | -0.21356 | 0.67957 | 1.3619 | 2.0184 | 0.015433 | 0.71931 | -0.99105 | -0.91 | -0.6824 | 3.2972 | 3.8654 | 1.9641 | 2.5926 | 3.8739 | 3.5975
N-1 | 38 | Dhaka University 33/11 KV S/S | 38 | 0.81432 | 0.021568 | 0.24911 | 1.7162 | 0 | 0.395 | -0.011609 | 0.13207 | 1.0276 | 0 | -0.013376 | 0.025484 | -0.034771 | 1.5 | 1.5 | 1.5441 | -0.14065 | 0.84541 | 0.19084 | 31.0328 | 0 | 2.9245 | 0.30864 | -0.31898 | -0.38873 | -0.08726 | 0.086228 | -0.10116 | 0.065617 | 0 | 0 | 0 | 0 | 0 | 0 | -0.79365 | 0 | 0 | #DIV/0! | 9.5166
N-2 | 39 | Monipuripara 33/11 KV S/S | 39 | 0.51746 | 0.33779 | 4.0099 | 1.6643 | 1.0098 | 1.368 | 5.9274 | -2.3189 | 2.5 | -0.86087 | 1.5736 | -0.17023 | 3.2331 | 4.7309 | 2.8365 | 0.15467 | 5.2095 | -1.0033 | 1.0522 | 4.3065 | 0.32439 | 0.2259 | 1.0612 | 1.0424 | 4.765 | 1.9502 | 0.96488 | 0.89767 | 0.95497 | 1.71 | 2.2348 | -0.91531 | 0.50605 | 0.68997 | 0.63829 | 5.4661 | -0.54678 | 4.8613
N-1 | 40 | BGB 33/11 KV S/S | 40 | 0.48002 | 0.9905 | 0.0035339 | 0.4942 | 1.2483 | 0.33186 | 0.34499 | 0.0099613 | -0.10335 | 0.068735 | 1.7018 | 1.2085 | 1.118 | 1.2304 | 0.49312 | 1.9323 | 1.2827 | 1.2356 | 1.4037 | 0.47625 | 1.3511 | 0.68431 | 0.87758 | 0.8337 | 0.94868 | 0.67127 | 1.23 | 0.58352 | 0.60863 | 1.28 | 0.76342 | 1.5342 | -0.32297 | 0.091134 | 0.70062
N-1 | 41 | BB Aveneu 33/11 KV S/S | 41 | 0.22998 | 1.3691 | 1.6496 | 1.7534 | 0.50085 | 1.7679 | -0.22053 | 1.4079 | 1.4124 | 0.77125 | 1.2426 | 2.7817 | 0.85393 | 0.67044 | 2.1698 | 1.9847 | 0.46928 | 1.897 | 0.84863 | 1.2604 | -0.28377 | 1.7227 | -0.29626 | -0.51843 | 0.9702 | -0.41466 | -0.35727 | 3.9689 | 0
N-1 | 42 | Jigatola 132/33 KV S/S | 42 | -0.23922 | -0.077832 | -0.078186 | 0.79587 | 0.0019311 | 1.7251 | -0.87194 | 0.23041 | 0.3831 | 0.10766 | 0.4173 | 0.18396 | 0.10353 | 0.12776 | 0.72539 | -0.12475 | -0.099075 | 0.34865 | -25.2075
N-1 | 43 | Jigatola New 33/11 KV S/S | 43 | 0.38993 | 0.14554 | 0.13635 | 0.97079 | 0.078701 | 2.1573 | -0.056601 | 0.4574 | 0.76157 | 0.30375 | 0.015348 | 0.22961 | 0.083476 | 0.6508 | 1.155 | 0.43669 | 0.24613 | 0.29421 | 0.4846
N-2 | 44 | Ispahani 33/11 KV S/S | 44 | 1.2312 | 0.62377 | 1.6517 | 0.74247 | 0.87404 | 1.2831 | 0.86748 | 1.7955 | -0.162 | 3.7374 |  |  | 0.86748 | 1.7955 | -0.162 | 3.7374
N-1 | 45 | Kamrangirchar-2 33/11 KV S/S | 45 | 0.095247 | 0.77279 | -0.070094 | 0.95721 | 1.8418 | 0.64068 | 0 | 1.7955 |  |  |  |  | 0 | 1.7955
SOUTH
| Sl. No. | Name of S/S | Page No. | July-2023 % of Loss | June-2023 % of Loss | May-2023 % of Loss | April-2023 % of Loss | March-2023 % of Loss | February-2023 % of Loss | January-2023 % of Loss | December-2022 % of Loss | November-2022 % of Loss | October-2022 % of Loss | September-2022 % of Loss | August-2022 % of Loss | July-2022 % of Loss | June-2022 % of Loss | May-2022 % of Loss | April-2022 % of Loss | March-2022 % of Loss | February-2022 % of Loss | January-2021 % of Loss | December-2021 % of Loss | November-2021 % of Loss | October-2021 % of Loss | September-2021 % of Loss | August-2021 % of Loss | July-2021 % of Loss | June-2021 % of Loss | May-2021 % of Loss | April-2021 % of Loss | March-2021 % of Loss | February-2021 % of Loss | January-2021 % of Loss | December--2020 % of Loss | November--2020 % of Loss | October--2020 % of Loss | Semtember--2020 % of Loss | August--2020 % of Loss | July--2020 % of Loss | June--2020 % of Loss | May--2020 % of Loss | April--2020 % of Loss | March--2020 % of Loss | February--2020 % of Loss | January--2020 % of Loss | December--19 % of Loss | November--19 % of Loss | October--19 % of Loss | September--19 % of Loss | August--19 % of Loss | July--19 % of Loss | June--19 % of Loss | May--19 % of Loss | April--19 % of Loss | March--19 % of Loss | Feb--19 % of Loss | Jan--19 % of Loss | Dec--18 % of Loss | Nov--18 % of Loss | Oct--18 % of Loss | Sep--18 % of Loss | August--18 % of Loss | June--18 % of Loss | May--18 % of Loss | April--18 % of Loss | March--17 % of Loss | Febrruary--17 % of Loss | Dceember--17 % of Loss | Dceember--17 % of Loss | October--17 % of Loss | September--17 % of Loss | August--17 % of Loss | July--17 % of Loss | June--17 % of Loss | May--17 % of Loss | April--17 % of Loss | March--17 % of Loss | February--17 % of Loss | January--17 % of Loss | December--16 % of Loss | November--16 % of Loss | October--16 % of Loss | September--16 % of Loss | August--16 % of Loss | July--16 % of Loss | June--16 % of Loss | May--16 % of Loss | April--16 % of Loss | March--16 % of Loss | February--16 % of Loss | January--16 % of Loss | DECEMBER--15 % of Loss | NOVEMBER--15 % of Loss | OCTOBER--15 % of Loss | SEPTEMBER--15 % of Loss | AUGUST--15 % of Loss | JULY--15 % of Loss | JUNE--15 % of Loss | MAy--15 % of Loss | April--15 % of Loss | March-15 % of Loss | February--15 % of Loss | January--15 % of Loss | December--14 % of Loss | November--14 % of Loss | October--14 % of Loss | Sept--14 % of Loss | August--14 % of Loss | JULY--14 % of Loss | May--14 % of Loss | April--14 % of Loss | March--14 % of Loss | February--14 % of Loss | January--14 % of Loss | December--13 % of Loss | November--13 % of Loss | October--13 % of Loss | September--13 % of Loss | August--13 % of Loss | JULY--13 % of Loss | JUNE--13 % of Loss | MAY--13 % of Loss | April--13 % of Loss | March--13 % of Loss | February-13 % of Loss | January-13 % of Loss | DEC-12 % of Loss | NOV-12 % of Loss | OCT-12 % of Loss | SEP-12 % of Loss | August-12 % of Loss | July-12 % of Loss | June-12 % of Loss | MAY-12 % of Loss | April-12 % of Loss | March-12 % of Loss | February-12 % of Loss | January-12 % of Loss | December-11 % of Loss | November-11 % of Loss | October-11 % of Loss | September-11 % of Loss | AUgust-11 % of Loss | July-11 % of Loss | June-11 % of Loss | May-11 % of Loss | April-11 % of Loss | March-11 % of Loss | february-11 % of Loss | January-11 % of Loss | 2011-12-10 | 2011-11-10 | Oct-10 % of Loss | August-10 % of Loss | July-10 % of Loss | June-10 % of Loss | MAY-10 % of Loss | April-10 % of Loss | March-10 % of Loss | February-10 % of Loss | January-10 % of Loss | December 09 % of Loss | November % of Loss | October % of Loss | September % of Loss | August % of Loss | JUly % of Loss | June % of Loss | May % of Loss | April % of Loss | March % of Loss | February % of Loss | January % of Loss
S-2 | 1 | Bangabhaban 132/11KV S/S | 1 | 0.24678 | 0.61506 | 1.0616 | 0.83693 | 2.2541 | 2.0557 | 0.34598 | 0.94783 | 0.61128 | 0.80127 | 1.4816 | 0.15513 | 0.79607 | 1.5974 | 0.039462 | 1.9908 | 0.32999 | 0.41972 | 0.41512 | 0.23228 | -0.050862 | 0.84208 | 1.2767 | 1.8662 | 2.2373 | 1.7014 | 3.1481 | -0.14433 | 2.688 | 0.55 | 1.8404 | 1.3332 | -0.84549 | 2.187 | 2.4855 | 1.0176 | 0.22897 | 2.272 | 0.31549 | 0.1576 | 1.8969 | 3.3853 | 3.0587 | 0.96413 | 0.64621 | 1.9208 | 3.8404 | 2.6392 | 3.8119 | 3.0188 | 3.1124 | 1.5843 | 0.66777 | -0.60973 | -1.5591 | -0.76341 | 0.2 | 0.05 | 0.52167 | 0.46393 | 1.2299 | -0.3653 | -7.6676 | -0.26676 | 0.98698 | 0.016551 | 0.72082 | 0.45889 | 0.41912 | 0.90593 | 0.18293 | 2.8447 | -3.8788 | 2.434 | 0.25033 | 1.1669 | 0.99811 | 0.37532 | 0.56083 | 0.73206 | 4.768 | 0.35 | 0.39112 | 0.33927 | 0.90501 | -0.57908 | 0.25474 | 1.2158 | -0.14627 | -0.4127 | 1.262 | 1.4317 | 8.1138 | -5.5253 | 0.80007 | 0.53336 | -0.55697 | 0.31574 | 0.96548 | 2.3832 | -1.487 | -1.232 | 1.8953 | 0.34879 | 0.31534 | 0.19835 | 0.2305 | -0.048875 | 0.45708 | 0.35158 | -0.28562 | 1.6933 | 0.79563 | -1.1751 | -0.11982 | 1.4096 | 0.53224 | 1.4944 | 0.31443 | 0.24161 | 0.319 | 0.21472 | 0.15235 | 0.3096 | 0.68872 | 0.51652 | 0.29398 | 0.26085 | 0.24119 | 0.31279 | 0.22231 | 0.26689 | 0.20247 | 0.19704 | -0.13001 | -0.097576 | -0.14342 | -0.29082 | -0.57998 | -0.50022 | -0.51335 | -0.48256 | -0.40703 | -0.33223 | -0.49683 | -0.29467 | -0.27466 | 0.10668 | 0.079304 | -0.0005093 | 0.10059 | 1.0211 | -0.014525 | -0.033128 | -0.045174 | -0.059512 | -0.011204 | -0.0024726 | -0.49282 | 1.1265 | -0.035741 | -0.68993 | 0.18128 | -0.17498 | -0.10331 | -0.065016 | -0.03241 | -0.044595 | -0.052189 | -0.052189 | 0.068628
S-2 | 2 | Narinda 132/33KV S/S | 2 | 0.43798 | 0.46529 | 0.072982 | -0.12873 | 0.097439 | 0.27758 | 0.34146 | 0.18724 | 0.023429 | 0.16366 | -0.20409 | 0.19951 | -0.13414 | 0.51525 | 0.14421 | 0.2041 | 0.28465 | 0.75153 | 0.34867 | 0 | 0.41295 | 0.26402 | -0.01317 | 0.026963 | 0.21626 | 0.61166 | 0.83844 | 0.77556 | 0.53796 | 0.34 | 0.12324 | -0.45121 | 0.23234 | 0.45507 | 0.19128 | 0.01618 | 0.16072 | 1.1009 | -0.15848 | 0.52697 | 0.11273 | 0.77314 | 0.89326 | -0.22975 | -0.67804 | 0.26862 | -0.48303 | 0.82395 | 0.81861 | 1.5308 | 0.88014 | 0.351 | 0.1733 | -0.10695 | 0.22127 | 0.28504 | -0.3759 | 0.060632 | 0.87124 | 0.34897 | 0.36451 | 0.46142 | 0.30905 | -0.42609 | 0.42587 | -0.045884 | -0.16184 | 0.11474 | -0.060131 | 0.98443 | -0.74528 | -1.3596 | 2.3313 | 0.59004 | 0.49071 | -0.047852 | -0.099859 | -0.10684 | 0.22582 | 0.017924 | 0.0060938 | -0.26208 | -0.14339 | -0.054058 | 0.01794 | 0.20391 | 0.097735 | 0.23983 | 0.29409 | -0.23209 | 0.47309 | 0.38928 | 0.58176 | 0.52261 | 0.20772 | 0.24897 | 0.079044 | 1.449 | 0.62482 | 1.0295 | 0.89532 | 0.25296 | -0.16431 | -0.056942 | 0.28197 | 0.48332 | -1.3533 | 0 | -0.14133 | -0.11016 | 0.14804 | 0.2518 | -0.22305 | 0.18804 | 0.27922 | 0.3776 | 0.15075 | 0.18311 | 0.67214 | -0.079002 | 0.21529 | 0.1851 | 0.22398 | 0.41177 | -0.28741 | -0.32117 | -0.099643 | -0.24037 | 0.13802 | 0.29612 | 0.068599 | 0.031416 | 0.55079 | 0.68755 | 0.31115 | 0.47529 | 0.41371 | 0.35109 | 0.082596 | 0.1766 | 0.19476 | 0.77142 | 0.76272 | 0.74278 | 0.81122 | 0.8225 | 0.25064 | 0.64774 | 0.22525 | 0.26051 | 0.24639 | 0.21992 | 0.08863 | 0.3517 | 0.19
S-2 | 3 | Narinda 33/11KV S/S | 3 | 1.6124 | 0.86739 | 0.8161 | 0.38685 | 0.20935 | 0.6 | 0.96825 | -0.7239 | 0.20745 | -0.58769 | 0.52955 | 0.55137 | 1.9689 | 2.4326 | 0.90687 | 1.265 | 0.98497 | 0.040492 | 1.1605 | 0 | 0.32885 | 1.1721 | -0.057261 | 0.50165 | 0.40371 | 0.56536 | 0.69159 | 0.52058 | 0.72396 | 0.37 | -0.37007 | -0.18316 | 0.4253 | 1.0968 | 0.74782 | 0.95656 | 0.83102 | 1.2166 | 1.2501 | 0.555 | 0.50559 | 0.3627 | 1.1497 | 1.9275 | 3.5061 | 1.9 | 1.8 | 1.5 | 1.4958 | 1.9598 | -0.40755 | 0.03137 | 0.74748 | 0.49766 | 0.21244 | 0.009187 | 0.54247 | 0.22664 | 0.27917 | 0.20222 | 0.41829 | 2.6716 | 6.3055 | -0.10715 | -0.84951 | 0.10977 | -0.33691 | -1.198 | 1.6922 | -0.64543 | 1.5015 | -0.86641 | 2.0234 | -3.0547 | 1.4833 | 0.51665 | -0.21467 | -1.0609 | 0.60983 | 0.0019189 | 0.36169 | 0.51737 | 0.78653 | 0.80539 | 0.79637 | -0.9213 | 2.3589 | 0.42953 | -0.13572 | 0.25236 | 1.759 | 1.3521 | 1.1014 | 1.5297 | 1.0939 | 0.89993 | 0.49529 | 2.6841 | 1.8057 | -0.024357 | 0.10589 | 1.776 | 0.60775 | 0.91964 | 1.4296 | 1.8054 | 0.049634 | 1.2566 | 1.455 | 0.42091 | 0.96089 | 0.74675 | 0.61579 | 1.2128 | 1.3016 | 1.4923 | 1.091 | 1.4735 | 0.52321 | 1.8272 | 0.99546 | 0.97443 | 1.1331 | 0.73848 | -0.49275 | -0.36083 | 0.11867 | 0.022377 | -0.32591 | 0.62296 | 0.74793 | 1.3395 | 0.99161 | -0.30805 | 1.9642 | 1.8003 | 2.0486 | 1.8518 | 1.4414 | 1.2746 | 1.9596 | 1.3218 | 0.98177 | 0.98154 | 1.0814 | 0.6725 | 1.7322 | 2.0045 | 2.0018 | 1.8277 | 1.7587 | 1.8247 | 1.7042 | 1.7397 | 1.6525 | 1.5069 | 1.5941 | 0.059921 | 0.65905 | 0.40703 | 0.55627 | 1.1025 | 0.71624 | 1.9011 | 0.43652 | 0.28177 | 0.4169 | 0.29672 | 1.0543 | 1.0543 | 0.33618
S-2 | 4 | Kumertuly 33/11KV S/S | 4 | 0.12121 | 1.2983 | 1.4741 | 0.42673 | 1.749 | 0.84921 | -0.23825 | 0.77499 | 0.090594 | 0.61997 | 1.5296 | 1.0889 | 0.10128 | 1.908 | 0.80106 | 1.8548 | 0.5971 | 0.25467 | 1.6878 | 1.8513 | 2.2467 | 0.81456 | 0.49175 | 0.63095 | 0.54797 | 2.0085 | 2.4496 | -0.80833 | -0.42726 | 0.55 | 0.82825 | 0.31964 | 0.3777 | 0.7939 | 0.051406 | 0.99449 | 1.7311 | 1.2675 | 1.6171 | 0.049326 | 1.4678 | 0.55851 | 0.88294 | 0.51015 | -0.35698 | 0.70915 | 0.511 | 1.8611 | -0.043527 | 0.52988 | 1.9 | 1.8655 | -0.14589 | 0.90577 | 0.38433 | 1.7314 | 1.2112 | 1.3528 | 1.097 | 0.43706 | 0.45172 | 0.56001 | 0.46816 | 1.1422 | 1.178 | 1.9549 | 1.0108 | 2.0675 | -0.22366 | 0.34664 | 1.3952 | 1.0593 | 3.8137 | -0.07619 | 2.0716 | -0.67494 | 2.7382 | -1.9719 | 1.28 | 0.73089 | 0.87196 | 0.93024 | 0.80493 | 0.46411 | 1 | 0.93343 | 1.0022 | 0.91455 | 0.80743 | 1.2675 | 1.1584 | 0.41159 | 1.0176 | 0.63839 | 0.7562 | -0.99225 | 2.0676 | 3.754 | 0 | 0.74581 | 0.6829 | 0.3315 | 0.17381 | -1.0601 | 1.2498 | -1.6505 | 3.3256 | 2.1277 | 0.82351 | 0.47563 | 0.82606 | 0.74218 | 1.0514 | 1.4362 | 1.3776 | 1.2871 | 1.2318 | 1.3337 | 1.5511 | 0.4407 | 0.79195 | 0.61535 | 0.65498 | 1.051 | 2.9525 | 0.7308 | 0.91257 | 0.75365 | 1.2595 | 1.3264 | 1.4007 | 1.0202 | 1.5201 | 1.512 | 1.0468 | 1.2291 | 1.2375 | 1.0225 | 1.048 | 0.86711 | 1.5389 | 2.0907 | 1.5423 | 1.4977 | 1.6186 | 1.4178 | 0.95942 | 1.3961 | 0.77259 | 0.91843 | 1.019 | 1.0288 | 0.82218 | 1.2668 | 1.0127 | 1.0021 | 0.78197 | -0.97017 | -0.18085 | -0.45085 | -0.5209 | 0.23848 | -0.20467 | 0.055656 | -1.0278 | -0.85644 | -0.77715 | -1.1905 | -1.3897 | -1.3897 | -0.65374
S-2 | 5 | Maniknagar 132/33/11KV S/S | 5 | 0.8465 | 0.39872 | 0.63655 | 0.8671 | -0.17336 | 0.33649 | -0.70506 | 0.89285 | 0.65196 | 0.44962 | 0.34956 | 0.35881 | 0.24779 | -0.12414 | 0.23336 | 0.19434 | 0.51345 | 0.5175 | -0.039241 | -0.012556 | 0.3 | 0.42616 | 0.32519 | 0.29499 | 0.22474 | -0.024107 | 0.56836 | 0.20677 | -0.18904 | 0.4 | 0.49967 | 0.18293 | -0.15264 | 0.77788 | 0.81913 | 0.63673 | 0.036306 | 0.60405 | 0.65448 | 1.699 | 0.038827 | 0.48227 | 0.79342 | 1.0467 | -0.1882 | 0.17859 | 0.40728 | 0.76228 | 0.84199 | 1.2802 | 0.92998 | -0.15134 | 0.026185 | 0.73217 | 0.65794 | 0.46373 | 1.4656 | 0.77887 | 0.4879 | 0.29551 | -0.45708 | 0.98149 | 0.1858 | 0.1509 | 0.27753 | 0.35226 | 0.50351 | 0.31521 | 0.33446 | 0.023469 | -0.74914 | 0.75345 | 0.96498 | 1.1069 | 0.1761 | 0.53035 | -0.49378 | 0.55048 | 0.83676 | 0.40532 | 0.37033 | 0.2 | 0.6437 | 0.2 | 0.38556 | 0.20845 | -0.45491 | 0.31686 | 0.33763 | 0.099978 | 0.73899 | -0.021967 | 0.2 | 0.2 | 0.2 | -0.10782 | 0.5 | 1.6311 | 0 | 0 | 0 | 0.25157 | 0.068098 | 0.12832 | 0.36571 | 0.1187 | 0.19578 | 0.39084 | 0.1548 | 0.16141 | 0.21336 | 0.4532 | 0.15465 | 0.13594 | -0.084821 | 0.69447 | 0.60359 | 0.86041 | 0 | 0.2206 | 0.30789 | 0.24266 | 0.18219 | 0.30848 | 0.19884 | 0.26355 | 0.25719 | 2.8359 | -1.4552 | 0.27206 | 0.31435 | 0.25939 | 0.25792 | 0.26414 | 0.1943 | 0.19631 | 0.099908 | 0 | 0 | 0 | 0 | 0.2079 | 0.12149 | 0.26341 | 0.2006 | 0.48575 | 0.2961 | -0.034045 | 0.030727 | -0.048506 | 0.56045 | -0.14122 | 0.19691 | 0.19542 | 0.23587 | 0.25486 | 0.20101 | 0.26471 | 0.26314 | 0.23492 | 0.20951 | 0.19748 | 0.2363 | [6 empty] | -1.4845 | 5.0514
S-2 | 6 | Maniknagar 33/11KV S/S | 26 | 0.91224 | -0.053456 | 0.67465 | 1.0763 | -0.17066 | 0.51153 | 0.26377 | 0.74889 | 0.84096 | 0.058436 | 0.48763 | 0.46874 | 0.29581 | -0.32498 | 1.3241 | 1.7938 | 2.2817 | 2.2381 | 2.0307 | 0.86448 | 0.18868 | 1.0006 | 0.88892 | 1.2469 | 0.69046 | 0.38498 | 1.2623 | 0.20785 | 0.16831 | 1.25 | -0.0044279 | 1.4206 | 0.18835 | 2.0281 | 6.0251 | -0.6196 | 0.8739 | 2.3695 | 2.3844 | 2.8089 | 1.7283 | 4.8311 | 5.1039 | 5.7737 | 3.5 | 3.0025 | 5.1674 | 5.201 | 4.9107 | 5.4317 | 5.8071 | 4.5765 | 5.1497 | 6.2047 | 1.1067 | 0.95102 | 8.4269 | 7.9663 | 3.249 | 0.56422 | -0.21344 | 1.5896 | 0.89618 | 1.8407 | 0.2642 | 1.9022 | 0.49451 | 1.8634 | -2.3329 | -2.0522 | 0.024861 | 0.54196 | 1.2598 | 1.1586 | 1.4581 | 0.23978 | 2.1331 | 4.4335 | 8.6452 | 0.68915 | 2.0264 | 0.086501 | -0.65366 | 0.78569 | 0.90664 | 1.3622 | 0.08392 | 0.99373 | 0.94274 | 0.49505 | 1.2449 | 0.18795 | 0.87805 | 0.91424 | -0.17532 | 2.6141 | 2.3975 | 0.30714 | 2.4 | 2.7968 | 0.10404 | -0.56444 | -0.30855 | -0.24719 | -0.10735 | -0.25023 | 0.091927 | 0.20453 | 0.38125 | 0.43751 | 0.51337 | 0.75249 | 0.36516 | 0.4308 | 0.19784 | 0.92457 | 0.90761 | 1.0876 | 0.17924 | 0.39524 | 0.45367 | 0.56879 | 0.32381 | 0.40777 | 0.46195 | 0.31133 | 0.35265 | 3.2293 | -2.6331 | 0.5716 | 0.33476 | 0.31466 | 0.37644 | 0.25599 | 0.22281 | 0.30494 | 0.16324 | -0.04333 | 0.01031 | -0.59768 | -0.30992 | 2.4583
N-2 | 7 | Madarteck 132/33KV S/S | 6 | -0.052407 | -0.16535 | 0.39532 | 0.024309 | 0.12323 | -0.12167 | 0.1339 | -0.045535 | -0.81566 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0363 | 0.10729 | -0.36564 | -0.13196 | 0.068308 | 0.16335 | 0.10815 | -0.092582 | -0.093632 | 0.11384 | 0.28773 | -0.013267 | -0.13565 | -0.23699 | 0.57 | -0.39504 | 0.094253 | 0.066169 | 0.26963 | 0.49409 | 0.38288 | -0.18944 | -0.18675 | -0.54225 | -0.34937 | 0.028509 | 0.30257 | 0.33454 | 0.51078 | 0.1 | 1.3283 | -0.17536 | 0.15956 | 0.18962 | 0.2352 | 0.23267 | 0.285 | 0.26522 | 0.27806 | 0.36985 | 0.23977 | 0.27564 | 0.26389 | 0.22966 | 0.25478 | 0.24822 | 0.020926 | 0.30853 | -0.68031 | -0.14284 | -0.11468 | -0.097031 | -0.20562 | -0.26421 | -0.34949 | -0.49283 | 0.20768 | -0.58063 | -0.68491 | 0.60032 | 0.15222 | 0.16347 | -3.3967
N-2 | 8 | Madarteck 33/11KV S/S | 7 | 1.1191 | 0.70127 | 1.8368 | 2.4725 | 2.5445 | 2.3505 | 2.8384 | 2.5009 | 1.6991 | 2.061 | 2.2343 | 2.3384 | 2.3471 | 2.0476 | 2.338 | 0.32346 | 2.268 | 2.422 | 1.9834 | 2.7392 | 2.971 | 1.8349 | 2.1674 | 2.1647 | 1.5 | 1.8315 | 2.4275 | 2 | 3.4948 | 3.16 | 2.0348 | 3.5083 | 1.8489 | 2.9357 | 1.692 | 3.0069 | 3.8869 | 2.8056 | 1.3003 | 2.6145 | 2.3911 | 1.6173 | 1.7123 | 0.36356 | -1.6244 | 0.41128 | 2.8169 | 2.9412 | 0.46282 | 0.2 | 0.3 | 0.91537 | 1.0715 | -0.5 | -0.54746 | 1.6971 | 1.3282 | 0.63688 | 1.1825 | 0.25207 | 0.5627 | 1.1643 | 0.8878 | 1.8421 | 3.4313 | 3.6542 | 3.3827 | 2.815 | -4.7389 | 2.9856 | 2.5445 | 3.8768 | 3.6738 | 3.4806 | 2.5195 | 1 | 4.4326 | 0.12596 | 3.127 | 3.3861 | 0.38083 | 1.0552 | 3.3209 | 3.0238 | 2.3597 | 0.01 | 2.7202 | 2.768 | 2.5543 | -3.171 | 1.4836 | 1.9375 | 2.2103 | 1.3028 | 3.68 | 1.7489 | 0.93566 | 2.2068 | 1.2747 | 1.7484 | 1.5816 | 1.2282 | 2.8269 | 0.58919 | 1.0365 | 0.62728 | 3.5402 | 2.2578 | 1.9508 | 1.747 | 1.9984 | 1.791 | 2.4425 | 1.816 | 1.6986 | 1.4769 | 1.4913 | 1.5113 | 1.2466 | 1.3576 | 1.4447 | 2.3601 | 2.8194 | 1.8849 | 2.2542 | 3.2169 | 2.5418 | 5.1853 | 0.52849 | 2.4401 | 2.3862 | 2.5792 | 2.2764 | 1.4066 | 2.2247 | 2.2036 | 2.3573 | 2.134 | 2.1358 | 2.0088 | 2.5038 | 1.399 | 1.5126 | 1.7273 | 1.8479 | 1.928 | 1.5006 | 1.3194 | 1.5004 | 1.3136 | 2.0247 | 1.3249 | 1.7701 | 1.8555 | -0.62279 | 3.5516 | 3.5893 | 3.7896 | 5.7014 | 5.3954 | 2.5356 | 2.9877 | 3.7441 | 3.3541 | 5.0423 | 3.7989 | 3.7477 | 2.5213 | -1.4845 | 2.0541 | 1.9174
S-2 | 9 | Kazla 132/133 KV SS | 39 | 0.11379 | -0.053418 | 0.10914 | -0.34202 | 0.21123 | -0.44316 | 0.091713 | 0.079264 | 0.16754 | 0.06802 | 0.25021 | -0.11308 | 0.080583 | 0.32956 | 0.23486 | 0.24708 | 0.25654 | 0.057594 | 0.02325 | 0.17063 | 0.47777 | -0.63294 | 0.20279 | 0.3172 | 0.31467 | 0.70816 | 0.58514 | 4.7155
S-2 | 10 | Kazla 33/11KV S/S | 8 | 1.6094 | 1.6006 | 1.6954 | 2.5664 | 2.4702 | 1.8188 | 2.6914 | 2.6103 | 2.5 | -0.10251 | 2.2151 | 1.5173 | 2.7244 | 2.5553 | 1.4741 | 1.5064 | 2.5483 | 1.3816 | 1.2126 | 0.093689 | 1.5397 | 1.915 | 1.5815 | 1.5509 | 0.98444 | 1.8965 | -0.27365 | 2.2264 | 2.0027 | 1.3 | 1.5572 | 1.4028 | 2.1769 | 1.2884 | 2.6372 | 2.6033 | 1.5329 | 2.3391 | 1.7183 | 1.6582 | 0.72972 | 1.6627 | 2.564 | 2.2071 | 3.0207 | 3.2514 | 2.8169 | 1.9933 | 3.2492 | 1.7544 | 2.0415 | 0.48759 | 0.33587 | -0.6053 | 1.0316 | 0.63888 | 2.6913 | 1.2072 | 1.02 | 0.92138 | 0.43407 | 2.8588 | 0.47585 | 2.5888 | 0.53463 | 1.0269 | 2.1722 | 1.2641 | 2.0485 | 1.1637 | 3.3248 | -0.78306 | 5.6928 | 6.6384 | -1.8357 | 1.1829 | 0.49848 | 1.1307 | 2.325 | 2.1303 | 1.9365 | 3.3105 | 1.0435 | 0.041551 | 0.037093 | 0.03604 | 1.5094 | 0.15234 | 1.3558 | 0.26759 | 3.0815 | -0.013339 | 3.178 | 2.7404 | 2.0791 | 1.1675 | 1.811 | 2.6008 | 3.989 | 1.6088 | 0.51247 | 4.4029 | 0.82739 | 1.6674 | 0.62203 | -2.6691 | 3.798 | 1.5133 | 2.321 | 0.30325 | 2.3391 | 1.7674 | 3.9156 | 1.6986 | 2.5411 | 2.4563 | 3.8077 | 1.181 | 2.6398 | 3.2168 | -0.54481 | 0.013495 | -0.72543 | -0.047022 | 0.94572 | 1.336 | 2.9378 | 4.2639 | 0.18 | -0.073044 | 3.3303 | 3.6033 | 4.1208 | 3.3011 | 3.4968 | 1.6533 | 1.4294 | 1.8053 | 1.8776 | 2.3886 | 3.1575 | 2.4345 | 2.8199 | 2.702 | 2.4275 | 6.2464 | 3.2743 | 1.438 | 2.0404 | 2.008 | 2.8377 | 3.1645 | 3.3341 | 2.9881 | 3.2786 | 3.1168 | 2.6508 | 1.8806 | 1.6159 | 2.8698 | 4.2254 | 2.9722 | 3.4363 | 4.1317 | 4.3914 | 3.587 | 4.2658 | 2.3112 | 2.0541 | 0.56145 | -0.71885
S-2 | 11 | Shyampur 132/33KV S/S | 9 | 0.046574 | 0.061583 | 0.089319 | -0.10382 | 1.3732e-14 | 2.8117 | 0.32081 | 0.46208 | 0.14047 | 0.21103 | 0.38635 | 0.6047 | 0.50975 | 0.43264 | 1.1551 | 0.041438 | 1.2277e-14 | 0.1498 | 0.2164 | 0.22821 | 0.44726 | 0.8109 | 0.047133 | 1.0815 | 0 | 0.94321 | 1.2384 | 0.6801 | 0.95288 | 0.28 | 0.59945 | 0.11106 | 0.12703 | 0.36914 | 0.66602 | 0.48347 | 0.61459 | 0.30171 | 0.5151 | -0.082697 | 0.40853 | 0.49733 | 0.30329 | 0.52569 | 0.54987 | 1.3697 | 0.93456 | 0.4477 | 0.92301 | 0.83208 | 0.18646 | 0.29731 | 0.12844 | 1.1142 | 0.97162 | 0.22007 | 0.5063 | 0.74975 | -0.038177 | 0.44324 | 0.079475 | 0.84677 | 0.74296 | 0.25996 | 0.14766 | 0.55473 | 0.33275 | 1.415 | -0.554 | 0.89567 | 0.30067 | -0.6948 | 1.7553 | -0.015566 | 0.1 | 0.01 | -0.011679 | 0.91956 | -0.098665 | -0.493 | 0.016172 | 0.2216 | 0.25684 | 0.1 | 0.01 | 0.01 | 0.2 | 0.23416 | 0.26209 | 0.26311 | -0.91322 | 0 | 0 | 0.10363 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | -0.21665 | 0.17256 | -0.3837 | 0.19768 | 0.038976 | 0.12129 | 0 | -0.030113 | -0.036613 | -0.31134 | 0.017413 | 2.5567 | -3.2171 | -0.667 | 0.1723 | 0.021345 | -0.20739 | 0.073597 | 0.53092 | 0.25476 | 0.050428 | 0.37524 | 0.28143 | 0.59672 | 0.062374 | 0.32592 | 0.055709 | 0.45373 | -0.19024 | 0.76897 | -0.28522 | 0.045933 | -0.24128 | -0.45448 | -0.038466 | -0.18078 | 0.20117 | 0.2218 | 0.21541 | -0.099249 | -0.040581 | 0.28405 | -0.36672 | -0.36528 | -0.021147 | 0.74217 | 0.30717 | 0.19259 | 0.094163 | 0.016216 | -0.33956 | -0.31759 | 0.56145 | 7.0602 | 19.5017
S-2 | 12 | Shyampur 33/11KV S/S | 10 | 0.55024 | 0.11648 | 0.18794 | -0.043009 | 1.3039 | 0.021094 | -0.14439 | -0.046802 | 0.073091 | 0.33017 | 2.1993 | -0.041543 | 0.18882 | 0.6323 | 0.23634 | -0.37588 | 1.7938 | 0.808 | 0.0033864 | 0.63558 | 1.3231 | -0.15316 | 1.2005 | 1.4301 | 0.24345 | 1.1124 | 1.6849 | 0.79605 | 0.89182 | 0.49 | 0.5775 | 0.77526 | -0.12024 | -0.29291 | 0.5896 | 1.0102 | 0.97797 | 2.2348 | 0 | 0.85705 | 0.75451 | -1.1995 | 2.9296 | 0.98334 | 1.2676 | 1.7845 | 0.99783 | 1.4701 | 1.7219 | 0.12211 | 0.56455 | 1.7848 | 1.2319 | 2.0379 | 0.68377 | 1.9373 | 1.7887 | 1.0219 | -0.20469 | 1.0251 | 0.21752 | 0.14996 | 1.9523 | 2.2047 | 1.096 | 1.3055 | 1.6454 | 1.4223 | -0.21587 | 0.25502 | 2.54 | 0.62064 | 1.2801 | 0.82867 | 1.4162 | 2.621 | 0.35219 | 2.9217 | 3.4946 | 2.5495 | 0.6726 | 1.4608 | -0.25189 | 2.6287 | -0.19393 | 1.2898 | 0.8072 | 1.385 | 2.9357 | 0.82875 | 3.051 | 2.1091 | 2.7509 | 1.9183 | 2.5139 | 1.6818 | 1.9351 | -0.18177 | 1.0977 | 0.27519 | 2.0062 | 2.3956 | -0.14018 | 0.46754 | 0.17817 | 0.45506 | 0.40835 | 0.17945 | 0.10036 | 0.46909 | 1.175 | 0.45309 | 1.0116 | 1.2424 | 1.9376 | 0.13809 | 0.38683 | 1.0431 | -0.51834 | 0.76806 | 0.492 | 0.43406 | 1.0293 | 0.012492 | 0.58166 | 0.60231 | 1.5302 | 4.5447 | -0.21793 | 1.1125 | 0.76278 | 0.51032 | 3.3231 | -0.68905 | 1.1097 | 0.87853 | -0.080214 | 1.1996 | 1.7961 | 1.8603 | 1.6056 | 1.957 | 1.116 | 1.0788 | 1.0788 | 0.73244 | 0.039948 | 0.24627 | -0.20472 | 0.21662 | 1.0097 | 0.693 | 1.6073 | 1.2813 | 2.4271 | 2.7071 | 3.6341 | 2.6462 | 3.3712 | 2.5272 | 3.4492 | 4.0943 | 7.7968 | 3.9063 | 3.979 | 4.1641 | 3.7755 | 4.3646 | 7.0602 | 3.4926 | 7.3347
S-2 | 13 | Shyampur BISIC 33/11KV S/S | 11 | -0.75983 | -2.9769 | -2.2715 | 0 | -0.066511 | -0.30737 | 0.5914 | -0.43053 | -0.8828 | 0.14746 | -0.49544 | -0.18561 | -0.24974 | 1.2179 | 0.14363 | 0.33812 | 0.7625 | 1.8535 | -0.84759 | 2.0779 | 1.516 | 0.76561 | 1.0655 | 2.7182 | -0.48385 | 2.1023 | 2.419 | 1.8226 | 2.3588 | 0.96 | 1.3403 | -0.28984 | 0.27354 | -0.78744 | 0.52688 | 1.9107 | -1.349 | -2.2236 | -1.5366 | -1.8727 | -0.76007 | 2.4229 | 0.035332 | 2.2937 | 1.14 | 4.5501 | 3.5082 | 3.3476 | 4.4243 | -1.3825 | 3.7088 | 1.5298 | 1.9796 | 2.1945 | -0.86536 | 1.8978 | 0.94038 | 0.84946 | 1.2087 | 1.1569 | 0.64125 | 1.7619 | 0.1805 | 1.9113 | 0.39439 | -1.4801 | 1.363 | 2.346 | 1.538 | 1.0881 | 1.0661 | 0.24561 | 2.6405 | 0.92898 | 0.97554 | 0.53829 | 0.90395 | 1.8993 | 0.4897 | 0.49473 | 1.1099 | 0.82588 | 1.5252 | 0.85553 | 0.94414 | 0.5 | 1.0041 | 0.97951 | 0.11899 | 0.56668 | 1.9139 | 1.0336 | 0.69534 | 0.81394 | 1.1414 | 1.117 | 1.2299 | 1.2962 | 0.86757 | 1.2094 | 1.274 | 0.98042 | 1.0193 | 1.3059 | 1.2335 | 1.3019 | 1.4115 | 1.1828 | 2.59 | 1.6779 | 0.83051 | 1.0878 | 1.3579 | 0.97236 | 1.3773 | 0.81831 | 0.87198 | 1.2565 | 0.26657 | 1.2561 | 1.0018 | 1.0935 | 1.2963 | 1.0092 | 0.30602 | 2.1698 | 0.97036 | 3.6675 | -1.7741 | 0.34733 | 0.76344 | -0.16099 | 1.7704 | 2.7811 | 1.56 | -0.44933 | 0.99268 | 1.3607 | 1.3211 | 1.6061 | 1.0364 | 2.7687 | -0.45632 | 1.445 | 0.70601 | 1.8861 | 0.88156 | 2.3294 | 1.0532 | 0.041307 | 1.745 | 0.85926 | 1.2445 | 3.6855 | 1.2478 | 5.3063 | 2.961 | 4.9875 | 3.2458 | 1.3043 | 1.5177 | 1.9231 | 3.2281 | 3.3257 | 1.74 | 1.279 | 0.93856 | 2.0147 | 3.4926 | -2.7762 | 3.4016
S-2 | 14 | Postogola 132/33 KV S/S | 43 | -0.030239 | -0.069867 | -0.076128 | 0.79042 | 0.30206 | 0.34498 | 0.27345 | 0.33441 | 0.26633 | 0.14804 | 0.12875 | 0.1517 | 0.123 | 0.53542 | 0.61108 | 0.11946 | 4.3536
S-2 | 15 | Postogola 33/11KV S/S | 12 | 0.24136 | 0.23622 | 0.26724 | 0.45712 | 2.1271 | 1.2959 | 0.67797 | 1.0831 | 0.20018 | 0.049934 | 0.29946 | 0.37918 | 0.11597 | 0.57623 | 0.20671 | -0.0030855 | 0.40242 | 0.95349 | 1.7974 | 1.044 | 1.9546 | 0.98204 | 0.79262 | 2.5738 | -0.6562 | 1.6496 | 1.48 | 3.6261 | 0.1579 | 0.93 | 2.0148 | 1.4242 | 0.35452 | 1.7418 | 2.9741 | 1.6042 | 2.0456 | 1.7729 | 1.4218 | 1.0208 | 2.6986 | 1.8103 | 1.8718 | 1.1561 | -1.1198 | 2.2154 | 2.339 | 3.9844 | 0.81359 | 1.8067 | 2.3529 | 4.2433 | 2.1917 | 3.1803 | 0.39475 | 1.8815 | 0.65042 | 1.1063 | 1.3685 | 0.21485 | 0.18232 | 0.16501 | 0.2052 | 0.18905 | 0.15201 | 0.18275 | 1.1868 | 2.2321 | 0.27924 | 1.6019 | 0.80218 | -0.19827 | 2.264 | -0.015566 | 0.6005 | 0.51005 | 0.48826 | 0.02 | 0.14356 | -0.28085 | 0.51625 | 0.56155 | 1.2478 | -0.25834 | -0.45 | -0.45 | 1.9139 | 0.74284 | 2.4636 | 1.1271 | -0.12288 | 1.0592 | 0.85491 | -2.0429 | 1.0386 | 1.2311 | 1.1641 | -0.54753 | 2.6824 | -0.23623 | 0.98366 | 1.0252 | 0.13093 | 1.1206 | 1.1645 | 1.1859 | 3.3767 | 1.1783 | 1.7371 | 1.2091 | 1.1287 | 1.0373 | 1.2494 | 1.2112 | 1.0701 | 0.8908 | 0.63226 | -0.79803 | -0.16422 | 2.0065 | 0.5407 | 0.28 | -0.081863 | 2.1812 | 0.43263 | 0.75525 | 1.1454 | 3.5652 | -1.7517 | 0.45131 | 1.3799 | -0.37128 | 2.4599 | -0.32855 | 1.3354 | -0.71487 | -0.063214 | 0.10349 | 0.54111 | 0.023393 | 0.9778 | 1.4953 | 0.87207 | 0.95631 | 0.13425 | -0.033126 | -0.24274 | -1.4551 | -0.91408 | 0.46814 | -0.95581 | -0.17018 | -0.84162 | 0.61799 | 0.43735 | -0.011038 | 0.084468 | 1.1749 | 2.1259 | 3.8987 | 0.66835 | 1.9587 | 1.3873 | 1.5344 | 1.5401 | 1.2068 | 8.9469 | 7.7188 | -2.7762 | 2.7987 | 2.7468
S-1 | 16 | Fatullah Old 33/11KV S/S | 13 | -1.237 | 0.074395 | 0.18564 | 1.648 | 0.38107 | 0.88945 | 0.10682 | 0.27655 | 1.1647 | 0.55164 | 0.30021 | 0.56409 | 0.53436 | 0.37216 | -0.051061 | 0.36997 | 0.30596 | 0.65664 | 0.0070571 | -0.41038 | 1.0476 | 0.22592 | 0.088594 | 0.85504 | -0.23149 | 0.86898 | 0.22759 | -0.15044 | 0.4821 | 0.02 | -0.17697 | -0.37517 | 1.5284 | 1.2385 | 0.87375 | 0 | -0.74901 | 0.80792 | 1.1846 | 0.40801 | 1.0329 | 1.0103 | 2.001 | 2.2622 | 3.5043 | 2.8983 | 2.2596 | 2.5 | 1.5 | 2.299 | 3.971 | 2.7291 | 1.5073 | 2.5483 | 1.5612 | 1.3934 | 1.7607 | 2.1469 | 1.3732 | 0.63092 | 0.64133 | 2.297 | 0.80026 | 2.6168 | 1.9681 | 2.0765 | 1.8361 | 2.0779 | 3.8201 | 1.1643 | 1.5849 | 1.5941 | 2.2958 | 1.9495 | 2.0773 | 2.5044 | 1.7358 | 1.1752 | -0.6892 | 2.753 | 1.3196 | 3.004 | 1.407 | 3.8985 | 0.62865 | -0.013154 | 2.5594 | 2.2695 | 0.97922 | 2.2719 | 2.3193 | 1.9276 | 4.0242 | 2.6398 | 2.1901 | 2.0665 | 2.9982 | 2.7715 | -1.5227 | 2.3117 | 2.0258 | 0.99212 | 3.9174 | 0.45044 | 2.1127 | 1.9415 | 1.5408 | 2.0566 | 1.4224 | 1.4911 | 1.5633 | 1.7204 | 1.3806 | 0.87641 | 1.132 | 1.4371 | 1.6365 | -0.12189 | 1.6284 | 2.9555 | 2.6145 | 0.59633 | 2.3017 | 1.7397 | 1.1112 | 1.3948 | 2.094 | 4.8749 | -0.5037 | 2.2677 | 2.7993 | 1.0119 | 4.3115 | 1.1212 | 2.7517 | 2.4969 | 1.1728 | 2.9269 | 1.957 | 2.1758 | 1.955 | 1.8679 | 2.0207 | 2.4881 | 2.5875 | 1.9358 | 3.6753 | 3.1859 | 2.6817 | 1.3643 | 4.7947 | 3.9781 | 1.1914 | 1.6387 | 3.5456 | 3.6035 | 3.5072 | 1.2469 | 4.0091 | 3.1469 | 2.6276 | 3.8266 | 3.1615 | 2.8226 | 2.98 | 2.4634 | 1.6593 | 3.3252 | 2.7987 | -1.6331 | -1.338
S-1 | 17 | Sitalakhya 132/33KV S/S | 14 | 0.074935 | 0.090376 | 0.025451 | 0.016298 | -0.34327 | 0.080748 | 0.064266 | 0.18358 | 0.1352 | 0.080802 | 0.19231 | 0.11332 | 0.17413 | 0.44192 | 0.37264 | 0.16934 | 0.22178 | -0.023485 | -0.023215 | 0.10721 | 0.019406 | 0.025622 | 0.016956 | 0.087997 | -0.039618 | 0.052092 | 0.032614 | 0.063475 | 0.094415 | 0.04 | -0.39417 | -0.10237 | -0.14836 | 0.14419 | 0.13896 | 0.082914 | 0.11766 | -0.097194 | -0.11611 | -0.030302 | -0.21854 | 0.20067 | -0.084602 | 0.16209 | 0.25726 | 0.37804 | 0.35783 | 0.014531 | 0.33333 | 0.92326 | 0.4021 | 0.095154 | 0.079401 | -0.48785 | -0.98314 | 1.5136 | 1.0568 | 0.19438 | 0.1436 | 0.051826 | 0.90602 | 0.67406 | -0.38051 | 0.35874 | -1.3962 | 0.11021 | 0.16839 | 0.19176 | 0.43846 | 0.19502 | 0.0079818 | 0.11098 | -0.097922 | 0.084705 | -0.19809 | 0.44411 | -0.16866 | -0.31065 | 0.035163 | -0.072082 | 0.21558 | 0.27844 | -0.72692 | 0.11191 | -0.67645 | 0.1875 | 0.10023 | 0.12588 | 0.1153 | 0.20193 | 0.35275 | -0.084806 | 0.12691 | 0.13701 | 0.018194 | 0.1125 | -0.065001 | 0.056758 | 0.53105 | -0.11707 | 0.16048 | -0.083799 | 0.094296 | -0.55238 | 0.18799 | 0.20777 | 0.10989 | -0.62596 | 0.26727 | 0.16316 | 0.12811 | 0.18082 | 0.072485 | 0.17156 | 0.27235 | 0.12068 | -0.30213 | 0.53074 | 0.18102 | 0.15682 | 0.18412 | 0.22276 | 0.10864 | 0.18555 | 0.1712 | 0.21357 | -0.008389 | 0.014114 | 0.075935 | 0.03968 | 0.14558 | 0.025169 | 0.0031906 | -0.0037119 | 0.081978 | 0.017043 | 0.063792 | 0.0189 | 0.15613 | 0.12427 | 0.075261 | 0.12801 | -0.076314 | -0.076371 | -0.06155 | -0.044993 | -0.059491 | 0.49767 | -0.21726 | 1.0249 | -0.025173 | 0.72725 | 0.091644 | -0.73887 | 0.31664 | 0.35968 | 0.31936 | 0.31559 | -0.19747 | 0.44025 | -2.5641 | 0.18205 | -0.41169 | -0.11765 | -0.034062 | -0.38739 | -4.29 |  |  | -3.0919 | 4.7394 | PT FUSE OFF june
S-1 | 18 | Sitalakhya 33/11KV S/S | 15 | 0.29099 | 0.082024 | 0.2243 | 0.28276 | -0.34218 | 0.49252 | 0.17829 | 0.355 | 0.17321 | 0.33195 | 0.054544 | 0.26017 | 0.24309 | 0.25865 | 0.54077 | 0.27039 | 0.21084 | 0.042731 | 0.073197 | 0.19774 | 0.12175 | 0.14913 | 0.13011 | 0.17598 | 0.011157 | 0.097591 | 0.023162 | 0.11132 | 0.14681 | 0.18 | 0.67039 | 0.86011 | -0.12883 | 0.07088 | 0.19989 | 0.20774 | 0.19607 | 1.2175 | 0.24335 | 0.67208 | 0.74143 | 0.46254 | 0.20584 | 1.3123 | 0.48989 | 0.64041 | 0.57479 | 0.25917 | 0.33451 | 0.38968 | 2.4285 | 0.47873 | 0.46949 | 0.034565 | -0.41051 | 2.1281 | 1.4905 | 0.58809 | 0.5682 | 0.55032 | 1.4293 | 1.1668 | 0.037692 | 0.8385 | -0.90384 | 0.075914 | -0.15471 | -0.39282 | -0.11188 | -0.24602 | -0.1208 | 0.039447 | -0.045857 | -3.1903 | 5.8548 | -0.4201 | 0.0042484 | -0.30067 | -0.27693 | 0.22251 | 0.42668 | 0.55136 | 0.01526 | 0.5 | -5.7674 | 1.4208 | 0.46314 | 0.39807 | 0.47987 | 0.53188 | 0.79782 | 0.45504 | 0.55831 | 0.47308 | 0.4303 | 0.62375 | 0.25743 | 0.53417 | 0.93823 | 0.2819 | 0.59532 | 0.35737 | 0.54392 | -1.1431 | 0.59029 | 0.50413 | 0.55034 | -0.21072 | 0.71238 | 0.60541 | 0.53153 | 0.47609 | 0.60231 | 0.46939 | 0.76857 | 0.63811 | -0.22918 | 1.344 | 0.62273 | 0.69603 | 0.73261 | 0.71973 | 0.51276 | 0.60382 | 0.43755 | 0.76675 | 0.49463 | 0.42832 | 0.4906 | 0.4814 | 0.52677 | 0.43189 | 0.42082 | 0.41058 | 0.3939 | 0.29063 | 0.37196 | 0.37288 | 0.51227 | 0.11332 | 0.082817 | 0.072712 | -0.095718 | -0.16008 | -0.15104 | -0.11577 | -0.18087 | -0.87558 | 0.21893 | 0.96127 | -0.10916 | 0.66959 | 0.059906 | 1.8451 | 0.31664 | 0.34014 | 0.26944 | 0.26238 | 1.1845 | -0.56874 | -3.0808 | -0.068432 | 0.17122 | 0.2081 | 0.53356 | 0.16078 | -3.8416 | -1.7911 | -1.6331 | 1.2309 | 0.99393
S-1 | 19 | Narayangonj (west) BSCIC33/11KV S/S | 16 | 1.3374 | 1.4288 | 1.2737 | 1.2502 | 0.7177 | 1.1695 | 1.0572 | 1.5652 | 1.2579 | 1.1804 | 2.4816 | 1.9025 | 0.43985 | 1.8015 | 1.1625 | 1.3471 | 1.2039 | 1.5062 | -0.50822 | 0.64619 | 0.46 | 1.4475 | 1.6919 | 2.3367 | 1.0938 | 1.9286 | 1.6963 | 1.4464 | 0.19063 | 0.05 | 0.64484 | 0.099973 | -0.20921 | 1.2467 | 1.8766 | 3.2794 | 1.1518 | 0.73247 | -0.24952 | -0.53792 | 2.7977 | 3.4592 | 0.75537 | 2.5535 | 2.0555 | 1.4162 | 0.83744 | 1.9454 | 2.0678 | 2.3709 | 2.321 | 2.6779 | 0.92805 | 1.4559 | 1.9485 | 1.3055 | 2.4101 | 1.8058 | 1.747 | 1.6989 | 1.4255 | -1.4809 | -0.032431 | 1.1427 | 1.1055 | -0.084311 | 0.83229 | 2.5177 | 1.1994 | 1.6429 | 2.0985 | 1.3858 | 0.85872 | 2.9912 | -1.659 | 2.4081 | 0.22565 | -1.1324 | 0.10503 | -0.68435 | 2.2039 | 0.17074 | 0.44629 | 0.4277 | 2.675 | 0.90112 | 1.469 | 1.164 | 1.013 | 1.186 | 2.1133 | 1.3632 | 0.69479 | 2.0403 | 1.3006 | 1.3597 | 1.4474 | 1.3988 | 1.7728 | 1.0483 | 0.56901 | 0.82489 | 0.4748 | 0.76019 | 1.6922 | 1.5285 | 1.5339 | 0.6564 | 1.9406 | 1.3101 | 0.80612 | 1.2306 | 1.1787 | 1.2746 | 1.7004 | 1.4725 | 0.71881 | 0.26872 | 0.88058 | 0.88058 | 0.88058 | 0.88058 | 0.80108 | 1.7661 | 1.7466 | 1.9304 | 1.2059 | 2.0075 | 1.1181 | 1.6511 | 1.4966 | 1.6001 | 0.6322 | 1.3808 | 1.0136 | 0.94257 | 1.0964 | 0.99899 | 1.3704 | 1.4825 | 1.4414 | 1.6916 | 1.0494 | 1.3268 | 1.2731 | 1.362 | 0.13132 | 1.7071 | 1.1766 | 0.093379 | 0.61985 | 0.85585 | 2.1047 | 0.90247 | 1.2513 | 1.3586 | 1.4166 | 1.4299 | 0.86502 | 1.3916 | -0.18682 | 1.0272 | 1.7604 |  | 1.5389 | 1.21 | -2.7234 | 0.8622 | -3.0919 | -0.78665 | -1.1645
S-1 |  | Char Syedpur 33/11KV S/S | 17 | #REF! | #REF! | #REF! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1.4211 | 0.73669 | 0.74592 | 1.2187 | 0.60781 | 0.52665 | 0.95977 | 0.57728 | 1.6347 | 0.20986 | 0.92083 | 0.58 | 0.49386 | 0.91234 | 0.88171 | 0.80537 | 1.0422 | 1.0763 | 1.6315 | 1.5776 | 2.3894 | 2.5027 | -0.24888 | 1.1689 | 1.2094 | 1.7426 | 2.8614 | 2.2215 | 1.1497 | 0.71004 | 1.1492 | 2.1203 | 0.71172 | 0.78253 | 1.1995 | -0.54688 | 0.5136 | 1.3104 | 1.8434 | 1.0813 | 0.90928 | 0.6242 | 1.7476 | 2.1145 | 0.60885 | 1.1239 | -0.55407 | 0.89088 | 1.0625 | 0.89447 | 1.1896 | 0.80413 | 0.64894 | 0.61859 | 0.47161 | 0.64331 | 0.55854 | 0.46251 | 0.61818 | -1.9672 | 0.18988 | 1.1156 | 1.0602 | 1.3126 | -2.0458 | 1.0522 | 0.099846 | 1.043 | 0.97546 | 1.1996 | 2.5849 | -1.118 | 1.2666 | 0.92145 | 1.2391 | 1.0194 | 1.085 | 1.5871 | 0.42894 | 0.6067 | -1.2946 | 1.8082 | 0.1848 | 0.8417 | 0.49292 | -0.6975 | 0.58292 | 0.89797 | -0.33105 | -0.87741 | -0.22907 | 0.76801 | -0.074771 | 0.47107 | -0.18943 | 0.10914 | 0.34077 | 0.52221 | 0.22044 | 1.3335 | 1.0951 | 0.63662 | 0.93772 | 1.3246 | 0.50674 | 0.29051 | 5.1666 | 1.2602 | 0.44173 | 1.7732 | 2.0175 | 1.3464 | 1.7903 | 1.6058 | 1.2527 | 1.4213 | 1.3173 | 1.02 | 1.543 | 0.98204 | 1.1194 | 1.074 | 1.0222 | 1.1011 | 0.8462 | 0.85413 | 0.958 | 0.82979 | 0.74663 | 1.2734 | 0.53405 | 1.8418 | 0.56149 | 1.3417 | 0.72228 | 0.37858 | 1.1886 | 1.3085 | 1.3799 | 1.3344 | 0.7035 | 1.5096 | -4.0021 | -1.0177 | 1.219 | 1.1366 | 1.5774 | 1.6682 | -3.1283 | -0.62548 | 1.2309 | -1.0224 | 0.50871
S-1 | 20 | Siddhirganj 132/33/11KV S/S | 18 | 0.14623 | 0.19647 | -0.31326 | -0.24126 | -0.44321 | 0.057699 | 0.09405 | -0.56788 | 0.19599 | 0.036024 | -1.3288 | -0.095675 | -0.053457 | -0.38126 | -0.023862 | -0.39347 | 0.058463 | 0.016456 | -0.048834 | -0.58244 | 0.92592 | -0.19647 | -0.026817 | -0.16649 | -0.14965 | -0.15912 | -0.27338 | 0.2897 | -0.54922 | -0.4 | 0.25696 | -0.57695 | 0.19796 | -0.92562 | -0.067853 | 0.016509 | -0.2414 | -0.43086 | -0.09965 | 0.48722 | -0.78284 | 0.29778 | -0.34514 | 0.36173 | -0.32983 | 0.056926 | -0.26063 | -0.4415 | 0.040826 | 0.1486 | 0.22729 | 1.1192 | 0.15521 | -1.1096 | -0.71877 | 0.13576 | 0.48532 | 0.14602 | -0.32131 | 0.47202 | 0.035164 | 0.91114 | -0.033044 | 0.18566 | -0.057205 | -0.19704 | -0.032341 | -0.61587 | -0.38108 | -0.36108 | -0.54395 | -0.60372 | -0.38105 | -0.82904 | -0.58104 | -0.22598 | -0.24697 | 0.0064174 | -0.58375 | -0.64222 | 0.29171 | -0.073625 | 0.32237 | 0 | -0.4124 | 0.28198 | -0.34697 | 0.50973 | -0.097334 | -0.009941 | 0.29679 | -0.31969 | 0.51973 | -0.566 | 0.63175 | -0.03507 | 0.98117 | 0.69114 | 0 | 1.3038 | 0 | -0.3782 | -0.17756 | 0.32693 | 0.49111 | 0.5163 | 0.3567 | 0.44973 | 1.0399 | -0.28448 | 0.4915 | 0.59183 | 0.74417 | -0.36399 | 0.25699 | 1.0823 | 0.12243 | 0.33359 | 0.65086 | -0.31011 | -0.031421 | 0.22639 | 0.19546 | 0.39708 | -0.0083007 | -0.071432 | 0.26543 | 2.3644 | -1.8307 | 0.80532 | 0.14963 | 0.21727 | 0.79059 | 0.2036 | 0.17793 | 0.34761 | 0.35906 | 0.31004 | 0.3576 | 0.40424 | 0.40116 | 0.37568 | 0.37731 | 0.30231 | 0.36086 | 0.35919 | 0.28212 | 0.21988 | 0.39111 | 0.37053 | 0.58958 | 0.85505 | 0.77513 | 0.66268 | 0.84446 | 0.83
S-1 | 21 | Siddhirganj 33/11KV S/S | 19 | 1.971 | 1.2405 | 0.73479 | 1.0085 | 2.251 | 2.0964 | 0.42696 | 1.1514 | -0.10893 | 0.49872 | 0.30501 | 0.49752 | 0 | 0.19506 | 0.032329 | 1.694 | -0.40876 | 0.59137 | 1.8255 | 0.11196 | -0.80996 | 0.92737 | 1.3348 | -0.24175 | 0.3521 | -0.43189 | -0.25444 | -0.2907 | 0.73714 | -0.4 | -0.042541 | -0.65715 | -1.0705 | 0.26371 | 0.24233 | -0.39844 | -0.51248 | 1.831 | -1.2739 | -0.37658 | 1.5522 | 0.66552 | -0.36673 | -1.0801 | 0.61749 | 0.39313 | 2.2067 | 0.81152 | 2.9167 | 1.3413 | 1.7237 | 1.024 | 1.1137 | 0.89589 | -1.6906 | -0.54122 | -0.15705 | -1.6428 | -0.034107 | 0.038396 | 2.5487 | 1.8895 | 1.4706 | 0.4656 | 1.3961 | 0.94889 | -0.93705 | 0.59231 | 0.18182 | 1.468 | -0.90774 | -0.35533 | 0.56886 | -0.30785 | 0.095604 | 1.0271 | -0.37764 | 11.3488 | -0.91644 | 2.5652 | 1.5 | 0.87073 | 0.16548 | 2.1698 | 0.84318 | -0.79396 | 1.9788 | 0.0069165 | -0.5668 | -0.26851 | -0.62677 | 0.37985 | 0.26097 | 1.043 | 2.4336 | 0.58568 | 0.7925 | 0.72048 | 0.51295 | -0.4454 | 4.3379 | -2.2769 | 0.502 | 0.46989 | -2.3241 | 5.8729 | -0.26863 | 0.86122 | -0.33236 | 0 | 0.82043 | -0.27365 | -0.78991 | -0.74371 | -0.93083 | 0.75819 | -0.61416 | 0.92181 | 1.7759 | -0.3688 | -1.6107 | 1.8805 | 0.19546 | 1.2371 | -0.42059 | -0.071432 | 0.23011 | 0.57459 | -3.1857 | -1.3535 | -1.0503 | 0.11632 | 1.7886 | -0.7532 | -2.0448 | 0.9536 | -0.70691 | -0.3121 | 0.026303 | 0.57145 | -0.98379 | -1.9389 | -1.419 | 0.78315 | -0.7446 | -0.70846 | -1.2376 | -1.234 | 1.0445 | -1.479 | 0.58958 | -1.4018 | -1.5255 | -1.1086 | -1.1639 | -0.91115 | -1.2565 | -2.1185 | -1.8746 | -2.5985 | -2.1729 | -0.93838 | -0.69389 | -1.2048 | -0.72052 | -1.1478 | -1.1397 | -1.028 | -0.78665 | 5.0754 | 5.4209
S-1 | 22 | Demra 33/11KV S/S | 20 | 2.2106 | 1.5874 | 1.1642 | 1.4257 | 0.9148 | 2.2588 | 1.917 | 0.59669 | 0.90419 | 0.52411 | 1.1861 | 0.08275 | 0.42897 | 2.7493 | 0.71563 | 1.5245 | 2.3391 | 1.8796 | 1.7706 | 1.2144 | 0.78975 | 1.2048 | 1.3146 | 1.3903 | 1.2741 | 0.99968 | 1.4939 | 3.2906 | 3.1992 | 1.85 | 1.4378 | -0.65144 | 0.60234 | 2.7674 | 1.5622 | 1.8902 | 0.076627 | 0.45038 | 0.79767 | 0.63472 | 0.28139 | 1.1818 | 1.0441 | 1.0527 | 1.5096 | 1.2447 | 1.7569 | 1.2997 | 1.1378 | 1.9309 | 1.9723 | 2.8515 | 1.303 | 4.704 | -0.78763 | 3.0022 | 3.1159 | 2.6667 | 1.3111 | 0.17628 | 1.947 | 0.79904 | 0.53627 | -0.68856 | 1.4257 | 0.34193 | 0.013853 | 0.44851 | 0.58734 | 0.20957 | 0.22342 | 0.14534 | 0.27567 | 2.789 | 1.7107 | 0.63908 | 0.45368 | 1.6027 | -0.72751 | 0.21754 | 0.53905 | 0.5 | 0.67958 | 0.77013 | 0.29456 | -1.5836 | 0.40131 | -1.9542 | 3.6909 | -0.094488 | 0.46345 | 0.30686 | 1.1289 | 0.052258 | 1.3654 | 1.2029 | 1.9007 | 1.3198 | 1.261 | 0.88928 | 1.6084 | 1.0943 | 1.3087 | 1.3857 | 1.6203 | 1.9165 | 1.0582 | 1.7143 | -0.83313 | 1.0133 | 0.25066 | 1.0274 | 0.9704 | 0.66996 | 1.0019 | 1.9931 | 1.9858 | 0.079945 | 2.7364 | 1.233 | 1.517 | 1.4751 | 0.7043 | 1.1206 | 1.5405 | 1.7198 | 0.2868 | 3.4522 | -1.0039 | 0.80303 | 1.7282 | 0.61346 | 2.0217 | 0.88267 | 2.422 | 1.5365 | 1.4564 | 1.471 | 1.1343 | 1.6866 | 1.8484 | 1.9708 | 1.9298 | 4.6733 | 2.4196 | 1.7502 | 0.94369 | 1.5528 | 1.1828 | 0.95907 | 1.1106 | 1.6151 | 1.3791 | 1.2875 | 1.3255 | 1.8864 | 1.471 | 0.064193 | 0.30949 | -0.40802 | 0.25217 | 1.4912 | 1.8904 | 1.3309 | 1.4457 | 0.69189 | 2.0207 | 0.81499 | -1.0224 | -0.32414 | 0.12243
S-1 | 23 | Mondalpara 33/11KV S/S | 21 | 0.34919 | 1.0397 | 0.70138 | 0.84351 | 0.35416 | 0.97962 | 0.72716 | 0.9048 | 0.92371 | 0.95054 | 0.56289 | 3.0656 | -1.2126 | 1.1261 | 1.0083 | 0.72421 | 0.56769 | 0.51496 | 0.75129 | 0.48621 | 0.40494 | 0.81069 | 0.54728 | 0.51866 | 0.35975 | 0.51555 | 0.5799 | 0.55437 | 0.46474 | 0.45 | 0.6305 | -0.50893 | 0.49794 | 0.60125 | 0.52059 | 0.56532 | 0.62442 | 0.41987 | 0.62368 | 0.33423 | -0.17063 | 1.4567 | 0.48859 | 0.30059 | 0.59416 | 2.4369 | 2.7806 | 0.53881 | 2.3259 | 0.49393 | 0.5606 | 0.42922 | 0.2307 | 0.45891 | 0.42479 | 0.72499 | 2.1234 | 3.3379 | -0.95719 | 0.33704 | -0.037996 | 3.1205 | 3.0908 | 0.35969 | 6.7624 | 2.9431 | 0.84064 | 1.8959 | -1.7469 | -3.2061 | -3.8488 | -1.4663 | 1.9065 | 2.4805 | 1.9603 | 2.419 | 3.0884 | 0 | 2.1684 | 2.4164 | 0.25724 | 1.8849 | 2 | 2 | 3.0977 | 1 | 3.1318 | 2.1376 | 1.6621 | 1.0678 | 1.4711 | 2.6702 | 3.2665 | 2.3844 | -0.70321 | 1.9525 | 3.4568 | 2.8998 | 3.6947 | -1.0502 | 2.3516 | 3.36 | 2.9054 | 2.1484 | 3.14 | 1.8634 | 2.9996 | 4.0902 | -0.23772 | 0.82813 | 1.4416 | 1.9797 | -0.63835 | 4.1354 | 3.4055 | 2.6642 | 4.6437 | 4.5843 | 3.662 | 3.2538 | 2.7564 | 1.0643 | 3.0799 | 2.4216 | 2.4004 | 1.687 | 0.10813 | 4.1694 | 1.3791 | 2.7103 | 1.1991 | 2.1662 | 2.4785 | 3.7333 | 3.3863 | 2.0313 | 1.8987 | 2.6161 | 2.3742 | 2.5824 | 2.2919 | 2.6045 | -0.090442 | 5.1217 | 2.7988 | 2.4143 | 2.2701 | 1.6534 | 1.7987 | 2.0908 | 2.1548 | 3.3038 | 2.8375 | 2.9 | 2.1792 | 3.4261 | 3.4153 | 1.4984 | -0.50246 | 5.3725 | 3.358 | 3.5385 | 3.6283 | 2.4985 | 2.0398 | 2.793 | 3.7584 | 5.4281 | 5.0754 | 1.0046 | 0.99377
S-1 | 24 | Khanpur 33/11KV S/S | 22 | 1.2525 | 1.2416 | 0.9244 | 1.2858 | 0.16068 | 1.4315 | 0.54407 | 1.2718 | 0.053074 | 1.4731 | 0.81806 | 1.5556 | 1.3117 | 0.26767 | 1.6758 | 1.2995 | 0.2961 | 0.13215 | 1.8015 | 1.7896 | 1.9834 | 2.0569 | 2.0969 | 1.8795 | 1.9543 | 2.0756 | 1.9602 | 2.6805 | 1.2044 | 1.6 | 1.8435 | 1.9266 | 2.1029 | 3.7126 | 1.2653 | 2.5327 | 2.467 | 1.3829 | 2.1827 | -0.32462 | 3.2839 | -1.5534 | 0.2524 | 0.61057 | 2.8157 | 3.8111 | 2.762 | 4.3031 | 0.066294 | 0.066294 | 4.2202 | 1.4237 | 0.6932 | 0.36398 | 1.5071 | 0.024543 | 1.918 | 0.46355 | -1.5077 | 0.37645 | -0.19112 | 1.6639 | 0.76348 | -0.87768 | 0.80593 | 2.9561 | 2.5419 | 2.8518 | 3.3327 | 3.3123 | 2.3812 | 3.4284 | 2.7407 | 4.2526 | 1.6871 | 4.8525 | 2.8328 | 1 | 0.062828 | -0.71375 | 2.8779 | 2.2404 | 2.8882 | 2.6865 | 1.5 | 1.5 | 2.3088 | 2.1344 | 2.9108 | 2.4362 | 3.0004 | 2.6392 | 2.97 | 3.1491 | 2.7294 | 0.15217 | 2.0794 | 2.7801 | 2.733 | 2.4127 | 2.9629 | 1.2254 | 2.3517 | 2.0846 | 2.9472 | 3.9413 | 1.7359 | 2.5187 | 3.903 | 2.4137 | 2.5843 | 1.8577 | 3.5977 | 2.6539 | 1.1495 | 2.9917 | 4.2976 | 0.21844 | 3.4566 | 1.897 | 3.1708 | 3.0711 | 3.7577 | 0.48635 | 4.2696 | 2.3387 | 2.1931 | 3.814 | 1.106 | 2.9859 | 1.7059 | 2.2132 | 1.8591 | 2.9657 | 3.9719 | 2.0257 | 2.1389 | -0.8418 | 4.9901 | 2.4063 | 2.4419 | 2.3902 | 2.1726 | 2.2273 | 2.1225 | 1.9147 | 1.7961 | 1.947 | 1.7301 | 2.2596 | 1.9492 | 3.1907 | 1.6607 | 1.6599 | 2.5525 | 2.1658 | 3.6945 | 3.2279 | 3.2983 | 3.1226 | 1.6093 | 3.7803 | 3.9735 | 3.509 | 4.2076 | 3.317 | 1.1294 | 1.1023 | -0.32414
S-1 | 25 | Matuail 132/33 KV S/S | 24 | 0.76309 | 0.6903 | 0.26597 | 0.078107 | 0.15886 | -0.12527 | -0.080605 | 1.1258 | -0.059153 | 0.023747 | 0.23726 | 0.11276 | -0.66729 | 0.22987 | 0.14398 | 0.070989 | 0.020709 | 0 | -0.044494 | -0.18373 | 0.10804 | -0.28581 | 0.16482 | 0.072096 | -0.15427 | -0.95961 | 0.24768 | -0.14928 | 0.2 | 0.2 | -0.98311 | -0.25361 | 0.26681 | 0.14155 | 0.5248 | 0.23312 | 0.90629 | -0.18812 | -0.81317 | 0.74089 | 0.46044 | 0.33043 | 0.36237 | 0.41158 | 0.53229 | 0.17226 | 0.061278 | 0.2685 | 0.30446 | 0.44116 | 0.13481 | 0.89479 | 0.26117 | 0.63817 | -0.37486 | 0.94892 | 0.30778 | -0.54061 | 0.16071 | 0.14613 | 0.82382 | 0.56617 | -0.00063484 | 0.26686 | -0.048233 | 0.17692 | -0.37574 | -0.65099 | 0.37626 | -0.79716 | -0.80724 | -0.91609 | -0.49705 | -0.34461 | -0.26402 | -0.003182 | -0.047362 | -0.17595 | 0.14019 | -0.12129 | -0.70273 | 0.1
S-1 | 26 | Matuail 33/11KV S/S | 23 | 1.0417 | 1.4349 | 1.0876 | 2.6926 | 2.6393 | 1.3816 | 0.39033 | -0.056785 | 1.3689 | 1.4517 | 1.475 | 1.9312 | 1.8818 | 1.3565 | 0.59561 | 1.4863 | 1.3756 | 2.0089 | 1.249 | 1.0318 | 0.52492 | -0.80987 | 2.342 | 0.90766 | 1.5869 | -0.91251 | 1.6625 | 0.33247 | 2.3449 | 2.04 | 1.9274 | 2.9715 | -2.4946 | 1.5153 | 1.1658 | 1.1759 | 1.1915 | 0.61374 | -0.042198 | 0.39388 | 0.47671 | 1.3276 | 1.4787 | -0.17195 | 0.86743 | 4.3327 | 1.9965 | 4.8063 | 3.9749 | 1.5002 | 3.1545 | 4.1624 | 1.2792 | 1.9398 | 0.9086 | 1.1548 | 2.2674 | 0.49243 | 0.91949 | 0.90439 | 1.4911 | 1.2393 | 0.69401 | 0.027029 | 0.53859 | -3.895 | -0.51578 | 0.93098 | -3.9363 | 2.1775 | -0.33117 | 0.54509 | -0.03601 | 0.93473 | 0.3 | 0 | 2.4057 | 0 | 0.3477 | 2.2834 | -0.24575 | 2.8678 | 1.0489 | 1.8481 | 0.14688 | 1.5 | 1.7853 | 0.20194 | 0.22495 | 0.43749 | 0.17341 | -0.077094 | -0.1277 | 0.54394 | -0.42727 | 0.33386 | 0.32875 | -0.27936 | 2.8346 | 1.1528 | 1.2055 | -1.3936 | -0.11684 | 0.061007 | 0.23473 | -0.042116 | 1.2839 | 0.35236 | 0.16456 | 0.52579 | 0.83764 | 0.10115 | 0.64594 | 0.71559 | 0.34436 | 0.058754 | -0.21966 | 1.7704 | 0.74224 | -0.53263 | -0.70429 | 0.91047 | 1.1766 | 0.71685 | 1.4931 | 0.944 | 0.070672 | 1.4854 | -1.3295 | 0.089202 | -0.01001 | 0.20738 | 0.21218 | -0.2995 | 0.1324 | 0.07314 | 1.0534 | -0.28655 | 2.2663 | 0.010937 | 1.7093 | 1.0048 | 0.91352 | 1.5179 | 2.4807 | 2.4329 | -0.3915 | 1.461 | 0.70238 | 0.66982 | 0.71566 | 0.43636 | 0.82334 | 0.64386 | 0.68018 | -0.065896 | 0.88703 | 1.1279 | 1.177 | 1.0522 | 0.47154 | 0.54385 | 0.49886 | 0.75558 | 0.70665 | 0.71669 | 0.74803 | 0.53618 | 1.0046 | 8.7188 | -5.241
S-1 | 27 | Sarulia 33/11KV S/S | 25 | 1.7088 | 3.475 | -2.324 | 1.371 | 2.474 | 2.2031 | 0.28637 | 0.2433 | 0.8429 | 0.98439 | 0.83658 | 1.1868 | 1.6013 | 0.28882 | 2.378 | 1.2251 | 0.97768 | 1.4941 | 1.1341 | 2.0238 | -0.32872 | 2.4821 | 1.1041 | 0.41015 | 1.8499 | 0.76033 | 1.1764 | 1.6376 | 1.7995 | 1.75 | -0.13406 | 1.1206 | 0.7149 | 1.4828 | 1.3576 | 0.40696 | 2.3078 | 0.94373 | 0.47124 | 1.6776 | 0.1152 | 1.0689 | 0.96755 | 0.80794 | 1.9094 | 1.9391 | 1.7405 | 1.4759 | 1.7457 | 1.6485 | 2.0009 | 1.8534 | 1.6182 | 0.26432 | 0.86109 | 1.9541 | 1.9194 | 1.1692 | 1.4699 | 0.46738 | 2.4989 | 1.8221 | 0.53425 | 0.36467 | 2.1146 | 0.63126 | 0.747 | 1.4395 | 1.0078 | 0.92426 | 1.305 | 0.40108 | 0.75407 | 0.8702 | 0.6034 | 1.2722 | 0.94916 | 0.68417 | 0.68847 | 0.83934 | -0.019128 | 2.3356 | 1.0213 | 1.6265 | 0.66004 | -0.72617 | 0.99952 | 0.77677 | 1.8246 | 0.12633 | 0.18363 | 0.83573 | 1.0495 | 0.65182 | 1.556 | 1.3706 | 2.9427 | 0.41019 | 2.0573 | 0.48746 | 2.1627 | -0.36369 | 0.84975 | 1.5698 | 1.3686 | 1.5759 | 0.61263 | 1.7955 | 0.020713 | 0.41778 | -0.59693 | 0.25446 | 0.80961 | -0.32998 | 1.3129 | 1.331 | 0.89642 | 0.59189 | 2.2167 | 1.4095 | 1.1135 | 0.025797 | 0.023711 | 0.59733 | 0.89812 | 1.1857 | -0.25528 | 2.7806 | -1.0807 | 1.6217 | -1.4029 | 2.2168 | -0.59885 | 2.0447 | 1.7206 | 1.0452 | 1.1095 | 0.72482 | 1.0787 | 0.95961 | 1.0501 | 1.4199 | 1.4583 | 1.641 | 0.17821 | 0.91489 | 0.86388 | 0.96568 | 0.90921 | 1.5221 | 1.3153 | 2.0531 | 2.1927 | 1.8217 | 2.057 | 1.7995 | 1.8247 | -0.076114 | 0.63764 | 0.17439 | 0.91581 | 2.5167 | 2.1655 | 1.4512 | 0.4683 | 7.9748 | 2.1809 | 1.3493 | 8.7188
S-2 | 28 | IG Gate GIS 33/11 kV | 27 | 0.75623 | 0.29609 | 0.89875 | 1.2562 | 0.5 | 0.52008 | 0.69376 | 0.98341 | 1.0825 | 0.6619 | 1.1642 | 1.0577 | 1.4044 | 0.01116 | 0.62818 | 0.19283 | 0.85259 | 0.19217 | 0.063244 | -0.019801 | 0.33791 | 0.45298 | 0.25958 | 1.618 | 0.48557 | 0.57826 | 1.2005 | 0.10167 | 1.0408 | 0.89 | 0.97999 | 0.7528 | -0.033557 | 0.50544 | 0.58455 | 0.57716 | 1.0179 | -0.45658 | 0.78231 | 0.28793 | 0.38782 | 0.47693 | -0.17933 | 0.9165 | 0.68454 | 1.2546 | 2.84 | 2.533 | 3.4942 | 1.1648 | 1.8885 | 1.2427 | 1.7501 | 1.1067 | 0.74492 | 0.65697 | 1.2461 | 0.61315 | 0.45933 | 0.040047 | 0.36855 | -0.048178 | 0.21496 | 0.45297 | 0.19106 | -1.9035 | 0.80352 | 1.239 | 0.661 | 1.5397 | 0.16959 | -0.52477 | 2.7262 | 0.36232 | 0.43505 | 0.94922 | 1.4867 | 0 | 0.68847 | 1.0773 | 1.8877 | 2.584 | 1.924 | 1.7988 | -0.29016 | -0.70203 | 0.80055 | 1.3354 | -0.13729 | -0.065217 | -0.52143 | 0.56127 | -0.55476 | 0.43238 | 0.22434 | -0.0082758 | -0.30549 | -0.05234 | -0.78725 | -1.3432 | -0.027567 | -0.40538 | -0.35421 | 2.8945 | -0.20423 | 0.16463 | 2.1658 | 0.19772 | 0 | 0.65115 | -1.0383 | -0.25348 | -0.16969 | -0.043543 | -0.066716 | -0.13647 | -0.046003 | 0.12488
S-2 | 29 | Motijheel Old 33/11 kV | 28 | 2.2501 | 2.1862 | 0.52184 | 0.065511 | 0.63636 | 0.60834 | 2.4001 | -0.91892 | 1.1115 | 0.01474 | 0.95818 | 2.1703 | 1.7382 | 0.74849 | 2.0875 | 0.42844 | 0.62806 | 2.0405 | 2.4913 | 3.4642 | 2.4816 | 1.4508 | 0.47545 | 2.9301 | 2.5212 | 2.001 | 3.4424 | 5.1621 | 2.0436 | 3.65 | 2.1997 | 0.11642 | 0.49474 | 2.1557 | 1.0892 | -0.92587 | 1.7198 | 2.7448 | 1.2446 | -0.39262 | 1.9846 | 0.33015 | 2.3786 | 1.4629 | 0.97652 | 3.7269 | 5.6226 | 4.404 | 1.5265 | 2.6437 | 1.2388 | 2.6421 | 5.1723 | 2.8758 | 2.1543 | 1.9033 | 3.0678 | 1.8929 | 1.2037 | 0.36413 | -0.093155 | 0.94487 | 2.279 | -0.57602 | 1.6704 | -0.051461 | 0.25753 | 0.049506 | -0.36117 | -1.6192 | -3.7471 | -3.9045 | 1.381 | 5.2472 | 0.46367 | -0.71795 | -0.56188 | 1.1503 | 0.97991 | 0.36292 | 0.32657 | 0.10852 | 0.83201 | 0.23477 | -4.7134 | -0.7177 | -0.56324 | 0.24652 | -5.4828 | 2.3151 | 1.6227 | -1.6392 | 2.0069 | -0.047305 | -0.0094599 | -0.60193 | -1.0794 | -3.6229 | 0 | 1.0325 | 0.5 | 0 | 0 | 2.4521 | 0.016671 | 0.1187 | 2.6753 | 1.4248 | -0.15373 | 1.858 | -3.7401 | 0.22225 | 0.12599 | 0.63662 | 0 | 0.45874 | -0.50135 | -4.7997
N-1 | 30 | Mitford 33/11 kV | 29 | -1.8287 | 0.32559 | 1.1436 | 2.5447 | 2.1498 | 0.014365 | 2.1559 | -0.026171 | 1.3395 | -0.32114 | 0.44577 | 0.10453 | 0.43259 | 0.361 | 0.31808 | -0.019895 | 0.32177 | -0.32705 | -0.44475 | -0.50475 | -0.077599 | 0.10692 | -0.5101 | 0.38559 | -0.14306 | -0.74671 | -0.75162 | -0.79717 | -0.16034 | -0.72 | 0.33409 | -0.81574 | -0.96883 | 0.019142 | 0.13719 | 0.69043 | -0.83952 | 1.5482 | 0.44533 | 1.0576 | -0.8413 | -0.66391 | 0.06476 | 1.434 | 2.4849 | 2.7119 | 0.16553 | 1.2723 | 0.015 | 0.5 | 0.53701 | 3.7931 | -0.31863 | 0.89077 | 1.6343 | 0.3 | 0.7925 | 0.86507 | 1.737 | 2.9461 | 0.55791 | 1.8755 | 1.6682 | -1.0589 | -1.2413 | -1.226 | -0.12714 | -0.30383 | -0.88493 | 1.0995 | 1.2215 | 1.0624 | 5.746 | 1.8297 | -0.75934 | -1.4869 | 0.2 | -2.5799 | -0.61754 | 1.9294 | -0.68188 | -0.70543 | -0.74521 | -0.9618 | -0.80399 | -0.98812 | -0.25933 | 1.1005 | -0.37896 | 0.74964 | -0.89014 | 1.3916 | 0.72626 | 0.55758 | 0.090892 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1.8541
N-1 | 31 | Biddyut Bhaban 33/11 KV | 30 | 0.45412 | 0.38532 | 0.39047 | 0.45917 | 0.90891 | -0.055893 | 0.63844 | 0.33939 | 4.5155 | 0.22136 | 0.46653 | 1.244 | 0.39551 | 0.30785 | 0.43087 | 1.366 | 0.1795 | 0.5288 | 0.85722 | 0.48814 | 0.9133 | 0.37654 | 1.3565 | 1.0017 | 0.63402 | 1.4697 | 0.69619 | 0.12641 | 0.1271 | 0.99 | 1.6215 | 1.4886 | 1.3994 | 1.331 | 3.0105 | 1.9318 | 2.3005 | 2.8458 | 2.8563 | 1.8307 | 2.3997 | 2.9449 | 0.28615 | 0.50833 | 0.74141 | -0.52892 | 0.10187 | 2.6407 | 0.76047 | 0.48036 | 0.51474 | 0.72877 | 0.90091 | 0.97357 | 1.3308 | 1.2744 | 0.94645 | 0.83275 | 0.90857 | 0.40881 | 0.70309 | 0.90394 | 3.6055 | 0.056477 | 1.0176 | 0.85055 | 0.73538 | 0.64839
S-2 | 32 | Nandalalpur 33/11 kV | 31 | 0.72202 | 0.71461 | 0.45128 | 0.73946 | 1.1096 | 0.99937 | 0.96808 | 1.1051 | 0.95543 | 1.81 | -0.74598 | 1.6956 | 1.4661 | 1.6679 | 1.825 | 1.693 | 2.2749 | 2.2399 | 0.91654 | 0.84748 | 2.8348 | 0.85261 | 1.9103 | 2.4318 | 0.45953 | 3.3191 | 2.9362 | 2.3613 | 3.7223 | 2.8 | 3.745 | 1.5928 | 1.6138 | 2.4547 | 1.8557 | 4.248 | 1.1001 | 2.6436 | 0.84202 | 2.8716 | 2.0309 | 1.055 | 0.81047 | 2.9782 | 2.9982 | 3.7467 | 3.1355 | 2.965 | 2.9689 | 1.9525 | 2.5889 | 0.69875 | 4.438 | 3.7223 | 2.4449 | 0.5 | 0.3 | 1.9199 | 5.8322
S-1 | 33 | Dapa 33/11 kV | 32 | 1.9819 | 0.54273 | -0.027636 | 0.64029 | 0.23842 | 2.345 | 2.719 | 2.1672 | 0.704 | 0.90828 | 0.892 | 0.93896 | 0.64654 | 0.79314 | 0.62592 | 0.5968 | 0.68495 | 0.77584 | 0.58116 | 0.72578 | 0.80877 | 0.73904 | 0.73595 | 1.1953 | 0.80001 | 0.57502 | 0.42432 | 0.34683 | 0.43178 | 0.38 | -0.86219 | 2.2607 | 0.89568 | 0.31341 | 0.31527 | 0.37518 | 0.27063 | 4.5542 | 2.2539 | 0.98676 | -0.42648 | 1.4713 | 1.7042 | 1.6212 | 1.8479 | 5.0073 | 4.3024 | 3.1591 | 2.5952 | 4.2337 | 3.2431 | 1.3661 | 3.42 | 1.1744 | -2.4986 | 0.40045 | 1.9537 | 1.1767 | 0.20233
S-1 | 34 | Laxmi Narayan Cotton Mill 33/11 kV | 33 | -0.072586 | 0.43344 | 1.8177 | 1.565 | 1.4467 | 1.2406 | 1.2201 | 2.2278 | 1.6623 | 0.15399 | 1.6335 | 1.3271 | 0.42922 | 2.4309 | 1.9111 | 2.119 | 2.2822 | 1.1314 | 0.82915 | 2.0133 | 1.4834 | 1.3639 | 0.80594 | 1.1955 | 1.1895 | 0.2091 | 1.3445 | 0.70565 | 1.7383 | 1.36 | 0.040886 | 1.1248 | 2.0596 | 1.2825 | 1.606 | 2.6051 | 2.901 | 2.7457 | 3.6828 | 2.83 | 2.8846 | 2.5218 | 3.2744 | 3.4339 | 1.8277 | 3.7366 | 1.5848 | 2.3815 | 2.6129 | 2.0177 | 3.2177 | 2.0657 | 4.2466 | -0.66655 | -2.0612 | 3.878 | 2.8465 | 1.7523 | 1.8092
S-1 | 35 | Amulia 33/11 kv | 34 | -0.20426 | 0.27324 | 1.3384 | 2.2922 | 0.13016 | -0.45214 | 0.64885 | 0.87963 | 0.18882 | 0.016725 | 0.01694 | 0.0086681 | -0.0074141 | 0.86386 | -0.074012 | 0.14547 | 2.1498 | 0.38089 | -0.47118 | 1.1297 | -0.80877 | -0.14378 | 1.7338 | 2.01 | 3.7029 | 2.0721 | 1.5472 | 1.4229 | 2.6673 | 2.2 | 1.3391 | 1.5612 | 3.1088 | 2.0467 | 0.87104 | 0.034855 | 3.4064 | 3.1912 | 0.62654 | 0.017251 | 3.6887 | 1.1817 | 0.45411 | 0.7583 | 0.063823 | 2.7233 | 0.082763
S-1 | 36 | New Fatullah 132/33 KV SS | 35 | -0.16978 | -0.081187 | -0.064451 | 0.39295 | 0.3876 | 0.39394 | 0.36916 | 0.43508 | 0.24831 | 0.3815 | 0.27622 | 0.35708 | 0.16899 | 0.13311 | 0.19402 | 0.093966 | 0.1682 | 0.24176 | 0.072305 | 0.049764 | 0.36235 | 0.28789 | 0.082414 | 0.57674 | 0.17456 | -0.086748 | -0.069018 | -0.079788 | -0.057915 | -0.13 | -0.047774 | 0.25329 | 0.24249 | 0.47914 | -2.1946 | 3.6391 | 0.27975 | 0.8301
S-1 | 37 | New Fatullah 33/11 KV SS | 36 | 0.078394 | 0.25585 | 0.247 | 0.7144 | 0.76103 | 0.70847 | 0.94604 | 0.94374 | 0.61604 | 0.70315 | 0.55554 | 0.6212 | 0.47384 | 0.45268 | 0.50666 | 0.38121 | 0.54205 | 0.66228 | 0.40905 | 0.47767 | 0.81699 | 0.60249 | 0.39129 | 0.98842 | 0.58705 | 0.30412 | 0.31171 | 0.30777 | 0.27377 | 1.03 | -0.11894 | 0.81935 | 0.72739 | 0.87285 | 0.095199 | 0.0749 | 0 | 2.0529
S-2 | 38 | P & T 33/11 KV SS | 37 | -0.098408 | 0.59239 | -0.69023 | 1.605 | 0.48673 | 1.6112 | 0.46242 | 0.23332 | -0.056663 | 1.0121 | 0.82185 | 2.18 | 0.20128 | 0.23407 | 1.8117 | 1.2335 | 1.8374 | 0.37184 | 0.12279 | -0.064714 | 2.3235 | -0.65716 | 1.3946 | 1.2128 | 2.0757 | 3.8787 | 2.5 | 1.001 | 1.3498 | 1.8 | 2.8624 | 0.61383 | -0.37918
S-2 | 39 | Motijheel 132/33 KV SS | 38 | -0.21338 | -0.14125 | -0.16963 | -0.12392 | -0.15352 | -0.16639 | -0.13729 | 0.73769 | 0.55339 | 0.11558 | 0.39039 | 0.039208 | 0.059869 | 0.050987 | 0.024103 | 0.070489 | 0.018073 | 0.063942 | -0.053024 | 0.34068 | 0.89054 | 0.5342 | 0.6157 | 2.2279 | 1.726 | 1.2319 | 1.4692e-14 | 0
S-2 | 40 | Motijheel 33/11 KV SS (new) | 39 | 0.32556 | 0.43035 | 0.41761 | -0.18102 | 0.22868 | -0.25709 | -0.069431 | -0.27059 | -0.11085 | -0.09126 | -0.40907 | 2.8412 | 0.4681 | 0.54018 | 0.49888 | 0.61732 | 1.0773 | 2.2037 | 0.12279 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
S-2 | 41 | Kamalapur Railway 33/11 KV SS | 40 | 1.2795 | 1.2491 | 0.53839 | 2.6306 | 2.3884 | 2.4103 | 0.83177 | 4.2379 | 2.2867 | 0.10553 | 0.051769 | 2.343 | 1.9498 | 4.2196 | 0.30651 | 2.2737 | 2.4563 | 0.1491 | -0.79821 | 1.9745 | 1.8185 | 2.1181 | 1.8157 | 0.02769 | 2.5
S-1 | 42 | Char Syedpur 132/33KV S/S | 41 | 0.14646 | 0.59854 | 0.26157 | -0.12248 | -0.19242 | -0.18229 | -0.26374 | 0.25081 | 0.040906 | -0.11633 | -0.19184 | -0.14387 | -0.28078 | 0.16644 | 0.16123 | 0.30059 | 0.083792 | 0.27267 | 0.79852 | 0.42989
S-1 | 43 | Char Syedpur 33/11 KV S/S New | 42 | -0.43094 | 0.23273 | 0.18322 | 0.46998 | 0.61927 | 0.25346 | 0.40353 | 1.0986 | 0.87877 | 1.2702 | 0.82772 | 0.59434 | 0.7397 | 0.81017 | 2.2414 | 1.3696 | 0.78557 | 0.75355 | 1.4768 | #DIV/0!
S-1 | 44 | MI CEMENT 132/33 kV | 43 | 0 | 0.033974

## NORTH-1
132 KV SIDE of___DHANMONDI 132/33/11 KV S/S | [13 empty] | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 132 KV SIDE
2: 132 KV DHANMONDI-1 CKT (IMP); 3: 132; 4: IMPORT; 6: 1; 10: 1000 | 0
2: 132 KV DHANMONDI-1 CKT(EXP); 3: 132; 6: 1; 10: 1000 |  | 0
2: 132 KV DHANMONDI-2 CKT (IMP); 3: 132; 6: 1; 10: 1000 | 0
2: 132 KV DHANMONDI-2 CKT(EXP); 3: 132; 6: 1; 10: 1000 |  | 0
| 132 KV DHANMONDI-3 CKT (IMP) | 132 |  |  | 1 |  |  |  | 1000
| 132 KV DHANMONDI-3 CKT(EXP) | 132 |  |  | 1 |  |  |  | 1000
9=8-7: Total Import/Export | 0 | 0
10: Net Total | 59777000
DHANMONDI 132 KV SIDE (RECEIVING)
2 | 132 kV Ullon Circuit-1 | 132 |  | SIEM0480 | 1 | 1632756 | 1632756 | 0 | 1000 | 0
| 132 kV Dhaka University | 132 |  | SIEM0480 | 1 | 68964 | 79348 | 10384 | 1000 | 10384000
3 | 132 kV Dhaka University | 132 |  | SIEM0488 | 1 | 281129 | 281129 | 0 | 1000 |  | 0
6 | 132 kV Ullon Circuit-2 | 132 |  | SIEM0481 | 1 | 2101057 | 2131079 | 30022 | 1000 | 30022000
8 | 132 kV Ullon Circuit-3 | 132 |  | SIEM0484 | 1 | 2857313 | 2887068 | 29755 | 1000 | 29755000
7: 0; 8: 0; 9=8-7: Total Import/Export | 70161000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 70161000
| DHANMONDI 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 132 KV Dhaka University (Export) | 132 | EXPORT |  | 1 | 281129 | 281129 | 0 | 1000 |  | 0
| 132 KV Dhaka University (Import) | 132 |  |  | 1 | 68964 | 79348 | 10384 | 1000 |  | 10384000
7: 0; 8: 0; 10: Total |  | 10384000
| DHANMONDI 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33kV, 50/75 MVA GT-4 (HV) | 132 | NET IMPORT | SIEM0487 | 1 | 858848 | 869330 | 10482 | 1000 |  | 10482000
5 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | SIEM0496 | 1 | 1455043 | 1463850 | 8807 | 2000 |  | 17614000
9 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | SIEM0493 | 1 | 1325611 | 1334171 | 8560 | 2000 |  | 17120000
10 | 132/33kV, 80/120 MVA GT-3 (HV) | 132 |  | SIEM0497 | 1 | 1286041 | 1298503 | 12462 | 2000 |  | 24924000
10: Total |  | 70140000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV DHANMONDI-3 CKT(EXP); 4: 70140000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 70140000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 70140000 | 132/33 kv GT LV Side |  | 69813600
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 326400
2: IMPORT-4 | LOSS % IN => |  | 0.4654%
| 132 KV TOTAL IMPORT |  | 70140000
1: 33 KV SIDE of___DHANMONDI 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2210.16 | 2234.48 | 24.32 | 720000 | 17510400
12 | 132/33 kV GT-2 Incoming | 33 |  | BD001818 | 1 | 2179.89 | 2203.57 | 23.68 | 720000 | 17049600
17 | 132/33 kV GT-3 Incoming | 33 |  | BD001863 | 1 | 1898.61 | 1933.1 | 34.49 | 720000 | 24832800
24 | 132/33 kV GT-4 Incoming | 33 |  | BD001916 | 1 | 1780.89 | 1802.6 | 21.71 | 480000 | 10420800
7: 0; 8: 0; 10: Total | 69813600 |  | 0
| DHANMONDI 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 |  |  |  |  | 15363980.8512 | Dhanmondi 33/11 kv ss | 0.46983 | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33/11 kV 20/28 MVA T-1 | 33 |  | BD001861 | 1 | 2052.39 | 2082.67 | 30.28 | 240000 |  | 7267200 | 7271355.7389 |  |  |  |  | 33/11 kV 20/28 MVA T-1 | 7271355.7389 | 6808513.9804 | 462841.7585 | 6.798 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 |  | BD001892 | 1 | 2349.96 | 2383.66 | 33.7 | 240000 |  | 8088000 | 8092625.1123 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 8092625.1123 | 8162534.3912 | -69909.2789 | -0.85647 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 15355200 | 15363980.8512 |  |  |  |  | 33 KV Feeders | 15363980.8512 | 14971048.3716 | 392932.4796 | 2.6246 | OK
5 | New Ramna Circuit-1 | 33 |  | BD001919 | 1 | 1451.13 | 1460.93 | 9.8 | 240000 |  | 2352000 | 2353344.9882 |  | 6190738.1423 | New Ramna 33/11 kv ss | 1.773 | New Ramna Circuit-1 | 2353344.9882 | 3773971.7832 | -1420626.7951 | -37.6428 | OK
8 | Kakrail Circuit-1 | 33 |  | BD001825 | 1 | 804.13 | 826.76 | 22.63 | 240000 |  | 5431200 | 5434305.8247 |  |  |  |  | Kakrail Circuit-1 | 5434305.8247 | 5236025.7374 | 198280.0873 | 3.7868 | OK
9 | Kawran Bazar Circuit-1 | 33 |  | BD001820 | 1 | 1826.25 | 1843.63 | 17.38 | 240000 |  | 4171200 | 4173585.2953 |  | 11010292.6232 | Kakrail 33/11 kv ss | 1 | Kawran Bazar Circuit-1 | 4173585.2953 | 3584312.8959 | 589272.3994 | 16.4403 | OK
10 | New Ramna Circuit-2 | 33 |  | BD001816 | 1 | 1176.39 | 1192.37 | 15.98 | 240000 |  | 3835200 | 3837393.1542 |  |  |  |  | New Ramna Circuit-2 | 3837393.1542 | 2840081.8191 | 997311.3351 | 35.1156 | OK
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 |  | 0 | 0 |  | 4173585.2953 | Kawran Bazar 33/11 kv ss | 0.49247 | Kawran BazarCircuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | DMC Hospital Feeder | 33 |  | BD001840 | 1 | 391.38 | 405.5 | 14.12 | 240000 |  | 3388800 | 3390737.8809 |  |  |  |  | DMC Hospital Feeder | 3390737.8809 | 3327433.1371 | 63304.7438 | 1.9025 | OK
15 | Green Road Circuit-2 (U/G) | 33 |  | BD001918 | 1 | 2059.78 | 2087.7 | 27.92 | 240000 |  | 6700800 | 6704631.8438 |  | 3390737.8809 | DMC Hospital 33/11 kv ss | 2.024 | Green Road Circuit-2 (U/G) | 6704631.8438 | 6698079.6916 | 6552.1522 | 0.097821 | OK
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1589.15 | 1612.37 | 23.22 | 240000 |  | 5572800 | 5575986.7985 |  |  |  |  | Kakrail Circuit-2 | 5575986.7985 | 5675362.1473 | -99375.3488 | -1.751 | OK
18 | BSMMU Hospital Circuit-1 | 33 |  | BD001920 | 1 | 694.88 | 710.95 | 16.07 | 240000 |  | 3856800 | 3859005.5061 |  | 14307376.979 | Green Road 33/11 kv ss | 0.39606 | BSMMU Hospital Circuit-1 | 3859005.5061 | 3663537.4944 | 195468.0117 | 5.3355 | OK
19 | Azimpur Circuit-1 | 33 |  | BD001822 | 1 | 1942.41 | 1978.52 | 36.11 | 240000 |  | 8666400 | 8671355.8696 |  |  |  |  | Azimpur Circuit-1 | 8671355.8696 | 8589867.074 | 81488.7956 | 0.94866 | OK
20 | Azimpur Circuit-2 | 33 |  | BD001857 | 1 | 1804.37 | 1809.7 | 5.33 | 240000 |  | 1279200 | 1279931.5089 |  | 5400686.6106 | BSMMU 33/11 kv ss | 0.51158 | Azimpur Circuit-2 | 1279931.5089 | 0 | 1279931.5089 | #DIV/0! | #DIV/0!
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 145.23 | 151.65 | 6.42 | 240000 |  | 1540800 | 1541681.1045 |  |  |  |  | BSMMU Hospital Circuit-2 | 1541681.1045 | 1318009.2296 | 223671.8748 | 16.9704 | OK
23 | Green Road Circuit-1 | 33 |  | BD001865 | 1 | 1379.43 | 1411.09 | 31.66 | 240000 |  | 7598400 | 7602745.1352 |  | 9951287.3785 | Azimpur 33/11 kv ss | 1.3852 | Green Road Circuit-1 | 7602745.1352 | 7610362.9471 | -7617.8119 | -0.1001 | OK
26 | 33/0.4 kV, 500 kVA AT-1 | 0.4 |  | 84.2659 | 1 | 313699 | 316189 | 2490 | 10 |  | 24900 | 24914.239 | Paribag |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 24914.239 | 24707.6715 | 206.5675 | 0.83605 | OK
25 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 |  | 84.2673 | 1 | 478688 | 478688 | 0 | 10 |  | 0 | 0 | Paribag |  |  |  | 33/0.4 kV, 1000 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 54418500 | 54449619.1488 | [5 empty] | 54449619.1488 | 52341751.6284 | 2107867.5204 | 4.0271 | OK
9=8-7: Grand Total | 69813600 | 69773700 | 69813600 | 0.057185
1: 11 KV SIDE of___DHANMONDI 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 11 KV SIDE
15 | 33/11 kV Transformer-2 Incoming | 11 | IMPORT | DHK60884 | 1 | 845791.6 | 890566.5 | 44774.9 | 180 | 8059482 |  | 8112980.4513
16 | 33/11 kV Transformer-1 Incoming | 11 |  | DHK60976 | 1 | 455929.7 | 495947.4 | 40017.7 | 180 | 7203186 |  | 7251000.3999
7: 0; 8: 0; 10: Total | 15262668 |  | 15363980.8512
| DHANMONDI 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 5173196 | 6440974 | 1267778 | 1 |  | 1267778 | 1273734.3863 | Paribag |  |  |  | 11 kV Balaka Feeder | 1273734.3863 | 1257653.9222 | 16080.4641 | 1.2786 | OK
5 | 11 kV Mogbazar O/H | 11 |  | HA021100463-02 | 1 | 46129640 | 47694141 | 1564501 | 1 |  | 1564501 | 1571851.4764 | Paribag |  |  |  | 11 kV Mogbazar O/H | 1571851.4764 | 1518772.8573 | 53078.6191 | 3.4948 | OK
6 | 11 kV Panthopath Feeder | 11 |  | HA021101078-02 | 1 | 59070322 | 61262551 | 2192229 | 1 |  | 2192229 | 2202528.7234 | Paribag |  |  |  | 11 kV Panthopath Feeder | 2202528.7234 | 2146238.9144 | 56289.809 | 2.6227 | OK
7 | 11 kV Shahbagh Feeder ( old University O/H) | 11 |  | DHK60882 | 1 | 208836.3 | 215574 | 6737.7 | 60 |  | 404262 | 406161.3393 | Paribag |  |  |  | 11 kV Shahbagh Feeder ( old University O/H) | 406161.3393 | 416714.2185 | -10552.8792 | -2.5324 | OK
8 | 11 kV P G Hospital Feeder | 11 |  | DHK60889 | 1 | 279161.7 | 283084.6 | 3922.9 | 60 |  | 235374 | 236479.8549 | Paribag |  |  |  | 11 kV P G Hospital Feeder | 236479.8549 | 217917.4597 | 18562.3951 | 8.5181 | OK
9 | 11 kV Abdul Monem Ltd | 11 |  | DHK60890 | 1 | 691.92 | 699.41 | 7.49 | 60000 |  | 449400 | 451511.4107 | Paribag |  |  |  | 11 kV Abdul Monem Ltd | 451511.4107 | 418508.0827 | 33003.328 | 7.8859 | OK
10 | 11 kV Surjasen Hall Feeder | 11 |  | DHK60880 | 1 | 538943.6 | 552176.6 | 13233 | 60 |  | 793980 | 797710.3468 | Ramna |  |  |  | 11 kV Surjasen Hall Feeder | 797710.3468 | 762400.0883 | 35310.2585 | 4.6315 | OK
11 | 11 kV Azimpur-1 Feeder | 11 |  | DHK60872 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV TSC Feeder | 11 |  | DHK60873 | 1 | 918512 | 928405.7 | 9893.7 | 60 |  | 593622 | 596411.0072 | Ramna |  |  |  | 11 kV TSC Feeder | 596411.0072 | 501019.2093 | 95391.7979 | 19.0395 | OK
13 | 11 kV SCADA Bhaban | 11 |  | DHK60883 | 1 | 28074.3 | 28176.9 | 102.6 | 60 |  | 6156 | 6184.9227 | Paribag |  |  |  | 11 kV SCADA Bhaban | 6184.9227 | 6569.6736 | -384.751 | -5.8565 | OK
14 | 11 kV DPH Sw/S-2 | 11 |  | DHK60871 | 1 | 474478.5 | 493864.3 | 19385.8 | 60 |  | 1163148 | 1168612.8044 | Paribag |  |  |  | 11 kV DPH Sw/S-2 | 1168612.8044 | 1138030.0608 | 30582.7436 | 2.6873 | OK
17 | 11 kV New Elephant Road Feeder | 11 |  | DHK60981 | 1 | 61120.9 | 82214.7 | 21093.8 | 60 |  | 1265628 | 1271574.285 | Paribag |  |  |  | 11 kV New Elephant Road Feeder | 1271574.285 | 1340854.1319 | -69279.847 | -5.1668 | OK
18 | 11 kV Dhanmondi O/H Feeder | 11 |  | DHK61110 | 1 | 380880.9 | 404842.1 | 23961.2 | 60 |  | 1437672 | 1444426.5973 | Paribag |  |  |  | 11 kV Dhanmondi O/H Feeder | 1444426.5973 | 1452129.1083 | -7702.5111 | -0.53043 | OK
19 | 11 kV Sonargaon Feeder | 11 |  | DHK61115 | 1 | 312180.8 | 340916.2 | 28735.4 | 60 |  | 1724124 | 1732224.4313 | Paribag |  |  |  | 11 kV Sonargaon Feeder | 1732224.4313 | 1700265.2603 | 31959.171 | 1.8797 | OK
20 | 11 kV Museum Feeder | 11 |  | DHK61107 | 1 | 545315.1 | 547755.5 | 2440.4 | 60 |  | 146424 | 147111.9421 | Ramna |  |  |  | 11 kV Museum Feeder | 147111.9421 | 139723.2891 | 7388.653 | 5.2881 | OK
21 | 11 kV Shanta property | 11 |  | DHK61112 | 1 | 338664.1 | 342098.2 | 3434.1 | 60 |  | 206046 | 207014.0635 | Paribag |  |  |  | 11 kV Shanta property | 207014.0635 | 222651.1173 | -15637.0539 | -7.0231 | OK
22 | 11 kV BIRDEM RMU Feeder | 11 |  | DHK61108 | 1 | 685561.8 | 701416.8 | 15855 | 60 |  | 951300 | 955769.4815 | Kakrail |  |  |  | 11 kV BIRDEM RMU Feeder | 955769.4815 | 767058.4747 | 188711.0068 | 24.6019 | OK
23 | 11 kV Azimpur-2 Feeder | 11 |  | DHK61109 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Azimpur |  |  |  | 11 kV Azimpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11 kV DPH Sw/S-1 | 11 |  | DHK60978 | 1 | 767608.4 | 782449.9 | 14841.5 | 60 |  | 890490 | 894673.7786 | Kakrail |  |  |  | 11 kV DPH Sw/S-1 | 894673.7786 | 964542.5031 | -69868.7245 | -7.2437 | OK
10: Total | 15363980.8512 | 15292134 | 15363980.8512 | 0.46983
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[6 empty] | Paribag at 33 KV level |  |  | 11997218.5341
[6 empty] | Azimpur at 33 KV level |  |  | 0
[6 empty] | Ramna at 33 KV level |  |  | 1541233.2961
[6 empty] | Kakrail at 33 KV level |  |  | 1850443.26
7: Total =; 10: 15388895.0903 | -5.0932e-10
1: 33 KV SIDE of___KAWRANBAZAR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHMANDI 33 KV SIDE
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1826.25 | 1843.63 | 17.38 | 240000 | 0 | 4171200 | 4173585.2953
11 | Kawran BazarCircuit-2 | 33 |  | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0
10: Total | 0 | 4171200 | 4173585.2953
MOGBAZAR 33 KV SIDE
14 | 33KV Karwan Bazar | 33 | 0 | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 | 0 | 0 | 0
10: Total | 0 | 0 | 0
KAWRANBAZAR 33 KV SIDE (RECEIVING)
1 | 33 kV Dhanmondi Circuit-1 | 33 |  | DHK61036 | 1 | 3405.32 | 3420.84 | 15.52 | 270000 | 4190400
5 | 33 kV Dhanmondi Circuit-2 | 33 |  | DHK61037 | 1 | 1157.06 | 1157.06 | 0 | 270000 | 0
4 | 33 kV Moghbazar | 33 |  | DHK 61038 | 1 | 1059.48 | 1059.48 | 0 | 270000 | 0
7: 0; 8: 0; 10: Total | 4190400 | 0 | 4173585.2953
| KAWRANBAZAR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| KAWRANBAZAR 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | DHK61039 | 1 | 5111.93 | 5135.19 | 23.26 | 180000 |  | 4186800
3 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | DHK61040 | 1 | 3308.49 | 3308.49 | 0 | 180000 |  | 0
10: Total |  | 4186800
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: DHMANDI 33 KV SIDE; 4: 4173585.2953; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 4173585.2953
2: MOGBAZAR 33 KV SIDE; 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 4173585.2953 | 33 KV TX HV SIDE |  | 4186800
2: IMPORT-3 | LOSS UNITS=> |  | -13214.7047
2: IMPORT-4 | LOSS % IN => |  | -0.3166%
| TOTAL IMPORT |  | 4173585.2953
1: 11 KV SIDE of___KAWRANBAZAR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAWRANBAZAR 11 KV SIDE
14 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK00182 | 1 | 13643.5 | 14055.6 | 412.1 | 10000 | 4121000 |  | 4173585.2953
15 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK00184 | 1 | 75128.4 | 75128.4 | 0 | 10000 | 0 |  | 0
7: 0; 8: 0; 10: Total | 4121000 |  | 4173585.2953
| KAWRANBAZAR 11 KV SIDE |  |  |  |  | 0 | 0
6 | WASA Bhaban | 11 |  | 8536188 | 1.2 | 2288.8 | 2503.3 | 214.5 | 1000 | 1046400 | 1046400 | 1051553.1772 | Shere b.nagar | From Customer End |  |  | WASA Bhaban | 1051553.1772 | 992894.4687 | 58658.7085 | 5.9078 | OK
7 | Sangsad Bhaban | 11 |  | 8536178 | 1.2 | 568300 | 572139 | 3839 | 44 |  | 202699.2 | 203697.4272 | Shere b.nagar |  |  |  | Sangsad Bhaban | 203697.4272 | 26163.5003 | 177533.9269 | 678.5557 | FAULT
8 | Air Port Road (West) | 11 |  | 8536182 | 1.2 | 100568.1 | 101503.6 | 935.5 | 1000 |  | 1122600 | 1128128.4372 | Shere b.nagar |  |  |  | Air Port Road (West) | 1128128.4372 | 1054483.651 | 73644.7863 | 6.984 | OK
9 | ICC (PM Office) | 11 |  | 8536193 | 1.2 | 32421.4 | 32421.4 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | ICC (PM Office) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | (UTC) Tower | 11 |  | DHK00183 | 1.2 | 15079.3 | 15757.4 | 678.1 | 444.44 |  | 361649.7168 | 363430.7232 | Shere b.nagar |  |  |  | (UTC) Tower | 363430.7232 | 289733.3028 | 73697.4203 | 25.4363 | OK
11 | Sonargaon Hotel | 11 |  | 8536190 | 1.2 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 62854.4448 | 63163.9823 | Kakrail | 4 days load Estimated |  |  | Sonargaon Hotel | 63163.9823 | 0 | 63163.9823 | #DIV/0! | #DIV/0!
12 | Panthopath | 11 |  | 8536184 | 1.2 | 34310.5 | 35309.1 | 998.6 | 1000 |  | 1198320 | 1204221.3334 | Shere b.nagar |  |  |  | Panthopath | 1204221.3334 | 1027392.6275 | 176828.7059 | 17.2114 | OK
13 | Titas Bhaban | 11 |  | DHK00190 | 1.2 | 55463.3 | 55753.9 | 290.6 | 444.44 |  | 154985.1168 | 155748.3677 | Kakrail |  |  |  | Titas Bhaban | 155748.3677 | 190247.4883 | -34499.1206 | -18.1338 | OK
16 | Green Road Dormatory s/s | 11 |  | DHK00021 | 1.2 | 0 | 0 | 0 | 444.44 |  | 0 | 0 |  |  |  |  | Green Road Dormatory s/s | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | Aux. Transformer, AT-1 | 11 |  | 85-12906 | 1.2 | 68255 | 68557 | 302 | 10 |  | 3624 | 3641.847 | Shere b.nagar |  |  |  | Aux. Transformer, AT-1 | 3641.847 | 3397.8572 | 243.9898 | 7.1807 | OK
27 | Aux. Transformer, AT-2 | 11 |  | 85-12909 | 1.2 | 58961 | 58961 | 0 | 10 |  | 0 | 0 | Shere b.nagar |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 4173585.2953 | 4153132.4784 | 4173585.2953 | 0.49247
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail at 33 KV level |  |  | 218912.3501
[5 empty] | Shere b.nagar at 33 KV level |  |  | 3954672.9452
[5 empty] | Total = |  |  | 4173585.2953 | 0
9=8-7: Customer Name; 10: Customer Number | Feeder name | Consumption | OMF
9=8-7: Square Hospital; 10: 27529489 | Wasa Bhaban | 1046400 | 6000
9=8-7: NOCS Name; 10: Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
9=8-7: ShereBangla Nagar; 10: 2365.07 | 2489.44 | 923.01 | 973.04
1: 33 KV SIDE of___NEW RAMNA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1451.13 | 1460.93 | 9.8 | 240000 | 0 | 2352000 | 2353344.9882
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1176.39 | 1192.37 | 15.98 | 240000 | 0 | 3835200 | 3837393.1542
10: Total | 0 | 6187200 | 6190738.1423
NARINDA 33 KV SIDE
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 2505600 | 2516574.0224
10: Total | 0 | 2505600 | 2516574.0224
NEW RAMNA 33 KV SIDE (RECEIVING)
3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0; 10: 180 |  | 0
3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
3: 33; 6: 1; 9=8-7: 0; 10: 180000 |  | 0
10: Total |  | 0 | 8707312.1647
NEW RAMNA 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT; 9=8-7: 0 |  | 0
2: Feeder No.2; 3: 33; 9=8-7: 0 |  | 0
10: Total |  | 0 | 0
NEW RAMNA 33 KV SIDE
2: 33/11 KV Transformer No.1.; 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
2: 33/11 KV Transformer No.2.; 3: 33; 6: 1; 9=8-7: 0 |  | 0
2: 33/11 KV Transformer No.3.; 3: 33; 6: 1; 9=8-7: 0 |  | 0
10: Total |  | 0 | 8707312.1647 | #DIV/0!
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: DHANMONDI 33 KV SIDE; 4: 6190738.1423; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 8707312.1647
2: NARINDA 33 KV SIDE; 4: 2516574.0224; 6: 33 KV NET IMPORT; 9=8-7: 8707312.1647 | 33 KV TX HV SIDE |  | 8707312.1647
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 8707312.1647
1: 11 KV SIDE of___NEW RAMNA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
NEW RAMNA 11 KV SIDE
14 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK 00002 | 1 | 24930.5 | 25162.8 | 232.3 | 10000 | 2323000 |  | 2345006.2788
15 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK 00007 | 1 | 13167.7 | 13547.4 | 379.7 | 10000 | 3797000 |  | 3832969.798
27 | 33/11 kV, 20/28 MVA T-3 (LV) Incoming | 11 |  | DHKA2182 | 1 | 583.17 | 597.09 | 13.92 | 180000 | 2505600 |  | 2529336.0879
10: Total | 8625600 |  | 8707312.1647
NEW RAMNA 11 KV SIDE
4 | Police Bhaban | 11 |  | DHK 00005 | 1 | 73101.3 | 73369.4 | 268.1 | 444.44 |  | 119154.364 | 121266.9463 | Ramna |  |  |  | Police Bhaban | 121266.9463 | 121013.0538 | 253.8925 | 0.20981 | OK
5 | Water Works | 11 |  | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Lalbag |  |  |  | Water Works | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | GPO | 11 |  | DHK 00060 | 1 | 97916.8 | 98412.6 | 495.8 | 444.44 |  | 220353.352 | 224260.1714 | Ramna |  |  |  | GPO | 224260.1714 | 278965.4908 | -54705.3194 | -19.6101 | OK
7 | Culvert Road | 11 |  | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 80 | 973062.72 | 990314.9211 | Ramna |  |  |  | Culvert Road | 990314.9211 | 787025.6832 | 203289.2379 | 25.8301 | OK
8 | Secretariat (East) | 11 |  | DHK00059 | 1 | 81719.4 | 81723.1 | 3.7 | 444.44 |  | 1644.428 | 1673.5834 | Ramna |  |  |  | Secretariat (East) | 1673.5834 | 2240.1359 | -566.5525 | -25.291 | OK
9 | Siddik Bazar | 11 |  | DHK00076 | 1 | 29231.2 | 30335.3 | 1104.1 | 444.44 |  | 490706.204 | 499406.3237 | Bangshal |  |  |  | Siddik Bazar | 499406.3237 | 894134.2296 | -394727.9059 | -44.1464 | CHECK
10 | Bokshi Bazar | 11 |  | DHK 00206 | 1 | 85464 | 86520.6 | 1056.6 | 444.44 |  | 469595.304 | 477921.1318 | Ramna |  |  |  | Bokshi Bazar | 477921.1318 | 520717.296 | -42796.1642 | -8.2187 | OK
11 | Ramna 11 kV Sw/S Circuit-1 | 11 |  | DHK00198 | 1 | 46597.3 | 46678.5 | 81.2 | 444.44 |  | 36088.528 | 36728.3702 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-1 | 36728.3702 | 1058898.5083 | -1022170.1381 | -96.5315 | CHECK
12 | TNT RMU | 11 |  | DHK 00207 | 1 | 60351.5 | 61321.1 | 969.6 | 444.44 |  | 430929.024 | 438569.3066 | Ramna |  |  |  | TNT RMU | 438569.3066 | 426631.5896 | 11937.717 | 2.7981 | OK
13 | DIT 11 kV Sw/S Circuit-1 | 11 |  | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 |  | 0 | 0 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Secretariat (West) | 11 |  | DHK 00006 | 1 | 67894.2 | 69075.5 | 1181.3 | 444.44 |  | 525016.972 | 534325.4145 | Ramna |  |  |  | Secretariat (West) | 534325.4145 | 379223 | 155102.4145 | 40.9001 | FAULT
17 | Ramna 11 kV Sw/S Circuit-2 | 11 |  | DHK00197 | 1 | 84763.4 | 86438.2 | 1674.8 | 444.44 |  | 744348.112 | 757545.2503 | Ramna |  |  |  | Ramna 11 kV Sw/S Circuit-2 | 757545.2503 | 868.6241 | 756676.6262 | 87112.091 | FAULT
18 | Sayed Nazrul Islam Road | 11 |  | DHK00186 | 1 | 24569.9 | 27519.2 | 2949.3 | 444.44 |  | 1310786.892 | 1334026.873 | Ramna |  |  |  | Sayed Nazrul Islam Road | 1334026.873 | 1329086.3239 | 4940.5491 | 0.37173 | OK
19 | Gulistan Complex | 11 |  | DHK00030 | 1 | 54446.3 | 54911.6 | 465.3 | 444.44 |  | 206797.932 | 210464.4166 | Ramna |  |  |  | Gulistan Complex | 210464.4166 | 215693.0819 | -5228.6652 | -2.4241 | OK
20 | Mohanagor Nattomanso | 11 |  | DHK 00008 | 1 | 99840.8 | 99993.3 | 152.5 | 444.44 |  | 67777.1 | 68978.774 | Ramna |  |  |  | Mohanagor Nattomanso | 68978.774 | 72827.2741 | -3848.5002 | -5.2844 | OK
21 | DIT 11 kV Sw/S Circuit-2 | 11 |  | DHK00196 | 1 | 24947 | 26040.2 | 1093.2 | 444.44 |  | 485861.808 | 494476.0375 | Motijheel |  |  |  | DIT 11 kV Sw/S Circuit-2 | 494476.0375 | 481492.0598 | 12983.9777 | 2.6966 | OK
22 | Jail | 11 |  | DHK00009 | 1 | 0 | 0 | 0 | 444.44 |  | 0 | 0 | Bangshal |  |  |  | Jail | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Kosturi Bazar | 11 |  | HA021100713-02 | 1 | 75962552 | 76731766 | 769214 | 1 |  | 769214 | 782852.0054 | Ramna |  |  |  | Kosturi Bazar | 782852.0054 | 108530.1819 | 674321.8235 | 621.3219 | FAULT
24 | Kaptan Bazar | 11 |  | HA021101251-02 | 1 | 6236867 | 6664226 | 427359 | 1 |  | 427359 | 434935.9868 | Narinda |  |  |  | Kaptan Bazar | 434935.9868 | 427872.7434 | 7063.2434 | 1.6508 | OK
25 | G.T.V | 11 |  | HA-021101054-02 | 1 | 71120147 | 71762722 | 642575 | 1 |  | 642575 | 653967.7221 | Ramna |  |  |  | G.T.V | 653967.7221 | 639660.2776 | 14307.4445 | 2.2367 | OK
26 | Kazi Alauddin Road | 11 |  | HA021100951-02 | 1 | 6043531 | 6674283 | 630752 | 1 |  | 630752 | 641935.1027 | Bangshal |  |  |  | Kazi Alauddin Road | 641935.1027 | 386345.3523 | 255589.7504 | 66.1558 | FAULT
28 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 |  | 2436 | 1 | 67423 | 67423 | 0 | 10 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 |  | 2437 | 1 | 88447 | 88807 | 360 | 10 |  | 3600 | 3663.8273 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 3663.8273 | 3672.2594 | -8.4322 | -0.22962 | OK
10: Grand Total | 8707312.1647 | 8555622.74 | 8707312.1647 | 1.773
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 6636558.7139
[5 empty] | Lalbag | at 33 KV level |  | 0
[5 empty] | Bangshal | at 33 KV level |  | 1141341.4264
[5 empty] | Motijheel | at 33 KV level |  | 494476.0375
[5 empty] | Narinda | at 33 KV level |  | 434935.9868
[5 empty] | Total = |  |  | 8707312.1647 | 0
1: 33 KV SIDE of___ KAKRAIL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi 33 KV SIDE
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 804.13 | 826.76 | 22.63 | 240000 | 0 | 5431200 | 5434305.8247
16 | Kakrail Circuit-2 | 33 |  | BD001821 | 1 | 1589.15 | 1612.37 | 23.22 | 240000 | 0 | 5572800 | 5575986.7985
10: Total | 0 | 11004000 | 11010292.6232
ULLON 33 KV SIDE
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9083 | 1163.9096 | 0.0013 | 240000 | 0 | 312 | 312.7997
10: Total | 0 | 312 | 312.7997
Taltola 33 KV SIDE
| 33 KV Kakrail Feeder | 33 | IMPORT |  | 1 | 226957 | 226957 | 0 | 1000 |  | 0
8: 0; 10: Total | 0 | 0 | 0
| KAKRAIL 33 KV SIDE (RECEIVING) | [5 empty] | 0
5 | 33 kV Dhanmondi-2 | 33 |  | 06604376 | 1 | 5254.06 | 5285.05 | 30.99 | 180000 | 5578200
2 | 33 kV Dhanmondi-1 | 33 |  | 06604375 | 1 | 2009.03 | 2039.54 | 30.51 | 180000 | 5491800
| 33 KV Kakrail From ULLON | 33 |  |  | 1 | 2063.69 | 2063.69 | 0 | 180000 | 0
| 33KV Kakrail From Taltola | 33 |  |  | 1 | 361.91 | 361.91 | 0 | 180000 | 0
10: Total | 11070000 | 0 | 0
KAKRAIL 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
KAKRAIL 33 KV SIDE
2: 33/11 KV Transformer No.1.; 3: 33; 4: NET IMPORT; 6: 1; 9=8-7: 0 |  | 0
2: 33/11 KV Transformer No.2.; 3: 33; 6: 1; 9=8-7: 0 |  | 0
10: Total |  | 0 | 0 | #DIV/0!
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Dhanmondi 33 KV SIDE; 4: 11010292.6232; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KAKRAIL 33 KV NET IMPORT |  | 11010605.4228
2: ULLON 33 KV SIDE; 4: 312.7997; 6: KAKRAIL 33 KV NET IMPORT; 9=8-7: 11010605.4228 | KAKRAIL KV NET IMPORT |  | 10888001.361
2: Taltola 33 KV SIDE; 4: 0 | LOSS UNITS=> |  | 122604.0618
2: IMPORT-4 | LOSS % IN => |  | 1.114%
| TOTAL IMPORT |  | 11010605.4228
1: 11 KV SIDE of___KAKRAIL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KAKRAIL 11 KV SIDE
14 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK00017 | 1 | 18397 | 19004 | 607 | 8888.89 | 5395556.23 |  | 5456312.7534
15 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK00018 | 1 | 5079 | 5696.9 | 617.9 | 8888.89 | 5492445.131 |  | 5554292.6694
7: 0; 8: 0; 10: Total | 10888001.361 |  | 11010605.4228
| KAKRAIL 11 KV SIDE |  |  |  |  | 0 | 0
7 | Pioneer | 11 |  | 06604395 | 1 | 23746.79 | 23854.78 | 107.99 | 8000 |  | 863920 | 872559.2 | Ramna |  |  |  | Pioneer | 872559.2 | 859758.1646 | 12801.0354 | 1.4889 | OK
8 | Pir Saheber Goli | 11 |  | DHK-00102 | 1 | 79643 | 83183.5 | 3540.5 | 444.444 |  | 1573553.982 | 1589289.5218 | Rajarbag |  |  |  | Pir Saheber Goli | 1589289.5218 | 1570646.0565 | 18643.4653 | 1.187 | OK
9 | Montri Para | 11 |  | DHK-00110 | 1 | 12608.2 | 12700.2 | 92 | 2222.22 |  | 204444.24 | 206488.6824 | Kakrail |  |  |  | Montri Para | 206488.6824 | 233752.6835 | -27264.0011 | -11.6636 | OK
10 | Baily Road 11 kV Sw/S-2 | 11 |  | 9119865 | 1 | 62736.7 | 65421.2 | 2684.5 | 1000 |  | 2684500 | 2711345 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-2 | 2711345 | 2187071.9465 | 524273.0535 | 23.9715 | OK
11 | Jamuna U/G 11 KV Jonaki O/H | 11 |  | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 |  | 0 | 0 | Rajarbag |  |  |  | Jamuna U/G 11 KV Jonaki O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | High Court | 11 |  | 1025651 | 1 | 28975.9 | 29238.4 | 262.5 | 1000 |  | 262500 | 265125 | Ramna |  |  |  | High Court | 265125 | 281963.0422 | -16838.0422 | -5.9717 | OK
13 | Secretaiat | 11 |  | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 |  | 0 | 0 | Ramna |  |  |  | Secretaiat | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Shanti Nagar Bazar | 11 |  | 06604402 | 1 | 5631.51 | 5671.14 | 39.63 | 40000 |  | 1585200 | 1601052 | Rajarbag |  |  |  | Shanti Nagar Bazar | 1601052 | 1588931.4952 | 12120.5048 | 0.76281 | OK
17 | Tottho Bhovon | 11 |  | 9119867 | 1 | 32076 | 32298 | 222 | 1000 |  | 222000 | 224220 | Kakrail |  |  |  | Tottho Bhovon | 224220 | 214756.2499 | 9463.7501 | 4.4067 | OK
18 | Central Police Hospital/ PNT (Circuit House) | 11 |  | DHK00199 | 1 | 78368.5 | 78681.8 | 313.3 | 2222.22 |  | 696221.526 | 703183.7413 | Kakrail |  |  |  | Central Police Hospital/ PNT (Circuit House) | 703183.7413 | 652674.6032 | 50509.1381 | 7.7388 | OK
19 | Baily Road 11 kV Sw/S-1 | 11 |  | DHK00027 | 1 | 55235.8 | 55889.6 | 653.8 | 2222.22 |  | 1452887.436 | 1467416.3104 | Kakrail |  |  |  | Baily Road 11 kV Sw/S-1 | 1467416.3104 | 1045890.5162 | 421525.7941 | 40.3031 | FAULT
20 | Bijoy Nagar | 11 |  | D1025656 | 1 | 65886.7 | 66935.36 | 1048.66 | 1000 |  | 1048660 | 1059146.6 | Ramna |  |  |  | Bijoy Nagar | 1059146.6 | 1027245.6372 | 31900.9628 | 3.1055 | OK
21 | Shilpakala Academy | 11 |  | D0086137 | 1 | 25394.3 | 25965.1 | 570.8 | 1000 |  | 570800 | 576508 | Ramna |  |  |  | Shilpakala Academy | 576508 | 916863.5723 | -340355.5723 | -37.1217 | OK
22 | Judges Complex | 11 |  | 06604344 | 1 | 670.94 | 674.7 | 3.76 | 40000 |  | 150400 | 151904 | Kakrail |  |  |  | Judges Complex | 151904 | 129118.504 | 22785.496 | 17.647 | OK
23 | Auxiliary Transformer, AT-1 | 11 |  | 39333 | 1 | 492441 | 492441 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Auxiliary Transformer, AT-2 | 11 |  | 39254 | 1 | 1195010 | 1195010 | 0 | 1 |  | 0 | 0 | Kakrail |  |  |  | Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 11428238.0558 | 11315087.184 | 11428238.0558 | 1
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2773338.8
[5 empty] | Rajarbag | at 33 KV level |  | 3190341.5218
[5 empty] | Kakrail | at 33 KV level |  | 5464557.734
[5 empty] | Total = |  |  | 11428238.0558 | 0
1: 33 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
DHANMONDI 33 KV SIDE
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 694.88 | 710.95 | 16.07 | 240000 | 0 | 3856800 | 3859005.5061
22 | BSMMU Hospital Circuit-2 | 33 |  | BD001862 | 1 | 145.23 | 151.65 | 6.42 | 240000 | 0 | 1540800 | 1541681.1045
10: Total |  | 5397600 | 5400686.6106 | 0.057185
BSMMU HOSPITAL 33 KV SIDE (RECEIVING)
3 | 33 kV Dhanmondi Incoming Circuit-1 | 33 |  | BD017073 | 1 | 64006.23 | 67868.12 | 3861.89 | 1000 | 3861890
4 | 33 kV Dhanmondi Incoming Circuit-2 | 33 |  | BD017074 | 1 | 34819.01 | 36358.02 | 1539.01 | 1000 | 1539010
| 33 KV Ullon-1 Feeder | 33 |  | DHK68132 | 1 | 349.1 | 349.1 | 0 | 180000 | 0
7: 0; 8: 0; 10: Total | 5400900 | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0 |  | Total
[6 empty] | 0 | 0
| BSMMU HOSPITAL 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017072 | 1 | 92337.81 | 96695.65 | 4357.84 | 888.89 |  | 3873640.3976
6 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017076 | 1 | 32017.33 | 33755.06 | 1737.73 | 888.89 |  | 1544650.8197
10: Total |  | 5418291.2173
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: DHANMONDI 33 KV SIDE; 4: 5400686.6106; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5400686.6106
6: 33 KV NET IMPORT; 9=8-7: 5400686.6106 | 33/11 KV XF HV SIDE |  | 5418291.2173
[10 empty] | LOSS UNITS=> |  | -17604.6067
[10 empty] | LOSS % IN => |  | -0.326%
| TOTAL IMPORT |  | 5400686.6106
1: 11 KV SIDE of___BSMMU HOSPITAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
BSMMU HOSPITAL 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD017081 | 1 | 69838.24 | 73678.91 | 3840.67 | 1000 | 3840670 |  | 3861682.4688
17 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD017082 | 1 | 27619.07 | 29149.7 | 1530.63 | 1000 | 1530630 |  | 1539004.1418
7: 0; 8: 0; 10: Total | 5371300 |  | 5400686.6106
| BSMMU HOSPITAL 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV Jamuna (F1) | 11 |  | BD017073 | 1 | 0.3625 | 0.3748 | 0.0123 | 2000 |  | 24.6 | 24.7258 | Kakrail |  |  |  | 11 kV Jamuna (F1) | 24.7258 | 22.8027 | 1.9232 | 8.4341 | OK
9 | 11 kV Pukur Par (F2) | 11 |  | BD017074 | 1 | 2906.26 | 2928.46 | 22.2 | 2000 |  | 44400 | 44627.1399 | Kakrail |  |  |  | 11 kV Pukur Par (F2) | 44627.1399 | 45645.6695 | -1018.5296 | -2.2314 | OK
10 | 11 kV BSMMU Convention center (F3) | 11 |  | BD017075 | 1 | 1714.95 | 1753.43 | 38.48 | 2000 |  | 76960 | 77353.7092 | Kakrail |  |  |  | 11 kV BSMMU Convention center (F3) | 77353.7092 | 38986.4869 | 38367.2222 | 98.4116 | FAULT
11 | 11 kV Unique Tower Sw/S-1 (F4) | 11 |  | BD017076 | 1 | 2929.26 | 3017.58 | 88.32 | 2000 |  | 176640 | 177543.6485 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-1 (F4) | 177543.6485 | 176710.4897 | 833.1588 | 0.47148 | OK
12 | 11 kV Holi Family Feeder (F5) | 11 |  | BD017077 | 1 | 14032.26 | 14405.79 | 373.53 | 2000 |  | 747060 | 750881.7825 | Kakrail |  |  |  | 11 kV Holi Family Feeder (F5) | 750881.7825 | 742559.3925 | 8322.3899 | 1.1208 | OK
13 | 11 kV Navy House Feeder (F6) | 11 |  | BD017078 | 1 | 26311.05 | 26649.82 | 338.77 | 2000 |  | 677540 | 681006.1346 | Kakrail |  |  |  | 11 kV Navy House Feeder (F6) | 681006.1346 | 662407.0498 | 18599.0848 | 2.8078 | OK
14 | 11 kV Paribagh Feeder (F7) | 11 |  | BD017079 | 1 | 31129.75 | 31963.13 | 833.38 | 2000 |  | 1666760 | 1675286.7504 | Paribag |  |  |  | 11 kV Paribagh Feeder (F7) | 1675286.7504 | 1691331.4714 | -16044.721 | -0.94864 | OK
15 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 |  | BD017080 | 1 | 6172.02 | 6399.81 | 227.79 | 2000 |  | 455580 | 457910.6397 | Paribag |  |  |  | 11 kV BSMMU C BLOCK Feeder (F8) | 457910.6397 | 432100.2302 | 25810.4094 | 5.9732 | OK
18 | 11 kV Oncology Bhaban (F9) | 11 |  | BD017083 | 1 | 2225.09 | 2293.72 | 68.63 | 2000 |  | 137260 | 137962.1897 | Paribag |  |  |  | 11 kV Oncology Bhaban (F9) | 137962.1897 | 128058.0984 | 9904.0913 | 7.7341 | OK
19 | Rupayan Trade Center | 11 |  | BD017084 | 1 | 1068.48 | 1218.74 | 150.26 | 2000 |  | 300520 | 302057.3893 | Kakrail |  |  |  | Rupayan Trade Center | 302057.3893 | 282490.5956 | 19566.7937 | 6.9265 | OK
20 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 |  | BD017085 | 1 | 2058.21 | 2119.1 | 60.89 | 2000 |  | 121780 | 122402.9977 | Kakrail |  |  |  | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 122402.9977 | 124143.3062 | -1740.3085 | -1.4019 | OK
21 | 11 kV BSMMU RMU (F12) | 11 |  | BD017086 | 1 | 1965.52 | 2052.22 | 86.7 | 2000 |  | 173400 | 174287.0734 | Paribag |  |  |  | 11 kV BSMMU RMU (F12) | 174287.0734 | 168699.2913 | 5587.7821 | 3.3123 | OK
22 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 |  | BD017087 | 1 | 4032.7 | 4149.43 | 116.73 | 2000 |  | 233460 | 234654.3262 | Paribag |  |  |  | 11 kV BSMMU Hospital D BLOCK (F13) | 234654.3262 | 236945.8228 | -2291.4966 | -0.9671 | OK
23 | 11 kV BCS Academy RMU (F14) | 11 |  | BD017088 | 1 | 995.07 | 1022.96 | 27.89 | 2000 |  | 55780 | 56065.3573 | Paribag |  |  |  | 11 kV BCS Academy RMU (F14) | 56065.3573 | 59004.3933 | -2939.036 | -4.981 | OK
24 | Spare | 11 |  | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | BSMMU Super Specialist Hospital RMU | 11 |  | BD017090 | 1 | 1147.96 | 1402.07 | 254.11 | 2000 |  | 508220 | 510819.9335 | Paribag |  |  |  | BSMMU Super Specialist Hospital RMU | 510819.9335 | 355842.5004 | 154977.4331 | 43.5523 | FAULT
26 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKD4418 | 1 | 2605.78 | 2759.07 | 153.29 | 100 |  | 15329 | 15407.4195 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 15407.4195 | 14685.5155 | 721.9041 | 4.9158 | OK
27 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 |  | 0 | 0 | Paribag |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 5418291.2173 | 5390713.6 | 5418291.2173 | 0.51158
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 2155897.5275
[5 empty] | Paribag | at 33 KV level |  | 3262393.6898
[5 empty] | Total = |  |  | 5418291.2173 | 0
1: 132 KV SIDE of___ LALBAGH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
132 KV SIDE (TARIFF POINT)
2 | Kallyanpur to Lalbagh 1 | 132 |  | 8993518 | 1 | 1098.154 | 1115.068 | 16.914 | 960000 | 0 | 16237440
|  | 132 |  |  | 1 | 70.056 | 70.056 | 0 | 960000 | 0 | 0
3 | Kallyanpur to Lalbagh 2 | 132 |  | 5014660 | 1 | 274.986 | 291.99 | 17.004 | 960000 | 0 | 16323840
|  | 132 |  |  | 1 | 4.361 | 4.361 | 0 | 960000 | 0 | 0
7 | Keraniganj to Lalbagh-3 | 132 |  | 38992597 | 1 | 575.795 | 609.476 | 33.681 | 1440000 | 0 | 48500640
|  | 132 |  |  | 1 | 0 | 0 | 0 | 1440000 | 0 | 0
9=8-7: Total Import/Export | 0 | 81061920
10: Net Total | 81061920
LALBAGH 132 KV SIDE (RECEIVING)
| Kallyanpur-1 | 132 | RECEIVE | 6604452 | 1 | 256887 | 272557 | 15670 | 1000 | 15670000
|  | 132 |  |  | 1 | 6755 | 6755 | 0 | 1000 |  | 0
| Hasnabad (Keranigonj) | 132 |  |  | 1 | 4330666 | 4379040 | 48374 | 1000 | 48374000
|  | 132 |  |  | 1 | 789 | 789 | 0 | 1000 |  | 0
| Kamrangirchar | 132 |  |  | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  |  | 1 | 479088 | 510202 | 31114 | 1000 |  | 31114000
| Kallyanpur-2 | 132 |  | 6604428 | 1 | 355386 | 370818 | 15432 | 1000 | 15432000
|  | 132 |  |  | 1 | 7111 | 7111 | 0 | 1000 |  | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 79476000 | 31114000
7: 0; 8: 0; 9=8-7: Net Total | 48362000
| LALBAGH 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
6 | Kamrangirchar | 132 |  | SIEM491 | 1 | 7525 | 7525 | 0 | 1000 | 0
|  | 132 |  | SIEM491 | 1 | 479088 | 510202 | 31114 | 1000 |  | 31114000
7: 0; 8: 0; 10: Total |  | 31114000
| LALBAGH 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | SIEM494 | 1 | 2172619 | 2196773 | 24154 | 1000 |  | 24154000
5 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | SIEM499 | 1 | 2284660 | 2308886 | 24226 | 1000 |  | 24226000
10: Total |  | 48380000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (TARIFF POINT); 4: 81061920; 6: EXPORT TO OTHER S/S; 9=8-7: 31114000 | 132 KV NET IMPORT |  | 49947920
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 49947920 | 132/33 KV GT LV SIDE |  | 48370000
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 1577920
2: IMPORT-4 | LOSS % IN => |  | 3.159%
| 132 KV TOTAL IMPORT |  | 81061920
1: 33 KV SIDE of___LALBAGH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 33 KV SIDE
11 | 132/33 kV GT-1 Incoming (LV) | 33 |  | SIEM0517 | 1 | 2172088 | 2196215 | 24127 | 1000 | 24127000
16 | 132/33 kV GT-2 Incoming (LV) | 33 |  | SIEM0518 | 1 | 2258654 | 2282897 | 24243 | 1000 | 24243000
7: 0; 8: 0; 10: Total | 48370000 |  | 0
| LALBAGH 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SIEM0502 | 1 | 831689 | 837341 | 5652 | 2000 |  | 11304000 | 11377882.4218 |  | 23071817.1331 | Lalbagh New 33/11 kv ss | 0.91748 | 33/11 kV, 20/28 MVA T-1 (HV) | 11377882.4218 | 12007552.0327 | -629669.6108 | -5.2439 | OK
14 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SIEM0501 | 1 | 824864 | 830673 | 5809 | 2000 |  | 11618000 | 11693934.7113 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 11693934.7113 | 12507278.9842 | -813344.2729 | -6.503 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 22922000 | 23071817.1331 |  |  |  |  | 33 KV Feeders | 23071817.1331 | 24514831.0168 | -1443013.8837 | -5.8863 | OK
9 | Spare | 33 |  | SIEM0500 | 1 | 0 | 0 |  | 2000 |  | 0 | 0 |  | 8692444.4971 | Mitford 33/11 kv ss | -1.8287 | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Mitford Circuit-1 | 33 |  | SIEM0513 | 1 | 316938 | 319597 | 2659 | 2000 |  | 5318000 | 5352758.2023 |  |  |  |  | Mitford Circuit-1 | 5352758.2023 | 5224967.6826 | 127790.5197 | 2.4458 | OK
12 | Azimpur Circuit-1 | 33 |  | SIEM0503 | 1 | 70528 | 70586 | 58 | 2000 |  | 116000 | 116758.1706 |  | 6800156.9039 | Azimpur 33/11 kv ss | 1.3852 | Azimpur Circuit-1 | 116758.1706 | 0 | 116758.1706 | #DIV/0! | #DIV/0!
15 | Azimpur Circuit-2 | 33 |  | SIEM0507 | 1 | 81718 | 85038 | 3320 | 2000 |  | 6640000 | 6683398.7333 |  |  |  |  | Azimpur Circuit-2 | 6683398.7333 | 7248055.825 | -564657.0918 | -7.7905 | OK
17 | Lalbagh old | 33 |  | SIEM0509 | 1 | 217599 | 222464 | 4865 | 2000 |  | 9730000 | 9793594.8305 |  | 9793594.8305 | Lalbagh old 33/11 kv ss | 0.18209 | Lalbagh old | 9793594.8305 | 10681663.5887 | -888068.7582 | -8.314 | OK
18 | Mitford Circuit-2 | 33 |  | SIEM0511 | 1 | 357147 | 358806 | 1659 | 2000 |  | 3318000 | 3339686.2947 |  |  |  |  | Mitford Circuit-2 | 3339686.2947 | 4249694.1159 | -910007.8212 | -21.4135 | OK
19 | 33/0.4 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKC7982 | 1 | 7177.43 | 7276.67 | 99.24 | 120 |  | 11908.8 | 11986.6354 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-1 | 11986.6354 | 12787.7709 | -801.1355 | -6.2649 | OK
20 | 33/0.4 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHU02670 | 1 | 27089.5 | 27089.5 | 0 | 120 |  | 0 | 0 |  |  |  |  | 33/0.4 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 25133908.8 | 25298182.8669 |  |  |  |  | 0 | 25298182.8669 | 27417168.9832 | -2118986.1163 | -7.7287 | OK
9=8-7: Grand Total | 48370000 | 48055908.8 | 48370000 | 0.6536
1: 11 KV SIDE of___ LALBAGH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH 11 KV SIDE
10 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK98833 | 1 | 583394.6 | 589023.51 | 5628.91 | 2000 | 11257820 |  | 11386959.3356
11 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK98832 | 1 | 579620 | 585396.17 | 5776.17 | 2000 | 11552340 |  | 11684857.7976
7: 0; 8: 0; 10: Total | 22810160 |  | 23071817.1331
| LALBAGH 11 kV SIDE |  |  |  |  | 0 | 0
3 | Chata Mosjid | 11 |  |  | 1 | 169591.28 | 171770.4353 | 2179.1553 | 1000 |  | 2179155.29 | 2199148.6226 | Kamrangirchar |  |  |  | Chata Mosjid | 2199148.6226 | 2319503.7751 | -120355.1525 | -5.1888 | OK
4 | AC mosjid | 11 |  |  | 1 | 5346.4008 | 6488.7556 | 1142.3548 | 1000 |  | 1142354.8 | 1152835.6866 | Lalbag |  |  |  | AC mosjid | 1152835.6866 | 1275218.63 | -122382.9434 | -9.597 | OK
5 | Kazi Reaz Uddin Road | 11 |  |  | 1 | 18853.63 | 20836.008 | 1982.378 | 1000 |  | 1982378 | 2000565.9387 | Lalbag |  |  |  | Kazi Reaz Uddin Road | 2000565.9387 | 2224217.61 | -223651.6713 | -10.0553 | OK
6 | Nazimuddin | 11 |  |  | 1 | 4214.292 | 4687.9236 | 473.6316 | 1000 |  | 473631.6 | 477977.0793 | Lalbag |  |  |  | Nazimuddin | 477977.0793 | 0 | 477977.0793 | #DIV/0! | #DIV/0!
7 | Kamal Bagh | 11 |  |  | 1 | 13296.26 | 14900.122 | 1603.862 | 1000 |  | 1603862 | 1618577.1268 | Lalbag |  |  |  | Kamal Bagh | 1618577.1268 | 1589844.4629 | 28732.664 | 1.8073 | OK
8 | Rahamatganj | 11 |  |  | 1 | 8699.95 | 10837.383 | 2137.433 | 1000 |  | 2137433 | 2157043.5386 | Lalbag |  |  |  | Rahamatganj | 2157043.5386 | 2473091.3867 | -316047.8481 | -12.7795 | OK
9 | Water Works 11kV Sw/S-1 | 11 |  |  | 1 | 20641.601 | 22372.9274 | 1731.3264 | 1000 |  | 1731326.4 | 1747210.9883 | Lalbag |  |  |  | Water Works 11kV Sw/S-1 | 1747210.9883 | 1862323.276 | -115112.2877 | -6.1811 | OK
12 | City Colony | 11 |  |  | 1 | 22484.11 | 24326.885 | 1842.775 | 1000 |  | 1842775 | 1859682.1079 | Lalbag |  |  |  | City Colony | 1859682.1079 | 2050289.3435 | -190607.2357 | -9.2966 | OK
13 | Water Works 11kV Sw/S-2 | 11 |  |  | 1 | 32750 | 35515.332 | 2765.332 | 1000 |  | 2765332 | 2790703.3917 | Lalbag |  |  |  | Water Works 11kV Sw/S-2 | 2790703.3917 | 2997202.1128 | -206498.7211 | -6.8897 | OK
14 | Chun Goli | 11 |  |  | 1 | 6376.308 | 7124.165 | 747.857 | 1000 |  | 747857 | 754718.4448 | Lalbag |  |  |  | Chun Goli | 754718.4448 | 841380.8401 | -86662.3953 | -10.3 | OK
15 | Alir Ghat | 11 |  |  | 1 | 119606.4 | 121324.8 | 1718.4 | 1000 |  | 1718400 | 1734165.991 | Lalbag |  |  |  | Alir Ghat | 1734165.991 | 1904122.5273 | -169956.5362 | -8.9257 | OK
16 | Club Ghat | 11 |  |  | 1 | 13974.46 | 16270.969 | 2296.509 | 1000 |  | 2296509 | 2317579.0304 | Lalbag |  |  |  | Club Ghat | 2317579.0304 | 2539875.5429 | -222296.5124 | -8.7523 | OK
17 | Debidas Ghat | 11 |  |  | 1 | 26831.902 | 29072.95 | 2241.048 | 1000 |  | 2241048 | 2261609.1864 | Lalbag |  |  |  | Debidas Ghat | 2261609.1864 | 2437761.5097 | -176152.3233 | -7.226 | OK
18 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 23071817.1331 | 22862062.09 | 23071817.1331 | 0.91748
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 2199148.6226
[5 empty] | Lalbag | at 33 KV level |  | 20872668.5105
[5 empty] | Total = |  |  | 23071817.1331 | 0
1: 33 KV SIDE of___ LALBAGH OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAG Grid 33 KV SIDE
17 | Lalbagh old | 33 | 0 | SIEM0509 | 1 | 217599 | 222464 | 4865 | 2000 | 0 | 9730000 | 9793594.8305
10: Total |  | 9730000 | 9793594.8305 | 0.6536
KAMRANGIRCHAR 33 KV SIDE
15 | Lalbagh Circuit-1 | 33 | 0 | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 | 0 | 0 | 0
10: Total |  | 0 | 0
LALBAGH OLD 33 KV SIDE (RECEIVING)
| 33 KV Lalbagh Incomming | 33 | RECEIVE |  | 1 | 202944 | 202944 | 0 | 2000 |  | 0
2: 33 KV KAMRANGIRCHAR-1; 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
2: 34 KV KAMRANGIRCHAR-2; 3: 33; 6: 1; 9=8-7: 0; 10: 240000 |  | 0
10: Total |  | 0 | 9793594.8305
LALBAGH OLD 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
LALBAGH OLD 33 KV SIDE
1: 6; 2: 33/11 kV, 10/14 MVA T4 (HV); 3: 33; 6: 1; 9=8-7: 0 |  | 0
1: 7; 2: 33/11 kV, 10/14 MVA T3 (HV); 3: 33; 6: 1; 9=8-7: 0 |  | 0
1: 8; 2: 33/11 kV, 10/14 MVA T1 (HV); 3: 33; 6: 1; 9=8-7: 0 |  | 0
1: 14; 2: 33/11 kV, 10/14 MVA T2 (HV); 3: 33; 6: 1; 9=8-7: 0 |  | 0
10: Total |  | 0 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: LALBAG Grid 33 KV SIDE; 4: 9793594.8305; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALBAGH OLD 33 KV NET IMPORT |  | 9793594.8305
2: KAMRANGIRCHAR 33 KV SIDE; 4: 0; 6: LALBAGH OLD 33 KV NET IMPORT; 9=8-7: 9793594.8305 | 33 KV TX HV SIDE |  | 9793594.8305
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 9793594.8305
1: 11 KV SIDE of___LALBAGH OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
LALBAGH OLD 11 KV SIDE
18 | 33/11 kV T4 Incoming (LV) | 11 |  | 8838010 | 1 | 77733.6 | 80354.8 | 2621.2 | 1000 | 2621200 |  | 3902312.2294
27 | 33/11 kV T1 Incoming (LV) | 11 |  | 06604426 | 1 | 35625.3 | 35775.5 | 150.2 | 16000 | 2403200 |  | 3577764.6687
28 | 33/11 kV T2 Incoming (LV) | 11 |  |  | 1 | 602442 | 603996 | 1554 | 1000 | 1554000 |  | 2313517.9324
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total | 6578400 |  | 9793594.8305
| LALBAGH OLD 11 KV SIDE |  |  |  |  | 0 | 0
15 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 160 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Sowari Ghat | 11 |  | 8838019 | 1 | 74886.8 | 77211.8 | 2325 | 1000 |  | 2325000 | 2329233.6447 | Lalbag |  | 50 |  | Sowari Ghat | 2329233.6447 | 2612060.995 | -282827.3503 | -10.8277 | OK
17 | Novo Kumar (Kara Odidoptor) | 11 |  | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 121632.84 | 121854.324 | Lalbag | 10 | 110 |  | Novo Kumar (Kara Odidoptor) | 121854.324 | 118483.0867 | 3371.2372 | 2.8453 | OK
19 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 36.6667 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  | 86.6667 |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Eidgah | 11 |  | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1094695.56 | 1096688.9157 | Lalbag | 90 |  |  | Eidgah | 1096688.9157 | 1303313.9541 | -206625.0384 | -15.8538 | OK
23 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | Modumoti | 11 |  |  | 1 | 87070.4 | 91067.8 | 3997.4 | 444.44 | Estimated | 1581226.92 | 1584106.2116 | Lalbag | 130 |  |  | Modumoti | 1584106.2116 | 1954970.9311 | -370864.7195 | -18.9703 | OK
25 | Lalbagh O/H | 11 |  | 61389152 | 1 | 440314 | 440978 | 664 | 1000 | Estimated | 1179838.548 | 1181986.9425 | Lalbag | 97 |  |  | Lalbagh O/H | 1181986.9425 | 1066347.7806 | 115639.1619 | 10.8444 | OK
26 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Water Works 11 kV Sw/S-2 | 11 |  | 61389109 | 1 | 400866 | 401739 | 873 | 1000 |  | 873000 | 874589.6653 | Lalbag |  |  |  | Water Works 11 kV Sw/S-2 | 874589.6653 | 951212.9635 | -76623.2982 | -8.0553 | OK
31 | Islambagh | 11 |  | 61389186 | 1 | 499228 | 500001 | 773 | 1000 |  | 773000 | 774407.5731 | Lalbag |  |  |  | Islambagh | 774407.5731 | 861627.8273 | -87220.2542 | -10.1227 | OK
32 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | WASA Low Lift Pump | 11 |  | 61389202 | 1 | 15477 | 15534 | 57 | 1000 |  | 57000 | 57103.7926 | Lalbag |  |  |  | WASA Low Lift Pump | 57103.7926 | 61401.0484 | -4297.2559 | -6.9987 | OK
34 | Shahi Mosjid | 11 |  | 06604459 | 1 | 35606.2 | 35827.5 | 221.3 | 8000 |  | 1770400 | 1773623.7611 | Azimpur |  |  |  | Shahi Mosjid | 1773623.7611 | 1752245.002 | 21378.7591 | 1.2201 | OK
35 | Spare | 11 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 | Lalbag |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 33/0.4 kV Auxiliary Transformer | 0.415 |  | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 |  | 0 | 0 | Lalbag |  |  |  | 33/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 9793594.8305 | 9775793.868 | 9793594.8305 | 0.18209
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Lalbag | at 33 KV level |  | 8019971.0694
[5 empty] | Azimpur | at 33 KV level |  | 1773623.7611
[5 empty] | Total = |  |  | 9793594.8305 | 0
1: 33 KV SIDE of___ MIDFORT 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 KV SIDE
10 | Mitford Circuit-1 | 33 | 0 | SIEM0513 | 1 | 316938 | 319597 | 2659 | 2000 | 0 | 5318000 | 5352758.2023
18 | Mitford Circuit-2 | 33 | 0 | SIEM0511 | 1 | 357147 | 358806 | 1659 | 2000 | 0 | 3318000 | 3339686.2947
10: Total | 0 | 8636000 | 8692444.4971
MIDFORT 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 1220.69 | 1231 | 10.31 | 540000 |  | 5567400
| Lalbagh Circuit-2 | 33 |  | DHK68131 | 1 | 1286.43 | 1292.58 | 6.15 | 540000 |  | 3321000
7: 0; 8: 0; 10: Total |  | 8888400
| MIDFORT 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
1 | Kumartuly Circuit-1 | 33 |  | DHK-66493 | 1 | 1285151 | 1286272 | 1121 | 180 |  | 201780
6 | Kumartuly Circuit-2 | 33 |  | DHK-60914 | 1 | 759469.7 | 761041 | 1571.3 | 180 |  | 282834
7: 0; 8: 0; 10: Total |  | 484614
[6 empty] | 0 | 0
| MIDFORT 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-66494 | 1 | 2793057 | 2844826 | 51769 | 180 | From Downstream | 5597280
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHKA-2193 | 1 | 558.559 | 578.7117 | 20.1527 | 180000 |  | 3627486
10: Total |  | 9224766
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: LALBAGH 33 KV SIDE; 4: 8692444.4971; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9224766
2: IMPORT-2; 4: 484614; 6: 33 KV NET IMPORT; 9=8-7: 9224766 | 33 KV TX HV SIDE |  | 9224766
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 9177058.4971
1: 11 KV SIDE of___MIDFORT 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
MIDFORT 11 KV SIDE
14 | 33/11 kV T1 Incoming (LV) | 11 |  | DHK-66484 | 1 | 2717650 | 2748746 | 31096 | 180 | 5597280 |  | 5606546.078
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK-66476 | 1 | 2041819 | 2061887 | 20068 | 180 | 3612240 |  | 3618219.922
7: 0; 8: 0; 10: Total | 9209520 |  | 9224766
| MIDFORT 11 KV SIDE |  |  |  |  | 0 | 0
7 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | DHK-66478 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Chawk Bazar | 11 |  | DHK-60904 | 1 | 963274.2 | 971432 | 8157.8 | 60 |  | 489468 | 480516.9276 | Lalbag |  |  |  | Chawk Bazar | 480516.9276 | 522405.3875 | -41888.4599 | -8.0184 | OK
10 | Spare | 11 |  | DHK-66482 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Chatrabas | 11 |  | DHK-66485 | 1 | 795411 | 816427 | 21016 | 60 |  | 1260960 | 1237900.3837 | Bangshal |  |  |  | Chatrabas | 1237900.3837 | 762976.1234 | 474924.2603 | 62.2463 | FAULT
12 | Begum Bazar | 11 |  | DHK-66481 | 1 | 3626756 | 3667458 | 40702 | 60 |  | 2442120 | 2397460.098 | Bangshal |  |  |  | Begum Bazar | 2397460.098 | 2421237.7604 | -23777.6624 | -0.98205 | OK
13 | SCC ROAD | 11 |  | DHK-60901 | 1 | 48991.1 | 74915 | 25923.9 | 60 |  | 1555434 | 1526989.2348 | Bangshal |  |  |  | SCC ROAD | 1526989.2348 | 1650255.6547 | -123266.42 | -7.4695 | OK
16 | Spare | 11 |  | DHK-66483 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Armanitola | 11 |  | DHK-61104 | 1 | 668332.7 | 684884 | 16551.3 | 60 |  | 993078 | 974917.2355 | Bangshal |  |  |  | Armanitola | 974917.2355 | 956708.8537 | 18208.3819 | 1.9032 | OK
18 | Mitford Hospital (RMU) | 11 |  | DHK-61101 | 1 | 383048.6 | 392201 | 9152.4 | 60 |  | 549144 | 539101.6117 | Bangshal |  |  |  | Mitford Hospital (RMU) | 539101.6117 | 513839.5885 | 25262.0232 | 4.9163 | OK
19 | Emamganj | 11 |  | DHK-68130 | 1 | 1447.92 | 1450.67 | 2.75 | 60000 |  | 165000 | 161982.5873 | Bangshal |  |  |  | Emamganj | 161982.5873 | 733781.3763 | -571798.789 | -77.925 | CHECK
20 | Kamal Dho Road | 11 |  | DHK-68129 | 1 | 1216.26 | 1225.4 | 9.14 | 60000 |  | 548400 | 538371.2175 | Lalbag |  |  |  | Kamal Dho Road | 538371.2175 | 628439.5052 | -90068.2877 | -14.3321 | OK
21 | Spare | 11 |  | DHK-68128 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Panghat | 11 |  | DHK-68127 | 1 | 1505.39 | 1528.54 | 23.15 | 60000 |  | 1389000 | 1363598.8715 | Bangshal |  |  |  | Panghat | 1363598.8715 | 1411581.0725 | -47982.201 | -3.3992 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | U0004460 | 1 | 5554.67 | 5594.68 | 40.01 | 100 |  | 4001 | 3927.8323 | Bangshal |  |  |  | 11/0.4 kV Auxiliary Transformer | 3927.8323 | 4152.4762 | -224.6439 | -5.4099 | OK
10: Grand Total | 9224766 | 9396605 | 9224766 | -1.8287
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 8205877.8549
[5 empty] | Lalbag | at 33 KV level |  | 1018888.1451
[5 empty] | Total = |  |  | 9224766 | 0
1: 33 KV SIDE of___ AZIMPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
LALBAGH 33 kV SIDE
12 | Azimpur Circuit-1 | 33 | 0 | SIEM0503 | 1 | 70528 | 70586 | 58 | 2000 | 0 | 116000 | 116758.1706
15 | Azimpur Circuit-2 | 33 | 0 | SIEM0507 | 1 | 81718 | 85038 | 3320 | 2000 | 0 | 6640000 | 6683398.7333
10: Total | 0 | 6756000 | 6800156.9039
DHANMONDI 33 kV SIDE
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1942.41 | 1978.52 | 36.11 | 240000 | 0 | 8666400 | 8671355.8696
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1809.7 | 5.33 | 240000 | 0 | 1279200 | 1279931.5089
10: Total | 0 | 9945600 | 9951287.3785
10: GRAND TOTAL |  | 16701600 | 16751444.2824
AZIMPUR 33 KV SIDE (RECEIVING)
| Lalbagh Circuit-1 | 33 | RECEIVE | DHK60891 | 1 | 782901 | 783543 | 642 | 180 |  | 115560
| Dhanmondi Circuit-1 | 33 |  | DHK68131 | 1 | 1169765 | 1185844 | 16079 | 540 |  | 8682660
| Dhanmondi Circuit-2 | 33 |  |  | 1 | 133153 | 135546 | 2393 | 540 |  | 1292220
| Lalbagh Circuit-2 | 33 |  | DHK68132 | 1 | 906735 | 943609 | 36874 | 180 |  | 6637320
7: 0; 8: 0; 10: Total |  | 16727760 | #REF!
| AZIMPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| Feeder No.1 | 33 | EXPORT |  | 1 | 0 | 0 |  |  |  | 0
2: Feeder No.2; 3: 33; 6: 1; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| AZIMPUR 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK61094 | 1 | 238697 | 287638 | 48941 | 180 |  | 8809380
4 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK60919 | 1 | 365851 | 409946 | 44095 | 180 |  | 7937100
10: Total |  | 16746480 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: LALBAGH 33 kV SIDE; 4: 6800156.9039; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | AZIMPUR 33 KV NET IMPORT |  | 16751444.2824
2: DHANMONDI 33 kV SIDE; 4: 9951287.3785; 6: AZIMPUR 33 KV NET IMPORT; 9=8-7: 16751444.2824 | 33 KV TX HV SIDE |  | 16746480
[10 empty] | LOSS UNITS=> |  | 4964.2824
[10 empty] | LOSS % IN => |  | 0.02963%
| TOTAL IMPORT |  | 16751444.2824
1: 11 KV SIDE of___AZIMPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
AZIMPUR 11 KV SIDE
14 | 33/11 kV T1Incoming (LV) | 11 |  | DHK60909 | 1 | 241529 | 290518 | 48989 | 180 | 8818020 |  | 8801901.7091
15 | 33/11 kV T2 Incoming (LV) | 11 |  | DHK60902 | 1 | 381108 | 425353 | 44245 | 180 | 7964100 |  | 7949542.5733
7: 0; 8: 0; 10: Total | 16782120 |  | 16751444.2824
| AZIMPUR 11 KV SIDE |  |  |  |  | 0 | 0
7 | Chadni chwok | 11 |  | DHK60916 | 1 | 399421 | 409665 | 10244 | 60 |  | 614640 | 623153.8648 | Paribag |  |  |  | Chadni chwok | 623153.8648 | 792142.0147 | -168988.1499 | -21.3331 | OK
8 | BGB | 11 |  | DHK61090 | 1 | 665574 | 676712 | 11138 | 60 |  | 668280 | 677536.8748 | Jigatola |  |  |  | BGB | 677536.8748 | 266970.3715 | 410566.5034 | 153.7873 | FAULT
9 | Pari Bibi Mazar | 11 |  | DHK61091 | 1 | 745025 | 780093 | 35068 | 60 |  | 2104080 | 2133225.2763 | Azimpur |  |  |  | Pari Bibi Mazar | 2133225.2763 | 2225341.7622 | -92116.4859 | -4.1394 | OK
10 | Azimpur | 11 |  | DHK61086 | 1 | 282859 | 301821 | 18962 | 60 |  | 1137720 | 1153479.4596 | Azimpur |  |  |  | Azimpur | 1153479.4596 | 1136633.6642 | 16845.7954 | 1.4821 | OK
11 | Aazd | 11 |  | DHK61089 | 1 | 960626 | 982542 | 21916 | 60 |  | 1314960 | 1333174.551 | Azimpur |  |  |  | Aazd | 1333174.551 | 1318714.278 | 14460.273 | 1.0965 | OK
12 | Dayra Sharif | 11 |  | DHK61088 | 1 | 498851 | 515887 | 17036 | 60 |  | 1022160 | 1036318.7466 | Azimpur |  |  |  | Dayra Sharif | 1036318.7466 | 1007533.0284 | 28785.7183 | 2.857 | OK
13 | Naya palton | 11 |  | DHK86065 | 1 | 1871.03 | 1899.17 | 28.14 | 60000 |  | 1688400 | 1711787.3638 | Azimpur |  |  |  | Naya palton | 1711787.3638 | 1744076.5145 | -32289.1507 | -1.8514 | OK
16 | Viqarunnisa Noon School | 11 |  | DHK66477 | 1 | 1584644 | 1609302 | 24658 | 60 |  | 1479480 | 1499973.4477 | Azimpur |  |  |  | Viqarunnisa Noon School | 1499973.4477 | 1460116.0121 | 39857.4355 | 2.7297 | OK
17 | Subal Das Lane | 11 |  | DHK66480 | 1 | 3981086 | 4005845 | 24759 | 60 |  | 1485540 | 1506117.3895 | Azimpur |  |  |  | Subal Das Lane | 1506117.3895 | 1034936.4652 | 471180.9243 | 45.5275 | FAULT
18 | Lalbagh | 11 |  | DHK61093 | 1 | 685659 | 726292 | 40633 | 60 |  | 2437980 | 2471750.3893 | Azimpur |  |  |  | Lalbagh | 2471750.3893 | 2403281.4122 | 68468.9771 | 2.849 | OK
19 | Zahrul Haque Hall | 11 |  | DHK66497 | 1 | 1228090 | 1239080 | 10990 | 60 |  | 659400 | 668533.8709 | Ramna |  |  |  | Zahrul Haque Hall | 668533.8709 | 616760.0188 | 51773.8521 | 8.3945 | OK
20 | Eden College | 11 |  | DHK60917 | 1 | 925859 | 933261 | 7402 | 60 |  | 444120 | 450271.8574 | Azimpur |  |  |  | Eden College | 450271.8574 | 455566.9136 | -5295.0562 | -1.1623 | OK
21 | Nilkhet/ PWD-01 | 11 |  | DHK60918 | 1 | 466773 | 478017 | 11244 | 60 |  | 674640 | 683984.9722 | Azimpur |  |  |  | Nilkhet/ PWD-01 | 683984.9722 | 653358.8311 | 30626.1411 | 4.6875 | OK
22 | BUET | 11 |  | DHK66496 | 1 | 949620 | 962739 | 13119 | 60 |  | 787140 | 798043.2987 | Ramna |  |  |  | BUET | 798043.2987 | 718091.8386 | 79951.4601 | 11.1339 | OK
23 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIG2780 | 1 | 385337 | 389374 | 4037 | 1 |  | 4037 | 4092.9197 | Azimpur |  |  |  | 11/0.4 kV Auxiliary Transformer | 4092.9197 | 4399.774 | -306.8543 | -6.9743 | OK
10: Grand Total | 16751444.2824 | 16522577 | 16751444.2824 | 1.3852
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 623153.8648
[5 empty] | Jigatola | at 33 KV level |  | 677536.8748
[5 empty] | Azimpur | at 33 KV level |  | 13984176.3731
[5 empty] | Ramna | at 33 KV level |  | 1466577.1697
[5 empty] | Total = |  |  | 16751444.2824 | 0
1: 132 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S |  |  |  |  | #REF! |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Keranigonj 132 KV SIDE (TARIFF POINT)
3 | Keraniganj to Kamrangirchar | 132 |  | 38992596 | 1 | 851.661 | 891.973 | 40.312 | 1440000 | 0 | 58049280
|  | 132 |  |  | 1 | 0.021 | 0.021 | 0 | 1440000 | 0 | 0
9=8-7: Total Import/Export | 0 | 58049280
10: Net Total | 58049280
KAMRANGIRCHAR 132 KV SIDE (RECEIVING)
| 132 kV Keranigonj | 132 | RECEIVE |  | 1 | 5638.47 | 5699.08 | 60.61 | 960000 | 58185600
|  | 132 | RECEIVE |  | 1 | 91.71 | 91.71 | 0 | 960000 |  | 0
| 132 kV Lalbagh | 132 |  |  | 1 | 3007.85 | 3040.28 | 32.43 | 960000 | 31132800
|  | 132 |  |  | 1 | 7.78 | 7.78 | 0 | 960000 |  | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 89318400 | 0
7: 0; 8: 0; 9=8-7: Net Total | 89318400
| KAMRANGIRCHAR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
5 | 132 kV Jigatola-1 | 132 |  | 42003953362 | 1 | 190.71 | 211.08 | 20.37 | 1440000 |  | 29332800
6 | 132 kV Jigatola-2 | 132 |  | 42003953364 | 1 | 186.66 | 206.51 | 19.85 | 1440000 |  | 28584000
7: 0; 8: 0; 10: Total |  | 57916800
| KAMRANGIRCHAR 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33 kV, 50/75 MVA GT-2 (HV) | 132 |  | 30799138 | 1 | 3372.07 | 3382.6 | 10.53 | 960000 |  | 10108800
2 | 132/33 kV, 50/75 MVA GT-1 (HV) | 132 |  | 30799148 | 1 | 3349.64 | 3360.22 | 10.58 | 960000 |  | 10156800
7 | 132/33 kV, 50/75 MVA GT-3 (HV) | 132 |  | BD001910 | 1 | 1149.12 | 1160.29 | 11.17 | 960000 |  | 10723200
10: Total |  | 30988800 | 88905600
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Keranigonj 132 KV SIDE (TARIFF POINT); 4: 58049280; 6: EXPORT TO OTHER S/S; 9=8-7: 57916800 | 132 KV NET IMPORT |  | 31265280
2: FROM LALBAGH 132/33 KV GRID; 4: 31132800; 6: 132 KV NET IMPORT; 9=8-7: 31265280 | 33 KV NET IMPORT |  | 30940800
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 324480
[10 empty] | LOSS % IN => |  | 1.038%
| 132 KV TOTAL IMPORT |  | 89182080
1: 33 KV SIDE of___ KAMRANGIRCHAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
12 | 132/33 kV GT-3 Incoming | 33 |  | BD001914 | 1 | 2312.97 | 2335.32 | 22.35 | 480000 | 10728000 |  | 10840505.8641
14 | 132/33 kV GT-1 Incoming (LV) | 33 |  | 30799094 | 1 | 6843.58 | 6864.81 | 21.23 | 480000 | 10190400 |  | 10297267.9863
19 | 132/33 kV GT-2 Incoming | 33 |  | 30799150 | 1 | 6744.71 | 6765.59 | 20.88 | 480000 | 10022400 |  | 10127506.1496
7: 0; 8: 0; 10: Total | 30940800 |  | 31265280
| KAMRANGIRCHAR 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 20/28 MVA T31 (HV) | 33 |  | 30799129 | 1 | 6805.63 | 6839.64 | 34.01 | 240000 |  | 8162400 | 8166327.3371 |  | 24734295.1776 | Kamrangir Char 33/11 kv ss | 0.82578 | 33/11 kV, 20/28 MVA T31 (HV) | 8166327.3371 | 8516522.3851 | -350195.048 | -4.1119 | OK
20 | 33/11 kV, 20/28 MVA T32 (HV) | 33 |  | 30799110 | 1 | 6702.87 | 6736.43 | 33.56 | 240000 |  | 8054400 | 8058275.3729 |  |  |  |  | 33/11 kV, 20/28 MVA T32 (HV) | 8058275.3729 | 8417436.8522 | -359161.4793 | -4.2669 | OK
21 | 33/11 kV, 20/28 MVA T-33 (HV) | 33 |  | 30799137 | 1 | 3843.56 | 3879 | 35.44 | 240000 |  | 8505600 | 8509692.4677 |  |  |  |  | 33/11 kV, 20/28 MVA T-33 (HV) | 8509692.4677 | 8997449.7275 | -487757.2598 | -5.4211 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 24722400 | 24734295.1776 |  |  |  |  | 33 KV Feeders | 24734295.1776 | 25931408.9648 | -1197113.7872 | -4.6165 | OK
8 | Dhaka Uddyan 2 | 33 |  | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 |  | 0 | 0 |  | 0 | Dhaka Uddan 33/11 kv ss | -0.2151 | Dhaka Uddyan 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Dhaka Uddyan 1 | 33 |  | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Dhaka Uddyan 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare Feeder -2 | 33 |  | 30799130 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 kV Transformer T-4 (Spare) | 33 |  | 30799125 | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33/11 kV Transformer T-4 (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Lalbagh Circuit-1 | 33 |  | 30799098 | 1 | 1759.2 | 1759.2 | 0 | 240000 |  | 0 | 0 |  | 6050909.9939 | Kamrangir Char-2 33/11 kv ss | 0.095247 | Lalbagh Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Zigatola Circuit-1 (BGB-1) | 33 |  | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Zigatola Circuit-1 (BGB-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare Feeder-1 | 33 |  |  | 1 | 0 | 0 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Spare Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Kamrangir Char-2 | 33 |  | 30799147 | 1 | 1491.72 | 1516.92 | 25.2 | 240000 |  | 6048000 | 6050909.9939 |  | 155594.8284 | BGB 33/11 kv ss | 0.48002 | Kamrangir Char-2 | 6050909.9939 | 6464726.8389 | -413816.8449 | -6.4011 | OK
22 | Zigatola Circuit-2 (BGB-2) | 33 |  | 30799131 | 1.35 | 1865.05 | 1865.53 | 0.48 | 240000 |  | 155520 | 155594.8284 |  |  |  |  | Zigatola Circuit-2 (BGB-2) | 155594.8284 | 3455064.1963 | -3299469.3679 | -95.4966 | CHECK
10: Total |  | 6203520 | 6206504.8224 |  |  |  |  | 0 | 6206504.8224 | 9919791.0352 | -3713286.2128 | -37.4331 | OK
9=8-7: Grand Total | 30940800 | 30925920 | 30940800 | 0.048115
1: 11 KV SIDE of___KAMRANGIRCHAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 11 KV SIDE
6 | 33/11 kV T-31 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 8031600 |  | 8145036.1318
11 | 33/11 kV T-32 Incoming | 11 |  | 6604433 | 1 | 7527.85 | 7572.47 | 44.62 | 180000 | 8031600 |  | 8145036.1318
22 | 33/11 kV T-33 Incoming | 11 |  | DHK 95817 | 1 | 4504936 | 4551195 | 46259 | 180 | 8326620 |  | 8444222.914
7: 0; 8: 0; 10: Total | 24389820 |  | 24734295.1776
| KAMRANGIRCHAR 11 kV SIDE |  |  |  |  | 0 | 0
4 | Rasulpur | 11 |  | HA-021101042-02 | 1 | 90531613 | 91923561 | 1391948 | 1 |  | 1391948 | 1403442.4135 | Kamrangirchar |  |  |  | Rasulpur | 1403442.4135 | 1475786.882 | -72344.4685 | -4.9021 | OK
5 | Bheribadh | 11 |  | HA-021101105-02 | 1 | 62150594 | 64458541 | 2307947 | 1 |  | 2307947 | 2327005.5404 | Kamrangirchar |  |  |  | Bheribadh | 2327005.5404 | 2450676.7878 | -123671.2474 | -5.0464 | OK
7 | Panna Tower 11 KV Faridpur Tower Express | 11 |  | 30799521 | 1 | 2629.31 | 2634.51 | 5.2 | 60000 |  | 312000 | 314576.4303 | Kamrangirchar |  |  |  | Panna Tower 11 KV Faridpur Tower Express | 314576.4303 | 364934.8739 | -50358.4435 | -13.7993 | OK
8 | Panna Battery Express | 11 |  | DHK15431 | 1 | 5261.14 | 5278.8 | 17.66 | 60000 |  | 1059600 | 1068349.9537 | Kamrangirchar |  |  |  | Panna Battery Express | 1068349.9537 | 1060687.1709 | 7662.7828 | 0.72244 | OK
9 | Eidgah | 11 |  | 30799460 | 1 | 5334.36 | 5369.43 | 35.07 | 60000 |  | 2104200 | 2121576.0406 | Kamrangirchar |  |  |  | Eidgah | 2121576.0406 | 2271856.6688 | -150280.6282 | -6.6149 | OK
10 | Bot Tola Mazar | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Jigatola |  |  |  | Bot Tola Mazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Huzur Para | 11 |  | HA-021101055-02 | 1 | 99457723 | 101275461 | 1817738 | 1 |  | 1817738 | 1832748.4977 | Kamrangirchar |  |  |  | Huzur Para | 1832748.4977 | 1797702.2907 | 35046.207 | 1.9495 | OK
13 | Kamrangirchar | 11 |  | HA-021101015-02 | 1 | 19288783 | 21147055 | 1858272 | 1 |  | 1858272 | 1873617.2189 | Kamrangirchar |  |  |  | Kamrangirchar | 1873617.2189 | 1726065.7983 | 147551.4206 | 8.5484 | OK
14 | Munshihati | 11 |  | HA-021100854-02 | 1 | 50106769 | 51488293 | 1381524 | 1 |  | 1381524 | 1392932.3343 | Kamrangirchar |  |  |  | Munshihati | 1392932.3343 | 1212171.698 | 180760.6363 | 14.9121 | OK
15 | Jhawchar | 11 |  | HA-021101028-02 | 1 | 98824125 | 100250925 | 1426800 | 1 |  | 1426800 | 1438582.214 | Kamrangirchar |  |  |  | Jhawchar | 1438582.214 | 1425641.3374 | 12940.8766 | 0.90772 | OK
16 | RMU Express | 11 |  | HA-021101248-02 | 1 | 5318135 | 5919945 | 601810 | 1 |  | 601810 | 606779.6203 | Kamrangirchar |  |  |  | RMU Express | 606779.6203 | 633839.2782 | -27059.6579 | -4.2692 | OK
17 | Koyla Ghat | 11 |  | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 1885309.02 | 1900877.505 | Kamrangirchar | 150 |  |  | Koyla Ghat | 1900877.505 | 2223108.4368 | -322230.9319 | -14.4946 | OK
18 | Muslimbagh | 11 |  | HA-021100908-02 | 1 | 24575572 | 26159019 | 1583447 | 1 |  | 1583447 | 1596522.772 | Kamrangirchar |  |  |  | Muslimbagh | 1596522.772 | 1696945.1326 | -100422.3607 | -5.9178 | OK
19 | Noyagaon | 11 |  | HA-021101087-02 | 1 | 3217494 | 5869693 | 2652199 | 1 |  | 2652199 | 2674100.301 | Kamrangirchar |  |  |  | Noyagaon | 2674100.301 | 2742632.8101 | -68532.5091 | -2.4988 | OK
20 | Nurbagh | 11 |  | HA-021100982-02 | 1 | 21245035 | 23098305 | 1853270 | 1 |  | 1853270 | 1868573.9135 | Kamrangirchar |  |  |  | Nurbagh | 1868573.9135 | 2159293.4513 | -290719.5378 | -13.4636 | OK
21 | Ali Nagar | 11 |  | HA-021101022-02 | 1 | 19758728 | 22030169 | 2271441 | 1 |  | 2271441 | 2290198.0816 | Kamrangirchar |  |  |  | Ali Nagar | 2290198.0816 | 2360084.8023 | -69886.7208 | -2.9612 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKE6223 | 1 | 42845.32 | 43047.09 | 201.77 | 120 |  | 24212.4 | 24412.3409 | Kamrangirchar |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 24412.3409 | 25361.4506 | -949.1097 | -3.7423 | OK
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 |  | 0 | 0 | Kamrangirchar |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 24734295.1776 | 24531717.42 | 24734295.1776 | 0.82578
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 24734295.1776
[5 empty] | Jigatola | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 24734295.1776 | 0
1: 33 KV SIDE of___ BGB 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1865.05 | 1865.53 | 0.48 | 240000 | 0 | 155520 | 155594.8284
10: TOTAL |  | 155520 | 155594.8284
SHATMASJID 33 KV VIA JIGATOLA OLD
8 | 33 kV Satmojid Via Zigatola Old | 33 | 0 | 43998033 | 1 | 151.9 | 182.259 | 30.359 | 270000 |  | 0 | 0
10: TOTAL |  | 0 | 0
NEW JIGATOLA 33 KV SIDE
2 | BGB-1 | 33 | 0 | 0 | 1 | 55.2 | 78.02 | 22.82 | 360000 | 0 | 8215200 | 8195547.638
11 | BGB-2 | 33 | 0 | 0 | 1 | 231.07 | 252.12 | 21.05 | 360000 | 0 | 7578000 | 7559871.9448
10: Total | 0 | 15793200 | 15755419.5827
10: GRAND TOTAL |  | 15948720 | 15911014.4111
BGB 33 KV SIDE (RECEIVING)
5 | 33 kV Kamrangirchar-1 | 33 |  | 43998032 | 1 | 1043.59 | 1043.59 | 0 | 270000 | 0
8 | 33 kV Satmojid Via Zigatola Old | 33 |  | 43998033 | 1 | 151.9 | 182.259 | 30.359 | 270000 | 8196930
| 33 kV Zigatola-1 | 33 |  | 43998033 | 1 | 0 | 0 | 0 | 270000 | 0
| 33 kV Kamrangirchar-2 | 33 |  | 43998027 | 1 | 755.48 | 756.089 | 0.609 | 270000 | 164430
| 33 kV Zigatola-2 | 33 |  | 43998031 | 1 | 307.36 | 335.616 | 28.256 | 270000 | 7629120
8: 0; 10: Total | 15990480 | 0 | 0
| BGB 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
8: 0; 10: Total |  | 0
0
| BGB 33 KV SIDE | [5 empty] | 0
6 | 33/11 kV T1 | 33 |  | 43998028 | 1 | 727.04 | 757.421 | 30.381 | 270000 |  | 8202870
9 | 33/11 kV T2 | 33 |  | 43998029 | 1 | 729.69 | 758.561 | 28.871 | 270000 |  | 7795170
11 | 33/11 kV T3 | 33 |  |  | 1 | 0 | 0 | 0 | 270000 |  | 0
10: Total |  | 15998040
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: NEW JIGATOLA 33 KV SIDE; 4: 15911014.4111; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BGB 33 KV NET IMPORT |  | 15911014.4111
6: BGB 33 KV NET IMPORT; 9=8-7: 15911014.4111 | 33 KV TX HV SIDE |  | 15998040
[10 empty] | LOSS UNITS=> |  | -87025.5889
[10 empty] | LOSS % IN => |  | -0.547%
| TOTAL IMPORT |  | 15911014.4111
1: 11 KV SIDE of___BGB 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BGB 11 KV SIDE
20 | 33/11 kV T-1 Incoming | 11 |  |  | 1 | 94784488 | 102906198 | 8121710 | 1 | 8121710 |  | 8200147.3554
29 | 33/11 kV T-2 Incoming | 11 |  |  | 1 | 95260896 | 102984199 | 7723303 | 1 | 7723303 |  | 7797892.6446
30 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 1 | 0 |  | 0
7: 0; 8: 0; 10: Total | 15845013 |  | 15998040
| BGB 11 KV SIDE |  |  |  |  | 0 | 0
12 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Nababgonj Park | 11 |  |  | 1 | 8188769 | 9205025 | 1016256 | 1 |  | 1016256 | 1021134.2367 | Azimpur |  |  |  | Nababgonj Park | 1021134.2367 | 1444952.9565 | -423818.7197 | -29.331 | OK
16 | Kholamura Ghat | 11 |  |  | 1 | 74784480 | 77275264 | 2490784 | 1 |  | 2490784 | 2502740.2728 | Kamrangirchar |  |  |  | Kholamura Ghat | 2502740.2728 | 2762472.0542 | -259731.7813 | -9.4022 | OK
17 | Khalpar | 11 |  |  | 1 | 82977184 | 84269168 | 1291984 | 1 |  | 1291984 | 1298185.7875 | Kamrangirchar |  |  |  | Khalpar | 1298185.7875 | 1375644.1828 | -77458.3953 | -5.6307 | OK
18 | Shahidnagar | 11 |  |  | 1 | 14195510 | 16043430 | 1847920 | 1 |  | 1847920 | 1856790.3941 | Azimpur |  |  |  | Shahidnagar | 1856790.3941 | 1877497.3089 | -20706.9148 | -1.1029 | OK
19 | BGB 1 No Gate | 11 |  |  | 1 | 31209790 | 32661410 | 1451620 | 1 |  | 1451620 | 1458588.073 | Azimpur |  |  |  | BGB 1 No Gate | 1458588.073 | 1375749.2129 | 82838.8601 | 6.0214 | OK
21 | Ganaktuli | 11 |  |  | 1 | 22588480 | 23467080 | 878600 | 1 |  | 878600 | 882817.4598 | Jigatola |  |  |  | Ganaktuli | 882817.4598 | 725654.1445 | 157163.3153 | 21.6582 | OK
22 | Thana | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Thana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Bot Tola Mazar | 11 |  |  | 1 | 30156751 | 32354152 | 2197401 | 1 |  | 2197401 | 2207948.9744 | Jigatola |  |  |  | Bot Tola Mazar | 2207948.9744 | 2074198.5352 | 133750.4392 | 6.4483 | OK
24 | Sikder Medical | 11 |  |  | 1 | 34515480 | 35690888 | 1175408 | 1 |  | 1175408 | 1181050.1989 | Jigatola |  |  |  | Sikder Medical | 1181050.1989 | 1134381.9061 | 46668.2927 | 4.114 | OK
25 | Gas Field | 11 |  |  | 1 | 51908120 | 53961540 | 2053420 | 1 |  | 2053420 | 2063276.8361 | Kamrangirchar |  |  |  | Gas Field | 2063276.8361 | 2061072.7993 | 2204.0369 | 0.10694 | OK
26 | Hazaribagh | 11 |  |  | 1 | 38417940 | 39936160 | 1518220 | 1 |  | 1518220 | 1525507.7666 | Jigatola |  |  |  | Hazaribagh | 1525507.7666 | 1485016.8997 | 40490.867 | 2.7266 | OK
27 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
31 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 |  |  | 1 | 2056.85 | 2117.04 | 60.19 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 |  |  | 1 | 1644.21 | 1699.35 | 55.14 | 10 |  |  | 0 | Azimpur | I don’t know which NOCS |  |  | 11/0.4 kV Aux. Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 15998040 | 15921613 | 15998040 | 0.48002
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Azimpur | at 33 KV level |  | 4336512.7038
[5 empty] | Kamrangirchar | at 33 KV level |  | 5864202.8965
[5 empty] | Jigatola | at 33 KV level |  | 5797324.3997
[5 empty] | Total = |  |  | 15998040 | 0
1: 132 KV SIDE of___ JIGATOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (SENDING)
5 | 132 kV Jigatola-1 | 132 | 0 | 42003953362 | 1 | 190.71 | 211.08 | 20.37 | 1440000 | 0 | 29332800 | 0
6 | 132 kV Jigatola-2 | 132 | 0 |  | 1 | 186.66 | 206.51 | 19.85 | 1440000 | 0 | 28584000 | 0
9=8-7: Total Import/Export | 0 | 57916800
10: Net Total | 57916800
JIGATOLA 132 KV SIDE (RECEIVING)
| 132 kV Kamrangirchar 1 | 132 | RECEIVE | 6604452 | 1 | 228.78 | 253.22 | 24.44 | 1200000 | 29328000
| 132 kV Kamrangirchar 2 | 132 |  |  | 1 | 223.76 | 247.55 | 23.79 | 1200000 | 28548000
7: 0; 8: 0; 9=8-7: Total Import/Export | 57876000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 57876000
| JIGATOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| JIGATOLA 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  |  | 1 | 179.19 | 198.23 | 19.04 | 1200000 |  | 22848000
3 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  |  | 1 | 273.54 | 302.73 | 29.19 | 1200000 |  | 35028000
10: Total |  | 57876000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (SENDING); 4: 57916800; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 57916800
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 57916800 | 33 KV NET IMPORT |  | 57549600
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 367200
2: IMPORT-4 | LOSS % IN => |  | 0.634%
| 132 KV TOTAL IMPORT |  | 57916800
1: 33 KV SIDE of___JIGATOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  |  | 1 | 296.99 | 328.71 | 31.72 | 720000 | 22838400
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  |  | 1 | 453.88 | 502.09 | 48.21 | 720000 | 34711200
7: 0; 8: 0; 10: Total | 57549600 |  | 0
| JIGATOLA 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  |  | 1 | 518.72 | 551.66 | 32.94 | 240000 |  | 7905600 | 7886688.2616 |  | 20152475.7431 | JIGATOLA NEW 3/11 KV SS | 0.38993 | 33/11 kV 28/35 MVA T-1 | 7886688.2616 | 6148810.5286 | 1737877.7331 | 28.2636 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  |  | 1 | 379.18 | 409.12 | 29.94 | 240000 |  | 7185600 | 7168410.6421 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 7168410.6421 | 8002566.5888 | -834155.9467 | -10.4236 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  |  | 1 | 323.26 | 344.55 | 21.29 | 240000 |  | 5109600 | 5097376.8394 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 5097376.8394 | 5201548.3761 | -104171.5368 | -2.0027 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 20200800 | 20152475.7431 |  |  |  |  | 33 KV Feeders | 20152475.7431 | 19352925.4935 | 799550.2496 | 4.1314 | OK
2 | BGB-1 | 33 |  |  | 1 | 55.2 | 78.02 | 22.82 | 360000 |  | 8215200 | 8195547.638 |  | 15755419.5827 | BGB 33/11 kv ss | 0.48002 | BGB-1 | 8195547.638 | 6676399.5755 | 1519148.0625 | 22.754 | OK
2 | Spair | 33 |  |  | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Dhaka Uddyan-1 | 33 |  |  | 1 | 171.09 | 189.31 | 18.22 | 360000 |  | 6559200 | 6543509.1132 |  |  |  |  | Dhaka Uddyan-1 | 6543509.1132 | 6259124.602 | 284384.5112 | 4.5435 | OK
4 | Green Road -1 | 33 |  |  | 1 | 23.2 | 23.42 | 0.22 | 360000 |  | 79200 | 79010.5381 |  | 14182391.5961 | Dhaka Uddan 33/11 kv ss | -0.2151 | Green Road -1 | 79010.5381 | 0 | 79010.5381 | #DIV/0! | #DIV/0!
9 | Green Road -2 | 33 |  |  | 1 | 23.22 | 37.21 | 13.99 | 360000 |  | 5036400 | 5024351.9481 |  |  |  |  | Green Road -2 | 5024351.9481 | 4813050.9871 | 211300.961 | 4.3902 | OK
10 | Dhaka Uddyan-2 | 33 |  |  | 1 | 174.84 | 196.11 | 21.27 | 360000 |  | 7657200 | 7638882.4829 |  |  |  |  | Dhaka Uddyan-2 | 7638882.4829 | 7755558.9896 | -116676.5067 | -1.5044 | OK
11 | BGB-2 | 33 |  |  | 1 | 231.07 | 252.12 | 21.05 | 360000 |  | 7578000 | 7559871.9448 |  | 2355950.5918 | Jigatla Old 33/11 kv ss | -1.953e-14 | BGB-2 | 7559871.9448 | 3813029.93 | 3746842.0148 | 98.2642 | FAULT
12 | Jigatola Old | 33 |  |  | 1 | 10.26 | 16.82 | 6.56 | 360000 |  | 2361600 | 2355950.5918 |  |  |  |  | Jigatola Old | 2355950.5918 | 2169110.4224 | 186840.1694 | 8.6137 | OK
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  |  | 1 | 0 | 0 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 37486800 | 37397124.2569 |  |  |  |  | 0 | 37397124.2569 | 31486274.5065 | 5910849.7504 | 18.7728 | OK
9=8-7: Grand Total | 57549600 | 57687600 | 57549600 | -0.23922
1: 11 KV SIDE of___JIGATOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JIGATOLA 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 92.16 | 123.48 | 31.32 | 250000 | 7830000 |  | 7860218.4343
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 105.52 | 134.01 | 28.49 | 250000 | 7122500 |  | 7149987.9691
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 77.62 | 98.11 | 20.49 | 250000 | 5122500 |  | 5142269.3397
7: 0; 8: 0; 10: Total | 20075000 |  | 20152475.7431
| JIGATOLA 11 kV SIDE |  |  |  |  | 0 | 0
| Salek Garden | 11 |  | 2761 | 1 | 549.1 | 593.11 | 44.01 | 60000 |  | 2640600 | 2650896.5462 | Jigatola |  |  |  | Salek Garden | 2650896.5462 | 2562123.5191 | 88773.027 | 3.4648 | OK
4 | Jigatola Local | 11 |  | 2850 | 1 | 438.35 | 469.67 | 31.32 | 60000 |  | 1879200 | 1886527.6034 | Jigatola |  |  |  | Jigatola Local | 1886527.6034 | 1807426.7227 | 79100.8807 | 4.3764 | OK
5 | Modina Rayer Bazar | 11 |  | 2851 | 1 | 603.31 | 628.51 | 25.2 | 60000 |  | 1512000 | 1517895.7729 | Switching |  |  |  | Modina Rayer Bazar | 1517895.7729 | 0 | 1517895.7729 | #DIV/0! | #DIV/0!
6 | City College | 11 |  | 2784 | 1 | 479.78 | 510.17 | 30.39 | 60000 |  | 1823400 | 1830510.0213 | Jigatola |  |  |  | City College | 1830510.0213 | 1777383.0604 | 53126.9609 | 2.9891 | OK
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Post Office | 11 |  | 2836 | 1 | 358.58 | 386.41 | 27.83 | 60000 |  | 1669800 | 1676311.0857 | Jigatola |  |  |  | Post Office | 1676311.0857 | 1671629.3692 | 4681.7165 | 0.28007 | OK
11 | Leather Institute | 11 |  | 2835 | 1 | 57.38 | 58.33 | 0.95 | 60000 |  | 57000 | 57222.2613 | Jigatola |  |  |  | Leather Institute | 57222.2613 | 189875.9456 | -132653.6843 | -69.8633 | CHECK
12 | Mina Bazar | 11 |  | 2853 | 1 | 181.89 | 194.57 | 12.68 | 60000 |  | 760800 | 763766.6032 | Jigatola |  |  |  | Mina Bazar | 763766.6032 | 746284.571 | 17482.0322 | 2.3425 | OK
13 | Mitali | 11 |  | 2852 | 1 | 330.42 | 368.1 | 37.68 | 60000 |  | 2260800 | 2269615.5842 | Switching |  |  |  | Mitali | 2269615.5842 | 3098703.3274 | -829087.7433 | -26.756 | OK
14 | Road-2 | 11 |  | 2839 | 1 | 584.66 | 624.12 | 39.46 | 60000 |  | 2367600 | 2376832.0316 | Jigatola |  |  |  | Road-2 | 2376832.0316 | 2301945.4038 | 74886.6278 | 3.2532 | OK
15 | SS-2 | 11 |  | 2838 | 1 | 272.32 | 291.23 | 18.91 | 60000 |  | 1134600 | 1139024.1692 | Jigatola |  |  |  | SS-2 | 1139024.1692 | 1127238.2087 | 11785.9605 | 1.0456 | OK
16 | Spare | 11 |  | 2772 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Bou Bazar | 11 |  | 2843 | 1 | 471.44 | 502.69 | 31.25 | 60000 |  | 1875000 | 1882311.2263 | Jigatola |  |  |  | Bou Bazar | 1882311.2263 | 1850088.7231 | 32222.5031 | 1.7417 | OK
18 | BGB | 11 |  | 2764 | 1 | 169.64 | 179.28 | 9.64 | 60000 |  | 578400 | 580655.3671 | Jigatola |  |  |  | BGB | 580655.3671 | 1007063.5596 | -426408.1925 | -42.3417 | CHECK
19 | Dhamondi-12 | 11 |  | 2763 | 1 | 375.07 | 400.32 | 25.25 | 60000 |  | 1515000 | 1520907.4708 | Dhanmondi |  |  |  | Dhamondi-12 | 1520907.4708 | 1213163.0828 | 307744.388 | 25.3671 | OK
10: Total | 20152475.7431 | 20074200 | 20152475.7431 | 0.38993
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Jigatola | at 33 KV level |  | 17952101.2033 | Including Switching
[5 empty] | Dhanmondi | at 33 KV level |  | 2200374.5399
[5 empty] | Total = |  |  | 20152475.7431 | 0
1: 11 KV SIDE of___JIGATOLA Switching S/S |  |  |  |  | Month July-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
No. | Name of Feeders. |  | CF | Number |  | 2023-04-01 | 2023-04-01 |  |  | Export | Import | Export | for Loss | Import
From Source End
5 | Modina Rayer Bazar | 11 | 0 | 2851 | 1 | 603.31 | 628.51 | 25.2 | 60000 | 0 | 1512000 | 1517895.7729 |  | 115
13 | Mitali | 11 | 0 | 2852 | 1 | 330.42 | 368.1 | 37.68 | 60000 | 0 | 2260800 | 2269615.5842 |  | 130
10: Total |  | 3772800 | 3787511.3571
Outgoing Feeder
2 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 676827.9 | 679467.069 | Dhanmondi | From 6/08/23 to 20/08/23
3 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1581226.92 | 1587392.6308 | Jigatola
3 | 11 kV Mitali | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1514745.18 | 1520651.6572 | Jigatola | Switching Total - Madina - Rayer Bazar
1: 33 KV SIDE of___ ZIGATOLA OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar 33 KV SIDE
16 | Zigatola Circuit-1 (BGB-1) | 33 | 0 | 30799088 | 1 | 5961.15 | 5961.15 | 0 | 240000 | 0 | 0 | 0
22 | Zigatola Circuit-2 (BGB-2) | 33 | 0 | 30799131 | 1.35 | 1865.05 | 1865.53 | 0.48 | 240000 | 0 | 155520 | 155594.8284
10: Total |  | 155520 | 155594.8284
Satmasjid 33 KV SIDE
13 | Jigatola U/G Circuit | 33 | 0 | 214393/37-2711 | 1 | 10131.445 | 10131.445 | 0 | 1000 | Estimated | 1566000 | 1558925.3967
10: Total |  | 1566000 | 1558925.3967
ZIGATOLA OLD 33 KV SIDE (RECEIVING)
3: 33; 4: RECEIVE; 6: 1; 9=8-7: 0 |  | 0
3: 33; 6: 1; 9=8-7: 0 |  | 0
3: 33; 6: 1; 9=8-7: 0 |  | 0
10: Total |  | 0 | 0
ZIGATOLA OLD 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
ZIGATOLA OLD 33 KV SIDE
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 | NET IMPORT | DHK61073 | 1 | 4005.95 | 4015.71 | 9.76 | 240000 |  | 2342400
2 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61075 | 1 | 4282.65 | 4282.65 | 0 | 240000 |  | 0
10: Total |  | 2342400
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Kamrangirchar 33 KV SIDE; 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 1558925.3967
2: Satmasjid 33 KV SIDE; 4: 1558925.3967; 6: 33 KV NET IMPORT; 9=8-7: 1558925.3967 | ZIGATOLA OLD 11 KV NET IMPORT |  | 2342400
2: IMPORT-3 | LOSS UNITS=> |  | -783474.6033
2: IMPORT-4 | LOSS % IN => |  | -50.26%
| TOTAL IMPORT |  | 1558925.3967
1: 11 KV SIDE of___ZIGATOLA OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
ZIGATOLA OLD 11 KV SIDE
9 | 33/11 kV T-3 Incoming | 11 |  |  | 1 | 0 | 0 | 0 | 60000 | 0 |  | 0
16 | 33/11 kV T-2 Incoming | 11 |  | DHK61029 | 1.25 | 4794.86 | 4794.86 | 0 | 180000 | 0 |  | 0
17 | 33/11 kV T-1 Incoming | 11 |  | DHK61028 | 1.32 | 1838.84 | 1848.08 | 9.24 | 180000 | 2195424 |  | 1558925.3967
7: 0; 8: 0; 10: Total | 2195424 |  | 1558925.3967
| ZIGATOLA OLD 11 KV SIDE |  |  |  |  | 0 | 0
6 | Lalmatia Sw/S(Dhanmondi Road 12A) | 11 |  | DHK60907 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Lalmatia SW |  |  |  | Lalmatia Sw/S(Dhanmondi Road 12A) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Mitali Road | 11 |  | DHK66479 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mitali Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Bou Bazar | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Bou Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Mina Bazar | 11 |  | DHK | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Jigatola |  |  |  | Mina Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | Simanto Square | 11 |  | DHK60946 | 1 | 1125.53 | 1141.66 | 16.13 | 60000 |  | 967800 | 967800 | Jigatola |  |  |  | Simanto Square | 967800 | 852145.3731 | 115654.6269 | 13.5722 | OK
12 | Post Office | 11 |  | DHK61074 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Post Office | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | Hazaribagh Sw/S-2 | 11 |  |  | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hazaribagh Sw/S-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Green Road Via Park | 11 |  | DHK61070 | 1 | 3415.05 | 3437.43 | 22.38 | 60000 |  | 1342800 | 1342800 | Jigatola |  |  |  | Green Road Via Park | 1342800 | 1229862.9154 | 112937.0846 | 9.1829 | OK
15 | PWD Quarters 11 kV Saleq Grand | 11 |  | DHK61028 | 1 | 3629.4 | 3630.54 | 1.14 | 60000 |  | 68400 | 68400 | Jigatola |  |  |  | PWD Quarters 11 kV Saleq Grand | 68400 | 74813.6195 | -6413.6195 | -8.5728 | OK
18 | Road No.-2 | 11 |  | DHK61035 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Road No.-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Hzaribagh O/H | 11 |  | DHK61033 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Hzaribagh O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | B.G.B | 11 |  | DHK61030 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | B.G.B | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV City College | 11 |  | DHK61031 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | 11 kV City College | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Modina Rayer Bazar | 11 |  | DHK61032 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Hazaribagh 11 kv s/s |  |  |  | Modina Rayer Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Jigatala Local | 11 |  | DHK61069 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Jigatola |  |  |  | Jigatala Local | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 |  | 243284 | 1 | 83791 | 84159 | 368 | 10 |  | 3680 | 3680 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-1 | 3680 | 2585.0234 | 1094.9766 | 42.3585 | FAULT
25 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 |  | 412277 | 1 | 39498 | 39663 | 165 | 10 |  | 1650 | 1650 | Jigatola |  |  |  | 33/0.4 kV Aux. Transformer AT-2 | 1650 | 5393.0685 | -3743.0685 | -69.4052 | CHECK
10: Grand Total | 2384330 | 2384330 | 2384330 | -1.953e-14
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Jigatola | at 33 KV level |  | 2384330
[5 empty] | Total = |  |  | 2384330 | 0
1: 33 KV SIDE of___ DHAKA UDDYAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KAMRANGIRCHAR 33 KV SIDE
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | 0 | BD001907 | 1 | 348.37 | 348.37 | 0 | 240000 | 0 | 0 | 0
1 | 34 kV Kamrangirchar Circuit-2 (O/H) | 33 | 0 | BD001912 | 1 | 428.23 | 428.23 | 0 | 240000 | 0 | 0 | 0
10: Total | 0 | 0 | 0
JIGATOLA 33 KV SIDE
3 | Dhaka Uddyan-1 | 33 | 0 | 0 | 1 | 171.09 | 189.31 | 18.22 | 360000 | 0 | 6559200 | 6543509.1132
10 | Dhaka Uddyan-2 | 33 | 0 | 0 | 1 | 174.84 | 196.11 | 21.27 | 360000 | 0 | 7657200 | 7638882.4829
10: Total | 0 | 14216400 | 14182391.5961
DHAKA UDDYAN 33 KV SIDE (RECEIVING)
| 33 kV Kamrangirchar Circuit-1 (O/H) | 33 | RECEIVE | BD017107 | 1 | 90469.03 | 90469.03 | 0 | 1125 |  | 0
| 33 kV Jigatala Incoming Circuit-1 | 33 |  | BD017098 | 1 | 54665.75 | 60324.25 | 5658.5 | 1125 |  | 6365812.5
| 33 kV Jigatala Incoming Circuit-2 | 33 |  | BD017097 | 1 | 56008.57 | 62541.61 | 6533.04 | 1125 |  | 7349670
| 33 kV Kamrangirchar Circuit-2 (O/H) | 33 |  | BD017108 | 1 | 73739.05 | 73739.05 | 0 | 1125 |  | 0
7: 0; 8: 0; 10: Total |  | 13715482.5 | 0
| DHAKA UDDYAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| DHAKA UDDYAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD017100 | 1 | 63967.95 | 70364.07 | 6396.12 | 1000 |  | 6396120
3 | 33/11 kV, 28/35 MVA T-3 (Future) | 33 |  | BD017075 | 1 | 0 | 0 |  | 1000 |  | 0
4 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD017109 | 1 | 46404.61 | 53777.98 | 7373.37 | 1000 |  | 7373370
10: Total |  | 13769490 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: KAMRANGIRCHAR 33 KV SIDE; 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 14182391.5961
2: JIGATOLA 33 KV SIDE; 4: 14182391.5961; 6: 33 KV NET IMPORT; 9=8-7: 14182391.5961 | 33 KV TX HV |  | 13769490
2: IMPORT-3 | LOSS UNITS=> |  | 412901.5961
2: IMPORT-4 | LOSS % IN => |  | 2.911%
| TOTAL IMPORT |  | 14182391.5961
1: 11 KV SIDE of___DHAKA UDDYAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UDDYAN 11 KV SIDE
14 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD014060 | 1 | 62776.85 | 69356.95 | 6580.1 | 1000 | 6580100 |  | 6297918.9235
15 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD014061 | 1 | 45509.07 | 53746.81 | 8237.74 | 1000 | 8237740 |  | 7884472.6726
7: 0; 8: 0; 10: Total | 14817840 |  | 14182391.5961
| DHAKA UDDYAN 11 KV SIDE |  |  |  |  | 0 | 0
7 | Spare | 11 |  | BD014030 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| D Block dhaka uddyan | 11 |  | BD014031 | 1 | 48613.5 | 48979.01 | 365.51 | 1000 |  | 365510 | 364723.8055 | Adabor |  |  |  | D Block dhaka uddyan | 364723.8055 | 376392.0985 | -11668.293 | -3.1 | OK
8 | Dill Mohammad O/H | 11 |  | BD014027 | 1 | 15908.7 | 17844.24 | 1935.54 | 1000 |  | 1935540 | 1931376.746 | Adabor |  |  |  | Dill Mohammad O/H | 1931376.746 | 1945233.0858 | -13856.3398 | -0.71232 | OK
9 | Turag O/H | 11 |  | BD014028 | 1 | 25472.56 | 26177.65 | 705.09 | 1000 |  | 705090 | 703573.3851 | Adabor |  |  |  | Turag O/H | 703573.3851 | 725059.1327 | -21485.7476 | -2.9633 | OK
10 | Nabadoy O/H | 11 |  | BD014025 | 1 | 34907.65 | 35784.32 | 876.67 | 1000 |  | 876670 | 874784.3247 | Adabor |  |  |  | Nabadoy O/H | 874784.3247 | 873886.7957 | 897.529 | 0.10271 | OK
11 | Chandrima O/H | 11 |  | BD014024 | 1 | 3855 | 4855.8 | 1000.8 | 1000 |  | 1000800 | 998647.327 | Adabor |  |  |  | Chandrima O/H | 998647.327 | 974655.0029 | 23992.3242 | 2.4616 | OK
12 | Shyamoli Housing Project-2 | 11 |  | BD014029 | 1 | 24761.38 | 26451.58 | 1690.2 | 1000 |  | 1690200 | 1686564.4606 | Adabor |  |  |  | Shyamoli Housing Project-2 | 1686564.4606 | 1305126.5223 | 381437.9383 | 29.2261 | OK
13 | Spare | 11 |  | BD014022 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Spare | 11 |  | BD014026 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | Spare | 11 |  | BD014023 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Adabor |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | U Lab | 11 |  | BD013959 | 1 | 35792.66 | 37965.55 | 2172.89 | 1000 |  | 2172890 | 2168216.2175 | Satmasjid |  |  |  | U Lab | 2168216.2175 | 2766170.13 | -597953.9125 | -21.6167 | OK
19 | Akota | 11 |  | BD014020 | 1 | 5565.65 | 6085.32 | 519.67 | 1000 |  | 519670 | 518552.2147 | Adabor |  |  |  | Akota | 518552.2147 | 529306.7232 | -10754.5085 | -2.0318 | OK
20 | Burigonga O/H | 11 |  | BD014019 | 1 | 4279.01 | 4671.23 | 392.22 | 1000 |  | 392220 | 391376.3535 | Adabor |  |  |  | Burigonga O/H | 391376.3535 | 420977.1349 | -29600.7813 | -7.0314 | OK
21 | Garden City | 11 |  | BD014021 | 1 | 81041.07 | 83851.34 | 2810.27 | 1000 |  | 2810270 | 2804225.2436 | Satmasjid |  |  |  | Garden City | 2804225.2436 | 2395190.4943 | 409034.7493 | 17.0773 | OK
22 | Avenue O/H | 11 |  | BD014017 | 1 | 11977.96 | 12957.25 | 979.29 | 1000 |  | 979290 | 977183.594 | Adabor |  |  |  | Avenue O/H | 977183.594 | 966250.121 | 10933.473 | 1.1315 | OK
23 | Chand Uddyan | 11 |  | BD014018 | 1 | 7472.53 | 8233.6 | 761.07 | 1000 |  | 761070 | 759432.9748 | Satmasjid |  |  |  | Chand Uddyan | 759432.9748 | 732469.8888 | 26963.086 | 3.6811 | OK
24 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4416 | 1 | 1760.35 | 1797.78 | 37.43 | 100 |  | 3743 | 3734.949 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 3734.949 | 3966.4616 | -231.5126 | -5.8368 | OK
25 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 |  | 0 | 0 | Adabor |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 14182391.5961 | 14212963 | 14182391.5961 | -0.2151
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 8450517.1602
[5 empty] | Satmasjid | at 33 KV level |  | 5731874.4359
[5 empty] | Total = |  |  | 14182391.5961 | 0
1: 132 KV SIDE of___ SATMOSJID 132/33/11 KV S/S |  |  |  |  | #REF! |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE (TARIFF POINT)
8 | Satmosjid-1 | 33 | IMPORT | 8993 638E | 1 | 4184.327 | 4191.915 | 7.588 | 180000 | 0 | 1365840
9 | Satmosjid -2 | 33 |  | 8993 669E | 1 | 5753.894 | 5801.534 | 47.64 | 180000 | 0 | 8575200
13 | Lalmatia | 33 |  |  | 1 | 5450.602 | 5452.879 | 2.277 | 180000 | 0 | 409860
14 | Transformer-1 | 33 |  | 50147586E | 1 | 3099.791 | 3141.193 | 41.402 | 750000 | 0 | 31051500
15 | Transformer-2 | 33 |  | 50148569E | 1 | 2739.184 | 2781.285 | 42.101 | 750000 | 0 | 31575750
9=8-7: Total Import/Export | 0 | 72978150
10: Net Total | 72978150
SATMOSJID 33 KV SIDE (RECEIVING)
| 33 KV GT-1 Incomming |  | RECEIVE |  | 1 |  |  | 0
| 33 KV GT-2 Incomming |  |  |  | 1 |  |  | 0
| 33 KV Satmosjid-1 Incomming |  |  |  | 1 |  |  | 0
Total Import/Export
9=8-7: Net Total | 0 | 0
SATMOSJID 132 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 4: EXPORT |  | 0
2: Feeder No.2 |  | 0
10: Total |  | 0
SATMOSJID 132 KV SIDE
10: Total |  | 0
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV SIDE (TARIFF POINT); 4: 72978150; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 72978150
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 72978150 | 33 KV NET IMPORT |  | 72978150
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 72978150
1: 33 KV SIDE of___SATMOSJID 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 33 KV SIDE
9 | 132/33 kV, 80/120 MVA GT-1 Incoming | 33 |  | 50147586 | 1 | 3099.791 | 3141.193 | 41.402 | 750000 | 31051500
10 | 132/33 kV, 80/120 MVA GT-2 Incoming | 33 |  | 50148569 | 1 | 2739.184 | 2781.285 | 42.101 | 750000 | 31575750
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  | 0 |  | 0
7: 0; 8: 0; 10: Total | 62627250 |  | 72978150
| SATMOSJID 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 |  | SICAM | 1 | 39.43 | 48.81 | 9.38 | 1000000 |  | 9380000 | 9337624.6623 |  | -0.13906 | Satmasjid 3/11 kv ss | 19601047.9318 | 33/11 kV, 20/28 MVA T-1 (HV) | 9337624.6623 | 9865381.5788 | -527756.9165 | -5.3496 | OK
11 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 |  | SICAM | 1 | 40.13 | 50.44 | 10.31 | 1000000 |  | 10310000 | 10263423.2695 |  |  |  |  | 33/11 kV, 20/28 MVA T-2 (HV) | 10263423.2695 | 9865381.5788 | 398041.6907 | 4.0347 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 19690000 | 19601047.9318 |  |  |  |  | 33 KV Feeders | 19601047.9318 | 19730763.1576 | -129715.2258 | -0.65743 | OK
6 | BGB | 33 |  | 214393/40-2711 | 1 | 31.16 | 35.2954 | 4.1354 | 1000 | Estimated | 0 | 0 |  | 0.48002 | BGB 33/11 KV SS | 0 | BGB | 0 | 1494155.0851 | -1494155.0851 | -100 | CHECK
| Asad Gate Circuit-1 | 33 |  | 214393/44-2711 | 1 | 54.83 | 63.8262 | 8.9962 | 1000 | Estimated | 9455256 | 9412540.6838 |  | 0.8 | ASADGATE 33/11 KV SS | 18243313.7037 | Asad Gate Circuit-1 | 9412540.6838 | 9798762.2837 | -386221.5999 | -3.9415 | OK
8 | Lalmatia Circuit-2 | 33 |  | SICAM | 1 | 82.53 | 105.9 | 23.37 | 1000 | Estimated | 14625630 | 14559556.8645 |  | 1.0252 | LALMATIA 33/11 KV SS | 14559556.8645 | Lalmatia Circuit-2 | 14559556.8645 | 15333258.5486 | -773701.6841 | -5.0459 | OK
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 235.65 | 9396.2208 | 9160.5708 | 1000 | Estimated | 8870848.2 | 8830773.02 |  | -1.953e-14 | JIGATOLA OLD 33/11 KV SS | 1558925.3967 | Asad Gate Circuit-2 | 8830773.02 | 6811012.7204 | 2019760.2996 | 29.6543 | OK
13 | Jigatola U/G Circuit | 33 |  | 214393/37-2711 | 1 | 10131.445 | 10131.445 | 0 | 1000 | Estimated | 1566000 | 1558925.3967 |  | -0.07909 | JAPAN GARDEN 33/11 KV SS | 19015306.1033 | Jigatola U/G Circuit | 1558925.3967 | 1481903.0134 | 77022.3833 | 5.1975 | OK
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 32260 | 41020 | 8760 | 1000 | Estimated | 19101600 | 19015306.1033 |  |  |  |  | Japan Garden City-2 | 19015306.1033 | 18772385.1912 | 242920.9121 | 1.294 | OK
10: Total |  | 53619334.2 | 53377102.0682 |  |  |  |  | 0 | 53377102.0682 | 53691476.8424 | -314374.7742 | -0.58552 | OK
9=8-7: Grand Total | 72978150 | 73309334.2 | 72978150 | -0.45176
1: 11 KV SIDE of___SATMOSJID 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
SATMOSJID 11 KV SIDE
23 | 33/11 kV T-1 Incoming | 11 |  | DHK60998 | 1 | 4739.43 | 4796.15 | 56.72 | 180000 | 10209600 |  | 9714884.9938
24 | 33/11 kV T-2 Incoming | 11 |  | DHK61044 | 1 | 4827.25 | 4884.97 | 57.72 | 180000 | 10389600 |  | 9886162.938
7: 0; 8: 0; 10: Total | 20599200 |  | 19601047.9318
| SATMOSJID 11 kV SIDE |  |  |  |  | 0 | 0
16 | Lalmatia O/H | 11 |  | DHK61042 | 1 | 3125.6 | 3147.3 | 21.7 | 60000 |  | 1302000 | 1300189.4979 | Satmasjid |  |  |  | Lalmatia O/H | 1300189.4979 | 1240075.1783 | 60114.3195 | 4.8476 | OK
16 | Asad Avenue (South) | 11 |  | DHK 60999 | 1 | 2895.94 | 2897.6 | 1.66 | 60000 |  | 99600 | 99461.5008 | Satmasjid |  |  |  | Asad Avenue (South) | 99461.5008 | 201384.8525 | -101923.3518 | -50.6112 | CHECK
17 | Madrasha Road | 11 |  | DHK61004 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Shyamoli |  |  |  | Madrasha Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Bashbari | 11 |  | DHK61002 | 1 | 2340.79 | 2370.58 | 29.79 | 60000 |  | 1787400 | 1784914.5226 | Satmasjid |  |  |  | Bashbari | 1784914.5226 | 1599091.6268 | 185822.8959 | 11.6205 | OK
19 | Road-27 | 11 |  | DHK61001 | 1 | 1432.05 | 1438.38 | 6.33 | 60000 |  | 379800 | 379271.8673 | Satmasjid |  |  |  | Road-27 | 379271.8673 | 89903.952 | 289367.9153 | 321.8634 | FAULT
20 | Boishakhi O/H | 11 |  | DHK61024 | 1 | 4043.27 | 4091.98 | 48.71 | 60000 |  | 2922600 | 2918535.965 | Dhanmondi |  |  |  | Boishakhi O/H | 2918535.965 | 3026167.0253 | -107631.0603 | -3.5567 | OK
21 | Katasur O/H | 11 |  | DHK61003 | 1 | 3581.57 | 3605.55 | 23.98 | 60000 |  | 1438800 | 1436799.27 | Satmasjid |  |  |  | Katasur O/H | 1436799.27 | 1431270.9163 | 5528.3537 | 0.38625 | OK
22 | Nurjahan Road | 11 |  | DHK61000 | 1 | 1793.34 | 1817.79 | 24.45 | 60000 |  | 1467000 | 1464960.0563 | Shyamoli |  |  |  | Nurjahan Road | 1464960.0563 | 1437863.8728 | 27096.1836 | 1.8845 | OK
25 | polpar over head | 11 |  | DHK61003 | 1 | 1761.42 | 1797.61 | 36.19 | 60000 |  | 2171400 | 2168380.5497 | Dhanmondi |  |  |  | polpar over head | 2168380.5497 | 2135518.5405 | 32862.0091 | 1.5388 | OK
26 | Satmosjid Housing | 11 |  | DHK61043 | 1 | 2792.38 | 2802.53 | 10.15 | 60000 |  | 609000 | 608153.1522 | Satmasjid |  |  |  | Satmosjid Housing | 608153.1522 | 0 | 608153.1522 | #DIV/0! | #DIV/0!
27 | Physical College | 11 |  | DHK61041 | 1 | 3216.68 | 3261.37 | 44.69 | 60000 |  | 2681400 | 2677671.3668 | Satmasjid |  |  |  | Physical College | 2677671.3668 | 2636583.2332 | 41088.1336 | 1.5584 | OK
28 | Asad Avenue (North) | 11 |  | DHK61022 | 1 | 2725.31 | 2725.37 | 0.06 | 60000 |  | 3600 | 3594.994 | Shyamoli |  |  |  | Asad Avenue (North) | 3594.994 | 0 | 3594.994 | #DIV/0! | #DIV/0!
29 | Spare Feeder | 11 |  | DHK61025 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Satmasjid |  |  |  | Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
30 | Ghraphic artch college | 11 |  | DHK61023 | 1 | 1042.11 | 1069.16 | 27.05 | 60000 |  | 1623000 | 1620743.1298 | Dhanmondi |  |  |  | Ghraphic artch college | 1620743.1298 | 1570921.7218 | 49821.408 | 3.1715 | OK
31 | Mohammadpur O/H | 11 |  | DHK61025 | 1 | 2132.57 | 2160.67 | 28.1 | 60000 |  | 1686000 | 1683655.5249 | Shyamoli |  |  |  | Mohammadpur O/H | 1683655.5249 | 1660825.6738 | 22829.8511 | 1.3746 | OK
32 | Bosila Feeder | 11 |  | DHK60997 | 1 | 4018.46 | 4059.26 | 40.8 | 60000 |  | 2448000 | 2444595.9223 | Satmasjid |  |  |  | Bosila Feeder | 2444595.9223 | 2900301.4925 | -455705.5702 | -15.7124 | OK
33 | 11/0.4 kV Auxiliary Transformer | 0.415 |  | ELIB 7375 | 1 | 5560.3 | 5698.37 | 138.07 | 60 |  | 8284.2 | 8272.6804 | Satmasjid |  |  |  | 11/0.4 kV Auxiliary Transformer | 8272.6804 | 8691.9141 | -419.2337 | -4.8233 | OK
10: Total | 20599200 | 20627884.2 | 20599200 | -0.13906
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Satmasjid | at 33 KV level |  | 10739329.7803
[5 empty] | Shyamoli | at 33 KV level |  | 3152210.5752
[5 empty] | Dhanmondi | at 33 KV level |  | 6707659.6445
[5 empty] | Total = |  |  | 20599200 | 0
1: 33 KV SIDE of___ JAPAN GERDEN CITY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SENDING SIDE (Tariff Point)
| Kallyanpur to Japangarden-1 | 33 |  | 38992490 (new) | 1 | 1.16 | 1.22 | 0.06 | 180000 | 0 | 10800 | 10800
| Kallyanpur to Japangarden-2 | 33 |  | 8993669E | 1 | 5753.894 | 5801.534 | 47.64 | 180000 | 0 | 8575200 | 8575200
14 | Japan Garden City-2 | 33 |  | SICAM | 1 | 32260 | 41020 | 8760 | 1000 | Estimated | 19101600 | 19015306.1033
10: Total | 0 | 27687600 | 27601306.1033
JAPAN GERDEN CITY 33 KV SIDE (RECEIVING)
| Satmosjid Incoming U/G | 33 | RECEIVE | DHK86051 | 1 | 2920.04 | 2953 | 32.96 | 270000 |  | 8899200
| kallyanpur U/G-2 | 33 |  | DHK61100 | 1 | 2807.02 | 2838.71 | 31.69 | 270000 |  | 8556300
7: 0; 8: 0; 10: Total |  | 17455500
| JAPAN GERDEN CITY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 33 KV Japan Genden City | 33 |  | DHK15681 | 1 | 358.27 | 442.67 | 84.4 | 18000 |  | 1519200 | 1519200 | Adabor
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total |  | 1519200
[6 empty] | 0 | 0
| JAPAN GERDEN CITY 33 KV SIDE |  |  |  |  | 0 | 0
| 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK61080 | 1 | 4181.99 | 4230.59 | 48.6 | 180000 |  | 8748000
3 | 33/11 kV 20/28 MVA T-1 (HV) | 33 |  | 86052 | 1 | 4942 | 4991.08 | 49.08 | 180000 |  | 8834400
10: Total |  | 17582400 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV SENDING SIDE (Tariff Point); 4: 19101600; 6: EXPORT TO OTHER S/S; 9=8-7: 1519200 | JAPAN GERDEN CITY 33 KV NET IMPORT |  | 17582400
2: IMPORT-2; 6: JAPAN GERDEN CITY 33 KV NET IMPORT; 9=8-7: 17582400 | 33 KV TX HV SIDE |  | 17582400
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 19101600
1: 11 KV SIDE of___JAPAN GERDEN CITY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
JAPAN GERDEN CITY 11 KV SIDE
9 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 |  | DHK61079 | 1 | 5575.08 | 5630.52 | 55.44 | 160000 | 8870400 |  | 8827823.3653
10 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK61082 | 1 | 4651.91 | 4706.89 | 54.98 | 160000 | 8796800 |  | 8754576.6347
7: 0; 8: 0; 10: Total | 17667200 |  | 17582400
| JAPAN GERDEN CITY 11 KV SIDE |  |  |  |  | 0 | 0
5 | Dhaka Uddyan | 11 |  | DHK86067 | 1 | 3249.81 | 3250.6 | 0.79 | 60000 |  | 47400 | 47362.5115 | Adabor |  |  |  | Dhaka Uddyan | 47362.5115 | 34177.6075 | 13184.904 | 38.5776 | OK
| Shia Mosjid | 11 |  | DHK60950 | 1 | 3392.62 | 3431.26 | 38.64 | 60000 |  | 2318400 | 2316566.3838 | Shyamoli |  |  |  | Shia Mosjid | 2316566.3838 | 2321079.2736 | -4512.8898 | -0.19443 | OK
6 | Shekhar Tek | 11 |  | DHK60977 | 1 | 2311.48 | 2346.34 | 34.86 | 60000 |  | 2091600 | 2089945.7593 | Adabor |  |  |  | Shekhar Tek | 2089945.7593 | 2160384.5576 | -70438.7984 | -3.2605 | OK
7 | Madrasha Road | 11 |  | DHK61083 | 1 | 1945.1 | 1969.45 | 24.35 | 60000 |  | 1461000 | 1459844.4991 | Shyamoli |  |  |  | Madrasha Road | 1459844.4991 | 1147648.0831 | 312196.416 | 27.2031 | OK
8 | Baitul Aman Housing | 11 |  | DHK668115 | 1 | 4021.57 | 4071 | 49.43 | 60000 |  | 2965800 | 2963454.3569 | Adabor |  |  |  | Baitul Aman Housing | 2963454.3569 | 2980047.5303 | -16593.1734 | -0.55681 | OK
11 | Shyamoli Square | 11 |  | DHK86063 | 1 | 452.52 | 458.1 | 5.58 | 30000 |  | 167400 | 167267.6038 | Shyamoli |  |  |  | Shyamoli Square | 167267.6038 | 170888.0374 | -3620.4337 | -2.1186 | OK
12 | Mohammadi Housing | 11 |  | DHK60948 | 1 | 3751.71 | 3785.19 | 33.48 | 60000 |  | 2008800 | 2007211.2456 | Adabor |  |  |  | Mohammadi Housing | 2007211.2456 | 1954719.3056 | 52491.94 | 2.6854 | OK
13 | Chand Housing | 11 |  | DHK60867 | 1 | 2147.7 | 2161.88 | 14.18 | 60000 |  | 850800 | 850127.1046 | Satmasjid |  |  |  | Chand Housing | 850127.1046 | 960570.6526 | -110443.548 | -11.4977 | OK
14 | PC Culture Housing | 11 |  | DHK60979 | 1 | 4021.99 | 4067.35 | 45.36 | 60000 |  | 2721600 | 2719447.494 | Adabor |  |  |  | PC Culture Housing | 2719447.494 | 2646665.9554 | 72781.5386 | 2.7499 | OK
15 | Mehedibagh | 11 |  | DHK68121 | 1 | 2208.55 | 2259.27 | 50.72 | 60000 |  | 3043200 | 3040793.1415 | Adabor |  |  |  | Mehedibagh | 3040793.1415 | 3013625.5306 | 27167.6109 | 0.90149 | OK
16 | 33/11 kV Incoming (Spare) | 11 |  |  | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor |  |  |  | 33/11 kV Incoming (Spare) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.4 kV Auxiliary Transformer | 11 |  |  | 1 | 642363 | 647547 | 5184 | 1 |  | 5184 | 5179.9 | Adabor |  |  |  | 11/0.4 kV Auxiliary Transformer | 5179.9 | 5393.4663 | -213.5663 | -3.9597 | OK
10: Grand Total | 17667200 | 17681184 | 17667200 | -0.07909
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Adabor | at 33 KV level |  | 12873394.4087
[5 empty] | Shyamoli | at 33 KV level |  | 3943678.4867
[5 empty] | Satmasjid | at 33 KV level |  | 850127.1046
[5 empty] | Total = |  |  | 17667200 | 0
1: 132 KV SIDE of___ DHAKA UNIVERSITY 132/33/11 KV S/S |  |  |  |  | #REF! |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
132 KV SIDE (TARIFF POINT)
1 | Dhaka University-1 (Exp) | 132 |  | 42627810 | 1 | 145.541 | 157.05 | 11.509 | 960000 | 0 | 11048640
2 | Dhaka University-1 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| Dhaka University-2 (Exp) | 132 |  | 42627812 | 1 | 146.811 | 158.41 | 11.599 | 960000 | 0 | 11135040
3 | Dhaka University-2 (Imp) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
9=8-7: Total Import/Export | 0 | 22183680
10: Net Total | 22183680
DHAKA UNIVERSITY 132 KV SIDE (RECEIVING)
| 132 kV Rampura 1 | 132 |  | 2877 | 1 | 116.48 | 125.9 | 9.42 | 1200000 |  | 11304000
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 234.01 | 234.01 | 0 | 1200000 |  | 0
| 132 kV Dhanmondi 1 | 132 |  | 2817 | 1 | 300 | 300 | 0 | 1200000 |  | 0
| 132 kV Rampura 2 | 132 |  | 2811 | 1 | 117.43 | 126.72 | 9.29 | 1200000 |  | 11148000
7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 22452000
7: 0; 8: 0; 9=8-7: Net Total | 22452000
| DHAKA UNIVERSITY 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 132 KV Dhanmondi | 132 | 0 | SIEM0480 | 1 | 68964 | 79348 | 10384 | 1000 |  | 10384000
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total |  | 10384000
| DHAKA UNIVERSITY 132 KV SIDE |  |  |  |  | 0 | 0
1 | 132/33kV, 80/120 MVA GT-1 (HV) | 132 |  | 2752 | 1 | 196.09 | 200.96 | 4.87 | 1200000 |  | 5844000
4 | 132/33kV, 80/120 MVA GT-2 (HV) | 132 |  | 2867 | 1 | 214.02 | 219.01 | 4.99 | 1200000 |  | 5988000
10: Total |  | 11832000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (TARIFF POINT); 4: 22183680; 6: EXPORT TO OTHER S/S; 9=8-7: 10384000 | 132 KV NET IMPORT |  | 11832000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 11832000 | 33 KV NET IMPORT |  | 11714400
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 117600
2: IMPORT-4 | LOSS % IN => |  | 0.9939%
| 132 KV TOTAL IMPORT |  | 22183680
1: 33 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
6 | 132/33 kV 80/120 MVA GT-1 Incomming | 33 |  | 2769 | 1 | 324.48 | 332.48 | 8 | 720000 | 5760000
7 | 132/33 kV 80/120 MVA GT-2 Incomming | 33 |  | 2830 | 1 | 353.43 | 361.7 | 8.27 | 720000 | 5954400
7: 0; 8: 0; 10: Total | 11714400 |  | 0
| DHAKA UNIVERSITY 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33/11 kV 28/35 MVA T-1 | 33 |  | 2751 | 1.15 | 31.01 | 32.6 | 1.59 | 240000 |  | 438840 | 440508.7167 |  | 0.81432 | DHAKA UNIVERSITY 33/11 KV SS | 1898030.038 | 33/11 kV 28/35 MVA T-1 | 440508.7167 | 399578.32 | 40930.3967 | 10.2434 | OK
8 | 33/11 kV 28/35 MVA T-2 | 33 |  | 4253 | 1 | 46.78 | 50.74 | 3.96 | 240000 |  | 950400 | 954013.9558 |  |  |  |  | 33/11 kV 28/35 MVA T-2 | 954013.9558 | 884442.1312 | 69571.8246 | 7.8662 | OK
13 | 33/11 kV 28/35 MVA T-3 | 33 |  | 2808 | 1 | 16.48 | 18.57 | 2.09 | 240000 |  | 501600 | 503507.3655 |  |  |  |  | 33/11 kV 28/35 MVA T-3 | 503507.3655 | 505395.5035 | -1888.138 | -0.3736 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 1890840 | 1898030.038 |  |  |  |  | 33 KV Feeders | 1898030.038 | 1789415.9547 | 108614.0833 | 6.0698 | OK
2 | Spare | 33 |  | 2805 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| BB Avenue-1 | 33 |  | 2804 | 1.5 | 139.96 | 147.58 | 7.62 | 360000 |  | 4114800 | 4130446.7857 |  | 0.22998 | BB AVENUE 33/11 KV SS | 5543399.2732 | BB Avenue-1 | 4130446.7857 | 4854712.5772 | -724265.7914 | -14.9188 | OK
3 | DMC Circuit-1 | 33 |  | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 |  | 0 | 0 |  |  |  |  | DMC Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Biddyut Bhaban Circuit-1 | 33 |  | 2858 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  | 2.024 | DMC 33/11 KV SS | 4272970.6888 | Biddyut Bhaban Circuit-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Biddyut Bhaban Circuit-2 | 33 |  | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Biddyut Bhaban Circuit-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | DMC Circuit-2 | 33 |  | 2803 | 1.03 | 288.56 | 300.04 | 11.48 | 360000 |  | 4256784 | 4272970.6888 |  | 0.45412 | BIDDYUT BHABAN 33/11 KV SS | 0 | DMC Circuit-2 | 4272970.6888 | 4785463.674 | -512492.9852 | -10.7094 | OK
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 180.09 | 184 | 3.91 | 360000 |  | 1407600 | 1412952.4875 |  |  |  |  | BB Avenue-2 | 1412952.4875 | 1501607.7941 | -88655.3066 | -5.904 | OK
12 | Spare | 33 |  | 2806 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33/0.4 kV, 500 kVA AT-1 | 0.415 |  | 7977 | 1 | 3535.99 | 3535.99 | 0 | 320 |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33/0.4 kV, 500 kVA AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 33/0.4 kV, 500 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 9779184 | 9816369.962 |  |  |  |  | 0 | 9816369.962 | 11141784.0453 | -1325414.0833 | -11.8959 | OK
9=8-7: Grand Total | 11714400 | 11670024 | 11714400 | 0.38026
1: 11 KV SIDE of___DHAKA UNIVERSITY 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 11 KV SIDE
3 | 33/11 kV Transformer-1 Incoming | 11 |  | 2762 | 1 | 38.03 | 40.3 | 2.27 | 250000 | 567500 |  | 520982.852
9 | 33/11 kV Transformer-2 Incoming | 11 |  | 2771 | 1 | 43.53 | 47.3 | 3.77 | 250000 | 942500 |  | 865244.6485
20 | 33/11 kV Transformer-3 Incoming | 11 |  | DHK61108 | 1 | 15.07 | 17.3 | 2.23 | 250000 | 557500 |  | 511802.5374
7: 0; 8: 0; 10: Total | 2067500 |  | 1898030.038
| DHAKA UNIVERSITY 11 kV SIDE |  |  |  |  | 0 | 0
| Mokarom Bhabon | 11 |  | 2761 | 1 | 46.92 | 50 | 3.08 | 60000 |  | 184800 | 186304.8566 | Ramna |  |  |  | Mokarom Bhabon | 186304.8566 | 168036.2342 | 18268.6224 | 10.8718 | OK
4 | 11 kV Shaid Minar RMU | 11 |  | 2850 | 1 | 110.73 | 116.8 | 6.07 | 60000 |  | 364200 | 367165.7402 | Ramna |  |  |  | 11 kV Shaid Minar RMU | 367165.7402 | 336672.5979 | 30493.1423 | 9.0572 | OK
5 | 11 kV Shaidulla Hall | 11 |  | 2851 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | 11 kV Shaidulla Hall | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  | 2784 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  | 2799 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  | 2775 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | MBA Bhabon | 11 |  | 2836 | 1 | 86.15 | 90.5 | 4.35 | 60000 |  | 261000 | 263125.3657 | Ramna |  |  |  | MBA Bhabon | 263125.3657 | 250253.9631 | 12871.4026 | 5.1433 | OK
11 | Suprime Court | 11 |  | 2835 | 1 | 44.16 | 50 | 5.84 | 60000 |  | 350400 | 353253.3645 | Ramna |  |  |  | Suprime Court | 353253.3645 | 298264.3158 | 54989.0488 | 18.4363 | OK
12 | Karjon Hall | 11 |  | 2853 | 1 | 50.23 | 55.9 | 5.67 | 60000 |  | 340200 | 342970.3043 | Ramna |  |  |  | Karjon Hall | 342970.3043 | 313267.551 | 29702.7533 | 9.4816 | OK
13 | Spare | 11 |  | 2852 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Swimming Pool | 11 |  | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 |  | 0 | 0 | Ramna |  |  |  | Swimming Pool | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | 2838 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Police Head Quarter RMU | 11 |  | 2772 | 1 | 62.93 | 72.1 | 9.17 | 60000 |  | 550200 | 554680.3686 | Ramna |  |  |  | Police Head Quarter RMU | 554680.3686 | 488505.3381 | 66175.0306 | 13.5464 | OK
17 | Spare | 11 |  | 2843 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | Spare | 11 |  | 2764 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Spare | 11 |  | 2763 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 2067500 | 2050800 | 2067500 | 0.81432
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2067500
[5 empty] | Total = |  |  | 2067500 | 0
1: 33 KV SIDE of___ BIDDYUT BHABAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 KV SIDE
4 | Biddyut Bhaban Circuit-1 | 33 | 0 | 2858 | 1 | 0 | 0 | 0 | 360000 | 0 | 0 | 0
9 | Biddyut Bhaban Circuit-2 | 33 | 0 | 2753 | 1 | 408.2 | 408.2 | 0 | 360000 | 0 | 0 | 0
10: Total | 0 | 0 | 0
0 | 33kV Biddyut Bhaban Circuit | 33 | Export | 0 | 1 | 476568 | 486697 | 10129 | 600 | 0 | 6077400 | 0 | 0
10: Total | 0 | 6077400 | 0
BIDDYUT BHABAN 33 KV SIDE (RECEIVING)
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 9268.7 | 31669.53 | 22400.83 | 270 | 0 | 6048224.1
| Motijheel Incoming | 33 |  | DHK-C9344 | 1 | 21216.15 | 21216.15 | 0 | 270 |  | 0
| Dhaka University Incoming-1 | 33 |  | DHK-C9341 | 1 | 0 | 0 | 0 | 270 |  | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58473.17 | 58473.3 | 0.13 | 270 | 35.1
| Dhaka University Incoming-2 | 33 |  | DHK-C9343 | 1 | 45329.41 | 45329.41 | 0 | 270 |  | 0
7: 0; 8: 0; 10: Total |  | 6048224.1 | 0
| BIDDYUT BHABAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| PNT S/W | 33 |  | DGK-C9340 | 1 | 58473.17 | 58473.3 | 0.13 | 270 |  | 35.1
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total |  | 35.1
[6 empty] | 0 | 0
| BIDDYUT BHABAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 20/28 MVA T1 (HV) | 33 |  | DHK-C9342 | 1 | 69335.3 | 76426.69 | 7091.39 | 270 |  | 1914675.3
3 | 33/11 kV, 20/28 MVA T2 (HV) | 33 |  | DHK-C9308 | 1 | 3692.2 | 19008.37 | 15316.17 | 270 |  | 4135365.9
10: Total |  | 6050041.2 | 6050076.3
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: DHAKA UNIVERSITY 33 KV SIDE; 4: 6048224.1; 6: EXPORT TO OTHER S/S; 9=8-7: 35.1 | 33 KV NET IMPORT |  | 6048189
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 6048189 | 33 KV TX HV SIDE |  | 6050041.2
2: IMPORT-3 | LOSS UNITS=> |  | -1852.2
2: IMPORT-4 | LOSS % IN => |  | -0.03062%
| TOTAL IMPORT |  | 6048224.1
1: 11 KV SIDE of___BIDDYUT BHABAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BIDDYUT BHABAN 11 KV SIDE
9 | 33/11 kV T-1 Incoming (LV) | 11 |  | DHK-C9316 | 1 | 48730 | 56646.38 | 7916.38 | 240 | 1899931.2 |  | 1905943.6214
10 | 33/11 kV T-2 Incoming (LV) | 11 |  | DHK-C9377 | 1 | 52497 | 69701.91 | 17204.91 | 240 | 4129178.4 |  | 4142245.3786
7: 0; 8: 0; 10: Total | 6029109.6 |  | 6048189
| BIDDYUT BHABAN 11 KV SIDE |  |  |  |  | 0 | 0
6 | Segunbagicha | 11 |  | DHK-C9360 | 1 | 71954 | 82917.41 | 10963.41 | 60 |  | 657804.6 | 660791.8145 | Ramna |  |  |  | Segunbagicha | 660791.8145 | 648570.0837 | 12221.7308 | 1.8844 | OK
| Secretariat RMU | 11 |  | DHK-C9379 | 1 | 68931.7 | 71809.95 | 2878.25 | 60 |  | 172695 | 173479.2405 | Ramna |  |  |  | Secretariat RMU | 173479.2405 | 157347.3651 | 16131.8754 | 10.2524 | OK
7 | NBR RMU | 11 |  | DHK-C9319 | 1 | 43622.4 | 51570.08 | 7947.68 | 60 |  | 476860.8 | 479026.3146 | Ramna |  |  |  | NBR RMU | 479026.3146 | 471677.0943 | 7349.2203 | 1.5581 | OK
8 | Ramna 11 kV Sw/S-2 | 11 |  | DHK-C9364 | 1 | 99344.1 | 108506.79 | 9162.69 | 60 |  | 549761.4 | 552257.97 | Ramna |  |  |  | Ramna 11 kV Sw/S-2 | 552257.97 | 1047973.9631 | -495715.9931 | -47.3023 | CHECK
11 | Ramna 11 kV Sw/S-1 | 11 |  | DHK-C9375 | 1 | 30685.5 | 46623.88 | 15938.38 | 60 |  | 956302.8 | 960645.5509 | Ramna |  |  |  | Ramna 11 kV Sw/S-1 | 960645.5509 | 37569.2064 | 923076.3446 | 2457.0025 | FAULT
12 | Family Planning | 11 |  | DHK-C9378 | 1 | 41466 | 49313.12 | 7847.12 | 60 |  | 470827.2 | 472965.3149 | Ramna |  |  |  | Family Planning | 472965.3149 | 459978.3897 | 12986.9252 | 2.8234 | OK
13 | Muktijuddho Montranalaya | 11 |  | DHK-C9376 | 1 | 26269.1 | 42919.82 | 16650.72 | 60 |  | 999043.2 | 1003580.0431 | Ramna |  |  |  | Muktijuddho Montranalaya | 1003580.0431 | 989924.3443 | 13655.6988 | 1.3795 | OK
14 | Purana Palton | 11 |  | DHK-C9318 | 1 | 43328.3 | 49147.44 | 5819.14 | 60 |  | 349148.4 | 350733.9486 | Ramna |  |  |  | Purana Palton | 350733.9486 | 318744.0733 | 31989.8753 | 10.0362 | OK
15 | Tip Top Feeder | 11 |  | DHK-C9318 | 1 | 66509.6 | 89567.58 | 23057.98 | 60 |  | 1383478.8 | 1389761.4375 | Kakrail |  |  |  | Tip Top Feeder | 1389761.4375 | 1427034.1549 | -37272.7173 | -2.6119 | OK
16 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 |  | DHKD3784 | 1 | 336257 | 341182 | 4925 | 1 |  | 4925 | 4947.3654 | Ramna |  |  |  | 11/0.4 kV Auxiliary Transformer, AT | 4947.3654 | 4696.0253 | 251.34 | 5.3522 | OK
10: Grand Total | 6048189 | 6020847.2 | 6048189 | 0.45412
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 4658427.5625
[5 empty] | Kakrail | at 33 KV level |  | 1389761.4375
[5 empty] | Total = |  |  | 6048189 | 0
1: 33 KV SIDE of___ DMCH 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DHAKA UNIVERSITY 33 kV SIDE
3 | DMC Circuit-1 | 33 | 0 | 2861 | 1 | 145.81 | 145.81 | 0 | 360000 | 0 | 0 | 0
10 | DMC Circuit-2 | 33 | 0 | 2803 | 1.03 | 288.56 | 300.04 | 11.48 | 360000 | 0 | 4256784 | 4272970.6888
10: Total | 0 | 4256784 | 4272970.6888
DHANMONDI 33 kV SIDE
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 391.38 | 405.5 | 14.12 | 240000 | 0 | 3388800 | 3390737.8809
10: Total |  | 3388800 | 3390737.8809
2: DMCH 33 KV SIDE (RECEIVING) |  |  | 7663708.5697
| 33 kV DU Incoming Circuit-1 | 33 |  | 00000072 | 1 | 73279888 | 73279888 | 0 | 1 |  | 0
| 33 kV Dhanmondi Incoming | 33 |  | 00000082 | 1 | 0 | 0 | 0 | 1 |  | 0
| 33 kV DU Incoming Circuit-2 | 33 |  | 00000081 | 1 | 0 | 0 | 0 | 1 |  | 0
10: Total |  | 0 | 0
DMCH 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
10: Total |  | 0
DMCH 33 KV SIDE
| 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | 00000069 | 1 | 122143200 | 125486880 | 3343680 | 1 |  | 3343680
2 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | 00000088 | 1 | 0 | 0 | 0 | 1 |  | 0
10: Total |  | 3343680
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: DHAKA UNIVERSITY 33 kV SIDE; 4: 4272970.6888; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7663708.5697
2: DHANMONDI 33 kV SIDE; 4: 3390737.8809; 6: 33 KV NET IMPORT; 9=8-7: 7663708.5697 | 33 KV TX HV SIDE |  | 7663708.5697
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7663708.5697
1: 11 KV SIDE of___DMCH 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
DMCH 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000056 | 1 | 120948056 | 124262264 | 3314208 | 1 | 3314208 |  | 3422044.2557
14 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000034 | 1 | 147954880 | 152062880 | 4108000 | 1 | 4108000 |  | 4241664.3139
7: 0; 8: 0; 10: Total | 7422208 |  | 7663708.5697
| DMCH 11 KV SIDE |  |  |  |  | 0 | 0
6 | Nearest O/H | 11 |  | 00000126 | 1 | 7074262 | 7294622 | 220360 | 1 |  | 220360 | 224820.1739 | Ramna |  |  |  | Nearest O/H | 224820.1739 | 210729.7741 | 14090.3998 | 6.6865 | OK
| Jagannath Hall | 11 |  | 00000002 | 1 | 2545753.8 | 2654153 | 108399.2 | 1 |  | 108399.2 | 110593.2428 | Ramna |  |  |  | Jagannath Hall | 110593.2428 | 113276.1711 | -2682.9282 | -2.3685 | OK
7 | Samsun Nahar Hall | 11 |  | 00000024 | 1 | 9054018 | 9370297 | 316279 | 1 |  | 316279 | 322680.6125 | Ramna |  |  |  | Samsun Nahar Hall | 322680.6125 | 293593.2672 | 29087.3453 | 9.9074 | OK
8 | Spare, 4L | 11 |  | 00000184 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 4L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | Board Office O/H, (5L) | 11 |  | 00000023 | 1 | 20726990 | 21315228 | 588238 | 1 |  | 588238 | 600144.1706 | Lalbag |  |  |  | Board Office O/H, (5L) | 600144.1706 | 492983.2953 | 107160.8752 | 21.7372 | OK
10 | OT- Complex | 11 |  | 00000167 | 1 | 5711026 | 6148345 | 437319 | 1 |  | 437319 | 446170.5101 | Ramna |  |  |  | OT- Complex | 446170.5101 | 427837.7768 | 18332.7333 | 4.285 | OK
11 | Alia Mdrasha O/H, (7L) | 11 |  | 00000148 | 1 | 9318217 | 9394377 | 76160 | 1 |  | 76160 | 77701.5086 | Lalbag |  |  |  | Alia Mdrasha O/H, (7L) | 77701.5086 | 75154.3226 | 2547.1861 | 3.3893 | OK
12 | Majed Sordar Road | 11 |  | 00000164 | 1 | 53489908 | 55060864 | 1570956 | 1 |  | 1570956 | 1602752.7729 | Bangshal |  |  |  | Majed Sordar Road | 1602752.7729 | 1759301.3409 | -156548.5681 | -8.8983 | OK
15 | Chankharpool, 9L | 11 |  | 00000001 | 1 | 45648168 | 46801764 | 1153596 | 1 |  | 1153596 | 1176945.2408 | Bangshal |  |  |  | Chankharpool, 9L | 1176945.2408 | 1201456.0712 | -24510.8303 | -2.0401 | OK
16 | Shahidullah College O/H, (10L) | 11 |  | 00000003 | 1 | 12584169 | 12842169 | 258000 | 1 |  | 258000 | 263222.0224 | Lalbag |  |  |  | Shahidullah College O/H, (10L) | 263222.0224 | 263967.4494 | -745.427 | -0.28239 | OK
17 | Ananda Bazar | 11 |  | 00000111 | 1 | 14714284 | 14878044 | 163760 | 1 |  | 163760 | 167074.5674 | Ramna |  |  |  | Ananda Bazar | 167074.5674 | 216784.0965 | -49709.5291 | -22.9304 | OK
18 | Hosseni Dalan O/H, (12L) | 11 |  |  | 1 | 23.41 | 50.74 | 27.33 | 60000 | Estimated | 1146913.2 | 1170127.1783 | Lalbag | Estimated from Grid SAS Data |  |  | Hosseni Dalan O/H, (12L) | 1170127.1783 | 1629339.2554 | -459212.0771 | -28.1839 | OK
19 | Badrun Nessa College | 11 |  | 00000006 | 1 | 19009274 | 19521592 | 512318 | 1 |  | 512318 | 522687.5196 | Lalbag |  |  |  | Badrun Nessa College | 522687.5196 | 511348.0734 | 11339.4462 | 2.2176 | OK
20 | Dhaka Medical College, Unit-II | 11 |  | 00000125 | 1 | 11353372 | 11679371 | 325999 | 1 |  | 325999 | 332597.3491 | Ramna |  |  |  | Dhaka Medical College, Unit-II | 332597.3491 | 314783.3957 | 17813.9534 | 5.6591 | OK
21 | Spare, 15L | 11 |  | 00000163 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | Spare, 15L | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Sheikh Hasina National Burn Institute | 11 |  | 00000127 | 1 | 19677112 | 20301830 | 624718 | 1 |  | 624718 | 637362.5402 | Ramna |  |  |  | Sheikh Hasina National Burn Institute | 637362.5402 | 594088.462 | 43274.0783 | 7.2841 | OK
23 | Aux. Transformer, AT-1 | 0.415 |  | DHKF-7804 | 1 | 2551.19 | 2637.73 | 86.54 | 100 |  | 8654 | 8829.1604 | Ramna |  |  |  | Aux. Transformer, AT-1 | 8829.1604 | 8254.0596 | 575.1008 | 6.9675 | OK
24 | Aux. Transformer, AT-2 | 0.415 |  | DHKF-7802 | 1 | 0 | 0 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 7663708.5697 | 7511669.4 | 7663708.5697 | 2.024
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 2250128.1564
[5 empty] | Lalbag | at 33 KV level |  | 2633882.3995
[5 empty] | Bangshal | at 33 KV level |  | 2779698.0137
[5 empty] | Total = |  |  | 7663708.5697 | 0
1: 33 KV SIDE of___ BB AVENEU 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
0 | BB Avenue-1 | 33 | 0 | 2804 | 1.5 | 139.96 | 147.58 | 7.62 | 360000 | 0 | 4114800 | 4130446.7857
11 | BB Avenue-2 | 33 |  | 2820 | 1 | 180.09 | 184 | 3.91 | 360000 | 0 | 1407600 | 1412952.4875
10: Total | 0 | 5522400 | 5543399.2732
BB AVENEU 33 KV SIDE (RECEIVING)
| 33 kV Dhaka University-1 | 33 |  | BD 017078 | 1 | 0 | 0 | 0 | 1125 |  | 0
| 33 kV Dhaka University-2 | 33 |  | BD 017090 | 1 | 64705.72 | 66181.63 | 1475.91 | 1125 |  | 1660398.75
7: 0; 8: 0; 10: Total | 0 | 1660398.75 | 0
| BB AVENEU 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| BB AVENEU 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV, 28/35 MVA T-1 (HV) | 33 |  | BD 017093 | 1 | 87852.83 | 91945.85 | 4093.02 | 1000 |  | 4093020
3 | 33/11 kV, 28/35 MVA T-2 (HV) | 33 |  | BD 017094 | 1 | 50094.48 | 51573.85 | 1479.37 | 1000 |  | 1479370
10: Total |  | 5572390
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV SIDE; 4: 5543399.2732; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | BB AVENEU 33 KV NET IMPORT |  | 5543399.2732
6: BB AVENEU 33 KV NET IMPORT; 9=8-7: 5543399.2732 | 33 KV TX HV SIDE |  | 5572390
[10 empty] | LOSS UNITS=> |  | -28990.7268
[10 empty] | LOSS % IN => |  | -0.523%
| TOTAL IMPORT |  | 5543399.2732
1: 11 KV SIDE of___BB AVENEU 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
BB AVENEU 11 KV SIDE
13 | 33/11 kV, 28/35 MVA T-1 (LV) Incoming | 11 |  | BD 014052 | 1 | 88103.06 | 92175.35 | 4072.29 | 1000 | 4072290 |  | 4079000.236
14 | 33/11 kV, 28/35 MVA T-2 (LV) Incoming | 11 |  | BD 014055 | 1 | 49590.96 | 51052.95 | 1461.99 | 1000 | 1461990 |  | 1464399.0372
7: 0; 8: 0; 10: Total | 5534280 |  | 5543399.2732
| BB AVENEU 11 KV SIDE |  |  |  |  | 0 | 0
6 | Secratariet East | 11 |  | BD 013966 | 1 | 3406.54 | 3666.02 | 259.48 | 1000 |  | 259480 | 260076.7434 | Ramna |  |  |  | Secratariet East | 260076.7434 | 245293.0009 | 14783.7425 | 6.027 | OK
| Taher Bag O/H | 11 |  | BD 014045 | 1 | 17659.83 | 18336.98 | 677.15 | 1000 |  | 677150 | 678707.287 | Narinda |  |  |  | Taher Bag O/H | 678707.287 | 744464.9674 | -65757.6804 | -8.8329 | OK
7 | Al Raji Complex | 11 |  | BD 013983 | 1 | 12982.02 | 13753.92 | 771.9 | 1000 |  | 771900 | 773675.1898 | Ramna |  |  |  | Al Raji Complex | 773675.1898 | 784809.8778 | -11134.688 | -1.4188 | OK
8 | Raduni | 11 |  | BD 013999 | 1 | 26506.32 | 27128.05 | 621.73 | 1000 |  | 621730 | 623159.8339 | Ramna |  |  |  | Raduni | 623159.8339 | 1293358.488 | -670198.6541 | -51.8185 | CHECK
9 | Sundor Bon Square O/H | 11 |  | BD 013954 | 1 | 12263.75 | 12696.85 | 433.1 | 1000 |  | 433100 | 434096.0289 | Narinda |  |  |  | Sundor Bon Square O/H | 434096.0289 | 473931.0551 | -39835.0262 | -8.4052 | OK
10 | Shromo Bhobon O/H | 11 |  | BD 013985 | 1 | 12112.38 | 12636.31 | 523.93 | 1000 |  | 523930 | 525134.9167 | Ramna |  |  |  | Shromo Bhobon O/H | 525134.9167 | 505142.6077 | 19992.309 | 3.9578 | OK
11 | Nawabpur Road | 11 |  | BD 013953 | 1 | 18556.72 | 19355.25 | 798.53 | 1000 |  | 798530 | 800366.4326 | Narinda |  |  |  | Nawabpur Road | 800366.4326 | 843066.7121 | -42700.2795 | -5.0649 | OK
12 | Spair | 11 |  | BD 013991 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spair | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Spare | 11 |  | BD 013942 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Ahad Police Box | 11 |  | BD 013984 | 1 | 10306.68 | 10672.48 | 365.8 | 1000 |  | 365800 | 366641.2546 | Ramna |  |  |  | Ahad Police Box | 366641.2546 | 470281.7667 | -103640.5121 | -22.038 | OK
17 | Nearest O/H | 11 |  | BD 013997 | 1 | 2390.76 | 2505.26 | 114.5 | 1000 |  | 114500 | 114763.3233 | Ramna |  |  |  | Nearest O/H | 114763.3233 | 117912.5625 | -3149.2392 | -2.6708 | OK
18 | Natab Bhaban | 11 |  | BD 014000 | 1 | 4625.24 | 4804.84 | 179.6 | 1000 |  | 179600 | 180013.0381 | Ramna |  |  |  | Natab Bhaban | 180013.0381 | 185708.2311 | -5695.193 | -3.0667 | OK
19 | Spare | 11 |  | BD 014043 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | Awami League Party Office | 11 |  | BD 013956 | 1 | 1404.54 | 1408.1 | 3.56 | 1000 |  | 3560 | 3568.1872 | Ramna |  |  |  | Awami League Party Office | 3568.1872 | 9417.1914 | -5849.0042 | -62.1099 | CHECK
21 | Khaddar Bazar | 11 |  | BD 014012 | 1 | 9317.61 | 9709.64 | 392.03 | 1000 |  | 392030 | 392931.5775 | Ramna |  |  |  | Khaddar Bazar | 392931.5775 | 394275.1992 | -1343.6217 | -0.34078 | OK
22 | Bangobondu National Stidium | 11 |  | BD 014008 | 1 | 6146.93 | 6536.3 | 389.37 | 1000 |  | 389370 | 390265.4601 | Ramna |  |  |  | Bangobondu National Stidium | 390265.4601 | 288658.7112 | 101606.7489 | 35.1996 | OK
23 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 |  | DHKH4418 | 1 | 1124.63 | 1124.63 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 |  | DHKH4413 | 1 | 41.9 | 41.9 | 0 | 100 |  | 0 | 0 | Ramna |  |  |  | 11/0.4 kV Aux. Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 5543399.2732 | 5530680 | 5543399.2732 | 0.22998
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Ramna | at 33 KV level |  | 3630229.5247
[5 empty] | Narinda | at 33 KV level |  | 1913169.7485
[5 empty] | Total = |  |  | 5543399.2732 | 0
1: 33 KV SIDE of___ KALLYANPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
| 0 | 0 | IMPORT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10: Total |  | 0 | 0 | #DIV/0!
KALLYANPUR 33 KV SIDE (RECEIVING)
33
33
33
10: Total |  | 0 | #REF!
KALLYANPUR 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
KALLYANPUR 33 KV SIDE
| 33/11 kV, 20/28 MVA T3 | 33 |  | 8993831 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T4 | 33 |  | 8993839 | 1 |  |  | 0 | 180000 |  | 0
1 | 33/11 kV, 20/28 MVA T5 | 33 |  | 8993835 | 1 |  |  | 0 | 180000 |  | 0
10: Total |  | 0 | 0 | #DIV/0!
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV SIDE; 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 0
6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 0 | KALLYANPUR 11 KV NET IMPORT |  | 0
6: TOTAL EXPORT; 9=8-7: 0 | LOSS UNITS=> |  | 0
6: 132KV NET LOSS =>; 9=8-7: #DIV/0! | LOSS % IN => |  | #DIV/0!
| TOTAL IMPORT |  | 0
1: 11 KV SIDE of___KALLYANPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
KALLYANPUR 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | DHK15942 | 1 | 3471.51 | 3471.51 | 0 | 160000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | DHK15943 | 1 | 5997.96 | 5997.96 | 0 | 160000 | 0
16 | 33/11 kV, 10/14 MVA T5 Incoming | 11 |  | 74819926 | 1 | 0 | 0 | 0
7: 0; 8: 0; 10: Total | 0 |  | 0
| KALLYANPUR 11 KV SIDE |  |  |  |  | 0 | 0
A | From Kallyanpur S/S. |  |  |  |  | 0 | 0
| 11 KV Gano Bhavan RMU | 11 |  | DHK14997 | 1 | 995.71 | 995.74 | 0.03 | 40000 |  | 1200 | 1230 | Shere b.nagar |  |  |  | 11 KV Gano Bhavan RMU | 1230 | 1230 | -4.6612e-09 | -3.7896e-10 | OK
| 11 KV Beribandh Feeder. | 11 |  | DHK14960 | 1 | 9640.43 | 9646.16 | 5.73 | 40000 |  | 229200 | 234930 | Adabor |  |  |  | 11 KV Beribandh Feeder. | 234930 | 301350 | -66420 | -22.0408 | OK
| 11 KV Adabor O/H | 11 |  | DHK14957 | 1 | 4371.7 | 4419.91 | 48.21 | 40000 |  | 1928400 | 1976610 | Adabor |  |  |  | 11 KV Adabor O/H | 1976610 | 2150040 | -173430 | -8.0664 | OK
| 11 KV Mansurabad | 11 |  | 77816681 | 1 | 51616.27 | 51898.42 | 282.15 | 8000 |  | 2257200 | 2313630 | Adabor |  |  |  | 11 KV Mansurabad | 2313630 | 2379804 | -66174 | -2.7806 | OK
| 11 KV Ring Road Feeder | 11 |  | 77816675 | 1 | 41775.56 | 41923.11 | 147.55 | 8000 |  | 1180400 | 1209910 | Adabor |  |  |  | 11 KV Ring Road Feeder | 1209910 | 1172682 | 37228 | 3.1746 | OK
| 11 KV Sewarage Pump | 11 |  | DHK14959 | 1 | 2054.75 | 2112.81 | 58.06 | 40000 |  | 2322400 | 2380460 | Adabor |  |  |  | 11 KV Sewarage Pump | 2380460 | 2601450 | -220990 | -8.4949 | OK
| 11 KV Technical School (DPDC) | 11 |  | DHK15019 | 1 | 8133.47 | 8192.03 | 58.56 | 40000 |  | 2342400 | 2400960 | Adabor |  |  |  | 11 KV Technical School (DPDC) | 2400960 | 2347660 | 53300 | 2.2703 | OK
| 11 KV Goidertek (DPDC) | 11 |  | DHK14996 | 1 | 9355.62 | 9369.92 | 14.3 | 40000 |  | 572000 | 586300 | Adabor |  |  |  | 11 KV Goidertek (DPDC) | 586300 | 591220 | -4920 | -0.83218 | OK
1: B; 2: From Agargaon S/S.; 3: 11 |  |  | 0
| 11 KV P.C Culture Housing | 11 |  | DHK-15019 | 1 | 5335.08 | 5335.08 | 0 | 40000 |  | 0 | 0
| 11 KV Shyamoli O/H | 11 |  | DHK-15026 | 1 | 9164.92 | 9179.18 | 14.26 | 40000 |  | 570400 | 584660 | Shere b.nagar
| 11 KV Nearest RMU | 11 |  | DHK-15027 | 1 | 3859.52 | 3863.97 | 4.45 | 40000 |  | 178000 | 182450 | Shere b.nagar
| 11 KV Sher-e-bangla Nagar | 11 |  | DHK-15025 | 1 | 3976.15 | 3977.36 | 1.21 | 40000 |  | 48400 | 49610 | Shere b.nagar
| 11 KV BCFCC Feeder. | 11 |  | DHK-15024 | 1 | 1038.1 | 1038.1 | 0 | 40000 |  | 0 | 0
| 11 KV NEC Feeder. | 11 |  | DHK-15023 | 1 | 431.56 | 431.56 | 0 | 40000 |  | 0 | 0
| 11 KV Manik Mia Feeder. | 11 |  | DHK27341 | 1 | 175.92 | 175.92 | 0 | 40000 |  | 0 | 0
7: Export To Desco; 9=8-7: 0; 10: Grand Total | 0 | 11630000 | 11920750 | 2.5
DESCO | 11 kV Tolarbugh | 11 |  | DHK27326 | 1 | 3273684 | 3273684 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Tolarbugh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV South Bisil | 11 |  | DHK15017 | 1 | 1073.15 | 1073.15 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV South Bisil | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Lalkhuthy | 11 |  | DHK15018 | 1 | 965.04 | 965.04 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Lalkhuthy | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Baghbari | 11 |  | DHK14956 | 1 | 9329.11 | 9329.11 | 0 | 40000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Baghbari | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara O/H | 11 |  | 74819924 | 1 | 3311 | 3311 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara O/H | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Kallyanpur | 11 |  | DHK27331 | 1 | 5017044 | 5017044 | 0 | 40 |  | 0 | 0 | DESCO |  |  |  | 11 kV Kallyanpur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 11 kV Paikpara Sw/S | 11 |  | 74819925 | 1 | 9865.733 | 9865.733 | 0 | 8000 |  | 0 | 0 | DESCO |  |  |  | 11 kV Paikpara Sw/S | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 0 | 0 | 0 | #DIV/0!
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Adabor | at 33 KV level |  | 11102800
[5 empty] | Shere b.nagar | at 33 KV level |  | 817950
[5 empty] | Satmasjid | at 33 KV level
[5 empty] | DESCO | at 33 KV level |  | 0
[5 empty] | Total = |  |  | 11920750 | 0
1: 33 KV SIDE of___ Kamrangirchar-2 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
33 KV SIDE
18 | Kamrangir Char-2 | 33 | 0 | 30799147 | 1 | 1491.72 | 1516.92 | 25.2 | 240000 | 0 | 6048000 | 6050909.9939
10: Total | 0 |  | 6050909.9939
Kamrangirchar-2 33 KV SIDE (RECEIVING)
33
10: Total | 0
Kamrangirchar-2 33 KV SIDE (EXPORT TO OTHER S/S)
2: Kamrangirchar Incoming; 3: 33; 4: EXPORT; 9=8-7: 0; 10: 240000 |  | 0
2: Lalbagh Incoming; 3: 33; 9=8-7: 0; 10: 240000 |  | 0
10: Total |  | 0
Kamrangirchar-2 33 KV SIDE
| Transformer-01 | 33 |  | BD017102 | 1 | 1393.51 | 1393.51 | 0 | 180000 |  | 0
1 | Transformer-02 | 33 |  | BD017105 | 1 | 1891.29 | 1891.29 | 0 | 180000 |  | 0
10: Total |  | 0 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV SIDE; 4: 6050909.9939; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | KALLYANPUR 33 KV NET IMPORT |  | 6050909.9939
2: IMPORT-2; 6: KALLYANPUR 33 KV NET IMPORT; 9=8-7: 6050909.9939 | KALLYANPUR 11 KV NET IMPORT |  | 6050909.9939
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6050909.9939
1: 11 KV SIDE of___Kamrangirchar-2 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
Kamrangirchar-2 11 KV SIDE
8 | 33/11 kV, 20/28 MVA T3 Incoming | 11 |  | 6604390 | 1 | 49400.1 | 49400.1 | 0 | 80000 | 0
9 | 33/11 kV, 20/28 MVA T4 Incoming | 11 |  | 6604450 | 1 | 336611 | 336611 | 0 | 80000 | 0
10: Total | 0 |  | 6050909.9939
Kamrangirchar-2 11 KV SIDE
1 | Nizambag | 11 |  | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1094695.56 | 1095738.2283 | Kamrangirchar | 90 |  |  | Nizambag | 1095738.2283 | 1008260.1492 | 87478.0791 | 8.6761 | OK
2 | Merry Stopes | 11 |  | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 364898.52 | 365246.0761 | Kamrangirchar | 30 |  |  | Merry Stopes | 365246.0761 | 355856.5232 | 9389.5529 | 2.6386 | OK
3 | Mujibur Ghat | 11 |  | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1216328.4 | 1217486.9203 | Kamrangirchar | 100 |  |  | Mujibur Ghat | 1217486.9203 | 1304807.2519 | -87320.3316 | -6.6922 | OK
4 | Madrasa | 11 |  | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1423104.228 | 1424459.6968 | Kamrangirchar | 117 |  |  | Madrasa | 1424459.6968 | 1542044.934 | -117585.2373 | -7.6253 | OK
5 | Thana | 11 |  | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1217486.9203 | Kamrangirchar | 100 |  |  | Thana | 1217486.9203 | 1423426.093 | -205939.1726 | -14.4679 | OK
6 | Al-Hera | 11 |  | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 |  | 0 | 0 | Kamrangirchar |  |  |  | Al-Hera | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Waz Uddin School | 11 |  | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 729797.04 | 730492.1522 | Kamrangirchar | 60 |  |  | Waz Uddin School | 730492.1522 | 830331.8876 | -99839.7354 | -12.0241 | OK
8 | 11/0.4 kV Auxiliary Transformer | 11 |  | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 |  | 0 | 0 | Kamrangirchar |  |  |  | 11/0.4 kV Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2: NB: Nizambag, Merry stopes, Mujibor Ghat Energy Meter Are Display Off; 10: Grand Total | 6050909.9939 | 6045152.148 | 6050909.9939 | 0.095247
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kamrangirchar | at 33 KV level |  | 6050909.9939
[5 empty] | Total = |  |  | 6050909.9939 | 0
Note on F941: User: Grid CF=1.5

## NORTH-2
Maghbazar 132/33/11 KV 3 x 50/75 MVA Substation. Grid North 2, Phone No. 028170002, 02-48119031
132 KV SIDE of___ MOGBAZAR 132/33/11 KV S/S | [13 empty] | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
| 132 KV Mogbazar-2 CKT (IMP) | 132 | IMPORT | 8993631 | 1 | 5756.396 | 5799.375 | 42.979 | 960000 | 0 | 41259840
| 132 KV Mogbazar-2 CKT(EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
| 132 KV Mogbazar-1 CKT (IMP) | 132 |  | 8993659 | 1 | 4914.803 | 4947.971 | 33.168 | 960000 | 0 | 31841280
| 132 KV Mogbazar-1 CKT(EXP) | 132 |  |  | 1 | 0.084 | 0.084 | 0 | 960000 | 0 | 0
9=8-7: Total Import/Export | 0 | 73101120
10: Net Total | 73101120
MOGBAZAR 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE | 6604452 | 1 | 9248.01 | 9305.1 | 57.09 | 720000 | 41104800
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  | 6604428 | 1 | 5533.5 | 5577.9 | 44.4 | 720000 | 31968000
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 720000 |  | 0
9=8-7: Total Import/Export | 73072800 | 0
9=8-7: Net Total | 73072800 | 0
MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 132; 4: EXPORT |  | 0 |  |  | future Scope
2: Feeder No.2; 3: 132 |  | 0
10: Total |  | 0
MOGBAZAR 132 KV SIDE
2: 132/33 KV GT-1; 3: 132; 4: NET IMPORT |  | 0 |  |  | No meter
2: 132/33 KV GT-2; 3: 132 |  | 0
2: 132/33 KV GT-3; 3: 132 |  | 0
10: Total |  | 73072800
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: RAMPURA 132 KV SIDE (TARIFF POINT); 4: 73101120; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 73101120
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 73101120 | MOGBAZAR 33 KV NET IMPORT |  | 72772800
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 328320
2: IMPORT-4 | LOSS % IN => |  | 0.4491%
| 132 KV TOTAL IMPORT |  | 73101120
1: 33 KV SIDE of___MOGBAZAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
| 132/33 KV GT-1 Incomming | 33 | IMPORT | 76026303 | 1 | 9864.79 | 9915.9 | 51.11 | 480000 | 24532800 |  | 24643481.5856
| 132/33 KV GT-2 Incomming | 33 |  | 76026307 | 1 | 9859.88 | 9911 | 51.12 | 480000 | 24537600 |  | 24648303.2412
| 132/33 KV GT-3 Incomming | 33 |  |  | 1 | 8069.92 | 8119.3 | 49.38 | 480000 | 23702400 |  | 23809335.1731
7: 0; 8: 0; 10: Total | 72772800 |  | 73101120
| MOGBAZAR 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33/11 KV Transformer No.1. | 33 |  | 6604465 | 1 | 6959.93 | 6975.8 | 15.87 | 180000 |  | 2856600 | 2875900.9036 |  | 20463233.9763 | MOGBAZAR 33/11 KV SS | 6.4535 | 33/11 KV Transformer No.1. | 2875900.9036 | 3899553.3751 | -1023652.4714 | -26.2505 | OK
| 33/11 KV Transformer No.2. | 33 |  | 202006985 | 1 | 35656606639 | 35658246233 | 1639594 | 3 | T2 Incomer side | 4974900 | 5008513.4094 |  |  |  |  | 33/11 KV Transformer No.2. | 5008513.4094 | 3704395.8376 | 1304117.5718 | 35.2046 | OK
| 33/11 KV Transformer No.3. | 33 |  | 6604338 | 1 | 7011.3 | 7041.7 | 30.4 | 180000 |  | 5472000 | 5508972.1153 |  |  |  |  | 33/11 KV Transformer No.3. | 5508972.1153 | 5475203.1705 | 33768.9448 | 0.61676 | OK
| 33/11 KV Transformer No.4 | 33 |  |  | 1 | 1034346 | 1030741 | -3605 | 180000 | T4 Incomer side | 7022400 | 7069847.548 |  |  |  |  | 33/11 KV Transformer No.4 | 7069847.548 | 7129195.7767 | -59348.2287 | -0.83247 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 20325900 | 20463233.9763 |  |  |  |  | 33 KV Feeders | 20463233.9763 | 20208348.1599 | 254885.8164 | 1.2613 | OK
8 | 33 kV Tejgaon U/G Feeder-1 | 33 |  | 76026300 | 1 | 6695.56 | 6718.6 | 23.04 | 360000 |  | 8294400 | 8350441.9432 |  | 22916599.1349 | Tejgoan 33/11 kv ss | 1.1843 | 33 kV Tejgaon U/G Feeder-1 | 8350441.9432 | 7943001.7086 | 407440.2346 | 5.1295 | OK
9 | 33 kV Tejgaon U/G Feeder-2 | 33 |  | 06604453 | 1 | 6474.31 | 6514.5 | 40.19 | 360000 |  | 14468400 | 14566157.1917 |  |  |  |  | 33 kV Tejgaon U/G Feeder-2 | 14566157.1917 | 13864279.2504 | 701877.9413 | 5.0625 | OK
10 | Bashundhara City | 33 |  | 660434 | 1 | 753.18 | 765.8 | 12.62 | 180000 |  | 2271600 | 2286948.2926 | Shere b.nagar | 6206654.4391 | Ispahani 33/11 kv ss | 1.2312 | Bashundhara City | 2286948.2926 | 2480389.347 | -193441.0544 | -7.7988 | OK
11 | Ispahani-1 | 33 |  |  | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0 |  |  |  |  | Ispahani-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | Ispahani-2 | 33 |  |  | 1 | 3824.35 | 3858.6 | 34.25 | 180000 |  | 6165000 | 6206654.4391 |  | 9269973.1514 | Green Road Dormatory 33/11 kv ss | 0.73671 | Ispahani-2 | 6206654.4391 | 5987828.9601 | 218825.479 | 3.6545 | OK
13 | 33 kV Green Road Dormitory | 33 |  | 76026305 | 1 | 8019.59 | 8045.2 | 25.61 | 180000 | Reading From G. Dormitory Side | 9207760 | 9269973.1514 |  |  |  |  | 33 kV Green Road Dormitory | 9269973.1514 | 9535149.4608 | -265176.3094 | -2.781 | OK
14 | 33 KV T&T-1 | 33 |  | 6604337 | 1 | 4533.36 | 4566.5 | 33.14 | 180000 |  | 5965200 | 6005504.4704 |  | 11612333.3273 | T&T 33/11 kv ss | -0.1882 | 33 KV T&T-1 | 6005504.4704 | 5825947.1318 | 179557.3386 | 3.082 | OK
13 | 33 KV T&T-2 | 33 |  | 6604336 | 1 | 5624.56 | 5655.5 | 30.94 | 180000 |  | 5569200 | 5606828.8568 |  |  |  |  | 33 KV T&T-2 | 5606828.8568 | 5414047.8132 | 192781.0437 | 3.5608 | OK
14 | 33KV Karwan Bazar | 33 |  | 74605366~4 | 1 | 1189.08 | 1189.08 | 0 | 180000 |  | 0 | 0 |  | 0 | Kawranbazar 33/11 kv ss | 0.49247 | 33KV Karwan Bazar | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | AT-1 | 33 |  | 6603338 | 1 | 1749.21 | 1961 | 211.79 | 80 |  | 16943.2 | 17057.6784 |  |  |  |  | AT-1 | 17057.6784 | 16208.1682 | 849.5102 | 5.2412 | OK
20 | AT-2 | 33 |  | 6603849 | 1 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 51958503.2 | 52309566.0237 |  |  |  |  | 0 | 52309566.0237 | 51066851.8401 | 1242714.1836 | 2.4335 | OK
9=8-7: Grand Total | 72772800 | 72284403.2 | 72772800 | 0.67566
-0.3377
7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[6 empty] | NOCS Sherebanglanagor at 33 KV level |  |  | 2286948.2926
9=8-7: Total =; 10: 2286948.2926 | 0 | [17 empty] | 1.4463
1: 11 KV SIDE of___MOGBAZAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 11 KV SIDE
1 | 33/11 kV Transformer-1 | 11 | Import | 6604457 | 1 | 532514.4 | 535345 | 2830.6 | 1000 | 2830600 |  | 2858599.5071
2 | 33/11 kV Transformer-2 | 11 | Import | 30/11009-1101 | 1 | 575362.3 | 580337.2 | 4974.9 | 1000 | 4974900 |  | 5024110.3258
3 | 33/11 kV Transformer-3 | 11 | Import | 6604454 | 1 | 569593.9 | 575028.8 | 5434.9 | 1000 | 5434900 |  | 5488660.5177
4 | 33/11 kV Transformer-4 | 11 | Import |  | 1 | 964.5 | 1008.39 | 43.89 | 160000 | 7022400 |  | 7091863.6257
7: 0; 8: 0; 10: Total | 20262800 |  | 20463233.9763
| MOGBAZAR 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40404.3 | 40464.9 | 60.6 | 1000 |  | 60600 | 65016.8533 | Moghbazar |  |  |  | 11 kV Doctor's Lane | 65016.8533 | 1691.4448 | 63325.4085 | 3743.8649 | FAULT
2 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 80555.5 | 80645.6 | 90.1 | 1000 |  | 90100 | 96666.9717 | Tejgaon |  |  |  | 11 kV T&T O/H Feeder | 96666.9717 | 802696.2793 | -706029.3075 | -87.9572 | CHECK
3 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 |  | 0 | 0 | Tejgaon |  |  |  | 11 kV Acore Ice Feeder (TEJ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 119107.7 | 119512.5 | 404.8 | 1000 |  | 404800 | 434303.9973 | Tejgaon |  |  |  | 11 kV Tejgaon S/S-1 | 434303.9973 | 326660.2796 | 107643.7177 | 32.9528 | OK
7 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 122850.8 | 125254.8 | 2404 | 1000 |  | 2404000 | 2579216.4264 | Moghbazar |  |  |  | 11KV Ambagan | 2579216.4264 | 2455343.5773 | 123872.8492 | 5.045 | OK
[6 empty] | 0 | 0
5 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11 kV Madhubagh | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 142744.5 | 144229.5 | 1485 | 1000 |  | 1485000 | 1593234.7726 | Tejgaon |  |  |  | 11 kV Moghbazar Nearest | 1593234.7726 | 1205154.4296 | 388080.343 | 32.2017 | OK
3 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9488.7 | 9654.6 | 165.9 | 1000 |  | 165900 | 177991.6827 | Tejgaon |  |  |  | 11 kV MP Suite Feeder | 177991.6827 | 170095.919 | 7895.7636 | 4.6419 | OK
4 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 120465.9 | 122581.3 | 2115.4 | 1000 |  | 2115400 | 2269581.709 | Kakrail |  |  |  | 11 kV Bangla Motor | 2269581.709 | 2138303.3901 | 131278.319 | 6.1394 | OK
1 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 172255.3 | 173266.6 | 1011.3 | 1000 |  | 1011300 | 1085008.9734 | Tejgaon |  |  |  | 11 kV Kunipara Feeder | 1085008.9734 | 952812.0065 | 132196.9669 | 13.8744 | OK
[6 empty] | 0 | 0
6 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 117632.1 | 119411.5 | 1779.4 | 1000 |  | 1779400 | 1909092.2251 | Kakrail |  |  |  | 11 kV Iskaton | 1909092.2251 | 1919578.4326 | -10486.2075 | -0.54628 | OK
5 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 82976.9 | 84471.2 | 1494.3 | 1000 |  | 1494300 | 1603212.6065 | Tejgaon |  |  |  | 11 kV Ispahani Feeder | 1603212.6065 | 1595983.8968 | 7228.7097 | 0.45293 | OK
2 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 122785.5 | 123156.6 | 371.1 | 1000 |  | 371100 | 398147.7603 | Moghbazar |  |  |  | 11 kV Nayatola Feeder | 398147.7603 | 399920.9831 | -1773.2227 | -0.44339 | OK
3 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 112406.9 | 113333.9 | 927 | 1000 |  | 927000 | 994564.7368 | Kakrail |  |  |  | 11 kV Garden Feeder (KAK) | 994564.7368 | 950591.9851 | 43972.7517 | 4.6258 | OK
4 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43325.7 | 0 | 1000 |  | 0 | 0 | Kakrail |  |  |  | 11 kV BSRS Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8423.8 | 8577.9 | 154.1 | 1000 |  | 154100 | 165331.6353 | Tejgaon |  |  |  | 11 kV Vumi Bhaban | 165331.6353 | 136267.0228 | 29064.6125 | 21.3292 | OK
5 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 |  | 0 | 0 | Moghbazar |  |  |  | 11kV Moghbazar(old.buil) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0 | 13371370.3506 | 12463000 | 13371370.3506 | 7.2885 |  |  |  |  | 13371370.3506 | 13055099.6465
1 | 11 kV TCB Feeder | 11 | T-4 |  | 1 | 34661.4 | 35701.5 | 1040.1 | 1000 |  | 1040100 | 1091208.9552 | Kakrail |  |  |  | 11 kV TCB Feeder | 1091208.9552 | 1058026.2525 | 33182.7028 | 3.1363 | OK
2 | 11 kV Tejgaon SS-2 | 11 | T-4 |  | 1 | 28639.4 | 30139.8 | 1500.4 | 1000 |  | 1500400 | 1574127.4074 | Tejgaon |  |  |  | 11 kV Tejgaon SS-2 | 1574127.4074 | 1532552.8114 | 41574.596 | 2.7128 | OK
3 | Holy Day Inn | 11 | T-4 |  | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 517320 | 542740.3295 | Tejgaon |  |  |  | Holy Day Inn | 542740.3295 | 522630.1141 | 20110.2154 | 3.8479 | OK
4 | Polly Bhabon-2 | 11 | T-4 |  | 1 | 18322 | 18361.1 | 39.1 | 1000 | Consumer meter damaged, 12 months average | 26592 | 27898.691 | Kakrail |  |  |  | Polly Bhabon-2 | 27898.691 | 30058.9479 | -2160.2568 | -7.1867 | OK
5 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 |  | 1 | 13294.2 | 15062.1 | 1767.9 | 1000 |  | 1767900 | 1854771.9565 | Kakrail |  |  |  | Polly Bhabon-1 / ambarsaha mosjid | 1854771.9565 | 1842884.7823 | 11887.1742 | 0.64503 | OK
6 | 11 kV Tejturibazar | 11 | T-4 |  | 1 | 129914.1 | 130665.9 | 751.8 | 1000 |  | 751800 | 788742.3253 | Kakrail |  |  |  | 11 kV Tejturibazar | 788742.3253 | 776669.7972 | 12072.5281 | 1.5544 | OK
7 | Songsad | 11 | T-4 |  | 1 | 2467.7 | 2920.7 | 453 | 1000 |  | 453000 | 475259.7411 | Shere b.nagar |  |  |  | Songsad | 475259.7411 | 544550.7215 | -69290.9804 | -12.7244 | OK
| Chennel 24 | 11 | T-4 |  | 1 | 7308.75 | 7312.34 | 3.59 | 1000 |  | 3590 | 3766.4072 | Moghbazar |  |  |  | Chennel 24 | 3766.4072 | 1700.7368 | 2065.6704 | 121.4574 | FAULT
8 | Sonargaon | 11 | T-4 |  | 1 | 38919 | 39618 | 699 | 1000 |  | 699000 | 733347.8124 | Kakrail |  |  |  | Sonargaon | 733347.8124 | 844174.3497 | -110826.5373 | -13.1284 | OK
| AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 |  |  | 0 | Moghbazar |  |  |  | AT -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 |  | 0 | 0 | Moghbazar |  |  |  | AT -2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
[10 empty] | 7091863.6257 | 6759702 | 7091863.6257 | 4.9139
10: Total | 20463233.9763 | 19222702 | 20463233.9763 | 6.4535
6: NOCS Wise 11 KV EXPORT; 9=8-7: KWH | [13 empty] | AMR Meter Information
6: Moghbazar; 7: at 33 KV level; 9=8-7: 3046147.4474 | [13 empty] | NOCS | Fedder Name | Customer No. | Consumption | OMF
6: Tejgaon; 7: at 33 KV level; 9=8-7: 7022618.3764 | Export to Kakrail |  | 250000 | [10 empty] | Tejgaon | 11 KV Holiday Inn | 37073921 | 59820 | 3000
6: Kakrail; 7: at 33 KV level; 9=8-7: 9919208.4115 | Import from Tejgaon |  | 250000 | [10 empty] | Tejgaon | 11 KV Holiday Inn | 37086001 | 457500 | 3000
6: Shere b.nagar; 7: at 33 KV level; 9=8-7: 475259.7411 | [13 empty] | Kakrail | 11 KV Polly Bhaban | 16370811 | 26592 | 300
[5 empty] | Total = |  |  | 20463233.9763 | 0
AMR Meter Information
[23 empty] | Customer Name | Previous Off-Peak | Present Off-Peak | Previous Peak | Present Peak
[23 empty] | Shah Garments | 751.49 | 771.43 | 206.17 | 206.17
[23 empty] | Habib Hotel | 2416.56 | 2528.57 | 789.46 | 829.95
[23 empty] | The Joint Director BRDB | 1083.78 | 1161.08 | 220.81 | 232.15
MOGBAZAR T&T 33/11 KV, 2X10/14 MVA SUBSTATION (NORTH) 222222016
1: 33 KV SIDE of___ Mogbazar T&T 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
14 | 33 KV T&T-1 | 33 | 0 | 6604337 | 1 | 4533.36 | 4566.5 | 33.14 | 180000 | 0 | 5965200 | 6005504.4704
13 | 33 KV T&T-2 | 33 | 0 | 6604336 | 1 | 5624.56 | 5655.5 | 30.94 | 180000 | 0 | 5569200 | 5606828.8568
0 | Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 | 0 | 0 | 0
10: Total | 0 | 11534400 | 11612333.3273
Mogbazar T&T 33 KV SIDE (RECEIVING)
1 | 33 kV Moghbazar-1 Feeder | 33 | Import | DHK60891 | 1 | 966779 | 977836 | 11057 | 360 | 3980520
2 | 33 kV Moghbazar-2 Feeder | 33 | Import | DHK68131 | 1 | 877078 | 888130 | 11052 | 360 | 3978720
| 33 kV Ullon Feeder | 33 | Import | DHK68132 | 1 | 349.75 | 349.75 | 0 | 180000 | 0
7: 0; 8: 0; 10: Total | 7959240 | 0 | 0
| Mogbazar T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| Mogbazar T&T 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 998825 | 1031989 | 33164 | 180 |  | 5969520
4 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 819230 | 840001 | 20771 | 180 |  | 5569200 |  |  | Meter Problem
10: Total |  | 11538720 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MOGBAZAR 33 KV SIDE; 4: 11612333.3273; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11612333.3273
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 11612333.3273 | 33/11 KV XF LV SIDE |  | 11628360
2: IMPORT-3 | LOSS UNITS=> |  | -16026.6727
2: IMPORT-4 | LOSS % IN => |  | -0.138%
| TOTAL IMPORT |  | 11612333.3273
1: 11 KV SIDE of___ Mogbazar T&T 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: Mogbazar T&T 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 14802 | 48176 | 33374 | 180 | 6007320 |  | 5999040.4703 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 959922 | 991150 | 31228 | 180 | 5621040 |  | 5613292.8569 | [7 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 11628360 |  | 11612333.3273 | -0.13782 | [6 empty] | 0 | #DIV/0! | #DIV/0!
2: Mogbazar T&T 11 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 133254 | 156809 | 23555 | 60 |  | 1413300 | 1410640.1386 | Kakrail |  |  |  | 11 kV post office | 1410640.1386 | 1413099.3422 | -2459.2036 | -0.17403 | OK
2 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 399215 | 423860 | 24645 | 60 |  | 1478700 | 1475917.0544 | Kakrail |  |  |  | 11 kV anarkoli | 1475917.0544 | 1466512.1688 | 9404.8856 | 0.64131 | OK
3 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 938252 | 944778 | 6526 | 60 |  | 391560 | 390823.0756 | Moghbazar |  |  |  | 11 kV sonalibagh | 390823.0756 | 376350.3769 | 14472.6986 | 3.8455 | OK
4 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1927455 | 1943262 | 15807 | 60 |  | 948420 | 946635.0529 | Moghbazar |  |  |  | 11 Kv desh tv | 946635.0529 | 901476.4809 | 45158.572 | 5.0094 | OK
5 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 561.01 | 590.39 | 29.38 | 60000 |  | 1762800 | 1759482.372 | Moghbazar |  |  |  | 11 Kv Btcl | 1759482.372 | 1708010.1623 | 51472.2098 | 3.0136 | OK
1 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 874964 | 885274 | 10310 | 60 |  | 618600 | 617435.7813 | Kakrail |  |  |  | 11 kV century | 617435.7813 | 612807.1598 | 4628.6216 | 0.75531 | OK
2 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 452115 | 470250 | 18135 | 60 |  | 1088100 | 1086052.1721 | Moghbazar |  |  |  | 11 kV cinema hall | 1086052.1721 | 1077858.8375 | 8193.3346 | 0.76015 | OK
3 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 669487 | 697644 | 28157 | 60 |  | 1689420 | 1686240.4748 | Khilgaon |  |  |  | 11 kV malibagh bazar | 1686240.4748 | 1646555.4045 | 39685.0703 | 2.4102 | OK
4 | 11 kv Sherebangla | 11 |  | DHK60915 | 1 | 668842 | 694633 | 25791 | 60 |  | 1547460 | 1544547.6466 | Moghbazar |  |  |  | 11 kv Sherebangla | 1544547.6466 | 1416880.2502 | 127667.3964 | 9.0105 | OK
5 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 308967 | 320497 | 11530 | 60 |  | 691800 | 690498.0173 | Moghbazar |  |  |  | 11 kV Nur Mosjid | 690498.0173 | 692746.3564 | -2248.3391 | -0.32455 | OK
6 | Auxiliary |  | Export | U0004461 | 1 | 8028.17 | 8095.99 | 67.82 | 60 |  | 4069.2 | 4061.5417 | Moghbazar |  |  |  | Auxiliary | 4061.5417 | 3583.4605 | 478.0811 | 13.3413 | OK
10: Grand Total | 11612333.3273 | 11634229.2 | 11612333.3273 | -0.1882
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Kakrail | at 33 KV level |  | 3503992.9743
[5 empty] | Moghbazar | at 33 KV level |  | 6422099.8781
[5 empty] | Khilgaon | at 33 KV level |  | 1686240.4748
[5 empty] | Total = |  |  | 11612333.3273 | 0
Ullon 132/33 KV 3 x 35/50 MVA Substation.(Central) Phone No. 9333940,55128099(dpdc)
1: 132 KV SIDE of___ULLON 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SIDDIRGONJ 132 KV SIDE (TARIFF POINT)
| Ullon-1 | 132 | IMPORT | 8993681 | 1 | 2618.149 | 2642.939 | 24.79 | 1440000 | 0 | 35697600
| Ullon-1 | 132 |  |  | 1 | 9.184 | 9.184 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  | 8993680 | 1 | 1373.548 | 1373.548 | 0 | 1440000 | 0 | 0
| Ullon-2 | 132 |  |  | 1 | 22.279 | 22.279 | 0 | 1440000 | 0 | 0
9=8-7: Total Import/Export | 0 | 35697600
9=8-7: Net Total | 35697600
HORIPUR 132 SIDE (TARIFF POINT)
| Maniknager-2 (new line to ullon) | 132 |  | 8993624 | 1 | 4768.057 | 4793.7 | 25.643 | 960000 | 0 | 24617280
| Maniknager-2 (new line to ullon) | 132 |  |  | 1 | 11.003 | 11.003 | 0 | 960000 | 0 | 0
9=8-7: Total Import/Export | 0 | 24617280
9=8-7: Net Total | 24617280
RAMPURA 132 KV SIDE (TARIFF POINT)
| Ullon U/G-1 | 132 |  | 8993659 | 1 | 4387.45 | 4400.359 | 12.909 | 960000 | 0 | 12392640
| Ullon U/G-1 | 132 |  |  | 1 | 1.56 | 1.561 | 0.001 | 960000 | 960 | 0
| Ullon U/G-2 | 132 |  | 8993660 | 1 | 4072.298 | 4084.578 | 12.28 | 960000 | 0 | 11788800
| Ullon U/G-2 | 132 |  |  | 1 | 1.329 | 1.33 | 0.001 | 960000 | 960 | 0
9=8-7: Total Import/Export | 1920 | 24181440
9=8-7: Net Total | 24179520
ULLON 132 KV SIDE (RECEIVING)
| 132 KV Rampura-1 (IMP) | 132 | RECEIVE |  | 1 | 3819.858 | 3819.858 | 0 | 1440000 | 0 |  |  |  | Meter is not working properly
| 132 KV Rampura-1 (EXP) | 132 |  |  | 1 | 1.737 | 1.737 | 0 | 1440000 |  | 0
| 132 KV Rampura-2 (IMP) | 132 |  |  | 1 | 3197.838 | 3197.838 | 0 | 1440000 | 0
| 132 KV Rampura-2 (EXP) | 132 |  |  | 1 | 3589.837 | 3589.837 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 146.887 | 146.887 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-1 Feeder | 132 |  |  | 1 | 5538.804 | 5538.804 | 0 | 1440000 |  | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 42.484 | 42.484 | 0 | 1440000 | 0
| 132 kV Siddhirgonj-2 Feeder | 132 |  |  | 1 | 1821.389 | 1821.389 | 0 | 1440000 |  | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 732658 | 732658 | 0 | 1000 | 0
| 132 KV HORIPUR Feeder. (IMP) | 132 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0
9=8-7: Total Import/Export | 0 | 0
9=8-7: Net Total | 0
2: EXPORT TO OTHERS 132/33 KV SS |  |  |  |  | AT Dhanmondi Side
| 132 kV Dhanmondi Circuit-1 | 132 |  |  | 1 | 1632756 | 1632756 | 0 | 1000 |  | 0 |  |  | 132 kV Ullon CKT-1 | 11397000
| 132 kV Dhanmondi Circuit-2 | 132 |  |  | 1 | 2101057 | 2131079 | 30022 | 1000 |  | 30022000 |  |  | 132 kV Ullon CKT-2 | 31143000
| 132 kV Dhanmondi Circuit-3 | 132 |  |  | 1 | 2857313 | 2887068 | 29755 | 1000 |  | 29755000 |  |  | 132 kV Ullon CKT-3 | 31978000
10: Total |  | 59777000 |  |  | Total | 74518000
ULLON 132 KV SIDE
2: 132/33 KV GT-1; 3: 132; 4: NET IMPORT |  | 0
2: 132/33 KV GT-2; 3: 132 |  | 0
2: 132/33 KV GT-3; 3: 132 |  | 0
10: Total |  | 24717400
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: SIDDIRGONJ 132 KV SIDE (TARIFF POINT); 4: 35697600; 6: EXPORT TO OTHER S/S; 9=8-7: 59777000 | 132 KV NET IMPORT |  | 24717400
2: HORIPUR 132 SIDE (TARIFF POINT); 4: 24617280; 6: 132 KV Net EXPORT; 9=8-7: 24717400 | 132/33 KV GT LV Side |  | 24225840
2: RAMPURA 132 KV SIDE (TARIFF POINT); 4: 24179520 | LOSS UNITS=>(132 HV-33 LV) |  | 491560
2: IMPORT-4 | LOSS % IN => |  | 1.989%
| 132 KV TOTAL IMPORT |  | 84494400
1: 33 KV SIDE of___ULLON 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: ULLON 33 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 132/33 kV XF-1 Incoming | 33 | Import | BD001812 | 1 | 2131.9868 | 2157.486 | 25.4992 | 480000 | 12239616 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 132/33 kV XF-2 Incoming | 33 | Import | BD001858 | 1 | 2054.3047 | 2079.276 | 24.9713 | 480000 | 11986224 | [9 empty] | 0 | #DIV/0! | #DIV/0!
3 | 132/33 kV XF-3 Incoming | 33 | Import | BD001856 | 1 | 1533.862 | 1533.862 | 0 | 480000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 24225840 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: ULLON 33 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1533.8259 | 1564.8785 | 31.0526 | 240000 |  | 7452624 | 7471725.0456 |  | 15514959.122 | Taltola 33/11 kv ss | 0.38493 | Taltala-1 | 7471725.0456 | 7335965.7983 | 135759.2474 | 1.8506 | OK
| Mgbazar T&T | 33 | Export | BD001859 | 1 | 333.6908 | 333.6908 | 0 | 240000 |  | 0 | 0 |  |  |  |  | Mgbazar T&T | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Kakrail | 33 | North-1 | BD001811 | 1 | 1163.9083 | 1163.9096 | 0.0013 | 240000 |  | 312 | 312.7997 |  | 0 | Mgbazar T&T 33/11 kv ss | -0.1882 | Kakrail | 312.7997 | 941.5329 | -628.7333 | -66.7776 | CHECK
2 | Taltala-2 | 33 | Export | BD001837 | 1 | 2495.751 | 2529.1788 | 33.4278 | 240000 |  | 8022672 | 8043234.0764 |  |  |  |  | Taltala-2 | 8043234.0764 | 7826069.8947 | 217164.1817 | 2.7749 | OK
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 |  | 0 | 0 |  | 312.7997 | Kakrail 33/11 kv ss | 1 | Goran | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 |  | 0 | 0 |  | 0 | Goran 33/11 kv ss | 0.14731 | Tejgaon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.9199 | 62.0687 | 0.1488 | 240000 |  | 35712 | 35803.5297 |  | 0 | Tejgoan 33/11 kv ss | 1.1843 | Khailgaon | 35803.5297 | 60354.6742 | -24551.1445 | -40.6781 | CHECK
4 | AT at GIS Building | 415 | Export | DHKE4577 | 1 | 141164 | 144728 | 3564 | 1 |  | 3564 | 3573.1345 |  | 35803.5297 | Khilgoan 33/11 kv ss | 2.8737 | AT at GIS Building | 3573.1345 | 7166.1117 | -3592.9771 | -50.1384 | CHECK
7: 0; 8: 0; 10: TOTAL= |  | 15514884 | 15554648.5859 |  |  |  |  | 0 | 15554648.5859 | 15230498.0117 | 324150.5742 | 2.1283 | OK
| 33 KV Local Feeder -1 | 33 | NET IMPORT |  | 1 | 1116.0406 | 1134.3375 | 18.2969 | 240000 |  | 4391256 | 4402510.7716 |  | 8671191.4141 | Ullon 33/11 kv ss | 0.40829 | 33 KV Local Feeder -1 | 4402510.7716 | 4417141.3282 | -14630.5565 | -0.33122 | OK
| 33KV Local Feeder- 2 | 33 |  |  | 1 | 845.0281 | 862.7688 | 17.7407 | 240000 |  | 4257768 | 4268680.6424 |  |  |  |  | 33KV Local Feeder- 2 | 4268680.6424 | 4269320.6601 | -640.0177 | -0.014991 | OK
10: TOTAL= |  | 8649024 | 8671191.4141 |  |  |  |  | 0 | 8671191.4141 | 8686461.9883 | -15270.5742 | -0.1758 | OK
10: Grand Total | 24225840 | 24163908 | 24225840 | 0.2563
1: 11 KV SIDE of___ULLON 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: ULLON 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | 2007-755109 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | 30799464 | 1 |  |  | 0 | 160000 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
10: Total | 8649024 |  | 8671191.4141 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: ULLON 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | West Malibagh | 11 | Mogbazar | 30799488 | 1 |  |  | 0 | 60000 | Estimated | 1033879.14 | 1038100.3806 | Moghbazar | 85 |  |  | West Malibagh | 1038100.3806 | 1138226.0536 | -100125.6731 | -8.7966 | OK
2 | Ullon | 11 | Mogbazar | 307994528 | 1 |  |  | 0 | 60000 | Estimated | 1642043.34 | 1648747.6632 | Moghbazar | 135 |  |  | Ullon | 1648747.6632 | 1617479.1288 | 31268.5344 | 1.9332 | OK
3 | Mohanagar | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1763676.18 | 1770877.1198 | Moghbazar | 145 |  |  | Mohanagar | 1770877.1198 | 1677385.7633 | 93491.3565 | 5.5736 | OK
4 | Bagichartek | 11 | Mogbazar | 30799497 | 1 |  |  | 0 | 60000 | Estimated | 1277144.82 | 1282359.2936 | Moghbazar | 105 |  |  | Bagichartek | 1282359.2936 | 1317945.9568 | -35586.6632 | -2.7002 | OK
1 | Mirbagh | 11 | Mogbazar | 30799487 | 1 |  |  | 0 | 60000 | Estimated | 1642043.34 | 1648747.6632 | Moghbazar | 135 |  |  | Mirbagh | 1648747.6632 | 1557572.4944 | 91175.1688 | 5.8537 | OK
2 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 |  |  | 0 | 60000 | Estimated | 1277144.82 | 1282359.2936 | Moghbazar | 105 |  |  | West Rampura | 1282359.2936 | 1377852.5912 | -95493.2976 | -6.9306 | OK
3 | Jilkanon | 11 | Mogbazar | 30799461 | 1 |  |  | 0 | 60000 |  | 0 | 0 | Moghbazar |  |  |  | Jilkanon | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | AT-1 | 11 | Export | 5395187 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | AT-2 | 11 | Export | 5379456 | 1 |  |  | 0 | 2 |  | 0 | 0 | Moghbazar |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 8671191.4141 | 8635931.64 | 8671191.4141 | 0.40829
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 8671191.4141
[5 empty] | Total = |  |  | 8671191.4141 | 0
Madertek 132/33 KV Substation. ( North 2) Phone: 47292879
1: 132 KV SIDE of___MADERTEK 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
RAMPURA 132 KV SIDE (TARIFF POINT)
1 | Rampura to Madartek-1 | 132 | Export | 50146667 | 1 | 1758.566 | 1786.459 | 27.893 | 960000 | 0 | 26777280
2 | Rampura to Madartek-2 | 132 | Export | 50146668 | 1 | 1552.894 | 1580.626 | 27.732 | 960000 | 0 | 26622720
9=8-7: Total Import/Export | 0 | 53400000
9=8-7: Net Total | 53400000
MADERTEK 132 KV SIDE (RECEIVING)
1 | 132 kV Rampura-1 | 132 | Import | SIEM0492 | 1 | 1545900 | 1572642 | 26742 | 1000 | 26742000
|  | 132 | Export |  | 1 | 0 | 0 | 0
2 | 132 kV Rampura-2 | 132 | Import | SIEM0489 | 1 | 1495344 | 1522099 | 26755 | 1000 | 26755000
|  | 132 | Export |  | 1 | 0 | 0 | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 53497000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 53497000
| MADERTEK 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| MADERTEK 132 KV SIDE |  |  |  |  | 0 | 0
3 | 133 kV GT-1 | 132 | Export |  | 1 | 1381875 | 1408768 | 26893 | 1000 |  | 26893000
4 | 133 kV GT-2 | 132 | Export |  | 1 | 1370463 | 1397199 | 26736 | 1000 |  | 26736000
10: Total |  | 53629000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: RAMPURA 132 KV SIDE (TARIFF POINT); 4: 53400000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 53400000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 53400000 | 33 KV NET IMPORT |  | 53728000
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | -328000
2: IMPORT-4 | LOSS % IN => |  | -0.6142%
| 132 KV TOTAL IMPORT |  | 53400000
1: 33 KV SIDE of___MADERTEK 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0516 | 1 | 1530511 | 1557416 | 26905 | 1000 | 26905000 |  | 26740749.7022
2 | 132/33 kV XF-1 Incoming | 33 | Import | SIEM0515 | 3 | 508172 | 517113 | 8941 | 1000 | 26823000 |  | 26659250.2978
7: 0; 8: 0; 10: Total | 53728000 |  | 53400000
| MADERTEK 33 KV SIDE |  |  |  |  | 0 | 0
| 33/11 kv Transforfers |  |  |  |  | 0 | 0
1 | 33 kV T-1 | 33 | Import | SIEM0512 | 1 | 403503 | 407868 | 4365 | 2000 |  | 8730000 | 8725424.8709 |  | 20779104.5894 | Madartek 33/11 kv ss
2 | 33 kV T-3 | 33 | Export |  | 1 | 74323 | 75919 | 1596 | 2000 |  | 3192000 | 3190327.1693
2 | 33 kV T-2 | 33 | Export | SIEM0505 | 1 | 406313 | 410747 | 4434 | 2000 |  | 8868000 | 8863352.5492
2: 33 kv Feeders; 7: 0; 8: 0; 10: Total |  | 20790000 | 20779104.5894 |  | 15295979.6361 | Banasree 33/11 kv ss
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 98470 | 103409 | 4939 | 2000 |  | 9878000 | 9872823.2388
1 | Goran | 33 | Export | SIEM0510 | 1 | 344806 | 349987 | 5181 | 2000 |  | 10362000 | 10356569.589 |  | 10356569.589 | Goran 33/11 kv ss
3 | Amulia | 33 | Export | SIEM0505 | 1 | 35220 | 36382 | 1162 | 6000 |  | 6972000 | 6968346.1855
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 88263 | 90976 | 2713 | 2000 |  | 5426000 | 5423156.3974 |  | 6968346.1855 | Amulia 33/11 kv ss
10: Total |  | 32638000 | 32620895.4106
9=8-7: Grand Total | 53400000 | 53428000 | 53400000 | -0.052407
1: 11 KV SIDE of___MADERTEK 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Pos; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: Madertek 11 kV Side | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | 33/11 kV Transformer-1 Incoming | 11 | Import | GJU 71154 | 1 | 376390.4 | 380729.6 | 4339.2 | 2000 | 8678400 |  | 8718640.3104 |  | Consumption of Other NOCS | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | 33/11 kV Transformer-2 Incoming | 11 | Import | GJU 71155 | 1 | 379344.7 | 383760.4 | 4415.7 | 2000 | 8831400 |  | 8872349.7462 |  | 6701570.4775 | [5 empty] | 0 | #DIV/0! | #DIV/0!
3 | 33/11 kV Transformer-3 Incoming | 11 | Import | 6604399 | 1 | 4670.14 | 4687.77 | 17.63 | 180000 | 3173400 |  | 3188114.5328 |  | Consumption of Mugpadara Check | [5 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 20683200 |  | 20779104.5894 |  | 13981629.5225 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: Madertek 11 kV Side; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 8.4955 | 10.3885 | 1.8929 | 1000000 |  | 1892944.4 | 1914129.2674 | Mugdapara | Opening Conveted to GWH from MWH |  |  | Sobujbagh | 1914129.2674 | 1830321.6533 | 83807.6141 | 4.5788 | OK
2 | Madertek | 11 | Mugdapara | D0086134 | 1 | 97494.4 | 99487.1 | 1992.7 | 1000 |  | 1992700 | 2015001.2811 | Mugdapara |  |  |  | Madertek | 2015001.2811 | 1947058.9925 | 67942.2886 | 3.4895 | OK
3 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 7021.7968 | 8440.3928 | 1418.596 | 1000 | Calculated | 2014583.4653 | 2037129.655 | Mugdapara | Calculation Attached |  |  | Rajarbagh | 2037129.655 | 2033626.6462 | 3503.0088 | 0.17225 | OK
| Goran | 11 |  | X1390296 | 1 | 26638.6 | 28663.4 | 2024.8 | 1000 |  | 2024800 | 2047460.5279 | Bashabo |  |  |  | Goran | 2047460.5279 | 1968306.9598 | 79153.5681 | 4.0214 | OK
5 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 8205.6192 | 9771.1 | 1565.4808 | 1000 |  | 1565480.8 | 1583000.8619 | Mugdapara |  |  |  | Dhakhingaon | 1583000.8619 | 1493157.2972 | 89843.5647 | 6.017 | OK
6 | Manda | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 |  | 0 | 0 | Maniknagar | Cable Fault No Load |  |  | Manda | 0 | 373198.8946 | -373198.8946 | -100 | CHECK
7 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 510.4637 | 744.7806 | 234.317 | 1000 |  | 234316.96 | 236939.3158 | Mugdapara |  |  |  | Green Model Town | 236939.3158 | 229733.5056 | 7205.8102 | 3.1366 | OK
1 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 2474.7662 | 3045.3432 | 570.577 | 1000 |  | 570577 | 576962.6065 | Mugdapara |  |  |  | Biswa Road | 576962.6065 | 679941.1966 | -102978.59 | -15.1452 | OK
2 | Mugdapara | 11 |  | X0854272 | 1 | 3786.4 | 3885.1 | 98.7 | 1000 |  | 98700 | 99804.6 | Maniknagar |  |  |  | Mugdapara | 99804.6 | 280453.0279 | -180648.4279 | -64.4131 | CHECK
| Singapur | 11 |  | X1390302 (N) | 1 | 31151.7 | 33574.1 | 2422.4 | 1000 |  | 2422400 | 2449510.2642 | Banosree |  |  |  | Singapur | 2449510.2642 | 2359732.7837 | 89777.4805 | 3.8046 | OK
| Trimohony | 11 |  | X1390308 | 1 | 24527.3 | 26608.8 | 2081.5 | 1000 |  | 2081500 | 2104795.0854 | Banosree |  |  |  | Trimohony | 2104795.0854 | 2021980.735 | 82814.3504 | 4.0957 | OK
5 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 10561.687 | 12357.722 | 1796.035 | 1000 |  | 1796035 | 1816135.3069 | Mugdapara | Closing Conveted to MWH from GWH |  |  | Mayakanon | 1816135.3069 | 1942171.9601 | -126036.6532 | -6.4895 | OK
6 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 3952.1608 | 4655.1844 | 703.0236 | 1000 |  | 703023.6 | 710891.4812 | Mugdapara |  |  |  | Ahmedbagh | 710891.4812 | 850151.1099 | -139259.6286 | -16.3806 | OK
1 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 712365 | 720580 | 8215 | 200 |  | 1643000 | 1661387.6173 | Mugdapara |  |  |  | Wasa Road | 1661387.6173 | 1892982.4123 | -231594.795 | -12.2344 | OK
2 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 746576 | 754033 | 7457 | 200 |  | 1491400 | 1508090.9874 | Mugdapara |  |  |  | Nandipara | 1508090.9874 | 1450702.4488 | 57388.5387 | 3.9559 | OK
| AT-1 | 0.415 |  |  | 1 | 357.37 | 502.11 | 144.74 | 80 |  | 11579.2 | 11708.7885 | Mugdapara |  |  |  | AT-1 | 11708.7885 | 9611.7345 | 2097.054 | 21.8176 | OK
3 | AT-2 | 0.415 |  | 63394003 | 1 | 157.43 | 233.54 | 76.11 | 80 |  | 6088.8 | 6156.9427 | Mugdapara |  |  |  | AT-2 | 6156.9427 | 5477.3433 | 679.5994 | 12.4075 | OK
10: Total | 20779104.5894 | 20549129.2253 | 20779104.5894 | [7 empty] | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 20779104.5894 | 20549129.2253 | 20779104.5894 | 1.1191
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 4554305.3496
[5 empty] | Bashabo | at 33 KV level |  | 2047460.5279
[5 empty] | Maniknagar | at 33 KV level |  | 99804.6
[5 empty] | Mugdapara | at 33 KV level |  | 14077534.1118
[5 empty] | Total = |  |  | 20779104.5894 | 0
Tejgaon 33/11KV, 2x 20/28 MVA Substation(North). Phone No. 8878501,8870313(CR)
1: 33 KV SIDE of___TEJGOAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV SIDE
8 | 33 kV Tejgaon U/G Feeder-1 | 33 | 0 | 76026300 | 1 | 6695.56 | 6718.6 | 23.04 | 360000 | 0 | 8294400 | 8350441.9432
9 | 33 kV Tejgaon U/G Feeder-2 | 33 | 0 | 06604453 | 1 | 6474.31 | 6514.5 | 40.19 | 360000 | 0 | 14468400 | 14566157.1917
0 | Tejgaon | 33 | Export | 6604342 | 1 | 2164.99 | 2164.99 | 0 | 240000 | 0 | 0 | 0
10: Total | 0 | 22762800 | 22916599.1349
TEJGOAN 33 KV SIDE (RECEIVING)
7: 0; 8: 0; 10: Total | 0
| TEJGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| TEJGOAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33/11 kV Transfomer-1 (T1) | 33 | Export | DHK61080 | 1 | 640150.1 | 668563.1 | 28413 | 270 |  | 7671510
2 | 33/11 kV Transfomer-2 (T2) | 33 | Export | DHK61100 | 1 | 432407.9 | 486279.6 | 53871.7 | 180 |  | 9696906
3 | 33/11 kV Transfomer-3 (T3) | 33 | Export | BD001872 | 1 | 209525.9 | 216375 | 6849.1 | 180000 |  | 6849100
10: Total |  | 24217516 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: 33 KV SIDE; 4: 22916599.1349; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TEJGOAN 33 KV NET IMPORT |  | 22916599.1349
2: IMPORT-2; 6: TEJGOAN 33 KV NET IMPORT; 9=8-7: 22916599.1349 | 33 KV TX HV Side |  | 24217516
2: IMPORT-3 | LOSS UNITS=> |  | -1300916.8651
2: IMPORT-4 | LOSS % IN => |  | -5.677%
| TOTAL IMPORT |  | 22916599.1349
1: 11 KV SIDE of___ TEJGOAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: TEJGOAN 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHK61079 | 1 | 791843.8 | 834789.6 | 42945.8 | 180 | 7730244 |  | 7972219.0604 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHK61082 | 1 | 706686.8 | 749140.6 | 42453.8 | 180 | 7641684 |  | 7880886.9213 | [7 empty] | 0 | #DIV/0! | #DIV/0!
3 | Transfomer-3 Incoming | 11 | Import | BD001875 | 1 | 209525.9 | 216375 | 6849.1 | 1000 | 6849100 |  | 7063493.1532 | [7 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 22221028 |  | 22916599.1349 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: TEJGOAN 11 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Nakhal Para Feeder | 11 |  | DHK60950 | 1 | 201859.3 | 228050.8 | 26191.5 | 60 |  | 1571490 | 1590100.5899 | Tejgaon |  |  |  | Nakhal Para Feeder | 1590100.5899 | 1545202.0376 | 44898.5523 | 2.9057 | OK
2 | Badda-Meghna Feeder | 11 |  | DHK60979 | 1 | 888283.6 | 901418.5 | 13134.9 | 60 |  | 788094 | 797427.1133 | Tejgaon |  |  |  | Badda-Meghna Feeder | 797427.1133 | 711868.0468 | 85559.0665 | 12.019 | OK
3 | Rasulbagh Feeder | 11 |  | DHK60948 | 1 | 961752.1 | 991762.3 | 30010.2 | 60 |  | 1800612 | 1821935.9992 | Tejgaon |  |  |  | Rasulbagh Feeder | 1821935.9992 | 1845073.9247 | -23137.9255 | -1.254 | OK
4 | Lukas | 11 |  | 8A021100948-02 | 1 | 64421346 | 66843300 | 2421954 | 1 |  | 2421954 | 2450636.3287 | Tejgaon |  |  |  | Lukas | 2450636.3287 | 2356930.5125 | 93705.8162 | 3.9758 | OK
5 | PWD RMU | 11 |  |  | 1 | 652660.7 | 654515.2 | 1854.5 | 1 |  | 1854.5 | 1876.4622 | Tejgaon |  |  |  | PWD RMU | 1876.4622 | 1825.2484 | 51.2138 | 2.8059 | OK
1 | Civil Aviation Feeder | 11 |  | DHK60977 | 1 | 791561.7 | 840529.6 | 48967.9 | 60 |  | 2938074 | 2972868.5519 | Tejgaon |  |  |  | Civil Aviation Feeder | 2972868.5519 | 2843930.4649 | 128938.0871 | 4.5338 | OK
2 | Ahasanullah Eng. | 11 |  | DHK60867 | 1 | 859374.2 | 870599.2 | 11225 | 60 |  | 673500 | 681476.0179 | Tejgaon |  |  |  | Ahasanullah Eng. | 681476.0179 | 638085.1899 | 43390.828 | 6.8002 | OK
3 | New GMG Feeder | 11 |  | DHK61106 | 1 | 7264.2 | 46250.7 | 38986.5 | 60 |  | 2339190 | 2366892.1845 | Tejgaon |  |  |  | New GMG Feeder | 2366892.1845 | 2233355.6797 | 133536.5048 | 5.9792 | OK
4 | Shikajo | 11 |  | HA021101036-02 | 1 | 62704679 | 63571582 | 866903 | 1 |  | 866903 | 877169.4199 | Tejgaon |  |  |  | Shikajo | 877169.4199 | 833321.8823 | 43847.5376 | 5.2618 | OK
5 | Kahinur | 11 |  |  | 1 | 496661.5 | 518848.9 | 22187.4 | 60 |  | 1331244 | 1347009.4431 | Tejgaon |  |  |  | Kahinur | 1347009.4431 | 1251045.3402 | 95964.1029 | 7.6707 | OK
6 | Link road | 11 |  | 8A021100380-02 | 1 | 63919556 | 64330013 | 410457 | 1 |  | 410457 | 415317.8944 | Tejgaon |  |  |  | Link road | 415317.8944 | 416737.628 | -1419.7337 | -0.34068 | OK
7 | Shanta | 11 |  |  | 1 | 299552.9 | 310614.7 | 11061.8 | 60 |  | 663708 | 671568.0547 | Tejgaon |  |  |  | Shanta | 671568.0547 | 608607.1616 | 62960.8931 | 10.3451 | OK
1 | Karnafuly Feeder | 11 |  | DHK61084 | 1 | 33696.3 | 34410.6 | 714.3 | 1000 |  | 714300 | 722759.1976 | Tejgaon |  |  |  | Karnafuly Feeder | 722759.1976 | 686952.8872 | 35806.3104 | 5.2123 | OK
2 | Butex | 11 |  |  | 1 | 892.3 | 991.5 | 99.2 | 1000 |  | 99200 | 100374.7899 | Tejgaon |  |  |  | Butex | 100374.7899 | 90006.1656 | 10368.6243 | 11.5199 | OK
3 | OriON LAB | 11 |  |  | 1 | 8007550 | 8102262 | 94712 | 1 |  | 94712 | 95833.6401 | Tejgaon |  |  |  | OriON LAB | 95833.6401 | 88588.4676 | 7245.1725 | 8.1785 | OK
4 | Nina kabbo | 11 |  | 201101025-2 | 1 | 16563888 | 16842033 | 278145 | 1 |  | 278145 | 281438.971 | Tejgaon |  |  |  | Nina kabbo | 281438.971 | 283127.915 | -1688.9439 | -0.59653 | OK
5 | Satrong | 11 |  | HA021100515-2 | 1 | 89639487 | 91425148 | 1785661 | 1 |  | 1785661 | 1806807.9399 | Tejgaon |  |  |  | Satrong | 1806807.9399 | 1563100.3489 | 243707.5911 | 15.5913 | OK
6 | South East RMU | 11 |  |  | 1 | 601.9 | 729.2 | 127.3 | 1000 |  | 127300 | 128807.568 | Tejgaon |  |  |  | South East RMU | 128807.568 | 139045.3993 | -10237.8313 | -7.3629 | OK
7 | Rangs Bhaban | 11 |  | HA021100939-2 | 1 | 270974 | 432458 | 161484 | 1 |  | 161484 | 163396.3968 | Tejgaon |  |  |  | Rangs Bhaban | 163396.3968 | 151255.7649 | 12140.6319 | 8.0266 | OK
8 | Babli | 11 |  |  | 1 | 54005.3 | 56089.7 | 2084.4 | 1000 |  | 2084400 | 2109084.7983 | Tejgaon |  |  |  | Babli | 2109084.7983 | 2111815.0669 | -2730.2686 | -0.12929 | OK
| SPL | 11 |  |  | 1 | 3461.1 | 3911.5 | 450.4 | 1000 |  | 450400 | 455733.9249 | Tejgaon |  |  |  | SPL | 455733.9249 | 408962.9923 | 46770.9326 | 11.4365 | OK
9 | DNCC Hospital | 11 |  |  | 1 | 13491.4 | 14537.1 | 1045.7 | 1000 |  | 1045700 | 1058083.8484 | Tejgaon |  |  |  | DNCC Hospital | 1058083.8484 | 992388.6083 | 65695.2401 | 6.6199 | OK
| 11/.415 kv Local transformer | 0.415 |  | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 |  |  | 0 | Tejgaon
10: Grand Total | 22916599.1349 | 22648382.5 | 22916599.1349 | 1.1843
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Tejgaon | at 33 KV level |  | 22916599.1349
[5 empty] | Total = |  |  | 22916599.1349 | 0
1: 33 KV SIDE of___ASADGATE 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Satmosjid 33 KV SIDE
0 | Asad Gate Circuit-1 | 33 | 0 | 214393/44-2711 | 1 | 54.83 | 63.8262 | 8.9962 | 1000 | Estimated | 9455256 | 9412540.6838
12 | Asad Gate Circuit-2 | 33 |  | 214393/43-2711 | 1 | 235.65 | 9396.2208 | 9160.5708 | 1000 | Estimated | 8870848.2 | 8830773.02
10: Total |  | 18326104.2 | 18243313.7037
ASADGATE 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import | DHKC9350 | 1 | 77676.95 | 111497.5 | 33820.55 | 270 | 9131548.5
2 | Shatmasjid-2 | 33 | Import | DHKC9354 | 1 | 123054.55 | 123054.55 | 0 | 270 | 0
7: 0; 8: 0; 10: Total | 9131548.5
| ASADGATE 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| ASADGATE 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transfomer-1 (T1) | 33 | Export | DHKC9353 | 1 | 84521.34 | 137395.2 | 52873.86 | 180 |  | 9517294.8
2 | Transfomer-2 (T2) | 33 | Export | DHKC9305 | 1 | 99475.18 | 149274.9 | 49799.72 | 180 |  | 8963949.6
10: Total |  | 18481244.4 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Satmosjid 33 KV SIDE; 4: 18243313.7037; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | ASADGATE 33 KV NET IMPORT |  | 18243313.7037
2: IMPORT-2; 6: ASADGATE 33 KV NET IMPORT; 9=8-7: 18243313.7037 | ASADGATE 11 KV NET IMPORT |  | 18691342.7904
2: IMPORT-3 | LOSS UNITS=> |  | -448029.0867
2: IMPORT-4 | LOSS % IN => |  | -2.456%
| TOTAL IMPORT |  | 18243313.7037
1: 11 KV SIDE of___ASADGATE 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: ASADGATE 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transfomer-1 Incoming | 11 | Import | DHKC9371 | 1 | 57772.67 | 110301.87 | 52529.2 | 180 | 9455256 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transfomer-2 Incoming | 11 | Import | DHKC9337 | 1 | 1243.83 | 50526.32 | 49282.49 | 180 | 8870848.2 | [9 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 18326104.2 |  | 18243313.7037 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: ASADGATE 11 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Gonobhaban | 11 |  | DHKC9332 | 1 | 69014.8 | 72755.2 | 3740.4 | 60 |  | 224424 | 226219.392 | Shere b.nagar |  |  |  | Gonobhaban | 226219.392 | 216875.2359 | 9344.1561 | 4.3085 | OK
2 | Rapa Plaza Feeder | 11 |  | DHKC9339 | 1 | 56103.84 | 76499.17 | 20395.33 | 60 |  | 1223719.8 | 1233509.5584 | Dhanmondi |  |  |  | Rapa Plaza Feeder | 1233509.5584 | 1199461.0668 | 34048.4916 | 2.8386 | OK
3 | Shukrabad/ South Plaza | 11 |  | DHKC9324 | 1 | 95989.52 | 115754.76 | 19765.24 | 60 |  | 1185914.4 | 1195401.7152 | Shere b.nagar |  |  |  | Shukrabad/ South Plaza | 1195401.7152 | 1120705.5276 | 74696.1876 | 6.6651 | OK
4 | Wasa O/H | 11 |  | DHKC9333 | 1 | 78543.28 | 100442.81 | 21899.53 | 60 |  | 1313971.8 | 1324483.5744 | Satmasjid |  |  |  | Wasa O/H | 1324483.5744 | 2118683.8855 | -794200.3111 | -37.4856 | OK
5 | Bangabandhu Memorial Museum | 11 |  | DHKC9334 | 1 | 15026.42 | 15376.97 | 350.55 | 60 |  | 21033 | 21201.264 | Dhanmondi |  |  |  | Bangabandhu Memorial Museum | 21201.264 | 20854.3329 | 346.9311 | 1.6636 | OK
6 | Iqbal Road O/H | 11 |  | DHKC9330 | 1 | 42849.53 | 72221.61 | 29372.08 | 60 |  | 1762324.8 | 1776423.3984 | Shyamoli |  |  |  | Iqbal Road O/H | 1776423.3984 | 1626760.4818 | 149662.9166 | 9.2001 | OK
7 | Town Hall | 11 |  | DHKC9351 | 1 | 61880.78 | 100798.64 | 38917.86 | 60 |  | 2335071.6 | 2353752.1728 | Shyamoli |  |  |  | Town Hall | 2353752.1728 | 1991480.522 | 362271.6508 | 18.1911 | OK
8 | Post Office | 11 |  | DHKC9331 | 1 | 37135.17 | 64790.66 | 27655.49 | 60 |  | 1659329.4 | 1672604.0352 | Shyamoli |  |  |  | Post Office | 1672604.0352 | 1378440.8932 | 294163.142 | 21.3403 | OK
9 | Shangshad Bhaban | 11 |  | DHKC9370 | 1 | 6671.66 | 11515.28 | 4843.62 | 60 |  | 290617.2 | 292942.1376 | Shere b.nagar |  |  |  | Shangshad Bhaban | 292942.1376 | 474363.1372 | -181420.9996 | -38.2452 | OK
10 | Jakir Hossain Road | 11 |  | DHKC9373 | 1 | 81724.89 | 108235.46 | 26510.57 | 60 |  | 1590634.2 | 1603359.2736 | Satmasjid |  |  |  | Jakir Hossain Road | 1603359.2736 | 1792634.4006 | -189275.127 | -10.5585 | OK
11 | New Colony O/H Feeder | 11 |  | DHKC9369 | 1 | 69251.43 | 86475.56 | 17224.13 | 60 |  | 1033447.8 | 1041715.3824 | Satmasjid |  |  |  | New Colony O/H Feeder | 1041715.3824 | 0 | 1041715.3824 | #DIV/0! | #DIV/0!
12 | Aurangzeb Feeder | 11 |  | DHKC9321 | 1 | 42513.02 | 69565.32 | 27052.3 | 60 |  | 1623138 | 1636123.104 | Shyamoli |  |  |  | Aurangzeb Feeder | 1636123.104 | 1847282.7847 | -211159.6807 | -11.4308 | OK
13 | Asadgate Local Feeder | 11 |  | DHKC9338 | 1 | 32726.29 | 67929.33 | 35203.04 | 60 |  | 2112182.4 | 2129079.8592 | Satmasjid |  |  |  | Asadgate Local Feeder | 2129079.8592 | 2381609.9379 | -252530.0787 | -10.6033 | OK
14 | Sonarbangla Road | 11 |  | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Sonarbangla Road | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | Humayun Road | 11 |  | DHKC9366 | 1 | 47034.27 | 78786.74 | 31752.47 | 60 |  | 1905148.2 | 1920389.3856 | Shyamoli |  |  |  | Humayun Road | 1920389.3856 | 263604.1533 | 1656785.2323 | 628.5126 | FAULT
16 | NHA | 11 |  | DHKC9374 | 1 | 52748.02 | 57115.39 | 4367.37 | 60 |  | 262042.2 | 264138.5376 | Shyamoli |  |  |  | NHA | 264138.5376 | 26450.7883 | 237687.7493 | 898.6036 | FAULT
17 | Auxiliary transformer | 0.415 |  |  | 1 | 633994 | 633994 | 0 | 1 |  | 0 | 0 | Satmasjid |  |  |  | Auxiliary transformer | 0 | 7372.3763 | -7372.3763 | -100 | CHECK
10: Grand Total | 18691342.7904 | 18542998.8 | 18691342.7904 | 0.8
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 1714563.2448
[5 empty] | Dhanmondi | at 33 KV level |  | 1254710.8224
[5 empty] | Satmasjid | at 33 KV level |  | 6098638.0896
[5 empty] | Shyamoli | at 33 KV level |  | 9623430.6336
at 33 KV level
[5 empty] | Total = |  |  | 18691342.7904 | 0
1: 33 KV SIDE of___ BANASREE 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADARTEK 33 KV SIDE
3 | Banasree-1 | 33 | Export | SIEM0504 | 1 | 98470 | 103409 | 4939 | 2000 | 0 | 9878000 | 9872823.2388
4 | Banasree-2 | 33 | Export | SIEM0506 | 1 | 88263 | 90976 | 2713 | 2000 | 0 | 5426000 | 5423156.3974
10: Total |  | 15304000 | 15295979.6361 | -0.052407
BANASREE 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import |  | 1 | 5548420 | 15589610 | 10041190 | 1 | 10041190
2 | Madertek Circuit-02 | 33 | Import |  | 1 | 5713980 | 11242090 | 5528110 | 1 | 5528110
3 | Ullon O/H | 33 | Import |  | 1 | 639920 | 639920 | 0 | 1 | 0
10: Total | 15569300 | 0 | 0
BANASREE 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
BANASREE 33 KV SIDE
1 | Transformer-01 | 33 | Export | 14 | 1 | 1566520 | 11612560 | 10046040 | 1 |  | 10046040
2 | Transformer-02 | 33 | Export | 74 | 1 | 2581140 | 8110080 | 5528940 | 1 |  | 5528940 |  |  | Meter Problem
10: Total |  | 15574980
2: 33 KV IMPORT; 4: KWH; 6: 33 KV Import; 9=8-7: KWH | BUS LOSS |  | KWH
2: MADARTEK 33 KV SIDE; 4: 15295979.6361; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 15295979.6361
2: IMPORT-2; 6: 33 KV Net Import; 9=8-7: 15295979.6361 | 33 KV TX HV SIDE |  | 15574980
2: IMPORT-3 | LOSS UNITS=> |  | -279000.3639
2: IMPORT-4 | LOSS % IN => |  | -1.824%
| TOTAL IMPORT |  | 15295979.6361
1: 11 KV SIDE of___BANASREE 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS | [6 empty] | 0 | #DIV/0! | #DIV/0!
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: BANASREE 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | 141 | 1 | 12785000 | 12785000 | 0 | 1 | 10046040 |  | 9866081.5785 |  | Meter Problem | [5 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | 198 | 1 |  |  | 0 | 1 | 5528940 |  | 5429898.0576 | [7 empty] | 0 | #DIV/0! | #DIV/0!
10: Total | 15574980 |  | 15295979.6361 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: BANASREE 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Angur Jora | 11 |  | 141 | 1 | 3861980 | 6021560 | 2159580 | 1 |  | 2159580 | 2182461.1184 | Banosree |  |  |  | Angur Jora | 2182461.1184 | 2168323.5267 | 14137.5917 | 0.65201 | OK
2 | Block F-G Avenue | 11 |  | 68 | 1 | 5519540 | 8177840 | 2658300 | 1 |  | 2658300 | 2686465.1418 | Banosree |  |  |  | Block F-G Avenue | 2686465.1418 | 2772883.9436 | -86418.8018 | -3.1166 | OK
3 | Banasree Main Road(Monpura) | 11 |  | 168 | 1 | 4446260 | 6283880 | 1837620 | 1 |  | 1837620 | 1857089.8973 | Banosree |  |  |  | Banasree Main Road(Monpura) | 1857089.8973 | 1771391.1453 | 85698.7519 | 4.8379 | OK
4 | Baitul Kuddus | 11 |  | 62 | 1 | 7309220 | 9606640 | 2297420 | 1 |  | 2297420 | 2321761.5567 | Banosree |  |  |  | Baitul Kuddus | 2321761.5567 | 2248090.2296 | 73671.3271 | 3.2771 | OK
5 | Ideal | 11 |  |  | 1 | 7487660 | 8292520 | 804860 | 1 |  | 804860 | 813387.6289 | Banosree |  |  |  | Ideal | 813387.6289 | 785714.1589 | 27673.4701 | 3.5221 | OK
6 | Central Mosque | 11 |  | 46 | 1 | 7813780 | 10042320 | 2228540 | 1 |  | 2228540 | 2252151.7613 | Banosree |  |  |  | Central Mosque | 2252151.7613 | 2213991.1776 | 38160.5837 | 1.7236 | OK
7 | Larive | 11 |  | 47 | 1 | 8407420 | 9603880 | 1196460 | 1 |  | 1196460 | 1209136.6977 | Banosree |  |  |  | Larive | 1209136.6977 | 1154817.1834 | 54319.5143 | 4.7037 | OK
8 | Bank Colony | 11 |  |  | 1 | 3914160 | 4697520 | 783360 | 1 |  | 783360 | 791659.8328 | Khilgaon |  |  |  | Bank Colony | 791659.8328 | 743707.201 | 47952.6318 | 6.4478 | OK
9 | Salambagh | 11 |  |  | 1 | 2367500 | 3153240 | 785740 | 1 |  | 785740 | 794065.0493 | Khilgaon |  |  |  | Salambagh | 794065.0493 | 937481.2326 | -143416.1833 | -15.298 | OK
10 | Titas Road | 11 |  |  | 1 | 1963420 | 2347080 | 383660 | 1 |  | 383660 | 387724.9431 | Khilgaon |  |  |  | Titas Road | 387724.9431 | 442215.7606 | -54490.8175 | -12.3222 | OK
11 | AT-1 | 0.415 |  | 7734 | 1 | 3257.088 | 3332.3 | 75.212 | 1 |  | 75.212 | 76.0089 | Banosree |  |  |  | AT-1 | 76.0089 | 145.5702 | -69.5613 | -47.7854 | CHECK
12 | AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 15295979.6361 | 15135615.212 | 15295979.6361 | 1.0595
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 13322529.811
[5 empty] | Khilgaon | at 33 KV level |  | 1973449.8252
[5 empty] | Total = |  |  | 15295979.6361 | 0
1: 33 KV SIDE of___GORAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MADERTEK 33 KV SIDE
1 | Goran | 33 | Export | SIEM0510 | 1 | 344806 | 349987 | 5181 | 2000 | 0 | 10362000 | 10356569.589
ULLON 33 KV SIDE
1 | Goran | 33 | Export | BD001819 | 1 | 2.305 | 2.305 | 0 | 240000 | 0 | 0 | 0
10: Total | 0 | 10362000 | 10356569.589
GORAN 33 KV SIDE (RECEIVING)
1 | Madertek Circuit-01 | 33 | Import | HA-030701133-03 | 1 | 98517711 | 108926360 | 10408649 | 1 | 10408649
2 | Ullon O/H | 33 | Import | HA-030800195-03 | 1 | 49598106 | 49598106 | 0 | 1 | 0
7: 0; 8: 0; 10: Total | 10408649 | 0 | 0
| GORAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| GORAN 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transformer-01 | 33 | Export | HA-030800176-03 | 1 | 12308534 | 15424360 | 3115826 | 1 |  | 3115826
2 | Transformer-02 | 33 | Export | HA-030701133-03 | 1 | 78054579 | 81116710 | 3062131 | 1 |  | 3062131
3 | Transformer-03 | 33 | Export | DHK-57075 | 1 | 11600.76 | 11776.31 | 175.55 | 120000 |  | 4184043 |  |  | Problem
10: Total |  | 10362000
2: 33 KV IMPORT; 4: KWH; 6: 33 KV IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: MADERTEK 33 KV SIDE; 4: 10356569.589; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10356569.589
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 10356569.589 | 33 KV TX HV SIDE |  | 10362000
2: IMPORT-3 | LOSS UNITS=> |  | -5430.411
2: IMPORT-4 | LOSS % IN => |  | -0.05243%
| TOTAL IMPORT |  | 10356569.589
1: 11 KV SIDE of___GORAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GORAN 11 KV SIDE
| 33/11 kV Transfomer-1 Incoming | 11 | IMPORT |  | 1 | 52909528 | 56020760 | 3111232 | 1 | 3111232 |  | 3108939.925
| 33/11 kV Transfomer-2 Incoming | 11 |  |  | 1 | 85589016 | 88643160 | 3054144 | 1 | 3054144 |  | 3051893.9823
| 33/11 kV Transfomer-3 Incoming | 11 |  |  | 1 | 67657591 | 71856420 | 4198829 | 1 | 4198829 |  | 4195735.6817
7: 0; 8: 0; 10: Total | 10364205 |  | 10356569.589
| GORAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | Meradia | 11 |  | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | Meradia | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Shipahibagh | 11 |  | HA-021001030-02 | 1 | 36289191 | 37940830 | 1651639 | 1 |  | 1651639 | 1654071.9922 | Bashabo |  |  |  | Shipahibagh | 1654071.9922 | 1292900.8718 | 361171.1204 | 27.9349 | OK
3 | Farazi Hospital | 11 |  | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 |  | 0 | 0 | Banosree |  |  |  | Farazi Hospital | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | West Bansree | 11 |  | New Meter | 1 | 91131594 | 93104250 | 1972656 | 1 |  | 1972656 | 1975561.8751 | Banosree |  |  |  | West Bansree | 1975561.8751 | 1966878.4605 | 8683.4146 | 0.44148 | OK
5 | Model School(Nearest) | 11 |  | HA-030701099-03 | 1 | 15066081 | 17587620 | 2521539 | 1 |  | 2521539 | 2525253.4223 | Banosree |  |  |  | Model School(Nearest) | 2525253.4223 | 2475694.1412 | 49559.2811 | 2.0018 | OK
6 | Bhuiyan Para | 11 |  | HA-021100508-02 | 1 | 53101375 | 55705410 | 2604035 | 1 |  | 2604035 | 2607870.9453 | Banosree |  |  |  | Bhuiyan Para | 2607870.9453 | 2554505.4549 | 53365.4904 | 2.0891 | OK
7 | Bonobithi (Ideal) School | 11 |  | HA-021100879-02 | 1 | 14133451 | 15718670 | 1585219 | 1 |  | 1585219 | 1587554.1504 | Banosree |  |  |  | Bonobithi (Ideal) School | 1587554.1504 | 1568260.1835 | 19293.9669 | 1.2303 | OK
8 | AT-01 | 0.415 |  | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 |  | 0 | 0 | Banosree |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-02 | 0.415 |  | 3043146 | 1 | 4704.4 | 4782.5 | 78.1 | 80 |  | 6248 | 6257.2038 | Banosree |  |  |  | AT-02 | 6257.2038 | 5424.4075 | 832.7963 | 15.3528 | OK
10: Grand Total | 10356569.589 | 10341336 | 10356569.589 | 0.14731
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Banosree | at 33 KV level |  | 8702497.5968
[5 empty] | Bashabo | at 33 KV level |  | 1654071.9922
[5 empty] | Total = |  |  | 10356569.589 | 0
1: 33 KV SIDE of___ LALMATIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE
8 | Lalmatia Circuit-2 | 33 | 0 | SICAM | 1 | 82.53 | 105.9 | 23.37 | 1000 | Estimated | 14625630 | 14559556.8645
10: Total |  | 14625630 | 14559556.8645
Lalmatia 33 KV SIDE (RECEIVING)
1 | Shatmasjid-1 | 33 | Import |  | 1 |  |  | 0 |  | 0
2 | Shatmasjid-2 | 33 | Import |  | 1 |  |  | 0 |  | 0
3 | Kallayanpur | 33 | Import | G005323170 | 1 |  |  | 0 |  | 0
10: Total | 0 | 0 | 0
Lalmatia 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
Lalmatia 33 KV X_F SIDE
1 | Transformer-01 | 33 | Export | DHK 00164 | 1 |  |  | 0 | 10000 |  | 0
2 | Transformer-02 | 33 | Export | DHK 00179 | 1 |  |  | 0 | 10000 |  | 0
10: Total |  | 0 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 33 KV Sending SIDE; 4: 14559556.8645; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | LALMATIA 33 KV NET IMPORT |  | 14559556.8645
2: IMPORT-2; 6: LALMATIA 33 KV NET IMPORT; 9=8-7: 14559556.8645 | LALMATIA 11 KV NET IMPORT |  | 14625630
2: IMPORT-3 | LOSS UNITS=> |  | -66073.1355
2: IMPORT-4 | LOSS % IN => |  | -0.4538%
| TOTAL IMPORT |  | 14559556.8645
1: 11 KV SIDE of___LALMATIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: Lalmatia 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Transformer-1 Incoming | 11 | Import | DHK000180 | 1 | 2720296 | 2789889 | 69593 | 90 | 6263370 | [9 empty] | 0 | #DIV/0! | #DIV/0!
2 | Transformer-2 Incoming | 11 | Import | DHK000177 | 1 | 2698105 | 2791019 | 92914 | 90 | 8362260 | [9 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 14625630 |  | 0 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: Lalmatia 11 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
1 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 138 | 1678533.192 | 1695740.7049 | Dhanmondi | Estimated |  |  | Shankor O/H | 1695740.7049 | 1418643.1678 | 277097.537 | 19.5326 | OK
2 | Bangabobondhu museum | 11 | Export |  | 1 | 627449 | 627449 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Bangabobondhu museum | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | Road No-13/A | 11 | Export | 202006950 | 1 | 78185685 | 80492544 | 2306859 | 1 |  | 2306859 | 2330507.8061 | Dhanmondi |  |  |  | Road No-13/A | 2330507.8061 | 2062161.6863 | 268346.1197 | 13.0129 | OK
4 | Jaforabad | 11 | Export | DHK00163 | 1 | 99151250 | 100978738 | 1827488 | 1 |  | 1827488 | 1846222.5257 | Dhanmondi |  |  |  | Jaforabad | 1846222.5257 | 2324395.3174 | -478172.7917 | -20.5719 | OK
5 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Dhanmondi |  |  |  | Asadgate U/G | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25444.9 | 25639.6 | 194.7 | 3333.33 |  | 648999.351 | 655652.5794 | Dhanmondi |  |  |  | Road 32 ( Lalmatia 11 kV S/S) | 655652.5794 | 676925.663 | -21273.0836 | -3.1426 | OK
1 | Road No -15 | 11 | Export | DHK00162 | 1 | 69354.4 | 69712.4 | 358 | 3333.33 |  | 1193332.14 | 1205565.6057 | Dhanmondi |  |  |  | Road No -15 | 1205565.6057 | 1637075.4163 | -431509.8107 | -26.3586 | OK
2 | Road No-27 South | 11 | Export | DHK00161 | 1 | 77227.8 | 77687.3 | 459.5 | 3333.33 |  | 1531665.135 | 1547367.0274 | Dhanmondi |  |  |  | Road No-27 South | 1547367.0274 | 1547019.5294 | 347.4979 | 0.022462 | OK
| Road 25 | 11 | Export |  | 1 | 69810.6 | 70235.1 | 424.5 | 3333.3 |  | 1414985.85 | 1429491.6026 | Dhanmondi |  |  |  | Road 25 | 1429491.6026 | 1320696.1949 | 108795.4077 | 8.2377 | OK
3 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37703.6 | 37836.9 | 133.3 | 3333.33 |  | 444332.889 | 448887.9755 | Dhanmondi |  |  |  | Ibne Sina | 448887.9755 | 428853.4986 | 20034.4769 | 4.6716 | OK
4 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 59045605 | 60236116 | 1190511 | 1 |  | 1190511 | 1202715.5447 | Dhanmondi |  |  |  | Road No-31 (PARI) | 1202715.5447 | 1761856.4725 | -559140.9278 | -31.7359 | OK
5 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 67161693 | 69402203 | 2240510 | 1 |  | 2240510 | 2263478.6281 | Dhanmondi |  |  |  | Satmoszid Road West | 2263478.6281 | 2215613.0537 | 47865.5744 | 2.1604 | OK
10: Grand Total | 14625630 | 14477216.557 | 14625630 | 1.0252
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Dhanmondi | at 33 KV level |  | 14625630
[5 empty] | Total = |  |  | 14625630 | 0
Green Road 33/11KV, 2x 20/28 MVA Substation. Phone No. 58616194 ( North 2)
1: 33 KV SIDE of___GREEN ROAD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Dhanmondi (33 KV Side)
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2059.78 | 2087.7 | 27.92 | 240000 | 0 | 6700800 | 6704631.8438
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1379.43 | 1411.09 | 31.66 | 240000 | 0 | 7598400 | 7602745.1352
10: Total | 0 | 14299200 | 14307376.979
Green Road 33 KV SIDE (RECEIVING)
| 33KV Dhanmondi 1 | 33 |  |  | 1 | 0 | 0 | 0 | 3000 |  | 0
| 33KV Dhanmondi 2 | 33 |  |  | 1 | 0 | 0 | 0 | 3000
10: Total | 0 | 0 | 0
Green Road 33 KV SIDE (EXPORT TO OTHER S/S)
2: Green Road Dormatory; 3: 33; 4: EXPORT |  | 0
2: Green Road Dormatory; 3: 33 |  | 0
Total
Green Road 33 KV X-F SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 | 51025.7 | 51025.7 | 0 | 3000 |  | 0 | 0
| 33/11 KV Transformer No.2. | 33 |  |  | 1 | 94339.4 | 94339.4 | 0 | 3000 |  | 0 | 0
10: Total |  | 0 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Dhanmondi (33 KV Side); 4: 14307376.979; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | Green Road 33 KV NET IMPORT |  | 14307376.979
2: IMPORT-2; 6: Green Road 33 KV NET IMPORT; 9=8-7: 14307376.979 | Green Road 11 KV NET IMPORT |  | 14307376.979
2: IMPORT-3; 6: TOTAL EXPORT; 9=8-7: 14307376.979 | LOSS UNITS=> |  | 0
2: IMPORT-4; 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 14307376.979
1: 11 KV SIDE of___GREEN ROAD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Green Road 11 KV X-F SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 00138 | 1 | 2939427 | 3023673 | 84246 | 100 | 8424600
2 | Transfomer-2 Incoming | 11 | Import | HA-021101496 | 1 | 2649.9952 | 3394.4208 | 744.4256 | 10000 | 6700800
7: 0; 8: 0; 10: Total | 15125400 |  | 14307376.979
| Green Road 11 KV SIDE |  |  |  |  | 0 | 0
1 | Lab aid/local RMU | 11 |  | 3C65883 | 1 | 54004 | 59173 | 5169 | 300 |  | 1550700 | 1556841.7376 | Paribag |  |  |  | Lab aid/local RMU | 1556841.7376 | 1536617.643 | 20224.0945 | 1.3161 | OK
2 | Green View | 11 |  | DHK000151 | 1 | 66871.1 | 67239.7 | 368.6 | 3333.33 |  | 1228665.438 | 1233531.7182 | Paribag |  |  |  | Green View | 1233531.7182 | 1202336.4681 | 31195.2501 | 2.5946 | OK
3 | Central Road | 11 |  | 65943 | 1 | 15582 | 21383 | 5801 | 300 |  | 1740300 | 1747192.6716 | Paribag |  |  |  | Central Road | 1747192.6716 | 1761466.4931 | -14273.8214 | -0.81034 | OK
4 | New Market | 11 |  | DHK000194 | 1 | 46255.4 | 46585.3 | 329.9 | 3333.33 |  | 1099665.567 | 1104020.9274 | Jigatola |  |  |  | New Market | 1104020.9274 | 1190965.2748 | -86944.3474 | -7.3003 | OK
5 | DPH Feeder | 11 |  | HA-021100459 | 1 | 41476.6 | 41611.3 | 134.7 | 1 | 20 | 243265.68 | 244229.1636 | Paribag | Estimated |  |  | DPH Feeder | 244229.1636 | 236205.0715 | 8024.0921 | 3.3971 | OK
6 | Dhanmondi Rd 4(md Banglo | 11 |  | 6604464 | 1 | 4476.72 | 4502.72 | 26 | 60000 |  | 1560000 | 1566178.5714 | Jigatola |  |  |  | Dhanmondi Rd 4(md Banglo | 1566178.5714 | 1573640.9477 | -7462.3763 | -0.47421 | OK
1 | Green Road East | 11 |  | HA-021101050 | 1 | 93757224 | 95327346 | 1570122 | 1 |  | 1570122 | 1576340.6608 | Paribag |  |  |  | Green Road East | 1576340.6608 | 1533242.4019 | 43098.2589 | 2.8109 | OK
2 | North Road | 11 |  | HA-021100884 | 1 | 78525314 | 80273857 | 1748543 | 1 |  | 1748543 | 1755468.3191 | Paribag |  |  |  | North Road | 1755468.3191 | 1721328.8161 | 34139.5029 | 1.9833 | OK
3 | Green road SS | 11 |  | DHK00135 | 1 | 17244056 | 18489919 | 1245863 | 1 |  | 1245863 | 1250797.3933 | Paribag |  |  |  | Green road SS | 1250797.3933 | 1224610.5159 | 26186.8774 | 2.1384 | OK
4 | Plane Moszid | 11 |  | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 80 | 973062.72 | 976916.6543 | Paribag | Estimated |  |  | Plane Moszid | 976916.6543 | 944820.2858 | 32096.3684 | 3.3971 | OK
5 | Malancha | 11 |  | HA-021100953 | 1 | 31976092 | 33261839 | 1285747 | 1 |  | 1285747 | 1290839.3587 | Paribag |  |  |  | Malancha | 1290839.3587 | 1378192.0129 | -87352.6541 | -6.3382 | OK
2: AT -1; 7: 22891; 8: 22891; 10: 1 |  | 5000 | 5019.8031 | Paribag |  |  |  | AT -1 | 5019.8031 | 5016.7079 | 3.0952 | 0.061697 | OK
10: Grand Total | 14307376.979 | 14250934.405 | 14307376.979 | 0.39606
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 11637177.4802
[5 empty] | Jigatola | at 33 KV level |  | 2670199.4988
[5 empty] | Total = |  |  | 14307376.979 | 0
1: 33 KV SIDE of___ GREEN ROAD DORMITORY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MOGBAZAR 33 KV SIDE
13 | 33 kV Green Road Dormitory | 33 | 0 | 76026305 | 1 | 8019.59 | 8045.2 | 25.61 | 180000 | Reading From G. Dormitory Side | 9207760 | 9269973.1514
10: Total | 0 | 9207760 | 9269973.1514
NEW JIGATOLA 33 KV SIDE
4 | Green Road -1 | 33 | 0 | 0 | 1 | 23.2 | 23.42 | 0.22 | 360000 | 0 | 79200 | 79010.5381
9 | Green Road -2 | 33 | 0 | 0 | 1 | 23.22 | 37.21 | 13.99 | 360000 | 0 | 5036400 | 5024351.9481
10: Total | 0 | 5115600 | 5103362.4862
2: GREEN ROAD DORMITORY 33 KV SIDE (RECEIVING) |  | 14323360 | 14373335.6376
1 | Mogbazar Grid | 33 | Import | BD 017064 | 1 | 24188.38 | 33396.14 | 9207.76 | 1000 | 9207760
2 | Green Road SS | 33 | Import | BD 017070 | 1 | 32911.2 | 32911.2 | 0 | 1000 | 0
3 | Jigatola Ckt-1 | 33 | Import |  | 1 | 8292.49 | 8369.32 | 76.83 | 1000 | 76830
NEW | Jigatola Ckt-2 | 33 |  |  | 1 | 8339.09 | 13367.86 | 5028.77 | 1000 | 5028770 |  |  |  | NEW FOUND
7: 0; 8: 0; 10: Total | 14313360 | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| GREEN ROAD DORMITORY 33 KV SIDE |  |  |  |  | 0 | 0
1 | Transformer-01 | 33 | Export | BD 017065 | 1 | 108288.53 | 108288.53 | 0 | 888.89 |  | 0
2 | Transformer-02 | 33 | Export | BD 017069 | 1 | 94422.74 | 100094.22 | 5671.48 | 888.89 |  | 5041321.8572
10: Total |  | 5041321.8572 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MOGBAZAR 33 KV SIDE; 4: 14373335.6376; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | GREEN ROAD DORMITORY 33 KV NET IMPORT |  | 14373335.6376
6: GREEN ROAD DORMITORY 33 KV NET IMPORT; 9=8-7: 14373335.6376 | GREEN ROAD DORMITORY 11 KV NET IMPORT |  | 14373335.6376
6: TOTAL EXPORT; 9=8-7: 14373335.6376 | LOSS UNITS=> |  | 0
6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 14373335.6376
1: 11 KV SIDE of___GREEN ROAD DORMITORY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
GREEN ROAD DORMITORY 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD 014050 | 1 | 72549.81 | 81822.15 | 9272.34 | 1000 | 9272340
2 | Transformer-02 Incoming | 11 | Import | BD 014059 | 1 | 71630.36 | 76642.86 | 5012.5 | 1000 | 5012500
7: 0; 8: 0; 10: Total | 14284840 |  | 14373335.6376
| GREEN ROAD DORMITORY 11 KV SIDE |  |  |  |  | 0 | 0
1 | North Dhanmondi | 11 |  | BD 014039 | 1 | 21956.7 | 22196.95 | 240.25 | 2000 |  | 480500 | 484039.8994 | Paribag |  |  |  | North Dhanmondi | 484039.8994 | 504079.3978 | -20039.4984 | -3.9755 | OK
2 | Lake circus | 11 |  | BD 014047 | 1 | 34637.48 | 35647.16 | 1009.68 | 2000 |  | 2019360 | 2034236.8602 | Paribag |  |  |  | Lake circus | 2034236.8602 | 2046787.3073 | -12550.4471 | -0.61318 | OK
3 | Bashir Uddin | 11 |  | BD 014037 | 1 | 14070.93 | 14464.14 | 393.21 | 2000 |  | 786420 | 792213.6477 | Paribag |  |  |  | Bashir Uddin | 792213.6477 | 798302.5936 | -6088.9459 | -0.76274 | OK
4 | Raza Bazar | 11 |  | BD 013939 | 1 | 20615.43 | 21277.2 | 661.77 | 2000 |  | 1323540 | 1333290.6732 | Shere b.nagar |  |  |  | Raza Bazar | 1333290.6732 | 1329360.3858 | 3930.2874 | 0.29565 | OK
5 | Rasel Squar | 11 |  | BD 013970 | 1 | 31411.16 | 32377.3 | 966.14 | 2000 |  | 1932280 | 1946515.3317 | Shere b.nagar |  |  |  | Rasel Squar | 1946515.3317 | 1986224.7792 | -39709.4475 | -1.9992 | OK
6 | Bow Bazar | 11 |  | BD 013967 | 1 | 23561.5 | 24214.38 | 652.88 | 2000 |  | 1305760 | 1315379.6859 | Shere b.nagar |  |  |  | Bow Bazar | 1315379.6859 | 1361417.0663 | -46037.3804 | -3.3816 | OK
7 | BRB Hospital | 11 |  | BD 014003 | 1 | 12424.41 | 12842.2 | 417.79 | 2000 |  | 835580 | 841735.8151 | Shere b.nagar |  |  |  | BRB Hospital | 841735.8151 | 735319.9448 | 106415.8703 | 14.4721 | OK
8 | Green Road North | 11 |  | BD 013969 | 1 | 14760.23 | 15378.01 | 617.78 | 2000 |  | 1235560 | 1244662.5143 | Paribag |  |  |  | Green Road North | 1244662.5143 | 1225136.5003 | 19526.0141 | 1.5938 | OK
1 | Water Bhaban | 11 |  | BD 014004 | 1 | 4898.2 | 5081.77 | 183.57 | 2000 |  | 367140 | 369844.7631 | Shere b.nagar |  |  |  | Water Bhaban | 369844.7631 | 332111.9703 | 37732.7928 | 11.3615 | OK
2 | Alamin Road | 11 |  | BD 014006 | 1 | 18211.68 | 18531.9 | 320.22 | 2000 |  | 640440 | 645158.196 | Paribag |  |  |  | Alamin Road | 645158.196 | 644406.723 | 751.4731 | 0.11661 | OK
3 | Katal Bagan | 11 |  |  | 1 | 6635.26 | 7743.31 | 1108.05 | 2000 |  | 2216100 | 2232426.2667 | Paribag |  |  |  | Katal Bagan | 2232426.2667 | 2461917.3517 | -229491.085 | -9.3216 | OK
4 | Eastern Pantho chaya | 11 |  | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 |  | 0 | 0 | Paribag |  |  |  | Eastern Pantho chaya | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Kalabagan | 11 |  | BD 014005 | 1 | 5575.77 | 5746.51 | 170.74 | 2000 |  | 341480 | 343995.7229 | Paribag |  |  |  | Kalabagan | 343995.7229 | 360201.2398 | -16205.5169 | -4.499 | OK
6 | Univer Hospital | 11 |  | BD 013963 | 1 | 745.38 | 885.22 | 139.84 | 2000 |  | 279680 | 281740.4351 | Paribag |  |  |  | Univer Hospital | 281740.4351 | 275219.2974 | 6521.1378 | 2.3694 | OK
7 | Green Road Staff Quarter(Anowar Khan Medical) | 11 |  | BD 013971 | 1 | 9523.65 | 9775.84 | 252.19 | 2000 |  | 504380 | 508095.8262 | Paribag |  |  |  | Green Road Staff Quarter(Anowar Khan Medical) | 508095.8262 | 507213.6524 | 882.1737 | 0.17393 | OK
10: Grand Total | 14373335.6376 | 14268220 | 14373335.6376 | 0.73671
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Paribag | at 33 KV level |  | 8566569.3685
[5 empty] | Shere b.nagar | at 33 KV level |  | 5806766.2691
[5 empty] | Total = |  |  | 14373335.6376 | 0
1: 33 KV SIDE of___TALTOLA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
ULLON 33 KV SIDE
2 | Taltala-1 | 33 | Export | BD001906 | 1 | 1533.8259 | 1564.8785 | 31.0526 | 240000 | 0 | 7452624 | 7471725.0456
2 | Taltala-2 | 33 |  | BD001837 | 1 | 2495.751 | 2529.1788 | 33.4278 | 240000 | 0 | 8022672 | 8043234.0764
10: Total | 0 | 15475296 | 15514959.122
TALTOLA 33 KV SIDE (RECEIVING)
| 33 KV Ullon-ckt-1 incoming | 33 | RECEIVE |  | 1 |  |  | 0 | 1000 | 0 | 0
2: 33 KV Ullon-ckt-2 incoming; 3: 33; 6: 1; 9=8-7: 0; 10: 1000 | 0 | 0
10: Total | 0 | 0 | 15514959.122
TALTOLA 33 KV SIDE (EXPORT TO OTHER S/S)
2: 33 KV Kakrail Feeder.(import); 3: 33; 4: EXPORT |  | 0
2: 33 KV Khilgaon Feeder(Import); 3: 33 |  | 0
10: Total |  | 0
TALTOLA 33 KV SIDE
| 33/11 KV Transformer No.1. | 33 | NET IMPORT |  | 1 |  |  | 0 | 180 |  | 0 | 0
2: 33/11 KV Transformer No.2.; 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
2: 33/11 KV Transformer No.2.; 3: 33; 6: 1; 9=8-7: 0; 10: 180 |  | 0 | 0
10: Total |  | 0 | 15514959.122 | #DIV/0!
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: ULLON 33 KV SIDE; 4: 15514959.122; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | TALTOLA 33 KV NET IMPORT |  | 15514959.122
2: IMPORT-2; 6: TALTOLA 33 KV NET IMPORT; 9=8-7: 15514959.122 | TALTOLA 11 KV NET IMPORT |  | 15514959.122
2: IMPORT-3; 6: TOTAL EXPORT; 9=8-7: 15514959.122 | LOSS UNITS=> |  | 0
2: IMPORT-4; 6: 33 KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 15514959.122
1: 11 KV SIDE of___TALTOLA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
TALTOLA 11 KV SIDE
1 | Transformer-1 Incoming | 11 | Import | 06604431 | 1 | 8505.82 | 8555.67 | 49.85 | 160000 | 7976000
2 | Transformer-02 Incoming | 11 | Import | 06604341 | 1 | 9219.12 | 9269.53 | 50.41 | 160000 | 8065600
3 | Transformer-03 Incoming | 11 | Import | 0211001039-02 | 1 | 98491641 | 98491641 | 0 | 1 | 0
7: 0; 8: 0; 10: Total | 16041600 |  | 15514959.122
| TALTOLA 11 KV SIDE |  |  |  |  | 0 | 0
1 | Matir Masjid | 11 |  | DHK00170 | 1 | 20154.5 | 22583.2 | 2428.7 | 888.8889 |  | 2158844.4444 | 2167154.5553 | Khilgaon |  |  |  | Matir Masjid | 2167154.5553 | 2177028.2382 | -9873.6829 | -0.45354 | OK
2 | Hajipara | 11 |  | DHK-00108 | 1 | 2631.3 | 3643.3 | 1012 | 2222.2222 |  | 2248888.8889 | 2257545.6108 | Khilgaon |  |  |  | Hajipara | 2257545.6108 | 2323390.6234 | -65845.0125 | -2.834 | OK
3 | Nearest Feeder | 11 |  | DHK-00106 | 1 | 90788.1 | 90788.1 | 0 | 2222.222 |  | 0 | 0 | Bashabo |  |  |  | Nearest Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Reazbagh | 11 |  | DHK-00109 | 1 | 95125.7 | 95946.5 | 820.8 | 2222.222 |  | 1823999.8176 | 1831021.0001 | Khilgaon |  |  |  | Reazbagh | 1831021.0001 | 1850181.9906 | -19160.9905 | -1.0356 | OK
5 | Chowdhury Para | 11 |  | DHK-00107 | 1 | 52175.6 | 52456 | 280.4 | 2222.222 |  | 623111.0488 | 625509.6106 | Khilgaon |  |  |  | Chowdhury Para | 625509.6106 | 653692.0598 | -28182.4491 | -4.3113 | OK
6 | Model Colleg | 11 |  | 9122392 | 1 | 2474.25 | 2506.21 | 31.96 | 40000 |  | 1278400 | 1283320.9871 | Khilgaon |  |  |  | Model Colleg | 1283320.9871 | 723685.6707 | 559635.3165 | 77.3313 | FAULT
1 | East Rampura | 11 |  | DHK-00181 | 1 | 97687.4 | 98303.2 | 615.8 | 2222.222 |  | 1368444.3076 | 1373711.9053 | Khilgaon |  |  |  | East Rampura | 1373711.9053 | 1177184.4648 | 196527.4405 | 16.6947 | OK
2 | Adarshabagh | 11 |  | DHK-00090 | 1 | 48490.9 | 49532.6 | 1041.7 | 2222.222 |  | 2314888.6574 | 2323799.4344 | Bashabo |  |  |  | Adarshabagh | 2323799.4344 | 2249760.2414 | 74039.193 | 3.291 | OK
3 | Khailgaon Govt Colony | 11 |  | DHK00167 | 1 | 74331.4 | 75071.6 | 740.2 | 2222.222 |  | 1644888.7244 | 1651220.4486 | Khilgaon |  |  |  | Khailgaon Govt Colony | 1651220.4486 | 1644511.4325 | 6709.0161 | 0.40796 | OK
4 | TV Road | 11 |  | 6604434 | 1 | 5034.04 | 5070.34 | 36.3 | 40000 |  | 1452000 | 1457589.2313 | Khilgaon |  |  |  | TV Road | 1457589.2313 | 1435653.3713 | 21935.8601 | 1.5279 | OK
5 | Tilpa Para | 11 |  | 06604476 | 1 | 6549.26 | 6562.81 | 13.55 | 40000 |  | 542000 | 544086.3384 | Bashabo |  |  |  | Tilpa Para | 544086.3384 | 925315.57 | -381229.2316 | -41.1999 | CHECK
1 | Navana | 11 |  | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Navana | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Shantipur | 11 |  | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 |  | 0 | 0 | Bashabo |  |  |  | Shantipur | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | AT-01 | 0.415 |  | 9187958 | 1 | 288.03 | 288.03 | 0 | 80 |  | 0 | 0 | Bashabo |  |  |  | AT-01 | 0 | 388.7134 | -388.7134 | -100 | CHECK
3 | AT-02 | 0.415 |  | 9187959 | 1 | 123.08 | 123.08 | 0 | 10 |  | 0 | 0 | Bashabo |  |  |  | AT-02 | 0 | 1243.317 | -1243.317 | -100 | CHECK
10: Grand Total | 15514959.122 | 15455465.8891 | 15514959.122 | 0.38493
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Khilgaon | at 33 KV level |  | 12647073.3492
[5 empty] | Bashabo | at 33 KV level |  | 2867885.7728
[5 empty] | Total = |  |  | 15514959.122 | 0
1: 33 KV SIDE of___ SHER-E-BANGLANAGAR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
33 KV Sending SIDE (Tariff Point)
1 | Sher-e-Banglanagar Ckt-01 | 33 | Import | 35786569 | 1.0008 | 1885.528 | 1910.455 | 24.927 | 180000 | 0 | 4490336.4191
2 | Sher-e-Banglanagar Ckt-02 | 33 | Import | 35786575 | 1.0008 | 646.365 | 663.099 | 16.734 | 180000 | 0 | 3014453.7906
10: Total | 0 | 7504790.2097 | 0
10: Net Total | 7504790.2097
SHER-E-BANGLANAGAR 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | DHK 66505 | 1 |  |  | 0 | 540 | 0
2 | Agargaon Ckt-02 | 33 | Import | DHK 66507 | 1 | 222118 | 222118 | 0 | 540 | 0
10: Total | 0 | 0 | 0
SHER-E-BANGLANAGAR 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 33; 4: EXPORT |  | 0
2: Feeder No.2; 3: 33 |  | 0
10: Total |  | 0
SHER-E-BANGLANAGAR 33 KV SIDE
3 | Transformer-01 | 33 | Export | DHK 66510 | 1 | 0 | 0 | 0 | 180 |  | 0
4 | Transformer-02 | 33 | Export | DHK 66500 | 1 | 712641 | 729434.44 | 16793.44 | 180 |  | 3022819.2
10: Total |  | 3022819.2 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: 33 KV Sending SIDE (Tariff Point); 4: 7504790.2097; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | SHER-E-BANGLANAGAR 33 KV NET IMPORT |  | 7504790.2097
2: IMPORT-2; 6: SHER-E-BANGLANAGAR 33 KV NET IMPORT; 9=8-7: 7504790.2097 | 33 KV TX HV SIDE |  | 7504790.2097
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7504790.2097
1: 11 KV SIDE of___SHER-E-BANGLANAGAR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
SHER-E-BANGLANAGAR 11 KV SIDE
1 | Transfomer-1 Incoming | 11 | Import | DHK 66503 | 1 | 2157894 | 2183030 | 25136 | 180 | 4524480 |  | 4489941.6078
2 | Transfomer-2 Incoming | 11 | Import | DHK 66495 | 1 | 694894 | 711772 | 16878 | 180 | 3038040 |  | 3014848.6019
7: 0; 8: 0; 10: Total | 7562520 |  | 7504790.2097
| SHER-E-BANGLANAGAR 11 KV SIDE |  |  |  |  | 0 | 0
1 | Sher-e-Banglanagar Local | 11 |  | DHK 66503 | 1 | 76044 | 78207 | 2163 | 60 |  | 129780 | 127632.9783 | Shere b.nagar |  |  |  | Sher-e-Banglanagar Local | 127632.9783 | 130259.0089 | -2626.0306 | -2.016 | OK
2 | Mirpur Road East | 11 |  | DHK 60961 | 1 | 815519 | 825101 | 9582 | 60 |  | 574920 | 565408.7832 | Shere b.nagar |  |  |  | Mirpur Road East | 565408.7832 | 579726.769 | -14317.9859 | -2.4698 | OK
3 | Gonobhaban school | 11 |  | DHK 66492 | 1 | 523059 | 526229 | 3170 | 60 |  | 190200 | 187053.4171 | Shere b.nagar |  |  |  | Gonobhaban school | 187053.4171 | 201293.1928 | -14239.7757 | -7.0741 | OK
4 | Babor Road | 11 |  | DHK 66489 | 1 | 727817 | 741733 | 13916 | 60 |  | 834960 | 821146.7988 | Shyamoli |  |  |  | Babor Road | 821146.7988 | 2355047.2749 | -1533900.4761 | -65.1325 | CHECK
5 | College Gate | 11 |  | DHK 66487 | 1 | 2587196 | 2623105 | 35909 | 60 |  | 2154540 | 2118896.2632 | Shyamoli |  |  |  | College Gate | 2118896.2632 | 2029429.4244 | 89466.8388 | 4.4085 | OK
6 | Parade ground | 11 |  | DHK 66490 | 1 | 938247 | 938265 | 18 | 60 |  | 1080 | 1062.133 | Satmasjid |  |  |  | Parade ground | 1062.133 | 1780.3054 | -718.1724 | -40.3398 | CHECK
7 | Hospital RMU | 11 |  | DHK 66491 | 1 | 882954 | 893230 | 10276 | 60 |  | 616560 | 606359.9098 | Shere b.nagar |  |  |  | Hospital RMU | 606359.9098 | 560499.4711 | 45860.4387 | 8.1821 | OK
1 | Shamoly Square | 11 |  | DHK 61065 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 | Shyamoli |  |  |  | Shamoly Square | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Gonobhaban RMU | 11 |  | DHK 60964 | 1 | 191126.8 | 192801.1 | 1674.3 | 60 |  | 100458 | 98796.0682 | Shere b.nagar |  |  |  | Gonobhaban RMU | 98796.0682 | 102753.2911 | -3957.2229 | -3.8512 | OK
3 | Krishi University | 11 |  | DHK 60963 | 1 | 340100.1 | 350091.4 | 9991.3 | 60 |  | 599478 | 589560.5067 | Shere b.nagar |  |  |  | Krishi University | 589560.5067 | 563852.3796 | 25708.1271 | 4.5594 | OK
4 | NEC | 11 |  | DHK 86073 | 1 | 29.93 | 34.66 | 4.73 | 60000 |  | 283800 | 279104.941 | Shere b.nagar |  |  |  | NEC | 279104.941 | 274760.4607 | 4344.4803 | 1.5812 | OK
5 | Novo Theater/Army Musium | 11 |  | DHK 86074 | 1 | 342.41 | 362.71 | 20.3 | 60000 |  | 1218000 | 1197849.958 | Tejgaon+Shereb.nagar |  |  |  | Novo Theater/Army Musium | 1197849.958 | 1139395.431 | 58454.5271 | 5.1303 | OK
6 | Netor | 11 |  | DHK 60962 | 1 | 103402.9 | 114054.4 | 10651.5 | 60 |  | 639090 | 628517.1836 | Shere b.nagar |  |  |  | Netor | 628517.1836 | 620062.5542 | 8454.6295 | 1.3635 | OK
7 | BICC | 11 |  |  | 1 | 29.93 | 34.66 | 4.73 | 60000 |  | 283800 | 279104.941 | Shere b.nagar |  |  |  | BICC | 279104.941 | 193459.8492 | 85645.0917 | 44.2702 | FAULT
8 | Auxiliary | 0.415 |  |  | 1 | 5156.09 | 5228.9 | 72.81 | 60 |  | 4368.6 | 4296.3279 | Shere b.nagar |  |  |  | Auxiliary | 4296.3279 | 3895.3081 | 401.0197 | 10.2949 | OK
10: Grand Total | 7504790.2097 | 7631034.6 | 7504790.2097 | -1.6544
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 3856953.5395 | Including 41% of Novo Theatre
[5 empty] | Shyamoli | at 33 KV level |  | 2940043.062
[5 empty] | Satmasjid | at 33 KV level |  | 1062.133
[5 empty] | Tejgaon | at 33 KV level |  | 706731.4752 | 59% of Novo Theatre
[5 empty] | Total = |  |  | 7504790.2097 | 0
1: 33 KV SIDE of___ MUGDAPARA HOSPITAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MANKNAGAR 33 KV SIDE
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 10136608 | 10222414.2142
6 | 33kV Mugdapara Hospital-2 Feeder | 33 |  | ABB03918 | 1 | 292711 | 297786 | 5075 | 2000 | 0 | 10150000 | 10235919.5773
10: Total | 0 | 20286608 | 20458333.7915
MUGDAPARA HOSPITAL 33 KV SIDE (RECEIVING)
1 | Maniknagor Incoming-01 | 33 | Import | 38 | 1 | 280636640 | 290773248 | 10136608 | 1 | 10136608
2 | Maniknagor Incoming-02 | 33 | Import | 15 | 1 | 195727056 | 205869872 | 10142816 | 1 | 10142816
7: 0; 8: 0; 10: Total | 20279424 | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| MUGDAPARA HOSPITAL 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export | 16 | 1 | 269258400 | 279390240 | 10131840 | 1 |  | 10131840
4 | Transformer-02 | 33 | Export | 196 | 1 | 206984400 | 217124880 | 10140480 | 1 |  | 10140480
10: Total |  | 20272320 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: MANKNAGAR 33 KV SIDE; 4: 20279424; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 20279424
6: 33 KV NET IMPORT; 9=8-7: 20279424 | MUGDAPARA HOSPITAL 11 KV NET IMPORT |  | 20272320
[10 empty] | LOSS UNITS=> |  | 7104
[10 empty] | LOSS % IN => |  | 0.03503%
| TOTAL IMPORT |  | 20279424
1: 11 KV SIDE of___MUGDAPARA HOSPITAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MUGDAPARA HOSPITAL 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | 192 | 1 | 267260736 | 277339136 | 10078400 | 1 | 10078400 |  | 10129050.6877
2 | Transformer-02 Incoming | 11 | Import | 118 | 1 | 205509296 | 215608912 | 10099616 | 1 | 10099616 |  | 10150373.3123
7: 0; 8: 0; 10: Total | 20178016 |  | 20279424
| MUGDAPARA HOSPITAL 11 KV SIDE |  |  |  |  | 0 | 0
1 | City Corporation | 11 |  | 93 | 1 | 39720584 | 40386420 | 665836 | 1 |  | 665836 | 672002.1574 | Bashabo |  |  |  | City Corporation | 672002.1574 | 951549.8845 | -279547.7271 | -29.3781 | OK
2 | Bot tola | 11 |  |  | 1 | 51317676 | 53690908 | 2373232 | 1 |  | 2373232 | 2395209.9678 | Maniknagar |  |  |  | Bot tola | 2395209.9678 | 2298336.7826 | 96873.1852 | 4.2149 | OK
3 | Jhilpar | 11 |  | 145 | 1 | 33590076 | 34782876 | 1192800 | 1 |  | 1192800 | 1203846.2525 | Mugdapara |  |  |  | Jhilpar | 1203846.2525 | 1011093.8025 | 192752.45 | 19.0638 | OK
4 | Central Bashaboo | 11 |  | 128 | 1 | 35782472 | 37782388 | 1999916 | 1 |  | 1999916 | 2018436.7723 | Bashabo |  |  |  | Central Bashaboo | 2018436.7723 | 1763582.1465 | 254854.6258 | 14.451 | OK
5 | Kadamtala | 11 |  | 8 | 1.5 | 17980396 | 18572154 | 591758 | 1 |  | 887637 | 895857.2066 | Mugdapara |  |  |  | Kadamtala | 895857.2066 | 680353.9053 | 215503.3013 | 31.6752 | OK
6 | Ansar VDP | 11 |  | 119 | 1 | 18412676 | 19018394 | 605718 | 1 |  | 605718 | 611327.4182 | Khilgaon |  |  |  | Ansar VDP | 611327.4182 | 1128730.4864 | -517403.0682 | -45.8394 | CHECK
7 | Mugda Hospital Express-01 | 11 |  |  | 1 | 5599066 | 5903745 | 304679 | 1 |  | 304679 | 307500.5637 | Mugdapara |  |  |  | Mugda Hospital Express-01 | 307500.5637 | 293639.1125 | 13861.4512 | 4.7206 | OK
8 | Boro Masjid | 11 |  | 7 | 1.22 | 46545848 | 47940324 | 1394476 | 1 |  | 1701260.72 | 1717015.7129 | Mugdapara |  |  |  | Boro Masjid | 1717015.7129 | 1405726.812 | 311288.9009 | 22.1443 | OK
1 | Anandodhara | 11 |  | 120 | 1 | 45910688 | 46909724 | 999036 | 1 |  | 999036 | 1008287.8477 | Maniknagar |  |  |  | Anandodhara | 1008287.8477 | 964251.0175 | 44036.8302 | 4.5669 | OK
2 | Culvert | 11 |  | 117 | 1 | 36749792 | 38905824 | 2156032 | 1 |  | 2156032 | 2175998.5274 | Bashabo |  |  |  | Culvert | 2175998.5274 | 1824104.3237 | 351894.2037 | 19.2913 | OK
3 | Mugda Hospital Express-02 | 11 |  | 97 | 1 | 4845548 | 4845548 | 0 | 1 |  | 0 | 0 | Mugdapara |  |  |  | Mugda Hospital Express-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Jhor Pukur | 11 |  | 98 | 1 | 24721380 | 26401136 | 1679756 | 1 |  | 1679756 | 1695311.8425 | Bashabo |  |  |  | Jhor Pukur | 1695311.8425 | 1643349.6255 | 51962.217 | 3.162 | OK
5 | T&T | 11 |  | 99 | 1 | 22630184 | 23345024 | 714840 | 1 |  | 714840 | 721459.9725 | Mugdapara |  |  |  | T&T | 721459.9725 | 567104.166 | 154355.8065 | 27.2182 | OK
6 | Haider Ali | 11 |  | 9 | 1 | 64773440 | 67435952 | 2662512 | 1 |  | 2662512 | 2687168.9248 | Maniknagar |  |  |  | Haider Ali | 2687168.9248 | 2028073.3969 | 659095.5279 | 32.4986 | OK
| 11kv Tilpapara | 11 |  |  | 1 | 0 | 0 | 0 | 1 | Estimated | 2150000 | 2169910.6664 | Bashabo |  |  |  | 11kv Tilpapara | 2169910.6664
7 | AT-01 | 11 |  |  | 1 | 2875 | 2964 | 89 | 1 |  | 89 | 89.8242 | Mugdapara |  |  |  | AT-01 | 89.8242 | 94.3756 | -4.5514 | -4.8227 | OK
8 | AT-02 | 11 |  |  | 1 | 17 | 17.34 | 0.34 | 1 |  | 0.34 | 0.34315 | Mugdapara |  |  |  | AT-02 | 0.34315 | 0 | 0.34315 | #DIV/0! | #DIV/0!
10: Grand Total | 20279424 | 20093344.06 | 20279424 | 0.92608
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bashabo | at 33 KV level |  | 8731659.9661
[5 empty] | Maniknagar | at 33 KV level |  | 6090666.7403
[5 empty] | Mugdapara | at 33 KV level |  | 4845769.8755
[5 empty] | Khilgaon | at 33 KV level |  | 611327.4182
[5 empty] | Total = |  |  | 20279424 | 0
1: 33 KV SIDE of___KHILGOAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Taltola 33 KV SIDE
2 | Khailgaon | 33 | Export | BD001895 | 1 | 61.9199 | 62.0687 | 0.1488 | 240000 | 0 | 35712 | 35803.5297
MANKNAGAR 33 KV SIDE
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 267046 | 270635 | 3589 | 2000 | 0 | 7178000 | 7238761.6479
10: Total | 0 | 7213712 | 7274565.1776
Total
KHILGOAN 33 KV SIDE (RECEIVING)
| 33 KV Taltola 1 Incomming | 33 | RECEIVE |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 KV Taltola 2 Incomming | 33 |  |  | 1 | 0 | 0 | 0 |  |  | 0
| 33 kV Ullon Incoming | 33 |  |  | 1 | 56486 | 56639 | 153 | 270 |  | 41310
| 33 kV Maniknagor Incoming | 33 |  |  | 1.08 | 968067 | 1007578 | 39511 | 180 |  | 7680938.4
7: 0; 8: 0; 10: Total |  | 7722248.4
| KHILGOAN 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| KHILGOAN 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer -01 | 33 | Export | DHK60982 | 1 | 806471 | 806720 | 249 | 180 |  | 44820
4 | Transformer -02 | 33 | Export | DHK60947 | 1 | 718382 | 757892 | 39510 | 180 |  | 7111800
10: Total |  | 7156620 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: Taltola 33 KV SIDE; 4: 7274565.1776; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 7156620
6: 33 KV NET IMPORT; 9=8-7: 7156620 | 33 KV TX HV SIDE |  | 7156620
[10 empty] | LOSS UNITS=> |  | 0
[10 empty] | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 7274565.1776
1: 11 KV SIDE of___KHILGOAN 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
KHILGOAN 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | DHK60927 | 1 | 807197 | 807403 | 206 | 180 | 37080 |  | 38766.8285
2 | Transformer-02 Incoming | 11 | Import | DHK60928 | 1 | 879175 | 916998 | 37823 | 180 | 6808140 |  | 7117853.1715
7: 0; 8: 0; 10: Total | 6845220 |  | 7156620
| KHILGOAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | Shantinagar s/s-1 | 11 |  | DHK60932 | 1 | 277582 | 322430 | 44848 | 60 |  | 2690880 | 2768208.202 | Rajarbag |  |  |  | Shantinagar s/s-1 | 2768208.202 | 2755360.6206 | 12847.5814 | 0.46628 | OK
2 | Gulbagh | 11 |  | DHK60934 | 1 | 117195 | 122528 | 5333 | 60 |  | 319980 | 329175.3109 | Rajarbag |  |  |  | Gulbagh | 329175.3109 | 325114.8574 | 4060.4534 | 1.2489 | OK
3 | Rampura BTV | 11 |  | DHK60933 | 1 | 14073 | 14073 | 0 | 60 |  | 0 | 0 | Khilgaon | No Load |  |  | Rampura BTV | 0 | 1220.4011 | -1220.4011 | -100 | CHECK
4 | West Shantibag | 11 |  | DHK60926 | 1 | 505382 | 520515 | 15133 | 60 |  | 907980 | 934072.7507 | Rajarbag |  |  |  | West Shantibag | 934072.7507 | 932020.3326 | 2052.418 | 0.22021 | OK
1 | East Malibagh | 11 |  | DHK60929 | 1 | 560235 | 583078 | 22843 | 60 |  | 1370580 | 1409966.5528 | Rajarbag |  |  |  | East Malibagh | 1409966.5528 | 1377100.6198 | 32865.933 | 2.3866 | OK
2 | Police Line | 11 |  | DHK60930 | 1 | 555020 | 565142 | 10122 | 60 |  | 607320 | 624772.6414 | Rajarbag |  |  |  | Police Line | 624772.6414 | 596226.9654 | 28545.676 | 4.7877 | OK
3 | PWD RMU 11 KV Sajanpur Feeder. | 11 |  | DHK61017 | 1 | 190385 | 192855 | 2470 | 60 |  | 148200 | 152458.8445 | Rajarbag |  |  |  | PWD RMU 11 KV Sajanpur Feeder. | 152458.8445 | 149621.1769 | 2837.6676 | 1.8966 | OK
4 | Benjir Bagan | 11 |  | DHK60985 | 1 | 160865 | 164032 | 3167 | 60 |  | 190020 | 195480.6318 | Rajarbag |  |  |  | Benjir Bagan | 195480.6318 | 194653.9781 | 826.6538 | 0.42468 | OK
5 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 834990 | 846900 | 11910 | 60 |  | 714600 | 735135.562 | Switching |  |  |  | Shantinagar s/s-2 | 735135.562 | 245849.8049 | 489285.7571 | 199.0182 | FAULT
6 | AT-1 & AT-2 | 0.415 |  | ELIB 7374 | 1 | 1864.68 | 1983.75 | 119.07 | 60 |  | 7144.2 | 7349.5039 | Rajarbag |  |  |  | AT-1 & AT-2 | 7349.5039 | 14431.2432 | -7081.7393 | -49.0723 | CHECK
10: Grand Total | 7156620 | 6956704.2 | 7156620 | 2.8737
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH | Remark
[5 empty] | Rajarbag | at 33 KV level |  | 6946263.8291 | Including Switching
[5 empty] | Khilgaon | at 33 KV level |  | 0
[5 empty] | Moghbazar | at 33 KV level |  | 138756.0658
[5 empty] | Kakrail | at 33 KV level |  | 71600.1051
[5 empty] | Total = |  |  | 7156620 | 0
1: 11 KV SIDE of___Santinagar Switching S/S |  |  |  |  | Month July-2023
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
From Source End
1 | Shantinagar s/s-2 | 11 |  | DHK60935 | 1 | 834990 | 846900 | 11910 | 60 |  | 714600 | 735135.562 | 2.8737
Outgoing Feeders From Switching
1 | 11 KV Shahidbagh Feeder | 11 |  | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 510120 | 524779.3911 | Rajarbag
2 | 11 Fortune(MogBazar)-new | 11 |  | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 134880 | 138756.0658 | Moghbazar
3 | Centerpoint-Kakrail | 11 |  | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 69600 | 71600.1051 | Kakrail
[11 empty] | 714600 | 735135.562 | 2.8737
1: 33 KV SIDE of___ MONIPURIPARA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Agargoan 33 KV SIDE
1 | Sherebangla to Monipuripara-1 | 33 | Import |  | 1 | 1026.085 | 1061.83 | 35.745 | 180000 | 0 | 6439085.1407
2 | Sherebangla to Monipuripara-2 | 33 | Import |  | 1 | 741.116 | 766.09 | 24.974 | 180000 | 0 | 4498802.9739
10: Total | 0 | 10937888.1146 | 0
10: Net Total | 10937888.1146
MONIPURIPARA 33 KV SIDE (RECEIVING)
1 | Agargaon Ckt-01 | 33 | Import | BD017103 | 1 | 24341.45 | 30067.25 | 5725.8 | 1000 | 5725800
2 | Agargaon Ckt-02 | 33 | Import | BD017104 | 1 | 18474.38 | 22470.96 | 3996.58 | 1000 | 3996580
7: 0; 8: 0; 10: Total | 9722380 | 0 | 0
| MONIPURIPARA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| MONIPURIPARA 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export | BD017102 | 1 | 85228.28 | 91686.77 | 6458.49 | 888.8889 |  | 5740880.0718
4 | Transformer-02 | 33 | Export | BD017105 | 1 | 33794.26 | 38306.04 | 4511.78 | 888.8889 |  | 4010471.1612
8: 0; 10: Total |  | 9751351.233 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Agargoan 33 KV SIDE; 4: 10937888.1146; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 10937888.1146
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 10937888.1146 | 33 KV TX HV SIDE |  | 9751351.233
2: IMPORT-3 | LOSS UNITS=> |  | 1186536.8816
2: IMPORT-4 | LOSS % IN => |  | 10.85%
| TOTAL IMPORT |  | 10937888.1146
1: 11 KV SIDE of___MONIPURIPARA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
MONIPURIPARA 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import | BD014058 | 1 | 84552.88 | 90991.47 | 6438.59 | 1000 | 6438590 |  | 6445849.2359
2 | Transformer -02 Incoming | 11 | Import | BD014062 | 1 | 32917.48 | 37404.46 | 4486.98 | 1000 | 4486980 |  | 4492038.8788
7: 0; 8: 0; 10: Total | 10925570 | 0 | 10937888.1146
| MONIPURIPARA 11 KV SIDE |  |  |  |  | 0 | 0
1 | Spare | 11 |  | BD013944 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | Monipuripara west | 11 |  | BD013947 | 1 | 29462.81 | 30306.07 | 843.26 | 1000 |  | 843260 | 847623.509 | Shere b.nagar |  |  |  | Monipuripara west | 847623.509 | 861249.4503 | -13625.9413 | -1.5821 | OK
3 | Biggan College | 11 |  | BD013949 | 1 | 17308.18 | 18139.4 | 831.22 | 1000 |  | 831220 | 835521.2072 | Kakrail |  |  |  | Biggan College | 835521.2072 | 819870.1443 | 15651.0628 | 1.909 | OK
4 | Green Road South | 11 |  | BD013948 | 1 | 27673.13 | 28643.32 | 970.19 | 1000 |  | 970190 | 975210.3173 | Shere b.nagar |  |  |  | Green Road South | 975210.3173 | 1037302.1428 | -62091.8255 | -5.9859 | OK
5 | BARC Building O/H | 11 |  | BD014010 | 1 | 12194.37 | 12825.53 | 631.16 | 1000 |  | 631160 | 634425.9824 | Shere b.nagar |  |  |  | BARC Building O/H | 634425.9824 | 629218.3029 | 5207.6795 | 0.82764 | OK
6 | Green Road North | 11 |  | BD014036 | 1 | 55063.73 | 57019.83 | 1956.1 | 1000 |  | 1956100 | 1966221.9789 | Shere b.nagar |  |  |  | Green Road North | 1966221.9789 | 1919532.2257 | 46689.7532 | 2.4324 | OK
7 | Chundrima Uddan | 11 |  | BD014035 | 1 | 28003.9 | 29068.98 | 1065.08 | 1000 |  | 1065080 | 1070591.3324 | Shere b.nagar |  |  |  | Chundrima Uddan | 1070591.3324 | 1032887.2799 | 37704.0525 | 3.6504 | OK
8 | RMU-1 Feeder | 11 |  | BD013940 | 1 | 146.76 | 283.07 | 136.31 | 1000 |  | 136310 | 137015.3458 | Shere b.nagar |  |  |  | RMU-1 Feeder | 137015.3458 | 147255.7457 | -10240.3999 | -6.9542 | OK
1 | Spare-03 | 11 |  | BD013946 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Spare-03 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | kawran Bazar North | 11 |  | BD013964 | 1 | 40142.51 | 40221.55 | 79.04 | 1000 |  | 79040 | 79448.9981 | Kakrail |  |  |  | kawran Bazar North | 79448.9981 | 30221.7434 | 49227.2547 | 162.8869 | FAULT
3 | NAM Bhanan RMU | 11 |  | BD013950 | 1 | 14281.17 | 15281.88 | 1000.71 | 1000 |  | 1000710 | 1005888.2452 | Shere b.nagar |  |  |  | NAM Bhanan RMU | 1005888.2452 | 1030950.7605 | -25062.5152 | -2.431 | OK
4 | Novo Theater | 11 |  | BD013938 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Shere b.nagar |  |  |  | Novo Theater | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Monipuripara Nearest | 11 |  | BD013962 | 1.18 | 36592.1 | 37303.94 | 711.84 | 1000 |  | 839971.2 | 844317.6909 | Tejgaon | CF Due to PT B-Phase Missing |  |  | Monipuripara Nearest | 844317.6909 | 794156.578 | 50161.1129 | 6.3163 | OK
6 | Holy Cross | 11 |  | BD013965 | 1.18 | 35046.94 | 36115.46 | 1068.52 | 1000 |  | 1260853.6 | 1267377.9768 | Tejgaon |  |  |  | Holy Cross | 1267377.9768 | 1286005.418 | -18627.4411 | -1.4485 | OK
7 | Honda Goli | 11 |  | BD014011 | 1.18 | 12339.97 | 13245.54 | 905.57 | 1000 |  | 1068572.6 | 1074102.0051 | Tejgaon |  |  |  | Honda Goli | 1074102.0051 | 1068926.6085 | 5175.3966 | 0.48417 | OK
8 | Navy Quarter | 11 |  | BD013941 | 1.18 | 4964.2 | 5132.94 | 168.74 | 1000 |  | 199113.2 | 200143.5254 | Tejgaon |  |  |  | Navy Quarter | 200143.5254 | 202962.2853 | -2818.7598 | -1.3888 | OK
9 | AT-01 | 0.415 |  |  | 1 | 1834.42 | 1913.87 | 79.45 | 1 |  |  | 0 | Shere b.nagar |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 585.48 | 585.48 | 0 | 1 |  | 0 | 0 | Shere b.nagar |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 10937888.1146 | 10881580.6 | 10937888.1146 | 0.51746
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shere b.nagar | at 33 KV level |  | 6636976.7111
[5 empty] | Kakrail | at 33 KV level |  | 914970.2053
[5 empty] | Tejgaon | at 33 KV level |  | 3385941.1983
[5 empty] | Total = |  |  | 10937888.1146 | 0
1: 33 KV SIDE of___ Ispahani 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Mogbazar 33 KV SIDE
11 | Ispahani-1 | 33 | 0 | 0 | 1 | 1936.84 | 1936.84 | 0 | 180000 | From Ispahani Downsteam Estimated | 0 | 0
12 | Ispahani-2 | 33 | 0 | 0 | 1 | 3824.35 | 3858.6 | 34.25 | 180000 | 0 | 6165000 | 6206654.4391
10: Total | 0 | 6165000 | 6206654.4391
Ispahani 33 KV SIDE (RECEIVING)
1 | Mogbazar Ckt-01 | 33 | Import |  | 1 | 13649.76 | 13649.76 | 0 | 1000 | 0
2 | Mogbazar Ckt-02 | 33 | Import |  | 1 | 20256.66 | 26193.26 | 5936.6 | 1000 | 5936600
7: 0; 8: 0; 10: Total | 5936600 | 0 | 0
| Ispahani 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| Ispahani 33 KV SIDE |  |  |  |  | 0 | 0
3 | Transformer-01 | 33 | Export |  | 1 | 20804.63 | 20804.63 | 0 | 888.8889 |  | 0 |  | #DIV/0!
4 | Transformer-02 | 33 | Export |  | 1 | 17125.58 | 23804.91 | 6679.33 | 888.8889 |  | 5937182.2964
10: Total |  | 5937182.2964 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Mogbazar 33 KV SIDE; 4: 6206654.4391; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 5937182.2964
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 5937182.2964 | 33 KV TX HV SIDE |  | 5937182.2964
2: IMPORT-3 | LOSS UNITS=> |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| TOTAL IMPORT |  | 6206654.4391
1: 11 KV SIDE of___ Ispahani 33/11 KV S/S Phone No: 222227907 |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=10*9*6 | 12=10*9*6 | 13 | 14 | 15
Ispahani 11 KV SIDE
1 | Transformer-01 Incoming | 11 | Import |  | 1 | 18126.62 | 18126.62 | 0 | 1000 | 0 |  | 0
2 | Transformer -02 Incoming | 11 | Import |  | 1 | 4941.97 | 6871.6 | 1929.63 | 1000 | 5937182.2964 |  | 5937182.2964 |  | From Upstream
7: 0; 8: 0; 10: Total | 5937182.2964 | 0 | 5937182.2964
| Ispahani 11 KV SIDE |  |  |  |  | 0 | 0
1 | Doctor Goli | 11 |  | BD013944 | 1 | 6792.09 | 7728.79 | 936.7 | 1000 |  | 936700 | 948233.0953 | Moghbazar |  |  |  | Doctor Goli | 948233.0953 | 958270.3835 | -10037.2881 | -1.0474 | OK
2 | Ispahani | 11 |  | BD013947 | 1 | 7580.78 | 8623.82 | 1043.04 | 1000 |  | 1043040 | 1055882.4039 | Moghbazar |  |  |  | Ispahani | 1055882.4039 | 1058199.8531 | -2317.4492 | -0.219 | OK
3 | BTCL | 11 |  | BD013949 | 1 | 3962.52 | 4485.67 | 523.15 | 1000 |  | 523150 | 529591.2713 | Kakrail |  |  |  | BTCL | 529591.2713 | 523726.617 | 5864.6543 | 1.1198 | OK
4 | Vikarunnesa | 11 |  | BD013948 | 1 | 4102.97 | 5237.35 | 1134.38 | 1000 |  | 1134380 | 1148347.0254 | Kakrail |  |  |  | Vikarunnesa | 1148347.0254 | 1136233.5895 | 12113.4359 | 1.0661 | OK
5 | OASIS | 11 |  |  | 1 | 0 | 4.29 | 4.29 | 1000 |  | 4290 | 4342.8205 | Kakrail |  |  |  | OASIS | 4342.8205 | 0 | 4342.8205 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
1 | Wireless | 11 |  |  | 1 | 5737.24 | 6771.63 | 1034.39 | 1000 |  | 1034390 | 1047125.901 | Moghbazar |  |  |  | Wireless | 1047125.901 | 1048087.1638 | -961.2628 | -0.091716 | OK
2 | Kazir Goli | 11 |  |  | 1 | 4903.55 | 6092.57 | 1189.02 | 1000 |  | 1189020 | 1203659.779 | Kakrail |  |  |  | Kazir Goli | 1203659.779 | 1263311.3532 | -59651.5742 | -4.7218 | OK
3 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Spare | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | AT-01 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-01 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | AT-02 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | AT-02 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 5937182.2964 | 5864970 | 5937182.2964 | 1.2312
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Moghbazar | at 33 KV level |  | 3051241.4002
[5 empty] | Kakrail | at 33 KV level |  | 2885940.8962
[5 empty] | Total = |  |  | 5937182.2964 | 0

## SOUTH-1
132 KV SIDE of___SIDDHIRGANJ 132/33/11 KV S/S | [13 empty] | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SIDDHIRGANJ 132 KV SIDE (TARIFF POINT)
| XFR- T1 | 132 | IMPORT | 8993683 | 1 | 8298.965 | 8336.501 | 37.536 | 960000 | 0 | 36034560
| XFR- T2 | 132 |  | 8993682 | 1 | 8289.656 | 8326.822 | 37.166 | 960000 | 0 | 35679360
10: Total | 0 | 71713920
SIDDHIRGANJ 132 KV SIDE (RECEIVING)
| 132/33 kV Transformer-1(HV) ** | 132 | P. Cell | 08993685 | 1 | 8298.952 | 8336.492 | 37.54 | 960000 | 36038400
| 132/33 kV Transformer-2(HV) ** | 132 | P. Cell | 08993684 | 1 | 8289.645 | 8326.819 | 37.174 | 960000 | 35687040
10: Total | 71725440
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: SIDDHIRGANJ 132 KV SIDE (TARIFF POINT); 4: 71713920; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 71713920
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 71713920 | 33 KV NET IMPORT |  | 72239040
2: IMPORT-3; 6: TOTAL EXPORT; 9=8-7: 71713920 | LOSS UNITS=>(132 HV-33 LV) |  | -525120
2: IMPORT-4; 6: Loss Units=> (132 IMP-132 EXP); 9=8-7: 0 | LOSS % IN => |  | -0.7322%
| 132 KV TOTAL IMPORT |  | 71713920 |  | 132 KV NET LOSS => |  |  | 0%
| 33 KV GT INCOMING-NOCS |  | 72239040
| Loss Units=> (132 IMP-33 IMP) |  | -525120
| LOSS % IN => |  | -0.7322%
1: 33 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 33 KV SIDE (Incomming) |  | IMPORT
3 | 132/33 kV Transformer, T-1 (LV) | 33 | PGCB | J2002016494 | 1 | 21608.775 | 21858.207 | 249.432 | 144000 | 35918208
4 | 132/33 kV Transformer, T-2 (LV) | 33 | PGCB | J2002016859 | 1 | 31587.816 | 31835.056 | 247.24 | 144000 | 35602560
2: DPDC; 7: 0; 8: 0; 10: Total | 71520768
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | DPDC | 07389553 | 1 | 1527.81 | 1603.3 | 75.49 | 480000 | 36235200
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | DPDC | 07389485 | 1.038 | 925.57 | 995.7 | 70.13 | 480000 | 34941571.2
2: P.Cell; 7: 0; 8: 0; 10: Total | 71176771.2
| 132/33 kV Transformer-1 (GT-1) Incoming | 33 | P.Cell | 08993674 | 1 | 10793.03 | 10868.572 | 75.542 | 480000 | 36260160
| 132/33 kV Transformer-2 (GT-2) Incoming | 33 | P.Cell | 8993667 | 1 | 10703.004 | 10777.96 | 74.956 | 480000 | 35978880
10: Total | 72239040
SIDDHIRGANJ 33 kV SIDE
2: 33/11 KV Transforfers; 4: EXPORT | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 33 | DPDC | 07389555 | 1 | 5606.73 | 5636.56 | 29.83 | 240000 |  | 7159200 | 7169668.8084 |  | 15033951.8593 | Siddhirganj 33/11 kv ss | 1.971 | 33/11 kV, 20/28 MVA Transformer-1 (T-1) | 7169668.8084 | 6742821.4846 | 426847.3237 | 6.3304 | OK
|  | 33 | P.Cell | 08993675 | 1 | 4963.364 | 4993.2 | 29.836 | 240000 |  | 7160640 | 7171110.9141 |  |  |  |  | 0 | 7171110.9141 | 6744985.7283 | 426125.1857 | 6.3177 | OK
12 | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 33 | DPDC | 07389487 | 1 | 5775.4 | 5808.12 | 32.72 | 240000 |  | 7852800 | 7864283.0509 |  |  |  |  | 33/11 kV, 20/28 MVA Transformer-2 (T-2) | 7864283.0509 | 7478664.3428 | 385618.7081 | 5.1563 | OK
|  | 33 | P.Cell | 08993666 | 1 | 5039.611 | 5072.42 | 32.809 | 240000 |  | 7874160 | 7885674.2854 |  |  |  |  | 0 | 7885674.2854 | 7486840.3746 | 398833.9108 | 5.3271 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 15012000 | 15033951.8593 |  |  |  |  | 33 KV Feeders | 15033951.8593 | 14221485.8274 | 812466.0319 | 5.7129 | OK
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4197.894 | 4240.998 | 43.104 | 240000 |  | 10344960 | 10360087.3052 |  | 19291528.5697 | Sarulia 33/11 kv ss |  | 33 kV Sarulia-1 Feeder | 10360087.3052 | 10178197.6519 | 181889.6534 | 1.7871 | OK
|  | 33 | P.Cell | 08993679 | 1 | 4198.71 | 4241.94 | 43.23 | 240000 |  | 10375200 | 10390371.5248 |  |  |  |  | 0 | 10390371.5248 | 10184209.4399 | 206162.0849 | 2.0243 | OK
6 | 33 kV Kazla Feeder (Now AEPZ-2) | 33 | DPDC | 07389552 | 1 | 2213.32 | 2213.32 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla Feeder (Now AEPZ-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993663 | 1 | 2000.943 | 2000.943 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 |  | 0 | 0 |  | 0 | Khanpur 33/11 kv ss |  | 33 kV Khanpur-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6094.16 | 6133.76 | 39.6 | 240000 |  | 9504000 | 9517897.58 |  |  |  |  | 33 kV Demra-1 Feeder | 9517897.58 | 11179521.0706 | -1661623.4907 | -14.8631 | OK
|  | 33 | P.Cell | 08993676 | 1 | 5739.735 | 5779.4 | 39.665 | 240000 |  | 9519600 | 9533520.3917 |  |  |  |  | 0 | 9533520.3917 | 11188418.517 | -1654898.1253 | -14.7912 | OK
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5573.43 | 5632.25 | 58.82 | 240000 |  | 14116800 | 14137442.8196 |  | 23655340.3996 | Demra 33/11 kv ss |  | 33 kV Demra-2 Feeder | 14137442.8196 | 11989910.1007 | 2147532.7188 | 17.9112 | OK
|  | 33 | P.Cell | 08993665 | 1 | 5281.677 | 5340.51 | 58.833 | 240000 |  | 14119920 | 14140567.3819 |  |  |  |  | 0 | 14140567.3819 | 12000490.8477 | 2140076.5342 | 17.8332 | OK
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Khanpur-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4500.27 | 4526.7 | 26.43 | 240000 |  | 6343200 | 6352475.5818 | Siddirgonj |  |  |  | 33 kV Apollo Ispat Feeder | 6352475.5818 | 7317548.4229 | -965072.8411 | -13.1885 | OK
|  | 33 | P.Cell | 08993678 | 1 | 3745.951 | 3772.326 | 26.375 | 240000 |  | 6330000 | 6339256.2796 |  |  |  |  | 0 | 6339256.2796 | 7321636.4388 | -982380.1592 | -13.4175 | OK
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3922.19 | 3959.35 | 37.16 | 240000 |  | 8918400 | 8931441.2645 |  |  |  |  | 33 kV Sarulia-2 Feeder | 8931441.2645 | 8606475.7823 | 324965.4822 | 3.7758 | OK
|  | 33 | P.Cell | 08993663 | 1 | 3644.087 | 3680.325 | 36.238 | 240000 |  | 8697120 | 8709837.6895 |  |  |  |  | 0 | 8709837.6895 | 8611044.7412 | 98792.9483 | 1.1473 | OK
17 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 357772.9 | 361720 | 3947.1 | 2000 |  | 7894200 | 7905743.5896 | Siddirgonj |  |  |  | 33 kV Adamjee EPZ Feeder | 7905743.5896 | 8068621.1441 | -162877.5545 | -2.0187 | OK
10: Total | 72239040 | 72133560 | 72239040 | 0.14623
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 14258219.1714
[5 empty] | Total = |  |  | 14258219.1714 | 0
1: 11 KV SIDE of___ SIDDHIRGANJ 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Pos | Imp./Exp. | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| SIDDHIRGANJ 11 KV SIDE |  | IMPORT
8 | 33/11 kV Transformer-1 Incoming | 11 | New | XA587379 | 1 | 672550.3 | 679629.3 | 7079 | 1000 | 7079000 |  | 7172920.9355
9 | 33/11 kV Transformer-2 Incoming | 11 | New | DHKA9985 | 1 | 300376.2 | 308134.3 | 7758.1 | 1000 | 7758100 |  | 7861030.9238
7: 0; 8: 0; 10: Total | 14837100 |  | 15033951.8593
| SIDDHIRGANJ 11 kV SIDE |  | EXPORT |  |  | 0 | 0
3 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 210341.9 | 213015.1 | 2673.2 | 1000 |  | 2673200 | 2725888.0748 | Siddirgonj |  |  |  | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 2725888.0748 | 2549641.8301 | 176246.2447 | 6.9126 | OK
4 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16731.5 | 16876.9 | 145.4 | 1000 |  | 145400 | 148265.7961 | Siddirgonj |  |  |  | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 148265.7961 | 145583.9006 | 2681.8955 | 1.8422 | OK
5 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 106740.6 | 108320.7 | 1580.1 | 1000 |  | 1580100 | 1611243.3589 | Siddirgonj |  |  |  | 11 kV Narayangonj Direct Feeder (F-3) | 1611243.3589 | 1535819.0344 | 75424.3245 | 4.911 | OK
6 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 167267.3 | 169879.3 | 2612 | 1000 |  | 2612000 | 2663481.8388 | Siddirgonj |  |  |  | 11 kV Ekata Steel Feeder (F-4) | 2663481.8388 | 2529191.2405 | 134290.5983 | 5.3096 | OK
7 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6948.3 | 7001.5 | 53.2 | 1000 |  | 53200 | 54248.5581 | Siddirgonj |  |  |  | 11 kV Silo+Titas Feeder (F-5) | 54248.5581 | 41407.382 | 12841.1761 | 31.0118 | OK
10 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 73247.9 | 74651.5 | 1403.6 | 1000 |  | 1403600 | 1431264.5899 | Siddirgonj |  |  |  | 11 kV Monowar Feeder (F-6) | 1431264.5899 | 1311672.4727 | 119592.1173 | 9.1175 | OK
11 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Era Steel Feeder (F-7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New |  | 1 | 25.5757 | 25.5757 | 0 | 40000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Kalu Haji Road Feeder (F-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 144040.1 | 146439.6 | 2399.5 | 1000 |  | 2399500 | 2446793.5192 | Siddirgonj |  |  |  | 11 kV Mizmizi Feeder (F-9) | 2446793.5192 | 2328937.4468 | 117856.0724 | 5.0605 | OK
14 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 71.4752 | 79.1918 | 7.7166 | 40000 |  | 308664 | 314747.6869 | Matuail |  |  |  | 11 KV Jhilpar (F-10) | 314747.6869 | 291293.3394 | 23454.3475 | 8.0518 | OK
15 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Madrasha Road Feeder (F-11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 13546.5 | 14255.5 | 709 | 1000 |  | 709000 | 722974.2051 | Siddirgonj |  |  |  | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 722974.2051 | 681450.0937 | 41524.1114 | 6.0935 | OK
17 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 |  | 0 | 0 | Siddirgonj |  |  |  | Seven Horse Feeder (F-13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 143559.8 | 146418.5 | 2858.7 | 1000 |  | 2858700 | 2915044.2314 | Siddirgonj |  |  |  | 11 kV Shanti Nagar (F-14) | 2915044.2314 | 2806489.0873 | 108555.1442 | 3.868 | OK
10: Total | 15033951.8593 | 14743364 | 15033951.8593 | 1.971
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Siddirgonj | at 33 KV level |  | 14719204.1724
[5 empty] | Matuail | at 33 KV level |  | 314747.6869
[5 empty] | Total = |  |  | 15033951.8593 | 0
Name of the Substation: Demra 33/11 kV, 2×20/28 MVA Substation.
1: 33 KV SIDE of___ DEMRA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
8 | 33 kV Demra-1 Feeder | 33 | DPDC | 07389489 | 1 | 6094.16 | 6133.76 | 39.6 | 240000 | 0 | 9504000 | 9517897.58
0 | 0 | 33 | P.Cell | 08993676 | 1 | 5739.735 | 5779.4 | 39.665 | 240000 | 0 | 9519600 | 9533520.3917
13 | 33 kV Demra-2 Feeder | 33 | DPDC | 07389484 | 1 | 5573.43 | 5632.25 | 58.82 | 240000 | 0 | 14116800 | 14137442.8196
0 | 0 | 33 | P.Cell | 08993665 | 1 | 5281.677 | 5340.51 | 58.833 | 240000 | 0 | 14119920 | 14140567.3819
10: Total | 0 | 23620800 | 23655340.3996
DEMRA 33 KV SIDE (RECEIVING)
5 | 33 kV Siddhirgonj Feeder-2 | 33 | Digital | DHK60885 | 3 | 292407.2 | 318358.5 | 25951.3 | 240 | 18684936
6 | 33 kV Siddhirgonj Feeder-1 (Old Haripur Feeder) | 33 | Analog | 9155454 | 1 | 574 | 574 | 0 | 360000 | 0 |  |  |  | Meter damaged
7: 0; 8: 0; 10: Total | 18684936 | 0 | 0
| DEMRA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
10 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1008.73 | 1011.11 | 2.38 | 240000 |  | 571200 |  | Siddirgonj
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 571200
[6 empty] | 0 | 0
| DEMRA 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60886 | 1 | 690613.3 | 733035 | 42421.7 | 240 |  | 10181208
8 | 33/11 kV, 10/14 MVA T-2 (HV) | 33 | Digital | 05002303 | 1 | 0 | 0 |  | 240 |  | 0
9 | 33/11 kV, 20/28 MVA T-3 (HV) | 33 |  |  | 1 | 0 | 0 |  | 180 |  | 0
10: Total |  | 10181208 | 0
[5 empty] | 33 KV Export-Import |  |  | KWH
[5 empty] | Total Import |  |  | 23655340.3996
[5 empty] | Siddirgonj NOCS |  |  | 571200
[5 empty] | Net Import to Demra 33/11 KV SS |  |  | 23084140.3996
1: 11 KV SIDE of___DEMRA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.08.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DEMRA 11 KV SIDE
18 | 33/11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK60881 | 1 | 225987.3 | 282440.7 | 56453.4 | 180 | 10161612 |  | 12153667.4867
19 | 33/11 kV, 20/28 MVA T-3 Incoming. | 11 |  | DHK60925 | 1 | 650536.9 | 701308.6 | 50771.7 | 180 | 9138906 |  | 10930472.9128
7: 0; 8: 0; 10: Total | 19300518 |  | 23084140.3996
| DEMRA 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 |  | HA021101013-02 | 1 | 43772221 | 46067484 | 2295263 | 1 |  | 2295263 | 2346002.1943 | Matuail |  |  |  | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 2346002.1943 | 2312393.5546 | 33608.6397 | 1.4534 | OK
12 | 11 kV DND (WASA) Feeder. | 11 |  | HA021100992-02 | 1 | 5367438 | 5613260 | 245822 | 1 |  | 245822 | 251256.153 | Siddirgonj |  |  |  | 11 kV DND (WASA) Feeder. | 251256.153 | 80170.7162 | 171085.4368 | 213.4014 | FAULT
13 | 11 kV Local Feeder | 11 |  | HA021100794-02 | 1 | 8692106 | 9848922 | 1156816 | 1 |  | 1156816 | 1182388.6301 | Siddirgonj |  |  |  | 11 kV Local Feeder | 1182388.6301 | 2088621.9879 | -906233.3577 | -43.3891 | CHECK
14 | 11 kV Mouchak Feeder | 11 |  | DHK60888 | 1 | 855586.5 | 893731.2 | 38144.7 | 60 |  | 2288682 | 2339275.7144 | Siddirgonj |  |  |  | 11 kV Mouchak Feeder | 2339275.7144 | 2308639.9015 | 30635.8129 | 1.327 | OK
15 | 11 kV Overhead-1 Feeder | 11 |  | HA021100829-02 | 1 | 76972401 | 78137143 | 1164742 | 1 |  | 1164742 | 1190489.8427 | Siddirgonj |  |  |  | 11 kV Overhead-1 Feeder | 1190489.8427 | 1095153.438 | 95336.4047 | 8.7053 | OK
16 | 11 kV Provati Steel Feeder | 11 |  | DHK60874 | 1 | 544937.6 | 546973.2 | 2035.6 | 60 |  | 122136 | 124835.9443 | Siddirgonj |  |  |  | 11 kV Provati Steel Feeder | 124835.9443 | 0 | 124835.9443 | #DIV/0! | #DIV/0!
17 | 11 kV Islambagh Feeder. | 11 |  | DHKA2190 | 1 | 999.9264 | 1048.5044 | 48.578 | 60000 |  | 2914680 | 2979112.0563 | Matuail |  |  |  | 11 kV Islambagh Feeder. | 2979112.0563 | 3002442.9965 | -23330.9402 | -0.77707 | OK
20 | 11 kV Taj Jute Feeder. | 11 |  | DHK61062 | 1 | 590904.5 | 613805.1 | 22900.6 | 60 |  | 1374036 | 1404410.5059 | Siddirgonj |  |  |  | 11 kV Taj Jute Feeder. | 1404410.5059 | 1676660.8446 | -272250.3387 | -16.2377 | OK
21 | 11 kV Al-Aksa Steel Feeder | 11 |  | DHK61061 | 1 | 732963.2 | 758979.9 | 26016.7 | 60 |  | 1561002 | 1595509.5853 | Siddirgonj |  |  |  | 11 kV Al-Aksa Steel Feeder | 1595509.5853 | 1474597.4818 | 120912.1035 | 8.1997 | OK
22 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 |  | DHKA2189 | 1 | 945.7312 | 986.7258 | 40.9946 | 60000 |  | 2459676 | 2514049.716 | Siddirgonj |  |  |  | 11 kV Sahebpara O/H (Old Spare Feeder) | 2514049.716 | 2467512.3805 | 46537.3355 | 1.886 | OK
23 | 11 kV Over Head Feeder-2. | 11 |  | HA021100488-02 | 1 | 24800709 | 26957261 | 2156552 | 1 |  | 2156552 | 2204224.8423 | Demra |  |  |  | 11 kV Over Head Feeder-2. | 2204224.8423 | 2131027.6013 | 73197.2409 | 3.4348 | OK
24 | 11 kV Shimrail Express Feeder. | 11 |  | HA021100511-02 | 1 | 8095991 | 8169444 | 73453 | 1 |  | 73453 | 75076.7556 | Siddirgonj |  |  |  | 11 kV Shimrail Express Feeder. | 75076.7556 | 29225.6688 | 45851.0867 | 156.8864 | FAULT
25 | 11 kV Sarder & Khadem Steel Feeder | 11 |  | HA021100413-02 | 1 | 80407905 | 80731969 | 324064 | 1 |  | 324064 | 331227.7744 | Demra |  |  |  | 11 kV Sarder & Khadem Steel Feeder | 331227.7744 | 650733.1002 | -319505.3258 | -49.0993 | CHECK
26 | 11 kV Siddhirgonj Mazar Feeder | 11 |  | HA021100393-02 | 1 | 22161.663 | 23396.457 | 1234.794 | 1000 |  | 1234794 | 1262090.4156 | Siddirgonj | OMF Corrected |  |  | 11 kV Siddhirgonj Mazar Feeder | 1262090.4156 | 281800.301 | 980290.1146 | 347.867 | FAULT
27 | 11 kV AST Beverage Feeder | 11 |  |  | 1 | 20233737 | 21373122 | 1139385 | 1 |  | 1139385 | 1164572.2996 | Siddirgonj |  |  |  | 11 kV AST Beverage Feeder | 1164572.2996 | 1051751.2525 | 112821.0471 | 10.727 | OK
28 | 11 kV Karim Market Feeder | 11 |  |  | 1 | 53935.137 | 56008.912 | 2073.775 | 1000 |  | 2073775 | 2119617.9699 | Matuail | OMF Corrected |  |  | 11 kV Karim Market Feeder | 2119617.9699 | 2072299.946 | 47318.0239 | 2.2834 | OK
29 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 |  | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj |  |  |  | 11/0.415 kV Transformer,AT-1+AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 23084140.3996 | 22584878 | 23084140.3996 | 2.2106
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 7444732.2205
[5 empty] | Demra | at 33 KV level |  | 2535452.6166
[5 empty] | Siddirgonj | at 33 KV level |  | 13103955.5624
[5 empty] | Total = |  |  | 23084140.3996 | 0
1: 33 KV SIDE of___ SARULIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Siddhirgonj 33 KV SIDE
5 | 33 kV Sarulia-1 Feeder | 33 | DPDC | 7389488 | 1 | 4197.894 | 4240.998 | 43.104 | 240000 | 0 | 10344960 | 10360087.3052
0 | 0 | 33 | P.Cell | 08993679 | 1 | 4198.71 | 4241.94 | 43.23 | 240000 | 0 | 10375200 | 10390371.5248
16 | 33 kV Sarulia-2 Feeder | 33 | DPDC | 07389491 | 1 | 3922.19 | 3959.35 | 37.16 | 240000 | 0 | 8918400 | 8931441.2645
| 0 | 33 | P.Cell | 08993663 | 1 | 3644.087 | 3680.325 | 36.238 | 240000 | 0 | 8697120 | 8709837.6895
10: Total | 0 | 19072320 | 19100209.2143
SARULIA 33 KV SIDE (RECEIVING)
3 | 33 kV Siddhirgonj-2 Incoming (=L31) | 33 |  | 30799103 | 1 | 4297.89 | 4334.6 | 36.71 | 240000 | 8810400
7 | 33 kV Siddhirgonj-1 Incoming (=L41) | 33 |  | 30799100 | 1 | 4218.87 | 4261.05 | 42.18 | 240000 | 10123200
7: 0; 8: 0; 10: Total | 18933600 | 0 | 0
| SARULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| SARULIA 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33/11 kV Transformer-1 (=T31) | 33 |  | 30799099 | 1 | 4598.9 | 4647.76 | 48.86 | 180000 |  | 8794800
5 | 33/11 kV Transformer-2 (=T32) | 33 |  | 30799139 | 1 | 3992.89 | 4020.32 | 27.43 | 180000 |  | 4937400
6 | 33/11 kV Transformer-3 (=T33) | 33 |  | 30799102 | 1 | 1827.2 | 1827.2 | 0 | 240000 |  | 0 |  |  | Meter Problem
10: Total |  | 13732200 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Siddhirgonj 33 KV SIDE; 4: 19100209.2143; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 19100209.2143
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 19100209.2143 | 33 KV NET Receiving |  | 18933600
2: IMPORT-3; 6: TOTAL EXPORT; 9=8-7: 19100209.2143 | LOSS UNITS=> |  | 166609.2143
2: IMPORT-4; 6: 132KV NET LOSS =>; 9=8-7: 0% | LOSS % IN => |  | 0.8723%
| TOTAL IMPORT |  | 19100209.2143
1: 11 KV SIDE of___SARULIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SARULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-1 Incoming (=T31A) | 11 |  | 2007754972 | 1 | 9249.26 | 9304.21 | 54.95 | 160000 | 8792000 |  | 9761975.6759
15 | 33/11 kV Transformer, T-2 Incoming (=T32A) | 11 |  | 30799500 | 1 | 8762.37 | 8801.51 | 39.14 | 80000 | 3131200 |  | 3476649.026
20 | 33/11 kV Transformer, T-3 Incoming (=T33A) | 11 |  | HA021100368-02 | 1 | 38337970 | 43617132 | 5279162 | 1 | 5279162 |  | 5861584.5124
7: 0; 8: 0; 10: Total | 17202362 |  | 19100209.2143
| SARULIA 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV Dayagonj Feeder (=L11) | 11 |  | 2007755114 | 1 | 5723.87 | 5767.7 | 43.83 | 60000 |  | 2629800 | 2674737.7934 | Demra |  |  |  | 11 kV Dayagonj Feeder (=L11) | 2674737.7934 | 2648546.8605 | 26190.933 | 0.98888 | OK
9 | 11 kV Karim Jute Feeder (=L12) | 11 |  | 30799484 | 1 | 21.1189 | 21.3509 | 0.232 | 60000 |  | 13920 | 14157.8637 | Demra |  |  |  | 11 kV Karim Jute Feeder (=L12) | 14157.8637 | 13577.9934 | 579.8703 | 4.2707 | OK
11 | 11 kV Konapara (=L13) **** | 11 |  | DHKA2191 | 1 | 2005.823 | 2064.619 | 58.796 | 60000 |  | 3527760 | 3588042.0557 | Demra |  |  |  | 11 kV Konapara (=L13) **** | 3588042.0557 | 3482255.5223 | 105786.5334 | 3.0379 | OK
12 | 11 kV Sanarpar Feeder (=L14) | 11 |  | 575926 | 1 | 48458.1 | 51041.5 | 2583.4 | 1000 |  | 2583400 | 2627544.9143 | Matuail |  |  |  | 11 kV Sanarpar Feeder (=L14) | 2627544.9143 | 2556143.6589 | 71401.2554 | 2.7933 | OK
13 | 11 kV Latif Bawani Feeder (=L15) | 11 |  | 30799450 | 1 | 1804.9 | 1809.19 | 4.29 | 60000 |  | 257400 | 261798.4288 | Demra |  |  |  | 11 kV Latif Bawani Feeder (=L15) | 261798.4288 | 295524.6849 | -33726.2561 | -11.4123 | OK
14 | 11 kV Tengra Feeder (=L16) | 11 |  | 30799145 | 1 | 5426.47 | 5472.12 | 45.65 | 60000 |  | 2739000 | 2785803.7935 | Demra |  |  |  | 11 kV Tengra Feeder (=L16) | 2785803.7935 | 2203397.2826 | 582406.5109 | 26.4322 | OK
16 | 11 kV Police Line Feeder (=L17) | 11 |  | 30799480 | 1 | 3297.43 | 3317.32 | 19.89 | 60000 |  | 1193400 | 1213792.7153 | Demra |  |  |  | 11 kV Police Line Feeder (=L17) | 1213792.7153 | 1297576.8726 | -83784.1573 | -6.457 | OK
17 | 11 kV Demra Bazar Feeder (=L18) | 11 |  | 30799119 | 1 | 1630.73 | 1639.93 | 9.2 | 60000 |  | 552000 | 561432.5279 | Demra |  |  |  | 11 kV Demra Bazar Feeder (=L18) | 561432.5279 | 558765.1604 | 2667.3675 | 0.47737 | OK
18 | 11 kV Spare Feeder (=F9) | 11 |  | HA021100859-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Demra |  |  |  | 11 kV Spare Feeder (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Boxnagar Feeder (=F10) | 11 |  | HA021100493-02 | 1 | 77608653 | 80604576 | 2995923 | 1 |  | 2995923 | 3047117.0714 | Demra |  |  |  | 11 kV Boxnagar Feeder (=F10) | 3047117.0714 | 3001937.8862 | 45179.1852 | 1.505 | OK
21 | 11 kV Baser Pool Feeder (=L11) | 11 |  | HA021100518-02 | 1 | 50867999 | 50869565 | 1566 | 1 |  | 1566 | 1592.7597 | Demra |  |  |  | 11 kV Baser Pool Feeder (=L11) | 1592.7597 | 158210.2162 | -156617.4565 | -98.9933 | CHECK
22 | 11 kV Dip-Pur Feeder (=L12) | 11 |  | HA021100697-02 | 1 | 20487902 | 22773043 | 2285141 | 1 |  | 2285141 | 2324189.2905 | Demra |  |  |  | 11 kV Dip-Pur Feeder (=L12) | 2324189.2905 | 2304863.862 | 19325.4284 | 0.83846 | OK
23 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 |  | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 |  | 05395814 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Demra |  |  |  | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 19100209.2143 | 18779310 | 19100209.2143 | 1.7088
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Demra | at 33 KV level |  | 16472664.3
[5 empty] | Matuail | at 33 KV level |  | 2627544.9143
[5 empty] | Total = |  |  | 19100209.2143 | 0
1: 33 KV SIDE of___ KHANPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 1599.843 | 10966.771 | 9366.928 | 1000 | 0 | 9366928 | 9373947.1321
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 370.6713 | 404.5926 | 33.9213 | 240000 | 0 | 8141112 | 8147212.5637
2: Siddhirganj 33 KV SIDE; 10: Total |  | 17508040 | 17521159.6958
7 | 33 kV Khanpur-1 Feeder | 33 | DPDC | 7389554 | 1 | 4928.74 | 4928.74 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993677 | 1 | 4640.92 | 4640.92 | 0 | 240000 | 0 | 0 | 0
14 | 33 kV Khanpur-2 Feeder | 33 | DPDC | 07389490 | 1 | 2682.22 | 2682.22 | 0 | 240000 | 0 | 0 | 0
0 | 0 | 33 | P.Cell | 08993664 | 1 | 2389.632 | 2389.632 | 0 | 240000 | 0 | 0 | 0
10: Total |  | 0 | 0
KHANPUR 33 KV SIDE (RECEIVING)
5 | 33 kV Shitalakhya-1 Feeder (New) | 33 |  | 84663042 | 1 | 378.07 | 411.99 | 33.92 | 240000 | 8140800
6 | 33 kV Shitalakhya-2 Feeder (Old) | 33 |  | 05323185 | 1 | 0 | 0 | 0 | 240000 | 8141112 |  |  |  | Meter Problem
7 | 33 kV Siddhirgonj Feeder-1 | 33 |  | 06604382 | 1 | 6508.21 | 6508.21 | 0 | 180000 | 0
8 | 33 kV Siddhirgonj Feeder-2 | 33 |  | 06604343 | 1 | 6301.46 | 6301.46 | 0 | 180000 | 0
7: 0; 8: 0; 10: Total | 16281912 | 0 | 0
| KHANPUR 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
11 | 33 kV ACI Pharmacuticles Feeder | 33 |  | DHKC4791 | 1 | 885.85 | 900.2 | 14.35 | 90000 |  | 1291500 |  | N.Gonj (East)
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 1291500
[6 empty] | 0 | 0
| KHANPUR 33 KV SIDE |  |  |  |  | 0 | 0
9 | 33/11 kV, 20/28 MVA T1 Transformer | 33 |  | DHKC 9363 | 1 | 116865.34 | 116865.34 | 0 | 240 |  | 0 |  |  | Meter Problem
| 33/11 kV, 20/28 MVA T4 Transformer | 33 |  | DHKC 9361 | 1 | 40559.36 | 40559.36 | 0 | 240 |  | 0 |  |  | Meter Problem
10: Total |  | 14990412 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV EXPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: SITALAKHYA 33 KV SIDE; 4: 17521159.6958; 6: EXPORT TO N.Gonj (East); 9=8-7: 1291500 | 33 KV NET IMPORT |  | 16229659.6958
2: SIDDIRGANJ 33 KV SIDE; 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 16229659.6958 | 33 KV TX HV SIDE |  | 14990412
2: IMPORT-3 | LOSS UNITS=> |  | 1239247.6958
2: IMPORT-4 | LOSS % IN => |  | 7.636%
| TOTAL IMPORT |  | 17521159.6958
1: 11 KV SIDE of___KHANPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KHANPUR 11 KV SIDE
17 | 33/11 kV Transformer-3 Incoming. | 11 |  | DHKC 9313 | 1 | 17083226 | 21545963.56 | 4462737.56 | 1 | 4462737.56 |  | 5794140.4832
18 | 33/11 kV Transformer-2 Incoming. | 11 |  | DHKC 9346 | 1 | 42701376.1 | 42701376.1 | 0 | 1 | 0 |  | 0
24 | 33/11 kV 20/28 MVA T4 Incoming | 11 |  | 06604325 | 1 | 97.63 | 119.84 | 22.21 | 240000 | 5330400 |  | 6920659.3524
30 | 33/11 kV 20/28 MVA T1 Incoming | 11 |  | 06604374 | 1 | 53.66 | 64.94 | 11.28 | 240000 | 2707200 |  | 3514859.8602
7: 0; 8: 0; 10: Total | 12500337.56 |  | 16229659.6958
| KHANPUR 11 KV SIDE |  |  |  |  | 0 | 0
12 | 11 kV Khanpur Feeder | 11 |  | DHKC 9348 | 1 | 16751.32 | 47198.82 | 30447.5 | 60 |  | 1826850 | 1849730.4598 | N.Gonj (East) |  |  |  | 11 kV Khanpur Feeder | 1849730.4598 | 1858439.2031 | -8708.7433 | -0.46861 | OK
13 | 11 kV Mission Para Feeder. | 11 |  | DHKC 9347 | 1 | 3983.86 | 32560.85 | 28576.99 | 60 |  | 1714619.4 | 1736094.2229 | N.Gonj (East) |  |  |  | 11 kV Mission Para Feeder. | 1736094.2229 | 1666330.9001 | 69763.3228 | 4.1866 | OK
14 | 11 kV Esha Kha Feeder | 11 |  | DHKC 9311 | 1 | 64482.72 | 79951.21 | 15468.49 | 60 |  | 928109.4 | 939733.5453 | N.Gonj (East) |  |  |  | 11 kV Esha Kha Feeder | 939733.5453 | 917602.1317 | 22131.4135 | 2.4119 | OK
15 | 11 kV New Hazigonj Feeder | 11 |  | DHKC 9314 | 1 | 134.23 | 170.34 | 36.11 | 60000 |  | 2166600 | 2193735.673 | N.Gonj (East) |  |  |  | 11 kV New Hazigonj Feeder | 2193735.673 | 2054393.8757 | 139341.7973 | 6.7826 | OK
16 | 11 kV Spare Feeder. | 11 |  | DHKC 9345 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Hospital RMU Feeder. | 11 |  | 6604412 | 1 | 3.83 | 4.9 | 1.07 | 60000 |  | 64200 | 65004.0756 | N.Gonj (East) |  |  |  | 11 kV Hospital RMU Feeder. | 65004.0756 | 61352.3895 | 3651.6861 | 5.952 | OK
20 | 11 kV Old Hajiganj Feeder. | 11 |  | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 |  | 0 | 0 | N.Gonj (East) |  |  |  | 11 kV Old Hajiganj Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Siraj-ud-daullah Feeder. | 11 |  | 06604389 | 1 | 84767.18 | 106245.25 | 21478.07 | 60 |  | 1288684.2 | 1304824.3795 | N.Gonj (East) |  |  |  | 11 kV Siraj-ud-daullah Feeder. | 1304824.3795 | 1324560.4284 | -19736.0489 | -1.49 | OK
22 | 11 kV Spare Feeder. | 11 |  | 8576983 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 |  | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 |  | 0 | 0 |  |  |  |  | Old 33/11 kV 10/14 MVA T1 Incoming | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV B. B. Road West Feeder. | 11 |  | 6604415 | 1 | 186.02 | 234.81 | 48.79 | 40000 |  | 1951600 | 1976042.8964 | N.Gonj (West) |  |  |  | 11 kV B. B. Road West Feeder. | 1976042.8964 | 1840166.7201 | 135876.1763 | 7.3839 | OK
26 | 11 kV Mondalpara Feeder. | 11 |  | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 |  | 0 | 0 |  |  |  |  | 11 kV Mondalpara Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV B. B. Road East Feeder. | 11 |  | 06604392 | 1 | 145.84 | 183.1 | 37.26 | 40000 |  | 1490400 | 1509066.5776 | N.Gonj (East) |  |  |  | 11 kV B. B. Road East Feeder. | 1509066.5776 | 1463548.0912 | 45518.4864 | 3.1101 | OK
28 | 11 kV Bishaw Road Feeder. | 11 |  | 06604393 | 1 | 191.13 | 221.32 | 30.19 | 40000 |  | 1207600 | 1222724.6371 | N.Gonj (East) |  |  |  | 11 kV Bishaw Road Feeder. | 1222724.6371 | 1779421.78 | -556697.1429 | -31.2853 | OK
29 | 11 kV Chasara Feeder. | 11 |  | 06604391 | 1 | 204.54 | 258.76 | 54.22 | 40000 |  | 2168800 | 2195963.227 | N.Gonj (West) |  |  |  | 11 kV Chasara Feeder. | 2195963.227 | 2115948.7484 | 80014.4786 | 3.7815 | OK
31 | 11 kV Pathan Tully Feeder. | 11 |  | 06604388 | 1 | 32.71 | 33.69 | 0.98 | 40000 |  | 39200 | 39690.9621 | N.Gonj (East) |  |  |  | 11 kV Pathan Tully Feeder. | 39690.9621 | 0 | 39690.9621 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder. | 11 |  | 9120051 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Nayamati Feeder. | 11 |  | 6604289 | 1 | 139.69 | 169.17 | 29.48 | 40000 |  | 1179200 | 1193968.9401 | N.Gonj (East) |  |  |  | 11 kV Nayamati Feeder. | 1193968.9401 | 1316545.3361 | -122576.396 | -9.3105 | OK
34 | 11 kV Spare Feeder. | 11 |  | DHKC9310 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
35 | 11 kV Spare Feeder. | 11 |  | DHKC9349 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Spare Feeder. | 11 |  | DHKC9312 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
37 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 |  | 412109 | 1 | 9109.5 | 9113.7 | 4.2 | 10 |  | 42 | 42.526 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-1 | 42.526 | 0 | 42.526 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 |  | 243285 | 1 | 6388.1 | 6433.2 | 45.1 | 10 |  | 3000 | 3037.5736 | N.Gonj (East) |  |  |  | 33/0.415 kV Auxiliary Transformer-2 | 3037.5736 | 3037.247 | 0.32662 | 0.010754 | OK
10: Grand Total | 16229659.6958 | 16028905 | 16229659.6958 | 1.2525
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (West) | at 33 KV level |  | 4172006.1234
[5 empty] | N.Gonj (East) | at 33 KV level |  | 12057653.5725
[5 empty] | Total = |  |  | 16229659.6958 | 0
1: 132 KV SIDE of___ MATUAIL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Siddirganj to Matuail | 132 | Impt | 8993555 | 1 | 2753.041 | 2779.681 | 26.64 | 1440000 | 0 | 38361600
|  | 132 | Expt |  | 1 | 771.699 | 771.699 | 0 | 1440000 | 0 | 0
2 | 132 kV Matuail Feeder at Maniknagar | 132 | Impt |  | 1 |  |  | 0 |  | 0 | 0
3: 132; 4: Expt; 6: 1; 9=8-7: 0 | 0
9=8-7: Total Import/Export | 0 | 38361600
10: Net Total | 38361600
MATUAIL 132 KV SIDE (RECEIVING)
2 | 132 kV Maniknagar Feeder | 132 | Impt |  | 1 |  |  | 0 | 1 | 0
|  | 132 |  | 06604365 | 1 | 85.57 | 85.57 | 0 | 960000 | 0
|  | 132 | Expt |  | 1 | 8832555 | 8832614 | 59 | 1 | 59
|  | 132 |  | 06604365 | 1 | 977.77 | 977.77 | 0 | 960000 |  | 0
3 | 132 kV Siddhirgonj Feeder | 132 | Impt | HA040700237-03 | 1 | 35292309 | 35292309 | 0 | 1
|  | 132 |  | 06604364 | 1 | 6049.84 | 6080.18 | 30.34 | 960000 | 29126400
|  | 132 | Expt | HA040700237-04 | 1 | 0 | 0 | 0 | 1 |  | 0
|  | 132 |  | 06604364 | 1 | 0 | 0 | 0 | 960000 |  | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 29126459 | 0
7: 0; 8: 0; 9=8-7: Net Total | 29126459
| MOGBAZAR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| MOGBAZAR 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 KV Transformer, GT-1 | 132 | DPDC | H/A040700240-03 | 1 | 118600.357 | 118600.357 | 0 | 1000 |  | 0
|  | 132 | P. Cell | 08993572 | 1 | 4908.847 | 4948.74 | 39.893 | 480000 |  | 19148640
5 | 132/33 KV Transformer, GT-2 | 132 | DPDC | H/A030700918-03 | 1 | 79349.314 | 98510.075 | 19160.761 | 1000 |  | 19160761
|  | 132 | P. Cell | 08993577 | 1 | 4970.503 | 5010.41 | 39.907 | 480000 |  | 19155360
10: Total |  | 19160761
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV Sending From Tariff; 4: 38361600; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 38361600
2: 132 KV Sending From Maniknagar; 4: 0; 6: 132 KV NET IMPORT; 9=8-7: 38361600 | 132/33 KV GT LV Side |  | 38360688
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 912
2: IMPORT-4 | LOSS % IN => |  | 0.002377%
| 132 KV TOTAL IMPORT |  | 38361600
1: 33 KV SIDE of___ MATUAIL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| MATUAIL 33 KV SIDE |  | IMPORT
9 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 10045.545 | 29290.486 | 19244.941 | 1000 | 19244941
|  | 33 | P. Cell | 08993574 | 1 | 2952.64 | 2952.64 | 0 | 480000 | 0
13 | 132/33 KV Transformer, GT-2 Incoming | 33 | DPDC | H/A060300186-03 | 1 | 30959.684 | 50075.431 | 19115.747 | 1000 | 19115747
|  | 33 | P. Cell | 08993574 | 1 | 3493.81 | 3493.81 | 0 | 480000 | 0
7: 0; 8: 0; 10: Total | 38360688 |  | 0
| MATUAIL 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
7 | 33/11 KV Transformer, T-3 | 33 | DPDC | H/A060300287-03 | 1.45 | 50642.239 | 57612.348 | 6970.109 | 1000 |  | 10106658.05 | 10183781.0075 |  | 18296620.4841 | Matuail 33/11 kv ss | 1.0417 | 33/11 KV Transformer, T-3 | 10183781.0075 | 9811264.6101 | 372516.3974 | 3.7968 | OK
|  | 33 | P. Cell | 08993576 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33/11 KV Transformer, T-4 | 33 | DPDC | H/A060300190-03 | 1 | 45927.458 | 53987.849 | 8060.391 | 1000 |  | 8060391 | 8121899.086 |  |  |  |  | 33/11 KV Transformer, T-4 | 8121899.086 | 8144263.6895 | -22364.6034 | -0.27461 | OK
|  | 33 | P. Cell | 08993581 | 1 | 6159.359 | 6204.089 | 44.73 | 180000 |  | 8051400 | 8112839.4765 |  |  |  |  | 0 | 8112839.4765 | 8151021.0157 | -38181.5392 | -0.46843 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 18158058.05 | 18296620.4841 |  |  |  |  | 33 KV Feeders | 18296620.4841 | 17962285.6258 | 334334.8582 | 1.8613 | OK
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 3380800 | 10239520 | 6858720 | 1 |  | 6858720 | 6911058.2476 |  | 16000533.9035 | Laxmi Narayan Cotton Mill 33/11 kv ss |  | 33 kV Laxmi Narayan Cotton Mill-1**** | 6911058.2476 | 7442785.5606 | -531727.313 | -7.1442 | OK
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 |  | 0 | 0 |  |  |  |  | 33 KV Fatullah Circuit-1 (F-1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC |  | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 10361 | 10440.0638 | Matuail |  |  |  | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 10440.0638 | 10260.3419 | 179.7219 | 1.7516 | OK
|  | 33 | P. Cell | 08993573 | 1 | 0 | 0 | 0 | 180000 |  | 0 | 0 |  | 0 | Fatullah 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 59915.41 | 63937.809 | 4022.399 | 1000 |  | 4022399 | 4053093.5487 |  |  |  |  | 33 KV Panchabati Bscic (Feeder-2) | 4053093.5487 | 4593162.3776 | -540068.829 | -11.7581 | OK
|  | 33 | P. Cell | 08993580 | 1.5 | 1330.064 | 1345.024 | 14.96 | 180000 |  | 4039200 | 4070022.7555 |  |  |  |  | 0 | 4070022.7555 | 4616247.6435 | -546224.888 | -11.8327 | OK
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 |  | 0 | 0 |  | 4053093.5487 | Narayangonj 33/11 kv ss |  | 33 KV Fatullah Circuit-2 (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 | DPDC | 00000154 | 1 | 1857280 | 10877920 | 9020640 | 1 |  | 9020640 | 9089475.6559 |  |  |  |  | 33 kV Laxmi Narayan Cotton Mill-2**** | 9089475.6559 | 9097409.1761 | -7933.5202 | -0.087206 | OK
10: Total |  | 19912120 | 20064067.5159 |  |  |  |  | 0 | 20064067.5159 | 21143617.4563 | -1079549.9403 | -5.1058 | OK
9=8-7: Grand Total | 38360688 | 38070178.05 | 38360688 | 0.76309
[5 empty] | 33 KV EXPORT |  |  | KWH
[5 empty] | EXPORT TO Matuail |  |  | 10440.0638
[5 empty] | Total Export |  |  | 10440.0638 | 0
1: 11 KV SIDE of___ MATUAIL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 11 KV SIDE
10 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426631 | 1 | 7421109 | 7534732 | 113623 | 90 | 10226070 |  | 10272343.6568
11 | 33/11 kV Transformer, T-4 Incoming | 11 |  | 51426633 | 1 | 7115652 | 7204409 | 88757 | 90 | 7988130 |  | 8024276.8273
7: 0; 8: 0; 10: Total | 18214200 |  | 18296620.4841
| MATUAIL 11 kV SIDE |  |  |  |  | 0 | 0
3 | 11 kV Link Road Feeder | 11 | Backup | DHK66629 | 1 | 23250.37 | 23573.72 | 323.35 | 8000 |  | 2586800 | 2613745.6256 | N.Gonj (East) |  |  |  | 11 kV Link Road Feeder | 2613745.6256 | 1956558.029 | 657187.5965 | 33.589 | OK
|  | 11 |  | HA021100475-02 | 1 | 85577.974 | 88158.496 | 2580.522 | 1000 |  | 2580522 | 2607402.2302 | N.Gonj (East) |  |  |  | 0 | 2607402.2302 | 1951841.3049 | 655560.9253 | 33.5868 | OK
4 | 11 kV Lamapara Express Feeder | 11 |  | HA021100928-03 | 1 | 76566.376 | 77285.778 | 719.402 | 1000 |  | 719402 | 726895.7131 | N.Gonj (East) |  |  |  | 11 kV Lamapara Express Feeder | 726895.7131 | 1017580.9915 | -290685.2785 | -28.5663 | OK
5 | 11 kV Kutubpur Feeder*** | 11 |  | DHK66616 | 1 | 17507.52 | 17710.59 | 203.07 | 8000 |  | 1624560 | 1641482.3695 | N.Gonj (East) |  |  |  | 11 kV Kutubpur Feeder*** | 1641482.3695 | 1554956.8642 | 86525.5053 | 5.5645 | OK
|  | 11 | Backup | XA575929 | 1 | 38974.7 | 40597.4 | 1622.7 | 1000 |  | 1622700 | 1639602.9947 | N.Gonj (East) |  |  |  | 0 | 1639602.9947 | 1553475.9142 | 86127.0804 | 5.5442 | OK
6 | 11 kV Ramarbagh Feeder (F1) | 11 |  | DHK66625 | 1 | 3485.92 | 3508.42 | 22.5 | 60000 |  | 1350000 | 1364062.3916 | Fatullah |  |  |  | 11 kV Ramarbagh Feeder (F1) | 1364062.3916 | 1338941.0426 | 25121.3489 | 1.8762 | OK
|  | 11 | Backup |  | 1 | 8395.82 | 8395.82 | 0 | 1000 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Tushardhara Feeder (F2) | 11 |  | DHK66623 | 1 | 3746.82 | 3791.19 | 44.37 | 60000 |  | 2662200 | 2689931.0362 | Matuail |  |  |  | 11 kV Tushardhara Feeder (F2) | 2689931.0362 | 2755784.1096 | -65853.0734 | -2.3896 | OK
8 | 11 kV Matuail Medical Feeder (F3) | 11 |  | DHK66627 | 1 | 3271.85 | 3284.92 | 13.07 | 60000 |  | 784200 | 792368.687 | Matuail |  |  |  | 11 kV Matuail Medical Feeder (F3) | 792368.687 | 795452.7012 | -3084.0142 | -0.38771 | OK
|  | 11 | Backup |  | 1 | 63825.371 | 63825.371 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Rupayan Town Feeder (F4) | 11 |  | HA021101044-02 | 1 | 65208.095 | 65554.037 | 345.942 | 1000 |  | 345942 | 349545.5347 | Matuail |  |  |  | 11 kV Rupayan Town Feeder (F4) | 349545.5347 | 361905.6203 | -12360.0856 | -3.4153 | OK
12 | 11 kV Shibu Market Feeder (F7) | 11 |  | DHK66624 | 1 | 2362.42 | 2368.99 | 6.57 | 60000 |  | 394200 | 398306.2183 | Fatullah |  |  |  | 11 kV Shibu Market Feeder (F7) | 398306.2183 | 387075.6832 | 11230.5351 | 2.9014 | OK
13 | 11 kV Soma-Sagar Steel (F6) | 11 |  | HA060300286-03 | 1 | 2.105 | 961.358 | 959.253 | 1000 | 959253 | 1486842.15 | 1502329.9696 | Fatullah | 20 days converted to 31 days |  |  | 11 kV Soma-Sagar Steel (F6) | 1502329.9696 | 1201993.7471 | 300336.2226 | 24.9865 | OK
14 | 11 kV Jhalkuri Feeder (F8) | 11 |  | DHK66626 | 1 | 4334.87 | 4378.18 | 43.31 | 60000 |  | 2598600 | 2625668.5413 | Matuail |  |  |  | 11 kV Jhalkuri Feeder (F8) | 2625668.5413 | 2669361.5514 | -43693.0101 | -1.6368 | OK
15 | 11 kV Madani Nagar Feeder (F9) | 11 | Backup | HA021100922-02 | 1 | 42215.368 | 42215.368 | 0 | 1000 |  | 0 | 0 | Matuail |  |  |  | 11 kV Madani Nagar Feeder (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK6622 | 1 | 4168.25 | 4189.27 | 21.02 | 60000 |  | 1261200 | 1274337.3987 | Matuail |  |  |  | 0 | 1274337.3987 | 1416234.4574 | -141897.0587 | -10.0193 | OK
16 | 11 kV Rajmahal Feeder (F10) | 11 |  | DHKA2187 | 1 | 108.4909 | 112.4599 | 3.969 | 60000 |  | 238140 | 240620.6059 | Shyampur |  |  |  | 11 kV Rajmahal Feeder (F10) | 240620.6059 | 244740.1643 | -4119.5584 | -1.6832 | OK
17 | 11 kV Bhuighor Bazar | 11 |  | HA021100861-02 | 1 | 74536.429 | 75324.363 | 787.934 | 1000 | Estimated | 1277144.82 | 1290448.3093 | Matuail | 105 |  |  | 11 kV Bhuighor Bazar | 1290448.3093 | 1462145.9342 | -171697.6249 | -11.7429 | OK
18 | 11 kV Tokkar Math Feeder | 11 |  | HA021200298-02 | 1 | 79511.406 | 80274.518 | 763.112 | 1000 |  | 763112 | 771061.022 | Fatullah |  |  |  | 11 kV Tokkar Math Feeder | 771061.022 | 778486.6953 | -7425.6732 | -0.95386 | OK
19 | 11 kV Osmani Stadium Feeder***** | 11 |  | XA575922 | 1 | 184 | 193.1 | 9.1 | 1000 |  | 9100 | 9194.7909 | Fatullah |  |  |  | 11 kV Osmani Stadium Feeder***** | 9194.7909 | 13287.9755 | -4093.1846 | -30.8037 | OK
16 | 33/0.415 KV Transformer, AT-1 | 0.415 |  | 2001123043119 | 1 | 7271 | 7351.2 | 80.2 | 160 |  | 12832 | 12965.6656 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-1 | 12965.6656 | 12496.7831 | 468.8826 | 3.752 | OK
17 | 33/0.415 KV Transformer, AT-2 | 0.415 |  | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 |  | 0 | 0 | Shyampur |  |  |  | 33/0.415 KV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 18296620.4841 | 18107996.97 | 18296620.4841 | 1.0417
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 4975780.3128
6: Shyampur; 7: at 33 KV level; 9=8-7: 253586.2715 | Import From Matuail & Narinda |  | 550000
[5 empty] | Fatullah | at 33 KV level |  | 4044954.3925
6: Matuail; 7: at 33 KV level; 9=8-7: 9322299.5072 | Import From Shyampur |  | 300000
[5 empty] | Total = |  |  | 18596620.4841 | 300000
1: 33 KV SIDE of___LAXMI NARAYAN COTTON MILL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
6 | 33 kV Laxmi Narayan Cotton Mill-1**** | 33 | DPDC | 00000073 | 1 | 3380800 | 10239520 | 6858720 | 1 | 0 | 6858720 | 6911058.2476
15 | 33 kV Laxmi Narayan Cotton Mill-2**** | 33 |  | 00000154 | 1 | 1857280 | 10877920 | 9020640 | 1 | 0 | 9020640 | 9089475.6559
10: Total | 0 | 15879360 | 16000533.9035
LAXMI NARAYAN COTTON MILL 33 KV SIDE (RECEIVING)
3 | 33 kV Matuail-2 Feeder | 33 |  | 00000079 | 1 | 319364640 | 328295968 | 8931328 | 1 | 8931328
7 | 33 kV Matuail-1 Feeder | 33 |  | 00000114 | 1 | 261599760 | 268405376 | 6805616 | 1 | 6805616
7: 0; 8: 0; 10: Total | 15736944 | 0 | 0
| LAXMI NARAYAN COTTON MILL KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| LAXMI NARAYAN COTTON MILL 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000075 | 1 | 334076864 | 343010400 | 8933536 | 1 |  | 8933536
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000156 | 1 | 246952320 | 253757760 | 6805440 | 1 |  | 6805440
10: Total |  | 15738976
2: 33 KV IMPORT; 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | BUS LOSS |  | KWH
2: MATUAIL 33 KV SIDE; 4: 16000533.9035; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 16000533.9035
2: IMPORT-2; 6: 33 KV Net Import; 9=8-7: 16000533.9035 | 33 KV TX HV Side |  | 15738976
2: IMPORT-3 | LOSS UNITS=> |  | 261557.9035
2: IMPORT-4 | LOSS % IN => |  | 1.635%
| TOTAL IMPORT |  | 16000533.9035
1: 11 KV SIDE of___ LAXMI NARAYAN COTTON MILL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
LAXMI NARAYAN COTTON MILL 11 KV SIDE
17 | 11 kV T-2 Incoming | 11 |  | 00000144 | 1 | 332845958 | 341752352 | 8906394 | 1 | 8906394 |  | 9084635.3566
18 | 11 kV T-1 Incoming | 11 |  | 00000054 | 1 | 245411520 | 252191728 | 6780208 | 1 | 6780208 |  | 6915898.5468
7: 0; 8: 0; 10: Total | 15686602 |  | 16000533.9035
| LAXMI NARAYAN COTTON MILL 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Godnail (F16) | 11 |  | 00000109 | 1 | 22845784 | 24749340 | 1903556 | 1 |  | 1903556 | 1902174.2906 | Siddirgonj |  |  |  | 11 kV Godnail (F16) | 1902174.2906 | 1848814.9706 | 53359.3201 | 2.8861 | OK
2 | 11 kV M. Circus (F15) | 11 |  | 00000123 | 1 | 105458624 | 107396816 | 1938192 | 1 |  | 1938192 | 1936785.1498 | N.Gonj (East) |  |  |  | 11 kV M. Circus (F15) | 1936785.1498 | 1975646.3394 | -38861.1896 | -1.967 | OK
3 | 11 kV Wapderpool (F14) | 11 |  | 00000190 | 1 | 55796344 | 56271624 | 475280 | 1 |  | 475280 | 474935.0147 | N.Gonj (East) |  |  |  | 11 kV Wapderpool (F14) | 474935.0147 | 619875.2088 | -144940.1941 | -23.3822 | OK
4 | 11 kV Chowdhury Bari (F13) | 11 |  | 00000191 | 1 | 96441288 | 98646920 | 2205632 | 1 |  | 2205632 | 2204031.0267 | Siddirgonj |  |  |  | 11 kV Chowdhury Bari (F13) | 2204031.0267 | 2287431.9192 | -83400.8925 | -3.646 | OK
5 | 11 kV Ailpara (F12) | 1 |  | 00000192 | 1 | 49107040 | 51494196 | 2387156 | 1 |  | 2387156 | 2385423.2662 | N.Gonj (East) |  |  |  | 11 kV Ailpara (F12) | 2385423.2662 | 2312455.9158 | 72967.3504 | 3.1554 | OK
6 | 11 kV Spare (F11) | 11 |  | 00000193 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Spare (F10) | 11 |  | 00000194 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare (F9) | 11 |  | 00000195 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Spare (F8) | 11 |  | 00000196 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare (F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Zulfiqur Steel | 11 |  | 00000197 | 1 | 14248885 | 15359563 | 1110678 | 1 |  | 1110678 | 1109871.8066 | Siddirgonj |  |  |  | 11 kV Zulfiqur Steel | 1109871.8066 | 1233882.0915 | -124010.2849 | -10.0504 | OK
11 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 |  | 00000198 | 1 | 3997630 | 4078510 | 80880 | 1 |  | 80880 | 80821.2927 | N.Gonj (East) |  |  |  | 11 kV New Laxmi Narayan Cotton Mill (F6) | 80821.2927 | 12574.267 | 68247.0257 | 542.7515 | FAULT
12 | 11 kV Lucky Bazar (F5) | 11 |  | 00000199 | 1 | 87124224 | 88391024 | 1266800 | 1 |  | 1266800 | 1265880.4844 | N.Gonj (East) |  |  |  | 11 kV Lucky Bazar (F5) | 1265880.4844 | 1332623.2308 | -66742.7464 | -5.0084 | OK
13 | 11 kV Enayetnagar (F4) | 11 |  | 00000200 | 1 | 29163608 | 30771724 | 1608116 | 1 |  | 1608116 | 1606948.7378 | Siddirgonj |  |  |  | 11 kV Enayetnagar (F4) | 1606948.7378 | 1544300.7721 | 62647.9657 | 4.0567 | OK
14 | 11 kV Bhuiyapara (F3) | 11 |  | 00000201 | 1 | 62323408 | 64028044 | 1704636 | 1 |  | 1704636 | 1703398.6781 | Siddirgonj |  |  |  | 11 kV Bhuiyapara (F3) | 1703398.6781 | 2021560.4921 | -318161.814 | -15.7384 | OK
15 | 11 kV Arambagh (F2) | 11 |  | 00000202 | 1 | 6951863 | 7963900.5 | 1012037.5 | 1 |  | 1012037.5 | 1011302.9055 | N.Gonj (East) |  |  |  | 11 kV Arambagh (F2) | 1011302.9055 | 1033739.3311 | -22436.4256 | -2.1704 | OK
16 | 11 kV Spare (F1) | 11 |  | 00000203 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Siddirgonj |  |  |  | 11 kV Spare (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11/0.415 kV Aux. Transformer-1 | 0.415 |  | 00000204 | 1 | 1577 | 1627.32 | 50.32 | 100 |  | 5032 | 5028.3475 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-1 | 5028.3475 | 4509.4616 | 518.8859 | 11.5066 | OK
18 | 11/0.415 kV Aux. Transformer-2 | 0.415 |  | 00000205 | 1 | 60.71 | 60.72 | 0.01 | 100 |  | 1 | 0.99927 | N.Gonj (East) |  |  |  | 11/0.415 kV Aux. Transformer-2 | 0.99927 | 0 | 0.99927 | #DIV/0! | #DIV/0!
10: Grand Total | 15686602 | 15697996.5 | 15686602 | -0.072586
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 7160177.4602
[5 empty] | Siddirgonj | at 33 KV level |  | 8526424.5398
[5 empty] | Total = |  |  | 15686602 | 0
1: 33 KV SIDE of___ FATULLAH OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MATUAIL 33 KV SIDE
8 | 33 KV Fatullah Circuit-1 (F-1) | 33 | DPDC | H/A060300311-03 | 1.5 | 39497.251 | 39497.251 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993575 | 1.5 | 3439.516 | 3439.516 | 0 | 180000 | 0 | 0 | 0
14 | 33 KV Fatullah Circuit-2 (F-4) | 33 | DPDC | HA021100940-02 | 1.5 | 42619.196 | 42619.196 | 0 | 1000 | 0 | 0 | 0
0 | 0 | 33 | P. Cell | 08993578 | 1.5 | 3846.344 | 3846.344 | 0 | 180000 | 0 | 0 | 0
2: New Fatullah 33 kv Side; 10: Total | 0 | 0 | 0
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 659.92 | 685.41 | 25.49 | 360000 | 0 | 9176400 | 9160820.3735
0 | 0 | 33 | Backup | 041808904262 | 1 | 659.94 | 685.39 | 25.45 | 360000 | 0 | 9162000 | 9146444.8217
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 468.43 | 483.44 | 15.01 | 360000 | 0 | 5403600 | 5394425.8065
0 | 0 | 33 | Backup | 041808904258 | 1 | 468.61 | 483.26 | 14.65 | 360000 | 0 | 5274000 | 5265045.8404
10: Total | 0 | 14580000 | 14555246.18
FATULLAH OLD 33 KV SIDE (RECEIVING)
8 | 33 kV New Fatulla-1 (Previous Matuail Feeder-1) | 33 | Digital | DHK60875 | 1 | 193655.1 | 231451.9 | 37796.8 | 240 | 9071232
9 | 33 kV New Fatulla-2 | 33 | Digital | DHK2186 | 1 | 312.8299 | 327.6931 | 14.8632 | 360000 | 5350752
7: 0; 8: 0; 10: Total | 14421984 | 0 | 0
| FATULLAH OLD 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| FATULLAH OLD 33 KV SIDE |  |  |  |  | 0 | 0
12 | 33/11 kV, 20/28 MVA T-1 (HV) | 33 | Digital | DHK60980 | 1 | 897422.1 | 923239.5 | 25817.4 | 240 |  | 6196176
13 | 33/11 kV, 20/28 MVA T-2 (HV) | 33 | Digital | DHK60952 | 1 | 493721.2 | 505636.6 | 11915.4 | 240 |  | 9071232 |  |  | Meter Problem
10: Total |  | 15267408 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV Net Import; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MATUAIL 33 KV SIDE; 4: 0; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV Net Import |  | 14555246.18
2: New Fatullah 33 kv Side; 4: 14555246.18; 6: 33 KV Net Import; 9=8-7: 14555246.18 | 33 KV TX HV Side |  | 15267408
[10 empty] | LOSS UNITS=> |  | -712161.82
[10 empty] | LOSS % IN => |  | -4.893%
| TOTAL IMPORT |  | 14555246.18
1: 11 KV SIDE of___FATULLAH OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15 | [5 empty] | 0 | #DIV/0! | #DIV/0!
2: FATULLAH OLD 11 KV SIDE | [10 empty] | 0 | #DIV/0! | #DIV/0!
21 | 33/11 kV, 20/28 MVA T-1 Incoming | 11 | New | DHK61060 | 1 | 1009715.8 | 1009715.8 | 0 | 180 | 0 | [9 empty] | 0 | #DIV/0! | #DIV/0!
22 | 33/11 kV, 20/28 MVA T-2 Incoming | 11 | New | DHK61054 | 1 | 376872.2 | 392742.5 | 15870.3 | 180 | 2856654 |  | 5106826.7359 | [7 empty] | 0 | #DIV/0! | #DIV/0!
31 | 33/11 kV, 20/28 MVA T-3 Incoming | 11 | New | DHK60924 | 1.1 | 458218.3 | 465543.4 | 7325.1 | 180 | 1450369.8 |  | 2592819.1764 | [7 empty] | 0 | #DIV/0! | #DIV/0!
32 | 33/11 kV, 10/14 MVA T-4 Incoming | 11 | New | DHK61051 | 1 | 859768.4 | 902378.2 | 42609.8 | 90 | 3834882 |  | 6855600.2676 | [7 empty] | 0 | #DIV/0! | #DIV/0!
7: 0; 8: 0; 10: Total | 8141905.8 |  | 14555246.18 | [7 empty] | 0 | #DIV/0! | #DIV/0!
2: FATULLAH OLD 11 KV SIDE; 7: 0; 8: 0 | [10 empty] | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Minan Steel Feeder | 11 | New |  | 1 | 74957542 | 75456997 | 499455 | 1 |  | 499455 | 493276.6302 | N.Gonj (West) |  |  |  | 11 kV Minan Steel Feeder | 493276.6302 | 608736.535 | -115459.9048 | -18.9671 | OK
15 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 87261856 | 87945628 | 683772 | 1 |  | 683772 | 675313.5877 | N.Gonj (West) |  |  |  | 11 kV Shovon Garments | 675313.5877 | 687996.4568 | -12682.8691 | -1.8434 | OK
16 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 105562.1 | 129693.5 | 24131.4 | 60 |  | 1447884 | 1429973.3518 | Fatullah |  |  |  | 11 kV Mazar O/H Feeder | 1429973.3518 | 1348752.6633 | 81220.6885 | 6.0219 | OK
17 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shahjahan Steel. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 291780 | 308379.7 | 16599.7 | 60 |  | 995982 | 983661.4804 | Fatullah |  |  |  | 11 kV Pilkuni O/H Feeder. | 983661.4804 | 966418.4358 | 17243.0445 | 1.7842 | OK
19 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 938604.3 | 976902.1 | 38297.8 | 60 |  | 2297868 | 2269442.86 | Fatullah |  |  |  | 11 kV Narayangonj Express Feeder. | 2269442.86 | 1903765.6601 | 365677.1998 | 19.2081 | OK
20 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 48136.4 | 59040.7 | 10904.3 | 60 |  | 654258 | 646164.6825 | Fatullah |  |  |  | 11 kV Post Office Road Feeder. | 646164.6825 | 667510.2274 | -21345.5449 | -3.1978 | OK
23 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 602547.3 | 616341.5 | 13794.2 | 60 |  | 827652 | 817413.76 | Fatullah |  |  |  | 11 kV Fatullah Feeder. | 817413.76 | 827156.9088 | -9743.1487 | -1.1779 | OK
24 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 486964.4 | 504567.7 | 17603.3 | 60 |  | 1056198 | 1043132.595 | Fatullah |  |  |  | 11 kV Al-baraka & Shah Fatullah. | 1043132.595 | 1256184.2479 | -213051.6529 | -16.9602 | OK
25 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 860387.5 | 864279.2 | 3891.7 | 60 |  | 233502 | 230613.5281 | Fatullah |  |  |  | 11 kV Haque Steel & Shilpi Steel | 230613.5281 | 268951.939 | -38338.4108 | -14.2547 | OK
26 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 501840.9 | 514317.3 | 12476.4 | 60 |  | 748584 | 739323.8488 | Fatullah |  |  |  | 11 kV Dhaka Steel | 739323.8488 | 888156.2557 | -148832.4069 | -16.7575 | OK
27 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 99488328 | 100229225 | 740897 | 1 |  | 740897 | 731731.9387 | Sytalakhya |  |  |  | 11 kV Panchabati O/H Feeder | 731731.9387 | 686782.5544 | 44949.3843 | 6.5449 | OK
28 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24567287 | 24889601 | 322314 | 1 |  | 322314 | 318326.9039 | Sytalakhya |  |  |  | 11 kV Dharmagonj Feeder. | 318326.9039 | 335635.5116 | -17308.6077 | -5.157 | OK
29 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14795210 | 15173750 | 378540 | 1 |  | 378540 | 373857.3757 | Sytalakhya |  |  |  | 11 kV Sena Edible Oil Feeder. | 373857.3757 | 329133.6781 | 44723.6976 | 13.5883 | OK
30 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Kutubail Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 |  | 0 | 0 | Fatullah | No Load |  |  | 11 kV Aligonj Feeder | 0 | 123409.7429 | -123409.7429 | -100 | CHECK
34 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 11860750 | 13842626 | 1981876 | 1 |  | 1981876 | 1957359.7515 | Fatullah |  |  |  | 11 kV Gabtoli Feeder | 1957359.7515 | 2145386.8814 | -188027.1299 | -8.7643 | OK
35 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Jamuna Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
36 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 2718344 | 4587115 | 1868771 | 1 |  | 1868771 | 1845653.8856 | Fatullah |  |  |  | 11 kV Bishwa Road Feeder | 1845653.8856 | 1844325.072 | 1328.8136 | 0.072049 | OK
37 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 |  | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 33/0.415 kV, 200 kVA, AT-1+2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 14555246.18 | 14737553 | 14555246.18 | -1.237
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 11962739.7437
[5 empty] | N.Gonj (West) | at 33 KV level |  | 1168590.2179
[5 empty] | Sytalakhya | at 33 KV level |  | 1423916.2183
[5 empty] | Total = |  |  | 14555246.18 | 0
1: 132 KV SIDE of___ NEW FATULLAH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | 132 kV Shyampur-1 Feeder | 132 | Export | 041808902770 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904227 | 1 | 126.94 | 126.94 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902770 | 1 | 172.02 | 187.67 | 15.65 | 1200000 | 18780000
|  | 132 |  | 041808904227 | 1 | 172 | 187.64 | 15.64 | 1200000 | 18768000
3 | 132 kV Haripur Feeder | 132 | Export | 041808902766 | 1 | 52.36 | 52.36 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904230 | 1 | 52.38 | 52.38 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902766 | 1 | 719.42 | 719.42 | 0 | 1200000 | 0
|  | 132 |  | 041808904230 | 1 | 719.67 | 719.67 | 0 | 1200000 | 0
4 | 132 kV Aggreko Feeder | 132 | Export | 041808902768 | 1 | 30.52 | 30.52 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904219 | 1 | 30.52 | 30.52 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902768 | 1 | 257.68 | 257.68 | 0 | 1200000 | 0
|  | 132 |  | 041808904219 | 1 | 257.68 | 257.68 | 0 | 1200000 | 0
6 | 132 kV Shyampur-2 Feeder | 132 | Export | 041808902793 | 1 | 120.72 | 120.72 | 0 | 1200000 |  | 0
|  | 132 |  | 041808904278 | 1 | 120.73 | 120.73 | 0 | 1200000 |  | 0
|  | 132 | Import | 041808902793 | 1 | 163.55 | 179.32 | 15.77 | 1200000 | 18924000
|  | 132 |  | 041808904278 | 1 | 163.58 | 179.36 | 15.78 | 1200000 | 18936000
7: 0; 8: 0; 9=8-7: Total Import/Export | 37704000 | 0
7: 0; 8: 0; 10: Net Total | 37704000
| NEW FATULLAH 132 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 0 | 0
7: 0; 8: 0; 9=8-7: Net Total | 0
| FATULLAH 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| FATULLAH 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV, 80/120 MVA GT-1 | 132 | Export | 041808902767 | 1 | 557.72 | 575.53 | 17.81 | 1200000 |  | 21372000
|  | 132 | Export | 041808904228 | 1 | 557.58 | 575.38 | 17.8 | 1200000 |  | 21360000
5 | 132/33 kV, 80/120 MVA GT-2 | 132 | Export | 041808902792 | 1 | 427.55 | 441.17 | 13.62 | 1200000 |  | 16344000
|  | 132 | Export | 041808904251 | 1 | 427.39 | 441 | 13.61 | 1200000 |  | 16332000
10: Total |  | 37716000
2: 132 KV IMPORT; 4: KWH | TRANSMISSION LOSS |  | KWH
2: 132 Sending Side; 4: 37704000 | 132 KV NET IMPORT |  | 37704000
2: IMPORT-2 | 132/33 KV GT LV Side |  | 37396800
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 307200
2: IMPORT-4 | LOSS % IN => |  | 0.8148%
| 132 KV TOTAL IMPORT |  | 37704000
1: 33 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902796 | 1 | 925.15 | 954.68 | 29.53 | 720000 | 21261600
|  | 33 | Backup | 041808904255 | 1 | 925.15 | 954.68 | 29.53 | 720000 | 21261600
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902802 | 1 | 709.49 | 731.9 | 22.41 | 720000 | 16135200
|  | 33 | Backup | 041808904281 | 1 | 709.32 | 732.09 | 22.77 | 720000 | 16394400
7: 0; 8: 0; 10: Total | 37396800 |  | 0
| FATULLAH 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902868 | 1 | 731.27 | 755.4 | 24.13 | 240000 |  | 5791200 | 5781367.7419 |  | 11740033.9559 | New Fatullah 33/11 kv ss | 0.078394 | 33/11 kV, 28/35 MVA T-1 (=H5) | 5781367.7419 | 5817672.9516 | -36305.2097 | -0.62405 | OK
|  | 33 | Backup | 041808904277 | 1 | 730.82 | 755.88 | 25.06 | 240000 |  | 6014400 | 6004188.7946 |  |  |  |  | 0 | 6004188.7946 | 5812876.8486 | 191311.9459 | 3.2912 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902824 | 1 | 635.51 | 660.38 | 24.87 | 240000 |  | 5968800 | 5958666.2139 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 5958666.2139 | 5417198.3503 | 541467.8636 | 9.9953 | OK
|  | 33 | Backup | 041808904267 | 1 | 635.41 | 660.48 | 25.07 | 240000 |  | 6016800 | 6006584.7199 |  |  |  |  | 0 | 6006584.7199 | 5414800.2988 | 591784.4211 | 10.929 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 11760000 | 11740033.9559 |  |  |  |  | 33 KV Feeders | 11740033.9559 | 11234871.3019 | 505162.6539 | 4.4964 | OK
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 729.74 | 746.6 | 16.86 | 360000 |  | 6069600 | 6059295.0764 |  | 11101519.8642 | Dapa 33/11 kv ss |  | 33 kV Dapa Circuit-1 (=H1) | 6059295.0764 | 6294885.2012 | -235590.1248 | -3.7426 | OK
|  | 33 | Backup | 041808904220 | 1 | 729.37 | 746.97 | 17.6 | 360000 |  | 6336000 | 6325242.7844 |  |  |  |  | 0 | 6325242.7844 | 6291288.1239 | 33954.6605 | 0.53971 | OK
10 | 33 kV Outgoing Feeder-2 (=H2) | 33 | Main | 041808902872 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-2 (=H2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904260 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Fatullah Old Circuit-1 (=H3) | 33 | Main | 041808902828 | 1 | 659.92 | 685.41 | 25.49 | 360000 |  | 9176400 | 9160820.3735 |  | 14555246.18 | Old Fatullah 33/11 kv ss |  | 33 kV Fatullah Old Circuit-1 (=H3) | 9160820.3735 | 9456716.1108 | -295895.7373 | -3.1289 | OK
|  | 33 | Backup | 041808904262 | 1 | 659.94 | 685.39 | 25.45 | 360000 |  | 9162000 | 9146444.8217 |  |  |  |  | 0 | 9146444.8217 | 9456716.1108 | -310271.2891 | -3.281 | OK
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902827 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904264 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 502.29 | 516.32 | 14.03 | 360000 |  | 5050800 | 5042224.7878 |  |  |  |  | 33 kV Dapa Circuit-2 (=H11) | 5042224.7878 | 4503540.7268 | 538684.061 | 11.9613 | OK
|  | 33 | Backup | 041808904219 | 1 | 502.59 | 516.01 | 13.42 | 360000 |  | 4831200 | 4822997.6231 |  |  |  |  | 0 | 4822997.6231 | 4507137.804 | 315859.819 | 7.008 | OK
18 | 33 kV Fatullah Old Circuit-2 (=H12) | 33 | Main | 041808902873 | 1 | 468.43 | 483.44 | 15.01 | 360000 |  | 5403600 | 5394425.8065 |  |  |  |  | 33 kV Fatullah Old Circuit-2 (=H12) | 5394425.8065 | 5431586.6593 | -37160.8529 | -0.68416 | OK
|  | 33 | Backup | 041808904258 | 1 | 468.61 | 483.26 | 14.65 | 360000 |  | 5274000 | 5265045.8404 |  |  |  |  | 0 | 5265045.8404 | 5431586.6593 | -166540.8189 | -3.0662 | OK
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808904287 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808902819 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Outgoing Feeder-8 (=H14) | 33 | Main | 041808902847 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Outgoing Feeder-8 (=H14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904248 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907981 | 1 | 1135.45 | 1135.45 | 0 | 1 |  |  | 0 |  |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total |  | 25700400 | 25656766.0441 |  |  |  |  | 0 | 25656766.0441 | 25686728.6981 | -29962.6539 | -0.11665 | OK
9=8-7: Grand Total | 37396800 | 37460400 | 37396800 | -0.16978
1: 11 KV SIDE of___NEW FATULLAH 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FATULLAH 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902832 | 1 | 700.01 | 723.58 | 23.57 | 250000 | 5892500 |  | 5826755.1135
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902765 | 1 | 608.24 | 632.16 | 23.92 | 250000 | 5980000 |  | 5913278.8424
7: 0; 8: 0; 10: Total | 11872500 |  | 11740033.9559
| FATULLAH 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902834 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Outgoing Feeder-2 (=F2) | 11 |  | 041808902801 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-2 (=F2) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 855.85 | 887.81 | 31.96 | 60000 |  | 1917600 | 1919103.2774 | Sytalakhya |  |  |  | 11 kV Morakhalpar (=F3) | 1919103.2774 | 1925513.8961 | -6410.6187 | -0.33293 | OK
7 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 390.79 | 414.63 | 23.84 | 60000 |  | 1430400 | 1431521.3433 | Sytalakhya |  |  |  | 11 kV Achimtola (=F4) | 1431521.3433 | 1476167.1668 | -44645.8235 | -3.0244 | OK
8 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 518.47 | 530.35 | 11.88 | 60000 |  | 712800 | 713358.7902 | Sytalakhya |  |  |  | 11 kV Horihorpara (=F5) | 713358.7902 | 702593.0118 | 10765.7784 | 1.5323 | OK
9 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1147.26 | 1177.63 | 30.37 | 60000 |  | 1822200 | 1823628.4898 | Sytalakhya |  |  |  | 11 kV Amtola Feeder (=F6) | 1823628.4898 | 1708359.7204 | 115268.7694 | 6.7473 | OK
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902774 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902760 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902755 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Outgoing Feeder-10 (=F8) | 11 |  | 041808902788 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-10 (=F8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Outgoing Feeder-11 (=F9) | 11 |  | 041808902785 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-11 (=F9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 135.99 | 157.05 | 21.06 | 60000 |  | 1263600 | 1264590.5826 | Sytalakhya |  |  |  | 11 kV Nabinagar (=F10) | 1264590.5826 | 1201867.1554 | 62723.4273 | 5.2188 | OK
16 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 58.08 | 68.32 | 10.24 | 60000 |  | 614400 | 614881.6508 | Sytalakhya |  |  |  | 11 kV Dhalipara (=F11) | 614881.6508 | 573262.9625 | 41618.6883 | 7.26 | OK
17 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1064.3 | 1090.6 | 26.3 | 60000 |  | 1578000 | 1579237.0524 | Sytalakhya |  |  |  | 11 kV Etimkhana (=F12) | 1579237.0524 | 1146525.925 | 432711.1274 | 37.7411 | OK
18 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1275.93 | 1318 | 42.07 | 60000 |  | 2524200 | 2526178.8135 | Sytalakhya |  |  |  | 11 kV Premroad (=F13) | 2526178.8135 | 2500581.4639 | 25597.3495 | 1.0237 | OK
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902781 | 1 | 0 | 0 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 11872500 | 11863200 | 11872500 | 0.078394
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 11872500
[5 empty] | Total = |  |  | 11872500 | 0
1: 33 KV SIDE of___DAPA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NEW FATULLAH 33 KV SIDE
9 | 33 kV Dapa Circuit-1 (=H1) | 33 | Main | 041808902822 | 1 | 729.74 | 746.6 | 16.86 | 360000 | 0 | 6069600 | 6059295.0764
0 | 0 | 33 | Backup | 041808904220 | 1 | 729.37 | 746.97 | 17.6 | 360000 | 0 | 6336000 | 6325242.7844
17 | 33 kV Dapa Circuit-2 (=H11) | 33 | Main | 041808902825 | 1 | 502.29 | 516.32 | 14.03 | 360000 | 0 | 5050800 | 5042224.7878
0 | 0 | 33 | Backup | 041808904219 | 1 | 502.59 | 516.01 | 13.42 | 360000 | 0 | 4831200 | 4822997.6231
2: DAPA 33 KV SIDE (RECEIVING); 10: Total | 0 | 11120400 | 11101519.8642
5 | 33 kV New Fatullah Incoming Circuit-2 | 33 | Import |  | 1 | 180495536 | 185429248 | 4933712 | 1 | 4933712
6 | 33 kV Shyampur Incoming Circuit | 33 | Import | 00000186 | 1 | 108089912 | 108089912 | 0 | 1 | 0
8 | 33 kV Old Fatullah Feeder | 33 | Export | 00000185 | 1 | 23104980 | 23104980 | 0 | 1 |  | 0
|  | 33 | Import | 00000185 | 1 | 3086100 | 3086100 | 0 | 1 | 0
9 | 33 kV New Fatullah Incoming Circuit-1 | 33 | Import |  | 1 | 262254512 | 268448864 | 6194352 | 1 | 6194352
7: 0; 8: 0; 10: Total | 11128064 | 0 | 0
| DAPA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| DAPA 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV, 28/35 MVA T-2 Transformer (HV) | 33 | Export | 00000135 | 1 | 272058944 | 276992640 | 4933696 | 1 |  | 4933696
10 | 33/11 kV, 28/35 MVA T-1 Transformer (HV) | 33 | Export | 00000193 | 1 | 263941440 | 270130304 | 6188864 | 1 |  | 6188864
10: Total |  | 11122560 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: NEW FATULLAH 33 KV SIDE; 4: 11101519.8642; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 11101519.8642
6: 33 KV NET IMPORT; 9=8-7: 11101519.8642 | 33 KV TX HV SIDE |  | 11122560
[10 empty] | LOSS UNITS=> |  | -21040.1358
[10 empty] | LOSS % IN => |  | -0.1895%
| TOTAL IMPORT |  | 11101519.8642
1: 11 KV SIDE of___DAPA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
DAPA 11 KV SIDE
16 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 00000035 | 1 | 62408928 | 68569536 | 6160608 | 1 | 6160608 |  | 6174463.526
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000143 | 1 | 270876320 | 275792320 | 4916000 | 1 | 4916000 |  | 4927056.3382
7: 0; 8: 0; 10: Total | 11076608 |  | 11101519.8642
| DAPA 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11 kV Katherpol Feeder | 11 |  | 00000031 | 1 | 61558008 | 63394284 | 1836276 | 1 |  | 1836276 | 1872668.2415 | Fatullah |  |  |  | 11 kV Katherpol Feeder | 1872668.2415 | 1825325.1091 | 47343.1324 | 2.5937 | OK
12 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Union Parishad Feeder | 11 |  | 00000032 | 1 | 63039328 | 64364204 | 1324876 | 1 |  | 1324876 | 1351133.0591 | Fatullah |  |  |  | 11 kV Union Parishad Feeder | 1351133.0591 | 1174339.0851 | 176793.974 | 15.0548 | OK
14 | 11 kV Shiachar Feeder | 11 |  | 00000030 | 1 | 63888724 | 65776000 | 1887276 | 1 |  | 1887276 | 1924678.9852 | Fatullah |  |  |  | 11 kV Shiachar Feeder | 1924678.9852 | 1907532.8668 | 17146.1184 | 0.89886 | OK
15 | 11 kV Sastapur Feeder | 11 |  | 00000106 | 1 | 69229072 | 70349912 | 1120840 | 1 |  | 1120840 | 1143053.371 | Fatullah |  |  |  | 11 kV Sastapur Feeder | 1143053.371 | 1344939.9892 | -201886.6182 | -15.0108 | OK
17 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Jalal Ahmed Express | 11 |  | 00000172 | 1 | 4960188 | 4960348 | 160 | 1 |  | 160 | 163.171 | Fatullah |  |  |  | 11 kV Jalal Ahmed Express | 163.171 | 71453.7073 | -71290.5363 | -99.7716 | CHECK
19 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  |  | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Lalpur Feeder | 11 |  | 00000044 | 1 | 76099056 | 77520128 | 1421072 | 1 |  | 1421072 | 1449235.5198 | Fatullah |  |  |  | 11 kV Lalpur Feeder | 1449235.5198 | 1159780.4978 | 289455.022 | 24.9577 | OK
23 | 11 kV Kotaler Bag Feeder | 11 |  | 00000050 | 1 | 81048560 | 82482440 | 1433880 | 1 |  | 1433880 | 1462297.3552 | Fatullah |  |  |  | 11 kV Kotaler Bag Feeder | 1462297.3552 | 1401235.8745 | 61061.4807 | 4.3577 | OK
24 | 11 kV Idrakpur Feeder | 11 |  | 00000021 | 1 | 74625056 | 75647336 | 1022280 | 1 |  | 1022280 | 1042540.0593 | Fatullah |  |  |  | 11 kV Idrakpur Feeder | 1042540.0593 | 1114166.2721 | -71626.2128 | -6.4287 | OK
25 | 11 kV Isdair Feeder | 11 |  | 00000029 | 1 | 39230944 | 40064264 | 833320 | 1 |  | 833320 | 849835.155 | Fatullah |  |  |  | 11 kV Isdair Feeder | 849835.155 | 794122.676 | 55712.4789 | 7.0156 | OK
26 | 11 kV Shah Fateullah Express | 11 |  | 0000051 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Shah Fateullah Express | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 |  | DHKF 7522 | 1 | 2955 | 3013 | 58 | 100 |  | 5800 | 5914.9473 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-1 | 5914.9473 | 5529.8501 | 385.0972 | 6.964 | OK
30 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 |  | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah |  |  |  | 11/0.415 kV Auxiliary Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 11101519.8642 | 10885780 | 11101519.8642 | 1.9819
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 11101519.8642
[5 empty] | Total = |  |  | 11101519.8642 | 0
1: 132 KV SIDE of___SITALAKHYA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Tranformer 3 | 132 | IMPORT | 50501730 | 1 | 2778.291 | 2821.29 | 42.999 | 480000 | 0 | 20639520
2 | Tranformer 1 | 132 |  | 80505634 | 1 | 8380.88 | 8421.345 | 40.465 | 480000 | 0 | 19423200
3 | Tranformer 2 | 132 |  | 80505637 | 1 | 8332.942 | 8373.619 | 40.677 | 480000 | 0 | 19524960
4 | MI CEMENT | 132 |  | 38992489 (New) | 1 | 256.334 | 278.728 | 22.394 | 480000 | 0 | 10749120
9=8-7: Total Import/Export | 0 | 70336800
10: Net Total | 70336800
SITALAKHYA 132 KV SIDE (RECEIVING)
132
132
132
132
9=8-7: Total Import/Export | 0 | 0
9=8-7: Net Total | 0
SITALAKHYA 132 KV SIDE (EXPORT TO OTHER S/S)
7 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 256.333 | 278.72 | 22.387 | 480000 |  | 10745760
|  | 132 | DPDC | 16402670 | 1 | 1781.37 | 1803.746 | 22.376 | 480000 |  | 10740480
10: Total |  | 10740480
SITALAKHYA 132 KV SIDE
2: 132/33 KV GT-1; 3: 132; 4: NET IMPORT |  | 0
2: 132/33 KV GT-2; 3: 132 |  | 0
2: 132/33 KV GT-3; 3: 132 |  | 0
10: Total |  | 59596320
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SENDING SIDE (TARIFF POINT); 4: 70336800; 6: EXPORT TO OTHER S/S; 9=8-7: 10740480 | 132 KV NET IMPORT |  | 59596320
2: IMPORT-2; 6: 132 KV NET IMPORT for Sitalakhya 33/11 KV; 9=8-7: 59596320 | GT (33 KV Side) |  | 59622737
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | -26417
2: IMPORT-4 | LOSS % IN => |  | -0.04433%
| 132 KV TOTAL IMPORT |  | 70336800
1: 33 KV SIDE of___SITALAKHYA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
11 | 132/33 KV Transformer, GT-1 Incoming | 33 | DPDC | H/A030701130-03 | 1 | 52592.299 | 72155.148 | 19562.849 | 1000 | 19562849
|  | 33 | P. Cell | 08993595 | 1 | 5208.452 | 5208.452 | 0 | 480000 | 0
15 | 132/33 KV Transformer, GT-2 Incoming | 33 | P. Cell | 08993927 | 1 | 4480.302 | 4480.302 | 0 | 480000 | 0
|  | 33 | DPDC | BD001913 | 1 | 1688.3762 | 1728.8978 | 40.5216 | 480000 | 19450368
18 | 132/33 KV Transformer, GT-3 Incoming | 33 | DPDC | BD001915 | 1 | 2770.8003 | 2813.7368 | 42.9365 | 480000 | 20609520
7: 0; 8: 0; 10: Total | 59622737 |  | 0
| SITALAKHYA 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0
9 | 33/11 KV Transformer T-3 | 33 | DPDC | H/A030701089-03 | 1 | 61282.784 | 70391.605 | 9108.821 | 1000 |  | 9108821 | 9115646.719 |  | 14027300.5237 | Sytalakhya 33/11 kv ss |  | 33/11 KV Transformer T-3 | 9115646.719 | 8807019.2728 | 308627.4462 | 3.5043 | OK
|  | 33 | P. Cell | 08993597 | 1 | 5829.305 | 5867.204 | 37.899 | 240000 |  | 9095760 | 9102575.9317 |  |  |  |  | 0 | 9102575.9317 | 8848149.4111 | 254426.5206 | 2.8755 | OK
13 | 33/11 KV Transformer T-4 | 33 | DPDC | H/A030701087-03 | 1 | 66370.552 | 71278.528 | 4907.976 | 1000 |  | 4907976 | 4911653.8047 |  |  |  |  | 33/11 KV Transformer T-4 | 4911653.8047 | 4789029.2402 | 122624.5645 | 2.5605 | OK
|  | 33 | P. Cell | 08993925 | 1 | 5629.89 | 5657.145 | 27.255 | 180000 |  | 4905900 | 4909576.2491 |  |  |  |  | 0 | 4909576.2491 | 4801695.6773 | 107880.5717 | 2.2467 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 14016797 | 14027300.5237 |  |  |  |  | 33 KV Feeders | 14027300.5237 | 13596048.513 | 431252.0107 | 3.1719 | OK
10 | 33 KV Char Syedpur Feeder (F1) | 33 | DPDC | H/A030701083-03 | 1 | 42622.665 | 42622.665 | 0 | 1000 |  | 0 | 0 |  | 0 | Char Sayedpur 33/11 kv ss |  | 33 KV Char Syedpur Feeder (F1) | 0 | 2.0018 | -2.0018 | -100 | CHECK
| 34 KV Char Syedpur Feeder (F1) | 33 | P. Cell | 08993596 | 1 | 2186.817 | 2186.817 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 34 KV Char Syedpur Feeder (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 8788.348 | 18741.026 | 9952.678 | 1000 |  | 9952678 | 9960136.0654 |  | 9960136.0654 | Narayangonj BSCIC 33/11 kv ss |  | 33 KV Panchabati BSCIC Feeder (F3) | 9960136.0654 | 9812552.2159 | 147583.8496 | 1.504 | OK
| 33 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9673.683 | 9728.932 | 55.249 | 180000 |  | 9944820 | 9952272.177 |  |  |  |  | 33 KV Panchabati BSCIC Feeder (F3) | 9952272.177 | 9842287.0649 | 109985.1122 | 1.1175 | OK
14 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 37583.454 | 40076.123 | 2492.669 | 1000 |  | 2492669 | 2494536.8881 | Sytalakhya |  |  |  | 33 KV Shah Cement Feeder (F2) | 2494536.8881 | 923421.8011 | 1571115.087 | 170.1406 | FAULT
|  | 33 | P. Cell | 08993926 | 1 | 2284.281 | 2298.1 | 13.819 | 180000 |  | 2487420 | 2489283.9547 |  | 17521159.6958 | Khanpur 33/11 kv ss |  | 0 | 2489283.9547 | 924955.1856 | 1564328.7691 | 169.1248 | FAULT
16 | 33 KV Khanpur-02 (Old) Feeder (F4) | 33 | DPDC | H/A030800200-03 | 1 | 1599.843 | 10966.771 | 9366.928 | 1000 |  | 9366928 | 9373947.1321 |  |  |  |  | 33 KV Khanpur-02 (Old) Feeder (F4) | 9373947.1321 | 8965472.3475 | 408474.7846 | 4.5561 | OK
|  | 33 | P. Cell | 08993600 | 1 | 4885.69 | 4885.69 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1522.167 | 1564.4804 | 42.3134 | 180000 |  | 7616412 | 7622119.3784 |  | 15614848.266 | Mondolpara 33/11 kv ss |  | 33 kV Mondolpara-2 | 7622119.3784 | 7595730.5431 | 26388.8353 | 0.34742 | OK
19 | 33 kV Khanpur-01(New) Feeder | 33 | DPDC | BD001864 | 1 | 370.6713 | 404.5926 | 33.9213 | 240000 |  | 8141112 | 8147212.5637 |  |  |  |  | 33 kV Khanpur-01(New) Feeder | 8147212.5637 | 8481674.5037 | -334461.94 | -3.9433 | OK
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1258.6652 | 1291.9433 | 33.2781 | 240000 |  | 7986744 | 7992728.8876 |  |  |  |  | 33 kV Mondolpara-1 Feeder | 7992728.8876 | 7982119.4318 | 10609.4558 | 0.13292 | OK
21 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 |  | 0 | 0 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4646.3 | 4676 | 29.7 | 160 |  | 4752 | 4755.5609 | Sytalakhya |  |  |  | 33/0.415 KV Transformer AT-2 | 4755.5609 | 4035.644 | 719.917 | 17.839 | OK
10: Total |  | 45561295 | 45595436.4763 |  |  |  |  | 0 | 45595436.4763 | 43765006.487 | 1830429.9893 | 4.1824 | OK
9=8-7: Grand Total | 59622737 | 59578092 | 59622737 | 0.074935
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 2499292.449
[5 empty] | Total = |  |  | 2499292.449
1: 11 KV SIDE of___SITALAKHYA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 11 KV SIDE
9 | 33/11 kV Transformer, T-3 Incoming | 11 |  | DHK 9372 | 1 | 19718.09 | 70276.2518 | 50558.1618 | 180 | 9100469.124 |  | 9128496.4253
10 | 33/11 kV Transformer, T-4 Incoming | 11 |  | DHK 9368 | 1 | 60988.1285 | 88120.1466 | 27132.0181 | 180 | 4883763.258 |  | 4898804.0985
7: 0; 8: 0; 10: Total | 13984232.382 |  | 14027300.5237
| SITALAKHYA 11 kV SIDE |  |  |  |  | 0 | 0
3 | 11 kV Bholail Feeder (F-3) | 11 |  | DHK 9335 | 1 | 68294.86 | 120042.476 | 51747.616 | 60 |  | 3104856.96 | 3113891.785 | Sytalakhya |  |  |  | 11 kV Bholail Feeder (F-3) | 3113891.785 | 3046734.2178 | 67157.5671 | 2.2042 | OK
4 | 11 kV Crony Apparels (F-2) | 11 |  | DHK 9336 | 1 | 28231.2805 | 48142.2979 | 19911.0174 | 60 |  | 1194661.044 | 1198137.3888 | Sytalakhya |  |  |  | 11 kV Crony Apparels (F-2) | 1198137.3888 | 1083589.5043 | 114547.8845 | 10.5712 | OK
5 | 11 kV Baburail Feeder (F-5) | 11 |  | DHK 9322 | 1 | 48193.1576 | 82394.5117 | 34201.3541 | 60 |  | 2052081.246 | 2058052.5984 | N.Gonj (West) |  |  |  | 11 kV Baburail Feeder (F-5) | 2058052.5984 | 2038840.2789 | 19212.3195 | 0.94232 | OK
6 | 11 kV Goghchar Feeder (F-1) | 11 |  | DHK 9323 | 1 | 90249.8775 | 112256.5511 | 22006.6736 | 60 |  | 1320400.416 | 1324242.6499 | Sytalakhya |  |  |  | 11 kV Goghchar Feeder (F-1) | 1324242.6499 | 1303267.9767 | 20974.6732 | 1.6094 | OK
7 | 11 kV Norshinghopur (F-2) | 11 |  | DHK 9365 | 1 | 70175.942 | 93513.646 | 23337.704 | 60 |  | 1400262.24 | 1404336.8639 | Sytalakhya |  |  |  | 11 kV Norshinghopur (F-2) | 1404336.8639 | 1352601.3966 | 51735.4673 | 3.8249 | OK
8 | 11 kV Geddar Bazar Feeder (F-4) | 11 |  | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 |  | 0 | 0 | Sytalakhya |  |  |  | 11 kV Geddar Bazar Feeder (F-4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Noluyapara Feeder (F-6)*** | 11 |  | H/A030701125-03 | 1 | 72836.303 | 73081.722 | 245.419 | 1000 |  | 245419 | 246133.1449 | N.Gonj (East) |  |  |  | 11 kV Noluyapara Feeder (F-6)*** | 246133.1449 | 234255.9876 | 11877.1573 | 5.0702 | OK
12 | 11 kV Kashipur Feeder (F-7) | 11 |  | H/A030800169-03 | 1 | 33256.036 | 34992.83 | 1736.794 | 1000 |  | 1736794 | 1741847.8978 | Sytalakhya |  |  |  | 11 kV Kashipur Feeder (F-7) | 1741847.8978 | 1664580.229 | 77267.6688 | 4.6419 | OK
13 | 11 kV Spare Feeder (F-6) | 11 |  |  | 1 | 0 | 0 |  | 1000 |  |  | 0 | N.Gonj (West) |  |  |  | 11 kV Spare Feeder (F-6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Paikpara Feeder (F-8) | 11 |  | H/A030701098-03 | 1 | 77120.905 | 78252.992 | 1132.087 | 1000 |  | 1132087 | 1135381.2606 | N.Gonj (West) |  |  |  | 11 kV Paikpara Feeder (F-8) | 1135381.2606 | 1090515.7468 | 44865.5138 | 4.1142 | OK
15 | 11 kV B. K. Road Feeder (F-9) | 11 |  | H/A030800205-03 | 1 | 93822.411 | 94550.082 | 727.671 | 1000 |  | 727671 | 729788.4502 | N.Gonj (East) |  |  |  | 11 kV B. K. Road Feeder (F-9) | 729788.4502 | 786055.2221 | -56266.7718 | -7.1581 | OK
16 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 |  | H/A030701091-03 | 1 | 52130.183 | 53202.551 | 1072.368 | 1000 |  | 1072368 | 1075488.4842 | Sytalakhya |  |  |  | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 1075488.4842 | 1015821.5301 | 59666.9541 | 5.8738 | OK
10: Total | 14027300.5237 | 13986600.906 | 14027300.5237 | 0.29099
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | N.Gonj (East) | at 33 KV level |  | 975921.5951
[5 empty] | Sytalakhya | at 33 KV level |  | 9857945.0696
[5 empty] | N.Gonj (West) | at 33 KV level |  | 3193433.8589
[5 empty] | Total = |  |  | 14027300.5237 | 0
1: MI CEMENT 132/33 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
1 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 256.333 | 278.72 | 22.387 | 480000 | 10745760 |  | 10749120
|  | 132 | DPDC | 16402670 | 1 | 1781.37 | 1803.746 | 22.376 | 480000 | 10740480
2 | 132/33 kV Transformer (132 kV Side) | 132 |  | 06502030 | 1 | 3542.414 | 3587.422 | 45.008 | 240000 |  | 10801920
7: 0; 8: 0; 9=8-7: Total Import/Export | 10740480 | 10801920
[6 empty] | 0 | 0 |  | Net Total
[6 empty] | 0 | 0
3 | 132/33 kV Transformer (33 kV Side) | 33 |  | 14718815 | 1 | 6990.664 | 7079.67 | 89.006 | 120000 | 10680720
4 | 33 kV Outgoing Feeder-1 | 33 |  | 11745824 | 1 | 3630.823 | 3669.351 | 38.528 | 120000 |  | 4623360
5 | 33 kV Outgoing Feeder-2 | 33 |  |  | 1 | 0 | 0 | 0 | 120000 |  | 6057360
9=8-7: Total Import/Export | 10680720 | 10680720
9=8-7: Net Total | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 10749120
[5 empty] | Total = |  |  | 10749120
192
1: 33 KV SIDE of___MONDALPARA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
17 | 33 kV Mondolpara-2 | 33 | DPDC | BD001911 | 1 | 1522.167 | 1564.4804 | 42.3134 | 180000 | 0 | 7616412 | 7622119.3784
20 | 33 kV Mondolpara-1 Feeder | 33 | DPDC | BD001823 | 1 | 1258.6652 | 1291.9433 | 33.2781 | 240000 | 0 | 7986744 | 7992728.8876
10: Total | 0 | 15603156 | 15614848.266
MONDOLPARA 33 KV SIDE (RECEIVING)
3 | 33 kV Shitalakhya-2 Feeder | 33 |  | 00000188 | 1 | 305372960 | 312969952 | 7596992 | 1 | 7596992
7 | 33 kV Shitalakhya-1 Feeder | 33 |  | 00000153 | 1 | 302469120 | 310465440 | 7996320 | 1 | 7996320
7: 0; 8: 0; 10: Total | 15593312 | 0 | 0
| MONDOLPARA33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| MONDOLPARA 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 28/35 MVA T-2 Transformer | 33 |  | 00000116 | 1 | 309984960 | 317581696 | 7596736 | 1 |  | 7596736
8 | 33/11 kV, 28/35 MVA T-1 Transformer | 33 |  | 00000194 | 1 | 297679680 | 305673600 | 7993920 | 1 |  | 7993920
10: Total |  | 15590656
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: SITALAKHYA 33 KV SIDE; 4: 15614848.266; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 15614848.266
6: 33 KV NET IMPORT; 9=8-7: 15614848.266 | 33 KV TX HV SIDE |  | 15590656
[10 empty] | LOSS UNITS=> |  | 24192.266
[10 empty] | LOSS % IN => |  | 0.1549%
| TOTAL IMPORT |  | 15614848.266
1: 11 KV SIDE of___MONDALPARA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MONDOLPARA 11 KV SIDE
15 | 11 kV T-1 Incoming | 11 |  | 00000055 | 1 | 296240160 | 304193962 | 7953802 | 1 | 7953802 |  | 8042618.4364
19 | 11 kV T-2 Incoming | 11 |  | 00000017 | 1 | 307651360 | 315139968 | 7488608 | 1 | 7488608 |  | 7572229.8296
7: 0; 8: 0; 10: Total | 15442410 |  | 15614848.266
| MONDOLPARA 11 KV SIDE |  |  |  |  | 0 | 0
9 | 11 kV River View | 11 |  | 00000061 | 1 | 5548248 | 6387048 | 838800 | 1 |  | 838800 | 841728.9793 | N.Gonj (East) |  |  |  | 11 kV River View | 841728.9793 | 838140.6773 | 3588.302 | 0.42813 | OK
10 | 11 kV Railgate B.B. Road | 11 |  | 00000191 | 1 | 22140866 | 22810540 | 669674 | 1 |  | 669674 | 672012.4136 | N.Gonj (East) |  |  |  | 11 kV Railgate B.B. Road | 672012.4136 | 662899.4007 | 9113.0128 | 1.3747 | OK
11 | 11 kV DIT | 11 |  | 00000174 | 1 | 133509912 | 136605064 | 3095152 | 1 |  | 3095152 | 3105959.8639 | N.Gonj (West) |  |  |  | 11 kV DIT | 3105959.8639 | 3165323.9759 | -59364.112 | -1.8755 | OK
12 | 11 kV Dalpatti | 11 |  | 00000182 | 1 | 3037272 | 3675991 | 638719 | 1 |  | 638719 | 640949.3228 | N.Gonj (East) |  |  |  | 11 kV Dalpatti | 640949.3228 | 661646.5082 | -20697.1854 | -3.1281 | OK
13 | 11 kV South Chasara | 11 |  | 00000043 | 1 | 91543376 | 94325328 | 2781952 | 1 |  | 2781952 | 2791666.2107 | N.Gonj (West) |  |  |  | 11 kV South Chasara | 2791666.2107 | 2659640.365 | 132025.8457 | 4.964 | OK
14 | 11 kV Spare | 11 |  | 00000137 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV NCC Express | 11 |  | 00000019 | 1 | 96919 | 130297 | 33378 | 1 |  | 33378 | 33494.5516 | N.Gonj (East) |  |  |  | 11 kV NCC Express | 33494.5516 | 30069.4219 | 3425.1297 | 11.3907 | OK
17 | 11 kV Spare | 11 |  | 00000041 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Masuya Bazar | 11 |  | 00000173 | 1 | 4304069 | 5319947 | 1015878 | 1 |  | 1015878 | 1019425.3124 | N.Gonj (East) |  |  |  | 11 kV Masuya Bazar | 1019425.3124 | 1009868.8027 | 9556.5097 | 0.94631 | OK
20 | 11 kV Nitaigonj | 11 |  | 00000189 | 1 | 57402260 | 58092820 | 690560 | 1 |  | 690560 | 692971.3447 | N.Gonj (East) |  |  |  | 11 kV Nitaigonj | 692971.3447 | 773236.8002 | -80265.4554 | -10.3804 | OK
21 | 11 kV Shahid Nagar | 11 |  | 00000020 | 1 | 55724624 | 57039820 | 1315196 | 1 |  | 1315196 | 1319788.4916 | Sytalakhya |  |  |  | 11 kV Shahid Nagar | 1319788.4916 | 1324869.236 | -5080.7445 | -0.38349 | OK
22 | 11 kV Bangla Bazar | 11 |  | 00000139 | 1 | 67598832 | 69252312 | 1653480 | 1 |  | 1653480 | 1659253.7348 | N.Gonj (West) |  |  |  | 11 kV Bangla Bazar | 1659253.7348 | 1635218.8108 | 24034.924 | 1.4698 | OK
23 | 11 kV Vogoban Gonj | 11 |  | 00000181 | 1 | 1911915 | 2365594 | 453679 | 1 |  | 453679 | 455263.1874 | N.Gonj (East) |  |  |  | 11 kV Vogoban Gonj | 455263.1874 | 451404.0608 | 3859.1267 | 0.85492 | OK
24 | 11 kV Tanbazar | 11 |  | 00000138 | 1 | 47659964 | 48640480 | 980516 | 1 |  | 980516 | 983939.833 | N.Gonj (East) |  |  |  | 11 kV Tanbazar | 983939.833 | 990185.2541 | -6245.4211 | -0.63073 | OK
25 | 11 kV SS Road | 11 |  | 00000175 | 1 | 63912244 | 65297040 | 1384796 | 1 |  | 1384796 | 1389631.5256 | N.Gonj (West) |  |  |  | 11 kV SS Road | 1389631.5256 | 1367265.5042 | 22366.0214 | 1.6358 | OK
26 | 11 kV Spare | 11 |  | 00000094 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
27 | 33/0.415 kV Auxiliary-1 | 0.415 |  |  | 1 | 2413.05 | 2500.38 | 87.33 | 100 |  | 8733 | 8763.4945 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-1 | 8763.4945 | 8081.1571 | 682.3374 | 8.4436 | OK
28 | 33/0.415 kV Auxiliary-2 | 0.415 |  |  | 1 | 3.98 | 3.98 | 0 | 100 |  | 0 | 0 | N.Gonj (West) |  |  |  | 33/0.415 kV Auxiliary-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 15614848.266 | 15560513 | 15614848.266 | 0.34919
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 1319788.4916
[5 empty] | N.Gonj (East) | at 33 KV level |  | 5339784.9449
[5 empty] | N.Gonj (West) | at 33 KV level |  | 8955274.8295
[5 empty] | Total = |  |  | 15614848.266 | 0
1: 33 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SITALAKHYA 33 KV SIDE
12 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | DPDC | H/A030701082-03 | 1 | 8788.348 | 18741.026 | 9952.678 | 1000 | 0 | 9952678 | 9960136.0654
0 | 33 KV Panchabati BSCIC Feeder (F3) | 33 | P. Cell | 08993594 | 1 | 9673.683 | 9728.932 | 55.249 | 180000 | 0 | 9944820 | 9952272.177
2: MATUAIL 33 KV SIDE; 10: Total |  | 9952678 | 9960136.0654
12 | 33 KV Panchabati Bscic (Feeder-2) | 33 | DPDC | H/A060300263-03 | 1 | 59915.41 | 63937.809 | 4022.399 | 1000 | 0 | 4022399 | 4053093.5487
0 | 0 | 33 | P. Cell | 08993580 | 1.5 | 1330.064 | 1345.024 | 14.96 | 180000 | 0 | 4039200 | 4070022.7555
10: Total | 0 | 4022399 | 4053093.5487
2: NARAYANGONJ BSCIC 33 KV SIDE (RECEIVING); 10: Total |  | 13975077 | 14013229.6141
3 | 33 kV Matuail Feeder | 33 | Digital | ABB03910 | 1 | 80771.768 | 81538.1627 | 766.3947 | 4000 | 3065578.76
6 | 33 kV Shitalakhya Feeder | 33 | Old | HA030800161-03 | 1.5 | 113039.175 | 113039.175 | 0 | 1000 | 0
|  | 33 | New | DHKA2199 | 1 | 4085.7267 | 4138.69 | 52.9633 | 180000 | 9533394
7: 0; 8: 0; 10: Total | 3065578.76 | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| NARAYANGONJ BSCIC 33 KV SIDE |  |  |  |  | 0 | 0
5 | 33/11 kV, 20/28 MVA Transformer-3 | 33 | Old | HA021100524-02 | 1 | 0 | 0 | 0 | 1000 |  | 0
|  | 33 | New | DHKA2200 | 1 | 4271.1911 | 4292.5688 | 21.3777 | 180000 |  | 3847986
7 | 33/11 kV, 10/14 MVA Transformer-2 | 33 | Old | HA030800199-03 | 1 | 34464.969 | 39412.298 | 4947.329 | 1000 |  | 4947329
|  | 33 | New | DHKA2195 | 1 | 4424.2755 | 4476.1316 | 51.8561 | 90000 |  | 4667049
8 | 33/11 kV, 10/14 MVA Transformer-1 | 33 | Digital | ABB03909 | 1 | 420502.76 | 425384.895 | 4882.135 | 1000 |  | 4882134.98
10: Total |  | 13677449.98
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: SITALAKHYA 33 KV SIDE; 4: 9960136.0654; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 14013229.6141
2: MATUAIL 33 KV SIDE; 4: 4053093.5487; 6: 33 KV NET IMPORT; 9=8-7: 14013229.6141 | 33 KV TX HV SIDE |  | 13677449.98
[10 empty] | LOSS UNITS=> |  | 335779.6341
[10 empty] | LOSS % IN => |  | 2.396%
| TOTAL IMPORT |  | 14013229.6141
1: 11 KV SIDE of___NARAYANGONJ BSCIC 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARAYANGONJ BSCIC 11 KV SIDE
9 | 33/11 kV Transformer, T-2 Incoming | 11 |  | 51426632 | 1 | 3672086 | 3726568 | 54482 | 90 | 4903380 |  | 4991538.3971
16 | 33/11 kV Transformer, T-1 Incoming | 11 |  | DHKA2192 | 1 | 3789.2958 | 3844.1774 | 54.8816 | 90000 | 4939344 |  | 5028148.9977
22 | 33/11 kV Transformer, T-3 Incoming | 11 |  | 51426630 | 1 | 3976918 | 4020507 | 43589 | 90 | 3923010 |  | 3993542.2193
7: 0; 8: 0; 10: Total | 13765734 |  | 14013229.6141
| NARAYANGONJ BSCIC 11 KV SIDE |  |  |  |  | 0 | 0
10 | 11 kV Masdair Feeder (F-8) | 11 |  | XA575914 | 1 | 209842.6 | 212991.1 | 3148.5 | 1000 |  | 3148500 | 3190609.1379 | N.Gonj (West) |  |  |  | 11 kV Masdair Feeder (F-8) | 3190609.1379 | 3086175.0273 | 104434.1106 | 3.3839 | OK
11 | 11 kV Narayangonj (F-7) | 11 |  | XA575915 | 1 | 164247.4 | 165452.9 | 1205.5 | 1000 |  | 1205500 | 1221622.7778 | N.Gonj (West) |  |  |  | 11 kV Narayangonj (F-7) | 1221622.7778 | 1186514.4598 | 35108.3179 | 2.9589 | OK
12 | 11 kV Nearest Feeder (F-6) | 11 |  | XA575927 | 1 | 104635.5 | 105393.1 | 757.6 | 1000 |  | 757600 | 767732.4068 | N.Gonj (West) |  |  |  | 11 kV Nearest Feeder (F-6) | 767732.4068 | 814473.5094 | -46741.1025 | -5.7388 | OK
13 | 11 kV BSCIC-2 Feeder (F-5) | 11 |  | XA575916 | 1 | 115029.2 | 116133.1 | 1103.9 | 1000 |  | 1103900 | 1118663.9439 | N.Gonj (West) |  |  |  | 11 kV BSCIC-2 Feeder (F-5) | 1118663.9439 | 1197874.4889 | -79210.545 | -6.6126 | OK
14 | 11 kV Abonti Color Tex. (F-4) | 11 |  | XA575912 | 1 | 54099.1 | 54786 | 686.9 | 1000 |  | 686900 | 696086.8403 | N.Gonj (West) |  |  |  | 11 kV Abonti Color Tex. (F-4) | 696086.8403 | 614760.142 | 81326.6984 | 13.229 | OK
15 | 11 kV BSCIC-1 Feeder (F-3) | 11 |  | DHK66615 | 1 | 180.4877 | 194.7091 | 14.2215 | 60000 |  | 853287.3 | 864699.4622 | N.Gonj (West) |  |  |  | 11 kV BSCIC-1 Feeder (F-3) | 864699.4622 | 933339.9033 | -68640.4411 | -7.3543 | OK
17 | 11 kV Shasongaon Feeder (F-2) | 11 |  | XA575920 | 1 | 230751.7 | 231721.5 | 969.8 | 1000 |  | 969800 | 982770.4437 | Sytalakhya |  |  |  | 11 kV Shasongaon Feeder (F-2) | 982770.4437 | 813154.9346 | 169615.5091 | 20.8589 | OK
18 | 11 kV Fakir Apparels Feeder (F-1) | 11 |  | XA575929 | 1 | 19036.6 | 20181.2 | 1144.6 | 1000 |  | 1144600 | 1159908.2799 | N.Gonj (West) |  |  |  | 11 kV Fakir Apparels Feeder (F-1) | 1159908.2799 | 1225868.8461 | -65960.5662 | -5.3807 | OK
19 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 |  | HA021100913-02 | 1 | 38386.576 | 38961.791 | 575.215 | 1000 |  | 575215 | 582908.1262 | N.Gonj (West) |  |  |  | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 582908.1262 | 649651.6597 | -66743.5335 | -10.2737 | OK
20 | 11 kV BSCIC-4 Feeder (F-11) | 11 |  | HA021100682-02 | 1 | 57586.384 | 59519.019 | 1932.635 | 1000 |  | 1932635 | 1958482.735 | N.Gonj (West) |  |  |  | 11 kV BSCIC-4 Feeder (F-11) | 1958482.735 | 2197501.257 | -239018.5219 | -10.8768 | OK
21 | 11 kV BSCIC-3 Feeder (F-10) | 11 |  | HA021100455-02 | 1 | 53001.889 | 54442.541 | 1440.652 | 1000 |  | 1440652 | 1459919.7827 | N.Gonj (West) |  |  |  | 11 kV BSCIC-3 Feeder (F-10) | 1459919.7827 | 1675803.0813 | -215883.2986 | -12.8824 | OK
23 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3753.3 | 3813.8 | 60.5 | 160 |  | 9680 | 9809.4637 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-1 | 9809.4637 | 10077.9686 | -268.5049 | -2.6643 | OK
24 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4101.3 | 4101.4 | 0.1 | 160 |  | 16 | 16.214 | N.Gonj (West) |  |  |  | 11/0.415 KV Transformer,AT-2 | 16.214 | 519.3156 | -503.1016 | -96.8778 | CHECK
10: Grand Total | 14013229.6141 | 13828285.3 | 14013229.6141 | 1.3374
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 982770.4437
[5 empty] | N.Gonj (West) | at 33 KV level |  | 13030459.1704
[5 empty] | Total = |  |  | 14013229.6141 | 0
| Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part) | Substation: Char Syedpur 132/33 kV, 2×80/120 MVA Grid Substation (132 kV Part)
1: 132 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SENDING SIDE (TARIFF POINT)
1 | Madonganj to Charsyedpur-1 |  | IMPORT | 42627811 | 1 | 247.775 | 259.986 | 12.211 | 960000 | 0 | 11722560
| Madonganj to Charsyedpur-2 |  |  | 42627824 | 1 | 159.043 | 171.744 | 12.701 | 960000 | 0 | 12192960
9=8-7: Total Import/Export | 0 | 23915520 | 0
10: Net Total | 23915520
CHAR SYEDPUR 132 KV SIDE (RECEIVING)
| 132 kV Madanganj Circuit-1 | 132 |  | 041808902821 | 1 | 205.73 | 215.46 | 9.73 | 1200000 | 11676000
|  | 132 |  | 041808904222 | 3 | 67.94 | 71.22 | 3.28 | 1200000 | 11808000
| 132 kV Madanganj Circuit-2 | 132 |  | 041808902865 | 1 | 127.26 | 137.4 | 10.14 | 1200000 | 12168000
|  | 132 |  | 041808904240 | 1 | 127.3 | 137.44 | 10.14 | 1200000 | 12168000
7: 0; 8: 0; 9=8-7: Total Import/Export | 23844000 | 0 | 0
7: 0; 8: 0; 9=8-7: Net Total | 23844000
| CHAR SYEDPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| CHAR SYEDPUR 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV, 80/120 MVA GT-1 | 132 | EXPORT | 041808902864 | 1 | 155.92 | 165.82 | 9.9 | 1200000 | 11880000 | 11880000
|  | 132 |  | 041808904224 | 1 | 155.82 | 165.71 | 9.89 | 1200000 | 11868000 | 11868000
7 | 132/33 kV, 80/120 MVA GT-2 | 132 |  | 041808902848 | 1 | 177.03 | 187 | 9.97 | 1200000 | 11964000 | 11964000
|  | 132 |  | 041808904244 | 1 | 177.11 | 187.09 | 9.98 | 1200000 | 11976000 | 11976000
10: Total |  | 23844000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV EXPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SENDING SIDE (TARIFF POINT); 4: 23915520; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 23844000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 23844000 | 132/33 KV LV SIDE |  | 23716800
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 127200
2: IMPORT-4 | LOSS % IN => |  | 0.5335%
| 132 KV TOTAL IMPORT |  | 23915520
1: 33 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 33 KV SIDE
14 | 132/33 kV, 80/120 MVA GT-1 Incoming (=H6) | 33 | Main | 041808902859 | 1 | 258.18 | 274.58 | 16.4 | 720000 | 11808000 |  | 11871329.6903
|  | 33 | Backup | 041808904285 | 1 | 258.18 | 274.58 | 16.4 | 720000 | 11808000 |  | 11871329.6903
15 | 132/33 kV, 80/120 MVA GT-2 Incoming (=H9) | 33 | Main | 041808902812 | 1 | 293.67 | 310.21 | 16.54 | 720000 | 11908800 |  | 11972670.3097
|  | 33 | Backup | 041808904276 | 1 | 293.69 | 310.23 | 16.54 | 720000 | 11908800 |  | 11972670.3097
7: 0; 8: 0; 10: Total | 23716800 |  | 23844000
| CHAR SYEDPUR 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33/11 kV, 28/35 MVA T-1 (=H5) | 33 | Main | 041808902875 | 1 | 200.92 | 211.11 | 10.19 | 240000 |  | 2445600 | 2449181.8955 |  |  |  |  | 33/11 kV, 28/35 MVA T-1 (=H5) | 2449181.8955 | 2501282.1097 | -52100.2142 | -2.0829 | OK
|  | 33 | Backup | 041808904241 | 1 | 200.86 | 211.05 | 10.19 | 240000 |  | 2445600 | 2449181.8955 |  |  |  |  | 0 | 2449181.8955 | 2501282.1097 | -52100.2142 | -2.0829 | OK
16 | 33/11 kV, 28/35 MVA T-2 (=H10) | 33 | Main | 041808902844 | 3 | 56.7 | 59.77 | 3.07 | 240000 |  | 2210400 | 2213637.4149 |  |  |  |  | 33/11 kV, 28/35 MVA T-2 (=H10) | 2213637.4149 | 2129469.9042 | 84167.5107 | 3.9525 | OK
|  | 33 | Backup | 041808904259 | 3 | 56.7 | 59.77 | 3.07 | 240000 |  | 2210400 | 2213637.4149 |  |  |  |  | 0 | 2213637.4149 | 2129469.9042 | 84167.5107 | 3.9525 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 4656000 | 4662819.3103 |  |  |  |  | 33 KV Feeders | 4662819.3103 | 4630752.0138 | 32067.2965 | 0.69249 | OK
9 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 288.61 | 307.61 | 19 | 360000 |  | 6840000 | 6850018.059 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-1 (=H1) | 6850018.059 | 6815752.3123 | 34265.7467 | 0.50274 | OK
|  | 33 | Backup | 041808904221 | 1 | 288.74 | 307.96 | 19.22 | 360000 |  | 6919200 | 6929334.0576 |  |  |  |  | 0 | 6929334.0576 | 6855589.3343 | 73744.7232 | 1.0757 | OK
10 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 93.75 | 100.77 | 7.02 | 360000 |  | 2527200 | 2530901.4092 | Sytalakhya |  |  |  | 33 kV Delta Agro Premier Cement (=H2) | 2530901.4092 | 2430058.343 | 100843.0661 | 4.1498 | OK
|  | 33 | Backup | 041808904237 | 1 | 93.75 | 100.77 | 7.02 | 360000 |  | 2527200 | 2530901.4092 |  |  |  |  | 0 | 2530901.4092 | 2430058.343 | 100843.0661 | 4.1498 | OK
11 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-3 (=H3) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904239 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-4 (=H4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904245 | 1 | 0.05 | 0.05 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 42.67 | 43.78 | 1.11 | 360000 |  | 399600 | 400185.2656 | Sytalakhya |  |  |  | 33 kV Premier Cement VRM Circuit-2 (=H11) | 400185.2656 | 1006790.1928 | -606604.9272 | -60.2514 | CHECK
|  | 33 | Backup | 041808904232 | 1 | 42.69 | 43.8 | 1.11 | 360000 |  | 399600 | 400185.2656 |  |  |  |  | 0 | 400185.2656 | 1003168.6453 | -602983.3798 | -60.1079 | CHECK
18 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-6 (=H12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904233 | 1 | 0.08 | 0.08 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 | Sytalakhya |  |  |  | 33 kV Outgoing Feeder-7 (=H13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 041808904234 | 1 | 0.06 | 0.06 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 434.74 | 460.46 | 25.72 | 360000 |  | 9259200 | 9272761.2883 | Sytalakhya |  |  |  | 33 kV Shah Cement VRM (=H14) | 9272761.2883 | 10712537.375 | -1439776.0867 | -13.4401 | OK
|  | 33 | Backup | 041808904242 | 1 | 434.78 | 460.5 | 25.72 | 360000 |  | 9259200 | 9272761.2883 |  |  |  |  | 0 | 9272761.2883 | 10716158.9225 | -1443397.6342 | -13.4694 | OK
| 33/0.415 kV Transformer AT-1 |  |  |  | 1 | 1481.22 | 1595.72 | 114.5 | 1 |  | 114.5 | 114.6677 | [5 empty] | 114.6677 | 109.7631
10: Total |  | 19026114.5 | 19053980.6897 |  |  |  |  | 0 | 19053980.6897 | 20965247.9862 | -1911267.2965 | -9.1164 | OK
9=8-7: Grand Total | 23716800 | 23682114.5 | 23716800 | 0.14646
1: 11 KV SIDE of___CHAR SYEDPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
CHAR SYEDPUR 11 KV SIDE
3 | 33/11 kV, 28/35 MVA T-1 Incoming | 11 |  | 041808902756 | 1 | 192 | 201.74 | 9.74 | 250000 | 2435000 |  | 2859868.7742
20 | 33/11 kV, 28/35 MVA T-2 Incoming | 11 |  | 041808902778 | 1.72 | 115.22 | 118.79 | 3.57 | 250000 | 1535100 |  | 1802950.5361
7: 0; 8: 0; 10: Total | 3970100 |  | 4662819.3103
| CHAR SYEDPUR 11 kV SIDE |  |  |  |  | 0 | 0
4 | 11 kV Outgoing Feeder-1 (=F1) | 11 |  | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-1 (=F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Char-Syedpur Feeder(=F2) | 11 |  | 041808902749 | 1 | 381.72 | 402.78 | 21.06 | 60000 |  | 1263600 | 1258154.7044 | Sytalakhya |  |  |  | 11 kV Char-Syedpur Feeder(=F2) | 1258154.7044 | 1256317.0074 | 1837.697 | 0.14628 | OK
6 | 11 kV UltraTech Cement Feeder (=F3) | 11 |  | 041808902759 | 1 | 418.63 | 438.15 | 19.52 | 60000 |  | 1171200 | 1166152.8884 | Sytalakhya |  |  |  | 11 kV UltraTech Cement Feeder (=F3) | 1166152.8884 | 1226848.5855 | -60695.6971 | -4.9473 | OK
7 | 11 kV Outgoing Feeder-4 (=F4) | 11 |  | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-4 (=F4) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Outgoing Feeder-5 (=F5) | 11 |  | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-5 (=F5) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Outgoing Feeder-6 (=F6) | 11 |  | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-6 (=F6) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Outgoing Feeder-7 (=F7) | 11 |  | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-7 (=F7) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 |  | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-8 with BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 |  | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-9 with BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Mokterpur Feeder (=F8) | 11 |  | 041808902786 | 1 | 252.09 | 275.64 | 23.55 | 60000 |  | 1413000 | 1406910.8874 | Sytalakhya |  |  |  | 11 kV Mokterpur Feeder (=F8) | 1406910.8874 | 1384414.4332 | 22496.4541 | 1.625 | OK
14 | 11 kV Dhaleshwary Feeder (=F9) | 11 |  | 041808902789 | 1 | 164.08 | 178 | 13.92 | 60000 |  | 835200 | 831600.8302 | Sytalakhya |  |  |  | 11 kV Dhaleshwary Feeder (=F9) | 831600.8302 | 763171.9877 | 68428.8425 | 8.9664 | OK
15 | 11 kV Outgoing Feeder-12 (=F10) | 11 |  | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-12 (=F10) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Outgoing Feeder-13 (=F11) | 11 |  | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-13 (=F11) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11 kV Outgoing Feeder-14 (=F12) | 11 |  | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-14 (=F12) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Outgoing Feeder-15 (=F13) | 11 |  | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-15 (=F13) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 kV Outgoing Feeder-16 (=F14) | 11 |  | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Outgoing Feeder-16 (=F14) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33/0.415 kV Transformer AT-1 | 0.415 |  | 041811907976 | 1 | 1481.22 | 1595.72 | 114.5 | 1 |  |  | 0 | Sytalakhya |  |  |  | 33/0.415 kV Transformer AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 33/0.415 kV Transformer AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 4662819.3103 | 4683000 | 4662819.3103 | -0.43094
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 23716685.3323
[5 empty] | Total = |  |  | 23716685.3323 | 19053866.022
1: 33 KV SIDE of___AMULIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
FROM MADERTEK 33 KV SIDE
3 | Amulia | 33 | Export | SIEM0505 | 1 | 35220 | 36382 | 1162 | 6000 | 0 | 6972000 | 6968346.1855
10: Total |  | 6972000 | 6968346.1855
AMULIA 33 KV SIDE (RECEIVING)
| 33 kV Madartek Receiving | 33 |  |  | 1 | 1254.53 | 1293.34 | 38.81 | 180000 | 6985800
[6 empty] | 0 | 0
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total | 6985800 | 0 | 0
| AMULIA 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| AMULIA 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV Transformer, T-1 | 33 |  | DHKA2194 | 1 | 339.3168 | 353.9938 | 14.677 | 240000 |  | 3522480
4 | 33/11 kV Transformer, T-2 | 33 |  | DHKA2198 | 1 | 515.8374 | 530.5001 | 14.6627 | 240000 |  | 3519048
10: Total |  | 7041528 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: FROM MADERTEK 33 KV SIDE; 4: 6968346.1855; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 6968346.1855
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 6968346.1855 | 33 KV TX HV SIDE |  | 7041528
2: IMPORT-3 | LOSS UNITS=> |  | -73181.8145
2: IMPORT-4 | LOSS % IN => |  | -1.05%
| TOTAL IMPORT |  | 6968346.1855
1: 11 KV SIDE of___AMULIA 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
AMULIA 11 KV SIDE
10 | 33/11 kV Transformer, T-2 Incoming | 11 |  | HA021100461-02 | 1 | 13429981 | 16952600 | 3522619 | 1 | 3522619 |  | 3884629.2773
11 | 33/11 kV Transformer, T-1 Incoming | 11 |  | HA021100478-02 | 1 | 84126188 | 86922532 | 2796344 | 1 | 2796344 |  | 3083716.9083
7: 0; 8: 0; 10: Total | 6318963 |  | 6968346.1855
| AMULIA 11 KV SIDE |  |  |  |  | 0 | 0
5 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 69350978 | 70057178 | 706200 | 1 |  | 706200 | 704760.429 | Mugdapara |  |  |  | 11 kV Manikdia Feeder | 704760.429 | 655997.4572 | 48762.9717 | 7.4334 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 12677425 | 14050902 | 1373477 | 1 |  | 1373477 | 1370677.2015 | Demra |  |  |  | 11 kV Kayetpara Feeder | 1370677.2015 | 1292488.6152 | 78188.5863 | 6.0495 | OK
8 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 331582 | 878768 | 547186 | 1 |  | 547186 | 546070.575 | Demra | Meter Reset |  |  | 11 kV Paity Feeder | 546070.575 | 498813.9667 | 47256.6083 | 9.4738 | OK
9 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 61396460 | 63742776 | 2346316 | 1 |  | 2346316 | 2341533.0936 | Demra |  |  |  | 11 kV Bamuil Feeder | 2341533.0936 | 2143176.0462 | 198357.0474 | 9.2553 | OK
12 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 13507195 | 14096671 | 589476 | 1 |  | 589476 | 588274.3679 | Mugdapara |  |  |  | 11 kV Ali Ahmed School Feeder | 588274.3679 | 552448.5186 | 35825.8494 | 6.4849 | OK
13 | 11 kV Amulia Model Town Feeder | 11 | Demra |  | 1 | 51481502 | 51647116 | 165614 | 1 |  | 165614 | 165276.4 | Demra |  |  |  | 11 kV Amulia Model Town Feeder | 165276.4 | 158821.9675 | 6454.4325 | 4.0639 | OK
14 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 9680550 | 10934861 | 1254311 | 1 |  | 1254311 | 1251754.1184 | Demra |  |  |  | 11 kV Rajakhali Feeder | 1251754.1184 | 1263380.0786 | -11625.9602 | -0.92023 | OK
15 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33/0.415 kV Transformer, AT-2 | 0.415 |  |  | 1 | 0 | 0 | 0 | 160 |  | 0 | 0 |  |  |  |  | 33/0.415 kV Transformer, AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 6968346.1855 | 6982580 | 6968346.1855 | -0.20426
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Mugdapara | at 33 KV level |  | 1293034.7969
[5 empty] | Demra | at 33 KV level |  | 5675311.3886
[5 empty] | Total = |  |  | 6968346.1855 | 0
Modongonj 132/33 KV 2 x 35/50 MVA Substation. (SOUTH) Phone No.
1: 33 KV SIDE of___Modongonj 132/33 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
2: MOGBAZAR T&T 11 KV SIDE | Bus Loss From PDB
12 | 33 kV Shah Cement Feeder | 33 |  | 8993 841 | 1 | 39285.417 | 39374.588 | 89.171 | 36000 | 0 | 3210156 | 3210156 | Sytalakhya |  |  |  | 33 kV Shah Cement Feeder | 3210156 | 3227092 | -16936 | -0.52481 | OK
13 | 33 kV Mondol Para (Premire cement) Feeder | 33 |  | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya |  |  |  | 33 kV Mondol Para (Premire cement) Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total |  | 3210156 | 3210156 | 0
[5 empty] | NOCS Wise 33 KV EXPORT |  |  | KWH
[5 empty] | Sytalakhya | at 33 KV level |  | 3210156
[5 empty] | Total = |  |  | 3210156 | 0
Note on H480: User: Meter was faulty and New meter is installed properly in 12.07.23

## SOUTH-2
132 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S | [13 empty] | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.07.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 230/132 KV SIDE (TARIFF POINT)
| Maniknagar-1 | 132 | IMPORT | 50147584 | 1 | 3134.038 | 3181.398 | 47.36 | 1920000 | 0 | 90931200
| Maniknagar-2 | 132 |  | 50147585 | 1 | 3127.49 | 3174.787 | 47.297 | 1920000 | 0 | 90810240
9=8-7: Total Import/Export | 0 | 181741440
10: Net Total | 181741440
MANIKNAGAR 132 KV SIDE (RECEIVING)
0
0
0
0
9=8-7: Total Import/Export | 0 | 0
9=8-7: Net Total | 181741440
MANIKNAGAR 132 KV SIDE (EXPORT TO OTHER S/S)
| 132 kV Narinda Circuit-1 | 132 | EXPORT | 06604331 | 1 | 8833.87 | 8876.04 | 42.17 | 480000 |  | 20241600 |  |  | Wrong Reading by Grid
| 132 kV Narinda Circuit-2 | 132 |  | 06604334 | 1 | 8842.46 | 8884.95 | 42.49 | 480000 |  | 20395200
| 132kV Motijheel Circuit-1 | 132 |  | 06604332 | 1 | 1809.31 | 1823.15 | 13.84 | 1440000 |  | 19929600
| 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1619.13 | 1625.76 | 6.63 | 1440000 |  | 9547200
| 132 kV Kazla Circuit-1 | 132 |  | ABB03905 | 1 | 714735 | 747732 | 32997 | 1000 |  | 32997000
| 132 kV Kazla Circuit-2 | 132 |  | ABB03904 | 1 | 536435 | 560011 | 23576 | 1000 |  | 23576000
7: 0; 8: 0; 10: Total |  | 126686600
| MANIKNAGAR 132 KV SIDE |  |  |  |  | 0 | 0
9 | 132/33 kV 50/75 MVA GT-1 (HV) | 132 | Export | Nill | 1 | 0 | 0 | 0 | 1000 |  | 27215000 |  |  | Export to Maniknagar Grid at 132 kV Level=
10 | 132/33 kV 50/75 MVA GT-2 (HV) | 132 | Export | ABB03903 | 1 | 284234 | 311836 | 27602 | 1000 |  | 27602000 |  |  | 54817000
10: Total |  | 54817000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MANIKNAGAR 230/132 KV SIDE (TARIFF POINT); 4: 181741440; 6: EXPORT TO OTHER S/S; 9=8-7: 126686600 | 132 KV NET IMPORT |  | 55054840
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 55054840 | 33 KV NET IMPORT |  | 54797000
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 257840
2: IMPORT-4 | LOSS % IN => |  | 0.4683%
| 132 KV TOTAL IMPORT |  | 181741440
1: 33 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Maniknagar 33 KV SIDE
1 | 33 kV 50/75 MVA GT-1 Incoming (LV) | 33 | Digital | ABB03907 | 1 | 24044 | 51259 | 27215 | 1000 | 27215000
8 | 33kV 50/75 MVA GT-2 Incoming (LV) | 33 | Digital | ABB03906 | 1 | 191259 | 218841 | 27582 | 1000 | 27582000
7: 0; 8: 0; 10: Total | 54797000 |  | 0
| Maniknagar 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 10/14 MVA Transformer-1 | 33 | Digital | ABB03912 | 1 | 202618 | 202618 | 0 | 2000 |  | 0 | 0 |  | 11500968.2039 | Maniknagar 33/11 kv ss |  | 33 kV 10/14 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 11 |  | DHK00121 | 2 | 10067.8 | 10067.8 | 0 | 4444 | Estimated | 4126429.8988 | 4161360.0577 |  |  |  |  | 0 | 4161360.0577 | 3717504.4134 | 443855.6443 | 11.9396 | OK
7 | 33 kV 20/28 MVA Transformer-2 | 33 | Digital | ABB03913 | 1 | 378209 | 381848 | 3639 | 2000 |  | 7278000 | 7339608.1462 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 | 7339608.1462 | 7027910.4855 | 311697.6606 | 4.4351 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 11404429.8988 | 11500968.2039 |  |  |  |  | 33 KV Feeders | 11500968.2039 | 10745414.8989 | 755553.305 | 7.0314 | OK
2 |  | 33 | Digital | ABB03916 | 1 | 0 | 0 | 0 | 2000 |  | 0 | 0 |  | 14993857.367 | Motijheel 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 33kV Motijheel-1 Feeder | 33 |  | DHK86054 | 1 | 2425.39 | 2452.59 | 27.2 | 270000 |  | 7344000 | 7406166.835 |  |  |  |  | 33kV Motijheel-1 Feeder | 7406166.835 | 6408249.5782 | 997917.2569 | 15.5724 | OK
3 | 33kV Mugdapara Hospital-1 Feeder | 33 | Digital | ABB03911 | 1 | 207821 | 207821 | 0 | 2000 | From Downstream | 10136608 | 10222414.2142 |  |  |  |  | 33kV Mugdapara Hospital-1 Feeder | 10222414.2142 | 9409882.1944 | 812532.0199 | 8.6349 | OK
|  | 33 |  | 38 | 1 | 252376832 | 252376832 | 0 | 1 |  | 0 | 0 |  | 20458333.7915 | Mugdapara Hospital 33/11 kv ss |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33kV Mugdapara Hospital-2 Feeder | 33 | Digital | ABB03918 | 1 | 292711 | 297786 | 5075 | 2000 |  | 10150000 | 10235919.5773 |  |  |  |  | 33kV Mugdapara Hospital-2 Feeder | 10235919.5773 | 9437479.7949 | 798439.7824 | 8.4603 | OK
9 | 33kV Khilgaon Feeder | 33 | Digital | ABB03915 | 1 | 267046 | 270635 | 3589 | 2000 |  | 7178000 | 7238761.6479 |  | 0 | Kazla 33/11 kv ss |  | 33kV Khilgaon Feeder | 7238761.6479 | 6535956.7515 | 702804.8963 | 10.7529 | OK
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 |  | 0 | 0 |  |  |  |  | 33kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 277648 | 281410 | 3762 | 2000 |  | 7524000 | 7587690.532 |  | 7238761.6479 | Khilgoan 33/11 kv ss |  | 33kV Motijheel-2 Feeder | 7587690.532 | 6413470.3117 | 1174220.2203 | 18.3087 | OK
12 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20647 | 20947 | 300 | 2000 |  | 600000 | 605078.9898 | Maniknagar |  |  |  | 33kV Water Treatment Plant | 605078.9898 | 1062218.4705 | -457139.4807 | -43.0363 | CHECK
10: Total |  | 42932608 | 43296031.7961 |  |  |  |  | 0 | 43296031.7961 | 39267257.1011 | 4028774.695 | 10.2599 | OK
9=8-7: Grand Total | 54797000 | 54337037.8988 | 54797000 | 0.8465
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 605078.9898
[5 empty] | Total = |  |  | 605078.9898 | 0
1: 11 KV SIDE of___MANIKNAGAR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 11 KV SIDE
8 | 11kV 20/28 MVA Transformer T-2 | 11 | Import | 6604357 | 1 | 5378.73 | 5424.13 | 45.4 | 160000 | 7264000 |  | 11500968.2039
9 | 11kV 10/14 MVA Transformer T-1 | 11 | Import | DHK00121 | 2 | 10067.8 | 10067.8 | 0 | 4444 | 0 |  | 0 |  | Converted to 30 days
7: 0; 8: 0; 10: Total | 7264000 |  | 11500968.2039
| MANIKNAGAR 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Nearest Feeder | 11 |  | HA021101060-02 | 1 | 73698434 | 75374744 | 1676310 | 1 |  | 1676310 | 1691601.9901 | Maniknagar |  |  |  | 11 kV Nearest Feeder | 1691601.9901 | 1589546.8433 | 102055.1468 | 6.4204 | OK
2 | 11kV Spare | 11 |  | HA021100679-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Maniknagar |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV City Palli Feeder | 11 |  | HA021100937-02 | 1 | 76283711 | 77211413 | 927702 | 1 |  | 927702 | 936164.8797 | Maniknagar |  |  |  | 11 kV City Palli Feeder | 936164.8797 | 876024.4652 | 60140.4145 | 6.8652 | OK
4 | 11 kV R K Mission Road Feeder | 11 |  | HA021101035-02 | 1 | 12539189 | 14171862 | 1632673 | 1 |  | 1632673 | 1647566.9154 | Maniknagar |  |  |  | 11 kV R K Mission Road Feeder | 1647566.9154 | 1564049.4804 | 83517.4351 | 5.3398 | OK
5 | 11 kV Janapath Feeder | 11 |  | HA021100864-02 | 1 | 25420957 | 27595235 | 2174278 | 1 |  | 2174278 | 2194112.6593 | Maniknagar |  |  |  | 11 kV Janapath Feeder | 2194112.6593 | 2093083.5306 | 101029.1286 | 4.8268 | OK
6 | 11 kV Dhalpur Feeder | 11 |  | HA021100851-02 | 1 | 85288108 | 86139684 | 851576 | 1 |  | 851576 | 859344.4269 | Maniknagar |  |  |  | 11 kV Dhalpur Feeder | 859344.4269 | 844664.2379 | 14680.189 | 1.738 | OK
7 | 11kV WTP | 11 |  | X0599387 | 1 | 1406.5 | 1406.5 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11kV WTP | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11kV Kamalapur Water pumping | 11 |  | HA021100474-02 | 1 | 7638435 | 7638435 | 0 | 1 | Estimated | 36489.852 | 36822.7275 | Maniknagar | 3 | Ampere to be taken | 22243.3033 | 11kV Kamalapur Water pumping | 36822.7275 | 20221.1849 | 16601.5426 | 82.0998 | FAULT
11 | 11 kV Wasa Road Feeder | 11 |  | HA021001011-02 | 1 | 25380490 | 25380490 | 0 | 1 | Estimated | 2079921.564 | 2098895.465 | Maniknagar | 171 | Ampere to be taken | 2050110.9142 | 11 kV Wasa Road Feeder | 2098895.465 | 1863737.1947 | 235158.2703 | 12.6176 | OK
12 | 11kV Sutikhalpar Feeder | 11 |  | HA021101047-02 | 1 | 79907658 | 79907658 | 0 | 1 | Estimated | 2006941.86 | 2025250.0101 | Maniknagar | 165 | Ampere to be taken | 2071048.1161 | 11kV Sutikhalpar Feeder | 2025250.0101 | 1882771.0147 | 142478.9954 | 7.5675 | OK
13 | 11kV Spare | 11 |  | HA021101029-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 |  | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11kV Spare | 11 |  | HA021101068-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Spare | 11 |  | HA021101243-02 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 11kV Spare | 11 |  | Nill | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| Axuxilary -1 | 0.415 |  | AH14044078 | 1 | 397817.5 | 403596.2 | 5778.7 | 1 |  | 5778.7 | 5831.4157 | Maniknagar |  |  |  | Axuxilary -1 | 5831.4157 | 6475.0369 | -643.6212 | -9.94 | OK
| Axuxilary -2 | 0.415 |  | AH14044072 | 1 | 369244.1 | 374573.2 | 5329.1 | 1 |  | 5329.1 | 5377.7142 | Maniknagar |  |  |  | Axuxilary -2 | 5377.7142 | 4841.9103 | 535.8039 | 11.066 | OK
13 | AT-1 | 0.415 |  | 6603506 | 1 | 0 | 0 |  | 1 |  | 0 | 0 | Maniknagar |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 11500968.2039 | 11397000.076 | 11500968.2039 | 0.91224
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 11500968.2039
[5 empty] | Total = |  |  | 11500968.2039 | 0
1: 33 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 33 KV SIDE
0 | 33kV Motijheel-1 Feeder | 33 | 0 | DHK86054 | 1 | 2425.39 | 2452.59 | 27.2 | 270000 | 0 | 7344000 | 7406166.835
11 | 33kV Motijheel-2 Feeder | 33 | Digital | ABB03914 | 1 | 277648 | 281410 | 3762 | 2000 | 0 | 7524000 | 7587690.532
10: Total | 0 | 14868000 | 14993857.367
Motijheel 33 KV SIDE (RECEIVING)
3 | 33 kV Maniknagar Circuit-1 | 33 | Import | DHK86054 | 1 | 2425.39 | 2452.59 | 27.2 | 270000 | 7344000
6 | 33 kV Maniknaga Circuit-2 at Motijhil (T-2) | 33 | Import | DHK68120 | 1 | 2322.11 | 2128.45 | -193.66 | 270000 | 7524000 |  |  |  | From Upstream
7: 0; 8: 0; 10: Total | 14868000 | 0 | 0
| Motijheel 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
| 33kV Biddyut Bhaban Circuit | 33 | Export |  | 1 | 476568 | 486697 | 10129 | 600 |  | 6077400
7: 0; 8: 0; 10: Total |  | 6077400
7: 0; 8: 0 | 8790600
| Motijheel 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK86053 | 1 | 2935.58 | 2961.62 | 26.04 | 180000 |  | 4687200
5 | 33/11 kV 20/28 MVA Transformer (T-2) (Ckt-2) | 33 | Export | DHK86055 | 1 | 2290.59 | 2290.59 | 0 | 180000 |  | 0
10: Total |  | 4687200
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: MANIKNAGAR 33 KV SIDE; 4: 14868000; 6: EXPORT TO OTHER S/S; 9=8-7: 6077400 | 33 KV NET IMPORT |  | 8790600
6: 33 KV NET IMPORT; 9=8-7: 8790600 | 33 KV TX HV SIDE |  | 4687200
[10 empty] | LOSS UNITS=> |  | 4103400
[10 empty] | LOSS % IN => |  | 46.68%
| TOTAL IMPORT |  | 14868000
1: 11 KV SIDE of___MOTIJHEEL OLD 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
13 | 33/11 kV 20/28 MVATransformer-1 | 11 | Import | DHK86059 | 1 | 3319.16 | 3349.09 | 29.93 | 160000 | 4788800 |  | 4737174.2528 |  | 0
14 | 33/11 kV 20/28 MVA Transformer-2 | 11 | Import | DHK86057 | 1 | 2572.46 | 2598.07 | 25.61 | 160000 | 4097600 |  | 4053425.7472
7: 0; 8: 0; 10: Total | 8886400 |  | 8790600
| MOTIJHEEL 11 KV SIDE |  |  |  |  | 0 | 0
6 | 11kV Fakirapul Panir Tank Feeder | 11 |  | DHK86058 | 1 | 1678.29 | 1695.96 | 17.67 | 60000 |  | 1060200 | 1084055.9235 | Motijheel |  |  |  | 11kV Fakirapul Panir Tank Feeder | 1084055.9235 | 997541.2473 | 86514.6762 | 8.6728 | OK
7 | 11kV Station Road Feeder | 11 |  | DHK86075 | 1 | 2374.67 | 2376.46 | 1.79 | 60000 |  | 107400 | 109816.6442 | Motijheel |  |  |  | 11kV Station Road Feeder | 109816.6442 | 95033.1244 | 14783.5198 | 15.5562 | OK
8 | 11kV Box Culvert Road Feeder | 11 |  | DHK86071 | 1 | 3125.25 | 3155.14 | 29.89 | 60000 |  | 1793400 | 1833753.908 | Motijheel |  |  |  | 11kV Box Culvert Road Feeder | 1833753.908 | 1479451.1554 | 354302.7526 | 23.9483 | OK
9 | 11kV Mohamedan Club Feeder | 11 |  | DHK86062 | 1 | 1662.49 | 1678.4 | 15.91 | 60000 |  | 954600 | 976079.7817 | Motijheel |  |  |  | 11kV Mohamedan Club Feeder | 976079.7817 | 1139171.2585 | -163091.4767 | -14.3167 | OK
10 | 11kV Amina Ahmed Co. | 11 |  | DHK95754 | 1 | 104040 | 108136 | 4096 | 60 |  | 245760 | 251289.93 | Motijheel |  |  |  | 11kV Amina Ahmed Co. | 251289.93 | 373020.341 | -121730.4111 | -32.6337 | OK
11 | 11kV Bangabhaban -1 | 11 |  | DHK95752 | 1 | 4382 | 4382 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban -1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11kV Sonali Bank | 11 |  | DHK95753 | 1 | 50590 | 59617 | 9027 | 60 |  | 541620 | 553807.1772 | Motijheel |  |  |  | 11kV Sonali Bank | 553807.1772 | 446839.6196 | 106967.5577 | 23.9387 | OK
15 | 11kV NCC Bank Feeder | 11 |  | DHK68123 | 1 | 316.13 | 320 | 3.87 | 60000 |  | 232200 | 237424.8118 | Motijheel |  |  |  | 11kV NCC Bank Feeder | 237424.8118 | 404044.0578 | -166619.246 | -41.2379 | CHECK
16 | 11kV IFIC BANK Feeder | 11 |  | DHK68116 | 1 | 389.19 | 397.35 | 8.16 | 60000 |  | 489600 | 500616.6574 | Ramna |  |  |  | 11kV IFIC BANK Feeder | 500616.6574 | 354381.5863 | 146235.0711 | 41.2649 | FAULT
17 | 11kV Arambagh Feeder | 11 |  | DHK68117 | 1 | 3354.56 | 3367.9 | 13.34 | 60000 | Calculated | 1239791.6453 | 1267688.622 | Motijheel | From Load Profile |  |  | 11kV Arambagh Feeder | 1267688.622 | 59250.2714 | 1208438.3506 | 2039.5491 | FAULT
18 | 11kV Nikotborti Feeder | 11 |  | DHK68114 | 1 | 1410.57 | 1425.76 | 15.19 | 60000 |  | 911400 | 931907.7237 | Motijheel |  |  |  | 11kV Nikotborti Feeder | 931907.7237 | 862042.4055 | 69865.3182 | 8.1046 | OK
19 | 11kV Agrani Bank Feeder | 11 |  | DHK95756 | 1 | 363305 | 367476 | 4171 | 60 |  | 250260 | 255891.186 | Motijheel |  |  |  | 11kV Agrani Bank Feeder | 255891.186 | 369219.0161 | -113327.83 | -30.6939 | OK
20 | 11kV Bangladesh Bank-2 | 11 |  | DHK95755 | 1 | 521 | 527 | 6 | 60000 | Calculated | 764674.8795 | 781881.091 | Motijheel | From Load Profile |  |  | 11kV Bangladesh Bank-2 | 781881.091 | 669891.5592 | 111989.5318 | 16.7176 | OK
21 | 11kV PDB Design Feeder 14 | 11 |  | DHK95747 | 1 | 44960 | 44960 | 0 | 60 |  | 0 | 0 | Motijheel |  |  |  | 11kV PDB Design Feeder 14 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11kV Bangabhaban-2 | 11 |  | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 |  | 0 | 0 | Motijheel |  |  |  | 11kV Bangabhaban-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | 11/0.4 kV AT | 0.415 |  | ELIC5429 | 1 | 405596 | 411842 | 6246 | 1 |  | 6246 | 6386.5434 | Motijheel |  |  |  | 11/0.4 kV AT | 6386.5434 | 8270.9474 | -1884.404 | -22.7834 | OK
10: Grand Total | 8790600 | 8597152.5248 | 8790600 | 2.2501
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 8289983.3426
[5 empty] | Ramna | at 33 KV level |  | 500616.6574
[5 empty] | Total = |  |  | 8790600 | 0
1: 132 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE (TARIFF POINT)
1 | 132kV Motijheel Circuit-1 | 132 | 0 | 06604332 | 1 | 1809.31 | 1823.15 | 13.84 | 1440000 | 0 | 19929600
2 | 132kV Motijheel Circuit-2 | 132 |  | 06604330 | 1 | 1619.13 | 1625.76 | 6.63 | 1440000 | 0 | 9547200
9=8-7: Total Import/Export | 0 | 29476800
10: Net Total | 29476800
MOTIJHEEL 132 KV SIDE (RECEIVING)
4 | 132 kV Mniknagar Circuit-1 | 132 | Imp/Main | 41812909527 | 1 | 299.67 | 315.61 | 15.94 | 1200000 | 19128000
|  | 132 | Imp/Backup | 41812909575 | 1 | 299.74 | 315.69 | 15.95 | 1200000 | 19140000
5 | 132 kV Mniknagar Circuit-2 | 132 | Imp/Main | 41812909512 | 1 | 118.86 | 126.51 | 7.65 | 1200000 | 9180000
|  | 132 | Imp/Backup | 41812909591 | 1 | 118.88 | 126.54 | 7.66 | 1200000 | 9192000
7: 0; 8: 0; 9=8-7: Total Import/Export | 28308000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 28308000
| MOTIJHEEL 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 34.19 | 36.32 | 2.13 | 1200000 |  | 2556000
|  | 132 | Exp/Backup | 41812909570 | 1 | 34.17 | 36.12 | 1.95 | 1200000 |  | 2340000
7 | 132 kV Bangabhaban Circuit-2 | 132 | Exp/Main | 41812909559 | 1 | 83.53 | 86.61 | 3.08 | 1200000 |  | 3696000
|  | 132 | Exp/Backup | 41812909569 | 1 | 83.53 | 86.61 | 3.08 | 1200000 |  | 3696000
7: 0; 8: 0; 10: Total |  | 6252000
| MOTIJHEEL 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41812909509 | 1 | 193.98 | 207.8 | 13.82 | 1200000 |  | 16584000
|  | 132 | Exp/Backup | 41812909594 | 1 | 193.98 | 207.8 | 13.82 | 1200000 |  | 16584000
6 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41812909508 | 1 | 106.87 | 111.44 | 4.57 | 1200000 |  | 5484000
|  | 132 | Exp/Backup | 41812909592 | 1 | 106.84 | 111.41 | 4.57 | 1200000 |  | 5484000
10: Total |  | 22068000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MANIKNAGAR 132 KV SIDE (TARIFF POINT); 4: 29476800; 6: EXPORT TO OTHER S/S; 9=8-7: 6252000 | 132 KV NET IMPORT |  | 23224800
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 23224800 | 33 KV NET IMPORT |  | 22795200
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 429600
2: IMPORT-4 | LOSS % IN => |  | 1.85%
| 132 KV TOTAL IMPORT |  | 29476800
1: 33 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE
15 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41812909543 | 1 | 320.98 | 344.84 | 23.86 | 720000 | 17179200
|  | 33 | Backup | 41812909617 | 1 | 321.2 | 345.08 | 23.88 | 720000 | 17193600
16 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41812909468 | 1 | 176.11 | 183.91 | 7.8 | 720000 | 5616000
|  | 33 | Backup | 41812909600 | 1 | 176.08 | 183.88 | 7.8 | 720000 | 5616000
7: 0; 8: 0; 10: Total | 22795200 |  | 0
| MOTIJHEEL 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV 28/35 MVA T-1 (HV) | 33 | Main | 41812909546 | 1 | 105.03 | 113.58 | 8.55 | 240000 |  | 2052000 | 2047621.479 |  | 4346705.2449 | Motijheel 33/11 kv ss |  | 33 kV 28/35 MVA T-1 (HV) | 2047621.479 | 1989186.2453 | 58435.2337 | 2.9376 | OK
|  | 33 | Backup | 41812909616 | 1 | 105 | 113.55 | 8.55 | 240000 |  | 2052000 | 2047621.479 |  |  |  |  | 0 | 2047621.479 | 1989186.2453 | 58435.2337 | 2.9376 | OK
17 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41812909482 | 1 | 188.24 | 197.84 | 9.6 | 240000 |  | 2304000 | 2299083.7659 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 2299083.7659 | 2221657.4089 | 77426.357 | 3.4851 | OK
|  | 33 | Backup | 42003953371 | 1 | 188.28 | 197.89 | 9.61 | 240000 |  | 2306400 | 2301478.6448 |  |  |  |  | 0 | 2301478.6448 | 2221657.4089 | 79821.2359 | 3.5929 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 4356000 | 4346705.2449 |  |  |  |  | 33 KV Feeders | 4346705.2449 | 4210843.6543 | 135861.5907 | 3.2265 | OK
10 | 33 kV Spare Feeder 1 | 33 | Main | 41812909466 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909599 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Spare Feeder 2 | 33 | Main | 41812909467 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909601 | 1 | 0.03 | 0.03 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 405.36 | 420.51 | 15.15 | 360000 |  | 5454000 | 5442362.3521 |  | 5442362.3521 | P & T 33/11 kv ss |  | 33 kV P & T Circuit-1 | 5442362.3521 | 6283911.2473 | -841548.8952 | -13.3921 | OK
|  | 33 | Backup | 41812909610 | 1 | 405.51 | 420.66 | 15.15 | 360000 |  | 5454000 | 5442362.3521 |  |  |  |  | 0 | 5442362.3521 | 6287506.1622 | -845143.8101 | -13.4416 | OK
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 191.2 | 218.11 | 26.91 | 360000 |  | 9687600 | 9666928.772 |  |  |  |  | 33 kV Kamlapur Circuit-1 | 9666928.772 | 6176063.8003 | 3490864.9717 | 56.5225 | FAULT
|  | 33 | Backup | 41812909595 | 1 | 191.27 | 218.2 | 26.93 | 360000 |  | 9694800 | 9674113.4088 |  | 12979046.3223 | Kamlapur Railway 33/11 kv ss |  | 0 | 9674113.4088 | 6176063.8003 | 3498049.6085 | 56.6388 | FAULT
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 66.37 | 75.59 | 9.22 | 360000 |  | 3319200 | 3312117.5503 |  |  |  |  | 33 kV Kamlapur- 2 Feeder | 3312117.5503 | 3303726.7942 | 8390.7561 | 0.25398 | OK
|  | 33 | Backup | 41621865733 | 1 | 66.38 | 75.6 | 9.22 | 360000 |  | 3319200 | 3312117.5503 |  |  |  |  | 0 | 3312117.5503 | 3303726.7942 | 8390.7561 | 0.25398 | OK
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 136.08 | 136.08 | 0 | 360000 |  | 0 | 0 |  | No Load Due to Fdr Trip from 29/06/23 |  |  | 33 kV P & T - 2 Feeder | 0 | 4378606.3497 | -4378606.3497 | -100 | CHECK
|  | 33 | Backup | 41812909598 | 1 | 136.04 | 136.04 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 4375011.4348 | -4375011.4348 | -100 | CHECK
20 | 33 kV Spare Feeder 9 | 33 | Main | 41812909469 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909597 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Spare Feeder 10 | 33 | Main | 41812909478 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 10 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909620 | 1 | 0.02 | 0.02 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
| 0415 kV Aux Transformer (1000 KVA) | 0.415 |  |  | 1 | 1040.3 | 1130.78 | 90.48 | 300 |  | 27144 | 27086.0806 | [5 empty] | 27086.0806 | 26048.1542
10: Total |  | 18487944 | 18448494.7551 |  |  |  |  | 0 | 18448494.7551 | 20168356.3457 | -1719861.5907 | -8.5275 | OK
9=8-7: Grand Total | 22795200 | 22843944 | 22795200 | -0.21338
1: 11 KV SIDE of___MOTIJHEEL 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 11 KV SIDE
1 | 33/11 kV 28/35 MVA T-1 Incoming (LV) | 11 |  | 41812909493 | 1 | 100.03 | 108.19 | 8.16 | 250000 | 2040000 |  | 2047870.3694
18 | 33/11 kV 28/35 MVA T-2 Incoming (LV) | 11 |  | 41812909496 | 1 | 179.85 | 189.01 | 9.16 | 250000 | 2290000 |  | 2298834.8755
7: 0; 8: 0; 10: Total | 4330000 |  | 4346705.2449
| MOTIJHEEL 11 kV SIDE |  |  |  |  | 0 | 0
2 | 11 kV Central Weman | 11 |  | 41812909492 | 1 | 136.75 | 146.96 | 10.21 | 60000 |  | 612600 | 614594.3851 | Motijheel |  |  |  | 11 kV Central Weman | 614594.3851 | 602582.0913 | 12012.2938 | 1.9935 | OK
3 | 11 kV Spare Feeder 2 | 11 |  | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV K. M. Das Len | 11 |  | 41812909499 | 1 | 233.82 | 250.96 | 17.14 | 60000 |  | 1028400 | 1031748.0667 | Swamibag |  |  |  | 11 kV K. M. Das Len | 1031748.0667 | 1006914.6746 | 24833.3921 | 2.4663 | OK
5 | 11 kV Gopibag | 11 |  | 41812909517 | 1 | 34.11 | 36.93 | 2.82 | 60000 |  | 169200 | 169750.8488 | Motijheel |  |  |  | 11 kV Gopibag | 169750.8488 | 161492.0005 | 8258.8483 | 5.1141 | OK
6 | 11kV SPICE TV | 11 |  | 41812909518 | 1 | 11.09 | 14.9 | 3.81 | 60000 |  | 228600 | 229344.2319 | Narinda |  |  |  | 11kV SPICE TV | 229344.2319 | 216326.9708 | 13017.2611 | 6.0174 | OK
7 | 11 kV Spare Feeder 6 | 11 |  | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | 11 kV Spare Feeder 7 | 11 |  | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV BPT-1 | 11 |  | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV BPT-2 | 11 |  | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV BPT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 10 kV Spare Feeder 8 | 11 |  | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 10 kV Spare Feeder 8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 11 kV Spare Feeder 9 | 11 |  | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 9 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV South Kamlapur | 11 |  | 41812909473 | 1 | 367.96 | 377.45 | 9.49 | 60000 |  | 569400 | 571253.7429 | Motijheel |  |  |  | 11 kV South Kamlapur | 571253.7429 | 550760.0315 | 20493.7114 | 3.721 | OK
14 | 11 kV Spare Feeder 11 | 11 |  | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 |  | 0 | 0 |  |  |  |  | 11 kV Spare Feeder 11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Answer Camp | 11 |  | 41812909514 | 1 | 166.1 | 179.13 | 13.03 | 60000 |  | 781800 | 784345.2339 | Motijheel |  |  |  | 11 kV Answer Camp | 784345.2339 | 758048.2709 | 26296.963 | 3.469 | OK
16 | 11 kV Shapla Chattar | 11 |  | 41812909516 | 1 | 126.45 | 137.07 | 10.62 | 60000 |  | 637200 | 639274.4731 | Motijheel |  |  |  | 11 kV Shapla Chattar | 639274.4731 | 598966.5988 | 40307.8743 | 6.7296 | OK
17 | 11 kV Sayedabad | 11 |  | 41812909497 | 1 | 89.79 | 94.88 | 5.09 | 60000 |  | 305400 | 306394.2625 | Swamibag |  |  |  | 11 kV Sayedabad | 306394.2625 | 315753.0159 | -9358.7533 | -2.9639 | OK
22 | 33/0.4 kV Aux Transformer | 0.415 |  | 41901920686 | 1 | 1040.3 | 1130.78 | 90.48 | 1 |  |  | 0 | Motijheel |  |  |  | 33/0.4 kV Aux Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 4346705.2449 | 4332600 | 4346705.2449 | 0.32556
[6 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
7: Motijheel; 8: at 33 KV level; 10: 2479218.6838 |  | Export to Narinda | 300000
[6 empty] | Swamibag | at 33 KV level |  | 1338142.3292
[6 empty] | Narinda | at 33 KV level |  | 229344.2319
7: Total =; 10: 4046705.2449 | -300000
1: 33 KV SIDE of___P & T 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOTIJHEEL 33 KV SIDE (Sending)
12 | 33 kV P & T Circuit-1 | 33 | Main | 41812909463 | 1 | 405.36 | 420.51 | 15.15 | 360000 | 0 | 5454000 | 5442362.3521
0 | 0 | 33 | Backup | 41812909610 | 1 | 405.51 | 420.66 | 15.15 | 360000 | 0 | 5454000 | 5442362.3521
19 | 33 kV P & T - 2 Feeder | 33 | Main | 42003953363 | 1 | 136.08 | 136.08 | 0 | 360000 | 0 | 0 | 0
0 | 0 | 33 | Backup | 41812909598 | 1 | 136.04 | 136.04 | 0 | 360000 | 0 | 0 | 0
10: Total | 0 | 5454000 | 5442362.3521
Kamalapur Railway 33 KV SIDE (Sending)
1 | 33 kV P&T Circuit | 33 | 0 | 102 | 1 | 0 | 14.2 | 14.2 | 270000 |  | 3834000
10: Total |  | 9276362.3521
MOGBAZAR T&T 33 KV SIDE (RECEIVING)
5 | 33 kV Bidyut Bhaban Circuit | 33 | Import | BD017079 | 1 | 15736.93 | 15739.3 | 2.37 | 1000 | 2370
|  | 33 | Export | BD017079 | 1 | 0 | 0 | 0 | 1000 |  | 0
7 | 33 kV Motijheel Circuit-1 | 33 | Import | BD017081 | 1 | 132983 | 132983 | 0 | 1000 | 0
8 | 33 kV Motijheel Circuit-2 | 33 | Import | BD017082 | 1 | 21371.33 | 21371.33 | 0 | 1000 | 0
11 | 33 kV Kamlapur Circuit | 33 | Import | BD017085 | 1 | 0 | 0 | 0 | 1000 | 0
|  | 33 | Export | BD017085 | 1 | 0.27 | 0.27 | 0 | 1000 |  | 0
7: 0; 8: 0; 10: Total | 2370 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  |  |  |  | 0 | 0
6 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | BD017080 | 1 | 37374 | 43481 | 6107 | 888.88 |  | 5428390.16
10 | 33/11 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | BD017084 | 1 | 99683 | 104298 | 4615 | 888.88 |  | 4102181.2
10: Total |  | 9530571.36
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Sending Side; 4: 9276362.3521; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9276362.3521
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 9276362.3521 | 33 KV TX HV SIDE |  | 9530571.36
2: IMPORT-3 | LOSS UNITS=> |  | -254209.0079
2: IMPORT-4 | LOSS % IN => |  | -2.74%
| TOTAL IMPORT |  | 9276362.3521
1: 11 KV SIDE of___P & T 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MOGBAZAR T&T 11 KV SIDE
20 | 11 kV 20/28 MVATransformer-1 | 11 | Import | BD014056 | 1 | 77487.94 | 77487.94 | 0 | 1000 | 5428390.16 |  | 5180954.0809 |  | 0
21 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | BD014057 | 1 | 87870 | 92161 | 4291 | 1000 | 4291000 |  | 4095408.2713
7: 0; 8: 0; 10: Total | 9719390.16 |  | 9276362.3521
| MOGBAZAR T&T 11 KV SIDE |  |  |  |  | 0 | 0
12 | Inner Circular Road Feeder | 11 |  | BD014042 | 1 | 39265 | 40052 | 787 | 1000 |  | 787000 | 786225.5313 | Motijheel |  |  |  | Inner Circular Road Feeder | 786225.5313 | 2044037.2926 | -1257811.7612 | -61.5357 | CHECK
13 | NSI New Building Expres Feeder | 11 |  | BD013982 | 1 | 9206 | 9624 | 418 | 1000 |  | 418000 | 417588.6558 | Ramna |  |  |  | NSI New Building Expres Feeder | 417588.6558 | 429529.4901 | -11940.8343 | -2.78 | OK
14 | Police Hospital RMU Feeder | 11 |  | BD014044 | 1 | 3211 | 3401 | 190 | 1000 |  | 190000 | 189813.0254 | Rajarbag |  |  |  | Police Hospital RMU Feeder | 189813.0254 | 182072.2195 | 7740.8059 | 4.2515 | OK
15 | Kakrail 33/11 kV Substation U/G Feeder | 11 |  | BD014046 | 1 | 58.73 | 58.73 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Kakrail 33/11 kV Substation U/G Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | Jonaki O/H Feeder | 11 |  | BD014013 | 1 | 30996 | 32499 | 1503 | 1000 |  | 1503000 | 1501520.9321 | Rajarbag |  |  |  | Jonaki O/H Feeder | 1501520.9321 | 1581312.3149 | -79791.3828 | -5.0459 | OK
17 | Nayapalton Overhead Feeder | 11 |  | BD014014 | 1 | 22642 | 23646 | 1004 | 1000 |  | 1004000 | 1003011.9866 | Ramna |  |  |  | Nayapalton Overhead Feeder | 1003011.9866 | 1008941.636 | -5929.6494 | -0.58771 | OK
18 | Masjid Gali Over Head Feeder | 11 |  | BD014016 | 1 | 12776 | 13676 | 900 | 1000 |  | 900000 | 899114.3306 | Ramna |  |  |  | Masjid Gali Over Head Feeder | 899114.3306 | 924444.0314 | -25329.7008 | -2.74 | OK
19 | Spare Feeder (Feeder-8) | 11 |  | BD014009 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 |  |  |  |  | Spare Feeder (Feeder-8) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | Bangabhaban 132/11 Substation (Feeder 9) | 11 |  | BD013988 | 1 | 12.18 | 12.18 | 0 | 1000 |  | 0 | 0 | Import |  |  |  | Bangabhaban 132/11 Substation (Feeder 9) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
23 | Mid Way Over Head Feeder | 11 |  | BD014015 | 1 | 20857 | 21881 | 1024 | 1000 |  | 1024000 | 1022992.3051 | Ramna |  |  |  | Mid Way Over Head Feeder | 1022992.3051 | 1000894.2451 | 22098.0599 | 2.2078 | OK
24 | Palton Thana Over Head Feeder | 11 |  | BD014033 | 1 | 20890 | 22279 | 1389 | 1000 |  | 1389000 | 1387633.1169 | Rajarbag |  |  |  | Palton Thana Over Head Feeder | 1387633.1169 | 1346932.0545 | 40701.0624 | 3.0218 | OK
25 | Police Hospital (South) U/G Feeder 7 | 11 |  | BD014034 | 1 | 12022 | 12204 | 182 | 1000 |  | 182000 | 181820.898 | Rajarbag |  |  |  | Police Hospital (South) U/G Feeder 7 | 181820.898 | 172012.9808 | 9807.9171 | 5.7018 | OK
26 | China Town Express Feeder | 11 |  | BD013943 | 1 | 5830 | 6095 | 265 | 1000 |  | 265000 | 264739.2196 | Ramna |  |  |  | China Town Express Feeder | 264739.2196 | 295741.6161 | -31002.3966 | -10.4829 | OK
27 | Fakirapul Bazar O/H Feeder | 11 |  | BD014032 | 1 | 26543 | 27825 | 1282 | 1000 |  | 1282000 | 1280738.4132 | Motijheel |  |  |  | Fakirapul Bazar O/H Feeder | 1280738.4132 | 1354979.4454 | -74241.0322 | -5.4791 | OK
28 | PWD Ouarter (RMU) | 11 |  | BD013937 | 1 | 2011 | 2163 | 152 | 1000 |  | 152000 | 151850.4203 | Motijheel |  |  |  | PWD Ouarter (RMU) | 151850.4203 | 150888.5797 | 961.8406 | 0.63745 | OK
29 | Postal Quarter RMU | 11 |  | BD013945 | 1 | 2500 | 2678 | 178 | 1000 |  | 178000 | 177824.8343 | Motijheel |  |  |  | Postal Quarter RMU | 177824.8343 | 174024.8285 | 3800.0057 | 2.1836 | OK
30 | 11/0.4 kV AT-1 | 0.415 |  | DHKH4409 | 1 | 1316 | 1377 | 61 | 100 |  | 6100 | 6093.9971 | Rajarbag |  |  |  | 11/0.4 kV AT-1 | 6093.9971 | 301.7772 | 5792.22 | 1919.3699 | FAULT
31 | 11/0.4 kV AT-2 | 0.415 |  | DHKH4411 | 1 | 454 | 508 | 54 | 100 |  | 5400 | 5394.686 | Rajarbag |  |  |  | 11/0.4 kV AT-2 | 5394.686 | 0 | 5394.686 | #DIV/0! | #DIV/0!
10: Grand Total | 9276362.3521 | 9285500 | 9276362.3521 | -0.098408
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Motijheel | at 33 KV level |  | 2396639.1991
[5 empty] | Ramna | at 33 KV level |  | 3607446.4976
[5 empty] | Rajarbag | at 33 KV level |  | 3272276.6555
[5 empty] | Total = |  |  | 9276362.3521 | 0
1: 33 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Kamalapur Railway 33 KV SIDE (Sending)
13 | 33 kV Kamlapur Circuit-1 | 33 | Main | 41812909530 | 1 | 191.2 | 218.11 | 26.91 | 360000 | 0 | 9687600 | 9666928.772
0 | 0 | 33 | Backup | 41812909595 | 1 | 191.27 | 218.2 | 26.93 | 360000 | 0 | 9694800 | 9674113.4088
18 | 33 kV Kamlapur- 2 Feeder | 33 | Main | 41812909552 | 1 | 66.37 | 75.59 | 9.22 | 360000 | 0 | 3319200 | 3312117.5503
0 | 0 | 33 | Backup | 41621865733 | 1 | 66.38 | 75.6 | 9.22 | 360000 | 0 | 3319200 | 3312117.5503
10: Total | 0 | 13014000 | 12986230.9591
Kamalapur Railway 33 KV SIDE (RECEIVING)
1 | 33 kV Motijheel Circuit-1 | 33 | Import | 101 | 1 | 254.6 | 291 | 36.4 | 270000 | 9828000
6 | 33 kV Motijheel Circuit-2 | 33 | Import | 113 | 1 | 88.4 | 100.9 | 12.5 | 270000 | 3375000
7: 0; 8: 0; 10: Total | 13203000 | 0 | 0
[6 empty] | 0 | 0
1 | 33 kV P&T Circuit | 33 |  | 102 | 1 | 0 | 14.2 | 14.2 | 270000 |  | 3834000
10: Total | 0 | 3834000
[6 empty] | 0 | 0
| Kamalapur Railway 33 KV SIDE |  |  |  |  | 0 | 0
1 | 33 kV 28/35 MVA Transformer (T-1 ) | 33 | Export | 103 | 1 | 279.3 | 303.5 | 24.2 | 240000 |  | 5808000
4 | 33 kV 28/35 MVA Transformer (T-2 ) | 33 | Export | 104 | 1 | 106.5 | 120.5 | 14 | 240000 |  | 3360000
10: Total |  | 9168000
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Kamalapur Railway 33 KV SIDE (Sending); 4: 12986230.9591; 6: EXPORT TO OTHER S/S; 9=8-7: 3834000 | 33 KV NET IMPORT |  | 9152230.9591
6: 33 KV NET IMPORT; 9=8-7: 9152230.9591 | 33 KV TX HV SIDE |  | 9168000
[10 empty] | LOSS UNITS=> |  | -15769.0409
[10 empty] | LOSS % IN => |  | -0.1723%
| TOTAL IMPORT |  | 12986230.9591
1: 11 KV SIDE of___KAMALAPUR RAILWAY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAMALAPUR RAILWAY 11 KV SIDE
6 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | 42 | 1 | 332.5 | 361.3 | 28.8 | 200000 | 5760000 |  | 5780356.3952 |  | 0
10 | 11 kV 20/28 MVA Transformer-2 | 11 | Import | 64 | 1 | 125.7 | 142.5 | 16.8 | 200000 | 3360000 |  | 3371874.5639 |  | 8380000
7: 0; 8: 0; 10: Total | 9120000 |  | 9152230.9591
| KAMALAPUR RAILWAY 11 KV SIDE |  |  |  |  | 0 | 0
1 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 349.8 | 385 | 35.2 | 40000 |  | 1408000 | 1426015.7648 | Rajarbag |  |  |  | Amtola O/H Feeder | 1426015.7648 | 1381038.2208 | 44977.544 | 3.2568 | OK
2 | Police Telecom | 11 | Rajarbag | 130 | 1 | 58.9 | 63.9 | 5 | 40000 |  | 200000 | 202559.0575 | Rajarbag |  |  |  | Police Telecom | 202559.0575 | 214648.1692 | -12089.1117 | -5.6321 | OK
3 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 242.4 | 263.8 | 21.4 | 40000 |  | 856000 | 866952.7661 | Rajarbag |  |  |  | Railway Colony O/H | 866952.7661 | 866692.6078 | 260.1583 | 0.030017 | OK
4 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 617 | 672.9 | 55.9 | 40000 |  | 2236000 | 2264610.2629 | Rajarbag |  |  |  | Shahjahanpur O/H Feeder | 2264610.2629 | 2211281.1394 | 53329.1234 | 2.4117 | OK
5 | 11 KV Majar Feeder | 11 |  | 96 | 1 | 32 | 42.3 | 10.3 | 40000 |  | 412000 | 417271.6585 | Motijheel |  |  |  | 11 KV Majar Feeder | 417271.6585 | 400946.5802 | 16325.0782 | 4.0716 | OK
7 | 11 kV Feeder-6 | 11 |  | 11 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
8 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 304.8 | 318.7 | 13.9 | 40000 |  | 556000 | 563114.1799 | Rajarbag |  |  |  | Momenbagh O/H | 563114.1799 | 1081340.777 | -518226.5971 | -47.9244 | CHECK
9 | 11 kV Feeder-8 | 11 |  | 179 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-8 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 198.6 | 207.3 | 8.7 | 40000 |  | 348000 | 352452.7601 | Rajarbag |  |  |  | 11 kV Uttara Bank Goli Feeder-9 | 352452.7601 | 340197.0984 | 12255.6617 | 3.6025 | OK
12 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 209.5 | 220.6 | 11.1 | 40000 |  | 444000 | 449681.1077 | Rajarbag |  |  |  | 11 kV Baraka O/H Feeder-10 | 449681.1077 | 437396.2693 | 12284.8383 | 2.8086 | OK
13 | 11 kV Feeder-11 | 11 |  | 92 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-11 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 53.5 | 59.2 | 5.7 | 40000 |  | 228000 | 230917.3256 | Motijheel |  |  |  | Dhaka Railway | 230917.3256 | 222748.1001 | 8169.2254 | 3.6675 | OK
15 | Jasimuddin Feeder-13 | 11 |  | 91 | 1 | 112.7 | 155 | 42.3 | 40000 |  | 1692000 | 1713649.6265 | Motijheel |  |  |  | Jasimuddin Feeder-13 | 1713649.6265 | 1656435.8718 | 57213.7546 | 3.454 | OK
16 | Police Box Feeder-14 | 11 |  | 18 | 1 | 52.8 | 69 | 16.2 | 40000 |  | 648000 | 656291.3463 | Motijheel |  |  |  | Police Box Feeder-14 | 656291.3463 | 664194.3349 | -7902.9886 | -1.1899 | OK
17 | 11 kV Feeder-15 | 11 |  | 171 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-15 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 11 kV Feeder-16 | 11 |  | 204 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-16 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | Auxiliary -1 (AT-1 ) | 0.415 |  | DHKF 7632 | 1 | 816.23 | 902.28 | 86.05 | 100 |  | 8605 | 8715.1034 | Rajarbag |  |  |  | Auxiliary -1 (AT-1 ) | 8715.1034 | 2871.4255 | 5843.6779 | 203.5114 | FAULT
20 | Auxiliary -1 (AT-2 ) | 0.415 |  | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 |  | 0 | 0 | Rajarbag |  |  |  | Auxiliary -1 (AT-2 ) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 9152230.9591 | 9036605 | 9152230.9591 | 1.2795
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Rajarbag | at 33 KV level |  | 6134101.0023
[5 empty] | Motijheel | at 33 KV level |  | 3018129.9568
[5 empty] | Total = |  |  | 9152230.9591 | 0
1: 132 KV SIDE of___ BANGABHABAN 132/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE MOTIJHEEL (SENDING)
3 | 132 kV Bangabhaban Circuit-1 | 132 | Exp/Main | 41812909556 | 1 | 34.19 | 36.32 | 2.13 | 1200000 | 0 | 2556000 | 0 | 0 | 0
7 | 132 kV Bangabhaban Circuit-2 | 132 |  | 41812909559 | 1 | 83.53 | 86.61 | 3.08 | 1200000 | 0 | 3696000 | 0 | 0 | 0 |  |  | 0 |  |  |  | 132 kV Bangabhaban Circuit-2
10: Total | 0 | 6252000 | 0
BANGABHABAN 33 KV SIDE (RECEIVING)
RECEIVE
10: Total | 0 | 0 | 0
BANGABHABAN 33 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 132; 4: EXPORT |  | 0
2: Feeder No.2; 3: 132 |  | 0
10: Total |  | 0
BANGABHABAN 33 KV SIDE
3: 132; 4: NET IMPORT |  | 0
3: 132 |  | 0
10: Total |  | 0 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: 132 KV SIDE MOTIJHEEL (SENDING); 4: 6252000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 6252000
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 6252000 | 33 KV TX HV SIDE |  | 6252000
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 0
2: IMPORT-4 | LOSS % IN => |  | 0%
| 132 KV TOTAL IMPORT |  | 6252000
1: 11 KV SIDE of___BANGABHABAN 132/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGABHABAN 11 KV SIDE
11 | 11 kV 28/35 MVA Transformer (GT-2) | 11 | Import | 4150744 | 1 | 1513142.4 | 1516831.3 | 3688.9 | 1000 | 3688900 |  | 3715823.6744
12 | 11 kV 28/35 MVA Transformer (GT-1) | 11 | Import | 4150742 | 1 | 1437263.2 | 1439781 | 2517.8 | 1000 | 2517800 |  | 2536176.3256
7: 0; 8: 0; 10: Total | 6206700 |  | 6252000
| BANGABHABAN 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 214079.71 | 215236.15 | 1156.44 | 1000 | Estimated | 814940.028 | 816951.1322 | Motijheel | 67 | Meter Bad |  | 11 kV DIT S/S-1 Feeder | 816951.1322 | 793502.3098 | 23448.8224 | 2.9551 | OK
2 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 24049.87 | 24132.19 | 82.32 | 1000 |  | 82320 | 82523.1488 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-1 | 82523.1488 | 83389.7606 | -866.6118 | -1.0392 | OK
3 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 |  | 0 | 0 | Maniknagar |  |  |  | 11 kV Saidabad Water Treatment | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Bangladesh Bank Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV P & T Substation | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33840.33 | 33853.02 | 12.69 | 1000 | Estimated | 0 | 0 | Ramna |  |  |  | 11 kV Osmani Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 729797.04 | 731598.0289 | Motijheel | 60 | Meter Bad |  | 11 kV Modhumita via Ovisar | 731598.0289 | 710599.0834 | 20998.9455 | 2.9551 | OK
8 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15730.83 | 15810 | 79.17 | 1000 |  | 79170 | 79365.3753 | Motijheel |  |  |  | 11 kV Sugar Bhaban & Car Parking | 79365.3753 | 70158.8804 | 9206.4949 | 13.1224 | OK
9 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 245496.9 | 246649.65 | 1152.75 | 1000 |  | 1152750 | 1155594.7497 | Motijheel |  |  |  | 11 kV Navana O/H Feeder | 1155594.7497 | 1181422.0182 | -25827.2685 | -2.1861 | OK
13 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14313.16 | 14474.96 | 161.8 | 1000 |  | 161800 | 162199.2891 | Motijheel |  |  |  | 11 kV Bangabhaban Switching Circuit-2 | 162199.2891 | 174416.2041 | -12216.915 | -7.0045 | OK
14 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Motijheel |  |  |  | 11 kV Motijheel-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 243265.68 | 243866.0096 | Motijheel | 20 | Meter Bad |  | 11 kV WAPDA building RMU Feeder | 243866.0096 | 236866.3611 | 6999.6485 | 2.9551 | OK
16 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163401.03 | 163764.06 | 363.03 | 1000 |  | 363030 | 363925.8833 | Motijheel |  |  |  | 11 kV PDB Design Feeder | 363925.8833 | 326878.2024 | 37047.6809 | 11.3338 | OK
17 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20538.85 | 20596.96 | 58.11 | 1000 | Estimated | 243265.68 | 243866.0096 | Motijheel | 20 | Meter Bad |  | 11 kV BB Hospital Zone RMU Feeder | 243866.0096 | 236866.3611 | 6999.6485 | 2.9551 | OK
18 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 340571.952 | 341412.4135 | Motijheel | 28 | Meter Bad |  | 11 kV Sonali Bank RMU Feeder | 341412.4135 | 331612.9056 | 9799.5079 | 2.9551 | OK
19 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122597.98 | 122899.9 | 301.92 | 1000 |  | 301920 | 302665.0764 | Motijheel |  | Meter Bad |  | 11 kV Janata Bank Feeder | 302665.0764 | 348419.8864 | -45754.81 | -13.1321 | OK
20 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 272305.38 | 273094.04 | 788.66 | 1000 |  | 788660 | 790606.2505 | Motijheel |  |  |  | 11 kV DIT S/S RMU Feeder | 790606.2505 | 819439.2218 | -28832.9713 | -3.5186 | OK
21 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 80121.74 | 80707.72 | 585.98 | 1000 |  | 585980 | 587426.078 | Motijheel |  |  |  | 11 kV Sena Kalyan Feeder | 587426.078 | 481785.1466 | 105640.9314 | 21.927 | OK
22 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192447.87 | 192560.77 | 112.9 | 1000 | Estimated | 340571.952 | 341412.4135 | Motijheel | 28 | Meter Bad |  | 11 kV BCIC Feeder | 341412.4135 | 331612.9056 | 9799.5079 | 2.9551 | OK
23 | 11/0.4 kV AT-1 | 0.415 |  | 63412931 | 1 | 63258 | 66825 | 3567 | 1 |  | 3567 | 3575.8026 | Motijheel |  |  |  | 11/0.4 kV AT-1 | 3575.8026 | 0 | 3575.8026 | #DIV/0! | #DIV/0!
24 | 11/0.4 kV AT-2 | 0.415 |  | 63403117 | 1 | 13772 | 22885 | 9113 | 1 | Estimated | 5000 | 5012.339 | Motijheel |  |  |  | 11/0.4 kV AT-2 | 5012.339 | 5030.7529 | -18.414 | -0.36603 | OK
10: Grand Total | 6252000 | 6236609.332 | 6252000 | 0.24678
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Maniknagar | at 33 KV level |  | 0
[5 empty] | Ramna | at 33 KV level |  | 0
[5 empty] | Swamibag | at 33 KV level |  | 0
[5 empty] | Motijheel | at 33 KV level |  | 6252000
[5 empty] | Total = |  |  | 6252000 | 0
1: 132 KV SIDE of___NARINDA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
MANIKNAGAR 132 KV SIDE
1 | 132 kV Maniknagar Circuit-1 at Maniknagar | 132 | Import | 06604331 | 1 | 8833.87 | 8876.04 | 42.17 | 480000 | 20241600 |  |  |  | Reading Corrected
2 | 132 kV Maniknagar Circui-2 at Maniknagar | 132 | Import | 06604334 | 1 | 8842.46 | 8884.95 | 42.49 | 480000 | 20395200
9=8-7: Total Import/Export | 40636800 | 0
10: Net Total | 40636800
NARINDA 132 KV SIDE (RECEIVING)
9=8-7: Total Import/Export | 0 | 0
9=8-7: Net Total | 40636800
NARINDA 132 KV SIDE (EXPORT TO OTHER S/S)
2: Feeder No.1; 3: 132; 4: EXPORT |  | 0
2: Feeder No.2; 3: 132 |  | 0
10: Total |  | 0
NARINDA 132 KV SIDE
2: 132/33 KV GT-1; 3: 132; 4: NET IMPORT |  | 0
2: 132/33 KV GT-2; 3: 132 |  | 0
10: Total |  | 40636800
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: MANIKNAGAR 132 KV SIDE; 4: 40636800; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 40636800
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 40636800 | 33 KV NET IMPORT |  | 40627200
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 9600
2: IMPORT-4 | LOSS % IN => |  | 0.02362%
| 132 KV TOTAL IMPORT |  | 40636800
1: 33 KV SIDE of___NARINDA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
6 | 132/33 kV 50/75 MVA GT-1 Incoming | 33 | Import | 06604301 | 1 | 9208.93 | 9251.22 | 42.29 | 480000 | 20299200
7 | 132/33 kV 50/75 MVA GT-2 Incoming | 33 | Import | 06604304 | 1 | 9033.03 | 9075.38 | 42.35 | 480000 | 20328000
7: 0; 8: 0; 10: Total | 40627200 |  | 0
| NARINDA 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 33 kV 20/28 MVA Transformer T-3 | 33 | Export | 06604300 | 1 | 9670.71 | 9719.91 | 49.2 | 180000 |  | 8856000 | 8894787.493 |  | 18087875.7861 | Narinda 33/11 kv ss |  | 33 kV 20/28 MVA Transformer T-3 | 8894787.493 | 8996666.7386 | -101879.2456 | -1.1324 | OK
8 | 33 kV 20/28 MVA Transformer T-4 | 33 | Export | 06604303 | 1 | 9799.67 | 9850.52 | 50.85 | 180000 |  | 9153000 | 9193088.2931 |  |  |  |  | 33 kV 20/28 MVA Transformer T-4 | 9193088.2931 | 8931565.2305 | 261523.0626 | 2.9281 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 18009000 | 18087875.7861 |  |  |  |  | 33 KV Feeders | 18087875.7861 | 17928231.9691 | 159643.817 | 0.89046 | OK
1 | 33 kV New Ramna Feeder | 33 | Export | 9155465/9155477 | 1 | 29254 | 29254 | 0 | 1000 | From Downstream | 2505600 | 2516574.0224 |  | 2516574.0224 | New Ramna 33/11 kv ss |  | 33 kV New Ramna Feeder | 2516574.0224 | 1520843.5632 | 995730.4592 | 65.4722 | FAULT
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Bangshal-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 |  | 0 | 0 |  | 9376123.4544 | Bangshal 33/11 kv ss |  | 33 kV Kazla-1 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5643.19 | 5667.71 | 24.52 | 180000 |  | 4413600 | 4432930.6774 |  |  |  |  | 33 kV Kumertully-1 Feeder | 4432930.6774 | 4542638.5623 | -109707.8849 | -2.4151 | OK
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5507.58 | 5541.95 | 34.37 | 180000 |  | 6186600 | 6213696.0597 |  | 0 | Kazla 33/11 kv ss |  | 33 kV Kumertully-2 Feeder | 6213696.0597 | 5960404.7378 | 253291.3219 | 4.2496 | OK
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 |  | 0 | 0 |  |  |  |  | 33 kV Kazla-2 Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
11 | 33 kV Bangshal-2 Feeder | 33 | Export | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 9335237 | 9376123.4544 |  | 10646626.7371 | Kumartully 33/11 kv ss |  | 33 kV Bangshal-2 Feeder | 9376123.4544 | 10281481.1676 | -905357.7132 | -8.8057 | OK
10: Total |  | 22441037 | 22539324.2139 |  |  |  |  | 0 | 22539324.2139 | 22305368.0309 | 233956.183 | 1.0489 | OK
9=8-7: Grand Total | 40627200 | 40450037 | 40627200 | 0.43798
1: 11 KV SIDE of___NARINDA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 11 KV SIDE
8 | 33/11 kV 20/28 MVA T-3 Incoming | 11 | Import | 06604351 | 1 | 10875.13 | 10930.46 | 55.33 | 160000 | 8852800 |  | 8914243.9409
9 | 33/11 kV 20/28 MVA T-4 Incoming | 11 | Import | 06604295 | 1 | 11206.19 | 11263.13 | 56.94 | 160000 | 9110400 |  | 9173631.8452
7: 0; 8: 0; 10: Total | 17963200 |  | 18087875.7861
| NARINDA 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24616.19 | 24756.85 | 140.66 | 8000 |  | 1125280 | 1143423.9412 | Narinda |  |  |  | 11 kV Bonogram Feeder | 1143423.9412 | 1139801.4532 | 3622.488 | 0.31782 | OK
2 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16642.26 | 16724.98 | 82.72 | 8000 |  | 661760 | 672430.175 | Swamibag |  |  |  | 11 kV Sha Saheb Len Feeder | 672430.175 | 685656.1379 | -13225.9629 | -1.9289 | OK
3 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 487.34 | 500.94 | 13.6 | 40000 |  | 544000 | 552771.4205 | Maniknagar |  |  |  | 11 kV Sadiabad Water Treatment | 552771.4205 | 653217.1868 | -100445.7663 | -15.3771 | OK
4 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5501.64 | 5528.76 | 27.12 | 40000 |  | 1084800 | 1102291.2443 | Narinda |  |  |  | 11 kV Manashi Feeder | 1102291.2443 | 1122855.7324 | -20564.4881 | -1.8314 | OK
5 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3373.76 | 3426.03 | 52.27 | 40000 |  | 2090800 | 2124511.9226 | Swamibag | Old Maniknagar |  |  | 11 kV Jatrabari Feeder | 2124511.9226 | 2030258.73 | 94253.1926 | 4.6424 | OK
6 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8518.25 | 8559.74 | 41.49 | 40000 |  | 1659600 | 1686359.282 | Narinda | Old Jatrabari |  |  | 11 kV Wari Feeder | 1686359.282 | 1652611.2397 | 33748.0423 | 2.0421 | OK
7 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7262.99 | 7302.23 | 39.24 | 40000 |  | 1569600 | 1594908.1278 | Narinda |  |  |  | 11 kV Narinda Feeder | 1594908.1278 | 1590073.4608 | 4834.667 | 0.30405 | OK
10 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5965.54 | 5997.97 | 32.43 | 40000 |  | 1297200 | 1318115.968 | Swamibag |  |  |  | 11 kV Distillary Feeder | 1318115.968 | 1326607.8506 | -8491.8826 | -0.64012 | OK
11 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 5006.32 | 5033.32 | 27 | 40000 |  | 1080000 | 1097413.8494 | Narinda |  |  |  | 11 kV Thatari Bazar Feeder | 1097413.8494 | 1083315.7174 | 14098.132 | 1.3014 | OK
12 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7762.22 | 7795.93 | 33.71 | 40000 |  | 1348400 | 1370141.5135 | Swamibag |  |  |  | 11 kV Swamibagh Feeder | 1370141.5135 | 1100261.4381 | 269880.0753 | 24.5287 | OK
13 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6347.36 | 6375.33 | 27.97 | 40000 |  | 1118800 | 1136839.4581 | Narinda |  |  |  | 11 kV Tipu Sultan Feeder | 1136839.4581 | 1115189.8112 | 21649.6469 | 1.9413 | OK
14 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 |  | 0 | 0 | Narinda | Old Wari |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 26064.5 | 30046.6 | 3982.1 | 444.44 |  | 1769804.524 | 1798340.7365 | Narinda |  |  |  | 11 kV Folder Street Feeder | 1798340.7365 | 1748933.3106 | 49407.4259 | 2.825 | OK
16 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 384194 | 394199 | 10005 | 80 |  | 800400 | 813305.5973 | Narinda |  |  |  | 11 kV Bhajohari Feeder | 813305.5973 | 819688.7194 | -6383.1221 | -0.77873 | OK
17 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 31907.7 | 34337.3 | 2429.6 | 444.44 |  | 1079811.424 | 1097222.2328 | Narinda |  |  |  | 11 kV Lal mohon shaha Feeder | 1097222.2328 | 1092539.7614 | 4682.4714 | 0.42859 | OK
18 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 36247.2 | 36817.8 | 570.6 | 1000 |  | 570600 | 579800.3171 | Swamibag |  |  |  | 11 kV Dupkhola Feeder | 579800.3171 | 568589.4506 | 11210.8665 | 1.9717 | OK
1 | 11/0.4 kV Aux Transformer-1 | 0.415 |  | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11/0.4 kV Aux Transformer-2 | 0.415 |  | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 |  | 0 | 0 | Narinda |  |  |  | 11/0.4 kV Aux Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 18087875.7861 | 17800855.948 | 18087875.7861 | 1.6124
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
6: Narinda; 7: at 33 KV level; 9=8-7: 12120104.4695 | Import from Shyampur, Motijeel &Swamibagh |  | 650000
[5 empty] | Maniknagar | at 33 KV level |  | 552771.4205
6: Swamibag; 7: at 33 KV level; 9=8-7: 5964999.8962 | Export to Narinda |  | 100000
[5 empty] | Total = |  |  | 18637875.7861 | 550000
1: 33 KV SIDE of___KUMERTULY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
4 | 33 kV Kumertully-1 Feeder | 33 | Export | 06604318 | 1 | 5643.19 | 5667.71 | 24.52 | 180000 | 0 | 4413600 | 4432930.6774
9 | 33 kV Kumertully-2 Feeder | 33 | Export | 06604290 | 1 | 5507.58 | 5541.95 | 34.37 | 180000 | 0 | 6186600 | 6213696.0597
2: MITFORD 33 KV SIDE |  | 10600200 | 10646626.7371
1 | Kumartuly Circuit-1 | 33 | 0 | DHK-66493 | 1 | 1285151 | 1286272 | 1121 | 180 | 0 | 201780 | 201780
6 | Kumartuly Circuit-2 | 33 | 0 | DHK-60914 | 1 | 759469.7 | 761041 | 1571.3 | 180 | 0 | 282834 | 282834
10: Total |  | 484614 | 484614
KUMERTULY 33 KV SIDE (RECEIVING)
5 | 33 kV Mitford Circuit-1 | 33 | Import | DHK60965 | 1 | 279488 | 280611.3 | 1123.3 | 180 | 202194
6 | 33 kV Narinda Circuit-1 | 33 | Import | DHK60959 | 1 | 973808 | 982002.8 | 8194.8 | 540 | 4425192
9 | 33 kV Mitford Circuit-2 | 33 | Import | DHK86072 | 1 | 1760.52 | 1762.1 | 1.58 | 180000 | 284400
10 | 33 kV Narinda Circuit-2 | 33 | Import | DHK60957 | 1 | 882448.2 | 893878.6 | 11430.4 | 540 | 6172416
7: 0; 8: 0; 10: Total | 11084202 | 0 | 0
| KUMERTULY 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| KUMERTULY 33 KV SIDE |  |  |  |  | 0 | 0
7 | 33/11 kV 20/28 MVA Transformer (T-1) | 33 | Export | DHK60960 | 1 | 96076.8 | 119591.5 | 23514.7 | 180 |  | 4232646
8 | 33/11 kV 20/28 MVA Transformer (T-2) | 33 | Export | DHK60958 | 1 | 261765.4 | 294551.8 | 32786.4 | 180 |  | 5901552
10: Total |  | 10134198
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: NARINDA 33 KV SIDE; 4: 10646626.7371; 6: EXPORT TO OTHER S/S; 9=8-7: 484614 | 33 KV NET IMPORT |  | 10162012.7371
2: MITFORD 33 KV SIDE; 4: 0; 6: 33 KV NET IMPORT; 9=8-7: 10162012.7371 | 33 KV TX HV SIDE |  | 11084202
2: IMPORT-3 | LOSS UNITS=> |  | -922189.2629
2: IMPORT-4 | LOSS % IN => |  | -9.075%
| TOTAL IMPORT |  | 10646626.7371
1: 11 KV SIDE of___KUMERTULY 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KUMERTULY 11 KV SIDE
19 | 33/11 kV 20/28 MVA T-1 Incoming | 11 | Import | 06604403 | 1 | 7219.28 | 7226.87 | 7.59 | 160000 | 4232646 |  | 4250618.3452 |  | From Upstream
20 | 33/11 kV 20/28 MVA T-2 Incoming | 11 | Import | 06604410 | 1 | 6629.02 | 6665.81 | 36.79 | 160000 | 5886400 |  | 5911394.3919
7: 0; 8: 0; 10: Total | 10119046 |  | 10162012.7371
| KUMERTULY 11 KV SIDE |  |  |  |  | 0 | 0
11 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62362.9 | 62634.8 | 271.9 | 2222.22 |  | 604221.618 | 604954.0102 | Banglabazar |  |  |  | 11kV Babubazar Feeder | 604954.0102 | 476949.7245 | 128004.2857 | 26.8381 | OK
12 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4560.66 | 4589.74 | 29.08 | 40000 |  | 1163200 | 1164609.944 | Banglabazar |  |  |  | 11kV Islampur Feeder | 1164609.944 | 1430849.1736 | -266239.2296 | -18.6071 | OK
13 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 |  | 0 | 0 | Bangshal |  |  |  | 11kV Champatully Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5132.38 | 5143.44 | 11.06 | 40000 |  | 442400 | 442936.2442 | Banglabazar |  |  |  | 11kV Majar O/H Feeder | 442936.2442 | 536568.4401 | -93632.1959 | -17.4502 | OK
15 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 |  |  |  |  | 11kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5420.2 | 5442.14 | 21.94 | 40000 |  | 877600 | 878663.7611 | Banglabazar |  |  |  | 11kV Sadarghat Feeder | 878663.7611 | 1216221.7976 | -337558.0365 | -27.7546 | OK
17 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 |  | 0 | 0 | Bangshal | No Load |  |  | 11kV Mitford Hospital Feeder | 0 | 40077.0255 | -40077.0255 | -100 | CHECK
18 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4052.11 | 4079.87 | 27.76 | 40000 |  | 1110400 | 1111745.9438 | Banglabazar |  |  |  | 11kV Zindabahar Feeder | 1111745.9438 | 834662.018 | 277083.9258 | 33.1971 | OK
21 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1216328.4 | 1217802.7423 | Banglabazar | 100 |  |  | 11kV Police fari Feeder | 1217802.7423 | 1144679.3389 | 73123.4034 | 6.3881 | OK
22 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5878.45 | 5901.7 | 23.25 | 40000 |  | 930000 | 931127.2764 | Banglabazar |  |  |  | 11kV Patuatully Feeder | 931127.2764 | 1021492.1651 | -90364.8887 | -8.8464 | OK
23 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8147.67 | 8198.55 | 50.88 | 40000 |  | 2035200 | 2037666.9172 | Banglabazar |  |  |  | 11kV Laxmibazar Feeder | 2037666.9172 | 1989498.8221 | 48168.095 | 2.4211 | OK
24 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3746.74 | 3757.99 | 11.25 | 40000 |  | 450000 | 450545.4563 | Banglabazar |  |  |  | 11kV Jhonson Road Feeder | 450545.4563 | 410865.9482 | 39679.5081 | 9.6575 | OK
25 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7200.1 | 7226.32 | 26.22 | 40000 |  | 1048800 | 1050071.2769 | Banglabazar |  |  |  | 11kV Dholaikhal Feeder | 1050071.2769 | 1251993.0269 | -201921.7501 | -16.128 | OK
26 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3579.1 | 3585.71 | 6.61 | 40000 |  | 264400 | 264720.4859 | Banglabazar |  |  |  | 11kV Bikrompur Garden City Feeder | 264720.4859 | 275126.2119 | -10405.726 | -3.7822 | OK
27 | 11/0.4 kV AT-1 | 0.415 |  | 05379603 | 1 | 0 | 0 | 0 | 2 |  | 0 | 0 | Banglabazar |  |  |  | 11/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
28 | 11/0.4 kV AT-2 | 0.415 |  | 05378636 | 1 | 165364.8 | 168944.8 | 3580 | 2 |  | 7160 | 7168.6788 | Banglabazar |  |  |  | 11/0.4 kV AT-2 | 7168.6788 | 4775.6076 | 2393.0713 | 50.1103 | FAULT
10: Grand Total | 10162012.7371 | 10149710.018 | 10162012.7371 | 0.12121
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 0
[5 empty] | Banglabazar | at 33 KV level |  | 10162012.7371
[5 empty] | Total = |  |  | 10162012.7371 | 0
1: 33 KV SIDE of___BANGSHAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NARINDA 33 KV SIDE
2 | 33 kV Bangshal-1 Feeder | 33 | Export | 06604293 | 1 | 2613.5 | 2613.5 | 0 | 180000 | 0 | 0 | 0
11 | 33 kV Bangshal-2 Feeder | 33 |  | 06604328 | 1 | 0 | 0 | 0 | 180000 | Estimated SS End | 9335237 | 9376123.4544
10: Total | 0 | 9335237 | 9376123.4544
BANGSHAL 33 KV SIDE (RECEIVING)
2 | 33 kV Narinda Circuit-1 | 33 | Import | Mat-152447/1191738/007 | 1 | 114810700 | 117707400 | 2896700 | 1 | 2896700
5 | 33 kV Narinda Circuit-2 | 33 | Import | Mat-152447/1191738/002 | 1 | 229270900 | 233197900 | 3927000 | 1 | 3927000
7: 0; 8: 0; 10: Total | 6823700 | 0 | 0
| MOGBAZAR T&T 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| MOGBAZAR T&T 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33/11 kV 28/35 MVA Transformer (T-1) | 33 | Export | Mat-152447/1191738/009 | 1 | 121964700 | 124372000 | 2407300 | 1 |  | 2407300 |  |  | % diffn betn 33 kV Impt & 11 kV Expt=
4 | 33/11 kV 28/35 MVATransformer (T-2) | 33 | Export | Mat-152447/1191738/004 | 1 | 226792500 | 235669900 | 8877400 | 1 |  | 8877400 |  |  | #VALUE!
10: Total |  | 11284700
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: NARINDA 33 KV SIDE; 4: 9376123.4544; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 9376123.4544
6: 33 KV NET IMPORT; 9=8-7: 9376123.4544 | 33 KV TX HV SIDE |  | 11284700
[10 empty] | LOSS UNITS=> |  | -1908576.5456
[10 empty] | LOSS % IN => |  | -20.36%
| TOTAL IMPORT |  | 9376123.4544
1: 11 KV SIDE of___BANGSHAL 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
BANGSHAL 11 KV SIDE
6 | 33/11 kV 28/35 MVA Transformer-1 | 11 | Import | 340180016886 | 1 | 121982461 | 124893850 | 2911389 | 1 | 2911389 |  | 2924140.2964 |  | 0
7 | 33/11 kV 28/35 MVA Transformer-2 | 11 | Import | 340180012685 | 1 | 230097800 | 236521648 | 6423848 | 1 | 6423848 |  | 6451983.158
7: 0; 8: 0; 10: Total | 9335237 |  | 9376123.4544
| BANGSHAL 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 37591630 | 38350227 | 758597 | 1 |  | 758597 | 760951.1172 | Bangshal |  |  |  | 11 kV Bangladesh Math Feeder | 760951.1172 | 778854.3109 | -17903.1936 | -2.2987 | OK
2 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Bangshal |  |  |  | 11 kV Siddikbazar Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 48292149 | 49714612 | 1422463 | 1 |  | 1422463 | 1426877.2604 | Banglabazar |  |  |  | 11 kV Tatibazar feeder | 1426877.2604 | 1429747.5487 | -2870.2883 | -0.20075 | OK
5 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 19895217 | 20644794 | 749577 | 1 |  | 749577 | 751903.1259 | Bangshal |  |  |  | 11 kV Bangsal Road Feeder | 751903.1259 | 737930.5287 | 13972.5972 | 1.8935 | OK
8 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 45156791 | 46320451 | 1163660 | 1 |  | 1163660 | 1167271.1296 | Bangshal |  |  |  | 11 kV Hazi Osman Gani Feeder | 1167271.1296 | 1660584.0104 | -493312.8808 | -29.7072 | OK
9 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 61068329 | 62248027 | 1179698 | 1 |  | 1179698 | 1183358.8995 | Bangshal |  |  |  | 11 kV French Road Feeder | 1183358.8995 | 1169829.7548 | 13529.1448 | 1.1565 | OK
10 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 28992386 | 30418512 | 1426126 | 1 |  | 1426126 | 1430551.6276 | Bangshal |  |  |  | 11 kV North-South Road Feeder | 1430551.6276 | 1633419.2244 | -202867.5968 | -12.4198 | OK
11 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 61260126 | 62764098 | 1503972 | 1 |  | 1503972 | 1508639.2033 | Bangshal |  |  |  | 11 kV Nazirabazar Feeder | 1508639.2033 | 1596892.4609 | -88253.2576 | -5.5266 | OK
12 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 49123470 | 50259494 | 1136024 | 1 |  | 1136024 | 1139549.3681 | Narinda |  |  |  | 11 kV Suritolla Feeder | 1139549.3681 | 1267199.3373 | -127649.9692 | -10.0734 | OK
13 | AT-1 | 0.415 |  | DHK-4415 | 1 | 727.72 | 734.14 | 6.42 | 100 |  |  | 0 | Bangshal |  |  |  | AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | AT-2 | 0.415 |  | DHK-4410 | 1 | 659.01 | 684.51 | 25.5 | 100 |  | 7000 | 7021.7228 | Bangshal |  |  |  | AT-2 | 7021.7228 | 7023.9917 | -2.2689 | -0.032302 | OK
10: Grand Total | 9376123.4544 | 9347117 | 9376123.4544 | 0.31033
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Bangshal | at 33 KV level |  | 6809696.8259
[5 empty] | Banglabazar | at 33 KV level |  | 1426877.2604
[5 empty] | Narinda | at 33 KV level |  | 1139549.3681
[5 empty] | Total = |  |  | 9376123.4544 | 0
1: 132 KV SIDE of___KAZLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | 132kV Kazla Circuit-1 at Maniknagar | 132 | Import | ABB03905 | 1 | 714735 | 747732 | 32997 | 1000 | 32997000 |  |  |  | 132 kV line Loss=
2 | 132kV Kazla Circuit-2 at Maniknagar | 132 | Import | ABB03904 | 1 | 536435 | 560011 | 23576 | 1000 | 23576000 |  |  |  | 100
7: 0; 8: 0; 9=8-7: Total Import/Export | 56573000 | 0
7: 0; 8: 0; 10: Net Total | 56573000
| KAZLA 132 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
3 | 132kV Maniknagar Circuit-1 | 132 | Main | 41812909505 | 1 | 595.84 | 623.34 | 27.5 | 1200000 | 33000000
|  | 132 | Backup | 41812909603 | 1 | 595.82 | 623.32 | 27.5 | 1200000 | 33000000 |  |  |  | % diffn betn 132 kV Imp & 132 kV exp
6 | 132kV Maniknagar Circuit-2 | 132 | Main | 41812909540 | 1 | 446.1 | 465.71 | 19.61 | 1200000 | 23532000
|  | 132 | Backup | 41812909587 | 1 | 446.12 | 465.72 | 19.6 | 1200000 | 23520000 |  |  |  | % diffn betn 132 kV Imp & 33 kV exp
7: 0; 8: 0; 9=8-7: Total Import/Export | 56532000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 56532000
| KAZLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| KAZLA 132 KV SIDE |  |  |  |  | 0 | 0
4 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Main | 41812909542 | 1 | 596.18 | 623.76 | 27.58 | 1200000 |  | 33096000 |  |  | #DIV/0!
|  | 132 | Backup | 41812909589 | 1 | 596.53 | 624.12 | 27.59 | 1200000 |  | 33108000
7 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Main | 41812909501 | 1 | 445.95 | 465.48 | 19.53 | 1200000 |  | 23436000 |  |  | 100
|  | 132 | Backup | 41812909606 | 1 | 445.89 | 465.42 | 19.53 | 1200000 |  | 23436000
10: Total |  | 56532000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (SENDING); 4: 56573000; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 56573000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 56573000 | 33 KV NET IMPORT |  | 56325600
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 247400
2: IMPORT-4 | LOSS % IN => |  | 0.4373%
| 132 KV TOTAL IMPORT |  | 56573000
1: 33 KV SIDE of___KAZLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Narinda (33 kV Side)
3 | 33 kV Kazla-1 Feeder | 33 | Export | 06604297 | 1 | 4114.51 | 4114.51 | 0 | 180000 | 0 | 0 | 0
10 | 33 kV Kazla-2 Feeder | 33 | Export | 06604326 | 1 | 1828.4 | 1828.4 | 0 | 180000 | 0 | 0 | 0
MANKNAGAR 33 kV Side
5 | 33kV Kazla-1 Feeder | 33 | Digital | ABB03917 | 1 | 311310 | 311310 | 0 | 2000 | 0 | 0 | 0
10 | 33kV Kazla-2 Feeder | 33 | Digital | ABB03920 | 1 | 525397 | 525397 | 0 | 2000 | 0 | 0 | 0
KAZLA 33 kV Side
15 | 132/33 kV 80/120 MVA GT-1 Incomming (LV) | 33 | Main | 41812909533 | 1 | 989.76 | 1035.55 | 45.79 | 720000 | 32968800
|  | 33 | Backup | 41812909582 | 1 | 989.83 | 1035.63 | 45.8 | 720000 | 32976000
16 | 132/33 kV 80/120 MVA GT-2 Incomming (LV) | 33 | Main | 41812909479 | 1 | 740.83 | 773.27 | 32.44 | 720000 | 23356800
|  | 33 | Backup | 41812909622 | 1 | 740.73 | 773.17 | 32.44 | 720000 | 23356800
7: 0; 8: 0; 10: Total | 56325600 |  | 0
| KAZLA 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33/11 kV 20/28 MVA T-1 | 33 | Main | 41812909465 | 1 | 990.49 | 1040.01 | 49.52 | 240000 |  | 11884800 | 11898323.8721 |  | 38963887.131 | Kazla 33/11 kv ss | 1.6094 | 33/11 kV 20/28 MVA T-1 | 11898323.8721 | 11609794.9909 | 288528.8812 | 2.4852 | OK
|  | 33 | Backup | 41812909596 | 1 | 990.24 | 1039.74 | 49.5 | 240000 |  | 11880000 | 11893518.4102 |  |  |  |  | 0 | 11893518.4102 | 11607396.273 | 286122.1372 | 2.465 | OK
13 | 33/11 kV 28/35 MVA T-5 | 33 | Main | 41812909536 | 1 | 104.99 | 115.16 | 10.17 | 360000 |  | 3661200 | 3665366.1282 |  |  |  |  | 33/11 kV 28/35 MVA T-5 | 3665366.1282 | 3857138.5011 | -191772.3729 | -4.9719 | OK
|  | 33 | Backup | 41812909578 | 1 | 105 | 113.55 | 8.55 | 360000 |  | 3078000 | 3081502.4972 |  |  |  |  | 0 | 3081502.4972 | 3857138.5011 | -775636.0039 | -20.1091 | OK
14 | 33/11 kV 20/28 MVA T-2 | 33 | Main | 41812909554 | 1 | 996.99 | 1039.05 | 42.06 | 240000 |  | 10094400 | 10105886.5521 |  |  |  |  | 33/11 kV 20/28 MVA T-2 | 10105886.5521 | 10417632.1582 | -311745.606 | -2.9925 | OK
|  | 33 | Backup | 41812909613 | 1 | 996.01 | 1038.32 | 42.31 | 240000 |  | 10154400 | 10165954.8269 |  |  |  |  | 0 | 10165954.8269 | 10408037.2863 | -242082.4593 | -2.3259 | OK
17 | 33/11 kV 20/28 MVA T-3 | 33 | Main | 41812909544 | 1 | 869.25 | 903.03 | 33.78 | 240000 |  | 8107200 | 8116425.2908 |  |  |  |  | 33/11 kV 20/28 MVA T-3 | 8116425.2908 | 7973338.5434 | 143086.7475 | 1.7946 | OK
|  | 33 | Backup | 41812909614 | 1 | 869.27 | 903.06 | 33.79 | 240000 |  | 8109600 | 8118828.0218 |  |  |  |  | 0 | 8118828.0218 | 7970939.8254 | 147888.1964 | 1.8553 | OK
22 | 33/11 kV 10/14 MVA T-4 | 33 | Main | 41812909506 | 1 | 449.26 | 470.81 | 21.55 | 240000 |  | 5172000 | 5177885.2877 |  |  |  |  | 33/11 kV 10/14 MVA T-4 | 5177885.2877 | 5080484.6675 | 97400.6201 | 1.9172 | OK
|  | 33 | Backup | 41812909602 | 1 | 449.4 | 470.94 | 21.54 | 240000 |  | 5169600 | 5175482.5567 |  |  |  |  | 0 | 5175482.5567 | 5099674.4113 | 75808.1454 | 1.4865 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 38919600 | 38963887.131 |  |  |  |  | 33 KV Feeders | 38963887.131 | 38938388.8611 | 25498.2699 | 0.065484 | OK
10 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 550.9 | 571.22 | 20.32 | 360000 |  | 7315200 | 7323524.0635 | Kazla |  |  |  | 33 kV Shahriar Steel Feeder | 7323524.0635 | 7145780.8426 | 177743.2209 | 2.4874 | OK
|  | 33 | Backup | 41812909580 | 1 | 550.86 | 571.17 | 20.31 | 360000 |  | 7311600 | 7319919.967 |  |  |  |  | 0 | 7319919.967 | 7145780.8426 | 174139.1244 | 2.437 | OK
11 | 33 kV Kazla Outdoor Bus (Shahriar steel) | 33 | Main | 41812909531 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 | Kazla |  |  |  | 33 kV Kazla Outdoor Bus (Shahriar steel) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909581 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
12 | 33 kV Spare Feeder 3 | 33 | Main | 41812909529 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 3 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909574 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
18 | 33 kV Spare Feeder 5 | 33 | Main | 41812909545 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909618 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 33 kV Spare Feeder 6 | 33 | Main | 41812909481 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 6 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909560 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Spare Feeder 7 | 33 | Main | 41812909523 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909565 | 1 | 0 | 0 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 602.93 | 630.73 | 27.8 | 360000 |  | 10008000 | 10019388.2364 | Kazla |  |  |  | 33 kV Zahir Steel | 10019388.2364 | 9121125.0936 | 898263.1428 | 9.8482 | OK
|  | 33 | Backup | 41812909563 | 1 | 603.14 | 630.96 | 27.82 | 360000 |  | 10015200 | 10026596.4294 |  |  |  |  | 0 | 10026596.4294 | 9128321.2475 | 898275.1819 | 9.8405 | OK
| Auxiliary Transformer-3 (AT-3) | 0.415 |  |  | 1 | 2290.62 | 2407.99 | 117.37 | 160 |  | 18779.2 | 18800.5691 | [5 empty] | 18800.5691 | 18705.2028
10: Total |  | 17341979.2 | 17361712.869 |  |  |  |  | 0 | 17361712.869 | 16285611.1389 | 1076101.7301 | 6.6077 | OK
9=8-7: Grand Total | 56325600 | 56261579.2 | 56325600 | 0.11379
7: 33 KV EXPORT; 10: KWH | S/S % of Loss
[6 empty] | KAZLA at 33 KV level |  |  | 17342912.2999
[6 empty] | Kazla 33/11 KV Substation |  |  | 38963887.131
9=8-7: Total =; 10: 56306799.4309 | -18800.5691
1: 11 KV SIDE of___KAZLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
KAZLA 11 KV SIDE
16 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK-61009 | 1 | 7767478 | 7832262 | 64784 | 180 | 11661120 |  | 11898323.8721
30 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK-61124 | 1 | 752227.8 | 806735.8 | 54508 | 180 | 9811440 |  | 10105886.5521
24 | 33/11 kV 20/28 MVA T-3 Incoming | 11 |  | DHK-61015 | 1 | 393834.4 | 438680.6 | 44846.2 | 180 | 8072316 |  | 8116425.2908
39 | 33/11 kV 10/14 MVA T-4 Incoming | 11 |  | 8L55984 | 1 | 26726 | 27993.1 | 1267.1 | 4000 | 5068400 |  | 5177885.2877
42 | 33/11 kv 28/35 MVA T-5 Incomer | 11 |  | DHK00112 | 1 | 100858.5 | 104990.3 | 4131.8 | 888.8 | 3672343.84 |  | 3665366.1282
7: 0; 8: 0; 10: Total | 38285619.84 |  | 38963887.131
| KAZLA 11 kV SIDE |  |  |  |  | 0 | 0
17 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 813181.6 | 843800.5 | 30618.9 | 60 |  | 1837134 | 1866699.9643 | Kazla |  |  |  | 11 kV Nayanagor Feeder | 1866699.9643 | 1792344.292 | 74355.6723 | 4.1485 | OK
18 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1853855.1196 | Kazla | 150 |  |  | 11 kV Madrasa Bazar Feeder | 1853855.1196 | 1913492.0332 | -59636.9137 | -3.1167 | OK
19 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2980004.58 | 3027963.362 | Kazla | 245 |  |  | 11 kV Kazla Feeder | 3027963.362 | 3049627.928 | -21664.566 | -0.7104 | OK
20 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963854 | 36963861 | 7 | 1000 | Estimated | 973062.72 | 988722.7304 | Maniknagar | 80 |  |  | 11 kV Sayedabad Feeder | 988722.7304 | 1076339.2687 | -87616.5383 | -8.1402 | OK
21 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 |  | 0 | 0 | Kazla |  |  |  | 11 kV Zenith Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
22 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 112225.6 | 114727 | 2501.4 | 1000 |  | 2501400 | 2541656.3466 | Jurain |  |  |  | 11 kV Paterbagh Feeder | 2541656.3466 | 2207984.2138 | 333672.1328 | 15.1121 | OK
23 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 59876429 | 18851885 | 1 | Estimated | 1702859.76 | 1730264.7783 | Kazla | 140 |  |  | 11 kV Matuail Feeder | 1730264.7783 | 1734102.1551 | -3837.3769 | -0.22129 | OK
25 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 684518.2 | 723552 | 39033.8 | 60 |  | 2342028 | 2379719.4891 | Jurain |  |  |  | 11 kV Kutubkhali Feeder | 2379719.4891 | 2279252.9698 | 100466.5193 | 4.4079 | OK
26 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 602385.9 | 624583.7 | 22197.8 | 60 |  | 1331868 | 1353302.4526 | Kazla |  |  |  | 11 kV Mridhabari Feeder | 1353302.4526 | 1381440.9902 | -28138.5375 | -2.0369 | OK
27 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 986124.4 | 1025255.2 | 39130.8 | 60 |  | 2347848 | 2385633.1534 | Kazla |  |  |  | 11 kV Muslim Nagar Feeder | 2385633.1534 | 2345596.1288 | 40037.0246 | 1.7069 | OK
28 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 |  | 0 | 0 | Kazla |  |  |  | 11 kV Jatrabari Thana Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 212446.1 | 246764.7 | 34318.6 | 60 |  | 2059116 | 2092254.4374 | Swamibag |  |  |  | 11 kV Mirhazirbag Feeder | 2092254.4374 | 2069592.0061 | 22662.4313 | 1.095 | OK
31 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 73285.9 | 113721.9 | 40436 | 60 |  | 2426160 | 2465205.4697 | Jurain |  |  |  | 11 kV Mukti Sharani Feeder | 2465205.4697 | 2452063.3964 | 13142.0733 | 0.53596 | OK
32 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 290452 | 326888.5 | 36436.5 | 60 |  | 2186190 | 2221373.5062 | Shyampur |  |  |  | 11 kV Kadamtali Feeder | 2221373.5062 | 2471771.8805 | -250398.3743 | -10.1303 | OK
33 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 383226.2 | 404227.5 | 21001.3 | 60 |  | 1260078 | 1280357.0984 | Matuail |  |  |  | 11kV Rayerbagh Feeder | 1280357.0984 | 1277473.0974 | 2884.001 | 0.22576 | OK
34 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1945817 | 1980100 | 34283 | 60 |  | 2056980 | 2090084.0617 | Jurain |  |  |  | 11 kV Donia Feeder | 2090084.0617 | 2017361.1702 | 72722.8914 | 3.6049 | OK
35 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 27937314 | 29423230 | 1485916 | 1 |  | 1485916 | 1509829.6282 | Kazla |  |  |  | 11 kV Nimtoli Feeder | 1509829.6282 | 1633862.5979 | -124032.9697 | -7.5914 | OK
36 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 25965046 | 26674761 | 709715 | 1 |  | 709715 | 721136.817 | Kazla |  |  |  | 11 kV Gobindapur Feeder | 721136.817 | 697773.6086 | 23363.2083 | 3.3483 | OK
37 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 3086.1 | 3271.9 | 185.8 | 10000 |  | 1858000 | 1887901.7718 | Kazla |  |  |  | 11 kV Eidgaon (Kabarsthan) Feeder | 1887901.7718 | 1946667.4736 | -58765.7018 | -3.0188 | OK
38 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Samad Nagar Gate (Old) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
40 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 |  | 0 | 0 | Kazla | From 01-07-2023 17:25 No Load (Shifted to Jenith) |  |  | 11 kV Dharmik Para | 0 | 23977.7413 | -23977.7413 | -100 | CHECK
41 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 13448.4 | 14288.8 | 840.4 | 4000 |  | 3361600 | 3415699.9979 | Kazla |  |  |  | 11 kV Sheikhdi Feeder | 3415699.9979 | 3248780.7482 | 166919.2497 | 5.1379 | OK
43 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 1000 |  | 0 | 0 | Kazla |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
44 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 20321.3 | 20864.4 | 543.1 | 1000 |  | 543100 | 551840.3941 | Kazla |  |  |  | 11 kV Jenith Feeder | 551840.3941 | 574043.3834 | -22202.9893 | -3.8678 | OK
45 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 17160.4 | 17718.5 | 558.1 | 2000 |  | 1116200 | 1134163.594 | Kazla |  |  |  | 11 KV Samad Nagor Gate | 1134163.594 | 1293375.6231 | -159212.0291 | -12.3098 | OK
46 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 35605.2 | 36323.7 | 718.5 | 2000 |  | 1437000 | 1460126.3972 | Maniknagar |  |  |  | 11 KV Bibir Bagicha | 1460126.3972 | 1445370.1189 | 14756.2783 | 1.0209 | OK
47 | 33/0.4 kV AT-1 | 0.415 |  | 503043 | 1 | 96204 | 96204 | 0 | 10 |  | 0 | 0 | Kazla |  |  |  | 33/0.4 kV AT-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
48 | 33/0.4 kV AT-2 | 0.415 |  | 503044 | 1 | 93292 | 93994 | 702 | 10 |  | 6000 | 6096.5612 | Kazla |  |  |  | 33/0.4 kV AT-2 | 6096.5612 | 6096.0359 | 0.52523 | 0.0086159 | OK
23 | Auxiliary Transformer | 0.415 |  | 41901920685 | 1 | 2290.62 | 2407.99 | 117.37 | 160 |  |  | 0 | Kazla |  |  |  | Auxiliary Transformer | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 38963887.131 | 38346752.66 | 38963887.131 | 1.6094
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Matuail | at 33 KV level |  | 1280357.0984
[5 empty] | Jurain | at 33 KV level |  | 9476665.367
[5 empty] | Swamibag | at 33 KV level |  | 2092254.4374
[5 empty] | Maniknagar | at 33 KV level |  | 2448849.1277
[5 empty] | Shyampur | at 33 KV level |  | 2221373.5062
[5 empty] | Kazla | at 33 KV level |  | 21444387.5943
[5 empty] | Total = |  |  | 38963887.131 | 0
1: 132 KV SIDE of___SHYAMPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDNG)
| HASNABAD TO SHYAMPUR CKT | 132 |  | 8993532 | 1 | 2227.617 | 2227.617 | 0 | 960000 | 0 | 0
|  | 132 |  |  | 1 | 666.456 | 666.546 | 0.09 | 960000 | 86400 | 0
1 | Tranformer - 1 at Shyampur 230/132 | 132 |  | 38992560 | 1 | 1408.991 | 1441.023 | 32.032 | 1920000 | 0 | 61501440
|  | 132 |  | wp002497 | 1 | 0.245 | 0.245 | 0 | 1920000 | 0 | 0
2 | Tranformer - 2 at Shyampur 230/132 | 132 |  | 38992559 | 1 | 0.216 | 0.216 | 0 | 1920000 | 0 | 0
|  | 132 |  | 38992559 | 1 | 1500.185 | 1532.023 | 31.838 | 1920000 | 0 | 61128960
| Aggrekko 100 MW (Brammhongao) | 132 |  | PN-1711A04601 | 1 | 363.871 | 363.871 | 0 | 960000 | 0 | 0
|  | 132 |  |  | 1 | 5.419 | 5.419 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Exp | 132 |  | 38992544 | 1 | 32.177 | 32.177 | 0 | 960000 | 0 | 0
| Madanganj-Fatullah Imp | 132 |  | 38992544 | 1 | 18.041 | 18.041 | 0 | 960000 | 0 | 0
9=8-7: Total Import/Export | 86400 | 122630400
10: Net Total | 122544000
SHYAMPUR 132 KV SIDE (RECEIVING)
3 | 132 kV New Shyampur-1 (Old Haripur) | 132 | Import | 08993727 | 1 | 9008.629 | 9070.469 | 61.84 | 720000 | 44524800
|  | 132 | Export | 08993727 | 1 | 1.333 | 1.333 | 0 | 720000 |  | 0
4 | 132 kV New Shyampur-2 (Old Hasnabad) | 132 | Import | 08993726 | 1 | 6766.127 | 6822.265 | 56.138 | 720000 | 40419360
|  | 132 | Export | 08993726 | 1 | 118.73 | 118.73 | 0 | 720000 |  | 0
7: 0; 8: 0; 9=8-7: Total Import/Export | 84944160 | 0
7: 0; 8: 0; 9=8-7: Net Total | 84944160
| SHYAMPUR 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
|  | 132 |  |  |  | 0 | 0
|  | 132 |  |  |  | 0 | 0
[6 empty] | 0 | 0
[6 empty] | 0 | 0
7: 0; 8: 0; 10: Total |  | 37716000
| SHYAMPUR 132 KV SIDE |  |  |  |  | 0 | 0
5 | 132 kV 80/120 MVA ( GT-1) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
6 | 132 kV 80/120 MVA ( GT-2) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
7 | 132 kV 80/120 MVA ( GT-3) | 132 | Export | Nill | 1 | 0 | 0 | 0 |  |  | 0
8 | 132 kV 80/120 MVA ( GT-4) | 132 | Export | ABB3902 | 1 | 1883170.2 | 1883170.2 | 0 | 1300 |  | 0
10: Total |  | 47228160
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (SENDNG); 4: 122544000; 6: EXPORT TO OTHER S/S; 9=8-7: 37716000 | 132 KV NET IMPORT |  | 84828000
2: IMPORT-2; 6: 132 KV NET IMPORT; 9=8-7: 84828000 | 33 KV NET IMPORT |  | 84785712
2: IMPORT-3 | LOSS UNITS=>(132 HV-33 LV) |  | 42288
2: IMPORT-4 | LOSS % IN => |  | 0.04985%
| 132 KV TOTAL IMPORT |  | 122544000
1: 33 KV SIDE of___SHYAMPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
3 | 33 kV 80/120 MVA Transformer-1 (GT-1) | 33 | Import | BD001826 | 1 | 3337.1699 | 3379.2839 | 42.114 | 480000 | 20214720
9 | 33 kV 80/120 MVA Transformer-2 (GT-2) | 33 | Import | BD001850 | 1 | 3394.1149 | 3436.324 | 42.2091 | 480000 | 20260368
15 | 33 kV 50/75 MVA Transformer-3 (GT-3) | 33 | Import | BD001835 | 1 | 2881.364 | 2926.9819 | 45.6179 | 480000 | 21896592
21 | 33 kV 50/75 MVA Transformer-4 (GT-4) | 33 | Import | BD001831 | 1 | 3760.7241 | 3807.42 | 46.6959 | 480000 | 22414032
7: 0; 8: 0; 10: Total | 84785712
| SHYAMPUR 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 33 kV 20/28 MVA Transformer-1 (T-1) | 33 | Export | BD001808 | 1 | 2087.2119 | 2115.75 | 28.5381 | 240000 | From Downstream | 6830272 | 6833454.0489 |  | 24429567.8107 | Shyampur 33/11 kv s/s |  | 33 kV 20/28 MVA Transformer-1 (T-1) | 6833454.0489 | 7447912.9078 | -614458.8589 | -8.2501 | OK
10 | 33 kV 20/28 MVA Transformer-2 (T-2) | 33 | Export | BD001834 | 1 | 1894.634 | 1928.017 | 33.383 | 240000 | From Downstream | 6793872 | 6797037.0911 |  |  |  |  | 33 kV 20/28 MVA Transformer-2 (T-2) | 6797037.0911 | 7417093.9357 | -620056.8447 | -8.3598 | OK
16 | 33 kV 20/28 MVA Transformer-3 (T-3) | 33 | Export | BD001846 | 1 | 1398.6889 | 1422.083 | 23.3941 | 240000 |  | 5614584 | 5617199.691 |  |  |  |  | 33 kV 20/28 MVA Transformer-3 (T-3) | 5617199.691 | 5741430.4034 | -124230.7125 | -2.1638 | OK
22 | 33 kV 20/28 MVA Transformer-4 (T-4) | 33 | Export | BD001847 | 1 | 1261.1159 | 1282.697 | 21.5811 | 240000 |  | 5179464 | 5181876.9797 |  |  |  |  | 33 kV 20/28 MVA Transformer-4 (T-4) | 5181876.9797 | 4905763.9703 | 276113.0095 | 5.6283 | OK
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 24418192 | 24429567.8107 |  |  |  |  | 33 KV Feeders | 24429567.8107 | 25512201.2172 | -1082633.4065 | -4.2436 | OK
1 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 715.3204 | 725.5189 | 10.1985 | 240000 |  | 2447640 | 2448780.2928 | Shyampur |  |  |  | 33 kV Rani RRM Feeder | 2448780.2928 | 2460914.9302 | -12134.6373 | -0.49309 | OK
2 | 33 kV Postogola Feeder-1. | 33 | Export | BD001804 | 1 | 1564.541 | 1564.5419 | 0.0009 | 240000 |  | 216 | 216.1006 |  | 216.1006 | Postogola 33/11 kv s/s |  | 33 kV Postogola Feeder-1. | 216.1006 | 240.1478 | -24.0472 | -10.0135 | OK
5 | 33 kV Prime Textile Feeder. | 33 | Export | BD001810 | 1 | 510.6365 | 510.6365 | 0 | 240000 |  | 0 | 0 | Fatullah |  |  |  | 33 kV Prime Textile Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1248.0069 | 1278.1529 | 30.146 | 240000 | From Downstream | 7235040 | 7238410.62 |  | 12665897.97 | Nandalalpur 33/11 kv s/s |  | 33 kV Nondolalpur -1 feeder | 7238410.62 | 7161184.3988 | 77226.2212 | 1.0784 | OK
7 | 33 kV Nondolalpur -2 feeder | 33 | Export | BD001807 | 1 | 1085.453 | 1108.057 | 22.604 | 240000 |  | 5424960 | 5427487.35 |  |  |  |  | 33 kV Nondolalpur -2 feeder | 5427487.35 | 5732112.6675 | -304625.3175 | -5.3144 | OK
8 | 33 kV Postogola Feeder-2. | 33 | Export | BD001830 | 1 | 2131.894 | 2131.894 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV Postogola Feeder-2. | 0 | 480.2957 | -480.2957 | -100 | CHECK
11 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 629.3505 | 637.06 | 7.7095 | 240000 |  | 1850280 | 1851141.9981 | Shyampur |  |  |  | 33 kV Rahima Steel feeder | 1851141.9981 | 2281164.2763 | -430022.2782 | -18.851 | OK
12 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1102.925 | 1143.578 | 40.653 | 240000 |  | 9756720 | 9761265.4061 | Shyampur |  |  |  | 33 kV Salam Steel Feeder | 9761265.4061 | 10754060.1599 | -992794.7537 | -9.2318 | OK
13 | 33 kV Fatullah Feeder-2. | 33 | Export | BD001848 | 1 | 1604.13 | 1604.13 | 0 | 240000 |  | 0 | 0 |  | 1147950.5517 | Fatullah 33/11 kv s/s |  | 33 kV Fatullah Feeder-2. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2510.5759 | 2542.812 | 32.2361 | 240000 |  | 7891397.28 | 7895073.68 |  |  |  |  | 33 kV Shyampur BSCIC-1. | 7895073.68 | 8348902.7538 | -453829.0738 | -5.4358 | OK
17 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 672.5319 | 677.3128 | 4.7809 | 240000 | Prime Textile | 1147416 | 1147950.5517 | Fatullah | 17434019.5614 | Shyampur BSCIC 33/11 kv s/s | Old Dapa | 33 kV Akhter Steel Feeder | 1147950.5517 | 674551.2513 | 473399.3005 | 70.1799 | FAULT
18 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 129.9924 | 135.586 | 5.5936 | 240000 |  | 1342464 | 1343089.4196 | Shyampur |  |  |  | 33 kV Steel Famus feeder | 1343089.4196 | 1442423.9509 | -99334.5313 | -6.8866 | OK
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 |  | 0 | 0 |  | 0 | IG Gate 33/11 kv s/s |  | 33 kV IG Gate Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
20 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1488.4699 | 1511.052 | 22.5821 | 240000 |  | 5419704 | 5422228.9014 | Shyampur |  |  |  | 33 kV Rani Kamal Steel Feeder | 5422228.9014 | 6501978.5941 | -1079749.6927 | -16.6065 | OK
23 | 33 kV Shyampur BSCIC-2. | 33 | Export | BD001827 | 1 | 2423.1679 | 2462.895 | 39.7271 | 240000 |  | 9534504 | 9538945.8814 |  |  |  |  | 33 kV Shyampur BSCIC-2. | 9538945.8814 | 9140747.0102 | 398198.8711 | 4.3563 | OK
24 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2331.0006 | 2365.387 | 34.3864 | 240000 |  | 8252736 | 8256580.7385 | Shyampur |  |  |  | 33 kV Chakda Steel Feeder | 8256580.7385 | 8640663.1605 | -384082.422 | -4.4451 | OK
23 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 341.169 | 343.416 | 2.247 | 2400 |  | 5527.62 | 5527.62 | Fatullah
24 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 87.479 | 95.379 | 7.9 | 2400 |  | 19434 | 19434 | Fatullah
10: Total |  | 60328038.9 | 60356132.5603 |  |  |  |  | 0 | 60356132.5603 | 63160537.7769 | -2804405.2166 | -4.4401 | OK
9=8-7: Grand Total | 84785712 | 84746230.9 | 84785700.371 | 0.046574
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 29083086.7566
[5 empty] | Fatullah | at 33 KV level |  | 1172912.1717
[6 empty] | Export to Other SS |  | 54529701.4427
[5 empty] | Total = |  |  | 84785700.371 | 0
1: 11 KV SIDE of___SHYAMPUR 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 11 KV SIDE
9 | 11 kV 20/28 MVA Transformer-1 | 11 | Import | BD001926 | 1 | 2820.0408 | 2862.73 | 42.6892 | 160000 | 6830272 |  | 6849224.701 |  | 6830272
16 | 11 kV 20/28 MVA Transformer-2 | 11 |  | BD001952 | 1 | 2832.9583 | 2875.42 | 42.4617 | 160000 | 6793872 |  | 6812723.6979
27 | 11 kV20/28 MVA Transformer-3 | 11 |  | BD001927 | 1 | 1962.7445 | 1997.67 | 34.9255 | 160000 | 5588080 |  | 5603585.8553 |  | 1838544
36 | 11 kV 20/28 MVA Transformer-4 | 11 |  | BD001927 | 1 | 1887.3541 | 1919.54 | 32.1859 | 160000 | 5149744 |  | 5164033.5566 |  | 1838544
7: 0; 8: 0; 10: Total | 24361968 |  | 24429567.8107
| SHYAMPUR 11 kV SIDE |  |  |  |  | 0 | 0
5 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur |  | 1 | 579.6764 | 625.64 | 45.9636 | 40000 |  | 1838544 | 1848660.4463 | Shyampur |  |  |  | 11 kV HR (Hajrat_Rahima) Steel Express | 1848660.4463 | 1329002.2614 | 519658.1849 | 39.1014 | OK
6 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 11 kV Road No.-21 Feeder | 11 |  | BD001943 | 1 | 1030.3488 | 1043.7 | 13.3512 | 40000 |  | 534048 | 536986.5578 | Shyampur |  |  |  | 11 kV Road No.-21 Feeder | 536986.5578 | 689153.8135 | -152167.2556 | -22.0803 | OK
8 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1510.017 | 1527.03 | 17.013 | 40000 |  | 680520 | 684264.5087 | Shyampur |  |  |  | 11 kV New Chakda Feeder | 684264.5087 | 768373.9842 | -84109.4755 | -10.9464 | OK
10 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1400.2733 | 1416.53 | 16.2567 | 40000 |  | 650268 | 653846.0494 | Shyampur |  |  |  | 11 kV Burigonga Feeder | 653846.0494 | 678120.977 | -24274.9276 | -3.5797 | OK
11 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1286.4505 | 1313.82 | 27.3695 | 40000 |  | 1094780 | 1100803.9423 | Fatullah |  |  |  | 11 kV Dapa-Pagla Feeder | 1100803.9423 | 1060453.8119 | 40350.1305 | 3.805 | OK
12 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3240.1803 | 3283.24 | 43.0597 | 40000 |  | 1722388 | 1731865.3068 | Shyampur |  |  |  | 11 kV S. R. Steel Feeder. | 1731865.3068 | 2347543.3088 | -615678.0019 | -26.2265 | OK
13 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Rahima Steel Feeder. | 0 | 0 | 0 | #DIV/0! | #DIV/0!
14 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2102.0425 | 2133.5 | 31.4575 | 40000 |  | 1258300 | 1265223.6985 | Shyampur |  |  |  | 11 kV Chand Textile Feeder | 1265223.6985 | 1510257.147 | -245033.4485 | -16.2246 | OK
15 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 484.1231 | 486.4 | 2.2769 | 40000 |  | 91076 | 91577.1387 | Fatullah |  |  |  | 11 kV Kamalpur Feeder | 91577.1387 | 112254.6055 | -20677.4668 | -18.4202 | OK
17 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3076.6439 | 3122.73 | 46.0861 | 40000 |  | 1843444 | 1853587.4081 | Shyampur |  |  |  | 11 kV Alizan Steel Feeder | 1853587.4081 | 1927999.1795 | -74411.7714 | -3.8595 | OK
18 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1921.3681 | 1944.14 | 22.7719 | 40000 |  | 910876 | 915888.0248 | Shyampur |  |  |  | 11 kV Redwan Steel Feeder | 915888.0248 | 1677475.7016 | -761587.6768 | -45.4008 | CHECK
19 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1406.4167 | 1444.14 | 37.7233 | 40000 |  | 1508932 | 1517234.7817 | Shyampur | Wrong Reading by Grid |  |  | 11 kV Kadamtolly Steel Feeder | 1517234.7817 | 1359049.2203 | 158185.5614 | 11.6394 | OK
20 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
21 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 807.729 | 820.21 | 12.481 | 40000 |  | 499240 | 501987.0295 | Shyampur |  |  |  | 11 kV Orient-Al-Islam Feeder | 501987.0295 | 565017.3838 | -63030.3543 | -11.1555 | OK
22 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1294.1832 | 1313.8 | 19.6168 | 40000 |  | 784672 | 788989.597 | Shyampur |  |  |  | 11 kV Delpara Feeder | 788989.597 | 774228.7961 | 14760.8009 | 1.9065 | OK
23 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2914.5187 | 2984.83 | 70.3113 | 40000 |  | 2812452 | 2827927.2998 | Shyampur |  |  |  | 11 kV Wasa Feeder | 2827927.2998 | 2567335.031 | 260592.2687 | 10.1503 | OK
24 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1098.2827 | 1102.63 | 4.3473 | 40000 |  | 173892 | 174848.8273 | Shyampur |  |  |  | 11 kV Al Noor-Femous Steel Feeder | 174848.8273 | 295251.5179 | -120402.6906 | -40.7797 | CHECK
26 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1916.4054 | 1946.25 | 29.8446 | 40000 |  | 1193784 | 1200352.7042 | Shyampur |  |  |  | 11 kV Shyampur Bazar Feeder | 1200352.7042 | 1365805.0805 | -165452.3764 | -12.1139 | OK
28 | 11 kV Spare Feeder | 11 | Shympur |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
29 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1335.0577 | 1349.95 | 14.8923 | 40000 |  | 595692 | 598969.7492 | Shyampur |  |  |  | 11 kV Binimoy Feeder | 598969.7492 | 543740.6288 | 55229.1204 | 10.1573 | OK
30 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1300.6173 | 1323.77 | 23.1527 | 40000 |  | 926108 | 931203.8377 | Shyampur |  |  |  | 11 kV Akbar-Nabi Steel | 931203.8377 | 1080348.9594 | -149145.1217 | -13.8053 | OK
31 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
32 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
33 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
34 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2199.2196 | 2236.38 | 37.1604 | 40000 |  | 1486416 | 1494594.8892 | Shyampur |  |  |  | 11 kV Rasulpur Feeder | 1494594.8892 | 1526560.1151 | -31965.2259 | -2.0939 | OK
35 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 170.7545 | 172.64 | 1.8855 | 40000 |  | 75420 | 75834.9927 | Shyampur |  |  |  | 11 Kv Pioneer Steel Feeder | 75834.9927 | 95891.5675 | -20056.5748 | -20.9159 | OK
37 | 11 kV Spare Feeder | 11 |  |  | 1 | 0 | 0 | 0 | 40000 |  | 0 | 0 | Shyampur |  |  |  | 11 kV Spare Feeder | 0 | 0 | 0 | #DIV/0! | #DIV/0!
38 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1172.4449 | 1189.74 | 17.2951 | 40000 |  | 691804 | 695610.598 | Shyampur |  |  |  | 11 kV Sun Steel Feeder | 695610.598 | 869607.7672 | -173997.1692 | -20.0087 | OK
39 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3633.3532 | 3687.08 | 53.7268 | 40000 |  | 2149072 | 2160897.1026 | Shyampur |  |  |  | 11 kV Taher Steel Feeder | 2160897.1026 | 1905144.5888 | 255752.5138 | 13.4243 | OK
40 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1076.0762 | 1095.43 | 19.3538 | 40000 |  | 774153.6 | 778413.3204 | Shyampur |  |  |  | 11 kV Igloo Feeder | 778413.3204 | 463585.7706 | 314827.5497 | 67.9114 | FAULT
41 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 |  |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
42 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 63432.6 | 63890 | 457.4 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
25 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 |  |  | 1 | 586899 | 594876 | 7977 | 1 |  |  | 0 | Shyampur |  |  |  | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 11/0.4 kV Aux Transformer, T-2 | 0.415 |  | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 |  | 0 | Shyampur |  |  |  | 11/0.4 kV Aux Transformer, T-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Total | 24429567.8107 | 24295881.6 | 24429567.8107 | 0.55024
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Fatullah | at 33 KV level |  | 1192381.081
6: Shyampur; 7: at 33 KV level; 9=8-7: 22687186.7297 | Export to Matuail & Narinda |  | 550000
[5 empty] | Total = |  |  | 23879567.8107 | -550000
1: 33 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SIDE
14 | 33 kV Shyampur BSCIC-1. | 33 | Export | BD001805 | 1.02 | 2510.5759 | 2542.812 | 32.2361 | 240000 | 0 | 7891397.28 | 7895073.68
23 | 33 kV Shyampur BSCIC-2. | 33 |  | BD001827 | 1 | 2423.1679 | 2462.895 | 39.7271 | 240000 | 0 | 9534504 | 9538945.8814
10: Total | 0 | 17425901.28 | 17434019.5614
SHYAMPUR BISIC 33 KV SIDE (RECEIVING)
1 | 33 kV Shyampur Circuit-1 | 33 | Import | DHK61071 | 1 | 887930.8 | 916104.6 | 28173.8 | 270 | 7606926
5 | 33 kV Shyampur Circuit-2 | 33 | Import | DHK61067 | 1 | 676108.4 | 710976.9 | 34868.5 | 270 | 9414495
7: 0; 8: 0; 10: Total | 17021421 | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| SHYAMPUR BISIC 33 KV SIDE |  |  |  |  | 0 | 0
2 | 33 kV 20/28 MVA Transformer-1 | 33 | Export | DHK61068 | 1 | 845345.2 | 887669.7 | 42324.5 | 180 |  | 7618410
3 | 33 kV 20/28 MVA Transformer-2 | 33 | Export | DHK61066 | 1 | 508484 | 560787.9 | 52303.9 | 180 |  | 9414702
10: Total |  | 17033112 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: 33 KV SIDE; 4: 17434019.5614; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 17434019.5614
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 17434019.5614 | 33 KV TX HV SIDE |  | 17033112
2: IMPORT-3 | LOSS UNITS=> |  | 400907.5614
2: IMPORT-4 | LOSS % IN => |  | 2.3%
| TOTAL IMPORT |  | 17434019.5614
1: 11 KV SIDE of___SHYAMPUR BISIC 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR BISIC 11 KV SIDE
10 | 33/11 kV 20/28 MVA T-1 Incoming | 11 |  | DHK61019 | 1.05 | 959640.9 | 987931.5 | 28290.6 | 180 | 5346923.4 |  | 6390191.1924 |  | 0
11 | 33/11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK61018 | 1 | 631758.3 | 683096.1 | 51337.8 | 180 | 9240804 |  | 11043828.369
7: 0; 8: 0; 10: Total | 14587727.4 |  | 17434019.5614
| SHYAMPUR BISIC 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 35723650 | 37882493 | 2158843 | 1 |  | 2158843 | 2142439.5507 | Shyampur |  |  |  | 11 kV Nama shyampur Feeder | 2142439.5507 | 2098065.1104 | 44374.4403 | 2.115 | OK
2 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 20537911 | 21288823 | 750912 | 1 |  | 750912 | 745206.3758 | Jurain |  |  |  | 11 kV Bombay SweetsFeeder | 745206.3758 | 738065.3088 | 7141.067 | 0.96754 | OK
3 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 |  | 0 | 0 | Shyampur |  |  |  | 11 kV H. R Steel | 0 | 0 | 0 | #DIV/0! | #DIV/0!
4 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain |  |  |  | 11 kV Shyampur Incoming (F1) | 0 | 0 | 0 | #DIV/0! | #DIV/0!
5 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 410183.5 | 437001.6 | 26818.1 | 60 |  | 1609086 | 1596859.747 | Jurain |  |  |  | 11 kV Ali Bahar Feeder (F2) | 1596859.747 | 1920766.0882 | -323906.3412 | -16.8634 | OK
6 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 575495.8 | 593952.2 | 18456.4 | 60 |  | 1107384 | 1098969.809 | Jurain |  |  |  | 11 kV Mosjid Road Feeder (F3) | 1098969.809 | 1475476.6819 | -376506.8729 | -25.5176 | OK
7 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 594888.2 | 615565.9 | 20677.7 | 60 |  | 1240662 | 1231235.1282 | Jurain |  |  |  | 11 kV Shyampur O/H Feeder (F4) | 1231235.1282 | 1429313.0963 | -198077.9681 | -13.8583 | OK
8 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 337050 | 351956.3 | 14906.3 | 60 |  | 894378 | 887582.2839 | Shyampur |  |  |  | 11 kV Road No-11 Feeder (F5) | 887582.2839 | 954363.7317 | -66781.4478 | -6.9975 | OK
9 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511525.1 | 518004.2 | 6479.1 | 60 |  | 388746 | 385792.207 | Jurain |  |  |  | 11 kV Hanif Express Feeder (F6) | 385792.207 | 8184.8678 | 377607.3393 | 4613.4812 | FAULT
12 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 824930.4 | 871854.9 | 46924.5 | 60 |  | 2815470 | 2794077.3284 | Jurain |  |  |  | 11 kV Zia Sharani Road Feeder(F7) | 2794077.3284 | 2700808.4363 | 93268.892 | 3.4534 | OK
13 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 236095.8 | 256885.3 | 20789.5 | 60 |  | 1247370 | 1237892.1591 | Shyampur |  |  |  | 11 kV Road-12 & 13 Feeder(F8) | 1237892.1591 | 1229098.1908 | 8793.9683 | 0.71548 | OK
14 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 443790.5 | 455733.9 | 11943.4 | 60 |  | 716604 | 711159.0569 | Jurain |  |  |  | 11 kV Rahman and Baset (F9). | 711159.0569 | 480060.5409 | 231098.516 | 48.1395 | FAULT
15 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 482640.9 | 526918.2 | 44277.3 | 60 |  | 2656638 | 2636452.1751 | Jurain |  |  |  | 11 kV Sabujbagh Feeder (F10) | 2636452.1751 | 2526376.4464 | 110075.7287 | 4.3571 | OK
16 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 845435.7 | 856542.9 | 11107.2 | 60 |  | 666432 | 661368.2767 | Jurain |  |  |  | 11 kV Road No-7 & 8 Feeder(F11) | 661368.2767 | 689554.7346 | -28186.4579 | -4.0876 | OK
17 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 938845.6 | 960702.2 | 21856.6 | 60 |  | 1311396 | 1301431.6729 | Shyampur |  |  |  | 11 kV Hossain Express Feeder(F12) | 1301431.6729 | 1235612.3209 | 65819.352 | 5.3269 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB7380 | 1 | 604904 | 608485 | 3581 | 1 |  | 3581 | 3553.7906 | Shyampur |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 3553.7906 | 3904.2091 | -350.4185 | -8.9754 | OK
10: Grand Total | 17434019.5614 | 17567502 | 17434019.5614 | -0.75983
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5572899.4572
[5 empty] | Jurain | at 33 KV level |  | 11861120.1042
[5 empty] | Total = |  |  | 17434019.5614 | 0
1: 33 KV SIDE of___NANDALALPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
SHYAMPUR 33 KV SIDE
6 | 33 kV Nondolalpur -1 feeder | 33 | Export | BD001801 | 1 | 1248.0069 | 1278.1529 | 30.146 | 240000 | From Downstream | 7235040 | 7238410.62
7 | 33 kV Nondolalpur -2 feeder | 33 |  | BD001807 | 1 | 1085.453 | 1108.057 | 22.604 | 240000 | 0 | 5424960 | 5427487.35
10: Total | 0 | 12660000 | 12665897.97
NANDALALPUR 33 KV SIDE (RECEIVING)
3 | 33 kV Incoming Ckt-1 (At Nandalalpur) | 33 | Import | 00000084 | 1 | 292336064 | 306721216 | 14385152 | 1 | 14385152
6 | 33 kV Incoming Ckt-2 (At Nandalalpur) | 33 | Import | 00000070 | 1 | 275297536 | 286460160 | 11162624 | 1 | 11162624
8: 0; 10: Total | 25547776 | 0 | 0
| NANDALALPUR 33 KV SIDE (EXPORT TO OTHER S/S) | [5 empty] | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
8: 0; 10: Total |  | 0
0
| NANDALALPUR 33 KV SIDE | [5 empty] | 0
4 | 33 kV, 28/35 MVA T-1 | 33 | Export | 00000086 | 1 | 292542016 | 306919264 | 14377248 | 1 |  | 14377248
5 | 33 kV, 28/35 MVA T-2 | 33 | Export | 00000083 | 1 | 274750112 | 285906784 | 11156672 | 1 |  | 11156672
10: Total |  | 25533920 | 0
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: SHYAMPUR 33 KV SIDE; 4: 12665897.97; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 12665897.97
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 12665897.97 | 33 KV TX HV SIDE |  | 25533920
2: IMPORT-3 | LOSS UNITS=> |  | -12868022.03
2: IMPORT-4 | LOSS % IN => |  | -101.6%
| TOTAL IMPORT |  | 12665897.97
1: 11 KV SIDE of___NANDALALPUR 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
NANDALALPUR 11 KV SIDE
16 | 11 kV, 28/35 MVA T-1 Incoming. | 11 |  | 00000036 | 1 | 297872160 | 305067744 | 7195584 | 1 | 7195584 |  | 7233455.706 |  | 0
17 | 11 kV, 28/35 MVA T-2 Incoming | 11 |  | 00000033 | 1 | 279259936 | 284663936 | 5404000 | 1 | 5404000 |  | 5432442.2639
7: 0; 8: 0; 10: Total | 12599584 |  | 12665897.97
2: NANDALALPUR 11 KV SIDE; 7: 0; 8: 0 | [5 empty] | 80
8 | 11 kV Spare | 11 |  | 00000090 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  | 40 |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 11 kV Khaza Moinuddin | 11 |  | 00000026 | 1 | 4686068 | 5408547 | 722479 | 1 |  | 722479 | 727695.4191 | Fatullah |  | 40 |  | 11 kV Khaza Moinuddin | 727695.4191 | 676115.2751 | 51580.144 | 7.6289 | OK
10 | 11 kV Chitashal | 11 |  | 00000027 | 1 | 32447880 | 33243638 | 795758 | 1 |  | 795758 | 801503.5058 | Shyampur |  | 13.3333 |  | 11 kV Chitashal | 801503.5058 | 725908.576 | 75594.9297 | 10.4138 | OK
11 | 11 kV Local Feeder | 11 |  | 00000157 | 1.5 | 18223956 | 18439474 | 215518 | 1 | Estimated | 668980.62 | 673810.7719 | Shyampur | 55 | 53.3333 |  | 11 kV Local Feeder | 673810.7719 | 652026.96 | 21783.8118 | 3.3409 | OK
12 | 11 kV Rasel Germants | 11 |  | 00000124 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 | Fatullah |  |  |  | 11 kV Rasel Germants | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 11 kV Matuail Medical (Adorsho nagar) | 11 |  | 00000121 | 1 | 70737224 | 73062544 | 2325320 | 1 |  | 2325320 | 2342109.1991 | Matuail |  |  |  | 11 kV Matuail Medical (Adorsho nagar) | 2342109.1991 | 2438091.1118 | -95981.9128 | -3.9368 | OK
14 | 11 kV Nandalalpur | 11 |  | 00000010 | 1 | 82993360 | 83856192 | 862832 | 1 |  | 862832 | 869061.7913 | Fatullah |  |  |  | 11 kV Nandalalpur | 869061.7913 | 928548.3765 | -59486.5853 | -6.4064 | OK
15 | 11 kV Sharif Bagh | 11 |  | 00000132 | 1 | 70183192 | 71968184 | 1784992 | 1 |  | 1784992 | 1797879.9406 | Shyampur |  |  |  | 11 kV Sharif Bagh | 1797879.9406 | 1716982.5939 | 80897.3467 | 4.7116 | OK
18 | 11 kV Spare | 11 |  | 00000139 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
19 | 11 KV Nayamati | 11 |  | 00000158 | 1 | 64037524 | 65089840 | 1052316 | 1 |  | 1052316 | 1059913.8974 | Fatullah |  |  |  | 11 KV Nayamati | 1059913.8974 | 1145403.0364 | -85489.139 | -7.4637 | OK
20 | 11 kV Pulpar | 11 |  | 00000160 | 1 | 6979983 | 7628741 | 648758 | 1 |  | 648758 | 653442.1412 | Fatullah |  |  |  | 11 kV Pulpar | 653442.1412 | 808373.695 | -154931.5538 | -19.1658 | OK
21 | 11 kV Shahi Bazar | 11 |  | 00000170 | 1 | 40057984 | 40882420 | 824436 | 1 |  | 824436 | 830388.5657 | Shyampur |  |  |  | 11 kV Shahi Bazar | 830388.5657 | 784445.919 | 45942.6467 | 5.8567 | OK
22 | 11 kV Pagla Bazar | 11 |  | 00000060 | 1 | 49521320 | 50196196 | 674876 | 1 |  | 674876 | 679748.7175 | Fatullah |  |  |  | 11 kV Pagla Bazar | 679748.7175 | 834561.5067 | -154812.7892 | -18.5502 | OK
23 | 11 kV Delpara bazar | 11 |  | 00000063 | 1 | 77632408 | 79142768 | 1510360 | 1 |  | 1510360 | 1521265.0516 | Shyampur |  |  |  | 11 kV Delpara bazar | 1521265.0516 | 1508132.7308 | 13132.3208 | 0.87077 | OK
24 | 11 kV Bhuighor (Board mill) | 11 |  | 00000146 | 1 | 43051416 | 43749012 | 697596 | 1 |  | 697596 | 702632.7597 | Matuail |  |  |  | 11 kV Bhuighor (Board mill) | 702632.7597 | 668462.9794 | 34169.7804 | 5.1117 | OK
25 | 11 kV Spare | 11 |  | 00000059 | 1 | 0 | 0 | 0 | 1 |  | 0 | 0 |  |  |  |  | 11 kV Spare | 0 | 0 | 0 | #DIV/0! | #DIV/0!
26 | 33/0.415 kV, 200 kVA AT-1 | 11 |  | 7803 | 1 | 2371 | 2435 | 64 | 100 |  | 6400 | 6446.2091 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-1 | 6446.2091 | 6244.3055 | 201.9035 | 3.2334 | OK
27 | 33/0.415 kV, 200 kVA AT-2 | 11 |  | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur |  |  |  | 33/0.415 kV, 200 kVA AT-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10: Grand Total | 12665897.97 | 12575103.62 | 12665897.97 | 0.72202
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Shyampur | at 33 KV level |  | 5631294.0447
[5 empty] | Fatullah | at 33 KV level |  | 3989861.9665
[5 empty] | Matuail | at 33 KV level |  | 3044741.9588
[5 empty] | Total = |  |  | 12665897.97 | 0
1: 132 KV SIDE of___POSTOGOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
132 KV SIDE (SENDING)
1 | Hasnabad to Postogola-1 | 132 | Import | 4262 7826 | 1 | 260.441 | 289.542 | 29.101 | 960000 | 0 | 27936960
6: 1; 7: 0; 8: 0; 9=8-7: 0; 10: 960000 | 0 | 0
| Hasnabad to Postogola-2 | 132 |  | 4262 7815 | 1 | 125.28 | 133.648 | 8.368 | 960000 | 0 | 8033280
2 |  |  |  |  | 1 | 0 | 0 | 0 | 960000 | 0 | 0
9=8-7: Total Import/Export | 0 | 35970240
10: Net Total | 35970240
POSTOGOLA 132 KV SIDE (RECEIVING)
1 | 132kV Hasnabad Circuit-1 | 132 | Main | 41808902823 | 1 | 208.22 | 231.42 | 23.2 | 1200000 | 27840000
|  | 132 | Backup | 41808904269 | 1 | 208.22 | 231.42 | 23.2 | 1200000 | 27840000
4 | 132kV Hasnabad Circuit-2 | 132 | Imp/Main | 41808902845 | 1 | 100.14 | 106.82 | 6.68 | 1200000 | 8016000
|  | 132 | Imp/Backup | 41808904256 | 1 | 100.14 | 106.82 | 6.68 | 1200000 | 8016000
7: 0; 8: 0; 9=8-7: Total Import/Export | 35856000 | 0
7: 0; 8: 0; 9=8-7: Net Total | 35856000
| POSTOGOLA 132 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 132; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 132; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
| POSTOGOLA 132 KV SIDE |  |  |  |  | 0 | 0
2 | 132/33 kV 80/120 MVA GT-1 (HV) | 132 | Exp/Main | 41808902871 | 1 | 219.39 | 242.57 | 23.18 | 1200000 |  | 27816000
|  | 132 | Exp/Backup | 41808904257 | 1 | 219.39 | 242.57 | 23.18 | 1200000 |  | 27816000
5 | 132/33 kV 80/120 MVA GT-2 (HV) | 132 | Exp/Main | 41808902846 | 1 | 88.86 | 95.54 | 6.68 | 1200000 |  | 8016000
|  | 132 | Exp/Backup | 41808904243 | 1 | 88.86 | 95.54 | 6.68 | 1200000 |  | 8016000
10: Total |  | 35832000
2: 132 KV IMPORT; 4: KWH; 6: 132 KV NET IMPORT; 9=8-7: KWH | TRANSMISSION LOSS |  | KWH
2: 132 KV SIDE (SENDING); 4: 35970240; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 132 KV NET IMPORT |  | 35970240
6: 132 KV NET IMPORT; 9=8-7: 35970240 | 33 KV NET IMPORT |  | 35704800
[10 empty] | LOSS UNITS=>(132 HV-33 LV) |  | 265440
[10 empty] | LOSS % IN => |  | 0.7379%
| 132 KV TOTAL IMPORT |  | 35970240
1: 33 KV SIDE of___POSTOGOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
| POSTOGOLA 33 KV SIDE | [7 empty] | Total
11 | 132/33 kV 80/120 MVA GT-1 Incoming (LV) | 33 | Main | 41808902807 | 1 | 364.32 | 402.85 | 38.53 | 720000 | 27741600
|  | 33 | Backup | 41808904286 | 1 | 364.32 | 402.85 | 38.53 | 720000 | 27741600
12 | 132/33 kV 80/120 MVA GT-2 Incoming (LV) | 33 | Main | 41808902869 | 1 | 147.08 | 158.14 | 11.06 | 720000 | 7963200
|  | 33 | Backup | 41808904268 | 1 | 147.08 | 158.14 | 11.06 | 720000 | 7963200
7: 0; 8: 0; 10: Total | 35704800 |  | 0
| POSTOGOLA 33 kV SIDE |  |  |  |  | 0 | 0
2: 33/11 KV Transforfers; 4: EXPORT; 7: 0; 8: 0 | [7 empty] | 33/11 KV Transforfers | 0 | 0 | 0 | #DIV/0! | #DIV/0!
10 | 33 kV 28/35 MVA Transformer-1 | 33 | Main | 41812909528 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  | 0 | Postogola 33/11 kv ss |  | 33 kV 28/35 MVA Transformer-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904284 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
13 | 33 kV 28/35 MVA Transformer-2 | 33 | Main | 41808902809 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 33 kV 28/35 MVA Transformer-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904275 | 1 | 0.02 | 0.02 | 0 | 240000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2: 33 KV Feeders; 7: 0; 8: 0; 10: Total |  | 0 | 0 |  |  |  |  | 33 KV Feeders | 0 | 0 | 0 | #DIV/0! | #DIV/0!
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 363.42 | 391.16 | 27.74 | 360000 |  | 9986400 | 9983380.2238 |  | 17944172.2407 | IG Gate 33/11 kv ss |  | 33 kV IG Gate Ckt-2 | 9983380.2238 | 9957837.8681 | 25542.3557 | 0.25651 | OK
|  | 33 | Backup | 41808904225 | 1 | 363.42 | 391.16 | 27.74 | 360000 |  | 9986400 | 9983380.2238 |  |  |  |  | 0 | 9983380.2238 | 9957837.8681 | 25542.3557 | 0.25651 | OK
8 | 33 kV Spare Feeder 2 | 33 | Main | 41808902814 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904226 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
9 | 33kV Postogola circuit-1 | 33 | Main | 41808902810 | 1 | 365.86 | 415.21 | 49.35 | 360000 |  | 17766000 | 17760627.7593 |  |  |  |  | 33kV Postogola circuit-1 | 17760627.7593 | 18156505.6792 | -395877.9199 | -2.1804 | OK
|  | 33 | Backup | 41808904252 | 1 | 365.86 | 415.21 | 49.35 | 360000 |  | 17766000 | 17760627.7593 |  |  |  |  | 0 | 17760627.7593 | 18156505.6792 | -395877.9199 | -2.1804 | OK
14 | 31 kV Spare Feeder 4 | 33 | Main | 41808902750 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 31 kV Spare Feeder 4 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904289 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 32 kV Spare Feeder 5 | 33 | Main | 41808902831 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 32 kV Spare Feeder 5 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41808904265 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
16 | 33 kV Spare Feeder 7 | 33 | Main | 41812909525 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 33 kV Spare Feeder 7 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  | 33 | Backup | 41812909577 | 1 | 0.01 | 0.01 | 0 | 360000 |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 293.67 | 315.79 | 22.12 | 360000 |  | 7963200 | 7960792.0169 |  |  |  |  | 33 kV IG Gate Ckt-1 | 7960792.0169 | 7928856.4527 | 31935.5642 | 0.40278 | OK
|  | 33 | Backup | 41812909573 | 1 | 293.67 | 315.79 | 22.12 | 360000 |  | 7963200 | 7960792.0169 |  |  |  |  | 0 | 7960792.0169 | 7928856.4527 | 31935.5642 | 0.40278 | OK
10: Total |  | 35715600 | 35704800 |  |  |  |  | 0 | 35704800 | 36043200 | -338400 | -0.93887 | OK
9=8-7: Grand Total | 35704800 | 35715600 | 35704800 | -0.030239
1: 11 KV SIDE of___ POSTOGOLA 132/33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
33 KV SENDING SIDE
1 | 33 kV Postogola Circuit-1 at Postogola | 33 | Import | BD001804 | 1 | 365.86 | 415.21 | 49.35 | 360000 | 17766000 |  | 17760627.7593
2 | 33 kV Postogola Circuit-2 at Shyampur | 33 | Import | BD001830 | 1 | 2131.894 | 2131.894 | 0 | 240000 | 0 |  | 0
7: 0; 8: 0; 10: Total | 17766000 |  | 17760627.7593
| POSTOGOLA 33 KV SIDE (RECEIVING) |  |  |  |  | 0 | 0
1 | 32 kV Postogola Circuit-1 (U/G) (At Postogola) | 33 | Export | DHK60864 | 1 | 1016684.5 | 1016684.5 | 0 | 270 | 0
5 | 33 kV Shyampur Circuit-1 (U/G) (At Postogola) | 33 | Import | DHK60865 | 1 | 101410 | 101410 | 0 | 270 | 0
| 33 kV Shyampur Circuit-2 (U/G) (At Postogola) |  |  | DHK60863 | 1 | 309310.3 | 309310.3 | 0 | 270 | 0
7: 0; 8: 0; 10: Total | 0
| POSTOGOLA 33 KV SIDE |  |  |  |  | 0 | 0
3 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK61027 | 1 | 200581.5 | 244625.8 | 44044.3 | 180 |  | 7927974 |  |  | #DIV/0!
4 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60870 | 1 | 616186 | 671327.3 | 55141.3 | 180 |  | 9925434
7: 0; 8: 0; 10: Total |  | 17853408
| POSTOGOLA 11 KV SIDE |  |  |  |  | 0 | 0
8 | 11 kV 20/28 MVA T-1 Incoming. | 11 |  | DHK61005 | 1.165 | 799441.5 | 837889.7 | 38448.2 | 180 | 8062587.54 |  | 8000189.421 |  | 35706816
9 | 11 kV 20/28 MVA T-2 Incoming | 11 |  | DHK60861 | 1.165 | 842541.7 | 889449.5 | 46907.8 | 180 | 9836565.66 |  | 9760438.3383
7: 0; 8: 0; 10: Total | 17899153.2 |  | 17760627.7593
| POSTOGOLA 11 kV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 61037936 | 62369777 | 1331841 | 1 |  | 1331841 | 1335055.4691 | Postogola |  |  |  | 11 kV Station Road Feeder | 1335055.4691 | 1307497.2614 | 27558.2077 | 2.1077 | OK
2 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 8339686 | 9710567 | 1370881 | 1 |  | 1370881 | 1374189.6942 | Jurain |  |  |  | 11 kV Samon & Sons Feeder. | 1374189.6942 | 1360936.1962 | 13253.498 | 0.97385 | OK
3 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 23596442 | 24070248 | 473806 | 1 |  | 473806 | 474949.556 | Jurain |  |  |  | 11 kV Alam Bagh Feeder. | 474949.556 | 542387.1952 | -67437.6392 | -12.4335 | OK
4 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 72786262 | 74369662 | 1583400 | 1 |  | 1583400 | 1587221.6201 | Postogola |  |  |  | 11 kV Majar O/H Feeder | 1587221.6201 | 1546887.4107 | 40334.2094 | 2.6074 | OK
5 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 418110.9 | 428700.2 | 10589.3 | 60 |  | 635358 | 636891.4703 | Postogola |  |  |  | 11 kV Cyca Feeder | 636891.4703 | 664686.4068 | -27794.9365 | -4.1817 | OK
6 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 845528 | 866598.9 | 21070.9 | 60 |  | 1264254 | 1267305.3443 | Postogola |  |  |  | 11 kV Housing O/H Feeder. | 1267305.3443 | 1258808.5211 | 8496.8232 | 0.67499 | OK
7 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 727154.9 | 747895 | 20740.1 | 60 |  | 1244406 | 1247409.4401 | Postogola |  |  |  | 11 kV Munshi Bari | 1247409.4401 | 1227619.0196 | 19790.4205 | 1.6121 | OK
8 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 517862.7 | 520016 | 2153.3 | 60 |  | 129198 | 129509.8262 | Postogola |  |  |  | 11 kV Cantonment Feeder | 129509.8262 | 124992.5587 | 4517.2675 | 3.614 | OK
9 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 819569.4 | 837075.6 | 17506.2 | 60 |  | 1050372 | 1052907.1287 | Postogola |  |  |  | 11 kV DIT Feeder. | 1052907.1287 | 1323292.4846 | -270385.3559 | -20.4328 | OK
10 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 283639 | 324272.2 | 40633.2 | 60 |  | 2437992 | 2443876.2234 | Jurain |  |  |  | 11 kV Jurain WASA Road Feeder | 2443876.2234 | 2429557.5202 | 14318.7032 | 0.58935 | OK
11 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 36547113 | 38603647 | 2056534 | 1 |  | 2056534 | 2061497.5542 | Jurain |  |  |  | 11 kV Khorshed Ali O/H Feeder. | 2061497.5542 | 2071894.6482 | -10397.0939 | -0.50182 | OK
12 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 5929.5 | 8284 | 2354.5 | 1000 |  | 2354500 | 2360182.711 | Jurain |  |  |  | 11 kV Murad pur Feeder. | 2360182.711 | 2388027.6504 | -27844.9394 | -1.166 | OK
13 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 54442479 | 56071015 | 1628536 | 1 |  | 1628536 | 1632466.5583 | Postogola |  |  |  | 11 kV Habib Oil Feeder. | 1632466.5583 | 1639249.0712 | -6782.5129 | -0.41376 | OK
14 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52971025 | 53216071 | 245046 | 1 |  | 245046 | 245637.4316 | Postogola |  |  |  | 11 kV Rajabari Feeder. | 245637.4316 | 262708.1006 | -17070.669 | -6.498 | OK
15 | 11/0.415 kV, 200 kVA AT-1+2 | 11 |  | ELIB67385 | 1 | 314.92 | 368.64 | 53.72 | 80 |  | 4297.6 | 4307.9725 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 4307.9725 | 5751.9551 | -1443.9826 | -25.1042 | OK
10: Total | 17853408 | 17810421.6 | 17853408 | 0.24136
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Postogola | at 33 KV level |  | 9138712.2612
[5 empty] | Jurain | at 33 KV level |  | 8714695.7388
[5 empty] | Total = |  |  | 17853408 | 0
1: 33 KV SIDE of___IG GATE GIS 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
Shyampur 33 KV SIDE
19 | 33 kV IG Gate Feeder. | 33 | Export | BD001802 | 1 | 1544.89 | 1544.89 | 0 | 240000 | 0 | 0 | 0
2: Postogola 33 KV SIDE; 10: Total | 0 | 0 | 0
7 | 33 kV IG Gate Ckt-2 | 33 | Main | 41808902815 | 1 | 363.42 | 391.16 | 27.74 | 360000 | 0 | 9986400 | 9983380.2238
17 | 33 kV IG Gate Ckt-1 | 33 | Main | 41812909470 | 1 | 293.67 | 315.79 | 22.12 | 360000 | 0 | 7963200 | 7960792.0169
10: Total | 0 | 17949600 | 17944172.2407
IG GATE 33 KV SIDE (RECEIVING)
3 | 33 kV Postogola Incoming Feeder-1 | 33 | Import | DHK60973 | 1 | 249925.3 | 264626 | 14700.7 | 540 | 7938378
6 | 33 kV Postogola Incoming Feeder-2 | 33 | Import | DHK60966 | 1 | 425158.5 | 443595.2 | 18436.7 | 540 | 9955818
7: 0; 8: 0; 10: Total | 17894196 | 0 | 0
| IG GATE 33 KV SIDE (EXPORT TO OTHER S/S) |  |  |  |  | 0 | 0
2: Feeder No.1; 3: 33; 4: EXPORT; 7: 0; 8: 0 |  | 0
2: Feeder No.2; 3: 33; 7: 0; 8: 0 |  | 0
7: 0; 8: 0; 10: Total |  | 0
[6 empty] | 0 | 0
| IG GATE 33 KV SIDE |  |  |  |  | 0 | 0
4 | 33 kV, 20/28 MVA T-1 (HV Side) | 33 | Export | DHK60893 | 1 | 714538.2 | 758595.6 | 44057.4 | 180 |  | 7930332
5 | 33 kV, 20/28 MVA T-2 (HV Side) | 33 | Export | DHK60975 | 1 | 309221.7 | 364510.9 | 55289.2 | 180 |  | 9952056
10: Total |  | 17882388
2: 33 KV IMPORT; 4: KWH; 6: 33 KV NET IMPORT; 9=8-7: KWH | BUS LOSS |  | KWH
2: Shyampur 33 KV SIDE; 4: 17944172.2407; 6: EXPORT TO OTHER S/S; 9=8-7: 0 | 33 KV NET IMPORT |  | 17944172.2407
2: IMPORT-2; 6: 33 KV NET IMPORT; 9=8-7: 17944172.2407 | 33 KV TX HV SIDE |  | 17882388
2: IMPORT-3 | LOSS UNITS=> |  | 61784.2407
2: IMPORT-4 | LOSS % IN => |  | 0.3443%
| TOTAL IMPORT |  | 17944172.2407
1: 11 KV SIDE of___IG GATE GIS 33/11 KV S/S |  |  |  |  | Month July-2023 |  |  | Name of Feeders. | Month July-2023 | Month June-2023 | Diffferance | % of Increased/ Decreased | COMENTS
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
3: Possition; 5: Number; 7: Reading at 00.00hr 01.07.2023; 8: Reading at 00.00hr 01.08.2023; 9=8-7: Difference | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS |  |  |  |  | 15283200 | 15283200 | 0 | 0 | OK
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9=8-7 | 10 | 11=6*9*10 | 12=6*9*10 | 13 | 14 | 15
IG GATE 11 KV SIDE
8 | 11 kV, 20/28 MVA T-1 Incoming. | 11 |  | DHK68139 | 1 | 3655.67 | 3699.05 | 43.38 | 180000 | 7808400 |  | 8113593.8274 |  | 0
9 | 11 kV, 20/28 MVA T-2 Incoming | 11 |  | DHK68137 | 1 | 4268.47 | 4321.03 | 52.56 | 180000 | 9460800 |  | 9830578.4133
7: 0; 8: 0; 10: Total | 17269200 |  | 17944172.2407
| IG GATE 11 KV SIDE |  |  |  |  | 0 | 0
1 | 11 kV Feeder-1 | 11 |  | DHK60892 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-1 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
2 | 11 kV Feeder-2 | 11 |  | DHK60968 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-2 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
3 | 11 kV Dholaikal RMU | 11 |  | DHK60970 | 1 | 190281.3 | 223582.9 | 33301.6 | 60 |  | 1998096 | 2013206.2605 | Banglabazar |  |  |  | 11 kV Dholaikal RMU | 2013206.2605 | 1942348.072 | 70858.1885 | 3.6481 | OK
4 | 11 kV Alom Gonj | 11 |  | DHK60894 | 1 | 469945.6 | 479815.2 | 9869.6 | 60 |  | 592176 | 596654.2301 | Postogola |  |  |  | 11 kV Alom Gonj | 596654.2301 | 589855.3321 | 6798.898 | 1.1526 | OK
5 | 11 kV Dhalka Nagar Feeder (F-5) | 11 |  | DHK60895 | 1 | 505725.6 | 536337.9 | 30612.3 | 60 |  | 1836738 | 1850628.0181 | Postogola |  |  |  | 11 kV Dhalka Nagar Feeder (F-5) | 1850628.0181 | 1792355.2732 | 58272.7449 | 3.2512 | OK
6 | 11 kV Farashgonj Feeder (F-6) | 11 |  | DHK68133 | 1 | 3559.31 | 3589.15 | 29.84 | 60000 |  | 1790400 | 1803939.5949 | Banglabazar |  |  |  | 11 kV Farashgonj Feeder (F-6) | 1803939.5949 | 1748762.5817 | 55177.0132 | 3.1552 | OK
7 | 11 kV Doyaganj | 11 |  | DHK68134 | 1 | 2352.51 | 2380.418 | 27.908 | 60000 | 2414.18 | 1674480 | 1687142.9696 | Swamibag | Reading Error |  |  | 11 kV Doyaganj | 1687142.9696 | 1819772.2117 | -132629.242 | -7.2882 | OK
10 | 11 kV Faridabad | 11 |  | DHK68140 | 1 | 751.51 | 772.95 | 21.44 | 60000 |  | 1286400 | 1296128.1808 | Postogola |  |  |  | 11 kV Faridabad | 1296128.1808 | 1292615.9757 | 3512.205 | 0.27171 | OK
11 | 11 kV Gandaria | 11 |  | DHK60969 | 1 | 336244.2 | 372411.9 | 36167.7 | 60 |  | 2170062 | 2186472.7241 | Postogola |  |  |  | 11 kV Gandaria | 2186472.7241 | 2176408.4497 | 10064.2744 | 0.46243 | OK
12 | 11 kV Walter Road | 11 |  | DHK68136 | 1 | 950.44 | 973.45 | 23.01 | 60000 |  | 1380600 | 1391040.5522 | Banglabazar |  |  |  | 11 kV Walter Road | 1391040.5522 | 1437042.3417 | -46001.7895 | -3.2011 | OK
13 | 11 kV Murgitola Feeder (F-11) | 11 |  | DHK68138 | 1 | 3852.58 | 3890.75 | 38.17 | 60000 |  | 2290200 | 2307519.2472 | Swamibag |  |  |  | 11 kV Murgitola Feeder (F-11) | 2307519.2472 | 2337901.7997 | -30382.5525 | -1.2996 | OK
14 | 11 kV Feeder-12 | 11 |  | DHK60900 | 1 | 0 | 0 | 0 | 60 |  | 0 | 0 |  |  |  |  | 11 kV Feeder-12 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
15 | 11 kV Begumgonj Feeder (F-13) | 11 |  | DHK60899 | 1 | 638057.1 | 667472.2 | 29415.1 | 60 |  | 1764906 | 1778252.8009 | Swamibag |  |  |  | 11 kV Begumgonj Feeder (F-13) | 1778252.8009 | 1741101.9665 | 37150.8343 | 2.1338 | OK
16 | 11 kV Lohar Pool Feeder (F-14) | 11 |  | DHK60967 | 1 | 148948.3 | 166011.3 | 17063 | 60 |  | 1023780 | 1031522.1618 | Postogola |  |  |  | 11 kV Lohar Pool Feeder (F-14) | 1031522.1618 | 1006862.3928 | 24659.7689 | 2.4492 | OK
18 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 |  | ELIB2774 | 1 | 277674 | 279327 | 1653 | 1 |  | 1653 | 1665.5005 | Postogola |  |  |  | 11/0.415 kV, 200 kVA AT-1+2 | 1665.5005 | 1667.9239 | -2.4234 | -0.14529 | OK
10: Grand Total | 17944172.2407 | 17809491 | 17944172.2407 | 0.75623
[5 empty] | NOCS Wise 11 KV EXPORT |  |  | KWH
[5 empty] | Swamibag | at 33 KV level |  | 5772915.0177
[5 empty] | Banglabazar | at 33 KV level |  | 5208186.4076
[5 empty] | Postogola | at 33 KV level |  | 6963070.8154
[5 empty] | Total = |  |  | 17944172.2407 | 0
Note on I387: No Reading Due to PT Out
Note on K387: Reading From Higher Side
Note on I644: No Reading due to PT Open
Note on L644: Energy From Bangshal SS End
Note on L649: Energy From Bangshal SS End

## Sheet3 (hidden)
SL | NORTH-1 | NORTH-2 | SOUTH-1 | SOUTH-2
1 | DHANMONDI 132/33 KV S/S | MOGBAZAR 132/33 KV S/S | SIDDHIRGANJ 132/33/11KV S/S | MANIKNAGAR 132/33/11KV S/S
2 | DHANMONDI 33/11 KV S/S | MOGBAZAR LOCAL 33/11KV | SIDDHIRGANJ 33/11KV S/S | MANIKNAGAR 33/11KV S/S
3 | KAWRANBAZAR 33/11 KV S/S | MOGBAZAR T&T 33/11KV S/S | DEMRA 33/11KV S/S | MOTIJHEEL OLD 33/11 KV
4 | NEW RAMNA 33/11 KV S/S | ULLON 132/33 KV GIS S/S | SARULIA 33/11KV S/S | MOTIJHEEL 132/33 KV SS
5 | KAKRAIL 33/11 KV S/S | ULLON LOCAL 33/11 KV S/S | KHANPUR 33/11KV S/S | MOTIJHEEL 33/11 KV SS (NEW)
6 | BSMMU HOSPITAL 33/11 KV S/S | MADARTEK 132/33 KV S/S | MATUAIL 132/33 KV S/S | P & T 33/11 KV SS
7 | LALBAGH 132/33 KV S/S | MADARTEK LOCAL 33/11 KV S/S | MATUAIL 33/11KV S/S | KAMALAPUR RAILWAY 33/11 KV SS
8 | LALBAGH NEW 33/11 KV S/S | TEJGAON 33/11 KV S/S | LAXMI NARAYAN COTTON MILL 33/11 KV | BANGABHABAN 132/11KV S/S
9 | LALBAGH OLD 33/11 KV S/S | ASADGATE 33/11 KV S/S | FATULLAH OLD 33/11KV S/S | NARINDA 132/33KV S/S
10 | MIDFORT 33/11 KV S/S | BANASREE 33/11KV S/S | NEW FATULLAH 132/33 KV SS | NARINDA 33/11KV S/S
11 | AZIMPUR 33/11 KV S/S | GORAN 33/11 KV S/S | NEW FATULLAH 33/11 KV SS | KUMERTULY 33/11KV S/S
12 | KAMRANGIRCHAR 132/33 KV S/S | LALMATIA 33/11 KV S/S | DAPA 33/11 KV | BANGSHAL 33/11 KV
13 | KAMRANGIRCHAR 33/11 KV S/S | GREEN ROAD 33/11KV S/S | SITALAKHYA 132/33KV S/S | KAZLA 132/133 KV SS
14 | BGB 33/11 KV S/S | GREEN ROAD DORMETORY 33/11 KV S/S | SITALAKHYA 33/11KV S/S | KAZLA 33/11KV S/S
15 | JIGATOLA 132/33 KV S/S | TALTALA 33/11 KV S/S | MI CEMENT 132/33 KV | SHYAMPUR 132/33KV S/S
16 | JIGATOLA NEW 33/11 KV S/S | SHER-E-BANGLANAGAR 33/11KV S/S | MONDALPARA 33/11KV S/S | SHYAMPUR 33/11KV S/S
17 | ZIGATOLA OLD 33/11 KV S/S | MUGDAPARA HOSPITAL 33/11KV S/S | NARAYANGONJ BSCIC 33/11KV S/S | SHYAMPUR BISIC 33/11KV S/S
18 | DHAKA UDDYAN 33/11 KV S/S | KHILGAON 33/11 KV | CHAR SYEDPUR 132/33KV S/S | NANDALALPUR 33/11 KV
19 | SATMOSJID 132/33 KV S/S | MONIPURIPARA 33/11KV S/S | CHAR SYEDPUR 33/11 KV S/S NEW | POSTOGOLA 132/33 KV S/S
20 | SATMASJID 33/11KV S/S |  | AMULIA 33/11 KV | POSTOGOLA 33/11KV S/S
21 | JAPAN GERDEN CITY 33/11 KV S/S |  |  | IG GATE GIS 33/11 KV
22 | DHAKA UNIVERSITY 132/33 KV S/S
23 | DHAKA UNIVERSITY 33/11 KV S/S
24 | BIDDYUT BHABAN 33/11 KV S/S
25 | DMCH 33/11 KV S/S
26 | BB AVENEU 33/11 KV S/S
27 | KALLYANPUR 33/11 KV S/S

## Sheet1 (hidden)
1 | Moghbazar 33/11KV S/S
2 | Green Road 33/11KV S/S
3 | Lalmatia 33/11KV S/S
4 | Tejgoan 33/11KV S/S
5 | Dhanmondi 33/11KV S/S
6 | Kawranbazar 33/11KV S/S
7 | New Ramna 33/11KV S/S
8 | Dhanmondi 132/33kv S/S
9 | Khillgaon 33/11KV S/S
10 | Goran 33/11KV S/S
11 | Taltola 33/11KV S/S
12 | Satmasjid 33/11KV S/S
13 | Civil Aviation
14 | Japan garden Building
15 | Kallyanpur132/33 KV S/S
16 | Jigatola 33/11KV S/S
17 | Kallyanpur &Agargaon 33/11KV S/S
18 | Kamrangirchar 33/11 KV
19 | Lalbagh 33/11KV S/S
20 | Ullon 132/33/11 Kv S/S
21 | Kakrail 33/11KV S/S
22 | Banshal 33/11 KV S/S
23 | Baridhara 33/11KV S/S
24 | Japan Garden 33/11 KV
25 | Azimpur 33/11 KV
26 | T&T 33/11 KV
27 | SHERE BANGLANAGAR 33/11KV
28 | LALBAGH 33/11KV (GIS)
29 | biddut bhabon 33/11KV (GIS)
30 | Asad Gate 33/11 KV S/S
31 | Banasree 33/11SS
32 | Mugdhapara Hospital 33/11 kV
33 | DMC
34 | Green Road Dormatory
35 | BSMMU 33/11KV S/S
36 | Dhaka Uddyan 33/11KV S/S
37 | Dhaka University 33/11 KV SS
38 | Manipuripara 33/11 KV SS
39 | BGB 33/11 KV SS
40 | Moghbazar 132/33 KV Boshundhora City
41 | BB Avenue 33/11 KV SS
42 | Jigatola 132/33/11 New Grid
43 | Ispahani 33/11 KV SS
44 | Kamrangirchar SS-2 33/11 KV
45 | Bangabhaban 33/11KV S/S
46 | Narinda 33/11KV S/S
47 | Kumertully 33/11KV
48 | Maderteck 33/11KV S/S
49 | Kazla 33/11KV S/S
50 | Shyampur 132/11KV S/S
51 | Shyampur 33/11KV S/S
52 | Shyampur BISIC 33/11KV S/S
53 | Postogola 33/11KV S/S
54 | Fatullah 33/11KV S/S
55 | Sitalakhya 33/11KV S/S
56 | Sitalakhya 33/11KV S/S
57 | Ngonj BSCIC 33/11KV S/S
58 | Char Syedpuri 33/11KV S/S
59 | Siddhirganj 133/33KV S/S
60 | Siddhirganj 33/11KV S/S
61 | Sarulia 33/11KV S/S
62 | Demra 33/11KV S/S
63 | Mandalpara 33/11KV S/S
64 | Khanpur 33/11KV S/S
65 | Matuail 33/11KV S/S
66 | Modongonj 132/33 KV S/S
67 | Maniknagar33/11kv s/s 132/33 KV S/S
68 | IG Gate 33/11 kv
69 | Motijil 33/11kv
70 | Mitford 33/11kv
71 | Nandalalpr 33/11 kV SS
72 | MI CEMENT 132/ 33 KV Substation
73 | Dapa 33/11 kV
74 | Laxmi Narayan Cotton Mill
75 | Amulia 33/11 KV SS
76 | New Fatullah 33/11 KV SS
77 | P&T 33/11 KV SS
78 | Kazla 132/33 KV SS
79 | Kamalapur Railway 33/11 KV SS
80 | 132 KV Char Syedpur SS
81 | 132/33/11 KV Motijheel SS

## Linked_11KV
SL | Feeder_Name | Voltage | Type | Meter_No | CF | Opening_Reading | Closing_Reading | Difference | OMF | Blank | Consumption | Corrected_Consumption | NOCS | Substation_Name | June23_Consumption | May23_Consumption
1 | 11 kV Balaka Feeder | 11 | EXPORT | HA021100901-02 | 1 | 5173196 | 6440974 | 1267778 | 1 | 0 | 1267778 | 1273734.3863 | Paribag | Dhanmondi 33/11KV S/S | 1257653.9222 | 1137299.4891
2 | 11 kV Mogbazar O/H | 11 | 0 | HA021100463-02 | 1 | 46129640 | 47694141 | 1564501 | 1 | 0 | 1564501 | 1571851.4764 | Paribag | Dhanmondi 33/11KV S/S | 1518772.8573 | 1477894.3769
3 | 11 kV Panthopath Feeder | 11 | 0 | HA021101078-02 | 1 | 59070322 | 61262551 | 2192229 | 1 | 0 | 2192229 | 2202528.7234 | Paribag | Dhanmondi 33/11KV S/S | 2146238.9144 | 2162610.3185
4 | 11 kV Shahbagh Feeder ( old University O/H) | 11 | 0 | DHK60882 | 1 | 208836.3 | 215574 | 6737.7 | 60 | 0 | 404262 | 406161.3393 | Paribag | Dhanmondi 33/11KV S/S | 416714.2185 | 395540.6076
5 | 11 kV P G Hospital Feeder | 11 | 0 | DHK60889 | 1 | 279161.7 | 283084.6 | 3922.9 | 60 | 0 | 235374 | 236479.8549 | Paribag | Dhanmondi 33/11KV S/S | 217917.4597 | 226732.9713
6 | 11 kV Abdul Monem Ltd | 11 | 0 | DHK60890 | 1 | 691.92 | 699.41 | 7.49 | 60000 | 0 | 449400 | 451511.4107 | Paribag | Dhanmondi 33/11KV S/S | 418508.0827 | 415788.2923
7 | 11 kV Surjasen Hall Feeder | 11 | 0 | DHK60880 | 1 | 538943.6 | 552176.6 | 13233 | 60 | 0 | 793980 | 797710.3468 | Ramna | Dhanmondi 33/11KV S/S | 762400.0883 | 500947.7604
8 | 11 kV Azimpur-1 Feeder | 11 | 0 | DHK60872 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0 | 0
9 | 11 kV TSC Feeder | 11 | 0 | DHK60873 | 1 | 918512 | 928405.7 | 9893.7 | 60 | 0 | 593622 | 596411.0072 | Ramna | Dhanmondi 33/11KV S/S | 501019.2093 | 594864.6942
10 | 11 kV SCADA Bhaban | 11 | 0 | DHK60883 | 1 | 28074.3 | 28176.9 | 102.6 | 60 | 0 | 6156 | 6184.9227 | Paribag | Dhanmondi 33/11KV S/S | 6569.6736 | 7038.2714
11 | 11 kV DPH Sw/S-2 | 11 | 0 | DHK60871 | 1 | 474478.5 | 493864.3 | 19385.8 | 60 | 0 | 1163148 | 1168612.8044 | Paribag | Dhanmondi 33/11KV S/S | 1138030.0608 | 1225995.769
12 | 11 kV New Elephant Road Feeder | 11 | 0 | DHK60981 | 1 | 61120.9 | 82214.7 | 21093.8 | 60 | 0 | 1265628 | 1271574.285 | Paribag | Dhanmondi 33/11KV S/S | 1340854.1319 | 1236853.2667
13 | 11 kV Dhanmondi O/H Feeder | 11 | 0 | DHK61110 | 1 | 380880.9 | 404842.1 | 23961.2 | 60 | 0 | 1437672 | 1444426.5973 | Paribag | Dhanmondi 33/11KV S/S | 1452129.1083 | 1368507.5074
14 | 11 kV Sonargaon Feeder | 11 | 0 | DHK61115 | 1 | 312180.8 | 340916.2 | 28735.4 | 60 | 0 | 1724124 | 1732224.4313 | Paribag | Dhanmondi 33/11KV S/S | 1700265.2603 | 1714907.3622
15 | 11 kV Museum Feeder | 11 | 0 | DHK61107 | 1 | 545315.1 | 547755.5 | 2440.4 | 60 | 0 | 146424 | 147111.9421 | Ramna | Dhanmondi 33/11KV S/S | 139723.2891 | 145373.4466
16 | 11 kV Shanta property | 11 | 0 | DHK61112 | 1 | 338664.1 | 342098.2 | 3434.1 | 60 | 0 | 206046 | 207014.0635 | Paribag | Dhanmondi 33/11KV S/S | 222651.1173 | 196910.1041
17 | 11 kV BIRDEM RMU Feeder | 11 | 0 | DHK61108 | 1 | 685561.8 | 701416.8 | 15855 | 60 | 0 | 951300 | 955769.4815 | Kakrail | Dhanmondi 33/11KV S/S | 767058.4747 | 1048103.4598
18 | 11 kV Azimpur-2 Feeder | 11 | 0 | DHK61109 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Azimpur | Dhanmondi 33/11KV S/S | 0 | 0
19 | 11 kV DPH Sw/S-1 | 11 | 0 | DHK60978 | 1 | 767608.4 | 782449.9 | 14841.5 | 60 | 0 | 890490 | 894673.7786 | Kakrail | Dhanmondi 33/11KV S/S | 964542.5031 | 717844.627
20 | WASA Bhaban | 11 | 0 | 8536188 | 1.2 | 2288.8 | 2503.3 | 214.5 | 1000 | 1046400 | 1046400 | 1051553.1772 | Shere b.nagar | Kawranbazar 33/11KV S/S | 992894.4687 | 967717.4567
21 | Sangsad Bhaban | 11 | 0 | 8536178 | 1.2 | 568300 | 572139 | 3839 | 44 | 0 | 202699.2 | 203697.4272 | Shere b.nagar | Kawranbazar 33/11KV S/S | 26163.5003 | 291323.9838
22 | Air Port Road (West) | 11 | 0 | 8536182 | 1.2 | 100568.1 | 101503.6 | 935.5 | 1000 | 0 | 1122600 | 1128128.4372 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1054483.651 | 1142492.7318
23 | ICC (PM Office) | 11 | 0 | 8536193 | 1.2 | 32421.4 | 32421.4 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0 | 0
24 | (UTC) Tower | 11 | 0 | DHK00183 | 1.2 | 15079.3 | 15757.4 | 678.1 | 444.44 | 0 | 361649.7168 | 363430.7232 | Shere b.nagar | Kawranbazar 33/11KV S/S | 289733.3028 | 306081.9435
25 | Sonargaon Hotel | 11 | 0 | 8536190 | 1.2 | 51744.1 | 51744.1 | 0 | 1000 | 40 | 62854.4448 | 63163.9823 | Kakrail | Kawranbazar 33/11KV S/S | 0 | 0
26 | Panthopath | 11 | 0 | 8536184 | 1.2 | 34310.5 | 35309.1 | 998.6 | 1000 | 0 | 1198320 | 1204221.3334 | Shere b.nagar | Kawranbazar 33/11KV S/S | 1027392.6275 | 1044641.4249
27 | Titas Bhaban | 11 | 0 | DHK00190 | 1.2 | 55463.3 | 55753.9 | 290.6 | 444.44 | 0 | 154985.1168 | 155748.3677 | Kakrail | Kawranbazar 33/11KV S/S | 190247.4883 | 258497.9936
28 | Green Road Dormatory s/s | 11 | 0 | DHK00021 | 1.2 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | 0 | Kawranbazar 33/11KV S/S | 0 | 0
29 | Aux. Transformer, AT-1 | 11 | 0 | 85-12906 | 1.2 | 68255 | 68557 | 302 | 10 | 0 | 3624 | 3641.847 | Shere b.nagar | Kawranbazar 33/11KV S/S | 3397.8572 | 0
30 | Aux. Transformer, AT-2 | 11 | 0 | 85-12909 | 1.2 | 58961 | 58961 | 0 | 10 | 0 | 0 | 0 | Shere b.nagar | Kawranbazar 33/11KV S/S | 0 | 0
31 | Police Bhaban | 11 | 0 | DHK 00005 | 1 | 73101.3 | 73369.4 | 268.1 | 444.44 | 0 | 119154.364 | 121266.9463 | Ramna | New Ramna 33/11KV S/S | 121013.0538 | 111715.2077
32 | Water Works | 11 | 0 | DHK 00010 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Lalbag | New Ramna 33/11KV S/S | 0 | 0
33 | GPO | 11 | 0 | DHK 00060 | 1 | 97916.8 | 98412.6 | 495.8 | 444.44 | 0 | 220353.352 | 224260.1714 | Ramna | New Ramna 33/11KV S/S | 278965.4908 | 233730.721
34 | Culvert Road | 11 | 0 | 8536184 | 1 | 39940.4 | 39940.4 | 0 | 444.44 | 80 | 973062.72 | 990314.9211 | Ramna | New Ramna 33/11KV S/S | 787025.6832 | 769934.2629
35 | Secretariat (East) | 11 | 0 | DHK00059 | 1 | 81719.4 | 81723.1 | 3.7 | 444.44 | 0 | 1644.428 | 1673.5834 | Ramna | New Ramna 33/11KV S/S | 2240.1359 | 29358.1395
36 | Siddik Bazar | 11 | 0 | DHK00076 | 1 | 29231.2 | 30335.3 | 1104.1 | 444.44 | 0 | 490706.204 | 499406.3237 | Bangshal | New Ramna 33/11KV S/S | 894134.2296 | 765262.7858
37 | Bokshi Bazar | 11 | 0 | DHK 00206 | 1 | 85464 | 86520.6 | 1056.6 | 444.44 | 0 | 469595.304 | 477921.1318 | Ramna | New Ramna 33/11KV S/S | 520717.296 | 447450.7163
38 | Ramna 11 kV Sw/S Circuit-1 | 11 | 0 | DHK00198 | 1 | 46597.3 | 46678.5 | 81.2 | 444.44 | 0 | 36088.528 | 36728.3702 | Ramna | New Ramna 33/11KV S/S | 1058898.5083 | 1085933.5304
39 | TNT RMU | 11 | 0 | DHK 00207 | 1 | 60351.5 | 61321.1 | 969.6 | 444.44 | 0 | 430929.024 | 438569.3066 | Ramna | New Ramna 33/11KV S/S | 426631.5896 | 435698.3854
40 | DIT 11 kV Sw/S Circuit-1 | 11 | 0 | DHK 00052 | 1 | 2799.1 | 2799.1 | 0 | 444.44 | 0 | 0 | 0 | Motijheel | New Ramna 33/11KV S/S | 0 | 35665.375
41 | Secretariat (West) | 11 | 0 | DHK 00006 | 1 | 67894.2 | 69075.5 | 1181.3 | 444.44 | 0 | 525016.972 | 534325.4145 | Ramna | New Ramna 33/11KV S/S | 379223 | 77048.1002
42 | Ramna 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00197 | 1 | 84763.4 | 86438.2 | 1674.8 | 444.44 | 0 | 744348.112 | 757545.2503 | Ramna | New Ramna 33/11KV S/S | 868.6241 | 952.8917
43 | Sayed Nazrul Islam Road | 11 | 0 | DHK00186 | 1 | 24569.9 | 27519.2 | 2949.3 | 444.44 | 0 | 1310786.892 | 1334026.873 | Ramna | New Ramna 33/11KV S/S | 1329086.3239 | 1287356.6852
44 | Gulistan Complex | 11 | 0 | DHK00030 | 1 | 54446.3 | 54911.6 | 465.3 | 444.44 | 0 | 206797.932 | 210464.4166 | Ramna | New Ramna 33/11KV S/S | 215693.0819 | 200288.7599
45 | Mohanagor Nattomanso | 11 | 0 | DHK 00008 | 1 | 99840.8 | 99993.3 | 152.5 | 444.44 | 0 | 67777.1 | 68978.774 | Ramna | New Ramna 33/11KV S/S | 72827.2741 | 40429.8335
46 | DIT 11 kV Sw/S Circuit-2 | 11 | 0 | DHK00196 | 1 | 24947 | 26040.2 | 1093.2 | 444.44 | 0 | 485861.808 | 494476.0375 | Motijheel | New Ramna 33/11KV S/S | 481492.0598 | 701782.0483
47 | Jail | 11 | 0 | DHK00009 | 1 | 0 | 0 | 0 | 444.44 | 0 | 0 | 0 | Bangshal | New Ramna 33/11KV S/S | 0 | 0
48 | Kosturi Bazar | 11 | 0 | HA021100713-02 | 1 | 75962552 | 76731766 | 769214 | 1 | 0 | 769214 | 782852.0054 | Ramna | New Ramna 33/11KV S/S | 108530.1819 | 101993.6695
49 | Kaptan Bazar | 11 | 0 | HA021101251-02 | 1 | 6236867 | 6664226 | 427359 | 1 | 0 | 427359 | 434935.9868 | Narinda | New Ramna 33/11KV S/S | 427872.7434 | 409490.3581
50 | G.T.V | 11 | 0 | HA-021101054-02 | 1 | 71120147 | 71762722 | 642575 | 1 | 0 | 642575 | 653967.7221 | Ramna | New Ramna 33/11KV S/S | 639660.2776 | 603518.518
51 | Kazi Alauddin Road | 11 | 0 | HA021100951-02 | 1 | 6043531 | 6674283 | 630752 | 1 | 0 | 630752 | 641935.1027 | Bangshal | New Ramna 33/11KV S/S | 386345.3523 | 300171.4873
52 | 11/0.4 kV Aux. Transformer, AT-1 | 0.4 | 0 | 2436 | 1 | 67423 | 67423 | 0 | 10 | 0 | 0 | 0 | Ramna | New Ramna 33/11KV S/S | 0 | 10.2097
53 | 11/0.4 kV Aux. Transformer, AT-2 | 0.4 | 0 | 2437 | 1 | 88447 | 88807 | 360 | 10 | 0 | 3600 | 3663.8273 | Ramna | New Ramna 33/11KV S/S | 3672.2594 | 3624.4279
54 | Pioneer | 11 | 0 | 06604395 | 1 | 23746.79 | 23854.78 | 107.99 | 8000 | 0 | 863920 | 872559.2 | Ramna | Kakrail 33/11KV S/S | 859758.1646 | 826396.2524
55 | Pir Saheber Goli | 11 | 0 | DHK-00102 | 1 | 79643 | 83183.5 | 3540.5 | 444.444 | 0 | 1573553.982 | 1589289.5218 | Rajarbag | Kakrail 33/11KV S/S | 1570646.0565 | 1456807.534
56 | Montri Para | 11 | 0 | DHK-00110 | 1 | 12608.2 | 12700.2 | 92 | 2222.22 | 0 | 204444.24 | 206488.6824 | Kakrail | Kakrail 33/11KV S/S | 233752.6835 | 183436.8651
57 | Baily Road 11 kV Sw/S-2 | 11 | 0 | 9119865 | 1 | 62736.7 | 65421.2 | 2684.5 | 1000 | 0 | 2684500 | 2711345 | Kakrail | Kakrail 33/11KV S/S | 2187071.9465 | 2272508.865
58 | Jamuna U/G 11 KV Jonaki O/H | 11 | 0 | D0086136 | 1 | 54118.1 | 54118.1 | 0 | 1000 | 0 | 0 | 0 | Rajarbag | Kakrail 33/11KV S/S | 0 | 0
59 | High Court | 11 | 0 | 1025651 | 1 | 28975.9 | 29238.4 | 262.5 | 1000 | 0 | 262500 | 265125 | Ramna | Kakrail 33/11KV S/S | 281963.0422 | 304725.5352
60 | Secretaiat | 11 | 0 | DHK00150 | 1 | 16809.5 | 16809.5 | 0 | 2222.22 | 0 | 0 | 0 | Ramna | Kakrail 33/11KV S/S | 0 | 0
61 | Shanti Nagar Bazar | 11 | 0 | 06604402 | 1 | 5631.51 | 5671.14 | 39.63 | 40000 | 0 | 1585200 | 1601052 | Rajarbag | Kakrail 33/11KV S/S | 1588931.4952 | 1455327.1248
62 | Tottho Bhovon | 11 | 0 | 9119867 | 1 | 32076 | 32298 | 222 | 1000 | 0 | 222000 | 224220 | Kakrail | Kakrail 33/11KV S/S | 214756.2499 | 266523.7033
63 | Central Police Hospital/ PNT (Circuit House) | 11 | 0 | DHK00199 | 1 | 78368.5 | 78681.8 | 313.3 | 2222.22 | 0 | 696221.526 | 703183.7413 | Kakrail | Kakrail 33/11KV S/S | 652674.6032 | 659362.3521
64 | Baily Road 11 kV Sw/S-1 | 11 | 0 | DHK00027 | 1 | 55235.8 | 55889.6 | 653.8 | 2222.22 | 0 | 1452887.436 | 1467416.3104 | Kakrail | Kakrail 33/11KV S/S | 1045890.5162 | 1203453.6068
65 | Bijoy Nagar | 11 | 0 | D1025656 | 1 | 65886.7 | 66935.36 | 1048.66 | 1000 | 0 | 1048660 | 1059146.6 | Ramna | Kakrail 33/11KV S/S | 1027245.6372 | 1033096.3518
66 | Shilpakala Academy | 11 | 0 | D0086137 | 1 | 25394.3 | 25965.1 | 570.8 | 1000 | 0 | 570800 | 576508 | Ramna | Kakrail 33/11KV S/S | 916863.5723 | 907912.3538
67 | Judges Complex | 11 | 0 | 06604344 | 1 | 670.94 | 674.7 | 3.76 | 40000 | 0 | 150400 | 151904 | Kakrail | Kakrail 33/11KV S/S | 129118.504 | 137005.2472
68 | Auxiliary Transformer, AT-1 | 11 | 0 | 39333 | 1 | 492441 | 492441 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 0 | 0
69 | Auxiliary Transformer, AT-2 | 11 | 0 | 39254 | 1 | 1195010 | 1195010 | 0 | 1 | 0 | 0 | 0 | Kakrail | Kakrail 33/11KV S/S | 0 | 0
70 | 11 kV Jamuna (F1) | 11 | 0 | BD017073 | 1 | 0.3625 | 0.3748 | 0.0123 | 2000 | 0 | 24.6 | 24.7258 | Kakrail | BSMMU 33/11KV S/S | 22.8027 | 22.5473
71 | 11 kV Pukur Par (F2) | 11 | 0 | BD017074 | 1 | 2906.26 | 2928.46 | 22.2 | 2000 | 0 | 44400 | 44627.1399 | Kakrail | BSMMU 33/11KV S/S | 45645.6695 | 45879.8149
72 | 11 kV BSMMU Convention center (F3) | 11 | 0 | BD017075 | 1 | 1714.95 | 1753.43 | 38.48 | 2000 | 0 | 76960 | 77353.7092 | Kakrail | BSMMU 33/11KV S/S | 38986.4869 | 53187.5695
73 | 11 kV Unique Tower Sw/S-1 (F4) | 11 | 0 | BD017076 | 1 | 2929.26 | 3017.58 | 88.32 | 2000 | 0 | 176640 | 177543.6485 | Kakrail | BSMMU 33/11KV S/S | 176710.4897 | 172426.7726
74 | 11 kV Holi Family Feeder (F5) | 11 | 0 | BD017077 | 1 | 14032.26 | 14405.79 | 373.53 | 2000 | 0 | 747060 | 750881.7825 | Kakrail | BSMMU 33/11KV S/S | 742559.3925 | 663133.437
75 | 11 kV Navy House Feeder (F6) | 11 | 0 | BD017078 | 1 | 26311.05 | 26649.82 | 338.77 | 2000 | 0 | 677540 | 681006.1346 | Kakrail | BSMMU 33/11KV S/S | 662407.0498 | 617092.5697
76 | 11 kV Paribagh Feeder (F7) | 11 | 0 | BD017079 | 1 | 31129.75 | 31963.13 | 833.38 | 2000 | 0 | 1666760 | 1675286.7504 | Paribag | BSMMU 33/11KV S/S | 1691331.4714 | 1532172.4233
77 | 11 kV BSMMU C BLOCK Feeder (F8) | 11 | 0 | BD017080 | 1 | 6172.02 | 6399.81 | 227.79 | 2000 | 0 | 455580 | 457910.6397 | Paribag | BSMMU 33/11KV S/S | 432100.2302 | 400577.6906
78 | 11 kV Oncology Bhaban (F9) | 11 | 0 | BD017083 | 1 | 2225.09 | 2293.72 | 68.63 | 2000 | 0 | 137260 | 137962.1897 | Paribag | BSMMU 33/11KV S/S | 128058.0984 | 129888.7959
79 | Rupayan Trade Center | 11 | 0 | BD017084 | 1 | 1068.48 | 1218.74 | 150.26 | 2000 | 0 | 300520 | 302057.3893 | Kakrail | BSMMU 33/11KV S/S | 282490.5956 | 277634.2814
80 | 11 kV Unique Tower Sw/S-2 (Secretary Qtr.) (F11) | 11 | 0 | BD017085 | 1 | 2058.21 | 2119.1 | 60.89 | 2000 | 0 | 121780 | 122402.9977 | Kakrail | BSMMU 33/11KV S/S | 124143.3062 | 110824.2128
81 | 11 kV BSMMU RMU (F12) | 11 | 0 | BD017086 | 1 | 1965.52 | 2052.22 | 86.7 | 2000 | 0 | 173400 | 174287.0734 | Paribag | BSMMU 33/11KV S/S | 168699.2913 | 166467.8321
82 | 11 kV BSMMU Hospital D BLOCK (F13) | 11 | 0 | BD017087 | 1 | 4032.7 | 4149.43 | 116.73 | 2000 | 0 | 233460 | 234654.3262 | Paribag | BSMMU 33/11KV S/S | 236945.8228 | 229298.4167
83 | 11 kV BCS Academy RMU (F14) | 11 | 0 | BD017088 | 1 | 995.07 | 1022.96 | 27.89 | 2000 | 0 | 55780 | 56065.3573 | Paribag | BSMMU 33/11KV S/S | 59004.3933 | 75292.0174
84 | Spare | 11 | 0 | BD017089 | 1 | 0.05 | 0.05 | 0 | 2000 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 0 | 0
85 | BSMMU Super Specialist Hospital RMU | 11 | 0 | BD017090 | 1 | 1147.96 | 1402.07 | 254.11 | 2000 | 0 | 508220 | 510819.9335 | Paribag | BSMMU 33/11KV S/S | 355842.5004 | 253677.7304
86 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKD4418 | 1 | 2605.78 | 2759.07 | 153.29 | 100 | 0 | 15329 | 15407.4195 | Paribag | BSMMU 33/11KV S/S | 14685.5155 | 15087.5942
87 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 1666.67 | 1666.67 | 0 | 100 | 0 | 0 | 0 | Paribag | BSMMU 33/11KV S/S | 0 | 0
88 | Chata Mosjid | 11 | 0 | 0 | 1 | 169591.28 | 171770.4353 | 2179.1553 | 1000 | 0 | 2179155.29 | 2199148.6226 | Kamrangirchar | LALBAGH New 33/11 KV S/S | 2319503.7751 | 2426211.3577
89 | AC mosjid | 11 | 0 | 0 | 1 | 5346.4008 | 6488.7556 | 1142.3548 | 1000 | 0 | 1142354.8 | 1152835.6866 | Lalbag | LALBAGH New 33/11 KV S/S | 1275218.63 | 1340177.0113
90 | Kazi Reaz Uddin Road | 11 | 0 | 0 | 1 | 18853.63 | 20836.008 | 1982.378 | 1000 | 0 | 1982378 | 2000565.9387 | Lalbag | LALBAGH New 33/11 KV S/S | 2224217.61 | 2267338.6868
91 | Nazimuddin | 11 | 0 | 0 | 1 | 4214.292 | 4687.9236 | 473.6316 | 1000 | 0 | 473631.6 | 477977.0793 | Lalbag | LALBAGH New 33/11 KV S/S | 0 | 0
92 | Kamal Bagh | 11 | 0 | 0 | 1 | 13296.26 | 14900.122 | 1603.862 | 1000 | 0 | 1603862 | 1618577.1268 | Lalbag | LALBAGH New 33/11 KV S/S | 1589844.4629 | 1583845.5588
93 | Rahamatganj | 11 | 0 | 0 | 1 | 8699.95 | 10837.383 | 2137.433 | 1000 | 0 | 2137433 | 2157043.5386 | Lalbag | LALBAGH New 33/11 KV S/S | 2473091.3867 | 2558519.7488
94 | Water Works 11kV Sw/S-1 | 11 | 0 | 0 | 1 | 20641.601 | 22372.9274 | 1731.3264 | 1000 | 0 | 1731326.4 | 1747210.9883 | Lalbag | LALBAGH New 33/11 KV S/S | 1862323.276 | 1854345.8684
95 | City Colony | 11 | 0 | 0 | 1 | 22484.11 | 24326.885 | 1842.775 | 1000 | 0 | 1842775 | 1859682.1079 | Lalbag | LALBAGH New 33/11 KV S/S | 2050289.3435 | 2080353.5364
96 | Water Works 11kV Sw/S-2 | 11 | 0 | 0 | 1 | 32750 | 35515.332 | 2765.332 | 1000 | 0 | 2765332 | 2790703.3917 | Lalbag | LALBAGH New 33/11 KV S/S | 2997202.1128 | 3092062.2371
97 | Chun Goli | 11 | 0 | 0 | 1 | 6376.308 | 7124.165 | 747.857 | 1000 | 0 | 747857 | 754718.4448 | Lalbag | LALBAGH New 33/11 KV S/S | 841380.8401 | 894878.3402
98 | Alir Ghat | 11 | 0 | 0 | 1 | 119606.4 | 121324.8 | 1718.4 | 1000 | 0 | 1718400 | 1734165.991 | Lalbag | LALBAGH New 33/11 KV S/S | 1904122.5273 | 2096766.6729
99 | Club Ghat | 11 | 0 | 0 | 1 | 13974.46 | 16270.969 | 2296.509 | 1000 | 0 | 2296509 | 2317579.0304 | Lalbag | LALBAGH New 33/11 KV S/S | 2539875.5429 | 2741271.1594
100 | Debidas Ghat | 11 | 0 | 0 | 1 | 26831.902 | 29072.95 | 2241.048 | 1000 | 0 | 2241048 | 2261609.1864 | Lalbag | LALBAGH New 33/11 KV S/S | 2437761.5097 | 2619436.8857
101 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Lalbag | LALBAGH New 33/11 KV S/S | 0 | 0
102 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
103 | Sowari Ghat | 11 | 0 | 8838019 | 1 | 74886.8 | 77211.8 | 2325 | 1000 | 0 | 2325000 | 2329233.6447 | Lalbag | Lalbagh Old 33/11KV S/S | 2612060.995 | 2829205.9908
104 | Novo Kumar (Kara Odidoptor) | 11 | 0 | 8838014 | 1 | 81145.3 | 81145.3 | 0 | 1000 | Estimated | 121632.84 | 121854.324 | Lalbag | Lalbagh Old 33/11KV S/S | 118483.0867 | 132959.886
105 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
106 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
107 | Eidgah | 11 | 0 | 06604339 | 1 | 18579.25 | 18579.25 | 0 | 8000 | Estimated | 1094695.56 | 1096688.9157 | Lalbag | Lalbagh Old 33/11KV S/S | 1303313.9541 | 1329598.8604
108 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
109 | Modumoti | 11 | 0 | 0 | 1 | 87070.4 | 91067.8 | 3997.4 | 444.44 | Estimated | 1581226.92 | 1584106.2116 | Lalbag | Lalbagh Old 33/11KV S/S | 1954970.9311 | 2054834.6025
110 | Lalbagh O/H | 11 | 0 | 61389152 | 1 | 440314 | 440978 | 664 | 1000 | Estimated | 1179838.548 | 1181986.9425 | Lalbag | Lalbagh Old 33/11KV S/S | 1066347.7806 | 1087853.6131
111 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
112 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
113 | Water Works 11 kV Sw/S-2 | 11 | 0 | 61389109 | 1 | 400866 | 401739 | 873 | 1000 | 0 | 873000 | 874589.6653 | Lalbag | Lalbagh Old 33/11KV S/S | 951212.9635 | 980831.1601
114 | Islambagh | 11 | 0 | 61389186 | 1 | 499228 | 500001 | 773 | 1000 | 0 | 773000 | 774407.5731 | Lalbag | Lalbagh Old 33/11KV S/S | 861627.8273 | 876487.4197
115 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
116 | WASA Low Lift Pump | 11 | 0 | 61389202 | 1 | 15477 | 15534 | 57 | 1000 | 0 | 57000 | 57103.7926 | Lalbag | Lalbagh Old 33/11KV S/S | 61401.0484 | 45712.4958
117 | Shahi Mosjid | 11 | 0 | 06604459 | 1 | 35606.2 | 35827.5 | 221.3 | 8000 | 0 | 1770400 | 1773623.7611 | Azimpur | Lalbagh Old 33/11KV S/S | 1752245.002 | 1250534.8854
118 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
119 | 33/0.4 kV Auxiliary Transformer | 0.415 | 0 | 5395822 | 1 | 4391673 | 4391673 | 0 | 1 | 0 | 0 | 0 | Lalbag | Lalbagh Old 33/11KV S/S | 0 | 0
120 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0
121 | Spare | 11 | 0 | DHK-66478 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0
122 | Chawk Bazar | 11 | 0 | DHK-60904 | 1 | 963274.2 | 971432 | 8157.8 | 60 | 0 | 489468 | 480516.9276 | Lalbag | Mitford 33/11 kV | 522405.3875 | 508276.2976
123 | Spare | 11 | 0 | DHK-66482 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0
124 | Chatrabas | 11 | 0 | DHK-66485 | 1 | 795411 | 816427 | 21016 | 60 | 0 | 1260960 | 1237900.3837 | Bangshal | Mitford 33/11 kV | 762976.1234 | 353557.5482
125 | Begum Bazar | 11 | 0 | DHK-66481 | 1 | 3626756 | 3667458 | 40702 | 60 | 0 | 2442120 | 2397460.098 | Bangshal | Mitford 33/11 kV | 2421237.7604 | 2357293.0663
126 | SCC ROAD | 11 | 0 | DHK-60901 | 1 | 48991.1 | 74915 | 25923.9 | 60 | 0 | 1555434 | 1526989.2348 | Bangshal | Mitford 33/11 kV | 1650255.6547 | 1574186.7645
127 | Spare | 11 | 0 | DHK-66483 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0
128 | Armanitola | 11 | 0 | DHK-61104 | 1 | 668332.7 | 684884 | 16551.3 | 60 | 0 | 993078 | 974917.2355 | Bangshal | Mitford 33/11 kV | 956708.8537 | 952602.7371
129 | Mitford Hospital (RMU) | 11 | 0 | DHK-61101 | 1 | 383048.6 | 392201 | 9152.4 | 60 | 0 | 549144 | 539101.6117 | Bangshal | Mitford 33/11 kV | 513839.5885 | 528540.0121
130 | Emamganj | 11 | 0 | DHK-68130 | 1 | 1447.92 | 1450.67 | 2.75 | 60000 | 0 | 165000 | 161982.5873 | Bangshal | Mitford 33/11 kV | 733781.3763 | 1159712.4523
131 | Kamal Dho Road | 11 | 0 | DHK-68129 | 1 | 1216.26 | 1225.4 | 9.14 | 60000 | 0 | 548400 | 538371.2175 | Lalbag | Mitford 33/11 kV | 628439.5052 | 594724.3345
132 | Spare | 11 | 0 | DHK-68128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Mitford 33/11 kV | 0 | 0
133 | Panghat | 11 | 0 | DHK-68127 | 1 | 1505.39 | 1528.54 | 23.15 | 60000 | 0 | 1389000 | 1363598.8715 | Bangshal | Mitford 33/11 kV | 1411581.0725 | 1500768.6523
134 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | U0004460 | 1 | 5554.67 | 5594.68 | 40.01 | 100 | 0 | 4001 | 3927.8323 | Bangshal | Mitford 33/11 kV | 4152.4762 | 4434.1352
135 | Chadni chwok | 11 | 0 | DHK60916 | 1 | 399421 | 409665 | 10244 | 60 | 0 | 614640 | 623153.8648 | Paribag | Azimpur 33/11 KV | 792142.0147 | 648152.1238
136 | BGB | 11 | 0 | DHK61090 | 1 | 665574 | 676712 | 11138 | 60 | 0 | 668280 | 677536.8748 | Jigatola | Azimpur 33/11 KV | 266970.3715 | 253340.1998
137 | Pari Bibi Mazar | 11 | 0 | DHK61091 | 1 | 745025 | 780093 | 35068 | 60 | 0 | 2104080 | 2133225.2763 | Azimpur | Azimpur 33/11 KV | 2225341.7622 | 2144033.6462
138 | Azimpur | 11 | 0 | DHK61086 | 1 | 282859 | 301821 | 18962 | 60 | 0 | 1137720 | 1153479.4596 | Azimpur | Azimpur 33/11 KV | 1136633.6642 | 1104066.6214
139 | Aazd | 11 | 0 | DHK61089 | 1 | 960626 | 982542 | 21916 | 60 | 0 | 1314960 | 1333174.551 | Azimpur | Azimpur 33/11 KV | 1318714.278 | 1257709.9294
140 | Dayra Sharif | 11 | 0 | DHK61088 | 1 | 498851 | 515887 | 17036 | 60 | 0 | 1022160 | 1036318.7466 | Azimpur | Azimpur 33/11 KV | 1007533.0284 | 980271.2172
141 | Naya palton | 11 | 0 | DHK86065 | 1 | 1871.03 | 1899.17 | 28.14 | 60000 | 0 | 1688400 | 1711787.3638 | Azimpur | Azimpur 33/11 KV | 1744076.5145 | 1689342.4234
142 | Viqarunnisa Noon School | 11 | 0 | DHK66477 | 1 | 1584644 | 1609302 | 24658 | 60 | 0 | 1479480 | 1499973.4477 | Azimpur | Azimpur 33/11 KV | 1460116.0121 | 1388906.1459
143 | Subal Das Lane | 11 | 0 | DHK66480 | 1 | 3981086 | 4005845 | 24759 | 60 | 0 | 1485540 | 1506117.3895 | Azimpur | Azimpur 33/11 KV | 1034936.4652 | 1287496.6695
144 | Lalbagh | 11 | 0 | DHK61093 | 1 | 685659 | 726292 | 40633 | 60 | 0 | 2437980 | 2471750.3893 | Azimpur | Azimpur 33/11 KV | 2403281.4122 | 2365446.3751
145 | Zahrul Haque Hall | 11 | 0 | DHK66497 | 1 | 1228090 | 1239080 | 10990 | 60 | 0 | 659400 | 668533.8709 | Ramna | Azimpur 33/11 KV | 616760.0188 | 675859.2968
146 | Eden College | 11 | 0 | DHK60917 | 1 | 925859 | 933261 | 7402 | 60 | 0 | 444120 | 450271.8574 | Azimpur | Azimpur 33/11 KV | 455566.9136 | 455119.369
147 | Nilkhet/ PWD-01 | 11 | 0 | DHK60918 | 1 | 466773 | 478017 | 11244 | 60 | 0 | 674640 | 683984.9722 | Azimpur | Azimpur 33/11 KV | 653358.8311 | 648152.1238
148 | BUET | 11 | 0 | DHK66496 | 1 | 949620 | 962739 | 13119 | 60 | 0 | 787140 | 798043.2987 | Ramna | Azimpur 33/11 KV | 718091.8386 | 902348.6159
149 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIG2780 | 1 | 385337 | 389374 | 4037 | 1 | 0 | 4037 | 4092.9197 | Azimpur | Azimpur 33/11 KV | 4399.774 | 2203.9333
150 | Rasulpur | 11 | 0 | HA-021101042-02 | 1 | 90531613 | 91923561 | 1391948 | 1 | 0 | 1391948 | 1403442.4135 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1475786.882 | 1248201.2259
151 | Bheribadh | 11 | 0 | HA-021101105-02 | 1 | 62150594 | 64458541 | 2307947 | 1 | 0 | 2307947 | 2327005.5404 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2450676.7878 | 2398606.8547
152 | Panna Tower 11 KV Faridpur Tower Express | 11 | 0 | 30799521 | 1 | 2629.31 | 2634.51 | 5.2 | 60000 | 0 | 312000 | 314576.4303 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 364934.8739 | 488122.7019
153 | Panna Battery Express | 11 | 0 | DHK15431 | 1 | 5261.14 | 5278.8 | 17.66 | 60000 | 0 | 1059600 | 1068349.9537 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1060687.1709 | 1118589.0702
154 | Eidgah | 11 | 0 | 30799460 | 1 | 5334.36 | 5369.43 | 35.07 | 60000 | 0 | 2104200 | 2121576.0406 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2271856.6688 | 2848456.9491
155 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Jigatola | Kamrangirchar 33/11KV S/S | 0 | 0
156 | Huzur Para | 11 | 0 | HA-021101055-02 | 1 | 99457723 | 101275461 | 1817738 | 1 | 0 | 1817738 | 1832748.4977 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1797702.2907 | 1901795.8946
157 | Kamrangirchar | 11 | 0 | HA-021101015-02 | 1 | 19288783 | 21147055 | 1858272 | 1 | 0 | 1858272 | 1873617.2189 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1726065.7983 | 1737567.1439
158 | Munshihati | 11 | 0 | HA-021100854-02 | 1 | 50106769 | 51488293 | 1381524 | 1 | 0 | 1381524 | 1392932.3343 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1212171.698 | 1205376.9608
159 | Jhawchar | 11 | 0 | HA-021101028-02 | 1 | 98824125 | 100250925 | 1426800 | 1 | 0 | 1426800 | 1438582.214 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1425641.3374 | 1328999.0751
160 | RMU Express | 11 | 0 | HA-021101248-02 | 1 | 5318135 | 5919945 | 601810 | 1 | 0 | 601810 | 606779.6203 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 633839.2782 | 704501.3661
161 | Koyla Ghat | 11 | 0 | HA-021101259-02 | 1 | 15254118 | 15254118 | 0 | 1 | ESTIMATED | 1885309.02 | 1900877.505 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2223108.4368 | 1816011.9444
162 | Muslimbagh | 11 | 0 | HA-021100908-02 | 1 | 24575572 | 26159019 | 1583447 | 1 | 0 | 1583447 | 1596522.772 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 1696945.1326 | 1737474.4882
163 | Noyagaon | 11 | 0 | HA-021101087-02 | 1 | 3217494 | 5869693 | 2652199 | 1 | 0 | 2652199 | 2674100.301 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2742632.8101 | 2660587.4202
164 | Nurbagh | 11 | 0 | HA-021100982-02 | 1 | 21245035 | 23098305 | 1853270 | 1 | 0 | 1853270 | 1868573.9135 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2159293.4513 | 2300317.433
165 | Ali Nagar | 11 | 0 | HA-021101022-02 | 1 | 19758728 | 22030169 | 2271441 | 1 | 0 | 2271441 | 2290198.0816 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 2360084.8023 | 2402380.2856
166 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
167 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
168 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
169 | Nababgonj Park | 11 | 0 | 0 | 1 | 8188769 | 9205025 | 1016256 | 1 | 0 | 1016256 | 1021134.2367 | Azimpur | BGB 33/11 KV S/S | 1444952.9565 | 1573011.5868
170 | Kholamura Ghat | 11 | 0 | 0 | 1 | 74784480 | 77275264 | 2490784 | 1 | 0 | 2490784 | 2502740.2728 | Kamrangirchar | BGB 33/11 KV S/S | 2762472.0542 | 2841690.4191
171 | Khalpar | 11 | 0 | 0 | 1 | 82977184 | 84269168 | 1291984 | 1 | 0 | 1291984 | 1298185.7875 | Kamrangirchar | BGB 33/11 KV S/S | 1375644.1828 | 1437529.7992
172 | Shahidnagar | 11 | 0 | 0 | 1 | 14195510 | 16043430 | 1847920 | 1 | 0 | 1847920 | 1856790.3941 | Azimpur | BGB 33/11 KV S/S | 1877497.3089 | 1808709.9159
173 | BGB 1 No Gate | 11 | 0 | 0 | 1 | 31209790 | 32661410 | 1451620 | 1 | 0 | 1451620 | 1458588.073 | Azimpur | BGB 33/11 KV S/S | 1375749.2129 | 1318685.5995
174 | Ganaktuli | 11 | 0 | 0 | 1 | 22588480 | 23467080 | 878600 | 1 | 0 | 878600 | 882817.4598 | Jigatola | BGB 33/11 KV S/S | 725654.1445 | 693078.4919
175 | Thana | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
176 | Bot Tola Mazar | 11 | 0 | 0 | 1 | 30156751 | 32354152 | 2197401 | 1 | 0 | 2197401 | 2207948.9744 | Jigatola | BGB 33/11 KV S/S | 2074198.5352 | 1909183.4664
177 | Sikder Medical | 11 | 0 | 0 | 1 | 34515480 | 35690888 | 1175408 | 1 | 0 | 1175408 | 1181050.1989 | Jigatola | BGB 33/11 KV S/S | 1134381.9061 | 1138392.2283
178 | Gas Field | 11 | 0 | 0 | 1 | 51908120 | 53961540 | 2053420 | 1 | 0 | 2053420 | 2063276.8361 | Kamrangirchar | BGB 33/11 KV S/S | 2061072.7993 | 1985612.1672
179 | Hazaribagh | 11 | 0 | 0 | 1 | 38417940 | 39936160 | 1518220 | 1 | 0 | 1518220 | 1525507.7666 | Jigatola | BGB 33/11 KV S/S | 1485016.8997 | 1465699.7946
180 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
181 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | BGB 33/11 KV S/S | 0 | 0
182 | 11/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 0 | 1 | 2056.85 | 2117.04 | 60.19 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 0 | 0
183 | 11/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 0 | 1 | 1644.21 | 1699.35 | 55.14 | 10 | 0 | 0 | 0 | Azimpur | BGB 33/11 KV S/S | 0 | 0
184 | Salek Garden | 11 | 0 | 2761 | 1 | 549.1 | 593.11 | 44.01 | 60000 | 0 | 2640600 | 2650896.5462 | Jigatola | Jigatola New 33/11 KV S/S | 2562123.5191 | 2460950.9042
185 | Jigatola Local | 11 | 0 | 2850 | 1 | 438.35 | 469.67 | 31.32 | 60000 | 0 | 1879200 | 1886527.6034 | Jigatola | Jigatola New 33/11 KV S/S | 1807426.7227 | 1737565.9216
186 | City College | 11 | 0 | 2784 | 1 | 479.78 | 510.17 | 30.39 | 60000 | 0 | 1823400 | 1830510.0213 | Jigatola | Jigatola New 33/11 KV S/S | 1777383.0604 | 2346194.6487
187 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0
188 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0
189 | Post Office | 11 | 0 | 2836 | 1 | 358.58 | 386.41 | 27.83 | 60000 | 0 | 1669800 | 1676311.0857 | Jigatola | Jigatola New 33/11 KV S/S | 1671629.3692 | 1589764.671
190 | Leather Institute | 11 | 0 | 2835 | 1 | 57.38 | 58.33 | 0.95 | 60000 | 0 | 57000 | 57222.2613 | Jigatola | Jigatola New 33/11 KV S/S | 189875.9456 | 195265.8799
191 | Mina Bazar | 11 | 0 | 2853 | 1 | 181.89 | 194.57 | 12.68 | 60000 | 0 | 760800 | 763766.6032 | Jigatola | Jigatola New 33/11 KV S/S | 746284.571 | 706562.076
192 | Road-2 | 11 | 0 | 2839 | 1 | 584.66 | 624.12 | 39.46 | 60000 | 0 | 2367600 | 2376832.0316 | Jigatola | Jigatola New 33/11 KV S/S | 2301945.4038 | 2450136.1786
193 | SS-2 | 11 | 0 | 2838 | 1 | 272.32 | 291.23 | 18.91 | 60000 | 0 | 1134600 | 1139024.1692 | Jigatola | Jigatola New 33/11 KV S/S | 1127238.2087 | 1112715.1061
194 | Spare | 11 | 0 | 2772 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola New 33/11 KV S/S | 0 | 0
195 | Bou Bazar | 11 | 0 | 2843 | 1 | 471.44 | 502.69 | 31.25 | 60000 | 0 | 1875000 | 1882311.2263 | Jigatola | Jigatola New 33/11 KV S/S | 1850088.7231 | 1774816.6433
196 | BGB | 11 | 0 | 2764 | 1 | 169.64 | 179.28 | 9.64 | 60000 | 0 | 578400 | 580655.3671 | Jigatola | Jigatola New 33/11 KV S/S | 1007063.5596 | 934872.9509
197 | Dhamondi-12 | 11 | 0 | 2763 | 1 | 375.07 | 400.32 | 25.25 | 60000 | 0 | 1515000 | 1520907.4708 | Dhanmondi | Jigatola New 33/11 KV S/S | 1213163.0828 | 1602982.669
198 | Mitali Road | 11 | 0 | DHK66479 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
199 | Bou Bazar | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
200 | Mina Bazar | 11 | 0 | DHK | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
201 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
202 | Simanto Square | 11 | 0 | DHK60946 | 1 | 1125.53 | 1141.66 | 16.13 | 60000 | 0 | 967800 | 967800 | Jigatola | Jigatola Old 33/11KV S/S | 852145.3731 | 901151.3428
203 | Post Office | 11 | 0 | DHK61074 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
204 | Hazaribagh Sw/S-2 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
205 | Green Road Via Park | 11 | 0 | DHK61070 | 1 | 3415.05 | 3437.43 | 22.38 | 60000 | 0 | 1342800 | 1342800 | Jigatola | Jigatola Old 33/11KV S/S | 1229862.9154 | 476757.7712
206 | PWD Quarters 11 kV Saleq Grand | 11 | 0 | DHK61028 | 1 | 3629.4 | 3630.54 | 1.14 | 60000 | 0 | 68400 | 68400 | Jigatola | Jigatola Old 33/11KV S/S | 74813.6195 | 63933.0345
207 | Road No.-2 | 11 | 0 | DHK61035 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
208 | Hzaribagh O/H | 11 | 0 | DHK61033 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
209 | B.G.B | 11 | 0 | DHK61030 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
210 | 11 kV City College | 11 | 0 | DHK61031 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
211 | Jigatala Local | 11 | 0 | DHK61069 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Jigatola | Jigatola Old 33/11KV S/S | 0 | 0
212 | 33/0.4 kV Aux. Transformer AT-1 | 0.415 | 0 | 243284 | 1 | 83791 | 84159 | 368 | 10 | 0 | 3680 | 3680 | Jigatola | Jigatola Old 33/11KV S/S | 2585.0234 | 3440.2061
213 | 33/0.4 kV Aux. Transformer AT-2 | 0.415 | 0 | 412277 | 1 | 39498 | 39663 | 165 | 10 | 0 | 1650 | 1650 | Jigatola | Jigatola Old 33/11KV S/S | 5393.0685 | 0
214 | Spare | 11 | 0 | BD014030 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0
215 | D Block dhaka uddyan | 11 | 0 | BD014031 | 1 | 48613.5 | 48979.01 | 365.51 | 1000 | 0 | 365510 | 364723.8055 | Adabor | Dhaka Uddyan 33/11 KV S/S | 376392.0985 | 356370.9019
216 | Dill Mohammad O/H | 11 | 0 | BD014027 | 1 | 15908.7 | 17844.24 | 1935.54 | 1000 | 0 | 1935540 | 1931376.746 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1945233.0858 | 1925614.3584
217 | Turag O/H | 11 | 0 | BD014028 | 1 | 25472.56 | 26177.65 | 705.09 | 1000 | 0 | 705090 | 703573.3851 | Adabor | Dhaka Uddyan 33/11 KV S/S | 725059.1327 | 419185.0275
218 | Nabadoy O/H | 11 | 0 | BD014025 | 1 | 34907.65 | 35784.32 | 876.67 | 1000 | 0 | 876670 | 874784.3247 | Adabor | Dhaka Uddyan 33/11 KV S/S | 873886.7957 | 1264712.0241
219 | Chandrima O/H | 11 | 0 | BD014024 | 1 | 3855 | 4855.8 | 1000.8 | 1000 | 0 | 1000800 | 998647.327 | Adabor | Dhaka Uddyan 33/11 KV S/S | 974655.0029 | 879754.0777
220 | Shyamoli Housing Project-2 | 11 | 0 | BD014029 | 1 | 24761.38 | 26451.58 | 1690.2 | 1000 | 0 | 1690200 | 1686564.4606 | Adabor | Dhaka Uddyan 33/11 KV S/S | 1305126.5223 | 2226602.9518
221 | Spare | 11 | 0 | BD014022 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0
222 | Spare | 11 | 0 | BD014026 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0
223 | Spare | 11 | 0 | BD014023 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 0
224 | U Lab | 11 | 0 | BD013959 | 1 | 35792.66 | 37965.55 | 2172.89 | 1000 | 0 | 2172890 | 2168216.2175 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2766170.13 | 2585824.4138
225 | Akota | 11 | 0 | BD014020 | 1 | 5565.65 | 6085.32 | 519.67 | 1000 | 0 | 519670 | 518552.2147 | Adabor | Dhaka Uddyan 33/11 KV S/S | 529306.7232 | 494561.9781
226 | Burigonga O/H | 11 | 0 | BD014019 | 1 | 4279.01 | 4671.23 | 392.22 | 1000 | 0 | 392220 | 391376.3535 | Adabor | Dhaka Uddyan 33/11 KV S/S | 420977.1349 | 372374.7602
227 | Garden City | 11 | 0 | BD014021 | 1 | 81041.07 | 83851.34 | 2810.27 | 1000 | 0 | 2810270 | 2804225.2436 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 2395190.4943 | 2278829.2831
228 | Avenue O/H | 11 | 0 | BD014017 | 1 | 11977.96 | 12957.25 | 979.29 | 1000 | 0 | 979290 | 977183.594 | Adabor | Dhaka Uddyan 33/11 KV S/S | 966250.121 | 894892.5874
229 | Chand Uddyan | 11 | 0 | BD014018 | 1 | 7472.53 | 8233.6 | 761.07 | 1000 | 0 | 761070 | 759432.9748 | Satmasjid | Dhaka Uddyan 33/11 KV S/S | 732469.8888 | 645275.1572
230 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4416 | 1 | 1760.35 | 1797.78 | 37.43 | 100 | 0 | 3743 | 3734.949 | Adabor | Dhaka Uddyan 33/11 KV S/S | 3966.4616 | 1513.851
231 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4412 | 1 | 251.33 | 251.33 | 0 | 100 | 0 | 0 | 0 | Adabor | Dhaka Uddyan 33/11 KV S/S | 0 | 2409.7413
232 | Lalmatia O/H | 11 | 0 | DHK61042 | 1 | 3125.6 | 3147.3 | 21.7 | 60000 | 0 | 1302000 | 1300189.4979 | Satmasjid | Satmasjid 33/11KV S/S | 1240075.1783 | 1343819.1874
233 | Asad Avenue (South) | 11 | 0 | DHK 60999 | 1 | 2895.94 | 2897.6 | 1.66 | 60000 | 0 | 99600 | 99461.5008 | Satmasjid | Satmasjid 33/11KV S/S | 201384.8525 | 143036.2105
234 | Madrasha Road | 11 | 0 | DHK61004 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Shyamoli | Satmasjid 33/11KV S/S | 0 | 0
235 | Bashbari | 11 | 0 | DHK61002 | 1 | 2340.79 | 2370.58 | 29.79 | 60000 | 0 | 1787400 | 1784914.5226 | Satmasjid | Satmasjid 33/11KV S/S | 1599091.6268 | 1533732.8114
236 | Road-27 | 11 | 0 | DHK61001 | 1 | 1432.05 | 1438.38 | 6.33 | 60000 | 0 | 379800 | 379271.8673 | Satmasjid | Satmasjid 33/11KV S/S | 89903.952 | 435118.5562
237 | Boishakhi O/H | 11 | 0 | DHK61024 | 1 | 4043.27 | 4091.98 | 48.71 | 60000 | 0 | 2922600 | 2918535.965 | Dhanmondi | Satmasjid 33/11KV S/S | 3026167.0253 | 2814447.7883
238 | Katasur O/H | 11 | 0 | DHK61003 | 1 | 3581.57 | 3605.55 | 23.98 | 60000 | 0 | 1438800 | 1436799.27 | Satmasjid | Satmasjid 33/11KV S/S | 1431270.9163 | 1334804.3002
239 | Nurjahan Road | 11 | 0 | DHK61000 | 1 | 1793.34 | 1817.79 | 24.45 | 60000 | 0 | 1467000 | 1464960.0563 | Shyamoli | Satmasjid 33/11KV S/S | 1437863.8728 | 1376873.7739
240 | polpar over head | 11 | 0 | DHK61003 | 1 | 1761.42 | 1797.61 | 36.19 | 60000 | 0 | 2171400 | 2168380.5497 | Dhanmondi | Satmasjid 33/11KV S/S | 2135518.5405 | 2016930.7661
241 | Satmosjid Housing | 11 | 0 | DHK61043 | 1 | 2792.38 | 2802.53 | 10.15 | 60000 | 0 | 609000 | 608153.1522 | Satmasjid | Satmasjid 33/11KV S/S | 0 | 0
242 | Physical College | 11 | 0 | DHK61041 | 1 | 3216.68 | 3261.37 | 44.69 | 60000 | 0 | 2681400 | 2677671.3668 | Satmasjid | Satmasjid 33/11KV S/S | 2636583.2332 | 2184607.6683
243 | Asad Avenue (North) | 11 | 0 | DHK61022 | 1 | 2725.31 | 2725.37 | 0.06 | 60000 | 0 | 3600 | 3594.994 | Shyamoli | Satmasjid 33/11KV S/S | 0 | 0
244 | Spare Feeder | 11 | 0 | DHK61025 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Satmasjid | Satmasjid 33/11KV S/S | 0 | 0
245 | Ghraphic artch college | 11 | 0 | DHK61023 | 1 | 1042.11 | 1069.16 | 27.05 | 60000 | 0 | 1623000 | 1620743.1298 | Dhanmondi | Satmasjid 33/11KV S/S | 1570921.7218 | 1701409.7136
246 | Mohammadpur O/H | 11 | 0 | DHK61025 | 1 | 2132.57 | 2160.67 | 28.1 | 60000 | 0 | 1686000 | 1683655.5249 | Shyamoli | Satmasjid 33/11KV S/S | 1660825.6738 | 1343218.1949
247 | Bosila Feeder | 11 | 0 | DHK60997 | 1 | 4018.46 | 4059.26 | 40.8 | 60000 | 0 | 2448000 | 2444595.9223 | Satmasjid | Satmasjid 33/11KV S/S | 2900301.4925 | 3015179.277
248 | 11/0.4 kV Auxiliary Transformer | 0.415 | 0 | ELIB 7375 | 1 | 5560.3 | 5698.37 | 138.07 | 60 | 0 | 8284.2 | 8272.6804 | Satmasjid | Satmasjid 33/11KV S/S | 8691.9141 | 0
249 | Dhaka Uddyan | 11 | 0 | DHK86067 | 1 | 3249.81 | 3250.6 | 0.79 | 60000 | 0 | 47400 | 47362.5115 | Adabor | Japan Garden 33/11 KV | 34177.6075 | 0
250 | Shia Mosjid | 11 | 0 | DHK60950 | 1 | 3392.62 | 3431.26 | 38.64 | 60000 | 0 | 2318400 | 2316566.3838 | Shyamoli | Japan Garden 33/11 KV | 2321079.2736 | 1677029.4105
251 | Shekhar Tek | 11 | 0 | DHK60977 | 1 | 2311.48 | 2346.34 | 34.86 | 60000 | 0 | 2091600 | 2089945.7593 | Adabor | Japan Garden 33/11 KV | 2160384.5576 | 1966584.1503
252 | Madrasha Road | 11 | 0 | DHK61083 | 1 | 1945.1 | 1969.45 | 24.35 | 60000 | 0 | 1461000 | 1459844.4991 | Shyamoli | Japan Garden 33/11 KV | 1147648.0831 | 1148666.6379
253 | Baitul Aman Housing | 11 | 0 | DHK668115 | 1 | 4021.57 | 4071 | 49.43 | 60000 | 0 | 2965800 | 2963454.3569 | Adabor | Japan Garden 33/11 KV | 2980047.5303 | 2714650.3131
254 | Shyamoli Square | 11 | 0 | DHK86063 | 1 | 452.52 | 458.1 | 5.58 | 30000 | 0 | 167400 | 167267.6038 | Shyamoli | Japan Garden 33/11 KV | 170888.0374 | 163284.9924
255 | Mohammadi Housing | 11 | 0 | DHK60948 | 1 | 3751.71 | 3785.19 | 33.48 | 60000 | 0 | 2008800 | 2007211.2456 | Adabor | Japan Garden 33/11 KV | 1954719.3056 | 1343295.1846
256 | Chand Housing | 11 | 0 | DHK60867 | 1 | 2147.7 | 2161.88 | 14.18 | 60000 | 0 | 850800 | 850127.1046 | Satmasjid | Japan Garden 33/11 KV | 960570.6526 | 891350.9825
257 | PC Culture Housing | 11 | 0 | DHK60979 | 1 | 4021.99 | 4067.35 | 45.36 | 60000 | 0 | 2721600 | 2719447.494 | Adabor | Japan Garden 33/11 KV | 2646665.9554 | 2456140.6176
258 | Mehedibagh | 11 | 0 | DHK68121 | 1 | 2208.55 | 2259.27 | 50.72 | 60000 | 0 | 3043200 | 3040793.1415 | Adabor | Japan Garden 33/11 KV | 3013625.5306 | 2845397.7111
259 | 33/11 kV Incoming (Spare) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 160000 | 0 | 0 | 0 | Adabor | Japan Garden 33/11 KV | 0 | 0
260 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | 0 | 1 | 642363 | 647547 | 5184 | 1 | 0 | 5184 | 5179.9 | Adabor | Japan Garden 33/11 KV | 5393.4663 | 0
261 | Mokarom Bhabon | 11 | 0 | 2761 | 1 | 46.92 | 50 | 3.08 | 60000 | 0 | 184800 | 186304.8566 | Ramna | Dhaka University 33/11 KV S/S | 168036.2342 | 191876.7922
262 | 11 kV Shaid Minar RMU | 11 | 0 | 2850 | 1 | 110.73 | 116.8 | 6.07 | 60000 | 0 | 364200 | 367165.7402 | Ramna | Dhaka University 33/11 KV S/S | 336672.5979 | 339844.4752
263 | 11 kV Shaidulla Hall | 11 | 0 | 2851 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0 | 0
264 | Spare | 11 | 0 | 2784 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
265 | Spare | 11 | 0 | 2799 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
266 | Spare | 11 | 0 | 2775 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
267 | MBA Bhabon | 11 | 0 | 2836 | 1 | 86.15 | 90.5 | 4.35 | 60000 | 0 | 261000 | 263125.3657 | Ramna | Dhaka University 33/11 KV S/S | 250253.9631 | 301348.8178
268 | Suprime Court | 11 | 0 | 2835 | 1 | 44.16 | 50 | 5.84 | 60000 | 0 | 350400 | 353253.3645 | Ramna | Dhaka University 33/11 KV S/S | 298264.3158 | 306762.2696
269 | Karjon Hall | 11 | 0 | 2853 | 1 | 50.23 | 55.9 | 5.67 | 60000 | 0 | 340200 | 342970.3043 | Ramna | Dhaka University 33/11 KV S/S | 313267.551 | 333228.0341
270 | Spare | 11 | 0 | 2852 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
271 | Swimming Pool | 11 | 0 | 2839 | 1 | 0.8 | 0.8 | 0 | 60000 | 0 | 0 | 0 | Ramna | Dhaka University 33/11 KV S/S | 0 | 0
272 | Spare | 11 | 0 | 2838 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
273 | Police Head Quarter RMU | 11 | 0 | 2772 | 1 | 62.93 | 72.1 | 9.17 | 60000 | 0 | 550200 | 554680.3686 | Ramna | Dhaka University 33/11 KV S/S | 488505.3381 | 444504.5437
274 | Spare | 11 | 0 | 2843 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
275 | Spare | 11 | 0 | 2764 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
276 | Spare | 11 | 0 | 2763 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Dhaka University 33/11 KV S/S | 0 | 0
277 | Segunbagicha | 11 | 0 | DHK-C9360 | 1 | 71954 | 82917.41 | 10963.41 | 60 | 0 | 657804.6 | 660791.8145 | Ramna | Biddyut Bhaban 33/11 KV | 648570.0837 | 628132.1417
278 | Secretariat RMU | 11 | 0 | DHK-C9379 | 1 | 68931.7 | 71809.95 | 2878.25 | 60 | 0 | 172695 | 173479.2405 | Ramna | Biddyut Bhaban 33/11 KV | 157347.3651 | 189151.3106
279 | NBR RMU | 11 | 0 | DHK-C9319 | 1 | 43622.4 | 51570.08 | 7947.68 | 60 | 0 | 476860.8 | 479026.3146 | Ramna | Biddyut Bhaban 33/11 KV | 471677.0943 | 454185.7713
280 | Ramna 11 kV Sw/S-2 | 11 | 0 | DHK-C9364 | 1 | 99344.1 | 108506.79 | 9162.69 | 60 | 0 | 549761.4 | 552257.97 | Ramna | Biddyut Bhaban 33/11 KV | 1047973.9631 | 1309281.295
281 | Ramna 11 kV Sw/S-1 | 11 | 0 | DHK-C9375 | 1 | 30685.5 | 46623.88 | 15938.38 | 60 | 0 | 956302.8 | 960645.5509 | Ramna | Biddyut Bhaban 33/11 KV | 37569.2064 | 3932.094
282 | Family Planning | 11 | 0 | DHK-C9378 | 1 | 41466 | 49313.12 | 7847.12 | 60 | 0 | 470827.2 | 472965.3149 | Ramna | Biddyut Bhaban 33/11 KV | 459978.3897 | 450311.5022
283 | Muktijuddho Montranalaya | 11 | 0 | DHK-C9376 | 1 | 26269.1 | 42919.82 | 16650.72 | 60 | 0 | 999043.2 | 1003580.0431 | Ramna | Biddyut Bhaban 33/11 KV | 989924.3443 | 925250.3935
284 | Purana Palton | 11 | 0 | DHK-C9318 | 1 | 43328.3 | 49147.44 | 5819.14 | 60 | 0 | 349148.4 | 350733.9486 | Ramna | Biddyut Bhaban 33/11 KV | 318744.0733 | 328976.7665
285 | Tip Top Feeder | 11 | 0 | DHK-C9318 | 1 | 66509.6 | 89567.58 | 23057.98 | 60 | 0 | 1383478.8 | 1389761.4375 | Kakrail | Biddyut Bhaban 33/11 KV | 1427034.1549 | 1299449.2529
286 | 11/0.4 kV Auxiliary Transformer, AT | 0.415 | 0 | DHKD3784 | 1 | 336257 | 341182 | 4925 | 1 | 0 | 4925 | 4947.3654 | Ramna | Biddyut Bhaban 33/11 KV | 4696.0253 | 4800.6724
287 | Nearest O/H | 11 | 0 | 00000126 | 1 | 7074262 | 7294622 | 220360 | 1 | 0 | 220360 | 224820.1739 | Ramna | DMC 33/11 KV SS | 210729.7741 | 229906.9253
288 | Jagannath Hall | 11 | 0 | 00000002 | 1 | 2545753.8 | 2654153 | 108399.2 | 1 | 0 | 108399.2 | 110593.2428 | Ramna | DMC 33/11 KV SS | 113276.1711 | 96242.8599
289 | Samsun Nahar Hall | 11 | 0 | 00000024 | 1 | 9054018 | 9370297 | 316279 | 1 | 0 | 316279 | 322680.6125 | Ramna | DMC 33/11 KV SS | 293593.2672 | 312413.2678
290 | Spare, 4L | 11 | 0 | 00000184 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0 | 0
291 | Board Office O/H, (5L) | 11 | 0 | 00000023 | 1 | 20726990 | 21315228 | 588238 | 1 | 0 | 588238 | 600144.1706 | Lalbag | DMC 33/11 KV SS | 492983.2953 | 466712.6927
292 | OT- Complex | 11 | 0 | 00000167 | 1 | 5711026 | 6148345 | 437319 | 1 | 0 | 437319 | 446170.5101 | Ramna | DMC 33/11 KV SS | 427837.7768 | 405707.0733
293 | Alia Mdrasha O/H, (7L) | 11 | 0 | 00000148 | 1 | 9318217 | 9394377 | 76160 | 1 | 0 | 76160 | 77701.5086 | Lalbag | DMC 33/11 KV SS | 75154.3226 | 71193.4446
294 | Majed Sordar Road | 11 | 0 | 00000164 | 1 | 53489908 | 55060864 | 1570956 | 1 | 0 | 1570956 | 1602752.7729 | Bangshal | DMC 33/11 KV SS | 1759301.3409 | 1689289.8138
295 | Chankharpool, 9L | 11 | 0 | 00000001 | 1 | 45648168 | 46801764 | 1153596 | 1 | 0 | 1153596 | 1176945.2408 | Bangshal | DMC 33/11 KV SS | 1201456.0712 | 1157798.1959
296 | Shahidullah College O/H, (10L) | 11 | 0 | 00000003 | 1 | 12584169 | 12842169 | 258000 | 1 | 0 | 258000 | 263222.0224 | Lalbag | DMC 33/11 KV SS | 263967.4494 | 265403.8751
297 | Ananda Bazar | 11 | 0 | 00000111 | 1 | 14714284 | 14878044 | 163760 | 1 | 0 | 163760 | 167074.5674 | Ramna | DMC 33/11 KV SS | 216784.0965 | 169141.9631
298 | Hosseni Dalan O/H, (12L) | 11 | 0 | 0 | 1 | 23.41 | 50.74 | 27.33 | 60000 | Estimated | 1146913.2 | 1170127.1783 | Lalbag | DMC 33/11 KV SS | 1629339.2554 | 1651805.4359
299 | Badrun Nessa College | 11 | 0 | 00000006 | 1 | 19009274 | 19521592 | 512318 | 1 | 0 | 512318 | 522687.5196 | Lalbag | DMC 33/11 KV SS | 511348.0734 | 487810.3149
300 | Dhaka Medical College, Unit-II | 11 | 0 | 00000125 | 1 | 11353372 | 11679371 | 325999 | 1 | 0 | 325999 | 332597.3491 | Ramna | DMC 33/11 KV SS | 314783.3957 | 318669.3545
301 | Spare, 15L | 11 | 0 | 00000163 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | DMC 33/11 KV SS | 0 | 0
302 | Sheikh Hasina National Burn Institute | 11 | 0 | 00000127 | 1 | 19677112 | 20301830 | 624718 | 1 | 0 | 624718 | 637362.5402 | Ramna | DMC 33/11 KV SS | 594088.462 | 527600.9918
303 | Aux. Transformer, AT-1 | 0.415 | 0 | DHKF-7804 | 1 | 2551.19 | 2637.73 | 86.54 | 100 | 0 | 8654 | 8829.1604 | Ramna | DMC 33/11 KV SS | 8254.0596 | 7320.9952
304 | Aux. Transformer, AT-2 | 0.415 | 0 | DHKF-7802 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | Ramna | DMC 33/11 KV SS | 0 | 0
305 | Secratariet East | 11 | 0 | BD 013966 | 1 | 3406.54 | 3666.02 | 259.48 | 1000 | 0 | 259480 | 260076.7434 | Ramna | BB Aveneu 33/11 KV S/S | 245293.0009 | 245463.3743
306 | Taher Bag O/H | 11 | 0 | BD 014045 | 1 | 17659.83 | 18336.98 | 677.15 | 1000 | 0 | 677150 | 678707.287 | Narinda | BB Aveneu 33/11 KV S/S | 744464.9674 | 740283.3012
307 | Al Raji Complex | 11 | 0 | BD 013983 | 1 | 12982.02 | 13753.92 | 771.9 | 1000 | 0 | 771900 | 773675.1898 | Ramna | BB Aveneu 33/11 KV S/S | 784809.8778 | 793405.3649
308 | Raduni | 11 | 0 | BD 013999 | 1 | 26506.32 | 27128.05 | 621.73 | 1000 | 0 | 621730 | 623159.8339 | Ramna | BB Aveneu 33/11 KV S/S | 1293358.488 | 1280815.0384
309 | Sundor Bon Square O/H | 11 | 0 | BD 013954 | 1 | 12263.75 | 12696.85 | 433.1 | 1000 | 0 | 433100 | 434096.0289 | Narinda | BB Aveneu 33/11 KV S/S | 473931.0551 | 515871.5523
310 | Shromo Bhobon O/H | 11 | 0 | BD 013985 | 1 | 12112.38 | 12636.31 | 523.93 | 1000 | 0 | 523930 | 525134.9167 | Ramna | BB Aveneu 33/11 KV S/S | 505142.6077 | 521299.6391
311 | Nawabpur Road | 11 | 0 | BD 013953 | 1 | 18556.72 | 19355.25 | 798.53 | 1000 | 0 | 798530 | 800366.4326 | Narinda | BB Aveneu 33/11 KV S/S | 843066.7121 | 849749.7199
312 | Spair | 11 | 0 | BD 013991 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0
313 | Spare | 11 | 0 | BD 013942 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0
314 | Ahad Police Box | 11 | 0 | BD 013984 | 1 | 10306.68 | 10672.48 | 365.8 | 1000 | 0 | 365800 | 366641.2546 | Ramna | BB Aveneu 33/11 KV S/S | 470281.7667 | 423970.1788
315 | Nearest O/H | 11 | 0 | BD 013997 | 1 | 2390.76 | 2505.26 | 114.5 | 1000 | 0 | 114500 | 114763.3233 | Ramna | BB Aveneu 33/11 KV S/S | 117912.5625 | 115595.8875
316 | Natab Bhaban | 11 | 0 | BD 014000 | 1 | 4625.24 | 4804.84 | 179.6 | 1000 | 0 | 179600 | 180013.0381 | Ramna | BB Aveneu 33/11 KV S/S | 185708.2311 | 177165.0302
317 | Spare | 11 | 0 | BD 014043 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | BB Aveneu 33/11 KV S/S | 0 | 0
318 | Awami League Party Office | 11 | 0 | BD 013956 | 1 | 1404.54 | 1408.1 | 3.56 | 1000 | 0 | 3560 | 3568.1872 | Ramna | BB Aveneu 33/11 KV S/S | 9417.1914 | 9250.1106
319 | Khaddar Bazar | 11 | 0 | BD 014012 | 1 | 9317.61 | 9709.64 | 392.03 | 1000 | 0 | 392030 | 392931.5775 | Ramna | BB Aveneu 33/11 KV S/S | 394275.1992 | 392631.6173
320 | Bangobondu National Stidium | 11 | 0 | BD 014008 | 1 | 6146.93 | 6536.3 | 389.37 | 1000 | 0 | 389370 | 390265.4601 | Ramna | BB Aveneu 33/11 KV S/S | 288658.7112 | 290128.194
321 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKH4418 | 1 | 1124.63 | 1124.63 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 0 | 1718.8942
322 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHKH4413 | 1 | 41.9 | 41.9 | 0 | 100 | 0 | 0 | 0 | Ramna | BB Aveneu 33/11 KV S/S | 0 | 387.2849
323 | 11 KV Ring Road Feeder | 11 | 0 | 77816675 | 1 | 41775.56 | 41923.11 | 147.55 | 8000 | 0 | 1180400 | 1209910 | Adabor | Kallyanpur 33/11KV S/S | 1172682 | 1124384
324 | 11 KV Gano Bhavan RMU | 11 | 0 | DHK14997 | 1 | 995.71 | 995.74 | 0.03 | 40000 | 0 | 1200 | 1230 | Shere b.nagar | Kallyanpur 33/11KV S/S | 1230 | 1230
325 | 11 KV Adabor O/H | 11 | 0 | DHK14957 | 1 | 4371.7 | 4419.91 | 48.21 | 40000 | 0 | 1928400 | 1976610 | Adabor | Kallyanpur 33/11KV S/S | 2150040 | 2995460
326 | 11 KV Goidertek (DPDC) | 11 | 0 | DHK14996 | 1 | 9355.62 | 9369.92 | 14.3 | 40000 | 0 | 572000 | 586300 | Adabor | Kallyanpur 33/11KV S/S | 591220 | 558420
327 | 11 KV Beribandh Feeder. | 11 | 0 | DHK14960 | 1 | 9640.43 | 9646.16 | 5.73 | 40000 | 0 | 229200 | 234930 | Adabor | Kallyanpur 33/11KV S/S | 301350 | 184500
328 | 11 KV Sewarage Pump | 11 | 0 | DHK14959 | 1 | 2054.75 | 2112.81 | 58.06 | 40000 | 0 | 2322400 | 2380460 | Adabor | Kallyanpur 33/11KV S/S | 2601450 | 535870
329 | 11 KV Technical School (DPDC) | 11 | 0 | DHK15019 | 1 | 8133.47 | 8192.03 | 58.56 | 40000 | 0 | 2342400 | 2400960 | Adabor | Kallyanpur 33/11KV S/S | 2347660 | 2184890
330 | 11 KV Mansurabad | 11 | 0 | 77816681 | 1 | 51616.27 | 51898.42 | 282.15 | 8000 | 0 | 2257200 | 2313630 | Adabor | Kallyanpur 33/11KV S/S | 2379804 | 2220888
331 | 11 kV Doctor's Lane | 11 | T-1 | 21100462 | 1 | 40404.3 | 40464.9 | 60.6 | 1000 | 0 | 60600 | 65016.8533 | Moghbazar | Moghbazar 33/11KV S/S | 1691.4448 | 1119.369
332 | 11 kV T&T O/H Feeder | 11 | T-1 | 21100473 | 1 | 80555.5 | 80645.6 | 90.1 | 1000 | 0 | 90100 | 96666.9717 | Tejgaon | Moghbazar 33/11KV S/S | 802696.2793 | 1023306.7911
333 | 11 kV Acore Ice Feeder (TEJ) | 11 | T-1 | 21101043 | 1 | 157212.8 | 157212.8 | 0 | 1000 | 0 | 0 | 0 | Tejgaon | Moghbazar 33/11KV S/S | 0 | 1589911.0287
334 | 11 kV Tejgaon S/S-1 | 11 | T-1 | 30/11004-1101 | 1 | 119107.7 | 119512.5 | 404.8 | 1000 | 0 | 404800 | 434303.9973 | Tejgaon | Moghbazar 33/11KV S/S | 326660.2796 | 342221.6327
335 | 11 kV Madhubagh | 11 | T-2 | 30/11003-1101 | 1.027 | 23721.6 | 23721.6 | 0 | 1000 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0
336 | 11 kV Iskaton | 11 | T-3 | 30/11006-1101 | 1 | 117632.1 | 119411.5 | 1779.4 | 1000 | 0 | 1779400 | 1909092.2251 | Kakrail | Moghbazar 33/11KV S/S | 1919578.4326 | 1819483.4353
337 | 11KV Ambagan | 11 | T-1 | 21101054 | 1 | 122850.8 | 125254.8 | 2404 | 1000 | 0 | 2404000 | 2579216.4264 | Moghbazar | Moghbazar 33/11KV S/S | 2455343.5773 | 1989016.959
338 | 11 kV Moghbazar Nearest | 11 | T-2 | 30/11005-1101 | 1 | 142744.5 | 144229.5 | 1485 | 1000 | 0 | 1485000 | 1593234.7726 | Tejgaon | Moghbazar 33/11KV S/S | 1205154.4296 | 1055666.7314
339 | 11 kV Vumi Bhaban | 11 | T-3 | 21101039 | 1 | 8423.8 | 8577.9 | 154.1 | 1000 | 0 | 154100 | 165331.6353 | Tejgaon | Moghbazar 33/11KV S/S | 136267.0228 | 122011.2214
340 | 11 kV MP Suite Feeder | 11 | T-2 | 30/11010-1101 | 1 | 9488.7 | 9654.6 | 165.9 | 1000 | 0 | 165900 | 177991.6827 | Tejgaon | Moghbazar 33/11KV S/S | 170095.919 | 154167.6401
341 | 11 kV Bangla Motor | 11 | T-2 | 202006983 | 1 | 120465.9 | 122581.3 | 2115.4 | 1000 | 0 | 2115400 | 2269581.709 | Kakrail | Moghbazar 33/11KV S/S | 2138303.3901 | 1962152.1029
342 | 11 kV Ispahani Feeder | 11 | T-3 | 21101021 | 1 | 82976.9 | 84471.2 | 1494.3 | 1000 | 0 | 1494300 | 1603212.6065 | Tejgaon | Moghbazar 33/11KV S/S | 1595983.8968 | 78254.0694
343 | 11 kV Kunipara Feeder | 11 | T-2 | 30/11007-1102 | 1 | 172255.3 | 173266.6 | 1011.3 | 1000 | 0 | 1011300 | 1085008.9734 | Tejgaon | Moghbazar 33/11KV S/S | 952812.0065 | 1869447.9972
344 | 11 kV Nayatola Feeder | 11 | T-3 | 2110137 | 1 | 122785.5 | 123156.6 | 371.1 | 1000 | 0 | 371100 | 398147.7603 | Moghbazar | Moghbazar 33/11KV S/S | 399920.9831 | 690345.3929
345 | 11 kV Garden Feeder (KAK) | 11 | T-3 | 21101000 | 1 | 112406.9 | 113333.9 | 927 | 1000 | 0 | 927000 | 994564.7368 | Kakrail | Moghbazar 33/11KV S/S | 950591.9851 | 944645.6784
346 | 11 kV BSRS Feeder | 11 | T-3 | 21100870 | 1 | 43325.7 | 43325.7 | 0 | 1000 | 0 | 0 | 0 | Kakrail | Moghbazar 33/11KV S/S | 0 | 323294.1205
347 | 11kV Moghbazar(old.buil) | 11 | T-3 | 21101247 | 1 | 19576.2 | 19576.2 | 0 | 1000 | 13371370.3506 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0
348 | 11 kV TCB Feeder | 11 | T-4 | 0 | 1 | 34661.4 | 35701.5 | 1040.1 | 1000 | 0 | 1040100 | 1091208.9552 | Kakrail | Moghbazar 33/11KV S/S | 1058026.2525 | 587067.814
349 | 11 kV Tejgaon SS-2 | 11 | T-4 | 0 | 1 | 28639.4 | 30139.8 | 1500.4 | 1000 | 0 | 1500400 | 1574127.4074 | Tejgaon | Moghbazar 33/11KV S/S | 1532552.8114 | 1481122.0985
350 | Holy Day Inn | 11 | T-4 | 0 | 1 | 28111.1 | 28111.1 | 0 | 1000 | According to AMR meter reading | 517320 | 542740.3295 | Tejgaon | Moghbazar 33/11KV S/S | 522630.1141 | 493817.3233
351 | Polly Bhabon-2 | 11 | T-4 | 0 | 1 | 18322 | 18361.1 | 39.1 | 1000 | Consumer meter damaged, 12 months average | 26592 | 27898.691 | Kakrail | Moghbazar 33/11KV S/S | 30058.9479 | 29444.1053
352 | Polly Bhabon-1 / ambarsaha mosjid | 11 | T-4 | 0 | 1 | 13294.2 | 15062.1 | 1767.9 | 1000 | 0 | 1767900 | 1854771.9565 | Kakrail | Moghbazar 33/11KV S/S | 1842884.7823 | 1860061.7445
353 | 11 kV Tejturibazar | 11 | T-4 | 0 | 1 | 129914.1 | 130665.9 | 751.8 | 1000 | 0 | 751800 | 788742.3253 | Kakrail | Moghbazar 33/11KV S/S | 776669.7972 | 731592.6735
354 | Songsad | 11 | T-4 | 0 | 1 | 2467.7 | 2920.7 | 453 | 1000 | 0 | 453000 | 475259.7411 | Shere b.nagar | Moghbazar 33/11KV S/S | 544550.7215 | 126381.9385
355 | Chennel 24 | 11 | T-4 | 0 | 1 | 7308.75 | 7312.34 | 3.59 | 1000 | 0 | 3590 | 3766.4072 | Moghbazar | Moghbazar 33/11KV S/S | 1700.7368 | 1164.858
356 | Sonargaon | 11 | T-4 | 0 | 1 | 38919 | 39618 | 699 | 1000 | 0 | 699000 | 733347.8124 | Kakrail | Moghbazar 33/11KV S/S | 844174.3497 | 839625.5215
357 | AT -1 | 0.415 | T-4 | 6603338 | 1 | 1565803 | 1565803 | 0 | 0.75 | 0 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 7215.9345
358 | AT -2 | 0.415 | T-4 | 6603849 | 1 | 969318 | 969318 | 0 | 0.75 | 7091863.6257 | 0 | 0 | Moghbazar | Moghbazar 33/11KV S/S | 0 | 0
359 | 11 kV post office | 11 | Kakril | DHK60950 | 1 | 133254 | 156809 | 23555 | 60 | 0 | 1413300 | 1410640.1386 | Kakrail | T&T 33/11 KV | 1413099.3422 | 1314936.3633
360 | 11 kV anarkoli | 11 | Kakril | DHK60977 | 1 | 399215 | 423860 | 24645 | 60 | 0 | 1478700 | 1475917.0544 | Kakrail | T&T 33/11 KV | 1466512.1688 | 1363050.3594
361 | 11 kV sonalibagh | 11 | Mogbazar | DHK61083 | 1 | 938252 | 944778 | 6526 | 60 | 0 | 391560 | 390823.0756 | Moghbazar | T&T 33/11 KV | 376350.3769 | 416269.8468
362 | 11 Kv desh tv | 11 | Mogbazar | DHK60948 | 1 | 1927455 | 1943262 | 15807 | 60 | 0 | 948420 | 946635.0529 | Moghbazar | T&T 33/11 KV | 901476.4809 | 862940.0791
363 | 11 Kv Btcl | 11 | Mogbazar | DHK86070 | 1 | 561.01 | 590.39 | 29.38 | 60000 | 0 | 1762800 | 1759482.372 | Moghbazar | T&T 33/11 KV | 1708010.1623 | 1630130.9123
364 | 11 kV century | 11 | Kakril | DHK60867 | 1 | 874964 | 885274 | 10310 | 60 | 0 | 618600 | 617435.7813 | Kakrail | T&T 33/11 KV | 612807.1598 | 591251.5937
365 | 11 kV cinema hall | 11 | Mogbazar | DHK60979 | 1 | 452115 | 470250 | 18135 | 60 | 0 | 1088100 | 1086052.1721 | Moghbazar | T&T 33/11 KV | 1077858.8375 | 1046359.7284
366 | 11 kV malibagh bazar | 11 | Khailgaon | DHK61106 | 1 | 669487 | 697644 | 28157 | 60 | 0 | 1689420 | 1686240.4748 | Khilgaon | T&T 33/11 KV | 1646555.4045 | 1662984.8723
367 | 11 kv Sherebangla | 11 | 0 | DHK60915 | 1 | 668842 | 694633 | 25791 | 60 | 0 | 1547460 | 1544547.6466 | Moghbazar | T&T 33/11 KV | 1416880.2502 | 1438632.4204
368 | 11 kV Nur Mosjid | 11 | Khailgaon | DHK60913 | 1 | 308967 | 320497 | 11530 | 60 | 0 | 691800 | 690498.0173 | Moghbazar | T&T 33/11 KV | 692746.3564 | 708065.6738
369 | Auxiliary | 0 | Export | U0004461 | 1 | 8028.17 | 8095.99 | 67.82 | 60 | 0 | 4069.2 | 4061.5417 | Moghbazar | T&T 33/11 KV | 3583.4605 | 3045.4245
370 | West Malibagh | 11 | Mogbazar | 30799488 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1033879.14 | 1038100.3806 | Moghbazar | Ullon local 33/11KV S/S | 1138226.0536 | 978294.9507
371 | Ullon | 11 | Mogbazar | 307994528 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1642043.34 | 1648747.6632 | Moghbazar | Ullon local 33/11KV S/S | 1617479.1288 | 1406298.9916
372 | Mohanagar | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1763676.18 | 1770877.1198 | Moghbazar | Ullon local 33/11KV S/S | 1677385.7633 | 1345155.5572
373 | Bagichartek | 11 | Mogbazar | 30799497 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1277144.82 | 1282359.2936 | Moghbazar | Ullon local 33/11KV S/S | 1317945.9568 | 1100581.8195
374 | Mirbagh | 11 | Mogbazar | 30799487 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1642043.34 | 1648747.6632 | Moghbazar | Ullon local 33/11KV S/S | 1557572.4944 | 1345155.5572
375 | West Rampura | 11 | Mogbazar | 2007-75111 | 1 | 0 | 0 | 0 | 60000 | Estimated | 1277144.82 | 1282359.2936 | Moghbazar | Ullon local 33/11KV S/S | 1377852.5912 | 1222868.6883
376 | Jilkanon | 11 | Mogbazar | 30799461 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0
377 | AT-1 | 11 | Export | 5395187 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0
378 | AT-2 | 11 | Export | 5379456 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Moghbazar | Ullon local 33/11KV S/S | 0 | 0
379 | Sobujbagh | 11 | Mugdapara | 34140453696 | 1 | 8.4955 | 10.3885 | 1.8929 | 1000000 | 0 | 1892944.4 | 1914129.2674 | Mugdapara | Madarteck 33/11KV S/S | 1830321.6533 | 1753548.1446
380 | Madertek | 11 | Mugdapara | D0086134 | 1 | 97494.4 | 99487.1 | 1992.7 | 1000 | 0 | 1992700 | 2015001.2811 | Mugdapara | Madarteck 33/11KV S/S | 1947058.9925 | 1858521.5132
381 | Rajarbagh | 11 | Mugdapara | 34140313076 | 1 | 7021.7968 | 8440.3928 | 1418.596 | 1000 | Calculated | 2014583.4653 | 2037129.655 | Mugdapara | Madarteck 33/11KV S/S | 2033626.6462 | 1264456.5681
382 | Goran | 11 | 0 | X1390296 | 1 | 26638.6 | 28663.4 | 2024.8 | 1000 | 0 | 2024800 | 2047460.5279 | Bashabo | Madarteck 33/11KV S/S | 1968306.9598 | 1851494.7743
383 | Dhakhingaon | 11 | Mugdapara | 34140313075 | 1 | 8205.6192 | 9771.1 | 1565.4808 | 1000 | 0 | 1565480.8 | 1583000.8619 | Mugdapara | Madarteck 33/11KV S/S | 1493157.2972 | 2039169.8043
384 | Manda | 11 | Maniknagar | XC570267 | 1 | 79747.1 | 79747.1 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Madarteck 33/11KV S/S | 373198.8946 | 881499.2996
385 | Green Model Town | 11 | Mugdapara | 34140453695 | 1 | 510.4637 | 744.7806 | 234.317 | 1000 | 0 | 234316.96 | 236939.3158 | Mugdapara | Madarteck 33/11KV S/S | 229733.5056 | 209712.5124
386 | Biswa Road | 11 | Mugdapara | 34140313080 | 1 | 2474.7662 | 3045.3432 | 570.577 | 1000 | 0 | 570577 | 576962.6065 | Mugdapara | Madarteck 33/11KV S/S | 679941.1966 | 331641.7074
387 | Mugdapara | 11 | 0 | X0854272 | 1 | 3786.4 | 3885.1 | 98.7 | 1000 | 0 | 98700 | 99804.6 | Maniknagar | Madarteck 33/11KV S/S | 280453.0279 | 256934.2344
388 | Singapur | 11 | 0 | X1390302 (N) | 1 | 31151.7 | 33574.1 | 2422.4 | 1000 | 0 | 2422400 | 2449510.2642 | Banosree | Madarteck 33/11KV S/S | 2359732.7837 | 2200082.1244
389 | Trimohony | 11 | 0 | X1390308 | 1 | 24527.3 | 26608.8 | 2081.5 | 1000 | 0 | 2081500 | 2104795.0854 | Banosree | Madarteck 33/11KV S/S | 2021980.735 | 1604947.893
390 | Mayakanon | 11 | Mugdapara | 34140313073 | 1 | 10561.687 | 12357.722 | 1796.035 | 1000 | 0 | 1796035 | 1816135.3069 | Mugdapara | Madarteck 33/11KV S/S | 1942171.9601 | 1839386.3794
391 | Ahmedbagh | 11 | Mugdapara | 34140453691 | 1 | 3952.1608 | 4655.1844 | 703.0236 | 1000 | 0 | 703023.6 | 710891.4812 | Mugdapara | Madarteck 33/11KV S/S | 850151.1099 | 596386.824
392 | Wasa Road | 11 | Mugdapara | 61903686 | 1 | 712365 | 720580 | 8215 | 200 | 0 | 1643000 | 1661387.6173 | Mugdapara | Madarteck 33/11KV S/S | 1892982.4123 | 480873.3471
393 | Nandipara | 11 | Mugdapara | 61903558 | 1 | 746576 | 754033 | 7457 | 200 | 0 | 1491400 | 1508090.9874 | Mugdapara | Madarteck 33/11KV S/S | 1450702.4488 | 298789.1572
394 | Nakhal Para Feeder | 11 | 0 | DHK60950 | 1 | 201859.3 | 228050.8 | 26191.5 | 60 | 0 | 1571490 | 1590100.5899 | Tejgaon | Tejgoan 33/11KV S/S | 1545202.0376 | 1536369.5556
395 | Badda-Meghna Feeder | 11 | 0 | DHK60979 | 1 | 888283.6 | 901418.5 | 13134.9 | 60 | 0 | 788094 | 797427.1133 | Tejgaon | Tejgoan 33/11KV S/S | 711868.0468 | 842649.7133
396 | Rasulbagh Feeder | 11 | 0 | DHK60948 | 1 | 961752.1 | 991762.3 | 30010.2 | 60 | 0 | 1800612 | 1821935.9992 | Tejgaon | Tejgoan 33/11KV S/S | 1845073.9247 | 1902151.6741
397 | Lukas | 11 | 0 | 8A021100948-02 | 1 | 64421346 | 66843300 | 2421954 | 1 | 0 | 2421954 | 2450636.3287 | Tejgaon | Tejgoan 33/11KV S/S | 2356930.5125 | 2345545.782
398 | PWD RMU | 11 | 0 | 0 | 1 | 652660.7 | 654515.2 | 1854.5 | 1 | 0 | 1854.5 | 1876.4622 | Tejgaon | Tejgoan 33/11KV S/S | 1825.2484 | 1757.0539
399 | Civil Aviation Feeder | 11 | 0 | DHK60977 | 1 | 791561.7 | 840529.6 | 48967.9 | 60 | 0 | 2938074 | 2972868.5519 | Tejgaon | Tejgoan 33/11KV S/S | 2843930.4649 | 2795399.6317
400 | Ahasanullah Eng. | 11 | 0 | DHK60867 | 1 | 859374.2 | 870599.2 | 11225 | 60 | 0 | 673500 | 681476.0179 | Tejgaon | Tejgoan 33/11KV S/S | 638085.1899 | 673101.4258
401 | New GMG Feeder | 11 | 0 | DHK61106 | 1 | 7264.2 | 46250.7 | 38986.5 | 60 | 0 | 2339190 | 2366892.1845 | Tejgaon | Tejgoan 33/11KV S/S | 2233355.6797 | 2281871.6214
402 | Shikajo | 11 | 0 | HA021101036-02 | 1 | 62704679 | 63571582 | 866903 | 1 | 0 | 866903 | 877169.4199 | Tejgaon | Tejgoan 33/11KV S/S | 833321.8823 | 756034.1648
403 | Kahinur | 11 | 0 | 0 | 1 | 496661.5 | 518848.9 | 22187.4 | 60 | 0 | 1331244 | 1347009.4431 | Tejgaon | Tejgoan 33/11KV S/S | 1251045.3402 | 1294083.2246
404 | Link road | 11 | 0 | 8A021100380-02 | 1 | 63919556 | 64330013 | 410457 | 1 | 0 | 410457 | 415317.8944 | Tejgaon | Tejgoan 33/11KV S/S | 416737.628 | 435428.3198
405 | Shanta | 11 | 0 | 0 | 1 | 299552.9 | 310614.7 | 11061.8 | 60 | 0 | 663708 | 671568.0547 | Tejgaon | Tejgoan 33/11KV S/S | 608607.1616 | 630895.3248
406 | Karnafuly Feeder | 11 | 0 | DHK61084 | 1 | 33696.3 | 34410.6 | 714.3 | 1000 | 0 | 714300 | 722759.1976 | Tejgaon | Tejgoan 33/11KV S/S | 686952.8872 | 738300.0364
407 | Butex | 11 | 0 | 0 | 1 | 892.3 | 991.5 | 99.2 | 1000 | 0 | 99200 | 100374.7899 | Tejgaon | Tejgoan 33/11KV S/S | 90006.1656 | 91610.1416
408 | OriON LAB | 11 | 0 | 0 | 1 | 8007550 | 8102262 | 94712 | 1 | 0 | 94712 | 95833.6401 | Tejgaon | Tejgoan 33/11KV S/S | 88588.4676 | 248723.2522
409 | Nina kabbo | 11 | 0 | 201101025-2 | 1 | 16563888 | 16842033 | 278145 | 1 | 0 | 278145 | 281438.971 | Tejgaon | Tejgoan 33/11KV S/S | 283127.915 | 99489.3009
410 | Satrong | 11 | 0 | HA021100515-2 | 1 | 89639487 | 91425148 | 1785661 | 1 | 0 | 1785661 | 1806807.9399 | Tejgaon | Tejgoan 33/11KV S/S | 1563100.3489 | 1367977.887
411 | South East RMU | 11 | 0 | 0 | 1 | 601.9 | 729.2 | 127.3 | 1000 | 0 | 127300 | 128807.568 | Tejgaon | Tejgoan 33/11KV S/S | 139045.3993 | 149070.967
412 | Rangs Bhaban | 11 | 0 | HA021100939-2 | 1 | 270974 | 432458 | 161484 | 1 | 0 | 161484 | 163396.3968 | Tejgaon | Tejgoan 33/11KV S/S | 151255.7649 | 161670.1139
413 | Babli | 11 | 0 | 0 | 1 | 54005.3 | 56089.7 | 2084.4 | 1000 | 0 | 2084400 | 2109084.7983 | Tejgaon | Tejgoan 33/11KV S/S | 2111815.0669 | 1541422.4274
414 | SPL | 11 | 0 | 0 | 1 | 3461.1 | 3911.5 | 450.4 | 1000 | 0 | 450400 | 455733.9249 | Tejgaon | Tejgoan 33/11KV S/S | 408962.9923 | 372268.4438
415 | DNCC Hospital | 11 | 0 | 0 | 1 | 13491.4 | 14537.1 | 1045.7 | 1000 | 0 | 1045700 | 1058083.8484 | Tejgaon | Tejgoan 33/11KV S/S | 992388.6083 | 965076.0343
416 | 11/.415 kv Local transformer | 0.415 | 0 | DHK61106 | 1 | 78.6 | 78.6 | 0 | 60 | 0 | 0 | 0 | Tejgaon | Tejgoan 33/11KV S/S | 6054.2264 | 6134.6077
417 | Gonobhaban | 11 | 0 | DHKC9332 | 1 | 69014.8 | 72755.2 | 3740.4 | 60 | 0 | 224424 | 226219.392 | Shere b.nagar | Asad Gate 33/11 KV S/S | 216875.2359 | 216836.1836
418 | Rapa Plaza Feeder | 11 | 0 | DHKC9339 | 1 | 56103.84 | 76499.17 | 20395.33 | 60 | 0 | 1223719.8 | 1233509.5584 | Dhanmondi | Asad Gate 33/11 KV S/S | 1199461.0668 | 1170856.0696
419 | Shukrabad/ South Plaza | 11 | 0 | DHKC9324 | 1 | 95989.52 | 115754.76 | 19765.24 | 60 | 0 | 1185914.4 | 1195401.7152 | Shere b.nagar | Asad Gate 33/11 KV S/S | 1120705.5276 | 1130327.1946
420 | Wasa O/H | 11 | 0 | DHKC9333 | 1 | 78543.28 | 100442.81 | 21899.53 | 60 | 0 | 1313971.8 | 1324483.5744 | Satmasjid | Asad Gate 33/11 KV S/S | 2118683.8855 | 1049087.4751
421 | Bangabandhu Memorial Museum | 11 | 0 | DHKC9334 | 1 | 15026.42 | 15376.97 | 350.55 | 60 | 0 | 21033 | 21201.264 | Dhanmondi | Asad Gate 33/11 KV S/S | 20854.3329 | 20897.995
422 | Iqbal Road O/H | 11 | 0 | DHKC9330 | 1 | 42849.53 | 72221.61 | 29372.08 | 60 | 0 | 1762324.8 | 1776423.3984 | Shyamoli | Asad Gate 33/11 KV S/S | 1626760.4818 | 1601413.1174
423 | Town Hall | 11 | 0 | DHKC9351 | 1 | 61880.78 | 100798.64 | 38917.86 | 60 | 0 | 2335071.6 | 2353752.1728 | Shyamoli | Asad Gate 33/11 KV S/S | 1991480.522 | 2338946.2013
424 | Post Office | 11 | 0 | DHKC9331 | 1 | 37135.17 | 64790.66 | 27655.49 | 60 | 0 | 1659329.4 | 1672604.0352 | Shyamoli | Asad Gate 33/11 KV S/S | 1378440.8932 | 1492441.2314
425 | Shangshad Bhaban | 11 | 0 | DHKC9370 | 1 | 6671.66 | 11515.28 | 4843.62 | 60 | 0 | 290617.2 | 292942.1376 | Shere b.nagar | Asad Gate 33/11 KV S/S | 474363.1372 | 422562.5169
426 | Jakir Hossain Road | 11 | 0 | DHKC9373 | 1 | 81724.89 | 108235.46 | 26510.57 | 60 | 0 | 1590634.2 | 1603359.2736 | Satmasjid | Asad Gate 33/11 KV S/S | 1792634.4006 | 1277863.2905
427 | New Colony O/H Feeder | 11 | 0 | DHKC9369 | 1 | 69251.43 | 86475.56 | 17224.13 | 60 | 0 | 1033447.8 | 1041715.3824 | Satmasjid | Asad Gate 33/11 KV S/S | 0 | 1328527.8719
428 | Aurangzeb Feeder | 11 | 0 | DHKC9321 | 1 | 42513.02 | 69565.32 | 27052.3 | 60 | 0 | 1623138 | 1636123.104 | Shyamoli | Asad Gate 33/11 KV S/S | 1847282.7847 | 2012075.4293
429 | Asadgate Local Feeder | 11 | 0 | DHKC9338 | 1 | 32726.29 | 67929.33 | 35203.04 | 60 | 0 | 2112182.4 | 2129079.8592 | Satmasjid | Asad Gate 33/11 KV S/S | 2381609.9379 | 1832840.2298
430 | Sonarbangla Road | 11 | 0 | DHKC9320 | 1 | 2967.97 | 2967.97 | 0 | 60 | 0 | 0 | 0 | Shyamoli | Asad Gate 33/11 KV S/S | 0 | 0
431 | Humayun Road | 11 | 0 | DHKC9366 | 1 | 47034.27 | 78786.74 | 31752.47 | 60 | 0 | 1905148.2 | 1920389.3856 | Shyamoli | Asad Gate 33/11 KV S/S | 263604.1533 | 1670349.266
432 | NHA | 11 | 0 | DHKC9374 | 1 | 52748.02 | 57115.39 | 4367.37 | 60 | 0 | 262042.2 | 264138.5376 | Shyamoli | Asad Gate 33/11 KV S/S | 26450.7883 | 221861.5773
433 | Auxiliary transformer | 0.415 | 0 | 0 | 1 | 633994 | 633994 | 0 | 1 | 0 | 0 | 0 | Satmasjid | Asad Gate 33/11 KV S/S | 7372.3763 | 6148.5505
434 | Angur Jora | 11 | 0 | 141 | 1 | 3861980 | 6021560 | 2159580 | 1 | 0 | 2159580 | 2182461.1184 | Banosree | Banasree 33/11 SS | 2168323.5267 | 1879685.8324
435 | Block F-G Avenue | 11 | 0 | 68 | 1 | 5519540 | 8177840 | 2658300 | 1 | 0 | 2658300 | 2686465.1418 | Banosree | Banasree 33/11 SS | 2772883.9436 | 2653782.5782
436 | Banasree Main Road(Monpura) | 11 | 0 | 168 | 1 | 4446260 | 6283880 | 1837620 | 1 | 0 | 1837620 | 1857089.8973 | Banosree | Banasree 33/11 SS | 1771391.1453 | 1640446.1666
437 | Baitul Kuddus | 11 | 0 | 62 | 1 | 7309220 | 9606640 | 2297420 | 1 | 0 | 2297420 | 2321761.5567 | Banosree | Banasree 33/11 SS | 2248090.2296 | 2090165.4312
438 | Ideal | 11 | 0 | 0 | 1 | 7487660 | 8292520 | 804860 | 1 | 0 | 804860 | 813387.6289 | Banosree | Banasree 33/11 SS | 785714.1589 | 730886.4987
439 | Central Mosque | 11 | 0 | 46 | 1 | 7813780 | 10042320 | 2228540 | 1 | #REF! | 2228540 | 2252151.7613 | Banosree | Banasree 33/11 SS | 2213991.1776 | 2027033.5767
440 | Larive | 11 | 0 | 47 | 1 | 8407420 | 9603880 | 1196460 | 1 | 0 | 1196460 | 1209136.6977 | Banosree | Banasree 33/11 SS | 1154817.1834 | 1075325.8802
441 | Bank Colony | 11 | 0 | 0 | 1 | 3914160 | 4697520 | 783360 | 1 | 0 | 783360 | 791659.8328 | Khilgaon | Banasree 33/11 SS | 743707.201 | 684269.1356
442 | Salambagh | 11 | 0 | 0 | 1 | 2367500 | 3153240 | 785740 | 1 | 0 | 785740 | 794065.0493 | Khilgaon | Banasree 33/11 SS | 937481.2326 | 1234217.735
443 | Titas Road | 11 | 0 | 0 | 1 | 1963420 | 2347080 | 383660 | 1 | 0 | 383660 | 387724.9431 | Khilgaon | Banasree 33/11 SS | 442215.7606 | 461564.0031
444 | AT-1 | 0.415 | 0 | 7734 | 1 | 3257.088 | 3332.3 | 75.212 | 1 | 0 | 75.212 | 76.0089 | Banosree | Banasree 33/11 SS | 145.5702 | 0
445 | AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Banosree | Banasree 33/11 SS | 0 | 0
446 | Meradia | 11 | 0 | HA-030701100-03 | 1 | 79299989 | 79299989 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0
447 | Shipahibagh | 11 | 0 | HA-021001030-02 | 1 | 36289191 | 37940830 | 1651639 | 1 | 0 | 1651639 | 1654071.9922 | Bashabo | Goran 33/11KV S/S | 1292900.8718 | 1411235.5236
448 | Farazi Hospital | 11 | 0 | HA-030701081-03 | 1 | 50450357 | 50450357 | 0 | 1 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0
449 | West Bansree | 11 | 0 | New Meter | 1 | 91131594 | 93104250 | 1972656 | 1 | 0 | 1972656 | 1975561.8751 | Banosree | Goran 33/11KV S/S | 1966878.4605 | 1837316.4777
450 | Model School(Nearest) | 11 | 0 | HA-030701099-03 | 1 | 15066081 | 17587620 | 2521539 | 1 | 0 | 2521539 | 2525253.4223 | Banosree | Goran 33/11KV S/S | 2475694.1412 | 2316464.2537
451 | Bhuiyan Para | 11 | 0 | HA-021100508-02 | 1 | 53101375 | 55705410 | 2604035 | 1 | 0 | 2604035 | 2607870.9453 | Banosree | Goran 33/11KV S/S | 2554505.4549 | 2408712.741
452 | Bonobithi (Ideal) School | 11 | 0 | HA-021100879-02 | 1 | 14133451 | 15718670 | 1585219 | 1 | 0 | 1585219 | 1587554.1504 | Banosree | Goran 33/11KV S/S | 1568260.1835 | 1428642.8767
453 | AT-01 | 0.415 | 0 | 3043122 | 1 | 7023.2 | 7023.2 | 0 | 80 | 0 | 0 | 0 | Banosree | Goran 33/11KV S/S | 0 | 0
454 | AT-02 | 0.415 | 0 | 3043146 | 1 | 4704.4 | 4782.5 | 78.1 | 80 | 0 | 6248 | 6257.2038 | Banosree | Goran 33/11KV S/S | 5424.4075 | 4669.3803
455 | Shankor O/H | 11 | Export | HA-021100932-02 | 1 | 5900445 | 5900445 | 0 | 1 | 138 | 1678533.192 | 1695740.7049 | Dhanmondi | Lalmatia 33/11KV S/S | 1418643.1678 | 1399733.2864
456 | Bangabobondhu museum | 11 | Export | 0 | 1 | 627449 | 627449 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0 | 0
457 | Road No-13/A | 11 | Export | 202006950 | 1 | 78185685 | 80492544 | 2306859 | 1 | 0 | 2306859 | 2330507.8061 | Dhanmondi | Lalmatia 33/11KV S/S | 2062161.6863 | 2160918.3029
458 | Jaforabad | 11 | Export | DHK00163 | 1 | 99151250 | 100978738 | 1827488 | 1 | 0 | 1827488 | 1846222.5257 | Dhanmondi | Lalmatia 33/11KV S/S | 2324395.3174 | 2181617.4346
459 | Asadgate U/G | 11 | Export | DHK00174 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Dhanmondi | Lalmatia 33/11KV S/S | 0 | 0
460 | Road 32 ( Lalmatia 11 kV S/S) | 11 | Export | DHK00175 | 1 | 25444.9 | 25639.6 | 194.7 | 3333.33 | 0 | 648999.351 | 655652.5794 | Dhanmondi | Lalmatia 33/11KV S/S | 676925.663 | 643438.6457
461 | Road No -15 | 11 | Export | DHK00162 | 1 | 69354.4 | 69712.4 | 358 | 3333.33 | 0 | 1193332.14 | 1205565.6057 | Dhanmondi | Lalmatia 33/11KV S/S | 1637075.4163 | 1478674.7103
462 | Road No-27 South | 11 | Export | DHK00161 | 1 | 77227.8 | 77687.3 | 459.5 | 3333.33 | 0 | 1531665.135 | 1547367.0274 | Dhanmondi | Lalmatia 33/11KV S/S | 1547019.5294 | 1459995.3095
463 | Road 25 | 11 | Export | 0 | 1 | 69810.6 | 70235.1 | 424.5 | 3333.3 | 0 | 1414985.85 | 1429491.6026 | Dhanmondi | Lalmatia 33/11KV S/S | 1320696.1949 | 1108412.3257
464 | Ibne Sina | 11 | Export | DHK00165 | 1 | 37703.6 | 37836.9 | 133.3 | 3333.33 | 0 | 444332.889 | 448887.9755 | Dhanmondi | Lalmatia 33/11KV S/S | 428853.4986 | 403274.921
465 | Road No-31 (PARI) | 11 | Export | HA-021100490-02 | 1 | 59045605 | 60236116 | 1190511 | 1 | 0 | 1190511 | 1202715.5447 | Dhanmondi | Lalmatia 33/11KV S/S | 1761856.4725 | 924073.8841
466 | Satmoszid Road West | 11 | Export | HA-021101031-02 | 1 | 67161693 | 69402203 | 2240510 | 1 | 0 | 2240510 | 2263478.6281 | Dhanmondi | Lalmatia 33/11KV S/S | 2215613.0537 | 2070071.1797
467 | Lab aid/local RMU | 11 | 0 | 3C65883 | 1 | 54004 | 59173 | 5169 | 300 | 0 | 1550700 | 1556841.7376 | Paribag | Green Road 33/11KV S/S | 1536617.643 | 1422394.5672
468 | Green View | 11 | 0 | DHK000151 | 1 | 66871.1 | 67239.7 | 368.6 | 3333.33 | 0 | 1228665.438 | 1233531.7182 | Paribag | Green Road 33/11KV S/S | 1202336.4681 | 1154869.3417
469 | Central Road | 11 | 0 | 65943 | 1 | 15582 | 21383 | 5801 | 300 | 0 | 1740300 | 1747192.6716 | Paribag | Green Road 33/11KV S/S | 1761466.4931 | 1692090.5953
470 | New Market | 11 | 0 | DHK000194 | 1 | 46255.4 | 46585.3 | 329.9 | 3333.33 | 0 | 1099665.567 | 1104020.9274 | Jigatola | Green Road 33/11KV S/S | 1190965.2748 | 1011316.673
471 | DPH Feeder | 11 | 0 | HA-021100459 | 1 | 41476.6 | 41611.3 | 134.7 | 1 | 20 | 243265.68 | 244229.1636 | Paribag | Green Road 33/11KV S/S | 236205.0715 | 247670.0176
472 | Dhanmondi Rd 4(md Banglo | 11 | 0 | 6604464 | 1 | 4476.72 | 4502.72 | 26 | 60000 | 0 | 1560000 | 1566178.5714 | Jigatola | Green Road 33/11KV S/S | 1573640.9477 | 1319464.1465
473 | Green Road East | 11 | 0 | HA-021101050 | 1 | 93757224 | 95327346 | 1570122 | 1 | 0 | 1570122 | 1576340.6608 | Paribag | Green Road 33/11KV S/S | 1533242.4019 | 1471624.0188
474 | North Road | 11 | 0 | HA-021100884 | 1 | 78525314 | 80273857 | 1748543 | 1 | 0 | 1748543 | 1755468.3191 | Paribag | Green Road 33/11KV S/S | 1721328.8161 | 1634915.8518
475 | Green road SS | 11 | 0 | DHK00135 | 1 | 17244056 | 18489919 | 1245863 | 1 | 0 | 1245863 | 1250797.3933 | Paribag | Green Road 33/11KV S/S | 1224610.5159 | 1315498.6273
476 | Plane Moszid | 11 | 0 | HA-021100962 | 1 | 0 | 0 | 0 | 1 | 80 | 973062.72 | 976916.6543 | Paribag | Green Road 33/11KV S/S | 944820.2858 | 990680.0705
477 | Malancha | 11 | 0 | HA-021100953 | 1 | 31976092 | 33261839 | 1285747 | 1 | 0 | 1285747 | 1290839.3587 | Paribag | Green Road 33/11KV S/S | 1378192.0129 | 1148505.9825
478 | AT -1 | 0 | 0 | 0 | 0 | 22891 | 22891 | 0 | 1 | 0 | 5000 | 5019.8031 | Paribag | Green Road 33/11KV S/S | 5016.7079 | 5090.5253
479 | North Dhanmondi | 11 | 0 | BD 014039 | 1 | 21956.7 | 22196.95 | 240.25 | 2000 | 0 | 480500 | 484039.8994 | Paribag | Green Road Dormatory 33/11 SS | 504079.3978 | 452285.2955
480 | Lake circus | 11 | 0 | BD 014047 | 1 | 34637.48 | 35647.16 | 1009.68 | 2000 | 0 | 2019360 | 2034236.8602 | Paribag | Green Road Dormatory 33/11 SS | 2046787.3073 | 1887308.9386
481 | Bashir Uddin | 11 | 0 | BD 014037 | 1 | 14070.93 | 14464.14 | 393.21 | 2000 | 0 | 786420 | 792213.6477 | Paribag | Green Road Dormatory 33/11 SS | 798302.5936 | 740604.9957
482 | Raza Bazar | 11 | 0 | BD 013939 | 1 | 20615.43 | 21277.2 | 661.77 | 2000 | 0 | 1323540 | 1333290.6732 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1329360.3858 | 1277085.001
483 | Rasel Squar | 11 | 0 | BD 013970 | 1 | 31411.16 | 32377.3 | 966.14 | 2000 | 0 | 1932280 | 1946515.3317 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1986224.7792 | 1860400.7233
484 | Bow Bazar | 11 | 0 | BD 013967 | 1 | 23561.5 | 24214.38 | 652.88 | 2000 | 0 | 1305760 | 1315379.6859 | Shere b.nagar | Green Road Dormatory 33/11 SS | 1361417.0663 | 1195690.6937
485 | BRB Hospital | 11 | 0 | BD 014003 | 1 | 12424.41 | 12842.2 | 417.79 | 2000 | 0 | 835580 | 841735.8151 | Shere b.nagar | Green Road Dormatory 33/11 SS | 735319.9448 | 733624.2823
486 | Green Road North | 11 | 0 | BD 013969 | 1 | 14760.23 | 15378.01 | 617.78 | 2000 | 0 | 1235560 | 1244662.5143 | Paribag | Green Road Dormatory 33/11 SS | 1225136.5003 | 1163648.4072
487 | Water Bhaban | 11 | 0 | BD 014004 | 1 | 4898.2 | 5081.77 | 183.57 | 2000 | 0 | 367140 | 369844.7631 | Shere b.nagar | Green Road Dormatory 33/11 SS | 332111.9703 | 301428.8307
488 | Alamin Road | 11 | 0 | BD 014006 | 1 | 18211.68 | 18531.9 | 320.22 | 2000 | 0 | 640440 | 645158.196 | Paribag | Green Road Dormatory 33/11 SS | 644406.723 | 578607.7993
489 | Katal Bagan | 11 | 0 | 0 | 1 | 6635.26 | 7743.31 | 1108.05 | 2000 | 0 | 2216100 | 2232426.2667 | Paribag | Green Road Dormatory 33/11 SS | 2461917.3517 | 1880307.9323
490 | Eastern Pantho chaya | 11 | 0 | BD 014002 | 1 | 2793.55 | 2793.55 | 0 | 2000 | 0 | 0 | 0 | Paribag | Green Road Dormatory 33/11 SS | 0 | 0
491 | Kalabagan | 11 | 0 | BD 014005 | 1 | 5575.77 | 5746.51 | 170.74 | 2000 | 0 | 341480 | 343995.7229 | Paribag | Green Road Dormatory 33/11 SS | 360201.2398 | 320179.3518
492 | Univer Hospital | 11 | 0 | BD 013963 | 1 | 745.38 | 885.22 | 139.84 | 2000 | 0 | 279680 | 281740.4351 | Paribag | Green Road Dormatory 33/11 SS | 275219.2974 | 258266.1053
493 | Green Road Staff Quarter(Anowar Khan Medical) | 11 | 0 | BD 013971 | 1 | 9523.65 | 9775.84 | 252.19 | 2000 | 0 | 504380 | 508095.8262 | Paribag | Green Road Dormatory 33/11 SS | 507213.6524 | 520651.6433
494 | Matir Masjid | 11 | 0 | DHK00170 | 1 | 20154.5 | 22583.2 | 2428.7 | 888.8889 | 0 | 2158844.4444 | 2167154.5553 | Khilgaon | Taltola 33/11KV S/S | 2177028.2382 | 2023352.6919
495 | Hajipara | 11 | 0 | DHK-00108 | 1 | 2631.3 | 3643.3 | 1012 | 2222.2222 | 0 | 2248888.8889 | 2257545.6108 | Khilgaon | Taltola 33/11KV S/S | 2323390.6234 | 1505682.5673
496 | Nearest Feeder | 11 | 0 | DHK-00106 | 1 | 90788.1 | 90788.1 | 0 | 2222.222 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 102528.7436
497 | Reazbagh | 11 | 0 | DHK-00109 | 1 | 95125.7 | 95946.5 | 820.8 | 2222.222 | 0 | 1823999.8176 | 1831021.0001 | Khilgaon | Taltola 33/11KV S/S | 1850181.9906 | 1693614.7124
498 | Chowdhury Para | 11 | 0 | DHK-00107 | 1 | 52175.6 | 52456 | 280.4 | 2222.222 | 0 | 623111.0488 | 625509.6106 | Khilgaon | Taltola 33/11KV S/S | 653692.0598 | 575139.5465
499 | Model Colleg | 11 | 0 | 9122392 | 1 | 2474.25 | 2506.21 | 31.96 | 40000 | 0 | 1278400 | 1283320.9871 | Khilgaon | Taltola 33/11KV S/S | 723685.6707 | 1038453.9207
500 | East Rampura | 11 | 0 | DHK-00181 | 1 | 97687.4 | 98303.2 | 615.8 | 2222.222 | 0 | 1368444.3076 | 1373711.9053 | Khilgaon | Taltola 33/11KV S/S | 1177184.4648 | 1381135.5698
501 | Adarshabagh | 11 | 0 | DHK-00090 | 1 | 48490.9 | 49532.6 | 1041.7 | 2222.222 | 0 | 2314888.6574 | 2323799.4344 | Bashabo | Taltola 33/11KV S/S | 2249760.2414 | 2012766.0076
502 | Khailgaon Govt Colony | 11 | 0 | DHK00167 | 1 | 74331.4 | 75071.6 | 740.2 | 2222.222 | 0 | 1644888.7244 | 1651220.4486 | Khilgaon | Taltola 33/11KV S/S | 1644511.4325 | 1548206.2687
503 | TV Road | 11 | 0 | 6604434 | 1 | 5034.04 | 5070.34 | 36.3 | 40000 | 0 | 1452000 | 1457589.2313 | Khilgaon | Taltola 33/11KV S/S | 1435653.3713 | 1278251.1059
504 | Tilpa Para | 11 | 0 | 06604476 | 1 | 6549.26 | 6562.81 | 13.55 | 40000 | 0 | 542000 | 544086.3384 | Bashabo | Taltola 33/11KV S/S | 925315.57 | 631719.4629
505 | Navana | 11 | 0 | 021100963-02 | 1 | 62097435 | 62097435 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 0
506 | Shantipur | 11 | 0 | 0660444 | 1 | 10278394 | 10278394 | 0 | 1 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 0 | 232625.2878
507 | AT-01 | 0.415 | 0 | 9187958 | 1 | 288.03 | 288.03 | 0 | 80 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 388.7134 | 5004.1149
508 | AT-02 | 0.415 | 0 | 9187959 | 1 | 123.08 | 123.08 | 0 | 10 | 0 | 0 | 0 | Bashabo | Taltola 33/11KV S/S | 1243.317 | 0
509 | Sher-e-Banglanagar Local | 11 | 0 | DHK 66503 | 1 | 76044 | 78207 | 2163 | 60 | 0 | 129780 | 127632.9783 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 130259.0089 | 137740.1655
510 | Mirpur Road East | 11 | 0 | DHK 60961 | 1 | 815519 | 825101 | 9582 | 60 | 0 | 574920 | 565408.7832 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 579726.769 | 591320.8565
511 | Gonobhaban school | 11 | 0 | DHK 66492 | 1 | 523059 | 526229 | 3170 | 60 | 0 | 190200 | 187053.4171 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 201293.1928 | 178100.36
512 | Babor Road | 11 | 0 | DHK 66489 | 1 | 727817 | 741733 | 13916 | 60 | 0 | 834960 | 821146.7988 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 2355047.2749 | 1531864.2685
513 | College Gate | 11 | 0 | DHK 66487 | 1 | 2587196 | 2623105 | 35909 | 60 | 0 | 2154540 | 2118896.2632 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 2029429.4244 | 1693179.314
514 | Parade ground | 11 | 0 | DHK 66490 | 1 | 938247 | 938265 | 18 | 60 | 0 | 1080 | 1062.133 | Satmasjid | SHERE BANGLA NAGAR 33/11 KV S/S | 1780.3054
515 | Hospital RMU | 11 | 0 | DHK 66491 | 1 | 882954 | 893230 | 10276 | 60 | 0 | 616560 | 606359.9098 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 560499.4711 | 544171.0965
516 | Shamoly Square | 11 | 0 | DHK 61065 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | Shyamoli | SHERE BANGLA NAGAR 33/11 KV S/S | 0 | 0
517 | Gonobhaban RMU | 11 | 0 | DHK 60964 | 1 | 191126.8 | 192801.1 | 1674.3 | 60 | 0 | 100458 | 98796.0682 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 102753.2911 | 81921.1363
518 | Krishi University | 11 | 0 | DHK 60963 | 1 | 340100.1 | 350091.4 | 9991.3 | 60 | 0 | 599478 | 589560.5067 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 563852.3796 | 574020.0379
519 | NEC | 11 | 0 | DHK 86073 | 1 | 29.93 | 34.66 | 4.73 | 60000 | 0 | 283800 | 279104.941 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 274760.4607 | 284784.5503
520 | Novo Theater/Army Musium (41%) | 11 | 0 | DHK 86074 | 0.41 | 342.41 | 362.71 | 20.3 | 60000 | 0 | 499380 | 491118.4828 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 467152.1267 | 453385.8053
521 | Novo Theater/Army Musium (59%) | 11 | 0 | DHK 86074 | 0.59 | 342.41 | 362.71 | 20.3 | 60000 | 0 | 718620 | 706731.4752 | Tejgaon | SHERE BANGLA NAGAR 33/11 KV S/S | 672243.3043 | 652433.232
522 | Netor | 11 | 0 | DHK 60962 | 1 | 103402.9 | 114054.4 | 10651.5 | 60 | 0 | 639090 | 628517.1836 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 620062.5542 | 596532.4766
523 | BICC | 11 | 0 | 0 | 1 | 29.93 | 34.66 | 4.73 | 60000 | 0 | 283800 | 279104.941 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 193459.8492 | 69152.9813
524 | Auxiliary | 0.415 | 0 | 0 | 1 | 5156.09 | 5228.9 | 72.81 | 60 | 0 | 4368.6 | 4296.3279 | Shere b.nagar | SHERE BANGLA NAGAR 33/11 KV S/S | 3895.3081 | 5642.8833
525 | City Corporation | 11 | 0 | 93 | 1 | 39720584 | 40386420 | 665836 | 1 | 0 | 665836 | 672002.1574 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 951549.8845 | 660250.7383
526 | Bot tola | 11 | 0 | 0 | 1 | 51317676 | 53690908 | 2373232 | 1 | 0 | 2373232 | 2395209.9678 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 2298336.7826 | 2240795.0697
527 | Jhilpar | 11 | 0 | 145 | 1 | 33590076 | 34782876 | 1192800 | 1 | 0 | 1192800 | 1203846.2525 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1011093.8025 | 1160185.3486
528 | Central Bashaboo | 11 | 0 | 128 | 1 | 35782472 | 37782388 | 1999916 | 1 | 0 | 1999916 | 2018436.7723 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1763582.1465 | 1733572.9987
529 | Kadamtala | 11 | 0 | 8 | 1.5 | 17980396 | 18572154 | 591758 | 1 | 0 | 887637 | 895857.2066 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 680353.9053 | 1958904.8441
530 | Ansar VDP | 11 | 0 | 119 | 1 | 18412676 | 19018394 | 605718 | 1 | 0 | 605718 | 611327.4182 | Khilgaon | Mugdhapara Hospital 33/11 KV SS | 1128730.4864 | 727503.1317
531 | Mugda Hospital Express-01 | 11 | 0 | 0 | 1 | 5599066 | 5903745 | 304679 | 1 | 0 | 304679 | 307500.5637 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 293639.1125 | 272764.3875
532 | Boro Masjid | 11 | 0 | 7 | 1.22 | 46545848 | 47940324 | 1394476 | 1 | 0 | 1701260.72 | 1717015.7129 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 1405726.812 | 1342757.2732
533 | Anandodhara | 11 | 0 | 120 | 1 | 45910688 | 46909724 | 999036 | 1 | 0 | 999036 | 1008287.8477 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 964251.0175 | 915566.0508
534 | Culvert | 11 | 0 | 117 | 1 | 36749792 | 38905824 | 2156032 | 1 | 0 | 2156032 | 2175998.5274 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1824104.3237 | 1912589.1389
535 | Mugda Hospital Express-02 | 11 | 0 | 97 | 1 | 4845548 | 4845548 | 0 | 1 | 0 | 0 | 0 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0 | 0
536 | Jhor Pukur | 11 | 0 | 98 | 1 | 24721380 | 26401136 | 1679756 | 1 | 0 | 1679756 | 1695311.8425 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 1643349.6255 | 1429146.8866
537 | T&T | 11 | 0 | 99 | 1 | 22630184 | 23345024 | 714840 | 1 | 0 | 714840 | 721459.9725 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 567104.166 | 852556.8368
538 | Haider Ali | 11 | 0 | 9 | 1 | 64773440 | 67435952 | 2662512 | 1 | 0 | 2662512 | 2687168.9248 | Maniknagar | Mugdhapara Hospital 33/11 KV SS | 2028073.3969 | 1439434.5953
539 | 11kv Tilpapara | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | Estimated | 2150000 | 2169910.6664 | Bashabo | Mugdhapara Hospital 33/11 KV SS | 2181802.1625 | 2151612.2434
540 | AT-01 | 11 | 0 | 0 | 1 | 2875 | 2964 | 89 | 1 | 0 | 89 | 89.8242 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 94.3756 | 0
541 | AT-02 | 11 | 0 | 0 | 1 | 17 | 17.34 | 0.34 | 1 | 0 | 0.34 | 0.34315 | Mugdapara | Mugdhapara Hospital 33/11 KV SS | 0 | 8.4563
542 | Shantinagar s/s-1 | 11 | 0 | DHK60932 | 1 | 277582 | 322430 | 44848 | 60 | 0 | 2690880 | 2768208.202 | Rajarbag | Khillgaon 33/11KV S/S | 2755360.6206 | 2616486.0095
543 | Gulbagh | 11 | 0 | DHK60934 | 1 | 117195 | 122528 | 5333 | 60 | 0 | 319980 | 329175.3109 | Rajarbag | Khillgaon 33/11KV S/S | 325114.8574 | 314880.9114
544 | Rampura BTV | 11 | 0 | DHK60933 | 1 | 14073 | 14073 | 0 | 60 | 0 | 0 | 0 | Khilgaon | Khillgaon 33/11KV S/S | 1220.4011 | 241.3343
545 | West Shantibag | 11 | 0 | DHK60926 | 1 | 505382 | 520515 | 15133 | 60 | 0 | 907980 | 934072.7507 | Rajarbag | Khillgaon 33/11KV S/S | 932020.3326 | 912726.2746
546 | East Malibagh | 11 | 0 | DHK60929 | 1 | 560235 | 583078 | 22843 | 60 | 0 | 1370580 | 1409966.5528 | Rajarbag | Khillgaon 33/11KV S/S | 1377100.6198 | 1289630.0978
547 | Police Line | 11 | 0 | DHK60930 | 1 | 555020 | 565142 | 10122 | 60 | 0 | 607320 | 624772.6414 | Rajarbag | Khillgaon 33/11KV S/S | 596226.9654 | 576125.2774
548 | PWD RMU 11 KV Sajanpur Feeder. | 11 | 0 | DHK61017 | 1 | 190385 | 192855 | 2470 | 60 | 0 | 148200 | 152458.8445 | Rajarbag | Khillgaon 33/11KV S/S | 149621.1769 | 146188.2445
549 | Benjir Bagan | 11 | 0 | DHK60985 | 1 | 160865 | 164032 | 3167 | 60 | 0 | 190020 | 195480.6318 | Rajarbag | Khillgaon 33/11KV S/S | 194653.9781 | 180699.0476
550 | AT-1 & AT-2 | 0.415 | 0 | ELIB 7374 | 1 | 1864.68 | 1983.75 | 119.07 | 60 | 0 | 7144.2 | 7349.5039 | Rajarbag | Khillgaon 33/11KV S/S | 14431.2432 | 0
551 | Spare | 11 | 0 | BD013944 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Monipuripara 33/11 KV S/S | 0 | 0
552 | Monipuripara west | 11 | 0 | BD013947 | 1 | 29462.81 | 30306.07 | 843.26 | 1000 | 0 | 843260 | 847623.509 | Shere b.nagar | Monipuripara 33/11 KV S/S | 861249.4503 | 873090.4062
553 | Biggan College | 11 | 0 | BD013949 | 1 | 17308.18 | 18139.4 | 831.22 | 1000 | 0 | 831220 | 835521.2072 | Kakrail | Monipuripara 33/11 KV S/S | 819870.1443 | 853994.1863
554 | Green Road South | 11 | 0 | BD013948 | 1 | 27673.13 | 28643.32 | 970.19 | 1000 | 0 | 970190 | 975210.3173 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1037302.1428 | 986346.7996
555 | BARC Building O/H | 11 | 0 | BD014010 | 1 | 12194.37 | 12825.53 | 631.16 | 1000 | 0 | 631160 | 634425.9824 | Shere b.nagar | Monipuripara 33/11 KV S/S | 629218.3029 | 632910.7169
556 | Green Road North | 11 | 0 | BD014036 | 1 | 55063.73 | 57019.83 | 1956.1 | 1000 | 0 | 1956100 | 1966221.9789 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1919532.2257 | 1871294.3358
557 | Chundrima Uddan | 11 | 0 | BD014035 | 1 | 28003.9 | 29068.98 | 1065.08 | 1000 | 0 | 1065080 | 1070591.3324 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1032887.2799 | 1015615.1889
558 | RMU-1 Feeder | 11 | 0 | BD013940 | 1 | 146.76 | 283.07 | 136.31 | 1000 | 0 | 136310 | 137015.3458 | Shere b.nagar | Monipuripara 33/11 KV S/S | 147255.7457 | 0
559 | Spare-03 | 11 | 0 | BD013946 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0
560 | kawran Bazar North | 11 | 0 | BD013964 | 1 | 40142.51 | 40221.55 | 79.04 | 1000 | 0 | 79040 | 79448.9981 | Kakrail | Monipuripara 33/11 KV S/S | 30221.7434 | 0
561 | NAM Bhanan RMU | 11 | 0 | BD013950 | 1 | 14281.17 | 15281.88 | 1000.71 | 1000 | 0 | 1000710 | 1005888.2452 | Shere b.nagar | Monipuripara 33/11 KV S/S | 1030950.7605 | 1013545.3917
562 | Novo Theater | 11 | 0 | BD013938 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0
563 | Monipuripara Nearest | 11 | 0 | BD013962 | 1.18 | 36592.1 | 37303.94 | 711.84 | 1000 | 0 | 839971.2 | 844317.6909 | Tejgaon | Monipuripara 33/11 KV S/S | 794156.578 | 733061.8614
564 | Holy Cross | 11 | 0 | BD013965 | 1.18 | 35046.94 | 36115.46 | 1068.52 | 1000 | 0 | 1260853.6 | 1267377.9768 | Tejgaon | Monipuripara 33/11 KV S/S | 1286005.418 | 1126874.592
565 | Honda Goli | 11 | 0 | BD014011 | 1.18 | 12339.97 | 13245.54 | 905.57 | 1000 | 0 | 1068572.6 | 1074102.0051 | Tejgaon | Monipuripara 33/11 KV S/S | 1068926.6085 | 953126.0337
566 | Navy Quarter | 11 | 0 | BD013941 | 1.18 | 4964.2 | 5132.94 | 168.74 | 1000 | 0 | 199113.2 | 200143.5254 | Tejgaon | Monipuripara 33/11 KV S/S | 202962.2853 | 175339.91
567 | AT-01 | 0.415 | 0 | 0 | 1 | 1834.42 | 1913.87 | 79.45 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0
568 | AT-02 | 0.415 | 0 | 0 | 1 | 585.48 | 585.48 | 0 | 1 | 0 | 0 | 0 | Shere b.nagar | Monipuripara 33/11 KV S/S | 0 | 0
569 | Doctor Goli | 11 | 0 | BD013944 | 1 | 6792.09 | 7728.79 | 936.7 | 1000 | 0 | 936700 | 948233.0953 | Moghbazar | Ispahani 33/11 KV SS | 958270.3835 | 898591.0283
570 | Ispahani | 11 | 0 | BD013947 | 1 | 7580.78 | 8623.82 | 1043.04 | 1000 | 0 | 1043040 | 1055882.4039 | Moghbazar | Ispahani 33/11 KV SS | 1058199.8531 | 999582.0108
571 | BTCL | 11 | 0 | BD013949 | 1 | 3962.52 | 4485.67 | 523.15 | 1000 | 0 | 523150 | 529591.2713 | Kakrail | Ispahani 33/11 KV SS | 523726.617 | 532492.3633
572 | Vikarunnesa | 11 | 0 | BD013948 | 1 | 4102.97 | 5237.35 | 1134.38 | 1000 | 0 | 1134380 | 1148347.0254 | Kakrail | Ispahani 33/11 KV SS | 1136233.5895 | 1092064.7445
573 | OASIS | 11 | 0 | 0 | 1 | 0 | 4.29 | 4.29 | 1000 | 0 | 4290 | 4342.8205 | Kakrail | Ispahani 33/11 KV SS | 0 | 0
574 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
575 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
576 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
577 | Wireless | 11 | 0 | 0 | 1 | 5737.24 | 6771.63 | 1034.39 | 1000 | 0 | 1034390 | 1047125.901 | Moghbazar | Ispahani 33/11 KV SS | 1048087.1638 | 896344.5253
578 | Kazir Goli | 11 | 0 | 0 | 1 | 4903.55 | 6092.57 | 1189.02 | 1000 | 0 | 1189020 | 1203659.779 | Kakrail | Ispahani 33/11 KV SS | 1263311.3532 | 1182067.1763
579 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
580 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
581 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
582 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
583 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
584 | Spare | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
585 | AT-01 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
586 | AT-02 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Ispahani 33/11 KV SS | 0 | 0
587 | 11 kV DCM Feeder (F-1) (old AEPZ-1) | 11 | New | XA587377 | 1 | 210341.9 | 213015.1 | 2673.2 | 1000 | 0 | 2673200 | 2725888.0748 | Siddirgonj | Siddhirganj 33/11KV S/S | 2549641.8301 | 2438789.3271
588 | 11 kV Local & Staff Qtr (F-2) + Adamjeenagar Pump Station | 11 | New | XA587359 | 1 | 16731.5 | 16876.9 | 145.4 | 1000 | 0 | 145400 | 148265.7961 | Siddirgonj | Siddhirganj 33/11KV S/S | 145583.9006 | 138711.8093
589 | 11 kV Narayangonj Direct Feeder (F-3) | 11 | New | XA586385 | 1 | 106740.6 | 108320.7 | 1580.1 | 1000 | 0 | 1580100 | 1611243.3589 | Siddirgonj | Siddhirganj 33/11KV S/S | 1535819.0344 | 1523513.0022
590 | 11 kV Ekata Steel Feeder (F-4) | 11 | New | XA587376 | 1 | 167267.3 | 169879.3 | 2612 | 1000 | 0 | 2612000 | 2663481.8388 | Siddirgonj | Siddhirganj 33/11KV S/S | 2529191.2405 | 2405949.7847
591 | 11 kV Silo+Titas Feeder (F-5) | 11 | New | XA575929 | 1 | 6948.3 | 7001.5 | 53.2 | 1000 | 0 | 53200 | 54248.5581 | Siddirgonj | Siddhirganj 33/11KV S/S | 41407.382 | 36566.7297
592 | 11 kV Monowar Feeder (F-6) | 11 | New | XA587363 | 1 | 73247.9 | 74651.5 | 1403.6 | 1000 | 0 | 1403600 | 1431264.5899 | Siddirgonj | Siddhirganj 33/11KV S/S | 1311672.4727 | 1337959.5143
593 | 11 kV Era Steel Feeder (F-7) | 11 | New | XA587355 | 1 | 27327.2 | 27327.2 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0
594 | 11 kV Kalu Haji Road Feeder (F-8) | 11 | New | 0 | 1 | 25.5757 | 25.5757 | 0 | 40000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0
595 | 11 kV Mizmizi Feeder (F-9) | 11 | New | XA587358 | 1 | 144040.1 | 146439.6 | 2399.5 | 1000 | 0 | 2399500 | 2446793.5192 | Siddirgonj | Siddhirganj 33/11KV S/S | 2328937.4468 | 2238024.8856
596 | 11 KV Jhilpar (F-10) | 11 | New | XA587369 | 1 | 71.4752 | 79.1918 | 7.7166 | 40000 | 0 | 308664 | 314747.6869 | Matuail | Siddhirganj 33/11KV S/S | 291293.3394 | 424399.7103
597 | 11 kV Madrasha Road Feeder (F-11) | 11 | New | XA575919 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0
598 | 11 kV Orion Pharma Ltd (Old EGCB 335 MW) (F-12) | 11 | New | XA587383 | 1 | 13546.5 | 14255.5 | 709 | 1000 | 0 | 709000 | 722974.2051 | Siddirgonj | Siddhirganj 33/11KV S/S | 681450.0937 | 758130.0486
599 | Seven Horse Feeder (F-13) | 11 | New | XA587373 | 1 | 129895.9 | 129895.9 | 0 | 1000 | 0 | 0 | 0 | Siddirgonj | Siddhirganj 33/11KV S/S | 0 | 0
600 | 11 kV Shanti Nagar (F-14) | 11 | New | XA587371 | 1 | 143559.8 | 146418.5 | 2858.7 | 1000 | 0 | 2858700 | 2915044.2314 | Siddirgonj | Siddhirganj 33/11KV S/S | 2806489.0873 | 2820775.6603
601 | 11 kV New Town O/H (Old Sarulia U/G Cable Circuit-2) | 11 | 0 | HA021101013-02 | 1 | 43772221 | 46067484 | 2295263 | 1 | 0 | 2295263 | 2346002.1943 | Matuail | Demra 33/11KV S/S | 2312393.5546 | 2206583.7096
602 | 11 kV DND (WASA) Feeder. | 11 | 0 | HA021100992-02 | 1 | 5367438 | 5613260 | 245822 | 1 | 0 | 245822 | 251256.153 | Siddirgonj | Demra 33/11KV S/S | 80170.7162 | 6927.7253
603 | 11 kV Local Feeder | 11 | 0 | HA021100794-02 | 1 | 8692106 | 9848922 | 1156816 | 1 | 0 | 1156816 | 1182388.6301 | Siddirgonj | Demra 33/11KV S/S | 2088621.9879 | 1417684.9395
604 | 11 kV Mouchak Feeder | 11 | 0 | DHK60888 | 1 | 855586.5 | 893731.2 | 38144.7 | 60 | 0 | 2288682 | 2339275.7144 | Siddirgonj | Demra 33/11KV S/S | 2308639.9015 | 2074135.4747
605 | 11 kV Overhead-1 Feeder | 11 | 0 | HA021100829-02 | 1 | 76972401 | 78137143 | 1164742 | 1 | 0 | 1164742 | 1190489.8427 | Siddirgonj | Demra 33/11KV S/S | 1095153.438 | 1095304.9401
606 | 11 kV Provati Steel Feeder | 11 | 0 | DHK60874 | 1 | 544937.6 | 546973.2 | 2035.6 | 60 | 0 | 122136 | 124835.9443 | Siddirgonj | Demra 33/11KV S/S | 0 | 0
607 | 11 kV Islambagh Feeder. | 11 | 0 | DHKA2190 | 1 | 999.9264 | 1048.5044 | 48.578 | 60000 | 0 | 2914680 | 2979112.0563 | Matuail | Demra 33/11KV S/S | 3002442.9965 | 2983539.0327
608 | 11 kV Taj Jute Feeder. | 11 | 0 | DHK61062 | 1 | 590904.5 | 613805.1 | 22900.6 | 60 | 0 | 1374036 | 1404410.5059 | Siddirgonj | Demra 33/11KV S/S | 1676660.8446 | 1675376.4941
609 | 11 kV Al-Aksa Steel Feeder | 11 | 0 | DHK61061 | 1 | 732963.2 | 758979.9 | 26016.7 | 60 | 0 | 1561002 | 1595509.5853 | Siddirgonj | Demra 33/11KV S/S | 1474597.4818 | 1597579.1906
610 | 11 kV Sahebpara O/H (Old Spare Feeder) | 11 | 0 | DHKA2189 | 1 | 945.7312 | 986.7258 | 40.9946 | 60000 | 0 | 2459676 | 2514049.716 | Siddirgonj | Demra 33/11KV S/S | 2467512.3805 | 2370283.5934
611 | 11 kV Over Head Feeder-2. | 11 | 0 | HA021100488-02 | 1 | 24800709 | 26957261 | 2156552 | 1 | 0 | 2156552 | 2204224.8423 | Demra | Demra 33/11KV S/S | 2131027.6013 | 2071443.4949
612 | 11 kV Shimrail Express Feeder. | 11 | 0 | HA021100511-02 | 1 | 8095991 | 8169444 | 73453 | 1 | 0 | 73453 | 75076.7556 | Siddirgonj | Demra 33/11KV S/S | 29225.6688 | 0
613 | 11 kV Sarder & Khadem Steel Feeder | 11 | 0 | HA021100413-02 | 1 | 80407905 | 80731969 | 324064 | 1 | 0 | 324064 | 331227.7744 | Demra | Demra 33/11KV S/S | 650733.1002 | 409613.9007
614 | 11 kV Siddhirgonj Mazar Feeder | 11 | 0 | HA021100393-02 | 1 | 22161.663 | 23396.457 | 1234.794 | 1000 | 0 | 1234794 | 1262090.4156 | Siddirgonj | Demra 33/11KV S/S | 281800.301 | 832832.3648
615 | 11 kV AST Beverage Feeder | 11 | 0 | 0 | 1 | 20233737 | 21373122 | 1139385 | 1 | 0 | 1139385 | 1164572.2996 | Siddirgonj | Demra 33/11KV S/S | 1051751.2525 | 1163750.6238
616 | 11 kV Karim Market Feeder | 11 | 0 | 0 | 1 | 53935.137 | 56008.912 | 2073.775 | 1000 | 0 | 2073775 | 2119617.9699 | Matuail | Demra 33/11KV S/S | 2072299.946 | 2089377.8867
617 | 11/0.415 kV Transformer,AT-1+AT-2 | 0.415 | 0 | ELIB2771 | 1 | 375996 | 375996 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Demra 33/11KV S/S | 0 | 0
618 | 11 kV Dayagonj Feeder (=L11) | 11 | 0 | 2007755114 | 1 | 5723.87 | 5767.7 | 43.83 | 60000 | 0 | 2629800 | 2674737.7934 | Demra | Sarulia 33/11KV S/S | 2648546.8605 | 3036942.6611
619 | 11 kV Karim Jute Feeder (=L12) | 11 | 0 | 30799484 | 1 | 21.1189 | 21.3509 | 0.232 | 60000 | 0 | 13920 | 14157.8637 | Demra | Sarulia 33/11KV S/S | 13577.9934 | 12817.0467
620 | 11 kV Konapara (=L13) **** | 11 | 0 | DHKA2191 | 1 | 2005.823 | 2064.619 | 58.796 | 60000 | 0 | 3527760 | 3588042.0557 | Demra | Sarulia 33/11KV S/S | 3482255.5223 | 2467003.1131
621 | 11 kV Sanarpar Feeder (=L14) | 11 | 0 | 575926 | 1 | 48458.1 | 51041.5 | 2583.4 | 1000 | 0 | 2583400 | 2627544.9143 | Matuail | Sarulia 33/11KV S/S | 2556143.6589 | 2386518.0767
622 | 11 kV Latif Bawani Feeder (=L15) | 11 | 0 | 30799450 | 1 | 1804.9 | 1809.19 | 4.29 | 60000 | 0 | 257400 | 261798.4288 | Demra | Sarulia 33/11KV S/S | 295524.6849 | 302404.9427
623 | 11 kV Tengra Feeder (=L16) | 11 | 0 | 30799145 | 1 | 5426.47 | 5472.12 | 45.65 | 60000 | 0 | 2739000 | 2785803.7935 | Demra | Sarulia 33/11KV S/S | 2203397.2826 | 3315319.3041
624 | 11 kV Police Line Feeder (=L17) | 11 | 0 | 30799480 | 1 | 3297.43 | 3317.32 | 19.89 | 60000 | 0 | 1193400 | 1213792.7153 | Demra | Sarulia 33/11KV S/S | 1297576.8726 | 1183247.2468
625 | 11 kV Demra Bazar Feeder (=L18) | 11 | 0 | 30799119 | 1 | 1630.73 | 1639.93 | 9.2 | 60000 | 0 | 552000 | 561432.5279 | Demra | Sarulia 33/11KV S/S | 558765.1604 | 495803.4526
626 | 11 kV Spare Feeder (=F9) | 11 | 0 | HA021100859-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0
627 | 11 kV Boxnagar Feeder (=F10) | 11 | 0 | HA021100493-02 | 1 | 77608653 | 80604576 | 2995923 | 1 | 0 | 2995923 | 3047117.0714 | Demra | Sarulia 33/11KV S/S | 3001937.8862 | 2753359.8865
628 | 11 kV Baser Pool Feeder (=L11) | 11 | 0 | HA021100518-02 | 1 | 50867999 | 50869565 | 1566 | 1 | 0 | 1566 | 1592.7597 | Demra | Sarulia 33/11KV S/S | 158210.2162 | 30254.1689
629 | 11 kV Dip-Pur Feeder (=L12) | 11 | 0 | HA021100697-02 | 1 | 20487902 | 22773043 | 2285141 | 1 | 0 | 2285141 | 2324189.2905 | Demra | Sarulia 33/11KV S/S | 2304863.862 | 2171918.011
630 | 11/0.4 kV Auxiliary Transformer-1(AT-1) | 0.415 | 0 | 05378800 | 1 | 566454.55 | 566454.55 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0
631 | 11/0.4 kV Auxiliary Transformer-2 (AT-2) | 0.415 | 0 | 05395814 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Demra | Sarulia 33/11KV S/S | 0 | 0
632 | 11 kV Khanpur Feeder | 11 | 0 | DHKC 9348 | 1 | 16751.32 | 47198.82 | 30447.5 | 60 | 0 | 1826850 | 1849730.4598 | N.Gonj (East) | Khanpur 33/11KV S/S | 1858439.2031 | 1689432.0922
633 | 11 kV Mission Para Feeder. | 11 | 0 | DHKC 9347 | 1 | 3983.86 | 32560.85 | 28576.99 | 60 | 0 | 1714619.4 | 1736094.2229 | N.Gonj (East) | Khanpur 33/11KV S/S | 1666330.9001 | 1591097.4109
634 | 11 kV Esha Kha Feeder | 11 | 0 | DHKC 9311 | 1 | 64482.72 | 79951.21 | 15468.49 | 60 | 0 | 928109.4 | 939733.5453 | N.Gonj (East) | Khanpur 33/11KV S/S | 917602.1317 | 1040108.3114
635 | 11 kV New Hazigonj Feeder | 11 | 0 | DHKC 9314 | 1 | 134.23 | 170.34 | 36.11 | 60000 | 0 | 2166600 | 2193735.673 | N.Gonj (East) | Khanpur 33/11KV S/S | 2054393.8757 | 2135156.6373
636 | 11 kV Spare Feeder. | 11 | 0 | DHKC 9345 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
637 | 11 kV Hospital RMU Feeder. | 11 | 0 | 6604412 | 1 | 3.83 | 4.9 | 1.07 | 60000 | 0 | 64200 | 65004.0756 | N.Gonj (East) | Khanpur 33/11KV S/S | 61352.3895 | 59949.0945
638 | 11 kV Old Hajiganj Feeder. | 11 | 0 | DHK00189 | 1 | 8119.81 | 8119.81 | 0 | 60 | 0 | 0 | 0 | N.Gonj (East) | Khanpur 33/11KV S/S | 0 | 0
639 | 11 kV Siraj-ud-daullah Feeder. | 11 | 0 | 06604389 | 1 | 84767.18 | 106245.25 | 21478.07 | 60 | 0 | 1288684.2 | 1304824.3795 | N.Gonj (East) | Khanpur 33/11KV S/S | 1324560.4284 | 1260578.6756
640 | 11 kV Spare Feeder. | 11 | 0 | 8576983 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
641 | Old 33/11 kV 10/14 MVA T1 Incoming | 11 | 0 | 06604371 | 1 | 4422.93 | 4422.93 | 0 | 80000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
642 | 11 kV B. B. Road West Feeder. | 11 | 0 | 6604415 | 1 | 186.02 | 234.81 | 48.79 | 40000 | 0 | 1951600 | 1976042.8964 | N.Gonj (West) | Khanpur 33/11KV S/S | 1840166.7201 | 1800087.6245
643 | 11 kV Mondalpara Feeder. | 11 | 0 | 06604394 | 1 | 267.16 | 267.16 | 0 | 8000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
644 | 11 kV B. B. Road East Feeder. | 11 | 0 | 06604392 | 1 | 145.84 | 183.1 | 37.26 | 40000 | 0 | 1490400 | 1509066.5776 | N.Gonj (East) | Khanpur 33/11KV S/S | 1463548.0912 | 1396793.7162
645 | 11 kV Bishaw Road Feeder. | 11 | 0 | 06604393 | 1 | 191.13 | 221.32 | 30.19 | 40000 | 0 | 1207600 | 1222724.6371 | N.Gonj (East) | Khanpur 33/11KV S/S | 1779421.78 | 1969640.6189
646 | 11 kV Chasara Feeder. | 11 | 0 | 06604391 | 1 | 204.54 | 258.76 | 54.22 | 40000 | 0 | 2168800 | 2195963.227 | N.Gonj (West) | Khanpur 33/11KV S/S | 2115948.7484 | 2048765.3497
647 | 11 kV Pathan Tully Feeder. | 11 | 0 | 06604388 | 1 | 32.71 | 33.69 | 0.98 | 40000 | 0 | 39200 | 39690.9621 | N.Gonj (East) | Khanpur 33/11KV S/S | 0 | 0
648 | 11 kV Spare Feeder. | 11 | 0 | 9120051 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
649 | 11 kV Nayamati Feeder. | 11 | 0 | 6604289 | 1 | 139.69 | 169.17 | 29.48 | 40000 | 0 | 1179200 | 1193968.9401 | N.Gonj (East) | Khanpur 33/11KV S/S | 1316545.3361 | 1343505.6323
650 | 11 kV Spare Feeder. | 11 | 0 | DHKC9310 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
651 | 11 kV Spare Feeder. | 11 | 0 | DHKC9349 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
652 | 11 kV Spare Feeder. | 11 | 0 | DHKC9312 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | Khanpur 33/11KV S/S | 0 | 0
653 | 33/0.415 kV Auxiliary Transformer-1 | 0.415 | 0 | 412109 | 1 | 9109.5 | 9113.7 | 4.2 | 10 | 0 | 42 | 42.526 | N.Gonj (East) | Khanpur 33/11KV S/S | 0 | 0
654 | 33/0.415 kV Auxiliary Transformer-2 | 0.415 | 0 | 243285 | 1 | 6388.1 | 6433.2 | 45.1 | 10 | 0 | 3000 | 3037.5736 | N.Gonj (East) | Khanpur 33/11KV S/S | 3037.247 | 3027.732
655 | 11 kV Link Road Feeder | 11 | 0 | HA021100475-02 | 1 | 85577.974 | 88158.496 | 2580.522 | 1000 | 0 | 2580522 | 2607402.2302 | N.Gonj (East) | Matuail 33/11KV S/S | 1951841.3049 | 1877540.2045
656 | 11 kV Lamapara Express Feeder | 11 | 0 | HA021100928-03 | 1 | 76566.376 | 77285.778 | 719.402 | 1000 | 0 | 719402 | 726895.7131 | N.Gonj (East) | Matuail 33/11KV S/S | 1017580.9915 | 1063497.0225
657 | 11 kV Kutubpur Feeder*** | 11 | 0 | DHK66616 | 1 | 17507.52 | 17710.59 | 203.07 | 8000 | 0 | 1624560 | 1641482.3695 | N.Gonj (East) | Matuail 33/11KV S/S | 1554956.8642 | 1703285.4205
658 | 11 kV Ramarbagh Feeder (F1) | 11 | 0 | DHK66625 | 1 | 3485.92 | 3508.42 | 22.5 | 60000 | 0 | 1350000 | 1364062.3916 | Fatullah | Matuail 33/11KV S/S | 1338941.0426 | 835792.1765
659 | 11 kV Tushardhara Feeder (F2) | 11 | 0 | DHK66623 | 1 | 3746.82 | 3791.19 | 44.37 | 60000 | 0 | 2662200 | 2689931.0362 | Matuail | Matuail 33/11KV S/S | 2755784.1096 | 2760297.6743
660 | 11 kV Matuail Medical Feeder (F3) | 11 | 0 | DHK66627 | 1 | 3271.85 | 3284.92 | 13.07 | 60000 | 0 | 784200 | 792368.687 | Matuail | Matuail 33/11KV S/S | 795452.7012 | 696897.8308
661 | 11 kV Rupayan Town Feeder (F4) | 11 | 0 | HA021101044-02 | 1 | 65208.095 | 65554.037 | 345.942 | 1000 | 0 | 345942 | 349545.5347 | Matuail | Matuail 33/11KV S/S | 361905.6203 | 323912.9361
662 | 11 kV Shibu Market Feeder (F7) | 11 | 0 | DHK66624 | 1 | 2362.42 | 2368.99 | 6.57 | 60000 | 0 | 394200 | 398306.2183 | Fatullah | Matuail 33/11KV S/S | 387075.6832 | 615623.4101
663 | 11 kV Soma-Sagar Steel (F6) | 11 | 0 | HA060300286-03 | 1 | 2.105 | 961.358 | 959.253 | 1000 | 959253 | 1486842.15 | 1502329.9696 | Fatullah | Matuail 33/11KV S/S | 1201993.7471 | 1110650.3388
664 | 11 kV Jhalkuri Feeder (F8) | 11 | 0 | DHK66626 | 1 | 4334.87 | 4378.18 | 43.31 | 60000 | 0 | 2598600 | 2625668.5413 | Matuail | Matuail 33/11KV S/S | 2669361.5514 | 2690547.2387
665 | 11 kV Madani Nagar Feeder (F9) | 11 | 0 | DHK6622 | 1 | 4168.25 | 4189.27 | 21.02 | 60000 | 0 | 1261200 | 1274337.3987 | Matuail | Matuail 33/11KV S/S | 1416234.4574 | 1374993.3702
666 | 11 kV Rajmahal Feeder (F10) | 11 | 0 | DHKA2187 | 1 | 108.4909 | 112.4599 | 3.969 | 60000 | 0 | 238140 | 240620.6059 | Shyampur | Matuail 33/11KV S/S | 244740.1643 | 218634.2568
667 | 11 kV Bhuighor Bazar | 11 | 0 | HA021100861-02 | 1 | 74536.429 | 75324.363 | 787.934 | 1000 | Estimated | 1277144.82 | 1290448.3093 | Matuail | Matuail 33/11KV S/S | 1462145.9342 | 1034107.8281
668 | 11 kV Tokkar Math Feeder | 11 | 0 | HA021200298-02 | 1 | 79511.406 | 80274.518 | 763.112 | 1000 | 0 | 763112 | 771061.022 | Fatullah | Matuail 33/11KV S/S | 778486.6953 | 733095.2742
669 | 11 kV Osmani Stadium Feeder***** | 11 | 0 | XA575922 | 1 | 184 | 193.1 | 9.1 | 1000 | 0 | 9100 | 9194.7909 | Fatullah | Matuail 33/11KV S/S | 13287.9755 | 64493.8811
670 | 33/0.415 KV Transformer, AT-1 | 0.415 | 0 | 2001123043119 | 1 | 7271 | 7351.2 | 80.2 | 160 | 0 | 12832 | 12965.6656 | Shyampur | Matuail 33/11KV S/S | 12496.7831 | 11807.0303
671 | 33/0.415 KV Transformer, AT-2 | 0.415 | 0 | 2001123043157 | 1 | 4715.3 | 4715.3 | 0 | 160 | 0 | 0 | 0 | Shyampur | Matuail 33/11KV S/S | 0 | 129.3921
672 | 11 kV Godnail (F16) | 11 | 0 | 00000109 | 1 | 22845784 | 24749340 | 1903556 | 1 | 0 | 1903556 | 1902174.2906 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1848814.9706 | 1869406.9017
673 | 11 kV M. Circus (F15) | 11 | 0 | 00000123 | 1 | 105458624 | 107396816 | 1938192 | 1 | 0 | 1938192 | 1936785.1498 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1975646.3394 | 2135882.0516
674 | 11 kV Wapderpool (F14) | 11 | 0 | 00000190 | 1 | 55796344 | 56271624 | 475280 | 1 | 0 | 475280 | 474935.0147 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 619875.2088 | 595303.4365
675 | 11 kV Chowdhury Bari (F13) | 11 | 0 | 00000191 | 1 | 96441288 | 98646920 | 2205632 | 1 | 0 | 2205632 | 2204031.0267 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 2287431.9192 | 2194488.2982
676 | 11 kV Ailpara (F12) | 1 | 0 | 00000192 | 1 | 49107040 | 51494196 | 2387156 | 1 | 0 | 2387156 | 2385423.2662 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 2312455.9158 | 2506620.5244
677 | 11 kV Spare (F11) | 11 | 0 | 00000193 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
678 | 11 kV Spare (F10) | 11 | 0 | 00000194 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
679 | 11 kV Spare (F9) | 11 | 0 | 00000195 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
680 | 11 kV Spare (F8) | 11 | 0 | 00000196 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
681 | 11 kV Zulfiqur Steel | 11 | 0 | 00000197 | 1 | 14248885 | 15359563 | 1110678 | 1 | 0 | 1110678 | 1109871.8066 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1233882.0915 | 1248729.4855
682 | 11 kV New Laxmi Narayan Cotton Mill (F6) | 11 | 0 | 00000198 | 1 | 3997630 | 4078510 | 80880 | 1 | 0 | 80880 | 80821.2927 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 12574.267 | 42071.0581
683 | 11 kV Lucky Bazar (F5) | 11 | 0 | 00000199 | 1 | 87124224 | 88391024 | 1266800 | 1 | 0 | 1266800 | 1265880.4844 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1332623.2308 | 1392661.9878
684 | 11 kV Enayetnagar (F4) | 11 | 0 | 00000200 | 1 | 29163608 | 30771724 | 1608116 | 1 | 0 | 1608116 | 1606948.7378 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 1544300.7721 | 1576051.8888
685 | 11 kV Bhuiyapara (F3) | 11 | 0 | 00000201 | 1 | 62323408 | 64028044 | 1704636 | 1 | 0 | 1704636 | 1703398.6781 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 2021560.4921 | 1949356.1666
686 | 11 kV Arambagh (F2) | 11 | 0 | 00000202 | 1 | 6951863 | 7963900.5 | 1012037.5 | 1 | 0 | 1012037.5 | 1011302.9055 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 1033739.3311 | 1073358.7436
687 | 11 kV Spare (F1) | 11 | 0 | 00000203 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Siddirgonj | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
688 | 11/0.415 kV Aux. Transformer-1 | 0.415 | 0 | 00000204 | 1 | 1577 | 1627.32 | 50.32 | 100 | 0 | 5032 | 5028.3475 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 4509.4616 | 4713.1396
689 | 11/0.415 kV Aux. Transformer-2 | 0.415 | 0 | 00000205 | 1 | 60.71 | 60.72 | 0.01 | 100 | 0 | 1 | 0.99927 | N.Gonj (East) | Laxmi Narayan Cotton Mill 33/11 kV | 0 | 0
690 | 11 kV Minan Steel Feeder | 11 | New | 0 | 1 | 74957542 | 75456997 | 499455 | 1 | 0 | 499455 | 493276.6302 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 608736.535 | 686221.5647
691 | 11 kV Shovon Garments | 11 | New | HA021100480-02 | 1 | 87261856 | 87945628 | 683772 | 1 | 0 | 683772 | 675313.5877 | N.Gonj (West) | Fatullah OLD 33/11KV S/S | 687996.4568 | 904286.638
692 | 11 kV Mazar O/H Feeder | 11 | New | DHK61059 | 1 | 105562.1 | 129693.5 | 24131.4 | 60 | 0 | 1447884 | 1429973.3518 | Fatullah | Fatullah OLD 33/11KV S/S | 1348752.6633 | 1520277.0648
693 | 11 kV Shahjahan Steel. | 11 | New | DHK61055 | 1 | 115800.8 | 115800.8 | 0 | 60 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
694 | 11 kV Pilkuni O/H Feeder. | 11 | New | DHK61058 | 1 | 291780 | 308379.7 | 16599.7 | 60 | 0 | 995982 | 983661.4804 | Fatullah | Fatullah OLD 33/11KV S/S | 966418.4358 | 973413.7301
695 | 11 kV Narayangonj Express Feeder. | 11 | New | DHK61052 | 1 | 938604.3 | 976902.1 | 38297.8 | 60 | 0 | 2297868 | 2269442.86 | Fatullah | Fatullah OLD 33/11KV S/S | 1903765.6601 | 1898489.4903
696 | 11 kV Post Office Road Feeder. | 11 | New | DHK61053 | 1 | 48136.4 | 59040.7 | 10904.3 | 60 | 0 | 654258 | 646164.6825 | Fatullah | Fatullah OLD 33/11KV S/S | 667510.2274 | 661387.5474
697 | 11 kV Fatullah Feeder. | 11 | New | DHK61056 | 1 | 602547.3 | 616341.5 | 13794.2 | 60 | 0 | 827652 | 817413.76 | Fatullah | Fatullah OLD 33/11KV S/S | 827156.9088 | 863427.9271
698 | 11 kV Al-baraka & Shah Fatullah. | 11 | New | DHK61114 | 1 | 486964.4 | 504567.7 | 17603.3 | 60 | 0 | 1056198 | 1043132.595 | Fatullah | Fatullah OLD 33/11KV S/S | 1256184.2479 | 1130265.9765
699 | 11 kV Haque Steel & Shilpi Steel | 11 | New | DHK61111 | 1 | 860387.5 | 864279.2 | 3891.7 | 60 | 0 | 233502 | 230613.5281 | Fatullah | Fatullah OLD 33/11KV S/S | 268951.939 | 461817.7457
700 | 11 kV Dhaka Steel | 11 | New | DHK60923 | 1 | 501840.9 | 514317.3 | 12476.4 | 60 | 0 | 748584 | 739323.8488 | Fatullah | Fatullah OLD 33/11KV S/S | 888156.2557 | 505747.1466
701 | 11 kV Panchabati O/H Feeder | 11 | New | HA021100891-02 | 1 | 99488328 | 100229225 | 740897 | 1 | 0 | 740897 | 731731.9387 | Sytalakhya | Fatullah OLD 33/11KV S/S | 686782.5544 | 645276.6941
702 | 11 kV Dharmagonj Feeder. | 11 | New | HA021101231-02 | 1 | 24567287 | 24889601 | 322314 | 1 | 0 | 322314 | 318326.9039 | Sytalakhya | Fatullah OLD 33/11KV S/S | 335635.5116 | 326421.8579
703 | 11 kV Sena Edible Oil Feeder. | 11 | New | HA021101108-02 | 1 | 14795210 | 15173750 | 378540 | 1 | 0 | 378540 | 373857.3757 | Sytalakhya | Fatullah OLD 33/11KV S/S | 329133.6781 | 311868.8913
704 | 11 kV Kutubail Feeder | 11 | New | HA021101010-02 | 1 | 78709899 | 78709899 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
705 | 11 kV Aligonj Feeder | 11 | New | HA021100973-02 | 1 | 27036113 | 27036113 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 123409.7429 | 535601.4665
706 | 11 kV Gabtoli Feeder | 11 | New | HA021101005-02 | 1 | 11860750 | 13842626 | 1981876 | 1 | 0 | 1981876 | 1957359.7515 | Fatullah | Fatullah OLD 33/11KV S/S | 2145386.8814 | 2599917.6327
707 | 11 kV Jamuna Steel Feeder. | 11 | New | HA021101045-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
708 | 0 | 11 | Old | DHK00113 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
709 | 11 kV Bishwa Road Feeder | 11 | New | HA021100705-02 | 1 | 2718344 | 4587115 | 1868771 | 1 | 0 | 1868771 | 1845653.8856 | Fatullah | Fatullah OLD 33/11KV S/S | 1844325.072 | 1788794.6263
710 | 11 kV Spare Feeder | 11 | New | HA021100877-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
711 | 33/0.415 kV, 200 kVA, AT-1+2 | 11 | 0 | ELIB7380 | 1 | 223454 | 223454 | 0 | 1 | 0 | 0 | 0 | Fatullah | Fatullah OLD 33/11KV S/S | 0 | 0
712 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902834 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
713 | 11 kV Outgoing Feeder-2 (=F2) | 11 | 0 | 041808902801 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
714 | 11 kV Morakhalpar (=F3) | 11 | Shitalakhya | 041808902797 | 1 | 855.85 | 887.81 | 31.96 | 60000 | 0 | 1917600 | 1919103.2774 | Sytalakhya | Fatullah New 33/11 KV SS | 1925513.8961 | 2018573.5941
715 | 11 kV Achimtola (=F4) | 11 | Shitalakhya | 041808902780 | 1 | 390.79 | 414.63 | 23.84 | 60000 | 0 | 1430400 | 1431521.3433 | Sytalakhya | Fatullah New 33/11 KV SS | 1476167.1668 | 1492878.3256
716 | 11 kV Horihorpara (=F5) | 11 | Shitalakhya | 041808902782 | 1 | 518.47 | 530.35 | 11.88 | 60000 | 0 | 712800 | 713358.7902 | Sytalakhya | Fatullah New 33/11 KV SS | 702593.0118 | 691704.3007
717 | 11 kV Amtola Feeder (=F6) | 11 | Shitalakhya | 041808902773 | 1 | 1147.26 | 1177.63 | 30.37 | 60000 | 0 | 1822200 | 1823628.4898 | Sytalakhya | Fatullah New 33/11 KV SS | 1708359.7204 | 1811062.3039
718 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902774 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
719 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902760 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
720 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902755 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
721 | 11 kV Outgoing Feeder-10 (=F8) | 11 | 0 | 041808902788 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
722 | 11 kV Outgoing Feeder-11 (=F9) | 11 | 0 | 041808902785 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
723 | 11 kV Nabinagar (=F10) | 11 | Shitalakhya | 041808902841 | 1 | 135.99 | 157.05 | 21.06 | 60000 | 0 | 1263600 | 1264590.5826 | Sytalakhya | Fatullah New 33/11 KV SS | 1201867.1554 | 1168078.0452
724 | 11 kV Dhalipara (=F11) | 11 | Shitalakhya | 041808902842 | 1 | 58.08 | 68.32 | 10.24 | 60000 | 0 | 614400 | 614881.6508 | Sytalakhya | Fatullah New 33/11 KV SS | 573262.9625 | 566596.0446
725 | 11 kV Etimkhana (=F12) | 11 | Shitalakhya | 041808902840 | 1 | 1064.3 | 1090.6 | 26.3 | 60000 | 0 | 1578000 | 1579237.0524 | Sytalakhya | Fatullah New 33/11 KV SS | 1146525.925 | 1680540.7098
726 | 11 kV Premroad (=F13) | 11 | Shitalakhya | 041808902798 | 1 | 1275.93 | 1318 | 42.07 | 60000 | 0 | 2524200 | 2526178.8135 | Sytalakhya | Fatullah New 33/11 KV SS | 2500581.4639 | 2536449.5967
727 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902781 | 1 | 0 | 0 | 0 | 60000 | 0 | 0 | 0 | 0 | Fatullah New 33/11 KV SS | 0 | 0
728 | 11 kV Katherpol Feeder | 11 | 0 | 00000031 | 1 | 61558008 | 63394284 | 1836276 | 1 | 0 | 1836276 | 1872668.2415 | Fatullah | Dapa 33/11 kV | 1825325.1091 | 2095256.7912
729 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
730 | 11 kV Union Parishad Feeder | 11 | 0 | 00000032 | 1 | 63039328 | 64364204 | 1324876 | 1 | 0 | 1324876 | 1351133.0591 | Fatullah | Dapa 33/11 kV | 1174339.0851 | 1364658.7564
731 | 11 kV Shiachar Feeder | 11 | 0 | 00000030 | 1 | 63888724 | 65776000 | 1887276 | 1 | 0 | 1887276 | 1924678.9852 | Fatullah | Dapa 33/11 kV | 1907532.8668 | 1901950.2285
732 | 11 kV Sastapur Feeder | 11 | 0 | 00000106 | 1 | 69229072 | 70349912 | 1120840 | 1 | 0 | 1120840 | 1143053.371 | Fatullah | Dapa 33/11 kV | 1344939.9892 | 1492863.3157
733 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
734 | 11 kV Jalal Ahmed Express | 11 | 0 | 00000172 | 1 | 4960188 | 4960348 | 160 | 1 | 0 | 160 | 163.171 | Fatullah | Dapa 33/11 kV | 71453.7073 | 791901.0884
735 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
736 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
737 | 11 kV Lalpur Feeder | 11 | 0 | 00000044 | 1 | 76099056 | 77520128 | 1421072 | 1 | 0 | 1421072 | 1449235.5198 | Fatullah | Dapa 33/11 kV | 1159780.4978 | 373576.7292
738 | 11 kV Kotaler Bag Feeder | 11 | 0 | 00000050 | 1 | 81048560 | 82482440 | 1433880 | 1 | 0 | 1433880 | 1462297.3552 | Fatullah | Dapa 33/11 kV | 1401235.8745 | 1515181.1462
739 | 11 kV Idrakpur Feeder | 11 | 0 | 00000021 | 1 | 74625056 | 75647336 | 1022280 | 1 | 0 | 1022280 | 1042540.0593 | Fatullah | Dapa 33/11 kV | 1114166.2721 | 1068664.5804
740 | 11 kV Isdair Feeder | 11 | 0 | 00000029 | 1 | 39230944 | 40064264 | 833320 | 1 | 0 | 833320 | 849835.155 | Fatullah | Dapa 33/11 kV | 794122.676 | 792940.801
741 | 11 kV Shah Fateullah Express | 11 | 0 | 0000051 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0 | 0
742 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
743 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Dapa 33/11 kV | 0 | 0
744 | 11/0.415 kV Auxiliary Transformer, AT-1 | 0.415 | 0 | DHKF 7522 | 1 | 2955 | 3013 | 58 | 100 | 0 | 5800 | 5914.9473 | Fatullah | Dapa 33/11 kV | 5529.8501 | 5198.5629
745 | 11/0.415 kV Auxiliary Transformer, AT-2 | 0.415 | 0 | DHKF 7523 | 1 | 136 | 136 | 0 | 100 | 0 | 0 | 0 | Fatullah | Dapa 33/11 kV | 0 | 0
746 | 11 kV Bholail Feeder (F-3) | 11 | 0 | DHK 9335 | 1 | 68294.86 | 120042.476 | 51747.616 | 60 | 0 | 3104856.96 | 3113891.785 | Sytalakhya | Sitalakhya 33/11KV S/S | 3046734.2178 | 2464743.5384
747 | 11 kV Crony Apparels (F-2) | 11 | 0 | DHK 9336 | 1 | 28231.2805 | 48142.2979 | 19911.0174 | 60 | 0 | 1194661.044 | 1198137.3888 | Sytalakhya | Sitalakhya 33/11KV S/S | 1083589.5043 | 1409860.9795
748 | 11 kV Baburail Feeder (F-5) | 11 | 0 | DHK 9322 | 1 | 48193.1576 | 82394.5117 | 34201.3541 | 60 | 0 | 2052081.246 | 2058052.5984 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 2038840.2789 | 1960329.6227
749 | 11 kV Goghchar Feeder (F-1) | 11 | 0 | DHK 9323 | 1 | 90249.8775 | 112256.5511 | 22006.6736 | 60 | 0 | 1320400.416 | 1324242.6499 | Sytalakhya | Sitalakhya 33/11KV S/S | 1303267.9767 | 1261095.5642
750 | 11 kV Norshinghopur (F-2) | 11 | 0 | DHK 9365 | 1 | 70175.942 | 93513.646 | 23337.704 | 60 | 0 | 1400262.24 | 1404336.8639 | Sytalakhya | Sitalakhya 33/11KV S/S | 1352601.3966 | 1471201.0567
751 | 11 kV Geddar Bazar Feeder (F-4) | 11 | 0 | DHK 9367 | 1 | 106609.7103 | 106609.7103 | 0 | 60 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 33/11KV S/S | 0 | 554462.5713
752 | 11 kV Noluyapara Feeder (F-6)*** | 11 | 0 | H/A030701125-03 | 1 | 72836.303 | 73081.722 | 245.419 | 1000 | 0 | 245419 | 246133.1449 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 234255.9876 | 224598.6372
753 | 11 kV Kashipur Feeder (F-7) | 11 | 0 | H/A030800169-03 | 1 | 33256.036 | 34992.83 | 1736.794 | 1000 | 0 | 1736794 | 1741847.8978 | Sytalakhya | Sitalakhya 33/11KV S/S | 1664580.229 | 1652181.4751
754 | 11 kV Spare Feeder (F-6) | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 0 | 0
755 | 11 kV Paikpara Feeder (F-8) | 11 | 0 | H/A030701098-03 | 1 | 77120.905 | 78252.992 | 1132.087 | 1000 | 0 | 1132087 | 1135381.2606 | N.Gonj (West) | Sitalakhya 33/11KV S/S | 1090515.7468 | 1082731.082
756 | 11 kV B. K. Road Feeder (F-9) | 11 | 0 | H/A030800205-03 | 1 | 93822.411 | 94550.082 | 727.671 | 1000 | 0 | 727671 | 729788.4502 | N.Gonj (East) | Sitalakhya 33/11KV S/S | 786055.2221 | 765048.1281
757 | 11 kV Tamak Potti (Old Shahidnagar) Feeder (F-10) | 11 | 0 | H/A030701091-03 | 1 | 52130.183 | 53202.551 | 1072.368 | 1000 | 0 | 1072368 | 1075488.4842 | Sytalakhya | Sitalakhya 33/11KV S/S | 1015821.5301 | 958950.0681
758 | 11 kV River View | 11 | 0 | 00000061 | 1 | 5548248 | 6387048 | 838800 | 1 | 0 | 838800 | 841728.9793 | N.Gonj (East) | Mondalpara 33/11KV S/S | 838140.6773 | 803073.4017
759 | 11 kV Railgate B.B. Road | 11 | 0 | 00000191 | 1 | 22140866 | 22810540 | 669674 | 1 | 0 | 669674 | 672012.4136 | N.Gonj (East) | Mondalpara 33/11KV S/S | 662899.4007 | 611819.3181
760 | 11 kV DIT | 11 | 0 | 00000174 | 1 | 133509912 | 136605064 | 3095152 | 1 | 0 | 3095152 | 3105959.8639 | N.Gonj (West) | Mondalpara 33/11KV S/S | 3165323.9759 | 2992837.0935
761 | 11 kV Dalpatti | 11 | 0 | 00000182 | 1 | 3037272 | 3675991 | 638719 | 1 | 0 | 638719 | 640949.3228 | N.Gonj (East) | Mondalpara 33/11KV S/S | 661646.5082 | 714092.6513
762 | 11 kV South Chasara | 11 | 0 | 00000043 | 1 | 91543376 | 94325328 | 2781952 | 1 | 0 | 2781952 | 2791666.2107 | N.Gonj (West) | Mondalpara 33/11KV S/S | 2659640.365 | 2565218.7341
763 | 11 kV Spare | 11 | 0 | 00000137 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0
764 | 11 kV NCC Express | 11 | 0 | 00000019 | 1 | 96919 | 130297 | 33378 | 1 | 0 | 33378 | 33494.5516 | N.Gonj (East) | Mondalpara 33/11KV S/S | 30069.4219 | 22516.8296
765 | 11 kV Spare | 11 | 0 | 00000041 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0
766 | 11 kV Masuya Bazar | 11 | 0 | 00000173 | 1 | 4304069 | 5319947 | 1015878 | 1 | 0 | 1015878 | 1019425.3124 | N.Gonj (East) | Mondalpara 33/11KV S/S | 1009868.8027 | 967617.4501
767 | 11 kV Nitaigonj | 11 | 0 | 00000189 | 1 | 57402260 | 58092820 | 690560 | 1 | 0 | 690560 | 692971.3447 | N.Gonj (East) | Mondalpara 33/11KV S/S | 773236.8002 | 671875.6098
768 | 11 kV Shahid Nagar | 11 | 0 | 00000020 | 1 | 55724624 | 57039820 | 1315196 | 1 | 0 | 1315196 | 1319788.4916 | Sytalakhya | Mondalpara 33/11KV S/S | 1324869.236 | 1256708.9709
769 | 11 kV Bangla Bazar | 11 | 0 | 00000139 | 1 | 67598832 | 69252312 | 1653480 | 1 | 0 | 1653480 | 1659253.7348 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1635218.8108 | 1605498.2865
770 | 11 kV Vogoban Gonj | 11 | 0 | 00000181 | 1 | 1911915 | 2365594 | 453679 | 1 | 0 | 453679 | 455263.1874 | N.Gonj (East) | Mondalpara 33/11KV S/S | 451404.0608 | 442440.5963
771 | 11 kV Tanbazar | 11 | 0 | 00000138 | 1 | 47659964 | 48640480 | 980516 | 1 | 0 | 980516 | 983939.833 | N.Gonj (East) | Mondalpara 33/11KV S/S | 990185.2541 | 977004.8332
772 | 11 kV SS Road | 11 | 0 | 00000175 | 1 | 63912244 | 65297040 | 1384796 | 1 | 0 | 1384796 | 1389631.5256 | N.Gonj (West) | Mondalpara 33/11KV S/S | 1367265.5042 | 1304240.0244
773 | 11 kV Spare | 11 | 0 | 00000094 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Mondalpara 33/11KV S/S | 0 | 0
774 | 33/0.415 kV Auxiliary-1 | 0.415 | 0 | 0 | 1 | 2413.05 | 2500.38 | 87.33 | 100 | 0 | 8733 | 8763.4945 | N.Gonj (West) | Mondalpara 33/11KV S/S | 8081.1571 | 8402.5235
775 | 33/0.415 kV Auxiliary-2 | 0.415 | 0 | 0 | 1 | 3.98 | 3.98 | 0 | 100 | 0 | 0 | 0 | N.Gonj (West) | Mondalpara 33/11KV S/S | 0 | 0
776 | 11 kV Masdair Feeder (F-8) | 11 | 0 | XA575914 | 1 | 209842.6 | 212991.1 | 3148.5 | 1000 | 0 | 3148500 | 3190609.1379 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 3086175.0273 | 3077099.4263
777 | 11 kV Narayangonj (F-7) | 11 | 0 | XA575915 | 1 | 164247.4 | 165452.9 | 1205.5 | 1000 | 0 | 1205500 | 1221622.7778 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1186514.4598 | 1307443.1804
778 | 11 kV Nearest Feeder (F-6) | 11 | 0 | XA575927 | 1 | 104635.5 | 105393.1 | 757.6 | 1000 | 0 | 757600 | 767732.4068 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 814473.5094 | 997748.2737
779 | 11 kV BSCIC-2 Feeder (F-5) | 11 | 0 | XA575916 | 1 | 115029.2 | 116133.1 | 1103.9 | 1000 | 0 | 1103900 | 1118663.9439 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1197874.4889 | 1341268.5888
780 | 11 kV Abonti Color Tex. (F-4) | 11 | 0 | XA575912 | 1 | 54099.1 | 54786 | 686.9 | 1000 | 0 | 686900 | 696086.8403 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 614760.142 | 701320.2188
781 | 11 kV BSCIC-1 Feeder (F-3) | 11 | 0 | DHK66615 | 1 | 180.4877 | 194.7091 | 14.2215 | 60000 | 0 | 853287.3 | 864699.4622 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 933339.9033 | 1045632.3523
782 | 11 kV Shasongaon Feeder (F-2) | 11 | 0 | XA575920 | 1 | 230751.7 | 231721.5 | 969.8 | 1000 | 0 | 969800 | 982770.4437 | Sytalakhya | Narayangonj BSCIC 33/11KV S/S | 813154.9346 | 1189560.6195
783 | 11 kV Fakir Apparels Feeder (F-1) | 11 | 0 | XA575929 | 1 | 19036.6 | 20181.2 | 1144.6 | 1000 | 0 | 1144600 | 1159908.2799 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1225868.8461 | 1274022.8667
784 | 11 kV MS Dyeing (Old Enayetnagar) Feeder (F-9) | 11 | 0 | HA021100913-02 | 1 | 38386.576 | 38961.791 | 575.215 | 1000 | 0 | 575215 | 582908.1262 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 649651.6597 | 916096.371
785 | 11 kV BSCIC-4 Feeder (F-11) | 11 | 0 | HA021100682-02 | 1 | 57586.384 | 59519.019 | 1932.635 | 1000 | 0 | 1932635 | 1958482.735 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 2197501.257 | 2366722.3025
786 | 11 kV BSCIC-3 Feeder (F-10) | 11 | 0 | HA021100455-02 | 1 | 53001.889 | 54442.541 | 1440.652 | 1000 | 0 | 1440652 | 1459919.7827 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 1675803.0813 | 1827353.8856
787 | 11/0.415 KV Transformer,AT-1 | 0.415 | Analog | 2001123043161 | 1 | 3753.3 | 3813.8 | 60.5 | 160 | 0 | 9680 | 9809.4637 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 10077.9686 | 6902.8139
788 | 11/0.415 KV Transformer,AT-2 | 0.415 | Analog | 2001123043118 | 1 | 4101.3 | 4101.4 | 0.1 | 160 | 0 | 16 | 16.214 | N.Gonj (West) | Narayangonj BSCIC 33/11KV S/S | 519.3156 | 421.2985
789 | 11 kV Outgoing Feeder-1 (=F1) | 11 | 0 | 041808902757 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
790 | 11 kV Char-Syedpur Feeder(=F2) | 11 | 0 | 041808902749 | 1 | 381.72 | 402.78 | 21.06 | 60000 | 0 | 1263600 | 1258154.7044 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1256317.0074 | 1308593.1901
791 | 11 kV UltraTech Cement Feeder (=F3) | 11 | 0 | 041808902759 | 1 | 418.63 | 438.15 | 19.52 | 60000 | 0 | 1171200 | 1166152.8884 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1226848.5855 | 1401162.4833
792 | 11 kV Outgoing Feeder-4 (=F4) | 11 | 0 | 041808902748 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
793 | 11 kV Outgoing Feeder-5 (=F5) | 11 | 0 | 041808902754 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
794 | 11 kV Outgoing Feeder-6 (=F6) | 11 | 0 | 041808902758 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
795 | 11 kV Outgoing Feeder-7 (=F7) | 11 | 0 | 041808902776 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
796 | 11 kV Outgoing Feeder-8 with BPT-1 | 11 | 0 | 041808902855 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
797 | 11 kV Outgoing Feeder-9 with BPT-2 | 11 | 0 | 041808902854 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
798 | 11 kV Mokterpur Feeder (=F8) | 11 | 0 | 041808902786 | 1 | 252.09 | 275.64 | 23.55 | 60000 | 0 | 1413000 | 1406910.8874 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 1384414.4332 | 1059738.0772
799 | 11 kV Dhaleshwary Feeder (=F9) | 11 | 0 | 041808902789 | 1 | 164.08 | 178 | 13.92 | 60000 | 0 | 835200 | 831600.8302 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 763171.9877 | 845746.7241
800 | 11 kV Outgoing Feeder-12 (=F10) | 11 | 0 | 041808902800 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
801 | 11 kV Outgoing Feeder-13 (=F11) | 11 | 0 | 041808902787 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
802 | 11 kV Outgoing Feeder-14 (=F12) | 11 | 0 | 041808902777 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
803 | 11 kV Outgoing Feeder-15 (=F13) | 11 | 0 | 041808902779 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
804 | 11 kV Outgoing Feeder-16 (=F14) | 11 | 0 | 041808902783 | 1 | 0.03 | 0.03 | 0 | 60000 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
805 | 33/0.415 kV Transformer AT-1 | 0.415 | 0 | 041811907976 | 1 | 1481.22 | 1595.72 | 114.5 | 1 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 33/11 KV S/S New | 0 | 0
806 | 33/0.415 kV Transformer AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Char Syedpur 33/11 KV S/S New | 0 | 0
807 | 11 kV Manikdia Feeder | 11 | Mugdapara | HA021100482-02 | 1 | 69350978 | 70057178 | 706200 | 1 | 0 | 706200 | 704760.429 | Mugdapara | Amulia 33/11 kv | 655997.4572 | 731782.37
808 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0
809 | 11 kV Kayetpara Feeder | 11 | Demra | HA021100967-02 | 1 | 12677425 | 14050902 | 1373477 | 1 | 0 | 1373477 | 1370677.2015 | Demra | Amulia 33/11 kv | 1292488.6152 | 1242034.7233
810 | 11 kV Paity Feeder | 11 | Demra | HA021188676-02 | 1 | 331582 | 878768 | 547186 | 1 | 0 | 547186 | 546070.575 | Demra | Amulia 33/11 kv | 498813.9667 | 550647.0061
811 | 11 kV Bamuil Feeder | 11 | Demra | HA021100981-02 | 1 | 61396460 | 63742776 | 2346316 | 1 | 0 | 2346316 | 2341533.0936 | Demra | Amulia 33/11 kv | 2143176.0462 | 2258006.7634
812 | 11 kV Ali Ahmed School Feeder | 11 | Mugdapara | HA021101235-02 | 1 | 13507195 | 14096671 | 589476 | 1 | 0 | 589476 | 588274.3679 | Mugdapara | Amulia 33/11 kv | 552448.5186 | 1045691.8176
813 | 11 kV Amulia Model Town Feeder | 11 | Demra | 0 | 1 | 51481502 | 51647116 | 165614 | 1 | 0 | 165614 | 165276.4 | Demra | Amulia 33/11 kv | 158821.9675 | 145542.9861
814 | 11 kV Rajakhali Feeder | 11 | Demra | HA021100483-02 | 1 | 9680550 | 10934861 | 1254311 | 1 | 0 | 1254311 | 1251754.1184 | Demra | Amulia 33/11 kv | 1263380.0786 | 1242709.7581
815 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0
816 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0
817 | 33/0.415 kV Transformer, AT-2 | 0.415 | 0 | 0 | 1 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | Amulia 33/11 kv | 0 | 0
818 | 11 kV Nearest Feeder | 11 | 0 | HA021101060-02 | 1 | 73698434 | 75374744 | 1676310 | 1 | 0 | 1676310 | 1691601.9901 | Maniknagar | Maniknagar 33/11 KV SS | 1589546.8433 | 1558145.6337
819 | 11kV Spare | 11 | 0 | HA021100679-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 0
820 | 11 kV City Palli Feeder | 11 | 0 | HA021100937-02 | 1 | 76283711 | 77211413 | 927702 | 1 | 0 | 927702 | 936164.8797 | Maniknagar | Maniknagar 33/11 KV SS | 876024.4652 | 849393.0553
821 | 11 kV R K Mission Road Feeder | 11 | 0 | HA021101035-02 | 1 | 12539189 | 14171862 | 1632673 | 1 | 0 | 1632673 | 1647566.9154 | Maniknagar | Maniknagar 33/11 KV SS | 1564049.4804 | 1502639.6704
822 | 11 kV Janapath Feeder | 11 | 0 | HA021100864-02 | 1 | 25420957 | 27595235 | 2174278 | 1 | 0 | 2174278 | 2194112.6593 | Maniknagar | Maniknagar 33/11 KV SS | 2093083.5306 | 2005205.5254
823 | 11 kV Dhalpur Feeder | 11 | 0 | HA021100851-02 | 1 | 85288108 | 86139684 | 851576 | 1 | 0 | 851576 | 859344.4269 | Maniknagar | Maniknagar 33/11 KV SS | 844664.2379 | 860069.6023
824 | 11kV WTP | 11 | 0 | X0599387 | 1 | 1406.5 | 1406.5 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 145877.5724
825 | 11kV Kamalapur Water pumping | 11 | 0 | HA021100474-02 | 1 | 7638435 | 7638435 | 0 | 1 | Estimated | 36489.852 | 36822.7275 | Maniknagar | Maniknagar 33/11 KV SS | 20221.1849 | 24456.8935
826 | 11 kV Wasa Road Feeder | 11 | 0 | HA021001011-02 | 1 | 25380490 | 25380490 | 0 | 1 | Estimated | 2079921.564 | 2098895.465 | Maniknagar | Maniknagar 33/11 KV SS | 1863737.1947 | 2040994.3579
827 | 11kV Sutikhalpar Feeder | 11 | 0 | HA021101047-02 | 1 | 79907658 | 79907658 | 0 | 1 | Estimated | 2006941.86 | 2025250.0101 | Maniknagar | Maniknagar 33/11 KV SS | 1882771.0147 | 2076315.0532
828 | 11kV Spare | 11 | 0 | HA021101029-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0
829 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0
830 | 11kV Spare | 11 | 0 | HA021101068-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0
831 | 11kV Spare | 11 | 0 | HA021101243-02 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0
832 | 11kV Spare | 11 | 0 | Nill | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Maniknagar 33/11 KV SS | 0 | 0
833 | AT-1 | 0.415 | 0 | 6603506 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Maniknagar | Maniknagar 33/11 KV SS | 0 | 0
834 | 11kV Fakirapul Panir Tank Feeder | 11 | 0 | DHK86058 | 1 | 1678.29 | 1695.96 | 17.67 | 60000 | 0 | 1060200 | 1084055.9235 | Motijheel | Motijheel old 33/11 kV | 997541.2473 | 913140.3988
835 | 11kV Station Road Feeder | 11 | 0 | DHK86075 | 1 | 2374.67 | 2376.46 | 1.79 | 60000 | 0 | 107400 | 109816.6442 | Motijheel | Motijheel old 33/11 kV | 95033.1244 | 121832.4707
836 | 11kV Box Culvert Road Feeder | 11 | 0 | DHK86071 | 1 | 3125.25 | 3155.14 | 29.89 | 60000 | 0 | 1793400 | 1833753.908 | Motijheel | Motijheel old 33/11 kV | 1479451.1554 | 1996966.8828
837 | 11kV Mohamedan Club Feeder | 11 | 0 | DHK86062 | 1 | 1662.49 | 1678.4 | 15.91 | 60000 | 0 | 954600 | 976079.7817 | Motijheel | Motijheel old 33/11 kV | 1139171.2585 | 731597.9549
838 | 11kV Amina Ahmed Co. | 11 | 0 | DHK95754 | 1 | 104040 | 108136 | 4096 | 60 | 0 | 245760 | 251289.93 | Motijheel | Motijheel old 33/11 kV | 373020.341 | 139323.2709
839 | 11kV Bangabhaban -1 | 11 | 0 | DHK95752 | 1 | 4382 | 4382 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0
840 | 11kV Sonali Bank | 11 | 0 | DHK95753 | 1 | 50590 | 59617 | 9027 | 60 | 0 | 541620 | 553807.1772 | Motijheel | Motijheel old 33/11 kV | 446839.6196 | 345775.0268
841 | 11kV NCC Bank Feeder | 11 | 0 | DHK68123 | 1 | 316.13 | 320 | 3.87 | 60000 | 0 | 232200 | 237424.8118 | Motijheel | Motijheel old 33/11 kV | 404044.0578 | 147163.9744
842 | 11kV IFIC BANK Feeder | 11 | 0 | DHK68116 | 1 | 389.19 | 397.35 | 8.16 | 60000 | 0 | 489600 | 500616.6574 | Ramna | Motijheel old 33/11 kV | 354381.5863 | 554880.5594
843 | 11kV Arambagh Feeder | 11 | 0 | DHK68117 | 1 | 3354.56 | 3367.9 | 13.34 | 60000 | Calculated | 1239791.6453 | 1267688.622 | Motijheel | Motijheel old 33/11 kV | 59250.2714 | 488536.1447
844 | 11kV Nikotborti Feeder | 11 | 0 | DHK68114 | 1 | 1410.57 | 1425.76 | 15.19 | 60000 | 0 | 911400 | 931907.7237 | Motijheel | Motijheel old 33/11 kV | 862042.4055 | 655000.3125
845 | 11kV Agrani Bank Feeder | 11 | 0 | DHK95756 | 1 | 363305 | 367476 | 4171 | 60 | 0 | 250260 | 255891.186 | Motijheel | Motijheel old 33/11 kV | 369219.0161 | 144691.1372
846 | 11kV Bangladesh Bank-2 | 11 | 0 | DHK95755 | 1 | 521 | 527 | 6 | 60000 | Calculated | 764674.8795 | 781881.091 | Motijheel | Motijheel old 33/11 kV | 669891.5592 | 180939.3128
847 | 11kV PDB Design Feeder 14 | 11 | 0 | DHK95747 | 1 | 44960 | 44960 | 0 | 60 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0
848 | 11kV Bangabhaban-2 | 11 | 0 | DHK86056 | 1 | 4.09 | 4.09 | 0 | 60000 | 0 | 0 | 0 | Motijheel | Motijheel old 33/11 kV | 0 | 0
849 | 11/0.4 kV AT | 0.415 | 0 | ELIC5429 | 1 | 405596 | 411842 | 6246 | 1 | 0 | 6246 | 6386.5434 | Motijheel | Motijheel old 33/11 kV | 8270.9474 | 3518.2644
850 | 11 kV Central Weman | 11 | 0 | 41812909492 | 1 | 136.75 | 146.96 | 10.21 | 60000 | 0 | 612600 | 614594.3851 | Motijheel | Motijheel 33/11 KV SS (new) | 602582.0913 | 559727.7485
851 | 11 kV Spare Feeder 2 | 11 | 0 | 41812909500 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
852 | 11 kV K. M. Das Len | 11 | 0 | 41812909499 | 1 | 233.82 | 250.96 | 17.14 | 60000 | 0 | 1028400 | 1031748.0667 | Swamibag | Motijheel 33/11 KV SS (new) | 1006914.6746 | 933883.7569
853 | 11 kV Gopibag | 11 | 0 | 41812909517 | 1 | 34.11 | 36.93 | 2.82 | 60000 | 0 | 169200 | 169750.8488 | Motijheel | Motijheel 33/11 KV SS (new) | 161492.0005 | 148216.3898
854 | 11kV SPICE TV | 11 | 0 | 41812909518 | 1 | 11.09 | 14.9 | 3.81 | 60000 | 0 | 228600 | 229344.2319 | Narinda | Motijheel 33/11 KV SS (new) | 216326.9708 | 196416.8418
855 | 11 kV Spare Feeder 6 | 11 | 0 | 41812909485 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
856 | 11 kV Spare Feeder 7 | 11 | 0 | 41812909484 | 1 | 0.07 | 0.07 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
857 | 11 kV BPT-1 | 11 | 0 | 41812909551 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
858 | 11 kV BPT-2 | 11 | 0 | 41812909475 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
859 | 10 kV Spare Feeder 8 | 11 | 0 | 41812909549 | 1 | 0.02 | 0.02 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
860 | 11 kV Spare Feeder 9 | 11 | 0 | 41812909550 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
861 | 11 kV South Kamlapur | 11 | 0 | 41812909473 | 1 | 367.96 | 377.45 | 9.49 | 60000 | 0 | 569400 | 571253.7429 | Motijheel | Motijheel 33/11 KV SS (new) | 550760.0315 | 1048359.8303
862 | 11 kV Spare Feeder 11 | 11 | 0 | 41812909588 | 1 | 0.01 | 0.01 | 0 | 60000 | 0 | 0 | 0 | 0 | Motijheel 33/11 KV SS (new) | 0 | 0
863 | 11 kV Answer Camp | 11 | 0 | 41812909514 | 1 | 166.1 | 179.13 | 13.03 | 60000 | 0 | 781800 | 784345.2339 | Motijheel | Motijheel 33/11 KV SS (new) | 758048.2709 | 729031.836
864 | 11 kV Shapla Chattar | 11 | 0 | 41812909516 | 1 | 126.45 | 137.07 | 10.62 | 60000 | 0 | 637200 | 639274.4731 | Motijheel | Motijheel 33/11 KV SS (new) | 598966.5988 | 591058.0422
865 | 11 kV Sayedabad | 11 | 0 | 41812909497 | 1 | 89.79 | 94.88 | 5.09 | 60000 | 0 | 305400 | 306394.2625 | Swamibag | Motijheel 33/11 KV SS (new) | 315753.0159 | 300047.8135
866 | 33/0.4 kV Aux Transformer | 0.415 | 0 | 41901920686 | 1 | 1040.3 | 1130.78 | 90.48 | 1 | 0 | 0 | 0 | Motijheel | Motijheel 33/11 KV SS (new) | 0 | 0
867 | Inner Circular Road Feeder | 11 | 0 | BD014042 | 1 | 39265 | 40052 | 787 | 1000 | 0 | 787000 | 786225.5313 | Motijheel | P & T 33/11 KV SS | 2044037.2926 | 2028898.6132
868 | NSI New Building Expres Feeder | 11 | 0 | BD013982 | 1 | 9206 | 9624 | 418 | 1000 | 0 | 418000 | 417588.6558 | Ramna | P & T 33/11 KV SS | 429529.4901 | 413128.6457
869 | Police Hospital RMU Feeder | 11 | 0 | BD014044 | 1 | 3211 | 3401 | 190 | 1000 | 0 | 190000 | 189813.0254 | Rajarbag | P & T 33/11 KV SS | 182072.2195 | 167833.5123
870 | Jonaki O/H Feeder | 11 | 0 | BD014013 | 1 | 30996 | 32499 | 1503 | 1000 | 0 | 1503000 | 1501520.9321 | Rajarbag | P & T 33/11 KV SS | 1581312.3149 | 1420129.7195
871 | Nayapalton Overhead Feeder | 11 | 0 | BD014014 | 1 | 22642 | 23646 | 1004 | 1000 | 0 | 1004000 | 1003011.9866 | Ramna | P & T 33/11 KV SS | 1008941.636 | 976215.0449
872 | Masjid Gali Over Head Feeder | 11 | 0 | BD014016 | 1 | 12776 | 13676 | 900 | 1000 | 0 | 900000 | 899114.3306 | Ramna | P & T 33/11 KV SS | 924444.0314 | 878891.4697
873 | Spare Feeder (Feeder-8) | 11 | 0 | BD014009 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | P & T 33/11 KV SS | 0 | 0
874 | Mid Way Over Head Feeder | 11 | 0 | BD014015 | 1 | 20857 | 21881 | 1024 | 1000 | 0 | 1024000 | 1022992.3051 | Ramna | P & T 33/11 KV SS | 1000894.2451 | 972242.6541
875 | Palton Thana Over Head Feeder | 11 | 0 | BD014033 | 1 | 20890 | 22279 | 1389 | 1000 | 0 | 1389000 | 1387633.1169 | Rajarbag | P & T 33/11 KV SS | 1346932.0545 | 1294006.3108
876 | Police Hospital (South) U/G Feeder 7 | 11 | 0 | BD014034 | 1 | 12022 | 12204 | 182 | 1000 | 0 | 182000 | 181820.898 | Rajarbag | P & T 33/11 KV SS | 172012.9808 | 167833.5123
877 | China Town Express Feeder | 11 | 0 | BD013943 | 1 | 5830 | 6095 | 265 | 1000 | 0 | 265000 | 264739.2196 | Ramna | P & T 33/11 KV SS | 295741.6161 | 284025.9439
878 | Fakirapul Bazar O/H Feeder | 11 | 0 | BD014032 | 1 | 26543 | 27825 | 1282 | 1000 | 0 | 1282000 | 1280738.4132 | Motijheel | P & T 33/11 KV SS | 1354979.4454 | 1402253.9607
879 | PWD Ouarter (RMU) | 11 | 0 | BD013937 | 1 | 2011 | 2163 | 152 | 1000 | 0 | 152000 | 151850.4203 | Motijheel | P & T 33/11 KV SS | 150888.5797 | 145985.3628
880 | Postal Quarter RMU | 11 | 0 | BD013945 | 1 | 2500 | 2678 | 178 | 1000 | 0 | 178000 | 177824.8343 | Motijheel | P & T 33/11 KV SS | 174024.8285 | 164854.2192
881 | 11/0.4 kV AT-1 | 0.415 | 0 | DHKH4409 | 1 | 1316 | 1377 | 61 | 100 | 0 | 6100 | 6093.9971 | Rajarbag | P & T 33/11 KV SS | 301.7772 | 0
882 | 11/0.4 kV AT-2 | 0.415 | 0 | DHKH4411 | 1 | 454 | 508 | 54 | 100 | 0 | 5400 | 5394.686 | Rajarbag | P & T 33/11 KV SS | 0 | 5362.7276
883 | Amtola O/H Feeder | 11 | Rajarbag | 112 | 1 | 349.8 | 385 | 35.2 | 40000 | 0 | 1408000 | 1426015.7648 | Rajarbag | Kamalapur Railway 33/11 KV SS | 1381038.2208 | 1302977.567
884 | Police Telecom | 11 | Rajarbag | 130 | 1 | 58.9 | 63.9 | 5 | 40000 | 0 | 200000 | 202559.0575 | Rajarbag | Kamalapur Railway 33/11 KV SS | 214648.1692 | 201076.785
885 | Railway Colony O/H | 11 | Rajarbag | 177 | 1 | 242.4 | 263.8 | 21.4 | 40000 | 0 | 856000 | 866952.7661 | Rajarbag | Kamalapur Railway 33/11 KV SS | 866692.6078 | 735941.0332
886 | Shahjahanpur O/H Feeder | 11 | Rajarbag | 12 | 1 | 617 | 672.9 | 55.9 | 40000 | 0 | 2236000 | 2264610.2629 | Rajarbag | Kamalapur Railway 33/11 KV SS | 2211281.1394 | 2079133.9572
887 | 11 KV Majar Feeder | 11 | 0 | 96 | 1 | 32 | 42.3 | 10.3 | 40000 | 0 | 412000 | 417271.6585 | Motijheel | Kamalapur Railway 33/11 KV SS | 400946.5802 | 382045.8916
888 | 11 kV Feeder-6 | 11 | 0 | 11 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0
889 | Momenbagh O/H | 11 | Rajarbag | 107 | 1 | 304.8 | 318.7 | 13.9 | 40000 | 0 | 556000 | 563114.1799 | Rajarbag | Kamalapur Railway 33/11 KV SS | 1081340.777 | 1001362.3894
890 | 11 kV Feeder-8 | 11 | 0 | 179 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0
891 | 11 kV Uttara Bank Goli Feeder-9 | 11 | Rajarbag | 169 | 1 | 198.6 | 207.3 | 8.7 | 40000 | 0 | 348000 | 352452.7601 | Rajarbag | Kamalapur Railway 33/11 KV SS | 340197.0984 | 337808.9988
892 | 11 kV Baraka O/H Feeder-10 | 11 | Rajarbag | 49 | 1 | 209.5 | 220.6 | 11.1 | 40000 | 0 | 444000 | 449681.1077 | Rajarbag | Kamalapur Railway 33/11 KV SS | 437396.2693 | 402153.5701
893 | 11 kV Feeder-11 | 11 | 0 | 92 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0
894 | Dhaka Railway | 11 | Motijheel | 150 | 1 | 53.5 | 59.2 | 5.7 | 40000 | 0 | 228000 | 230917.3256 | Motijheel | Kamalapur Railway 33/11 KV SS | 222748.1001 | 217162.9278
895 | Jasimuddin Feeder-13 | 11 | 0 | 91 | 1 | 112.7 | 155 | 42.3 | 40000 | 0 | 1692000 | 1713649.6265 | Motijheel | Kamalapur Railway 33/11 KV SS | 1656435.8718 | 1097879.2463
896 | Police Box Feeder-14 | 11 | 0 | 18 | 1 | 52.8 | 69 | 16.2 | 40000 | 0 | 648000 | 656291.3463 | Motijheel | Kamalapur Railway 33/11 KV SS | 664194.3349 | 643445.7121
897 | 11 kV Feeder-15 | 11 | 0 | 171 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0
898 | 11 kV Feeder-16 | 11 | 0 | 204 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kamalapur Railway 33/11 KV SS | 0 | 0
899 | Auxiliary -1 (AT-1 ) | 0.415 | 0 | DHKF 7632 | 1 | 816.23 | 902.28 | 86.05 | 100 | 0 | 8605 | 8715.1034 | Rajarbag | Kamalapur Railway 33/11 KV SS | 2871.4255 | 5128.4634
900 | Auxiliary -1 (AT-2 ) | 0.415 | 0 | DHKF 7733 | 1 | 119.59 | 119.59 | 0 | 100 | 0 | 0 | 0 | Rajarbag | Kamalapur Railway 33/11 KV SS | 0 | 0
901 | 11 kV DIT S/S-1 Feeder | 11 | Motijheel | 4150750 | 1 | 214079.71 | 215236.15 | 1156.44 | 1000 | Estimated | 814940.028 | 816951.1322 | Motijheel | Bangabhaban 132/11KV S/S | 793502.3098 | 860468.6016
902 | 11 kV Bangabhaban Switching Circuit-1 | 11 | Motijheel | 4150743 | 1 | 24049.87 | 24132.19 | 82.32 | 1000 | 0 | 82320 | 82523.1488 | Motijheel | Bangabhaban 132/11KV S/S | 83389.7606 | 79020.0597
903 | 11 kV Saidabad Water Treatment | 11 | Maniknagar | 4150749 | 1 | 4129.6 | 4129.6 | 0 | 1000 | 0 | 0 | 0 | Maniknagar | Bangabhaban 132/11KV S/S | 0 | 0
904 | 11 kV Bangladesh Bank Feeder | 11 | Motijheel | 4150738 | 1 | 77077.43 | 77077.43 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 240728.715
905 | 11 kV P & T Substation | 11 | Motijheel | 4150751 | 1 | 376848.18 | 376848.18 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0
906 | 11 kV Osmani Feeder | 11 | Ramna | 4150754 | 1 | 33840.33 | 33853.02 | 12.69 | 1000 | Estimated | 0 | 0 | Ramna | Bangabhaban 132/11KV S/S | 0 | 20212.3186
907 | 11 kV Modhumita via Ovisar | 11 | Motijheel | 4150741 | 1 | 48388.29 | 48388.29 | 0 | 1000 | Estimated | 729797.04 | 731598.0289 | Motijheel | Bangabhaban 132/11KV S/S | 710599.0834 | 737544.5157
908 | 11 kV Sugar Bhaban & Car Parking | 11 | Motijheel | 4150753 | 1 | 15730.83 | 15810 | 79.17 | 1000 | 0 | 79170 | 79365.3753 | Motijheel | Bangabhaban 132/11KV S/S | 70158.8804 | 76837.1293
909 | 11 kV Motijheel-1 Feeder | 11 | South-2 | 4150748 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0
910 | 11 kV Navana O/H Feeder | 11 | Motijheel | 4150752 | 1 | 245496.9 | 246649.65 | 1152.75 | 1000 | 0 | 1152750 | 1155594.7497 | Motijheel | Bangabhaban 132/11KV S/S | 1181422.0182 | 1217478.907
911 | 11 kV Bangabhaban Switching Circuit-2 | 11 | Motijheel | 4150737 | 1 | 14313.16 | 14474.96 | 161.8 | 1000 | 0 | 161800 | 162199.2891 | Motijheel | Bangabhaban 132/11KV S/S | 174416.2041 | 171420.6744
912 | 11 kV Motijheel-2 Feeder | 11 | South-2 | 4150735 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0
913 | 11 kV WAPDA building RMU Feeder | 11 | Motijheel | 4150736 | 1 | 94938.39 | 94938.39 | 0 | 1000 | Estimated | 243265.68 | 243866.0096 | Motijheel | Bangabhaban 132/11KV S/S | 236866.3611 | 245848.1719
914 | 11 kV PDB Design Feeder | 11 | Motijheel | 4150747 | 1 | 163401.03 | 163764.06 | 363.03 | 1000 | 0 | 363030 | 363925.8833 | Motijheel | Bangabhaban 132/11KV S/S | 326878.2024 | 270087.1078
915 | 11 kV BB Hospital Zone RMU Feeder | 11 | Motijheel | 4150739 | 1 | 20538.85 | 20596.96 | 58.11 | 1000 | Estimated | 243265.68 | 243866.0096 | Motijheel | Bangabhaban 132/11KV S/S | 236866.3611 | 245848.1719
916 | 11 kV Sonali Bank RMU Feeder | 11 | Motijheel | 4150746 | 1 | 82365.95 | 82365.95 | 0 | 1000 | Estimated | 340571.952 | 341412.4135 | Motijheel | Bangabhaban 132/11KV S/S | 331612.9056 | 368772.2578
917 | 11 kV Janata Bank Feeder | 11 | Motijheel | 4150755 | 1 | 122597.98 | 122899.9 | 301.92 | 1000 | 0 | 301920 | 302665.0764 | Motijheel | Bangabhaban 132/11KV S/S | 348419.8864 | 313139.3465
918 | 11 kV DIT S/S RMU Feeder | 11 | Motijheel | 4150740 | 1 | 272305.38 | 273094.04 | 788.66 | 1000 | 0 | 788660 | 790606.2505 | Motijheel | Bangabhaban 132/11KV S/S | 819439.2218 | 796304.7174
919 | 11 kV Sena Kalyan Feeder | 11 | Motijheel | 4150745 | 1 | 80121.74 | 80707.72 | 585.98 | 1000 | 0 | 585980 | 587426.078 | Motijheel | Bangabhaban 132/11KV S/S | 481785.1466 | 474463.9677
920 | 11 kV BCIC Feeder | 11 | Motijheel | 4150756 | 1 | 192447.87 | 192560.77 | 112.9 | 1000 | Estimated | 340571.952 | 341412.4135 | Motijheel | Bangabhaban 132/11KV S/S | 331612.9056 | 368772.2578
921 | 11/0.4 kV AT-1 | 0.415 | 0 | 63412931 | 1 | 63258 | 66825 | 3567 | 1 | 0 | 3567 | 3575.8026 | Motijheel | Bangabhaban 132/11KV S/S | 0 | 0
922 | 11/0.4 kV AT-2 | 0.415 | 0 | 63403117 | 1 | 13772 | 22885 | 9113 | 1 | Estimated | 5000 | 5012.339 | Motijheel | Bangabhaban 132/11KV S/S | 5030.7529 | 5053.0797
923 | 11 kV Bonogram Feeder | 11 | Narinda | 06604467 | 1 | 24616.19 | 24756.85 | 140.66 | 8000 | 0 | 1125280 | 1143423.9412 | Narinda | Narinda 33/11KV S/S | 1139801.4532 | 1096395.2732
924 | 11 kV Sha Saheb Len Feeder | 11 | Narinda | 06604469 | 1 | 16642.26 | 16724.98 | 82.72 | 8000 | 0 | 661760 | 672430.175 | Swamibag | Narinda 33/11KV S/S | 685656.1379 | 629657.0471
925 | 11 kV Sadiabad Water Treatment | 11 | Maniknagar | 06604354 | 1 | 487.34 | 500.94 | 13.6 | 40000 | 0 | 544000 | 552771.4205 | Maniknagar | Narinda 33/11KV S/S | 653217.1868 | 492385.8425
926 | 11 kV Manashi Feeder | 11 | Narinda | 06604353 | 1 | 5501.64 | 5528.76 | 27.12 | 40000 | 0 | 1084800 | 1102291.2443 | Narinda | Narinda 33/11KV S/S | 1122855.7324 | 1066634.3599
927 | 11 kV Jatrabari Feeder | 11 | Maniknagar | 06604324 | 1 | 3373.76 | 3426.03 | 52.27 | 40000 |  | 2090800 | 2124511.9226 | Swamibag | Narinda 33/11KV S/S | 2030258.73 | 1913892.8816
928 | 11 kV Wari Feeder | 11 | Swamibag | 06604291 | 1 | 8518.25 | 8559.74 | 41.49 | 40000 | 0 | 1659600 | 1686359.282 | Narinda | Narinda 33/11KV S/S | 1652611.2397 | 1532808.0158
929 | 11 kV Narinda Feeder | 11 | Narinda | 06604348 | 1 | 7262.99 | 7302.23 | 39.24 | 40000 | 0 | 1569600 | 1594908.1278 | Narinda | Narinda 33/11KV S/S | 1590073.4608 | 1585232.3889
930 | 11 kV Distillary Feeder | 11 | Swamibag | 06604347 | 1 | 5965.54 | 5997.97 | 32.43 | 40000 | 0 | 1297200 | 1318115.968 | Swamibag | Narinda 33/11KV S/S | 1326607.8506 | 1271895.9437
931 | 11 kV Thatari Bazar Feeder | 11 | Narinda | 06604296 | 1 | 5006.32 | 5033.32 | 27 | 40000 | 0 | 1080000 | 1097413.8494 | Narinda | Narinda 33/11KV S/S | 1083315.7174 | 1015016.5156
932 | 11 kV Swamibagh Feeder | 11 | Swamibag | 06604352 | 1 | 7762.22 | 7795.93 | 33.71 | 40000 | 0 | 1348400 | 1370141.5135 | Swamibag | Narinda 33/11KV S/S | 1100261.4381 | 886375.1694
933 | 11 kV Tipu Sultan Feeder | 11 | Narinda | 06604322 | 1 | 6347.36 | 6375.33 | 27.97 | 40000 | 0 | 1118800 | 1136839.4581 | Narinda | Narinda 33/11KV S/S | 1115189.8112 | 1101315.099
934 | 11 kV Spare | 11 | Narinda | 06604294 | 1 | 7330.46 | 7330.46 | 0 | 40000 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0
935 | 11 kV Folder Street Feeder | 11 | Narinda | DHK00089 | 1 | 26064.5 | 30046.6 | 3982.1 | 444.44 | 0 | 1769804.524 | 1798340.7365 | Narinda | Narinda 33/11KV S/S | 1748933.3106 | 1624153.5662
936 | 11 kV Bhajohari Feeder | 11 | Narinda | DHK27842 | 1 | 384194 | 394199 | 10005 | 80 | 0 | 800400 | 813305.5973 | Narinda | Narinda 33/11KV S/S | 819688.7194 | 775800.0686
937 | 11 kV Lal mohon shaha Feeder | 11 | Narinda | DHK00086 | 1 | 31907.7 | 34337.3 | 2429.6 | 444.44 | 0 | 1079811.424 | 1097222.2328 | Narinda | Narinda 33/11KV S/S | 1092539.7614 | 1048880.237
938 | 11 kV Dupkhola Feeder | 11 | Swamibag | 8838024/8838029 | 1 | 36247.2 | 36817.8 | 570.6 | 1000 | 0 | 570600 | 579800.3171 | Swamibag | Narinda 33/11KV S/S | 568589.4506 | 537047.3757
939 | 11/0.4 kV Aux Transformer-1 | 0.415 | 0 | DHK-21032 | 1 | 127912 | 127912 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0
940 | 11/0.4 kV Aux Transformer-2 | 0.415 | 0 | DHK-21094 | 1 | 214733 | 214733 | 0 | 4 | 0 | 0 | 0 | Narinda | Narinda 33/11KV S/S | 0 | 0
941 | 11kV Babubazar Feeder | 11 | Banglabazar | DHK00004 | 1 | 62362.9 | 62634.8 | 271.9 | 2222.22 | 0 | 604221.618 | 604954.0102 | Banglabazar | Kumertuly 33/11KV S/S | 476949.7245 | 555416.4351
942 | 11kV Islampur Feeder | 11 | Banglabazar | 06604381 | 1 | 4560.66 | 4589.74 | 29.08 | 40000 | 0 | 1163200 | 1164609.944 | Banglabazar | Kumertuly 33/11KV S/S | 1430849.1736 | 1481110.4937
943 | 11kV Champatully Feeder | 11 | Bangshal | 06604404 | 1 | 903.15 | 903.15 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 0 | 0
944 | 11kV Majar O/H Feeder | 11 | Banglabazar | 06604385 | 1 | 5132.38 | 5143.44 | 11.06 | 40000 | 0 | 442400 | 442936.2442 | Banglabazar | Kumertuly 33/11KV S/S | 536568.4401 | 493703.4979
945 | 11kV Spare | 11 | Banglabazar | 06604380 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | Kumertuly 33/11KV S/S | 0 | 0
946 | 11kV Sadarghat Feeder | 11 | Banglabazar | 06604315 | 1 | 5420.2 | 5442.14 | 21.94 | 40000 | 0 | 877600 | 878663.7611 | Banglabazar | Kumertuly 33/11KV S/S | 1216221.7976 | 1419397.5564
947 | 11kV Mitford Hospital Feeder | 11 | Bangshal | 06604409 | 1 | 1013.7 | 1013.7 | 0 | 40000 | 0 | 0 | 0 | Bangshal | Kumertuly 33/11KV S/S | 40077.0255 | 0
948 | 11kV Zindabahar Feeder | 11 | Banglabazar | 06604405 | 1 | 4052.11 | 4079.87 | 27.76 | 40000 | 0 | 1110400 | 1111745.9438 | Banglabazar | Kumertuly 33/11KV S/S | 834662.018 | 740555.2468
949 | 11kV Police fari Feeder | 11 | Banglabazar | 06604408 | 1 | 5739.2 | 5739.2 | 0 | 40000 | Estimated | 1216328.4 | 1217802.7423 | Banglabazar | Kumertuly 33/11KV S/S | 1144679.3389 | 925694.0585
950 | 11kV Patuatully Feeder | 11 | Banglabazar | 06604383 | 1 | 5878.45 | 5901.7 | 23.25 | 40000 | 0 | 930000 | 931127.2764 | Banglabazar | Kumertuly 33/11KV S/S | 1021492.1651 | 1019206.2302
951 | 11kV Laxmibazar Feeder | 11 | Banglabazar | 06604407 | 1 | 8147.67 | 8198.55 | 50.88 | 40000 | 0 | 2035200 | 2037666.9172 | Banglabazar | Kumertuly 33/11KV S/S | 1989498.8221 | 1947085.7372
952 | 11kV Jhonson Road Feeder | 11 | Banglabazar | 06604384 | 1 | 3746.74 | 3757.99 | 11.25 | 40000 | 0 | 450000 | 450545.4563 | Banglabazar | Kumertuly 33/11KV S/S | 410865.9482 | 427409.0643
953 | 11kV Dholaikhal Feeder | 11 | Banglabazar | 06604379 | 1 | 7200.1 | 7226.32 | 26.22 | 40000 | 0 | 1048800 | 1050071.2769 | Banglabazar | Kumertuly 33/11KV S/S | 1251993.0269 | 1073805.1079
954 | 11kV Bikrompur Garden City Feeder | 11 | Banglabazar | 06604406 | 1 | 3579.1 | 3585.71 | 6.61 | 40000 | 0 | 264400 | 264720.4859 | Banglabazar | Kumertuly 33/11KV S/S | 275126.2119 | 281286.3072
955 | 11/0.4 kV AT-1 | 0.415 | 0 | 05379603 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | Banglabazar | Kumertuly 33/11KV S/S | 0 | 0
956 | 11/0.4 kV AT-2 | 0.415 | 0 | 05378636 | 1 | 165364.8 | 168944.8 | 3580 | 2 | 0 | 7160 | 7168.6788 | Banglabazar | Kumertuly 33/11KV S/S | 4775.6076 | 4915.4072
957 | 11 kV Bangladesh Math Feeder | 11 | Bangshal | 340180017728 | 1 | 37591630 | 38350227 | 758597 | 1 | 0 | 758597 | 760951.1172 | Bangshal | Banshal 33/11KV S/S | 778854.3109 | 716311.3918
958 | 11 kV Spare Feeder | 11 | Bangshal | 340180025257 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0
959 | 11 kV Siddikbazar Feeder | 11 | Bangshal | 340180016897 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0
960 | 11 kV Tatibazar feeder | 11 | Banglabazar | 340180016042 | 1 | 48292149 | 49714612 | 1422463 | 1 | 0 | 1422463 | 1426877.2604 | Banglabazar | Banshal 33/11KV S/S | 1429747.5487 | 1353751.6158
961 | 11 kV Bangsal Road Feeder | 11 | Bangshal | 340180015747 | 1 | 19895217 | 20644794 | 749577 | 1 | 0 | 749577 | 751903.1259 | Bangshal | Banshal 33/11KV S/S | 737930.5287 | 715455.6721
962 | 11 kV Hazi Osman Gani Feeder | 11 | Bangshal | 340180012709 | 1 | 45156791 | 46320451 | 1163660 | 1 | 0 | 1163660 | 1167271.1296 | Bangshal | Banshal 33/11KV S/S | 1660584.0104 | 1409457.3709
963 | 11 kV French Road Feeder | 11 | Bangshal | 340180016889 | 1 | 61068329 | 62248027 | 1179698 | 1 | 0 | 1179698 | 1183358.8995 | Bangshal | Banshal 33/11KV S/S | 1169829.7548 | 1127796.6211
964 | 11 kV North-South Road Feeder | 11 | Bangshal | 340180015534 | 1 | 28992386 | 30418512 | 1426126 | 1 | 0 | 1426126 | 1430551.6276 | Bangshal | Banshal 33/11KV S/S | 1633419.2244 | 1486833.0286
965 | 11 kV Nazirabazar Feeder | 11 | Bangshal | 340180025261 | 1 | 61260126 | 62764098 | 1503972 | 1 | 0 | 1503972 | 1508639.2033 | Bangshal | Banshal 33/11KV S/S | 1596892.4609 | 1498407.2378
966 | 11 kV Suritolla Feeder | 11 | Narinda | 340180025212 | 1 | 49123470 | 50259494 | 1136024 | 1 | 0 | 1136024 | 1139549.3681 | Narinda | Banshal 33/11KV S/S | 1267199.3373 | 1145519.8164
967 | AT-1 | 0.415 | 0 | DHK-4415 | 1 | 727.72 | 734.14 | 6.42 | 100 | 0 | 0 | 0 | Bangshal | Banshal 33/11KV S/S | 0 | 0
968 | AT-2 | 0.415 | 0 | DHK-4410 | 1 | 659.01 | 684.51 | 25.5 | 100 | 0 | 7000 | 7021.7228 | Bangshal | Banshal 33/11KV S/S | 7023.9917 | 6997.7081
969 | 11 kV Nayanagor Feeder | 11 | Kazla | DHK-61125 | 1 | 813181.6 | 843800.5 | 30618.9 | 60 | 0 | 1837134 | 1866699.9643 | Kazla | Kazla 33/11KV S/S | 1792344.292 | 1710856.4639
970 | 11 kV Madrasa Bazar Feeder | 11 | Kazla | HA-021101033-02 | 3 | 38764513 | 38764513 | 0 | 1 | Estimated | 1824492.6 | 1853855.1196 | Kazla | Kazla 33/11KV S/S | 1913492.0332 | 1855425.2355
971 | 11 kV Kazla Feeder | 11 | Kazla | HA021101071 | 1 | 94698216 | 94698216 | 0 | 1 | Estimated | 2980004.58 | 3027963.362 | Kazla | Kazla 33/11KV S/S | 3049627.928 | 2968680.3768
972 | 11 kV Sayedabad Feeder | 11 | Maniknagar | HA021101239-02 | 1 | 36963854 | 36963861 | 7 | 1000 | Estimated | 973062.72 | 988722.7304 | Maniknagar | Kazla 33/11KV S/S | 1076339.2687 | 556627.5706
973 | 11 kV Zenith Feeder | 11 | Kazla | HA-021101068-02 | 1 | 4111597 | 4111597 | 0 | 1 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0
974 | 11 kV Paterbagh Feeder | 11 | Jurain | HA-021200060 | 1 | 112225.6 | 114727 | 2501.4 | 1000 | 0 | 2501400 | 2541656.3466 | Jurain | Kazla 33/11KV S/S | 2207984.2138 | 2092993.2394
975 | 11 kV Matuail Feeder | 11 | Kazla | HA-021100984 | 1 | 41024544 | 59876429 | 18851885 | 1 | Estimated | 1702859.76 | 1730264.7783 | Kazla | Kazla 33/11KV S/S | 1734102.1551 | 1855425.2355
976 | 11 kV Kutubkhali Feeder | 11 | Jurain | DHK-61117 | 1 | 684518.2 | 723552 | 39033.8 | 60 | 0 | 2342028 | 2379719.4891 | Jurain | Kazla 33/11KV S/S | 2279252.9698 | 2232712.5636
977 | 11 kV Mridhabari Feeder | 11 | Kazla | DHK-61118 | 1 | 602385.9 | 624583.7 | 22197.8 | 60 | 0 | 1331868 | 1353302.4526 | Kazla | Kazla 33/11KV S/S | 1381440.9902 | 1371332.0993
978 | 11 kV Muslim Nagar Feeder | 11 | Kazla | DHK-61011 | 1 | 986124.4 | 1025255.2 | 39130.8 | 60 | 0 | 2347848 | 2385633.1534 | Kazla | Kazla 33/11KV S/S | 2345596.1288 | 2459477.0573
979 | 11 kV Jatrabari Thana Feeder | 11 | Kazla | DHK-61010 | 1 | 104864.1 | 104864.1 | 0 | 60 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0
980 | 11 kV Mirhazirbag Feeder | 11 | Swamibag | DHK-61008 | 1 | 212446.1 | 246764.7 | 34318.6 | 60 | 0 | 2059116 | 2092254.4374 | Swamibag | Kazla 33/11KV S/S | 2069592.0061 | 1962979.7252
981 | 11 kV Mukti Sharani Feeder | 11 | Jurain | DHK-61014 | 1 | 73285.9 | 113721.9 | 40436 | 60 | 0 | 2426160 | 2465205.4697 | Jurain | Kazla 33/11KV S/S | 2452063.3964 | 2370251.5382
982 | 11 kV Kadamtali Feeder | 11 | Shympur | DHK-61006 | 1 | 290452 | 326888.5 | 36436.5 | 60 | 0 | 2186190 | 2221373.5062 | Shyampur | Kazla 33/11KV S/S | 2471771.8805 | 3092469.9692
983 | 11kV Rayerbagh Feeder | 11 | Matuail | DHK-61012 | 1 | 383226.2 | 404227.5 | 21001.3 | 60 | 0 | 1260078 | 1280357.0984 | Matuail | Kazla 33/11KV S/S | 1277473.0974 | 837095.6004
984 | 11 kV Donia Feeder | 11 | Jurain | DHK-61013 | 1 | 1945817 | 1980100 | 34283 | 60 | 0 | 2056980 | 2090084.0617 | Jurain | Kazla 33/11KV S/S | 2017361.1702 | 1952856.964
985 | 11 kV Nimtoli Feeder | 11 | Kazla | HA-021100855-02 | 1 | 27937314 | 29423230 | 1485916 | 1 | 0 | 1485916 | 1509829.6282 | Kazla | Kazla 33/11KV S/S | 1633862.5979 | 1591423.3402
986 | 11 kV Gobindapur Feeder | 11 | Kazla | HA-021101057-02 | 1 | 25965046 | 26674761 | 709715 | 1 | 0 | 709715 | 721136.817 | Kazla | Kazla 33/11KV S/S | 697773.6086 | 686441.9856
987 | 11 kV Eidgaon (Kabarsthan) Feeder | 11 | Kazla | 9A56136 | 1 | 3086.1 | 3271.9 | 185.8 | 10000 | 0 | 1858000 | 1887901.7718 | Kazla | Kazla 33/11KV S/S | 1946667.4736 | 1703398.1226
988 | 11 kV Samad Nagar Gate (Old) | 11 | Kazla | 8L55983 | 1 | 15354.9 | 15354.9 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0
989 | 11 kV Dharmik Para | 11 | Kazla | 8K55676 | 1 | 814.2 | 814.2 | 0 | 4000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 23977.7413 | 1140208.9403
990 | 11 kV Sheikhdi Feeder | 11 | Kazla | 9A56133 | 1 | 13448.4 | 14288.8 | 840.4 | 4000 | 0 | 3361600 | 3415699.9979 | Kazla | Kazla 33/11KV S/S | 3248780.7482 | 3103743.9224
991 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0
992 | 11 kV Jenith Feeder | 11 | Kazla | 61903661 | 1 | 20321.3 | 20864.4 | 543.1 | 1000 | 0 | 543100 | 551840.3941 | Kazla | Kazla 33/11KV S/S | 574043.3834 | 0
993 | 11 KV Samad Nagor Gate | 11 | Kazla | 61903675 | 1 | 17160.4 | 17718.5 | 558.1 | 2000 | 0 | 1116200 | 1134163.594 | Kazla | Kazla 33/11KV S/S | 1293375.6231 | 1288887.6302
994 | 11 KV Bibir Bagicha | 11 | Maniknagar | 61903557 | 1 | 35605.2 | 36323.7 | 718.5 | 2000 | 0 | 1437000 | 1460126.3972 | Maniknagar | Kazla 33/11KV S/S | 1445370.1189 | 1356006.601
995 | 33/0.4 kV AT-1 | 0.415 | 0 | 503043 | 1 | 96204 | 96204 | 0 | 10 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 244.069
996 | 33/0.4 kV AT-2 | 0.415 | 0 | 503044 | 1 | 93292 | 93994 | 702 | 10 | 0 | 6000 | 6096.5612 | Kazla | Kazla 33/11KV S/S | 6096.0359 | 6101.7246
997 | Auxiliary Transformer | 0.415 | 0 | 41901920685 | 1 | 2290.62 | 2407.99 | 117.37 | 160 | 0 | 0 | 0 | Kazla | Kazla 33/11KV S/S | 0 | 0
998 | 11 kV HR (Hajrat_Rahima) Steel Express | 11 | Shympur | 0 | 1 | 579.6764 | 625.64 | 45.9636 | 40000 | 0 | 1838544 | 1848660.4463 | Shyampur | Shyampur 33/11KV S/S | 1329002.2614 | 1796570.0888
999 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1000 | 11 kV Road No.-21 Feeder | 11 | 0 | BD001943 | 1 | 1030.3488 | 1043.7 | 13.3512 | 40000 | 0 | 534048 | 536986.5578 | Shyampur | Shyampur 33/11KV S/S | 689153.8135 | 726162.1684
1001 | 11 kV New Chakda Feeder | 11 | Shympur | BD001932 | 1 | 1510.017 | 1527.03 | 17.013 | 40000 | 0 | 680520 | 684264.5087 | Shyampur | Shyampur 33/11KV S/S | 768373.9842 | 842780.9272
1002 | 11 kV Burigonga Feeder | 11 | Shympur | BD001946 | 1 | 1400.2733 | 1416.53 | 16.2567 | 40000 | 0 | 650268 | 653846.0494 | Shyampur | Shyampur 33/11KV S/S | 678120.977 | 664045.6474
1003 | 11 kV Dapa-Pagla Feeder | 11 | Fatulla | BD001953 | 1 | 1286.4505 | 1313.82 | 27.3695 | 40000 | 0 | 1094780 | 1100803.9423 | Fatullah | Shyampur 33/11KV S/S | 1060453.8119 | 1011898.1651
1004 | 11 kV S. R. Steel Feeder. | 11 | Shympur | BD001945 | 1 | 3240.1803 | 3283.24 | 43.0597 | 40000 | 0 | 1722388 | 1731865.3068 | Shyampur | Shyampur 33/11KV S/S | 2347543.3088 | 2415731.5404
1005 | 11 kV Rahima Steel Feeder. | 11 | Shympur | BD001956 | 1 | 191.09 | 191.09 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1006 | 11 kV Chand Textile Feeder | 11 | Shympur | BD001933 | 1 | 2102.0425 | 2133.5 | 31.4575 | 40000 | 0 | 1258300 | 1265223.6985 | Shyampur | Shyampur 33/11KV S/S | 1510257.147 | 1400226.6095
1007 | 11 kV Kamalpur Feeder | 11 | Fatulla | BD001922 | 1 | 484.1231 | 486.4 | 2.2769 | 40000 | 0 | 91076 | 91577.1387 | Fatullah | Shyampur 33/11KV S/S | 112254.6055 | 96981.9232
1008 | 11 kV Alizan Steel Feeder | 11 | Shympur | BD001931 | 1 | 3076.6439 | 3122.73 | 46.0861 | 40000 | 0 | 1843444 | 1853587.4081 | Shyampur | Shyampur 33/11KV S/S | 1927999.1795 | 1824622.7112
1009 | 11 kV Redwan Steel Feeder | 11 | Shympur | BD001933 | 1 | 1921.3681 | 1944.14 | 22.7719 | 40000 | 0 | 910876 | 915888.0248 | Shyampur | Shyampur 33/11KV S/S | 1677475.7016 | 1601003.2355
1010 | 11 kV Kadamtolly Steel Feeder | 11 | Shympur | BD001923 | 1 | 1406.4167 | 1444.14 | 37.7233 | 40000 | 0 | 1508932 | 1517234.7817 | Shyampur | Shyampur 33/11KV S/S | 1359049.2203 | 1887540.7358
1011 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1012 | 11 kV Orient-Al-Islam Feeder | 11 | Shympur | BD001949 | 1 | 807.729 | 820.21 | 12.481 | 40000 | 0 | 499240 | 501987.0295 | Shyampur | Shyampur 33/11KV S/S | 565017.3838 | 552636.6613
1013 | 11 kV Delpara Feeder | 11 | Shympur | BD001937 | 1 | 1294.1832 | 1313.8 | 19.6168 | 40000 | 0 | 784672 | 788989.597 | Shyampur | Shyampur 33/11KV S/S | 774228.7961 | 1030332.7456
1014 | 11 kV Wasa Feeder | 11 | Shympur | BD001928 | 1 | 2914.5187 | 2984.83 | 70.3113 | 40000 | 0 | 2812452 | 2827927.2998 | Shyampur | Shyampur 33/11KV S/S | 2567335.031 | 2104748.1835
1015 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1016 | 11 kV Al Noor-Femous Steel Feeder | 11 | Shympur | BD001938 | 1 | 1098.2827 | 1102.63 | 4.3473 | 40000 | 0 | 173892 | 174848.8273 | Shyampur | Shyampur 33/11KV S/S | 295251.5179 | 251271.3464
1017 | 11 kV Shyampur Bazar Feeder | 11 | Shympur | BD001939 | 1 | 1916.4054 | 1946.25 | 29.8446 | 40000 | 0 | 1193784 | 1200352.7042 | Shyampur | Shyampur 33/11KV S/S | 1365805.0805 | 1428279.2319
1018 | 11 kV Spare Feeder | 11 | Shympur | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1019 | 11 kV Binimoy Feeder | 11 | Shympur | BD001942 | 1 | 1335.0577 | 1349.95 | 14.8923 | 40000 | 0 | 595692 | 598969.7492 | Shyampur | Shyampur 33/11KV S/S | 543740.6288 | 732574.1964
1020 | 11 kV Akbar-Nabi Steel | 11 | Shympur | BD001941 | 1 | 1300.6173 | 1323.77 | 23.1527 | 40000 | 0 | 926108 | 931203.8377 | Shyampur | Shyampur 33/11KV S/S | 1080348.9594 | 971021.4868
1021 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1022 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1023 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1024 | 11 kV Rasulpur Feeder | 11 | Shympur | BD001943 | 1 | 2199.2196 | 2236.38 | 37.1604 | 40000 | 0 | 1486416 | 1494594.8892 | Shyampur | Shyampur 33/11KV S/S | 1526560.1151 | 1250345.4555
1025 | 11 Kv Pioneer Steel Feeder | 11 | Shympur | BD001924 | 1 | 170.7545 | 172.64 | 1.8855 | 40000 | 0 | 75420 | 75834.9927 | Shyampur | Shyampur 33/11KV S/S | 95891.5675 | 84558.6189
1026 | 11 kV Spare Feeder | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1027 | 11 kV Sun Steel Feeder | 11 | Shympur | BD001935 | 1 | 1172.4449 | 1189.74 | 17.2951 | 40000 | 0 | 691804 | 695610.598 | Shyampur | Shyampur 33/11KV S/S | 869607.7672 | 875642.5706
1028 | 11 kV Taher Steel Feeder | 11 | Shympur | BD001942 | 1 | 3633.3532 | 3687.08 | 53.7268 | 40000 | 0 | 2149072 | 2160897.1026 | Shyampur | Shyampur 33/11KV S/S | 1905144.5888 | 2092324.8793
1029 | 11 kV Igloo Feeder | 11 | Shympur | BD001942 | 1 | 1076.0762 | 1095.43 | 19.3538 | 40000 | 0 | 774153.6 | 778413.3204 | Shyampur | Shyampur 33/11KV S/S | 463585.7706 | 590307.3256
1030 | 11/0.4 kV Aux Transformer, T-1 | 0.415 | DPDC | DHK20964 | 1 | 504582.2 | 504582.2 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1031 | 33/0.4 kV Aux TR, GT-4 (At 11 kV) | 0.415 | DPDC | DHK26108 | 1 | 63432.6 | 63890 | 457.4 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1032 | 33/0.4 kV Aux TR, GT-3 (At-33 kV) | 0.415 | 0 | 0 | 1 | 586899 | 594876 | 7977 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1033 | 11/0.4 kV Aux Transformer, T-2 | 0.415 | 0 | DHK20964 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur 33/11KV S/S | 0 | 0
1034 | 11 kV Nama shyampur Feeder | 11 | Shympur | HA-021101066-02 | 1 | 35723650 | 37882493 | 2158843 | 1 | 0 | 2158843 | 2142439.5507 | Shyampur | Shyampur BISIC 33/11KV S/S | 2098065.1104 | 2051822.5774
1035 | 11 kV Bombay SweetsFeeder | 11 | Jurain | HA-021101063-02 | 1 | 20537911 | 21288823 | 750912 | 1 | 0 | 750912 | 745206.3758 | Jurain | Shyampur BISIC 33/11KV S/S | 738065.3088 | 731764.9753
1036 | 11 kV H. R Steel | 11 | Shympur | HA-021100377-02 | 1 | 24410033 | 24410033 | 0 | 1 | 0 | 0 | 0 | Shyampur | Shyampur BISIC 33/11KV S/S | 0 | 0
1037 | 11 kV Shyampur Incoming (F1) | 11 | Import | DHK61020 | 1 | 9697.2 | 9697.2 | 0 | 60 | 0 | 0 | 0 | Jurain | Shyampur BISIC 33/11KV S/S | 0 | 0
1038 | 11 kV Ali Bahar Feeder (F2) | 11 | Jurain | DHK61021 | 1 | 410183.5 | 437001.6 | 26818.1 | 60 | 0 | 1609086 | 1596859.747 | Jurain | Shyampur BISIC 33/11KV S/S | 1920766.0882 | 1940683.7189
1039 | 11 kV Mosjid Road Feeder (F3) | 11 | Jurain | DHK60936 | 1 | 575495.8 | 593952.2 | 18456.4 | 60 | 0 | 1107384 | 1098969.809 | Jurain | Shyampur BISIC 33/11KV S/S | 1475476.6819 | 1381608.0185
1040 | 11 kV Shyampur O/H Feeder (F4) | 11 | Jurain | DHK60938 | 1 | 594888.2 | 615565.9 | 20677.7 | 60 | 0 | 1240662 | 1231235.1282 | Jurain | Shyampur BISIC 33/11KV S/S | 1429313.0963 | 1378277.4296
1041 | 11 kV Road No-11 Feeder (F5) | 11 | Shympur | DHK60937 | 1 | 337050 | 351956.3 | 14906.3 | 60 | 0 | 894378 | 887582.2839 | Shyampur | Shyampur BISIC 33/11KV S/S | 954363.7317 | 1019394.7492
1042 | 11 kV Hanif Express Feeder (F6) | 11 | Jurain | DHK60939 | 1 | 511525.1 | 518004.2 | 6479.1 | 60 | 0 | 388746 | 385792.207 | Jurain | Shyampur BISIC 33/11KV S/S | 8184.8678 | 8596.203
1043 | 11 kV Zia Sharani Road Feeder(F7) | 11 | Jurain | DHK60940 | 1 | 824930.4 | 871854.9 | 46924.5 | 60 | 0 | 2815470 | 2794077.3284 | Jurain | Shyampur BISIC 33/11KV S/S | 2700808.4363 | 2561826.8196
1044 | 11 kV Road-12 & 13 Feeder(F8) | 11 | Shympur | DHK60941 | 1 | 236095.8 | 256885.3 | 20789.5 | 60 | 0 | 1247370 | 1237892.1591 | Shyampur | Shyampur BISIC 33/11KV S/S | 1229098.1908 | 1284557.7074
1045 | 11 kV Rahman and Baset (F9). | 11 | Jurain | DHK60944 | 1 | 443790.5 | 455733.9 | 11943.4 | 60 | 0 | 716604 | 711159.0569 | Jurain | Shyampur BISIC 33/11KV S/S | 480060.5409 | 1215195.8482
1046 | 11 kV Sabujbagh Feeder (F10) | 11 | Jurain | DHK61020 | 1 | 482640.9 | 526918.2 | 44277.3 | 60 | 0 | 2656638 | 2636452.1751 | Jurain | Shyampur BISIC 33/11KV S/S | 2526376.4464 | 2465450.8355
1047 | 11 kV Road No-7 & 8 Feeder(F11) | 11 | Jurain | DHK60943 | 1 | 845435.7 | 856542.9 | 11107.2 | 60 | 0 | 666432 | 661368.2767 | Jurain | Shyampur BISIC 33/11KV S/S | 689554.7346 | 725640.3272
1048 | 11 kV Hossain Express Feeder(F12) | 11 | Shympur | DHK60942 | 1 | 938845.6 | 960702.2 | 21856.6 | 60 | 0 | 1311396 | 1301431.6729 | Shyampur | Shyampur BISIC 33/11KV S/S | 1235612.3209 | 1199610.0995
1049 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB7380 | 1 | 604904 | 608485 | 3581 | 1 | 0 | 3581 | 3553.7906 | Shyampur | Shyampur BISIC 33/11KV S/S | 3904.2091 | 3633.5474
1050 | 11 kV Spare | 11 | 0 | 00000090 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0
1051 | 11 kV Khaza Moinuddin | 11 | 0 | 00000026 | 1 | 4686068 | 5408547 | 722479 | 1 | 0 | 722479 | 727695.4191 | Fatullah | Nandalalpur 33/11 kV | 676115.2751 | 672821.6526
1052 | 11 kV Chitashal | 11 | 0 | 00000027 | 1 | 32447880 | 33243638 | 795758 | 1 | 0 | 795758 | 801503.5058 | Shyampur | Nandalalpur 33/11 kV | 725908.576 | 676035.0889
1053 | 11 kV Local Feeder | 11 | 0 | 00000157 | 1.5 | 18223956 | 18439474 | 215518 | 1 | Estimated | 668980.62 | 673810.7719 | Shyampur | Nandalalpur 33/11 kV | 652026.96 | 610908.7086
1054 | 11 kV Rasel Germants | 11 | 0 | 00000124 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Fatullah | Nandalalpur 33/11 kV | 0 | 0
1055 | 11 kV Matuail Medical (Adorsho nagar) | 11 | 0 | 00000121 | 1 | 70737224 | 73062544 | 2325320 | 1 | 0 | 2325320 | 2342109.1991 | Matuail | Nandalalpur 33/11 kV | 2438091.1118 | 2521439.5722
1056 | 11 kV Nandalalpur | 11 | 0 | 00000010 | 1 | 82993360 | 83856192 | 862832 | 1 | 0 | 862832 | 869061.7913 | Fatullah | Nandalalpur 33/11 kV | 928548.3765 | 892208.2473
1057 | 11 kV Sharif Bagh | 11 | 0 | 00000132 | 1 | 70183192 | 71968184 | 1784992 | 1 | 0 | 1784992 | 1797879.9406 | Shyampur | Nandalalpur 33/11 kV | 1716982.5939 | 1682233.437
1058 | 11 kV Spare | 11 | 0 | 00000139 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0
1059 | 11 KV Nayamati | 11 | 0 | 00000158 | 1 | 64037524 | 65089840 | 1052316 | 1 | 0 | 1052316 | 1059913.8974 | Fatullah | Nandalalpur 33/11 kV | 1145403.0364 | 1037983.1413
1060 | 11 kV Pulpar | 11 | 0 | 00000160 | 1 | 6979983 | 7628741 | 648758 | 1 | 0 | 648758 | 653442.1412 | Fatullah | Nandalalpur 33/11 kV | 808373.695 | 916555.6279
1061 | 11 kV Shahi Bazar | 11 | 0 | 00000170 | 1 | 40057984 | 40882420 | 824436 | 1 | 0 | 824436 | 830388.5657 | Shyampur | Nandalalpur 33/11 kV | 784445.919 | 785444.6114
1062 | 11 kV Pagla Bazar | 11 | 0 | 00000060 | 1 | 49521320 | 50196196 | 674876 | 1 | 0 | 674876 | 679748.7175 | Fatullah | Nandalalpur 33/11 kV | 834561.5067 | 783154.3223
1063 | 11 kV Delpara bazar | 11 | 0 | 00000063 | 1 | 77632408 | 79142768 | 1510360 | 1 | 0 | 1510360 | 1521265.0516 | Shyampur | Nandalalpur 33/11 kV | 1508132.7308 | 1527622.8486
1064 | 11 kV Bhuighor (Board mill) | 11 | 0 | 00000146 | 1 | 43051416 | 43749012 | 697596 | 1 | 0 | 697596 | 702632.7597 | Matuail | Nandalalpur 33/11 kV | 668462.9794 | 1074021.0416
1065 | 11 kV Spare | 11 | 0 | 00000059 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | Nandalalpur 33/11 kV | 0 | 0
1066 | 33/0.415 kV, 200 kVA AT-1 | 11 | 0 | 7803 | 1 | 2371 | 2435 | 64 | 100 | 0 | 6400 | 6446.2091 | Shyampur | Nandalalpur 33/11 kV | 6244.3055 | 5725.7228
1067 | 33/0.415 kV, 200 kVA AT-2 | 11 | 0 | 7805 | 1 | 51 | 51 | 0 | 100 | 0 | 0 | 0 | Shyampur | Nandalalpur 33/11 kV | 0 | 0
1068 | 11 kV Station Road Feeder | 11 | Postogola | HA021100907-02 | 1 | 61037936 | 62369777 | 1331841 | 1 | 0 | 1331841 | 1335055.4691 | Postogola | Postogola 33/11KV S/S | 1307497.2614 | 1269812.3426
1069 | 11 kV Samon & Sons Feeder. | 11 | Jurain | HA021100501-02 | 1 | 8339686 | 9710567 | 1370881 | 1 | 0 | 1370881 | 1374189.6942 | Jurain | Postogola 33/11KV S/S | 1360936.1962 | 1367079.5822
1070 | 11 kV Alam Bagh Feeder. | 11 | Postogola | HA021100718-02 | 1 | 23596442 | 24070248 | 473806 | 1 | 0 | 473806 | 474949.556 | Jurain | Postogola 33/11KV S/S | 542387.1952 | 435813.5436
1071 | 11 kV Majar O/H Feeder | 11 | Postogola | HA021100714-02 | 1 | 72786262 | 74369662 | 1583400 | 1 | 0 | 1583400 | 1587221.6201 | Postogola | Postogola 33/11KV S/S | 1546887.4107 | 1509702.7057
1072 | 11 kV Cyca Feeder | 11 | Postogola | DHK61081 | 1 | 418110.9 | 428700.2 | 10589.3 | 60 | 0 | 635358 | 636891.4703 | Postogola | Postogola 33/11KV S/S | 664686.4068 | 678488.3278
1073 | 11 kV Housing O/H Feeder. | 11 | Postogola | DHK61085 | 1 | 845528 | 866598.9 | 21070.9 | 60 | 0 | 1264254 | 1267305.3443 | Postogola | Postogola 33/11KV S/S | 1258808.5211 | 1186933.4512
1074 | 11 kV Munshi Bari | 11 | Postogola | DHK61078 | 1 | 727154.9 | 747895 | 20740.1 | 60 | 0 | 1244406 | 1247409.4401 | Postogola | Postogola 33/11KV S/S | 1227619.0196 | 1164704.2052
1075 | 11 kV Cantonment Feeder | 11 | Jurain | DHK60953 | 1 | 517862.7 | 520016 | 2153.3 | 60 | 0 | 129198 | 129509.8262 | Postogola | Postogola 33/11KV S/S | 124992.5587 | 126222.4118
1076 | 11 kV DIT Feeder. | 11 | Postogola | DHK60868 | 1 | 819569.4 | 837075.6 | 17506.2 | 60 | 0 | 1050372 | 1052907.1287 | Postogola | Postogola 33/11KV S/S | 1323292.4846 | 1331811.5849
1077 | 11 kV Jurain WASA Road Feeder | 11 | Jurain | DHK60862 | 1 | 283639 | 324272.2 | 40633.2 | 60 | 0 | 2437992 | 2443876.2234 | Jurain | Postogola 33/11KV S/S | 2429557.5202 | 2393972.4885
1078 | 11 kV Khorshed Ali O/H Feeder. | 11 | Jurain | HA021100484-02 | 1 | 36547113 | 38603647 | 2056534 | 1 | 0 | 2056534 | 2061497.5542 | Jurain | Postogola 33/11KV S/S | 2071894.6482 | 1933992.5359
1079 | 11 kV Murad pur Feeder. | 11 | Jurain | HA021100680-02 | 1 | 5929.5 | 8284 | 2354.5 | 1000 | 0 | 2354500 | 2360182.711 | Jurain | Postogola 33/11KV S/S | 2388027.6504 | 2351667.7366
1080 | 11 kV Habib Oil Feeder. | 11 | Postogola | HA021101240-02 | 1 | 54442479 | 56071015 | 1628536 | 1 | 0 | 1628536 | 1632466.5583 | Postogola | Postogola 33/11KV S/S | 1639249.0712 | 1571920.5306
1081 | 11 kV Rajabari Feeder. | 11 | Postogola | HA021100681-02 | 1 | 52971025 | 53216071 | 245046 | 1 | 0 | 245046 | 245637.4316 | Postogola | Postogola 33/11KV S/S | 262708.1006 | 303872.8913
1082 | 11/0.415 kV, 200 kVA AT-1+2 | 11 | 0 | ELIB67385 | 1 | 314.92 | 368.64 | 53.72 | 80 | 0 | 4297.6 | 4307.9725 | Postogola | Postogola 33/11KV S/S | 5751.9551 | 4375.6621
1083 | 11 kV Feeder-1 | 11 | 0 | DHK60892 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0
1084 | 11 kV Feeder-2 | 11 | 0 | DHK60968 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0
1085 | 11 kV Dholaikal RMU | 11 | 0 | DHK60970 | 1 | 190281.3 | 223582.9 | 33301.6 | 60 | 0 | 1998096 | 2013206.2605 | Banglabazar | IG Gate GIS 33/11 kV | 1942348.072 | 1890634.7965
1086 | 11 kV Alom Gonj | 11 | 0 | DHK60894 | 1 | 469945.6 | 479815.2 | 9869.6 | 60 | 0 | 592176 | 596654.2301 | Postogola | IG Gate GIS 33/11 kV | 589855.3321 | 589628.102
1087 | 11 kV Dhalka Nagar Feeder (F-5) | 11 | 0 | DHK60895 | 1 | 505725.6 | 536337.9 | 30612.3 | 60 | 0 | 1836738 | 1850628.0181 | Postogola | IG Gate GIS 33/11 kV | 1792355.2732 | 1711977.4089
1088 | 11 kV Farashgonj Feeder (F-6) | 11 | 0 | DHK68133 | 1 | 3559.31 | 3589.15 | 29.84 | 60000 | 0 | 1790400 | 1803939.5949 | Banglabazar | IG Gate GIS 33/11 kV | 1748762.5817 | 1815572.1775
1089 | 11 kV Doyaganj | 11 | 0 | DHK68134 | 1 | 2352.51 | 2380.418 | 27.908 | 60000 | 2414.18 | 1674480 | 1687142.9696 | Swamibag | IG Gate GIS 33/11 kV | 1819772.2117 | 1955417.8504
1090 | 11 kV Faridabad | 11 | 0 | DHK68140 | 1 | 751.51 | 772.95 | 21.44 | 60000 | 0 | 1286400 | 1296128.1808 | Postogola | IG Gate GIS 33/11 kV | 1292615.9757 | 1233789.9626
1091 | 11 kV Gandaria | 11 | 0 | DHK60969 | 1 | 336244.2 | 372411.9 | 36167.7 | 60 | 0 | 2170062 | 2186472.7241 | Postogola | IG Gate GIS 33/11 kV | 2176408.4497 | 2008723.2675
1092 | 11 kV Walter Road | 11 | 0 | DHK68136 | 1 | 950.44 | 973.45 | 23.01 | 60000 | 0 | 1380600 | 1391040.5522 | Banglabazar | IG Gate GIS 33/11 kV | 1437042.3417 | 1402694.4766
1093 | 11 kV Murgitola Feeder (F-11) | 11 | 0 | DHK68138 | 1 | 3852.58 | 3890.75 | 38.17 | 60000 | 0 | 2290200 | 2307519.2472 | Swamibag | IG Gate GIS 33/11 kV | 2337901.7997 | 2438521.0841
1094 | 11 kV Feeder-12 | 11 | 0 | DHK60900 | 1 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | IG Gate GIS 33/11 kV | 0 | 0
1095 | 11 kV Begumgonj Feeder (F-13) | 11 | 0 | DHK60899 | 1 | 638057.1 | 667472.2 | 29415.1 | 60 | 0 | 1764906 | 1778252.8009 | Swamibag | IG Gate GIS 33/11 kV | 1741101.9665 | 1809148.9629
1096 | 11 kV Lohar Pool Feeder (F-14) | 11 | 0 | DHK60967 | 1 | 148948.3 | 166011.3 | 17063 | 60 | 0 | 1023780 | 1031522.1618 | Postogola | IG Gate GIS 33/11 kV | 1006862.3928 | 984580.1304
1097 | 11/0.415 kV, 200 kVA AT-1+2 | 0.415 | 0 | ELIB2774 | 1 | 277674 | 279327 | 1653 | 1 | 0 | 1653 | 1665.5005 | Postogola | IG Gate GIS 33/11 kV | 1667.9239 | 1718.3058
1098 | Nizambag | 11 | 0 | 6604414 | 1 | 3666.8 | 3666.8 | 0 | 8000 | Estimated | 1094695.56 | 1095738.2283 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1008260.1492 | 972380.6635
1099 | Merry Stopes | 11 | 0 | 6604287 | 1 | 21574.1 | 21574.1 | 0 | 8000 | Estimated | 364898.52 | 365246.0761 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 355856.5232 | 364642.7488
1100 | Mujibur Ghat | 11 | 0 | 6604387 | 1 | 4108.33 | 4108.33 | 0 | 8000 | Estimated | 1216328.4 | 1217486.9203 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1304807.2519 | 1337023.4124
1101 | Madrasa | 11 | 0 | 6604481 | 1 | 12880.37 | 12880.37 | 0 | 8000 | Estimated | 1423104.228 | 1424459.6968 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1542044.934 | 1701666.1612
1102 | Thana | 11 | 0 | 6604443 | 1 | 9206.44 | 9206.44 | 0 | 8000 | Estimated | 1216328.4 | 1217486.9203 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 1423426.093 | 1337023.4124
1103 | Al-Hera | 11 | 0 | 6604372 | 1 | 7218.69 | 7218.69 | 0 | 8000 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0 | 0
1104 | Waz Uddin School | 11 | 0 | 6604448 | 1 | 7366.66 | 7366.66 | 0 | 8000 | Estimated | 729797.04 | 730492.1522 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 830331.8876 | 972380.6635
1105 | 11/0.4 kV Auxiliary Transformer | 11 | 0 | BD014062 | 1 | 597.11 | 597.11 | 0 | 1 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar-2 33/11 KV S/S | 0 | 0
1106 | Bashundhara City | 33 | 0 | 660434 | 1 | 753.18 | 765.8 | 12.62 | 180000 | 0 | 2271600 | 2286948.2926 | Shere b.nagar | Moghbazar 132/33/11KV S/S | 2480389.347 | 2161081.9864
1107 | 33 kV Apollo Ispat Feeder | 33 | DPDC | 7389486 | 1 | 4500.27 | 4526.7 | 26.43 | 240000 | 0 | 6343200 | 6352475.5818 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 7317548.4229 | 5615154.9463
1108 | 33 kV Adamjee EPZ Feeder | 33 | DPDC | ABB03919 | 1 | 357772.9 | 361720 | 3947.1 | 2000 | 0 | 7894200 | 7905743.5896 | Siddirgonj | Siddhirganj 132/33/11KV S/S | 8068621.1441 | 8850787.3005
1109 | 33 KV Multi Oil Refinery*** | 33 | EXPORT | DHK95595 | 1 | 1008.73 | 1011.11 | 2.38 | 240000 | 0 | 571200 | 571200 | Siddirgonj | Demra 33/11KV S/S | 446400 | 0
1110 | 33 kV ACI Pharmacuticles Feeder | 33 | 0 | DHKC4791 | 1 | 885.85 | 900.2 | 14.35 | 90000 | 0 | 1291500 | 1291500 | N.Gonj (East) | Khanpur 33/11KV S/S | 1045800 | 0
1111 | 33 kV Azizu Recycling (Old Shyampur Feeder)[ Feeder-3] | 33 | DPDC | 0 | 1 | 9902.222 | 9902.222 | 0 | 1000 | From Customer End | 10361 | 10440.0638 | Matuail | Matuail 132/33 KV S/S | 10260.3419 | 10991.7418
1112 | 33 KV Shah Cement Feeder (F2) | 33 | DPDC | H/A030800181-03 | 1 | 37583.454 | 40076.123 | 2492.669 | 1000 | 0 | 2492669 | 2494536.8881 | Sytalakhya | Sitalakhya 132/33KV S/S | 923421.8011 | 1229303.7954
1113 | 33/0.415 KV Transformer AT-1 | 0.415 | DPDC | 2001123043108 | 1 | 6555.9 | 6555.9 | 0 | 160 | 0 | 0 | 0 | Sytalakhya | Sitalakhya 132/33KV S/S | 0 | 0
1114 | 33/0.415 KV Transformer AT-2 | 0.415 | DPDC | 2001123043171 | 1 | 4646.3 | 4676 | 29.7 | 160 | 0 | 4752 | 4755.5609 | Sytalakhya | Sitalakhya 132/33KV S/S | 4035.644 | 2848.7249
1115 | 33 kV Premier Cement VRM Circuit-1 (=H1) | 33 | Main | 041808902866 | 1 | 288.61 | 307.61 | 19 | 360000 | 0 | 6840000 | 6850018.059 | Sytalakhya | Char Syedpur 132/33KV S/S | 6815752.3123 | 6616060.3155
1116 | 33 kV Delta Agro Premier Cement (=H2) | 33 | Main | 041808902876 | 1 | 93.75 | 100.77 | 7.02 | 360000 | 0 | 2527200 | 2530901.4092 | Sytalakhya | Char Syedpur 132/33KV S/S | 2430058.343 | 2458012.5886
1117 | 33 kV Outgoing Feeder-3 (=H3) | 33 | Main | 041808902862 | 1 | 0.09 | 0.09 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0
1118 | 33 kV Outgoing Feeder-4 (=H4) | 33 | Main | 041808902826 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0
1119 | 33 kV Premier Cement VRM Circuit-2 (=H11) | 33 | Main | 041808902856 | 1 | 42.67 | 43.78 | 1.11 | 360000 | 0 | 399600 | 400185.2656 | Sytalakhya | Char Syedpur 132/33KV S/S | 1006790.1928 | 1108090.8439
1120 | 33 kV Outgoing Feeder-6 (=H12) | 33 | Main | 041808902816 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0
1121 | 33 kV Outgoing Feeder-7 (=H13) | 33 | Main | 041808902857 | 1 | 0.03 | 0.03 | 0 | 360000 | 0 | 0 | 0 | Sytalakhya | Char Syedpur 132/33KV S/S | 0 | 0
1122 | 33 kV Shah Cement VRM (=H14) | 33 | Main | 041808902860 | 1 | 434.74 | 460.46 | 25.72 | 360000 | 0 | 9259200 | 9272761.2883 | Sytalakhya | Char Syedpur 132/33KV S/S | 10712537.375 | 10817421.0397
1123 | 11 KV Shahidbagh Feeder | 11 | 0 | 202006932 | 1 | 1263498 | 1263498 | 0 | 1 | Calculated | 510120 | 524779.3911 | Rajarbag | Santinagar Switching S/S | 36416.7693 | -3994.0825
1124 | 11 Fortune(MogBazar)-new | 11 | 0 | 202006969 | 1 | 377976 | 377976 | 0 | 1 | From Sold Unit | 134880 | 138756.0658 | Moghbazar | Santinagar Switching S/S | 127666.1608 | 126229.899
1125 | Centerpoint-Kakrail | 11 | 0 | 952612030119 | 1 | 1658 | 1658 | 0 | 1200 | From Sold Unit | 69600 | 71600.1051 | Kakrail | Santinagar Switching S/S | 81766.8748 | 80846.9863
1126 | 11 KV Shyamoli O/H | 11 | 0 | DHK-15026 | 1 | 9164.92 | 9179.18 | 14.26 | 40000 | 0 | 570400 | 584660 | Shere b.nagar | Agargaon 33/11 KV S/S | 530950
1127 | 11 KV Nearest RMU | 11 | 0 | DHK-15027 | 1 | 3859.52 | 3863.97 | 4.45 | 40000 | 0 | 178000 | 182450 | Shere b.nagar | Agargaon 33/11 KV S/S | 165230
1128 | 11 KV Sher-e-bangla Nagar | 11 | 0 | DHK-15025 | 1 | 3976.15 | 3977.36 | 1.21 | 40000 | 0 | 48400 | 49610 | Shere b.nagar | Agargaon 33/11 KV S/S | 45920
1129 | Export to DESCO | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Shere b.nagar | Agargaon 33/11 KV S/S | -13837.5
1130 | 33/0.4 kV, 500 kVA AT-1 | 0.4 | 0 | 84.2659 | 1 | 313699 | 316189 | 2490 | 10 | 0 | 24900 | 24914.239 | Paribag | Dhanmondi 33/11KV S/S | 24707.6715
1131 | 33/0.4 kV, 1000 kVA AT-2 | 0.4 | 0 | 84.2673 | 1 | 478688 | 478688 | 0 | 10 | 0 | 0 | 0 | Paribag | Dhanmondi 33/11KV S/S | 0
1132 | 33 KV Japan Genden City | 33 | 0 | DHK15681 | 1 | 358.27 | 442.67 | 84.4 | 18000 | 0 | 1519200 | 1519200 | Adabor | Japan Garden 33/11 KV | 1531620
1133 | 11/0.4 kV Aux. Transformer, AT-1 | 0.415 | 0 | DHKE6223 | 1 | 42845.32 | 43047.09 | 201.77 | 120 | 0 | 24212.4 | 24412.3409 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 25361.4506
1134 | 11/0.4 kV Aux. Transformer, AT-2 | 0.415 | 0 | DHK37495 | 1 | 45593.9 | 45593.9 | 0 | 120 | 0 | 0 | 0 | Kamrangirchar | Kamrangirchar 33/11KV S/S | 0
1135 | AT-1 | 0.415 | 0 | 0 | 1 | 357.37 | 502.11 | 144.74 | 80 | 0 | 11579.2 | 11708.7885 | Mugdapara | Madarteck 33/11KV S/S | 9611.7345
1136 | AT-2 | 0.415 | 0 | 63394003 | 1 | 157.43 | 233.54 | 76.11 | 80 | 0 | 6088.8 | 6156.9427 | Mugdapara | Madarteck 33/11KV S/S | 5477.3433
1137 | 33 kV Shahriar Steel Feeder | 33 | Main | 41812909534 | 1 | 550.9 | 571.22 | 20.32 | 360000 | 0 | 7315200 | 7323524.0635 | Kazla | Kazla 132/133 KV SS | 7145780.8426
1138 | 33 kV Zahir Steel | 33 | Main | 41812909521 | 1 | 602.93 | 630.73 | 27.8 | 360000 | 0 | 10008000 | 10019388.2364 | Kazla | Kazla 132/133 KV SS | 9121125.0936
1139 | 33kV Water Treatment Plant | 33 | Digital | 80379618 | 1 | 20647 | 20947 | 300 | 2000 | 0 | 600000 | 605078.9898 | Maniknagar | Maniknagar 132/33 KV SS | 1062218.4705
1140 | Axuxilary -1 | 0.415 | 0 | AH14044078 | 1 | 397817.5 | 403596.2 | 5778.7 | 1 | 0 | 5778.7 | 5831.4157 | Maniknagar | Maniknagar 132/33/11KV S/S | 6475.0369
1141 | Axuxilary -2 | 0.415 | 0 | AH14044072 | 1 | 369244.1 | 374573.2 | 5329.1 | 1 | 0 | 5329.1 | 5377.7142 | Maniknagar | Maniknagar 132/33/11KV S/S | 4841.9103
1142 | 33 kV Rani RRM Feeder | 33 | Export | BD001809 | 1 | 715.3204 | 725.5189 | 10.1985 | 240000 | 0 | 2447640 | 2448780.2928 | Shyampur | Shyampur 132/33KV S/S | 2460914.9302
1143 | 33 kV Rahima Steel feeder | 33 | Export | BD001803 | 1 | 629.3505 | 637.06 | 7.7095 | 240000 | 0 | 1850280 | 1851141.9981 | Shyampur | Shyampur 132/33KV S/S | 2281164.2763
1144 | 33 kV Salam Steel Feeder | 33 | Export | BD001849 | 1 | 1102.925 | 1143.578 | 40.653 | 240000 | 0 | 9756720 | 9761265.4061 | Shyampur | Shyampur 132/33KV S/S | 10754060.1599
1145 | 33 kV Steel Famus feeder | 33 | Export | BD001806 | 1 | 129.9924 | 135.586 | 5.5936 | 240000 | 0 | 1342464 | 1343089.4196 | Shyampur | Shyampur 132/33KV S/S | 1442423.9509
1146 | 33 kV Rani Kamal Steel Feeder | 33 | Export | BD001829 | 1 | 1488.4699 | 1511.052 | 22.5821 | 240000 | 0 | 5419704 | 5422228.9014 | Shyampur | Shyampur 132/33KV S/S | 6501978.5941
1147 | 33 kV Chakda Steel Feeder | 33 | Export | BD001832 | 1 | 2331.0006 | 2365.387 | 34.3864 | 240000 | 0 | 8252736 | 8256580.7385 | Shyampur | Shyampur 132/33KV S/S | 8640663.1605
1148 | 33 kV Akhter Steel Feeder | 33 | Export | BD001828 | 1 | 672.5319 | 677.3128 | 4.7809 | 240000 | Prime Textile | 1147416 | 1147950.5517 | Fatullah | Shyampur 132/33KV S/S | 674551.2513
1149 | Aux Tr-1 | 0.44kv | Export | DHKG9742 | 1.025 | 341.169 | 343.416 | 2.247 | 2400 | 0 | 5527.62 | 5527.62 | Fatullah | Shyampur 132/33KV S/S | 10071.24
1150 | Aux Tr-2 | 0.44kv | Export | DHKG9743 | 1.025 | 87.479 | 95.379 | 7.9 | 2400 | 0 | 19434 | 19434 | Fatullah | Shyampur 132/33KV S/S | 11042.94
1151 | 132 kV MI Cement Feeder [MICFL] | 132 | P. Cell | 08993599 | 1 | 256.333 | 278.72 | 22.387 | 480000 |  | 10749120 | 10749120 | Sytalakhya | MI CEMENT 132/33 kV | 9239520
1152 | 33 kV Shah Cement Feeder | 33 | 0 | 8993 841 | 1 | 39285.417 | 39374.588 | 89.171 | 36000 | 0 | 3210156 | 3210156 | Sytalakhya | Madonganj 132/33 KV SS | 3227092
1153 | 33 kV Mondol Para (Premire cement) Feeder | 33 | 0 | 8993 842 | 1 | 2588.486 | 2588.486 | 0 | 180000 | 0 | 0 | 0 | Sytalakhya | Madonganj 132/33 KV SS | 0
1154 | 11 kV Rayer Bazar Feeder | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 676827.9 | 679467.069 | Dhanmondi | Jigatola Switching
1155 | 11 kV Madina Masjid Feeder | 11 | 1 | 61903725 | 1 | 231388 | 231388 | 0 | 200 | Estimated | 1581226.92 | 1587392.6308 | Jigatola | Jigatola Switching
1156 | 11 kV Mitali | 11 | 1 | 619003621 | 1 | 830347 | 830347 | 0 | 200 | Estimated | 1514745.18 | 1520651.6572 | Jigatola | Jigatola Switching
1157 | Export to Narinda | 11 | [8 empty] | -100000 | -100000 | Swamibag | Export-Import
1158 | Import from Swamibagh | 11 | [8 empty] | 100000 | 100000 | Narinda | Export-Import
1159 | Export to Narinda | 11 | [8 empty] | -250000 | -250000 | Shyampur | Export-Import
1160 | Import from Shyampur | 11 | [8 empty] | 250000 | 250000 | Narinda | Export-Import
1161 | Import from Shyampur | 11 | [8 empty] | 300000 | 300000 | Matuail | Export-Import
1162 | Export to Matuail | 11 | [8 empty] | -300000 | -300000 | Shyampur | Export-Import
1163 | Import from Tejgaon | 11 | [8 empty] | 200000 | 200000 | Kakrail | Export-Import
1164 | Export to Kakrail | 11 | [8 empty] | -200000 | -200000 | Tejgaon | Export-Import
1165 | Export to Narinda | 11 | [8 empty] | -300000 | -300000 | Motijheel | Export-Import
1166 | Import from Motijheel | 11 | [8 empty] | 300000 | 300000 | Narinda | Export-Import

## Summary
| NOCS Import Linked From Individual Sheet (North-1. North-2, South-1, South-2) | [5 empty] | Import Summary Report | [8 empty] | System Loss Summmary Report | [15 empty] | Convert ICT Format to T&EA Format
|  | North Grid | [13 empty] | Zone-Circle-Division wise Import & System loss at 33kv level for the Month July-2023
| Sl. No. | Name of S/S | No of Feeder | NOCS | import | S/S Total | Zone-Circle-Division wise Import & System loss at 33kv level for the Month July-2023 | [13 empty] | FINAL |  |  |  |  | Date: 03.07.2023 | [9 empty] | INPUT
| 1 | Moghbazar 33/11KV S/S |  | Kakrail | 9919208.4115 | 20463233.9763 | ZONE | IMPORT | CIRCLE | IMPORT | NOCS | IMPORT (This Month) | IMPORT (Last Month) | Diff | % of Increase/ Decrease | ZONE | IMPORT | SOLD | SYSTEM LOSS | CIRCLE | IMPORT | SOLD | SYSTEM LOSS | NOCS | IMPORT | SOLD | SYSTEM LOSS(%) |  |  |  |  | Dhaka Power Distribution Company Ltd. | [5 empty] | Dhaka Power Distribution Company Ltd.
|  |  |  | Tejgaon | 7022618.3764 |  | North | 313681791.7313 | Tejgaon | 62407175.0864 | Tejgaon | 34031890.1848 | 33326427.9121 | 705462.2727 | 2.1168 | North | 313681791.7313 | 277792927.47 | 11.4412 | Tejgaon | 62407175.0864 | 53250410 | 14.6726 | Tejgaon | 34031890.1848 | 29788753 | 12.4681 | #N/A | -955462.2727 | 33076427.9121 | 1 | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) |  | Sold Unit for July-2018
|  |  |  | Shere Bangla Nagar | 475259.7411 | [5 empty] | Kakrail | 28375284.9016 | 26542949.8477 | 1832335.0539 | 6.9033 | [8 empty] | Kakrail | 28375284.9016 | 23461657 | 17.3166 | #N/A | -1378678.1076 | 26996606.794 | 2 | Tejgaon | 29788753 | 158656 | 31866537 | CODE | NOCS | Sold Unit without PFC Unit(kwh) | PFC Unit(kwh) | Sold Unit with PFC Unit(kwh) | 26013611.1607 | -2361673.7409
|  |  |  | Maghbazar | 3046147.4474 |  |  |  | Moghbazar | 38247527.2729 | Moghbazar | 21329436.2056 | 20914248.216 | 415187.9896 | 1.9852 |  |  |  |  | Moghbazar | 38247527.2729 | 34916857 | 8.7082 | Moghbazar | 21329436.2056 | 18804662 | 11.837 | #N/A |  |  | 3 | Kakrail | 23461657 | 171692 | 24827727 | A1 | Motijheel | 21234194 | 180512 | 21213103
| 2 | Green Road 33/11KV S/S |  | Azimpur | 0 | 14307376.979 |  |  |  |  | Khilgaon | 16918091.0673 | 16885238.3373 | 32852.73 | 0.19456 | [8 empty] | Khilgaon | 16918091.0673 | 16112195 | 4.7635 | #N/A |  |  | 4 | Moghbazar | 18804662 | 108541 | 18290861 | A2 | Khilgaon | 16112195 | 126930 | 14744447
|  |  |  | Jigatola | 2670199.4988 |  |  |  | Satmasjid | 48971122.2867 | Satmosjid | 23421031.5433 | 23263785.2371 | 157246.3062 | 0.67593 |  |  |  |  | Satmasjid | 48971122.2867 | 44596574 | 8.9329 | Satmosjid | 23421031.5433 | 21821996 | 6.8273 | #N/A |  |  | 5 | Khilgaon | 16112195 | 126930 | 14744447 | A3 | Lalbag | 33146199 | 29808 | 32378332
|  |  |  | Paribagh | 11637177.4802 | [5 empty] | Sherebanglanagar | 25550090.7434 | 25060986.3423 | 489104.401 | 1.9517 | [8 empty] | Sherebangla nagar | 25550090.7434 | 22774578 | 10.863 | #N/A |  |  | 6 | Satmosjid | 21821996 | 69986 | 20656204 | A4 | Kazla | 33553123 | 83854 | 40432052
| 3 | Lalmatia 33/11KV S/S |  | Paribagh | 0 | 14625630 |  |  | Dhanmondi | 54269866.9833 | Dhanmondi | 24788375.0068 | 24559325.7701 | 229049.2367 | 0.93264 |  |  |  |  | Dhanmondi | 54269866.9833 | 48029470.51 | 11.4988 | Dhanmondi | 24788375.0068 | 22500728 | 9.2287 | #N/A |  |  | 7 | Sherebanglanagar | 22774578 | 177417 | 22172111 | A5 | Postogola | 14270101 | 103284 | 14440632
[11 empty] | Jhigatala | 29481491.9766 | 28755390.4901 | 726101.4865 | 2.5251 | [8 empty] | Jhigatala | 29481491.9766 | 25528742.51 | 13.4076 | #N/A |  |  | 8 | Dhanmondi | 22500728 | 85074 | 22650915 | A6 | Banglabazar | 15656318 | 53984 | 15635048
|  |  |  | Jigatola | 0 |  |  |  | Azimpur | 56180825.7754 | Azimpur | 20094312.838 | 19894403.1357 | 199909.7023 | 1.0049 |  |  |  |  | Azimpur | 56180825.7754 | 50379345.96 | 10.3264 | Azimpur | 20094312.838 | 17795270 | 11.4413 | #N/A |  |  | 9 | Jhigatala | 25528742.51 | 242541.6706 | 26390275.6506 | A7 | N.Gonj (West) | 27294969 | 162575 | 30141674
|  |  |  | Dhanmondi | 14625630 | [5 empty] | Paribagh | 36086512.9374 | 36106922.2961 | -20409.3587 | -0.056525 | [8 empty] | Paribagh | 36086512.9374 | 32584075.96 | 9.7057 | #N/A |  |  | 10 | Azimpur | 17795270 | 84677 | 17700392 | A8 | Siddirgonj | 45171661 | 359101 | 45978504
| 4 | Tejgoan 33/11KV S/S |  | Tejgaon | 22916599.1349 | 22916599.1349 |  |  | Shamoly | 53605274.3265 | Shyamoli | 19659362.7576 | 18256801.2634 | 1402561.4942 | 7.6824 |  |  |  |  | Shamoly | 53605274.3265 | 46620270 | 13.0304 | Shyamoli | 19659362.7576 | 16528202 | 15.9271 | #N/A |  |  | 11 | Paribagh | 32584075.96 | 255283.5864 | 31950833.9664 | A9 | Bashabo | 13544497 | 37574 | 12648695
| 5 | Dhanmondi 33/11KV S/S |  | Azimpur | 0 | 15388895.0903 |  |  |  |  | Adabor | 33945911.5689 | 33991693.0318 | -45781.4629 | -0.13468 | [8 empty] | Adabor | 33945911.5689 | 30092068 | 11.3529 | #N/A |  |  | 12 | Shyamoli | 16528202 | 72417 | 16790440 | B1 | Narinda | 13969000 | 133778 | 14047090
|  |  |  | RAMNA | 1541233.2961 |  | Central | 271835309.2341 | Lalbagh | 71393966.8153 | Lalbagh | 32545410.1246 | 35248383.1173 | -2702972.9927 | -7.6684 | Central | 271835309.2341 | 252222964.33 | 7.2148 | Lalbagh | 71393966.8153 | 68952853 | 3.4192 | Lalbagh | 32545410.1246 | 33146199 | -1.846 | #N/A |  |  | 13 | Adabor | 30092068 | 352167 | 28562841 | B2 | Maniknagar | 18931226 | 150970 | 18124164
|  |  |  | Kakrail | 1850443.26 | [5 empty] | Kamrangirchar | 38848556.6907 | 40610208.52 | -1761651.8293 | -4.338 | [8 empty] | Kamrangirchar | 38848556.6907 | 35806654 | 7.8302 | #N/A |  |  | 14 | Lalbagh | 33146199 | 29808 | 32378332 | B3 | Jurain | 26057714 | 329722 | 27570556
|  |  |  | Paribagh | 11997218.5341 |  |  |  | Ramna | 48675039.387 | Ramna | 29132056.3783 | 28248495.4309 | 883560.9474 | 3.1278 |  |  |  |  | Ramna | 48675039.387 | 43695449 | 10.2303 | Ramna | 29132056.3783 | 26497318 | 9.0441 | #N/A |  |  | 15 | Kamrangirchar | 35806654 | 109154 | 39588578 | B4 | Shyampur | 66408629 | 289766 | 70185393
| 6 | Kawranbazar 33/11KV S/S |  | Tejgaon | 0 | 4173585.2953 |  |  |  |  | Rajarbagh | 19542983.0087 | 19358621.1692 | 184361.8395 | 0.95235 | [8 empty] | Rajarbagh | 19542983.0087 | 17198131 | 11.9984 | #N/A |  |  | 16 | Ramna | 26497318 | 474835 | 25699296 | B5 | Swamibag | 13947175.33 | 23775 | 13239728.82
|  |  |  | Kakrail | 218912.3501 |  |  |  | Bashabo | 41880411.0163 | Bashabo | 15301078.259 | 14802303.8161 | 498774.4429 | 3.3696 |  |  |  |  | Bashabo | 41880411.0163 | 38477168 | 8.1261 | Bashabo | 15301078.259 | 13544497 | 11.4801 | #N/A |  |  | 17 | Rajarbagh | 17198131 | 82496 | 16960910 | B6 | Bangshal | 17929258 | 73977 | 17461454
|  |  |  | Paribagh | 0 | [5 empty] | Bonoseeri | 26579332.7573 | 26067833.1015 | 511499.6559 | 1.9622 | [8 empty] | Bonossri | 26579332.7573 | 24932671 | 6.1953 | #N/A |  |  | 18 | Bashabo | 13544497 | 37574 | 12648695 | B7 | N.Gonj (East) | 27517947 | 385947 | 29492332
|  |  |  | Shere Bangla Nagar | 3954672.9452 |  |  |  | Motijheel | 43146786.0041 | Motijheel | 22930447.2198 | 23157371.0896 | -226923.8698 | -0.97992 |  |  |  |  | Motijheel | 43146786.0041 | 39595743 | 8.2301 | Motijheel | 22930447.2198 | 21234194 | 7.3974 | #N/A |  |  | 19 | Bnossri | 24932671 | 70927 | 22161852 | B8 | Fateullah | 29117892 | 560066 | 32175783
| 7 | New Ramna 33/11KV S/S |  | Bangshal | 1141341.4264 | 8707312.1647 |  |  |  |  | Mughdapara | 20216338.7843 | 19531394.45 | 684944.3342 | 3.5069 | [8 empty] | Mughdapara | 20216338.7843 | 18361549 | 9.1747 | #N/A |  |  | 20 | Motijheel | 21234194 | 180512 | 21213103 | B9 | Mugdapara | 18361549 | 58942 | 16938115
|  |  |  | Lalbagh | 0 |  |  |  | Banglabazar | 35733690.526 | Banglabazar | 16797076.4051 | 17151582.8188 | -354506.4137 | -2.0669 |  |  |  |  | Banglabazar | 35733690.526 | 33585576 | 6.0115 | Banglabazar | 16797076.4051 | 15656318 | 6.7914 | #N/A |  |  | 21 | Mughdapara | 18361549 | 58942 | 16938115 | C1 | Tejgaon | 29788753 | 158656 | 31866537
|  |  |  | Narinda | 434935.9868 | [5 empty] | Bongshal | 18936614.1209 | 20320381.2069 | -1383767.086 | -6.8097 | [8 empty] | Bongshal | 18936614.1209 | 17929258 | 5.3196 | #N/A |  |  | 22 | Banglabazar | 15656318 | 53984 | 15635048 | C2 | Satmasjid | 21821996 | 69986 | 20656204
|  |  |  | Motijheel | 494476.0375 |  |  |  | Narinda | 31005415.4854 | Narinda | 15837103.8048 | 14687870.9921 | 1149232.8127 | 7.8244 |  |  |  |  | Narinda | 31005415.4854 | 27916175.33 | 9.9636 | Narinda | 15837103.8048 | 13969000 | 11.7957 | #N/A |  |  | 23 | Bongshal | 17929258 | 73977 | 17461454 | C3 | Paribagh | 32584075.96 | 255283.5864 | 31950833.9664
|  |  |  | RAMNA | 6636558.7139 | [5 empty] | Swamibagh | 15168311.6806 | 15102409.2817 | 65902.399 | 0.43637 | [8 empty] | Swamibagh | 15168311.6806 | 13947175.33 | 8.0506 | #N/A |  |  | 24 | Narinda | 13969000 | 133778 | 14047090 | C6 | Kakrail | 23461657 | 171692 | 24827727
| 8 | Dhanmondi 132/33kv S/S |  | Paribagh | 0 | 0 | South | 433013550.5398 | Kazla | 60085438.9762 | Kazla | 38787299.8942 | 37908086.6755 | 879213.2187 | 2.3193 | South | 433013550.5398 | 385852461 | 10.8914 | Kazla | 60085438.9762 | 52484349 | 12.6505 | Kazla | 38787299.8942 | 33553123 | 13.4946 | #N/A |  |  | 25 | Swamibagh | 13947175.33 | 23775 | 13239728.82 | D1 | Moghbazar | 18804662 | 108541 | 18290861
|  | Khillgaon 33/11KV S/S |  | Kakrail | 71600.1051 | 7156620 |  |  |  |  | Maniknagar | 21298139.082 | 20926873.0633 | 371266.0188 | 1.7741 | [8 empty] | Maniknagar | 21298139.082 | 18931226 | 11.1132 | #N/A |  |  | 26 | Kazla | 33553123 | 83854 | 40432052 | D2 | Dhanmondi | 22500728 | 85074 | 22650915
|  |  |  | Khilgaon | 0 |  |  |  | Shyampur | 89494290.2158 | Shyampur | 65449426.7658 | 70614491.3479 | -5165064.582 | -7.3145 |  |  |  |  | Shyampur | 89494290.2158 | 87352107 | 2.3937 | Shyampur | 65449426.7658 | 66408629 | -1.4656 | #N/A |  |  | 27 | Maniknagar | 18931226 | 150970 | 18124164 | D3 | Ramna | 26497318 | 474835 | 25699296
| 9 |  |  | Maghbazaar | 138756.0658 | [5 empty] | Matuail | 24044863.4499 | 23789745.4001 | 255118.0499 | 1.0724 | [8 empty] | Matuail | 24044863.4499 | 20943478 | 12.8983 | #N/A |  |  | 28 | Shyampur | 66408629 | 289766 | 70185393 | D4 | Shyamoli | 16528202 | 72417 | 16790440
|  |  |  | Rajarbagh | 6946263.8291 |  |  |  | Postogola | 46154264.2866 | Postogola | 16101783.0766 | 16221258.1373 | -119475.0607 | -0.73653 |  |  |  |  | Postogola | 46154264.2866 | 40327815 | 12.6239 | Postogola | 16101783.0766 | 14270101 | 11.3756 | #N/A |  |  | 29 | Matuail | 20943478 | 253556 | 20847840 | D5 | Shere b.nagar | 22774578 | 177417 | 22172111
| 10 | Goran 33/11KV S/S |  | Bashabo | 1654071.9922 | 10356569.589 |  |  |  |  | Jurain | 30052481.21 | 29718071.1615 | 334410.0485 | 1.1253 | [8 empty] | Jurain | 30052481.21 | 26057714 | 13.2926 | #N/A |  |  | 30 | Postogola | 14270101 | 103284 | 14440632 | D6 | Rajarbag | 17198131 | 82496 | 16960910
|  |  |  | Khilgaon |  |  |  |  | Narayangonj | 62320582.0857 | Narayangonj-West | 30519764.2002 | 30810293.9579 | -290529.7578 | -0.94296 |  |  |  |  | Narayangonj | 62320582.0857 | 54812916 | 12.0468 | Narayangonj- West | 30519764.2002 | 27294969 | 10.5663 | #N/A |  |  | 31 | Jurain | 26057714 | 329722 | 27570556 | D8 | Jhigatala | 25528742.51 | 242541.6706 | 26390275.6506
|  |  |  | Banosree | 8702497.5968 | [5 empty] | Narayangonj-East | 31800817.8855 | 31744596.4334 | 56221.4521 | 0.17711 | [8 empty] | Narayangonj- East | 31800817.8855 | 27517947 | 13.4678 | #N/A |  |  | 32 | Narayangonj-West | 27294969 | 162575 | 30141674 | D9 | Azimpur | 17795270 | 84677 | 17700392
| 11 | Taltola 33/11KV S/S |  | Khilgaon | 12647073.3492 | 15514959.122 |  |  | Demra | 75862431.7513 | Demra | 24683428.3053 | 24103097.7168 | 580330.5884 | 2.4077 |  |  |  |  | Demra | 75862431.7513 | 66531104 | 12.3003 | Demra | 24683428.3053 | 21359443 | 13.4665 | #N/A |  |  | 33 | Narayangonj-East | 27517947 | 385947 | 29492332 | E1 | Demra | 21359443 | 145204 | 21348197
|  |  |  | Maghbazar | 0 | [5 empty] | Siddhirgonj | 51179003.4461 | 51252886.2733 | -73882.8273 | -0.14415 | [8 empty] | Siddhirgonj | 51179003.4461 | 45171661 | 11.7379 | #N/A |  |  | 34 | Damra | 21359443 | 145204 | 21348197 | E2 | Matuail | 20943478 | 253556 | 20847840
|  |  |  | Bashabo | 2867885.7728 |  |  |  | Fatullah | 99096543.2242 | Fatulla | 33464369.2197 | 33019604.8442 | 444764.3755 | 1.347 |  |  |  |  | Fatullah | 99096543.2242 | 84344170 | 14.8869 | Fatulla | 33464369.2197 | 29117892 | 12.9884 | #N/A |  |  | 35 | Siddhirgonj | 45171661 | 359101 | 45978504 | E3 | Sytalakha | 55226278 | 304905 | 65859804
| 12 | Satmasjid 33/11KV S/S |  | Jigatola | 0 | 20599200 |  |  |  |  | Shitalakha | 65632174.0045 | 63181001.7532 | 2451172.2513 | 3.8796 | [8 empty] | Sytalakhya | 65632174.0045 | 55226278 | 15.8549 | #N/A | -2451535.2513 | 63180638.7532 | 36 | Fatulla | 29117892 | 560066 | 32175783 | F1 | Kamrangirchar | 35806654 | 109154 | 39588578
|  |  |  | Shyamoli | 3152210.5752 |  | TOTAL=> | 1018530651.5052 | TOTAL=> | 1018530651.5052 | TOTAL=> | 1018530651.5052 | 1015135033.6381 | 3395617.8671 | 0.3345 |  | 1018530651.5052 | 915868352.8 |  | TOTAL=> | 1018530651.5052 | 915868352.8 |  | Total=> | 1018530651.5052 | 915868352.8 | 10.0795 | #N/A |  |  | 37 | Shitalokko | 55226278 | 304905 | 65859804 | F2 | Banosree | 24932671 | 70927 | 22161852
|  |  |  | Shere Bangla Nagar | 0 | [26 empty] | Total => | 915868352.8 | 6364094.257 | 941172717.437 | G1 | Adabor | 30092068 | 352167 | 28562841
|  |  |  | Satmosjid | 10739329.7803 | [14 empty] | 132KV Import => |  |  |  |  | 1023462056.0593 | [11 empty] | Total => | 915868352.8 | 6364094.257 | 941172717.437
|  |  |  | Dhanmondi NOCS | 6707659.6445 |  | 132KV Import(As Certified by DPDC) => |  |  |  |  | 1023462056.0593 | [7 empty] | 33kv import of DPDC => |  |  |  |  | 1018530651.5052
|  | Civil Aviation |  | Tejgaon | 0 | 0 | 33kv import of DPDC=> |  |  |  |  | 1018530651.5052 | [7 empty] | Diff bet. 132KV Import & 33kv import of DPDC in % => |  |  |  |  | 0.48184
| 13 | Japan garden Building |  | Adabor | 1519200 | 1519200 | Diff bet.132kv import certified by DPDC & 33kv import of DPDC in % = |  |  |  |  | 0.48184 | [7 empty] | DPDC SOLD UNITS=> |  |  |  |  | 915868352.8
| 14 | Kallyanpur132/33 KV S/S |  | Shere Bangla Nagar | 0 | 0 |  |  |  |  | 4931404.5542 | [8 empty] | System loss at 132kv level => |  |  |  |  | 10.5127
| 15 | Jigatola 33/11KV S/S |  | Jigatola | 2384330 | 2384330
|  |  |  | Dhanmondi | 0
|  | Kallyanpur &Agargaon 33/11KV S/S |  | Adabor | 11102800 | 11920750
| 16 |  |  | Shere Bangla Nagar | 817950
|  |  |  | Shyamoli | 0
|  |  |  | Satmasjid | 0
| 17 | Kamrangirchar 33/11 KV |  | Kamrangirchar | 24734295.1776 | 24734295.1776
|  |  |  | Jigatola | 0
|  |  |  | Azimpur | 0
| 18 | Lalbagh 33/11KV S/S |  | Azimpur | 1773623.7611 | 9793594.8305
|  |  |  | Lalbagh | 8019971.0694
| 19 | Ullon 132/33/11 Kv S/S | 132kv | Shere Bangla Nagar | 0 | 8671191.4141
|  |  |  | Khilgaon | 0
|  |  | 33kv | Maghbazaar | 8671191.4141
|  | Kakrail 33/11KV S/S |  | Motijheel | 0
|  |  |  | RAMNA | 2773338.8 | 11428238.0558
|  |  |  | Rajarbaghl | 3190341.5218
|  |  |  | Kamalapur | 0
|  |  |  | Kakrail | 5464557.734 | 5464557.734
|  | Banshal 33/11 KV S/S |  | Bangshal | 6809696.8259 | 9376123.4544
|  |  |  | Banglabazar | 1426877.2604
|  |  |  | Narinda | 1139549.3681
| 1 | Baridhara 33/11KV S/S |  | Khilgaon | 0 | 0
|  | Japan Garden 33/11 KV |  | Adabor | 12873394.4087 | 17667200
|  |  |  | Shamoly | 3943678.4867
|  |  |  | Satmosjit | 850127.1046
|  | Azimpur 33/11 KV |  | jigatola | 677536.8748 | 16751444.2824
|  |  |  | Azimpur | 13984176.3731
|  |  |  | RAMNA | 1466577.1697
|  |  |  | Paribagh | 623153.8648
|  | T&T 33/11 KV |  | Kakrail | 3503992.9743 | 11612333.3273
|  |  |  | Mogbazar | 6422099.8781
|  |  |  | Khilgaon | 1686240.4748
|  | SHERE BANGLANAGAR 33/11KV |  | Shere Bangla Nagar | 3856953.5395 | 7504790.2097
|  |  |  | Shamoly | 2940043.062
|  |  |  | Tejgaon | 706731.4752
|  |  |  | Satmosjit | 1062.133
|  | LALBAGH 33/11KV (GIS) |  | LALBAGH | 20872668.5105 | 23071817.1331
|  |  |  | Kamrangirchar | 2199148.6226
|  | biddut bhabon 33/11KV (GIS) |  | RAMNA | 4658427.5625 | 6048189
|  |  |  | Kakrail | 1389761.4375
|  | Asad Gate 33/11 KV S/S |  | Dhanmondi | 1254710.8224
|  |  |  | Shere Bangla Nagar | 1714563.2448
|  |  |  | Shamoly | 9623430.6336
|  |  |  | Satmosjit | 6098638.0896
|  | Banasree 33/11SS |  | Khilgaon | 1973449.8252
|  |  |  | Bansree | 13322529.811 | 13322529.811
|  | Mugdhapara Hospital 33/11 kV |  | Khilgaon | 611327.4182 | 20279424
|  |  |  | Bashabo | 8731659.9661
|  |  |  | Mugdapara | 4845769.8755
|  |  |  | Maniknagor | 6090666.7403
|  | DMC |  | Bangshal | 2779698.0137
|  |  |  | RAMNA | 2250128.1564 | 4884010.556
|  |  |  | Lalbagh | 2633882.3995
|  | Green Road Dormatory |  | Paribagh | 8566569.3685
|  |  |  | Shere Bangla Nagar | 5806766.2691
|  | BSMMU 33/11KV S/S |  | Kakrail | 2155897.5275
|  |  |  | Paribagh | 3262393.6898
|  | Dhaka Uddyan 33/11KV S/S |  | Adabor | 8450517.1602
|  |  |  | Satmasjid | 5731874.4359
|  | Dhaka University 33/11 KV SS |  | RAMNA | 2067500
|  | Manipuripara 33/11 KV SS |  | Shere Bangla Nagar | 6636976.7111
|  |  |  | Kakrail | 914970.2053
|  |  |  | Tejgaon | 3385941.1983
|  | BGB 33/11 KV SS |  | Kamrangirchar | 5864202.8965
|  |  |  | Jigatola | 5797324.3997
|  |  |  | Azimpur | 4336512.7038
|  | Moghbazar 132/33 KV Boshundhora City |  | Shere Bangla Nagar | 2286948.2926
|  | BB Avenue 33/11 KV SS |  | Narinda | 1913169.7485
|  |  |  | Ramna | 3630229.5247
|  | Jigatola 132/33/11 New Grid |  | Jigatola | 17952101.2033
|  |  |  | Dhanmondi | 2200374.5399
|  | Ispahani 33/11 KV SS |  | Moghbazar | 3051241.4002
|  |  |  | Kakrail | 2885940.8962
|  | Kamrangirchar SS-2 33/11 KV |  | Kamrangirchar | 6050909.9939
|  |  |  | Total=> | 481572295.3977 | 316109846.9705
NORTH ZONE TOTAL=>
|  | NOCS |  | 481572295.3977 |  | 200857461
|  | diff |  |  | -481572295.3977
GRID SOUTH
| Sl. No. | Name of S/S |  | NOCS | import | S/S Total
| 1 | Bangabhaban 33/11KV S/S |  | Maniknagar | 0 | 6252000
|  |  |  | RAMNA | 0
|  |  |  | Swamibagh | 0
|  |  |  | Kamalapur | 6252000
| 2 | Narinda 33/11KV S/S |  | Maniknagar | 552771.4205 | 18637875.7861
|  |  |  | Swamibagh | 5964999.8962
|  |  |  | Postogola | 0
|  |  |  | Banglabazar | 0
|  |  |  | Lalbagh | 0
Motijeel
|  |  |  | Narinda | 12120104.4695
` | 3 | Kumertully 33/11KV |  | Lalbagh | 0 | 10162012.7371
|  |  |  | Bangshall | 0
|  |  |  | Banglabazar | 10162012.7371
| 4 | Maderteck 33/11KV S/S |  | Banosree | 4554305.3496 | 20779104.5894
|  |  |  | Bashabo | 2047460.5279
|  |  |  | Maniknagar | 99804.6
|  |  |  | Mugdapara | 14077534.1118
| 5 | Kazla 33/11KV S/S |  | Matual | 1280357.0984 | 38963887.131
|  |  |  | Jurain | 9476665.367
|  |  |  | Swamibagh | 2092254.4374
|  |  |  | Maniknagar | 2448849.1277
|  |  |  | Shyampur | 2221373.5062
|  |  |  | Kazla | 21444387.5943
|  | Shyampur 132/11KV S/S |  | Shyampur | 29083086.7566 | 30255998.9283
|  |  |  | Fatullah. | 1172912.1717
| 6 | Shyampur 33/11KV S/S |  | Jurain | 0 | 23879567.8107
|  |  |  | Fatullah | 1192381.081
|  |  |  | Shyampur | 22687186.7297
| 7 | Shyampur BISIC 33/11KV S/S |  | Shyampur | 5572899.4572 | 17434019.5614
|  |  |  | Jurain | 11861120.1042
| 8 | Postogola 33/11KV S/S |  | Jurain | 8714695.7388 | 17853408
|  |  |  | Banglabazar | 0
|  |  |  | Postogola | 9138712.2612
| 9 | Fatullah 33/11KV S/S |  | Fatullah | 11962739.7437 | 13386655.9621
|  |  |  | Narayanganj (West) | 1168590.2179
|  |  |  | Shitalakhy | 1423916.2183
| 10 | Sitalakhya 33/11KV S/S |  | Narayanganj (East) | 975921.5951 | 16526592.9727
|  |  |  | Shitalakhy | 9857945.0696
|  |  |  | Narayanganj (West) | 3193433.8589
|  | Sitalakhya 33/11KV S/S |  | Shitalakhy | 2499292.449
|  | Ngonj BSCIC 33/11KV S/S |  | Shitalakhy | 982770.4437
| 11 |  |  | Narayanganj (West) | 13030459.1704 | 14013229.6141
|  | Char Syedpuri 33/11KV S/S |  | Shitalakhy | 0 | 0
| 12 |  |  | Narayanganj (West) | 0
|  | Siddhirganj 133/33KV S/S |  | Siddhirganj | 14258219.1714 | 14258219.1714
| 13 | Siddhirganj 33/11KV S/S |  | Siddhirganj | 14719204.1724 | 14719204.1724
|  |  |  | Matuail | 314747.6869
| 14 | Sarulia 33/11KV S/S |  | Demra | 16472664.3 | 19100209.2143
|  |  |  | Matuail | 2627544.9143
|  | Demra 33/11KV S/S |  | Matuail | 7444732.2205 | 23655340.3996
| 15 |  |  | Demra | 2535452.6166
|  |  |  | Siddhirganj | 13675155.5624
|  | Mandalpara 33/11KV S/S |  | Shitalakhy | 1319788.4916
| 16 |  |  | Narayanganj (East) | 5339784.9449 | 14295059.7745
|  |  |  | Narayanganj (West) | 8955274.8295
| 16 | Khanpur 33/11KV S/S |  | Narayanganj (West) | 4172006.1234 | 17521159.6958
|  |  |  | Narayanganj (East) | 13349153.5725
| 17 | Matuail 33/11KV S/S |  | Narayanganj (East) | 4975780.3128 | 18607060.5479
|  |  |  | Jurain | 0
|  |  |  | Shyampur | 253586.2715
|  |  |  | Fatullah | 4044954.3925
|  |  |  | Matuail | 9332739.571
| 18 | Modongonj 132/33 KV S/S |  | Shitalakhy | 3210156 | 3210156
| 19 | Maniknagar33/11kv s/s 132/33 KV S/S |  | Maniknagar | 605078.9898
|  |  |  | Maniknagar | 11500968.2039 | 11500968.2039
|  | IG Gate 33/11 kv |  | Swamibagh | 5772915.0177 | 17944172.2407
|  |  |  | Banglabazr | 5208186.4076
|  |  |  | Postogola | 6963070.8154
|  | Motijil 33/11kv |  | kamlapur | 8289983.3426 | 8790600
|  |  |  | RAMNA | 500616.6574
|  | Mitford 33/11kv |  | Banshal | 8205877.8549 | 9224766
|  |  |  | Lalbagh | 1018888.1451
|  | Nandalalpr 33/11 kV SS |  | Shyampur | 5631294.0447 | 12665897.97
|  |  |  | Fatullah | 3989861.9665
|  |  |  | Matuail | 3044741.9588
|  | MI CEMENT |  | Shitalakhy | 10749120 | 10749120
|  | Dapa 33/11 kV |  | Fatullah | 11101519.8642 | 11101519.8642
|  | Laxmi Narayan Cotton Mill |  | N Gonj (East) | 7160177.4602 | 15686602
|  |  |  | Siddhirganj | 8526424.5398
|  | Amulia 33/11 KV SS |  | Mugdapara | 1293034.7969 | 6968346.1855
|  |  |  | Demra | 5675311.3886
|  | New Fatullah 33/11 KV SS |  | Sitalakhya | 11872500
|  | P&T 33/11 KV SS |  | Motijeel | 2396639.1991
|  |  |  | RAMNA | 3607446.4976
|  |  |  | Rajarbagh | 3272276.6555
|  | Kazla 132/33 KV SS |  | Kazla | 17342912.2999
|  | Kamalapur Railway 33/11 KV SS |  | Rajarbagh | 6134101.0023
|  |  |  | Motijeel | 3018129.9568
|  | 132 KV Char Syedpur SS |  | Sitalakhya | 23716685.3323
|  | 132/33/11 KV Motijheel SS |  | Motijeel | 2479218.6838
|  |  |  | Swamibagh | 1338142.3292
|  |  |  | Narinda | 229344.2319
|  |  |  | Total=> | 536958356.1075 | 424386286.4832
| South Zone |  |  |  | 512599242.3251
| NOCS |  |  |  | 536958356.1075
| Diff zone&Nocs |  |  |  | -24359113.7823
|  |  |  | Diff= | 0

## Forwarding
Forwarding
NOCS | Provisional Import | Final Import | Diff | % of Increase/ Decrease
Tejgaon | 33326427.9121 | 34031890.1848 | 705462.2727 | 2.0729
Kakrail | 26542949.8477 | 28375284.9016 | 1832335.0539 | 6.4575
Moghbazar | 20914248.216 | 21329436.2056 | 415187.9896 | 1.9465
Khilgaon | 16885238.3373 | 16918091.0673 | 32852.73 | 0.19419
Satmosjid | 23263785.2371 | 23421031.5433 | 157246.3062 | 0.67139
Sherebanglanagar | 25060986.3423 | 25550090.7434 | 489104.401 | 1.9143
Dhanmondi | 24559325.7701 | 24788375.0068 | 229049.2367 | 0.92402
Jhigatala | 28755390.4901 | 29481491.9766 | 726101.4865 | 2.4629
Azimpur | 19894403.1357 | 20094312.838 | 199909.7023 | 0.99486
Paribagh | 36106922.2961 | 36086512.9374 | -20409.3587 | -0.056557
Shyamoli | 18256801.2634 | 19659362.7576 | 1402561.4942 | 7.1343
Adabor | 33991693.0318 | 33945911.5689 | -45781.4629 | -0.13487
Lalbagh | 35248383.1173 | 32545410.1246 | -2702972.9927 | -8.3052
Kamrangirchar | 40610208.52 | 38848556.6907 | -1761651.8293 | -4.5347
Ramna | 28248495.4309 | 29132056.3783 | 883560.9474 | 3.033
Rajarbagh | 19358621.1692 | 19542983.0087 | 184361.8395 | 0.94337
Bashabo | 14802303.8161 | 15301078.259 | 498774.4429 | 3.2597
Bonoseeri | 26067833.1015 | 26579332.7573 | 511499.6559 | 1.9244
Motijheel | 23157371.0896 | 22930447.2198 | -226923.8698 | -0.98962
Mughdapara | 19531394.45 | 20216338.7843 | 684944.3342 | 3.3881
Banglabazar | 17151582.8188 | 16797076.4051 | -354506.4137 | -2.1105
Bongshal | 20320381.2069 | 18936614.1209 | -1383767.086 | -7.3074
Narinda | 14687870.9921 | 15837103.8048 | 1149232.8127 | 7.2566
Swamibagh | 15102409.2817 | 15168311.6806 | 65902.399 | 0.43447
Kazla | 37908086.6755 | 38787299.8942 | 879213.2187 | 2.2668
Maniknagar | 20926873.0633 | 21298139.082 | 371266.0188 | 1.7432
Shyampur | 70614491.3479 | 65449426.7658 | -5165064.582 | -7.8917
Matuail | 23789745.4001 | 24044863.4499 | 255118.0499 | 1.061
Postogola | 16221258.1373 | 16101783.0766 | -119475.0607 | -0.742
Jurain | 29718071.1615 | 30052481.21 | 334410.0485 | 1.1128
Narayangonj-West | 30810293.9579 | 30519764.2002 | -290529.7578 | -0.95194
Narayangonj-East | 31744596.4334 | 31800817.8855 | 56221.4521 | 0.17679
Damra | 24103097.7168 | 24683428.3053 | 580330.5884 | 2.3511
Siddhirgonj | 51252886.2733 | 51179003.4461 | -73882.8273 | -0.14436
Fatulla | 33019604.8442 | 33464369.2197 | 444764.3755 | 1.3291
Shitalakha | 63181001.7532 | 65632174.0045 | 2451172.2513 | 3.7347
TOTAL=> | 1015135033.6381 | 1018530651.5052 | 3395617.8671 | 0.33338

## Sheet2 (hidden)
NOCS
| 15 | Substation_Name
A1-Motijheel | Motijheel | Amulia 33/11 kv | 1 | Amulia 33/11 kv
A2-Khilgaon | Khilgaon | Asad Gate 33/11 KV S/S | 2 | Asad Gate 33/11 KV S/S
A3-Lalbag | Lalbag | Azimpur 33/11 KV | 3 | Azimpur 33/11 KV,
A4-Kazla | Kazla | Banasree 33/11 SS | 4 | Banasree 33/11 SS
A5-Postogola | Postogola | Bangabhaban 132/11KV S/S | 5 | Bangabhaban 132/11KV S/S
A6-Banglabazar | Banglabazar | Banshal 33/11KV S/S | 6 | Banshal 33/11KV S/S
A7-N.Gonj (West) | N.Gonj (West) | BB Aveneu 33/11 KV S/S | 7 | BB Aveneu 33/11 KV S/S
A8-Siddirgonj | Siddirgonj | BGB 33/11 KV S/S | 8 | BGB 33/11 KV S/S
A9-Bashabo | Bashabo | Biddyut Bhaban 33/11 KV | 9 | Biddyut Bhaban 33/11 KV
B1-Narinda | Narinda | BSMMU 33/11KV S/S | 10 | BSMMU 33/11KV S/S
B2-Maniknagar | Maniknagar | Char Syedpur 132/33KV S/S | 11 | Char Syedpur 132/33KV S/S
B3-Jurain | Jurain | Char Syedpur 33/11 KV S/S New | 12 | Char Syedpur 33/11 KV S/S New
B4-Shyampur | Shyampur | Dapa 33/11 kV | 13 | Dapa 33/11 kV
B5-Swamibag | Swamibag | Demra 33/11KV S/S | 14 | Demra 33/11KV S/S
B6-Bangshal | Bangshal | Dhaka Uddyan 33/11 KV S/S | 15 | Dhaka Uddyan 33/11 KV S/S
B7-N.Gonj (East) | N.Gonj (East) | Dhaka University 132/33 KV S/S | 16 | Dhaka University 132/33 KV S/S
B8-Fatullah | Fatullah | Dhaka University 33/11 KV S/S | 17 | Dhaka University 33/11 KV S/S
B9-Mugdapara | Mugdapara | Dhanmondi 132/33/11KV S/S | 18 | Dhanmondi 132/33/11KV S/S
C1-Tejgaon | Tejgaon | Dhanmondi 33/11KV S/S | 19 | Dhanmondi 33/11KV S/S
C2-Satmasjid | Satmasjid | DMC 33/11 KV SS | 20 | DMC
|  | Fatullah New 132/33 KV SS | 66 | Fatullah Old 33/11KV S/S
|  | Fatullah New 33/11 KV SS | 67 | Goran 33/11KV S/S
C3-Paribag | Paribag | Fatullah OLD 33/11KV S/S | 21 | Green Road 33/11KV S/S
C6-Kakrail | Kakrail | Goran 33/11KV S/S | 22 | Green Road Dormatory 33/11 SS
D1-Moghbazar | Moghbazar | Green Road 33/11KV S/S | 23 | IG Gate GIS 33/11 kV
D2-Dhanmondi | Dhanmondi | Green Road Dormatory 33/11 SS | 24 | Ispahani 33/11 KV S/S
D3-Ramna | Ramna | IG Gate GIS 33/11 kV | 25 | Japan Garden 33/11 KV,
D4-Shyamoli | Shyamoli | Ispahani 33/11 KV SS | 26 | Jigatola 132/33 KV S/S
D5-Shere b.nagar | Shere b.nagar | Japan Garden 33/11 KV | 27 | Jigatola 33/11KV S/S
D6-Rajarbag | Rajarbag | Jigatola 132/33 KV S/S | 28 | Jigatola New 33/11 KV S/S
D9-Azimpur | Azimpur | Jigatola New 33/11 KV S/S | 30 | Kakrail 33/11KV S/S
D8-Jigatola | Jigatola | Jigatola Old 33/11KV S/S | 29 | Kallyanpur & Agargaon 33/11KV S/S
E1-Demra | Demra | Kakrail 33/11KV S/S | 31 | Kamalapur Railway 33/11 KV SS
E2-Matuail | Matuail | Kallyanpur 33/11KV S/S | 32 | Kamrangirchar 132/33/11KV S/S
E3-Sytalakhya | Sytalakhya | Kamalapur Railway 33/11 KV SS | 33 | Kamrangirchar 33/11KV S/S
F1-Kamrangirchar | Kamrangirchar | Kamrangirchar 132/33/11KV S/S | 34 | Kawranbazar 33/11KV S/S
F2-Banosree | Banosree | Kamrangirchar 33/11KV S/S | 35 | Kazla 33/11KV S/S
|  | Kamrangirchar-2 33/11 KV S/S | 88 | Kazla 132/133 KV SS
G1-Adabor | Adabor | Kawranbazar 33/11KV S/S | 36 | Khanpur 33/11KV S/S
|  | Kazla 33/11KV S/S | 37 | Khillgaon 33/11KV S/S
|  | Kazla 132/133 KV SS | 38 | Kumertuly 33/11KV S/S
|  | Khanpur 33/11KV S/S | 39 | LALBAGH 132/33 KV S/S
|  | Khillgaon 33/11KV S/S | 40 | LALBAGH 33/11 KV S/S
|  | Kumertuly 33/11KV S/S | 41 | Lalbagh 33/11KV S/S
|  | LALBAGH 132/33 KV S/S | 42 | Lalmatia 33/11KV S/S
|  | LALBAGH New 33/11 KV S/S | 43 | Laxmi Narayan Cotton Mill 33/11 kV
|  | Lalbagh Old 33/11KV S/S | 44 | Madarteck 132/33KV S/S
|  | Lalmatia 33/11KV S/S | 45 | Madarteck 33/11KV S/S
|  | Laxmi Narayan Cotton Mill 33/11 kV | 46 | Maniknagar 132/33/11KV S/S
|  | Madarteck 132/33KV S/S | 47 | Maniknagar 33/11KV S/S
|  | Madarteck 33/11KV S/S | 48 | Matuail 132/33 KV S/S
|  | Maniknagar 132/33 S/S | 50 | Matuail 33/11KV S/S
|  | Maniknagar 33/11 KV SS | 51 | Mitford 33/11 kV
|  | Matuail 132/33 KV S/S | 52 | Moghbazar 132/33/11KV S/S
|  | Matuail 33/11KV S/S | 53 | Moghbazar 33/11KV S/S
|  | MI CEMENT 132/33 kV | 89 | Moghbazar T&T 33/11 KV,
|  | Mitford 33/11 kV | 54 | Mondalpara 33/11KV S/S
|  | Moghbazar 132/33/11KV S/S | 55 | Monipuripara 33/11 KV S/S
|  | Moghbazar 33/11KV S/S | 56 | Motijheel 132/33 KV SS
|  | Mondalpara 33/11KV S/S | 49 | Motijheel 33/11 KV SS (new)
|  | Monipuripara 33/11 KV S/S | 57 | Motijheel Old 33/11 kV
|  | Motijheel 132/33 KV SS | 58 | Mugdhapara Hospital
|  | Motijheel 33/11 KV SS (new) | 59 | Nandalalpur 33/11 kV
|  | Motijheel old 33/11 kV | 60 | Narayangonj (west) BSCIC33/11KV S/S
|  | Mugdhapara Hospital 33/11 KV SS | 61 | Narinda 132/33KV S/S
|  | Nandalalpur 33/11 kV | 62 | Narinda 33/11KV S/S
|  | Narayangonj BSCIC 33/11KV S/S | 63 | New Fatullah 132/33 KV SS
|  | Narinda 132/33KV S/S | 64 | New Fatullah 33/11 KV SS
|  | Narinda 33/11KV S/S | 65 | New Ramna 33/11KV S/S
|  | New Ramna 33/11KV S/S | 68 | P & T 33/11 KV SS
|  | P & T 33/11 KV SS | 69 | Postogola 132/33 KV S/S
|  | Postogola 132/33 KV S/S | 70 | Postogola 33/11KV S/S
|  | Postogola 33/11KV S/S | 71 | Sarulia 33/11KV S/S
|  | Sarulia 33/11KV S/S | 72 | Satmasjid 33/11KV S/S
|  | Satmasjid 33/11KV S/S | 73 | Shatmasjid 132/33 KV S/S
|  | Shatmasjid 132/33 KV S/S | 74 | SHERE BANGLA NAGAR 33/11 KV S/S
|  | SHERE BANGLA NAGAR 33/11 KV S/S | 75 | Shyampur 132/33KV S/S
|  | Shyampur 132/33KV S/S | 76 | Shyampur 33/11KV S/S
|  | Shyampur 33/11KV S/S | 77 | Shyampur BISIC 33/11KV S/S
|  | Shyampur BISIC 33/11KV S/S | 78 | Siddhirganj 33/11KV S/S
|  | Siddhirganj 33/11KV S/S | 79 | Siddhirganj 132/33/11KV S/S
|  | Siddhirganj 132/33/11KV S/S | 80 | Sitalakhya 132/33KV S/S
|  | Sitalakhya 132/33KV S/S | 81 | Sitalakhya 33/11KV S/S
|  | Sitalakhya 33/11KV S/S | 82 | Taltola 33/11KV S/S
|  | T&T 33/11 KV | 83 | Tejgoan 33/11KV S/S
|  | Taltola 33/11KV S/S | 84 | Ullon 132/33/11KV S/S
|  | Tejgoan 33/11KV S/S | 85 | Ullon local 33/11KV S/S
|  | Ullon 132/33/11KV S/S | 86 | Kamrangirchar-2 33/11 KV S/S
|  | Ullon local 33/11KV S/S | 87 | MI CEMENT 132/33 kV

## Linked_33KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2210.16 | 2234.48 | 24.32 | 720000 | 17510400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2179.89 | 2203.57 | 23.68 | 720000 | 17049600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1898.61 | 1933.1 | 34.49 | 720000 | 24832800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1780.89 | 1802.6 | 21.71 | 480000 | 10420800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2052.39 | 2082.67 | 30.28 | 240000 | 0 | 7267200 | 7271355.7389 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2349.96 | 2383.66 | 33.7 | 240000 | 0 | 8088000 | 8092625.1123 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1451.13 | 1460.93 | 9.8 | 240000 | 0 | 2352000 | 2353344.9882 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 804.13 | 826.76 | 22.63 | 240000 | 0 | 5431200 | 5434305.8247 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1826.25 | 1843.63 | 17.38 | 240000 | 0 | 4171200 | 4173585.2953 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1176.39 | 1192.37 | 15.98 | 240000 | 0 | 3835200 | 3837393.1542 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 391.38 | 405.5 | 14.12 | 240000 | 0 | 3388800 | 3390737.8809 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2059.78 | 2087.7 | 27.92 | 240000 | 0 | 6700800 | 6704631.8438 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1589.15 | 1612.37 | 23.22 | 240000 | 0 | 5572800 | 5575986.7985 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 694.88 | 710.95 | 16.07 | 240000 | 0 | 3856800 | 3859005.5061 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1942.41 | 1978.52 | 36.11 | 240000 | 0 | 8666400 | 8671355.8696 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1809.7 | 5.33 | 240000 | 0 | 1279200 | 1279931.5089 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 145.23 | 151.65 | 6.42 | 240000 | 0 | 1540800 | 1541681.1045 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1379.43 | 1411.09 | 31.66 | 240000 | 0 | 7598400 | 7602745.1352 | 0 | Dhanmondi 132/33/11KV S/S

## Linked_132KV (hidden)
Sl. No. | Name of Feeder/Transformer. | Meter |  |  | CF | Active Energy Reading at 00:00 Hr. on |  |  | OMF | Active Energy in kWh |  | Corrected |  | Remarks | CODE
|  | Possition |  | Number |  | Reading at 00.00hr 01.08.2023 | Reading at 00.00hr 01.08.2023 | Difference |  | kWh (Impt.) | kWh (Expt.) | for Loss | NOCS
1 | 2 | 4 |  | 5 | 7 | 9 | 9 | 10=9-8 | 11 | 12=11*10*7 | 13=11*10*7 | 14 | 15 | 16 | 17
7 | 132/33 kV GT-1 Incoming | 33 | IMPORT | BD001860 | 1 | 2210.16 | 2234.48 | 24.32 | 720000 | 17510400 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
12 | 132/33 kV GT-2 Incoming | 33 | 0 | BD001818 | 1 | 2179.89 | 2203.57 | 23.68 | 720000 | 17049600 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
17 | 132/33 kV GT-3 Incoming | 33 | 0 | BD001863 | 1 | 1898.61 | 1933.1 | 34.49 | 720000 | 24832800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
24 | 132/33 kV GT-4 Incoming | 33 | 0 | BD001916 | 1 | 1780.89 | 1802.6 | 21.71 | 480000 | 10420800 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
6 | 33/11 kV 20/28 MVA T-1 | 33 | 0 | BD001861 | 1 | 2052.39 | 2082.67 | 30.28 | 240000 | 0 | 7267200 | 7271355.7389 | 0 | Dhanmondi 132/33/11KV S/S
14 | 33/11 kV 20/28 MVA T-2 | 33 | 0 | BD001892 | 1 | 2349.96 | 2383.66 | 33.7 | 240000 | 0 | 8088000 | 8092625.1123 | 0 | Dhanmondi 132/33/11KV S/S
5 | New Ramna Circuit-1 | 33 | 0 | BD001919 | 1 | 1451.13 | 1460.93 | 9.8 | 240000 | 0 | 2352000 | 2353344.9882 | 0 | Dhanmondi 132/33/11KV S/S
8 | Kakrail Circuit-1 | 33 | 0 | BD001825 | 1 | 804.13 | 826.76 | 22.63 | 240000 | 0 | 5431200 | 5434305.8247 | 0 | Dhanmondi 132/33/11KV S/S
9 | Kawran Bazar Circuit-1 | 33 | 0 | BD001820 | 1 | 1826.25 | 1843.63 | 17.38 | 240000 | 0 | 4171200 | 4173585.2953 | 0 | Dhanmondi 132/33/11KV S/S
10 | New Ramna Circuit-2 | 33 | 0 | BD001816 | 1 | 1176.39 | 1192.37 | 15.98 | 240000 | 0 | 3835200 | 3837393.1542 | 0 | Dhanmondi 132/33/11KV S/S
11 | Kawran BazarCircuit-2 | 33 | 0 | BD001894 | 1 | 462.43 | 462.43 | 0 | 240000 | 0 | 0 | 0 | 0 | Dhanmondi 132/33/11KV S/S
13 | DMC Hospital Feeder | 33 | 0 | BD001840 | 1 | 391.38 | 405.5 | 14.12 | 240000 | 0 | 3388800 | 3390737.8809 | 0 | Dhanmondi 132/33/11KV S/S
15 | Green Road Circuit-2 (U/G) | 33 | 0 | BD001918 | 1 | 2059.78 | 2087.7 | 27.92 | 240000 | 0 | 6700800 | 6704631.8438 | 0 | Dhanmondi 132/33/11KV S/S
16 | Kakrail Circuit-2 | 33 | 0 | BD001821 | 1 | 1589.15 | 1612.37 | 23.22 | 240000 | 0 | 5572800 | 5575986.7985 | 0 | Dhanmondi 132/33/11KV S/S
18 | BSMMU Hospital Circuit-1 | 33 | 0 | BD001920 | 1 | 694.88 | 710.95 | 16.07 | 240000 | 0 | 3856800 | 3859005.5061 | 0 | Dhanmondi 132/33/11KV S/S
19 | Azimpur Circuit-1 | 33 | 0 | BD001822 | 1 | 1942.41 | 1978.52 | 36.11 | 240000 | 0 | 8666400 | 8671355.8696 | 0 | Dhanmondi 132/33/11KV S/S
20 | Azimpur Circuit-2 | 33 | 0 | BD001857 | 1 | 1804.37 | 1809.7 | 5.33 | 240000 | 0 | 1279200 | 1279931.5089 | 0 | Dhanmondi 132/33/11KV S/S
22 | BSMMU Hospital Circuit-2 | 33 | 0 | BD001862 | 1 | 145.23 | 151.65 | 6.42 | 240000 | 0 | 1540800 | 1541681.1045 | 0 | Dhanmondi 132/33/11KV S/S
23 | Green Road Circuit-1 | 33 | 0 | BD001865 | 1 | 1379.43 | 1411.09 | 31.66 | 240000 | 0 | 7598400 | 7602745.1352 | 0 | Dhanmondi 132/33/11KV S/S